## Disclaimer
Subtransmission Feeder Forecast
(Ergon Energy Distribution Annual Planning Report 2020)
This workbook forms part of the Ergon Energy Distribution Annual Planning Report 2020 (DAPR) and should be read in conjunction with the report document.
Readers are encouraged to take into account the details and content portrayed in the ‘Introduction & Notes’ section of this workbook when reviewing the associated data.
Disclaimer
Ergon Energy’s Distribution Annual Planning Report (DAPR) is prepared and made available solely for information purposes. While care was taken in the preparation of the information in the DAPR, and it is provided in good faith, Ergon Energy accepts no responsibility or liability (including without limitation, liability to any person by reason of negligence or negligent mis-statement) for any loss or damage that may be incurred by any person acting in reliance on this information or assumptions drawn from it, except to the extent that liability under any applicable Queensland or Commonwealth of Australia statute cannot be excluded.
It contains assumptions regarding, among other things, economic growth and load forecasts which may or may not prove to be correct. The forecasts included in the DAPR involve subjective judgements and analysis which are subject to significant uncertainties and contingencies, many of which are out of the control of Ergon Energy. Ergon Energy makes no representation or warranty as to the accuracy, reliability, completeness or suitability for any particular purpose of the information in this document. All information should be independently investigated, reviewed, analysed and verified, and must not be relied upon in connection with any investment proposal or decision. The information contained in the DAPR is subject to annual review. Ergon Energy is obligated to publish future editions by 31st December, in accordance with the National Electricity Rules.
All financials presented in the DAPR or within this document are correct at the time of writing and represent the existing organisational accounting treatment, which may be subject to change. Energy Queensland is finalising the alignment of its Cost Allocation Methodology between Ergon Energy and Energex, potentially impacting the treatment of some Capital and Operational Project costs.
Forecasted data is subject to ongoing variation due to COVID 19 impacts.

## Introduction & Notes
Subtransmission Feeder Forecast
(Ergon Energy Distribution Annual Planning Report 2020)
This workbook provides a forecast of Subtransmission Capacity constraints based on SIFT 10PoE temperature corrected forecast.
Forecast: 10 2020 Forecast | 47 2020 Base Forecast (Updated) | Approved Projects | 10PoE
Daily Load Profiles: SIFT 2019 Substation Profiles
Powerlink Model Used: Powerlink 2020 Load Flow Model, converted from PSSE to PowerFactory
PowerFactory Model: \bg036.IntUser\TransSubtrans_2020_LoadFlow.IntPrj
Model Version: V1-13-16 10Poe
Derived From: TransSubtrans_2020\V-1-13-16 MACT Vector Group
Process:
1 - Load Flow run for every half hour period during a Summer Day for each year
2 - Loading for All Lines are Recorded for each period
3 - Line with highest % of Rated A for each Feeder is recorded as the constrained element. If you two elements have the same % of Rated A, the line with higher Loading (A) is used
Limitations:
Each Feeder reports the most constrained element, not the highest loaded element
Exclusions:
Distribution Feeders
Feeders that supply single Customers
Charleville, Quilpie and Cunnamulla Feeders (See note)
7227 Woree to Cairns Terminal (see note)
NOTES:
Charleville, Quilpie and Cunnamulla Feeders
The feeders supplying Charleville, Quilpie and Cunnamulla substations have been excluded from this report due to modelling limitations.
When modelled as near coincident 50PoE temperature corrected loads as per the remaining model incorrect load flow results are produced.
This is because the area is voltage limited and relies upon an SVC at Charleville to produce stable voltages,
the coincident loads lead to voltage problems and the modelled SVC control system and load flow package drives the SVC beyond real limitations to produce convergence making the results invalid.
Modelling of the highest coincident load in 2020 had the lines operating below of rated capacity and stable voltages which indicates the lines ratings are not the limiting factor.
In addition, the 50PoE substation forecast does not indicate significant expected growth for the relevant substation.
Region ECORP ID Operational Number Feeder Name
SW 60026706 F214R CHARLEVILLE
SW 60026727 F257C QUILPIE
SW 60026726 F254C CUNNAMULLA
Woree to Cairns Terminal Feeder
This feeder is nominally owned in source data by Powerlink so is excluded by the data process. A section is owned by Ergon Energy but is not constrained.
Region ECORP ID Operational Number Feeder Name
FN 83842672 7227 WORE - CATE FDR
Explanation of some know issues and solutions
These feeders are overloaded due to a ramp-back scheme associated with the solar farm not being modelled
734 MR - Yarranlea
733 MR - Yarranlea
There is currently a substation rebuild planned which will unload this feeder
From EHBS to GASS / MASS&MLSS
Solar Farm Export
With a significant increase in the number of solar farms in the model how the export of solar farms is calculated has been changed.
Solar Farms that have been commissioned have been filled with a profile based on historical data.
All data since commissioning has been used to form a per unit maximum export daily profile, and days with a potential issue(s) removed.
Issues Causing Data Exclusion include:
1. Days with significant export and import from a mono directional solar farm
2. Days with export significantly above the rated capacity of the solar farm (more than 5% above rated)
3. The max value experienced is less than 67% of installed capacity (for exclusion of a maximum day)
4. The timestamps of the time series data are misaligned (The whole set of data for this solar farm was affected and ignored)
The top 50 valid days are over-lapped, and the highest value seen in each half hour time slot is recorded into the characteristic and scales the installed capacity
In addition, to prevent farms with no Q export when P is zero, farms without this occurring in historic data have had values below 0.1% of installed capacity are set to zero
For Solar Farms without historic data the worst case seen by the collection of solar farms was used.
Forecasted data is subject to ongoing variation due to COVID 19 impacts.

## SubtransmissionFdrForecast10PoE
[5 empty] | Year | 2021 | 2021 | 2021 | 2022 | 2022 | 2022 | 2023 | 2023 | 2023 | 2024 | 2024 | 2024 | 2025 | 2025 | 2025
[5 empty] | Ratings Period | SD | SE | SNM | SD | SE | SNM | SD | SE | SNM | SD | SE | SNM | SD | SE | SNM
Region | ECORP ID | Operational Number | Feeder Name | PF Feeder Obj Name | Variable
CA | 40000958 | 6074 | From LCSS to TANB | 6074_Lakes Creek - Tanby 66 kV
CA | 40000958 | 6074 | From LCSS to TANB | 6074_Lakes Creek - Tanby 66 kV | % of Rated A | 58.1842 | 64.7287 | 41.0205 | 58.5484 | 65.7233 | 41.6408 | 59.3696 | 67.143 | 42.2403 | 59.9727 | 67.3057 | 42.7461 | 60.5375 | 67.8613 | 43.4486
CA | 40000958 | 6074 | From LCSS to TANB | 6074_Lakes Creek - Tanby 66 kV | Loading (A) | 140.8058 | 156.6436 | 99.2697 | 141.6872 | 159.0504 | 100.7708 | 143.6743 | 162.4862 | 102.2216 | 145.134 | 162.8799 | 103.4454 | 146.5007 | 164.2244 | 105.1456
CA | 40000958 | 6074 | From LCSS to TANB | 6074_Lakes Creek - Tanby 66 kV | Power Factor | 0.98157 | 0.98253 | 0.99492 | 0.98464 | 0.98203 | 0.99464 | 0.98396 | 0.98002 | 0.99445 | 0.99509 | 0.99383 | 0.99981 | 0.9972 | 0.99525 | 0.99999
CA | 40000958 | 6074 | From LCSS to TANB | 6074_Lakes Creek - Tanby 66 kV | Rating (A) | 242 | 242 | 242 | 242 | 242 | 242 | 242 | 242 | 242 | 242 | 242 | 242 | 242 | 242 | 242
CA | 40000980 | 6047 | Coominglah Sub Tee | 6047_Coominglah Sub Tee 66 kV
CA | 40000980 | 6047 | Coominglah Sub Tee | 6047_Coominglah Sub Tee 66 kV | % of Rated A | 7.6829 | 7.297 | 5.7819 | 7.6824 | 7.2966 | 5.7816 | 7.6816 | 7.2959 | 5.7812 | 7.6814 | 7.2959 | 5.7813 | 7.6813 | 7.2957 | 5.7812
CA | 40000980 | 6047 | Coominglah Sub Tee | 6047_Coominglah Sub Tee 66 kV | Loading (A) | 11.8317 | 15.1048 | 11.5059 | 11.8309 | 15.104 | 11.5054 | 11.8296 | 15.1024 | 11.5046 | 11.8294 | 15.1024 | 11.5047 | 11.8292 | 15.1021 | 11.5046
CA | 40000980 | 6047 | Coominglah Sub Tee | 6047_Coominglah Sub Tee 66 kV | Power Factor | 0.92601 | 0.92251 | 0.92645 | 0.92602 | 0.92251 | 0.92645 | 0.92602 | 0.92251 | 0.92645 | 0.92602 | 0.92251 | 0.92645 | 0.92602 | 0.92251 | 0.92645
CA | 40000980 | 6047 | Coominglah Sub Tee | 6047_Coominglah Sub Tee 66 kV | Rating (A) | 154 | 207 | 199 | 154 | 207 | 199 | 154 | 207 | 199 | 154 | 207 | 199 | 154 | 207 | 199
CA | 40000983 | 6026 | From T27 to THSS | 6026_Moura - Theodore 66 kV
CA | 40000983 | 6026 | From T27 to THSS | 6026_Moura - Theodore 66 kV | % of Rated A | 14.2208 | 13.0315 | 12.9984 | 14.0974 | 12.9186 | 12.8864 | 14.0967 | 12.9179 | 12.886 | 14.0967 | 12.9179 | 12.8865 | 14.0968 | 12.918 | 12.8867
CA | 40000983 | 6026 | From T27 to THSS | 6026_Moura - Theodore 66 kV | Loading (A) | 103.6689 | 102.0362 | 92.2875 | 102.7691 | 101.1515 | 91.4925 | 102.7639 | 101.1463 | 91.4897 | 102.7639 | 101.1466 | 91.4932 | 102.7646 | 101.147 | 91.4948
CA | 40000983 | 6026 | From T27 to THSS | 6026_Moura - Theodore 66 kV | Power Factor | 0.99377 | 0.99385 | 0.99436 | 0.99382 | 0.9939 | 0.9944 | 0.99382 | 0.9939 | 0.9944 | 0.99382 | 0.9939 | 0.9944 | 0.99382 | 0.9939 | 0.9944
CA | 40000983 | 6026 | From T27 to THSS | 6026_Moura - Theodore 66 kV | Rating (A) | 729 | 783 | 710 | 729 | 783 | 710 | 729 | 783 | 710 | 729 | 783 | 710 | 729 | 783 | 710
CA | 40000986 | 6056 | From EMSS to CMSS | 6056_Comet - Emerald 66 kV
CA | 40000986 | 6056 | From EMSS to CMSS | 6056_Comet - Emerald 66 kV | % of Rated A | 68.951 | 42.1066 | 81.1869 | 68.9412 | 42.0946 | 81.1774 | 68.8888 | 42.0192 | 81.1225 | 68.8143 | 41.9209 | 81.046 | 68.7959 | 41.8968 | 81.0271
CA | 40000986 | 6056 | From EMSS to CMSS | 6056_Comet - Emerald 66 kV | Loading (A) | 230.2963 | 141.8993 | 237.0658 | 230.2637 | 141.8588 | 237.0381 | 230.0887 | 141.6047 | 236.8777 | 229.8397 | 141.2735 | 236.6544 | 229.7782 | 141.1923 | 236.5992
CA | 40000986 | 6056 | From EMSS to CMSS | 6056_Comet - Emerald 66 kV | Power Factor | 0.80935 | 0.70768 | 0.80679 | 0.80933 | 0.70763 | 0.80677 | 0.80916 | 0.70697 | 0.80662 | 0.80909 | 0.70659 | 0.80655 | 0.80904 | 0.70641 | 0.80651
CA | 40000986 | 6056 | From EMSS to CMSS | 6056_Comet - Emerald 66 kV | Rating (A) | 334 | 337 | 292 | 334 | 337 | 292 | 334 | 337 | 292 | 334 | 337 | 292 | 334 | 337 | 292
CA | 40000987 | 6065 | From H15 to TMSS | 6065_Lilyvale - Tieri Tee 66 kV
CA | 40000987 | 6065 | From H15 to TMSS | 6065_Lilyvale - Tieri Tee 66 kV | % of Rated A | 60.4219 | 47.8167 | 60.5612 | 60.4247 | 47.8174 | 60.5631 | 60.4194 | 47.8157 | 60.5591 | 60.4317 | 47.8188 | 60.5658 | 60.2439 | 48.1096 | 60.3707
CA | 40000987 | 6065 | From H15 to TMSS | 6065_Lilyvale - Tieri Tee 66 kV | Loading (A) | 146.8252 | 130.0615 | 150.1917 | 146.8321 | 130.0632 | 150.1965 | 146.8191 | 130.0587 | 150.1867 | 146.8491 | 130.0672 | 150.2031 | 146.3928 | 130.8582 | 149.7193
CA | 40000987 | 6065 | From H15 to TMSS | 6065_Lilyvale - Tieri Tee 66 kV | Power Factor | 0.84482 | 0.95388 | 0.87353 | 0.84478 | 0.95389 | 0.87351 | 0.84485 | 0.95387 | 0.87355 | 0.8447 | 0.9539 | 0.87347 | 0.84297 | 0.95475 | 0.87214
CA | 40000987 | 6065 | From H15 to TMSS | 6065_Lilyvale - Tieri Tee 66 kV | Rating (A) | 243 | 272 | 248 | 243 | 272 | 248 | 243 | 272 | 248 | 243 | 272 | 248 | 243 | 272 | 248
CA | 40000988 | 6067 | Emerald | 6067 Lilyvale - Emerald 66 kV
CA | 40000988 | 6067 | Emerald | 6067 Lilyvale - Emerald 66 kV | % of Rated A | 76.7978 | 59.0826 | 74.099 | 76.8049 | 59.0763 | 74.098 | 76.7392 | 59.1163 | 74.0944 | 76.6737 | 59.1478 | 74.0827 | 76.6815 | 59.1345 | 74.0779
CA | 40000988 | 6067 | Emerald | 6067 Lilyvale - Emerald 66 kV | Loading (A) | 261.8609 | 391.6583 | 675.7825 | 261.8851 | 391.6162 | 675.7726 | 261.661 | 391.8817 | 675.74 | 261.4376 | 392.0909 | 675.6338 | 261.4644 | 392.0027 | 675.5895
CA | 40000988 | 6067 | Emerald | 6067 Lilyvale - Emerald 66 kV | Power Factor | 0.92172 | 0.8919 | 0.88085 | 0.92176 | 0.8919 | 0.88087 | 0.92161 | 0.89225 | 0.88091 | 0.9216 | 0.89268 | 0.88105 | 0.92175 | 0.89267 | 0.88111
CA | 40000988 | 6067 | Emerald | 6067 Lilyvale - Emerald 66 kV | Rating (A) | 341 | 663 | 912 | 341 | 663 | 912 | 341 | 663 | 912 | 341 | 663 | 912 | 341 | 663 | 912
CA | 40000997 | 7153 | Lilyvale - Clermont 132 kV | 7153_Lilyvale - Clermont 132 kV
CA | 40000997 | 7153 | Lilyvale - Clermont 132 kV | 7153_Lilyvale - Clermont 132 kV | % of Rated A | 59.5947 | 46.6799 | 65.8407 | 59.5916 | 46.6752 | 65.8423 | 59.6188 | 46.7122 | 65.8727 | 59.5879 | 46.6648 | 65.8436 | 59.5854 | 46.6692 | 65.8409
CA | 40000997 | 7153 | Lilyvale - Clermont 132 kV | 7153_Lilyvale - Clermont 132 kV | Loading (A) | 421.9306 | 337.9626 | 419.4055 | 421.9085 | 337.9284 | 419.4155 | 422.1014 | 338.196 | 419.6089 | 421.8825 | 337.8528 | 419.4236 | 421.8649 | 337.885 | 419.4067
CA | 40000997 | 7153 | Lilyvale - Clermont 132 kV | 7153_Lilyvale - Clermont 132 kV | Power Factor | 0.96054 | 0.94887 | 0.96013 | 0.96049 | 0.94879 | 0.96009 | 0.96047 | 0.94873 | 0.96007 | 0.96046 | 0.94866 | 0.96005 | 0.96045 | 0.94865 | 0.96005
CA | 40000997 | 7153 | Lilyvale - Clermont 132 kV | 7153_Lilyvale - Clermont 132 kV | Rating (A) | 708 | 724 | 637 | 708 | 724 | 637 | 708 | 724 | 637 | 708 | 724 | 637 | 708 | 724 | 637
CA | 40001012 | 6011 | From T32 to CMSS | 6011_Blackwater - Comet 66 kV
CA | 40001012 | 6011 | From T32 to CMSS | 6011_Blackwater - Comet 66 kV | % of Rated A | 67.0395 | 40.3024 | 79.7297 | 67.0297 | 40.2906 | 79.7201 | 66.9777 | 40.2184 | 79.6651 | 66.903 | 40.1219 | 79.5885 | 66.8847 | 40.0986 | 79.5696
CA | 40001012 | 6011 | From T32 to CMSS | 6011_Blackwater - Comet 66 kV | Loading (A) | 223.909 | 135.8192 | 232.8079 | 223.8765 | 135.7795 | 232.7801 | 223.7027 | 135.5361 | 232.6193 | 223.4534 | 135.2107 | 232.3958 | 223.3921 | 135.1324 | 232.3406
CA | 40001012 | 6011 | From T32 to CMSS | 6011_Blackwater - Comet 66 kV | Power Factor | 0.70315 | 0.57685 | 0.72149 | 0.70313 | 0.57678 | 0.72148 | 0.70298 | 0.57599 | 0.72136 | 0.70297 | 0.5755 | 0.72137 | 0.70293 | 0.57528 | 0.72135
CA | 40001012 | 6011 | From T32 to CMSS | 6011_Blackwater - Comet 66 kV | Rating (A) | 334 | 337 | 292 | 334 | 337 | 292 | 334 | 337 | 292 | 334 | 337 | 292 | 334 | 337 | 292
CA | 40001013 | 6012 | From T32 to BFSS | 6012_Blackwater - Bedford Weir 66 kV
CA | 40001013 | 6012 | From T32 to BFSS | 6012_Blackwater - Bedford Weir 66 kV | % of Rated A | 37.2249 | 38.4756 | 35.4299 | 37.225 | 38.4758 | 35.43 | 37.2237 | 38.4745 | 35.4294 | 37.2249 | 38.4776 | 35.4319 | 36.947 | 38.1781 | 35.1678
CA | 40001013 | 6012 | From T32 to BFSS | 6012_Blackwater - Bedford Weir 66 kV | Loading (A) | 103.4828 | 113.8852 | 93.5328 | 103.4829 | 113.8857 | 93.5331 | 103.4794 | 113.882 | 93.5314 | 103.4827 | 113.891 | 93.5379 | 102.7101 | 113.0046 | 92.8408
CA | 40001013 | 6012 | From T32 to BFSS | 6012_Blackwater - Bedford Weir 66 kV | Power Factor | 0.98469 | 0.98239 | 0.98757 | 0.98469 | 0.98239 | 0.98757 | 0.98469 | 0.98239 | 0.98757 | 0.98469 | 0.98239 | 0.98757 | 0.98491 | 0.98263 | 0.98778
CA | 40001013 | 6012 | From T32 to BFSS | 6012_Blackwater - Bedford Weir 66 kV | Rating (A) | 278 | 296 | 264 | 278 | 296 | 264 | 278 | 296 | 264 | 278 | 296 | 264 | 278 | 296 | 264
CA | 40001019 | 6058 | From BFSS to BGSS | 6058_Bedford Weir - Bingegang 66 kV
CA | 40001019 | 6058 | From BFSS to BGSS | 6058_Bedford Weir - Bingegang 66 kV | % of Rated A | 14.3094 | 13.7856 | 14.8664 | 14.3094 | 13.7857 | 14.8664 | 14.3091 | 13.7853 | 14.8663 | 14.3096 | 13.7863 | 14.8673 | 14.3076 | 13.7838 | 14.866
CA | 40001019 | 6058 | From BFSS to BGSS | 6058_Bedford Weir - Bingegang 66 kV | Loading (A) | 39.7802 | 40.8054 | 39.2472 | 39.7802 | 40.8056 | 39.2473 | 39.7793 | 40.8044 | 39.2469 | 39.7807 | 40.8074 | 39.2498 | 39.7752 | 40.8001 | 39.2462
CA | 40001019 | 6058 | From BFSS to BGSS | 6058_Bedford Weir - Bingegang 66 kV | Power Factor | 0.9982 | 0.9984 | 0.99733 | 0.9982 | 0.9984 | 0.99733 | 0.9982 | 0.9984 | 0.99733 | 0.9982 | 0.9984 | 0.99733 | 0.9982 | 0.9984 | 0.99733
CA | 40001019 | 6058 | From BFSS to BGSS | 6058_Bedford Weir - Bingegang 66 kV | Rating (A) | 278 | 296 | 264 | 278 | 296 | 264 | 278 | 296 | 264 | 278 | 296 | 264 | 278 | 296 | 264
CA | 40001027 | 6085 | From TMSS to TISS | 6085_Tieri Tee - Tieri 66 kV
CA | 40001027 | 6085 | From TMSS to TISS | 6085_Tieri Tee - Tieri 66 kV | % of Rated A | 7.5648 | 7.0428 | 4.5422 | 7.5649 | 7.043 | 4.5423 | 7.5644 | 7.0426 | 4.5422 | 7.5647 | 7.0432 | 4.5426 | 7.5656 | 7.0441 | 4.5431
CA | 40001027 | 6085 | From TMSS to TISS | 6085_Tieri Tee - Tieri 66 kV | Loading (A) | 18.3824 | 19.1565 | 11.2646 | 18.3827 | 19.1569 | 11.2648 | 18.3816 | 19.1559 | 11.2645 | 18.3821 | 19.1575 | 11.2656 | 18.3844 | 19.1598 | 11.2668
CA | 40001027 | 6085 | From TMSS to TISS | 6085_Tieri Tee - Tieri 66 kV | Power Factor | 0.98715 | 0.98707 | 0.98819 | 0.98715 | 0.98707 | 0.98819 | 0.98715 | 0.98707 | 0.98819 | 0.98715 | 0.98707 | 0.98819 | 0.98715 | 0.98707 | 0.98819
CA | 40001027 | 6085 | From TMSS to TISS | 6085_Tieri Tee - Tieri 66 kV | Rating (A) | 243 | 272 | 248 | 243 | 272 | 248 | 243 | 272 | 248 | 243 | 272 | 248 | 243 | 272 | 248
CA | 40001028 | 6086 | From TMSS to MDSS | 6086_Tieri Tee - Middlemount 66 kV
CA | 40001028 | 6086 | From TMSS to MDSS | 6086_Tieri Tee - Middlemount 66 kV | % of Rated A | 78.7068 | 56.5863 | 78.2501 | 78.7092 | 56.5882 | 78.2521 | 78.7043 | 56.5817 | 78.2481 | 78.7136 | 56.5857 | 78.2548 | 78.7635 | 56.6142 | 78.2979
CA | 40001028 | 6086 | From TMSS to MDSS | 6086_Tieri Tee - Middlemount 66 kV | Loading (A) | 191.2575 | 153.9146 | 194.0603 | 191.2635 | 153.92 | 194.0652 | 191.2515 | 153.9022 | 194.0553 | 191.274 | 153.9132 | 194.0718 | 191.3954 | 153.9907 | 194.1788
CA | 40001028 | 6086 | From TMSS to MDSS | 6086_Tieri Tee - Middlemount 66 kV | Power Factor | 0.92888 | 0.95701 | 0.93985 | 0.92886 | 0.95699 | 0.93984 | 0.92889 | 0.95704 | 0.93986 | 0.92883 | 0.95701 | 0.93982 | 0.92851 | 0.9568 | 0.93956
CA | 40001028 | 6086 | From TMSS to MDSS | 6086_Tieri Tee - Middlemount 66 kV | Rating (A) | 243 | 272 | 248 | 243 | 272 | 248 | 243 | 272 | 248 | 243 | 272 | 248 | 243 | 272 | 248
CA | 40001036 | 6019 | From GFSS to T19 | 6019_Gladstone South - Friend St 66 kV
CA | 40001036 | 6019 | From GFSS to T19 | 6019_Gladstone South - Friend St 66 kV | % of Rated A | 16.4302 | 20.0827 | 24.3947 | 16.6736 | 20.2521 | 24.5323 | 16.9362 | 20.3923 | 24.6451 | 16.9299 | 20.4032 | 24.6193 | 23.8934 | 20.5324 | 24.7321
CA | 40001036 | 6019 | From GFSS to T19 | 6019_Gladstone South - Friend St 66 kV | Loading (A) | 40.254 | 68.6829 | 69.5248 | 40.8502 | 69.2621 | 69.9172 | 41.4937 | 69.7418 | 70.2385 | 41.4783 | 69.7789 | 70.165 | 58.5389 | 70.2208 | 70.4866
CA | 40001036 | 6019 | From GFSS to T19 | 6019_Gladstone South - Friend St 66 kV | Power Factor | 0.32358 | 0.70655 | 0.80784 | 0.86614 | 0.71442 | 0.80984 | 0.87196 | 0.72039 | 0.8115 | 0.87209 | 0.72134 | 0.81104 | 0.50344 | 0.72758 | 0.8125
CA | 40001036 | 6019 | From GFSS to T19 | 6019_Gladstone South - Friend St 66 kV | Rating (A) | 245 | 342 | 285 | 245 | 342 | 285 | 245 | 342 | 285 | 245 | 342 | 285 | 245 | 342 | 285
CA | 40001047 | 6020 | GLSO - BORT 6020 | 6020_Gladstone South - BORE 66 kV
CA | 40001047 | 6020 | GLSO - BORT 6020 | 6020_Gladstone South - BORE 66 kV | % of Rated A | 66.5796 | 56.1989 | 48.4605 | 66.952 | 56.5231 | 48.6947 | 66.951 | 56.5221 | 48.6946 | 67.3252 | 56.8483 | 48.9294 | 67.3124 | 57.349 | 49.3441
CA | 40001047 | 6020 | GLSO - BORT 6020 | 6020_Gladstone South - BORE 66 kV | Loading (A) | 140.4807 | 165.7836 | 118.7265 | 141.2664 | 166.7401 | 119.3003 | 141.2642 | 166.7369 | 119.3002 | 142.0539 | 167.6992 | 119.8753 | 142.0268 | 169.1764 | 120.8914
CA | 40001047 | 6020 | GLSO - BORT 6020 | 6020_Gladstone South - BORE 66 kV | Power Factor | 0.99775 | 0.9959 | 0.99887 | 0.9977 | 0.99583 | 0.99884 | 0.9977 | 0.99583 | 0.99884 | 0.99765 | 0.99576 | 0.99881 | 0.99771 | 0.99564 | 0.99874
CA | 40001047 | 6020 | GLSO - BORT 6020 | 6020_Gladstone South - BORE 66 kV | Rating (A) | 211 | 295 | 245 | 211 | 295 | 245 | 211 | 295 | 245 | 211 | 295 | 245 | 211 | 295 | 245
CA | 40001055 | 6079 | From T72 to LRSS | 6079_Barcaldine - Longreach 66 kV
CA | 40001055 | 6079 | From T72 to LRSS | 6079_Barcaldine - Longreach 66 kV | % of Rated A | 51.3886 | 93.9353 | 59.9666 | 51.975 | 92.86 | 59.3443 | 52.5617 | 91.7917 | 58.7236 | 52.5617 | 91.7921 | 58.7239 | 52.5617 | 91.7833 | 58.7213
CA | 40001055 | 6079 | From T72 to LRSS | 6079_Barcaldine - Longreach 66 kV | Loading (A) | 51.3886 | 93.9353 | 59.9666 | 51.975 | 92.86 | 59.3443 | 52.5617 | 91.7917 | 58.7236 | 52.5617 | 91.7921 | 58.7239 | 52.5617 | 91.7833 | 58.7213
CA | 40001055 | 6079 | From T72 to LRSS | 6079_Barcaldine - Longreach 66 kV | Power Factor | 0.99901 | 0.99272 | 0.99964 | 0.99885 | 0.99314 | 0.99953 | 0.99868 | 0.99355 | 0.99941 | 0.99868 | 0.99355 | 0.99941 | 0.99868 | 0.99356 | 0.99941
CA | 40001055 | 6079 | From T72 to LRSS | 6079_Barcaldine - Longreach 66 kV | Rating (A) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
CA | 40001056 | 7154 | Barcaldine | 7154_Clermont - Barcaldine 132 kV
CA | 40001056 | 7154 | Barcaldine | 7154_Clermont - Barcaldine 132 kV | % of Rated A | 60.8371 | 44.0424 | 60.9707 | 60.9125 | 44.1442 | 61.049 | 60.9772 | 44.2187 | 61.1167 | 60.9871 | 44.2317 | 61.1266 | 61.0479 | 44.3291 | 61.1812
CA | 40001056 | 7154 | Barcaldine | 7154_Clermont - Barcaldine 132 kV | Loading (A) | 219.0135 | 172.2059 | 214.0071 | 219.2851 | 172.6037 | 214.2821 | 219.5179 | 172.895 | 214.5195 | 219.5535 | 172.9458 | 214.5544 | 219.7724 | 173.3269 | 214.7461
CA | 40001056 | 7154 | Barcaldine | 7154_Clermont - Barcaldine 132 kV | Power Factor | 0.89877 | 0.84833 | 0.89496 | 0.89897 | 0.84884 | 0.89518 | 0.89913 | 0.84916 | 0.89535 | 0.89917 | 0.84925 | 0.89539 | 0.89941 | 0.84994 | 0.89561
CA | 40001056 | 7154 | Barcaldine | 7154_Clermont - Barcaldine 132 kV | Rating (A) | 360 | 391 | 351 | 360 | 391 | 351 | 360 | 391 | 351 | 360 | 391 | 351 | 360 | 391 | 351
CA | 40001069 | 6077 | Farnborough - Capricorn Resort 66kV | 6077_Farnborough - Capricorn Resort 66kV
CA | 40001069 | 6077 | Farnborough - Capricorn Resort 66kV | 6077_Farnborough - Capricorn Resort 66kV | % of Rated A | 0.068321 | 0.06123 | 0.077577 | 0.068301 | 0.061185 | 0.077556 | 0.068347 | 0.061259 | 0.077592 | 0.068695 | 0.061623 | 0.077799 | 0.068465 | 0.061423 | 0.077636
CA | 40001069 | 6077 | Farnborough - Capricorn Resort 66kV | 6077_Farnborough - Capricorn Resort 66kV | Loading (A) | 0.25962 | 0.25594 | 0.26299 | 0.25954 | 0.25576 | 0.26291 | 0.25972 | 0.25606 | 0.26304 | 0.26104 | 0.25758 | 0.26374 | 0.26017 | 0.25675 | 0.26319
CA | 40001069 | 6077 | Farnborough - Capricorn Resort 66kV | 6077_Farnborough - Capricorn Resort 66kV | Power Factor | 1.414e-06 | 1.4139e-06 | 1.414e-06 | 1.414e-06 | 1.414e-06 | 1.414e-06 | 1.414e-06 | 1.414e-06 | 1.414e-06 | 1.414e-06 | 1.414e-06 | 1.414e-06 | 1.414e-06 | 1.414e-06 | 1.414e-06
CA | 40001069 | 6077 | Farnborough - Capricorn Resort 66kV | 6077_Farnborough - Capricorn Resort 66kV | Rating (A) | 380 | 418 | 339 | 380 | 418 | 339 | 380 | 418 | 339 | 380 | 418 | 339 | 380 | 418 | 339
CA | 40001070 | 6023 | From GFSS to CISS | 6023_Friend St-Clinton Industrial 66 kV
CA | 40001070 | 6023 | From GFSS to CISS | 6023_Friend St-Clinton Industrial 66 kV | % of Rated A | 47.4773 | 45.8179 | 40.4473 | 47.5064 | 45.8523 | 40.4721 | 47.4997 | 45.8511 | 40.4687 | 47.6738 | 46.0061 | 40.5667 | 48.3152 | 46.1432 | 40.6858
CA | 40001070 | 6023 | From GFSS to CISS | 6023_Friend St-Clinton Industrial 66 kV | Loading (A) | 208.4253 | 219.9259 | 157.34 | 208.5531 | 220.0912 | 157.4365 | 208.5235 | 220.0854 | 157.4233 | 209.2878 | 220.8292 | 157.8045 | 212.1037 | 221.4871 | 158.2676
CA | 40001070 | 6023 | From GFSS to CISS | 6023_Friend St-Clinton Industrial 66 kV | Power Factor | 0.96659 | 0.92475 | 0.92594 | 0.96664 | 0.92492 | 0.92605 | 0.96659 | 0.92487 | 0.92599 | 0.96703 | 0.9257 | 0.92658 | 0.91799 | 0.92647 | 0.92727
CA | 40001070 | 6023 | From GFSS to CISS | 6023_Friend St-Clinton Industrial 66 kV | Rating (A) | 439 | 480 | 389 | 439 | 480 | 389 | 439 | 480 | 389 | 439 | 480 | 389 | 439 | 480 | 389
CA | 40001073 | 6001 | From T23 to PHSS | 6001_Glenmore - Parkhurst 66 kV
CA | 40001073 | 6001 | From T23 to PHSS | 6001_Glenmore - Parkhurst 66 kV | % of Rated A | 15.707 | 16.2234 | 14.9475 | 15.1352 | 16.3746 | 15.0511 | 15.8083 | 17.79 | 15.5169 | 16.4154 | 17.6473 | 15.7852 | 16.29 | 17.7745 | 16.0281
CA | 40001073 | 6001 | From T23 to PHSS | 6001_Glenmore - Parkhurst 66 kV | Loading (A) | 62.9064 | 67.8137 | 55.6047 | 60.6923 | 68.446 | 55.9903 | 63.3914 | 74.2836 | 57.7228 | 65.8259 | 73.7656 | 58.7208 | 65.3227 | 74.2975 | 59.6243
CA | 40001073 | 6001 | From T23 to PHSS | 6001_Glenmore - Parkhurst 66 kV | Power Factor | 0.99806 | 0.99393 | 0.95128 | 0.98565 | 0.99436 | 0.95251 | 0.989 | 0.99794 | 0.95774 | 0.9996 | 0.99962 | 0.94607 | 0.97498 | 0.99997 | 0.94079
CA | 40001073 | 6001 | From T23 to PHSS | 6001_Glenmore - Parkhurst 66 kV | Rating (A) | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372
CA | 40001074 | 6003 | From RGBS to BERS | 6003_Glenmore - Berserker 66 kV
CA | 40001074 | 6003 | From RGBS to BERS | 6003_Glenmore - Berserker 66 kV | % of Rated A | 76.0218 | 70.1351 | 56.0557 | 76.3304 | 70.2007 | 55.9815 | 74.8467 | 68.8627 | 55.3143 | 75.669 | 69.8825 | 55.9629 | 75.4714 | 69.2928 | 54.8735
CA | 40001074 | 6003 | From RGBS to BERS | 6003_Glenmore - Berserker 66 kV | Loading (A) | 304.8473 | 293.1647 | 208.5272 | 306.0849 | 293.4389 | 208.2511 | 300.1354 | 287.846 | 205.7691 | 303.4326 | 292.1087 | 208.1819 | 302.6402 | 289.6438 | 204.1293
CA | 40001074 | 6003 | From RGBS to BERS | 6003_Glenmore - Berserker 66 kV | Power Factor | 0.99244 | 0.99478 | 0.95817 | 0.9956 | 0.99487 | 0.9582 | 0.99488 | 0.9936 | 0.95728 | 0.99204 | 0.99397 | 0.9517 | 0.99904 | 0.99854 | 0.97404
CA | 40001074 | 6003 | From RGBS to BERS | 6003_Glenmore - Berserker 66 kV | Rating (A) | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372
CA | 40001075 | 6004 | From T23 to RSSS | 6004_Glenmore - Rockhampton South 66 kV
CA | 40001075 | 6004 | From T23 to RSSS | 6004_Glenmore - Rockhampton South 66 kV | % of Rated A | 23.2641 | 16.6113 | 19.8954 | 22.9874 | 16.4494 | 19.6079 | 20.6421 | 14.3111 | 18.0388 | 21.2477 | 17.3163 | 18.1792 | 20.6844 | 14.4027 | 18.4555
CA | 40001075 | 6004 | From T23 to RSSS | 6004_Glenmore - Rockhampton South 66 kV | Loading (A) | 85.3754 | 61.794 | 67.2464 | 84.3598 | 61.1918 | 66.2746 | 75.7566 | 53.2374 | 60.9712 | 77.979 | 64.4165 | 61.4456 | 75.9119 | 53.5781 | 62.3797
CA | 40001075 | 6004 | From T23 to RSSS | 6004_Glenmore - Rockhampton South 66 kV | Power Factor | 0.71406 | 0.55564 | 0.79292 | 0.71224 | 0.55201 | 0.79195 | 0.65917 | 0.22718 | 0.7634 | 0.48571 | 0.3572 | 0.76012 | 0.68767 | 0.37846 | 0.75611
CA | 40001075 | 6004 | From T23 to RSSS | 6004_Glenmore - Rockhampton South 66 kV | Rating (A) | 367 | 372 | 338 | 367 | 372 | 338 | 367 | 372 | 338 | 367 | 372 | 338 | 367 | 372 | 338
CA | 40001076 | 6006 | From T23 to FVSS | 6006_Glenmore - Frenchville 66 kV
CA | 40001076 | 6006 | From T23 to FVSS | 6006_Glenmore - Frenchville 66 kV | % of Rated A | 33.3058 | 35.1701 | 27.2307 | 32.4156 | 35.4134 | 27.4009 | 33.0776 | 37.0794 | 27.8895 | 34.1061 | 37.0192 | 28.0843 | 33.5157 | 37.2393 | 28.3226
CA | 40001076 | 6006 | From T23 to FVSS | 6006_Glenmore - Frenchville 66 kV | Loading (A) | 133.555 | 147.0102 | 101.2983 | 129.9858 | 148.0271 | 101.9315 | 132.6405 | 154.9908 | 103.749 | 136.7646 | 154.7394 | 104.4734 | 134.3976 | 155.6594 | 105.3601
CA | 40001076 | 6006 | From T23 to FVSS | 6006_Glenmore - Frenchville 66 kV | Power Factor | 0.98653 | 0.99442 | 0.99986 | 0.99691 | 0.99428 | 0.99989 | 0.99658 | 0.98593 | 0.99994 | 0.99185 | 0.99115 | 0.99961 | 0.99863 | 0.99012 | 0.99934
CA | 40001076 | 6006 | From T23 to FVSS | 6006_Glenmore - Frenchville 66 kV | Rating (A) | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372
CA | 40001077 | 6044 | From RLSS to EQSS - YWSS | 6044_Raglan-East End Quarry/Yarwun 66 kV
CA | 40001077 | 6044 | From RLSS to EQSS - YWSS | 6044_Raglan-East End Quarry/Yarwun 66 kV | % of Rated A | 11.9259 | 5.4684 | 8.9564 | 11.9262 | 5.4683 | 8.9564 | 11.9077 | 5.4679 | 8.9642 | 12.4801 | 5.6154 | 9.3779 | 12.5088 | 5.6147 | 9.3807
CA | 40001077 | 6044 | From RLSS to EQSS - YWSS | 6044_Raglan-East End Quarry/Yarwun 66 kV | Loading (A) | 15.7422 | 9.1322 | 14.2406 | 15.7426 | 9.1321 | 14.2406 | 15.7181 | 9.1314 | 14.2531 | 16.4738 | 9.3777 | 14.9108 | 16.5116 | 9.3766 | 14.9153
CA | 40001077 | 6044 | From RLSS to EQSS - YWSS | 6044_Raglan-East End Quarry/Yarwun 66 kV | Power Factor | 0.92608 | 0.68936 | 0.90148 | 0.9261 | 0.68945 | 0.90148 | 0.92528 | 0.68833 | 0.90145 | 0.9343 | 0.71289 | 0.91265 | 0.93535 | 0.71025 | 0.91284
CA | 40001077 | 6044 | From RLSS to EQSS - YWSS | 6044_Raglan-East End Quarry/Yarwun 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
CA | 40001079 | 6050 | From FVSS to PHSS | 6050_Parkhurst - Frenchville 66 kV
CA | 40001079 | 6050 | From FVSS to PHSS | 6050_Parkhurst - Frenchville 66 kV | % of Rated A | 10.2403 | 10.8638 | 7.6315 | 10.1958 | 10.8439 | 7.6195 | 8.9695 | 7.8649 | 7.3966 | 10.2241 | 10.9826 | 7.9684 | 9.8931 | 10.3805 | 8.2292
CA | 40001079 | 6050 | From FVSS to PHSS | 6050_Parkhurst - Frenchville 66 kV | Loading (A) | 41.0637 | 45.4106 | 28.3891 | 40.8851 | 45.3273 | 28.3445 | 35.9677 | 32.8754 | 27.5153 | 40.9985 | 45.9073 | 29.6426 | 39.6713 | 43.3903 | 30.6127
CA | 40001079 | 6050 | From FVSS to PHSS | 6050_Parkhurst - Frenchville 66 kV | Power Factor | 0.6804 | 0.69118 | 0.40434 | 0.67829 | 0.69005 | 0.40156 | 0.70083 | 0.74413 | 0.36192 | 0.71926 | 0.64307 | 0.34401 | 0.64548 | 0.68982 | 0.33166
CA | 40001079 | 6050 | From FVSS to PHSS | 6050_Parkhurst - Frenchville 66 kV | Rating (A) | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372
CA | 40001081 | 6024 | CALLIOPE | 6024_Awoonga - Calliope 66kV
CA | 40001081 | 6024 | CALLIOPE | 6024_Awoonga - Calliope 66kV | % of Rated A | 15.462 | 11.3864 | 10.2646 | 15.5013 | 11.4089 | 10.2789 | 15.5008 | 11.4085 | 10.2787 | 15.5401 | 11.4313 | 10.2931 | 15.5456 | 11.4978 | 10.3379
CA | 40001081 | 6024 | CALLIOPE | 6024_Awoonga - Calliope 66kV | Loading (A) | 26.1309 | 27.3272 | 24.0192 | 26.1971 | 27.3813 | 24.0526 | 26.1963 | 27.3803 | 24.0521 | 26.2628 | 27.4352 | 24.0859 | 26.272 | 27.5948 | 24.1906
CA | 40001081 | 6024 | CALLIOPE | 6024_Awoonga - Calliope 66kV | Power Factor | 0.57906 | 0.12302 | 0.17972 | 0.58048 | 0.12492 | 0.18072 | 0.58047 | 0.1248 | 0.18065 | 0.58186 | 0.12675 | 0.18169 | 0.57603 | 0.11521 | 0.16918
CA | 40001081 | 6024 | CALLIOPE | 6024_Awoonga - Calliope 66kV | Rating (A) | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234
CA | 40001083 | 6090 | From EHBS to RLSS | 6090_Egan's Hill - Raglan 66 kV
CA | 40001083 | 6090 | From EHBS to RLSS | 6090_Egan's Hill - Raglan 66 kV | % of Rated A | 35.1243 | 23.6486 | 25.6939 | 35.2495 | 23.6511 | 25.6933 | 35.1274 | 23.6118 | 25.664 | 36.3614 | 24.3995 | 26.5317 | 36.4263 | 24.3088 | 26.6001
CA | 40001083 | 6090 | From EHBS to RLSS | 6090_Egan's Hill - Raglan 66 kV | Loading (A) | 46.3641 | 39.4932 | 40.8532 | 46.5293 | 39.4973 | 40.8523 | 46.3681 | 39.4318 | 40.8058 | 47.9967 | 40.7471 | 42.1854 | 48.0824 | 40.5957 | 42.2941
CA | 40001083 | 6090 | From EHBS to RLSS | 6090_Egan's Hill - Raglan 66 kV | Power Factor | 0.99939 | 0.99829 | 0.99725 | 0.99946 | 0.9983 | 0.99725 | 0.99939 | 0.99824 | 0.99719 | 0.99958 | 0.99876 | 0.99781 | 0.99956 | 0.99868 | 0.99791
CA | 40001083 | 6090 | From EHBS to RLSS | 6090_Egan's Hill - Raglan 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
CA | 40001084 | 6091 | From EHBS to GASS / MASS&MLSS | 6091_Egan's Hill - Gavial 66 kV
CA | 40001084 | 6091 | From EHBS to GASS / MASS&MLSS | 6091_Egan's Hill - Gavial 66 kV | % of Rated A | 107.4705 | 92.3285 | 55.4049 | 108.9577 | 93.2412 | 55.9678 | 71.678 | 60.5381 | 36.6634 | 72.7151 | 61.6767 | 37.1628 | 73.8827 | 62.4507 | 37.8063
CA | 40001084 | 6091 | From EHBS to GASS / MASS&MLSS | 6091_Egan's Hill - Gavial 66 kV | Loading (A) | 153.6816 | 178.1926 | 103.0522 | 155.8083 | 179.9541 | 104.0991 | 102.4987 | 116.8375 | 68.1935 | 103.9817 | 119.035 | 69.1224 | 105.6514 | 120.5288 | 70.3192
CA | 40001084 | 6091 | From EHBS to GASS / MASS&MLSS | 6091_Egan's Hill - Gavial 66 kV | Power Factor | 0.97793 | 0.97109 | 0.9874 | 0.97737 | 0.97116 | 0.98715 | 0.98987 | 0.98551 | 0.9965 | 0.98968 | 0.98492 | 0.9963 | 0.98927 | 0.98463 | 0.99598
CA | 40001084 | 6091 | From EHBS to GASS / MASS&MLSS | 6091_Egan's Hill - Gavial 66 kV | Rating (A) | 143 | 193 | 186 | 143 | 193 | 186 | 143 | 193 | 186 | 143 | 193 | 186 | 143 | 193 | 186
CA | 40001085 | 6093 | GASS - MLSS | 6093_Gavial - Mt Morgan 66 kV
CA | 40001085 | 6093 | GASS - MLSS | 6093_Gavial - Mt Morgan 66 kV | % of Rated A | 6.9953 | 5.0698 | 5.0826 | 6.9953 | 5.0696 | 5.0826 | 6.9943 | 5.0731 | 5.0855 | 6.9945 | 5.0707 | 5.0868 | 6.9947 | 5.0732 | 5.0835
CA | 40001085 | 6093 | GASS - MLSS | 6093_Gavial - Mt Morgan 66 kV | Loading (A) | 9.2337 | 8.4665 | 8.0814 | 9.2338 | 8.4662 | 8.0814 | 9.2325 | 8.472 | 8.0859 | 9.2328 | 8.4681 | 8.0881 | 9.2331 | 8.4723 | 8.0828
CA | 40001085 | 6093 | GASS - MLSS | 6093_Gavial - Mt Morgan 66 kV | Power Factor | 0.72607 | 0.66431 | 0.61419 | 0.72608 | 0.66454 | 0.61419 | 0.72413 | 0.66047 | 0.6125 | 0.72458 | 0.66321 | 0.61169 | 0.72502 | 0.66032 | 0.61367
CA | 40001085 | 6093 | GASS - MLSS | 6093_Gavial - Mt Morgan 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
CA | 40001086 | 6094 | From GASS to MASS T | 6094_Malchi Tee - Malchi 66 kV
CA | 40001086 | 6094 | From GASS to MASS T | 6094_Malchi Tee - Malchi 66 kV | % of Rated A | 89.1015 | 74.2599 | 44.231 | 90.3561 | 74.9904 | 44.6826 | 58.5309 | 48.4923 | 29.1387 | 59.4102 | 49.4111 | 29.5427 | 60.4024 | 50.0418 | 30.0598
CA | 40001086 | 6094 | From GASS to MASS T | 6094_Malchi Tee - Malchi 66 kV | Loading (A) | 150.3037 | 177.9322 | 103.2465 | 152.4236 | 179.6866 | 104.3027 | 98.6699 | 116.1257 | 67.9556 | 100.1563 | 118.3302 | 68.9002 | 101.8324 | 119.8427 | 70.11
CA | 40001086 | 6094 | From GASS to MASS T | 6094_Malchi Tee - Malchi 66 kV | Power Factor | 0.96595 | 0.96172 | 0.97254 | 0.96556 | 0.96197 | 0.97238 | 0.9742 | 0.97192 | 0.97887 | 0.97422 | 0.97154 | 0.97874 | 0.97396 | 0.97135 | 0.97852
CA | 40001086 | 6094 | From GASS to MASS T | 6094_Malchi Tee - Malchi 66 kV | Rating (A) | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234
CA | 40001087 | 6095 | From EHBS to RSSS | 6095_Egan's Hill-Rockhampton South 66 kV
CA | 40001087 | 6095 | From EHBS to RSSS | 6095_Egan's Hill-Rockhampton South 66 kV | % of Rated A | 29.6397 | 23.8905 | 25.0984 | 27.1743 | 23.6668 | 24.8678 | 31.7959 | 29.3117 | 26.9196 | 32.1462 | 28.13 | 26.7353 | 30.8991 | 28.544 | 26.5747
CA | 40001087 | 6095 | From EHBS to RSSS | 6095_Egan's Hill-Rockhampton South 66 kV | Loading (A) | 73.4633 | 59.7263 | 55.1748 | 67.3641 | 59.1669 | 54.6677 | 78.8428 | 73.2744 | 59.1838 | 79.6873 | 70.3251 | 58.7799 | 76.6298 | 71.3599 | 58.4288
CA | 40001087 | 6095 | From EHBS to RSSS | 6095_Egan's Hill-Rockhampton South 66 kV | Power Factor | 0.9709 | 0.99679 | 0.9729 | 0.98757 | 0.99638 | 0.97321 | 0.99815 | 0.99964 | 0.97584 | 0.98028 | 0.97819 | 0.97779 | 0.99983 | 0.99828 | 0.98021
CA | 40001087 | 6095 | From EHBS to RSSS | 6095_Egan's Hill-Rockhampton South 66 kV | Rating (A) | 248 | 250 | 220 | 248 | 250 | 220 | 248 | 250 | 220 | 248 | 250 | 220 | 248 | 250 | 220
CA | 40001089 | 6097 | From EHBS To CNSS | 6097_Egan's Hill - Canning 66 kV
CA | 40001089 | 6097 | From EHBS To CNSS | 6097_Egan's Hill - Canning 66 kV | % of Rated A | 40.8423 | 38.2037 | 31.6426 | 39.7319 | 38.0143 | 31.5033 | 44.1889 | 42.9475 | 34.9469 | 44.0473 | 42.7733 | 34.9152 | 43.7984 | 42.5951 | 34.9229
CA | 40001089 | 6097 | From EHBS To CNSS | 6097_Egan's Hill - Canning 66 kV | Loading (A) | 101.2889 | 95.5093 | 69.6138 | 98.5351 | 95.0356 | 69.3072 | 109.5884 | 107.3687 | 76.8833 | 109.2373 | 106.9334 | 76.8134 | 108.62 | 106.4877 | 76.8304
CA | 40001089 | 6097 | From EHBS To CNSS | 6097_Egan's Hill - Canning 66 kV | Power Factor | 0.99972 | 0.97191 | 0.97768 | 0.97687 | 0.97125 | 0.97731 | 0.99084 | 0.98926 | 0.985 | 0.98926 | 0.9554 | 0.98333 | 0.98162 | 0.97988 | 0.98159
CA | 40001089 | 6097 | From EHBS To CNSS | 6097_Egan's Hill - Canning 66 kV | Rating (A) | 248 | 250 | 220 | 248 | 250 | 220 | 248 | 250 | 220 | 248 | 250 | 220 | 248 | 250 | 220
CA | 40001092 | 6029 | From LMSS to MVSS | 6029_Littlemore - Miriam Vale 66 kV
CA | 40001092 | 6029 | From LMSS to MVSS | 6029_Littlemore - Miriam Vale 66 kV | % of Rated A | 10.9873 | 10.9218 | 8.0238 | 10.9887 | 10.9235 | 8.0245 | 10.9883 | 10.923 | 8.0244 | 10.9901 | 10.9251 | 8.0252 | 10.8987 | 10.9286 | 8.027
CA | 40001092 | 6029 | From LMSS to MVSS | 6029_Littlemore - Miriam Vale 66 kV | Loading (A) | 14.5032 | 18.2393 | 12.7579 | 14.5051 | 18.2422 | 12.759 | 14.5045 | 18.2414 | 12.7588 | 14.5069 | 18.245 | 12.7601 | 14.3862 | 18.2508 | 12.763
CA | 40001092 | 6029 | From LMSS to MVSS | 6029_Littlemore - Miriam Vale 66 kV | Power Factor | 0.99544 | 0.99496 | 0.99567 | 0.99544 | 0.99495 | 0.99567 | 0.99544 | 0.99495 | 0.99567 | 0.99544 | 0.99495 | 0.99567 | 0.99547 | 0.99495 | 0.99567
CA | 40001092 | 6029 | From LMSS to MVSS | 6029_Littlemore - Miriam Vale 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
CA | 40001103 | 6031 | From CPSS to LMSS | 6031_Calliope - Littlemore 66 kV
CA | 40001103 | 6031 | From CPSS to LMSS | 6031_Calliope - Littlemore 66 kV | % of Rated A | 18.1151 | 16.1053 | 14.3033 | 18.1156 | 16.1063 | 14.3034 | 18.1154 | 16.106 | 14.3034 | 18.116 | 16.1072 | 14.3035 | 18.0869 | 16.1092 | 14.3038
CA | 40001103 | 6031 | From CPSS to LMSS | 6031_Calliope - Littlemore 66 kV | Loading (A) | 23.912 | 26.8958 | 22.7423 | 23.9126 | 26.8975 | 22.7424 | 23.9124 | 26.897 | 22.7424 | 23.9132 | 26.8991 | 22.7426 | 23.8747 | 26.9024 | 22.7431
CA | 40001103 | 6031 | From CPSS to LMSS | 6031_Calliope - Littlemore 66 kV | Power Factor | 0.83691 | 0.89088 | 0.80288 | 0.837 | 0.89097 | 0.80294 | 0.83697 | 0.89094 | 0.80293 | 0.83708 | 0.89104 | 0.803 | 0.83161 | 0.89121 | 0.80316
CA | 40001103 | 6031 | From CPSS to LMSS | 6031_Calliope - Littlemore 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
CA | 40001125 | 6039 | From CISS to BCSS | 6039_Clinton Industrial - Beecher 66 kV
CA | 40001125 | 6039 | From CISS to BCSS | 6039_Clinton Industrial - Beecher 66 kV | % of Rated A | 51.1653 | 44.7511 | 38.8012 | 51.3453 | 44.883 | 38.9123 | 51.4666 | 44.9676 | 38.9835 | 51.6265 | 45.0937 | 39.0478 | 53.6233 | 45.2791 | 39.2174
CA | 40001125 | 6039 | From CISS to BCSS | 6039_Clinton Industrial - Beecher 66 kV | Loading (A) | 81.3529 | 92.1872 | 65.186 | 81.639 | 92.4589 | 65.3727 | 81.832 | 92.6333 | 65.4923 | 82.0861 | 92.893 | 65.6002 | 85.261 | 93.275 | 65.8852
CA | 40001125 | 6039 | From CISS to BCSS | 6039_Clinton Industrial - Beecher 66 kV | Power Factor | 0.94643 | 0.87588 | 0.91139 | 0.94692 | 0.87686 | 0.912 | 0.94721 | 0.8774 | 0.91233 | 0.94774 | 0.87846 | 0.91283 | 0.85078 | 0.87998 | 0.9139
CA | 40001125 | 6039 | From CISS to BCSS | 6039_Clinton Industrial - Beecher 66 kV | Rating (A) | 159 | 206 | 168 | 159 | 206 | 168 | 159 | 206 | 168 | 159 | 206 | 168 | 159 | 206 | 168
CA | 40001136 | 6041 | From YWSS to BCSS | 6041_Yarwun - Boat Creek 66 kV
CA | 40001136 | 6041 | From YWSS to BCSS | 6041_Yarwun - Boat Creek 66 kV | % of Rated A | 0.88375 | 0.70187 | 0.74432 | 0.88378 | 0.70176 | 0.7443 | 0.88491 | 0.70228 | 0.74501 | 0.88502 | 0.70121 | 0.74519 | 0.88273 | 0.70218 | 0.74403
CA | 40001136 | 6041 | From YWSS to BCSS | 6041_Yarwun - Boat Creek 66 kV | Loading (A) | 1.1666 | 1.1721 | 1.1835 | 1.1666 | 1.1719 | 1.1834 | 1.1681 | 1.1728 | 1.1846 | 1.1682 | 1.171 | 1.1848 | 1.1652 | 1.1726 | 1.183
CA | 40001136 | 6041 | From YWSS to BCSS | 6041_Yarwun - Boat Creek 66 kV | Power Factor | 5.2977e-05 | 5.2978e-05 | 5.2977e-05 | 5.2976e-05 | 5.2977e-05 | 5.2976e-05 | 5.2978e-05 | 5.2977e-05 | 5.2977e-05 | 5.2977e-05 | 5.2977e-05 | 5.2976e-05 | 5.2978e-05 | 5.2976e-05 | 5.2977e-05
CA | 40001136 | 6041 | From YWSS to BCSS | 6041_Yarwun - Boat Creek 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
CA | 40001150 | 6005 | From T23 to CNSS | 6005_Rockhampton Glenmore-Canning 66 kV
CA | 40001150 | 6005 | From T23 to CNSS | 6005_Rockhampton Glenmore-Canning 66 kV | % of Rated A | 30.7428 | 29.3223 | 23.0201 | 30.668 | 29.2576 | 22.9519 | 28.3117 | 25.8309 | 21.7369 | 28.4632 | 26.818 | 21.7326 | 28.4881 | 25.7595 | 21.8117
CA | 40001150 | 6005 | From T23 to CNSS | 6005_Rockhampton Glenmore-Canning 66 kV | Loading (A) | 122.6638 | 121.6847 | 85.1742 | 122.3651 | 121.4159 | 84.922 | 112.9638 | 107.1913 | 80.4264 | 113.5613 | 111.2872 | 80.4105 | 113.6675 | 106.8994 | 80.7032
CA | 40001150 | 6005 | From T23 to CNSS | 6005_Rockhampton Glenmore-Canning 66 kV | Power Factor | 0.99424 | 0.99881 | 0.97465 | 0.99419 | 0.99885 | 0.97444 | 0.99103 | 0.99362 | 0.9697 | 0.99327 | 0.99251 | 0.97128 | 0.99323 | 0.99929 | 0.9741
CA | 40001150 | 6005 | From T23 to CNSS | 6005_Rockhampton Glenmore-Canning 66 kV | Rating (A) | 399 | 415 | 370 | 399 | 415 | 370 | 399 | 415 | 370 | 399 | 415 | 370 | 399 | 415 | 370
CA | 40001151 | 6053 | PDBS to PHSS | 6053_Parkhurst - Pandoin 66 kV
CA | 40001151 | 6053 | PDBS to PHSS | 6053_Parkhurst - Pandoin 66 kV | % of Rated A | 65.988 | 57.7625 | 43.9886 | 67.3124 | 57.8813 | 44.0821 | 65.577 | 54.8028 | 43.0125 | 64.4386 | 55.9558 | 43.307 | 66.7056 | 57.2482 | 43.7895
CA | 40001151 | 6053 | PDBS to PHSS | 6053_Parkhurst - Pandoin 66 kV | Loading (A) | 345.0381 | 341.8725 | 240.0859 | 351.9615 | 342.576 | 240.5955 | 342.888 | 324.4325 | 234.7577 | 337.0138 | 331.2515 | 236.3814 | 348.7894 | 338.8299 | 238.9964
CA | 40001151 | 6053 | PDBS to PHSS | 6053_Parkhurst - Pandoin 66 kV | Power Factor | 0.994 | 0.99371 | 0.99249 | 0.99349 | 0.99367 | 0.99239 | 0.99394 | 0.99997 | 0.99275 | 0.99996 | 0.99985 | 0.99496 | 0.99371 | 0.994 | 0.99215
CA | 40001151 | 6053 | PDBS to PHSS | 6053_Parkhurst - Pandoin 66 kV | Rating (A) | 523 | 592 | 546 | 523 | 592 | 546 | 523 | 592 | 546 | 523 | 592 | 546 | 523 | 592 | 546
CA | 40001158 | 6066 | BOCOOLIMA TEE WOODERSON | 6066_Bocoolima Tee -Wooderson 66 kV
CA | 40001158 | 6066 | BOCOOLIMA TEE WOODERSON | 6066_Bocoolima Tee -Wooderson 66 kV | % of Rated A | 44.2232 | 31.1769 | 31.7589 | 44.2289 | 31.1809 | 31.7616 | 44.2436 | 31.1797 | 31.761 | 44.2473 | 31.087 | 31.7644 | 44.1618 | 31.096 | 31.7715
CA | 40001158 | 6066 | BOCOOLIMA TEE WOODERSON | 6066_Bocoolima Tee -Wooderson 66 kV | Loading (A) | 74.7127 | 74.7994 | 74.2938 | 74.7222 | 74.8091 | 74.3002 | 74.7481 | 74.8063 | 74.2988 | 74.7544 | 74.5853 | 74.3066 | 74.6099 | 74.6067 | 74.3232
CA | 40001158 | 6066 | BOCOOLIMA TEE WOODERSON | 6066_Bocoolima Tee -Wooderson 66 kV | Power Factor | 0.99999 | 0.99999 | 1 | 0.99999 | 0.99999 | 1 | 1 | 0.99999 | 1 | 1 | 1 | 1 | 1 | 1 | 1
CA | 40001158 | 6066 | BOCOOLIMA TEE WOODERSON | 6066_Bocoolima Tee -Wooderson 66 kV | Rating (A) | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234
CA | 40001159 | 6051 | From PHSS to KESS | 6051_Parkhurst - Keppel 66 kV
CA | 40001159 | 6051 | From PHSS to KESS | 6051_Parkhurst - Keppel 66 kV | % of Rated A | 82.2853 | 63.0054 | 47.6075 | 83.7936 | 63.8372 | 48.2143 | 83.7264 | 63.7606 | 48.2208 | 83.9618 | 64.2366 | 48.8282 | 85.412 | 64.9525 | 49.5906
CA | 40001159 | 6051 | From PHSS to KESS | 6051_Parkhurst - Keppel 66 kV | Loading (A) | 174.426 | 186.4708 | 117.1115 | 177.6197 | 188.9323 | 118.6035 | 177.4765 | 188.7074 | 118.6195 | 177.9991 | 190.1142 | 120.1174 | 181.0734 | 192.2594 | 121.9929
CA | 40001159 | 6051 | From PHSS to KESS | 6051_Parkhurst - Keppel 66 kV | Power Factor | 0.99785 | 0.99618 | 0.99995 | 0.99691 | 0.99598 | 0.99992 | 0.99669 | 0.99654 | 0.99992 | 0.99951 | 0.99966 | 0.99602 | 0.99998 | 1 | 0.99766
CA | 40001159 | 6051 | From PHSS to KESS | 6051_Parkhurst - Keppel 66 kV | Rating (A) | 212 | 296 | 246 | 212 | 296 | 246 | 212 | 296 | 246 | 212 | 296 | 246 | 212 | 296 | 246
CA | 40001161 | 6082 | From KESS to YPSS | 6082_Farnborough Tee - Yeppoon 66 kV
CA | 40001161 | 6082 | From KESS to YPSS | 6082_Farnborough Tee - Yeppoon 66 kV | % of Rated A | 82.3335 | 63.0509 | 47.6173 | 83.8512 | 63.8838 | 48.2257 | 83.7862 | 63.8037 | 48.2322 | 83.9401 | 64.2278 | 48.7767 | 85.4076 | 64.9527 | 49.5515
CA | 40001161 | 6082 | From KESS to YPSS | 6082_Farnborough Tee - Yeppoon 66 kV | Loading (A) | 174.5464 | 186.6297 | 117.1384 | 177.7638 | 189.095 | 118.635 | 177.6258 | 188.8581 | 118.6509 | 177.953 | 190.1142 | 119.9906 | 181.0641 | 192.2597 | 121.8967
CA | 40001161 | 6082 | From KESS to YPSS | 6082_Farnborough Tee - Yeppoon 66 kV | Power Factor | 0.9979 | 0.99635 | 0.99983 | 0.99698 | 0.99618 | 0.99979 | 0.99676 | 0.99673 | 0.99979 | 0.99959 | 0.99993 | 0.99676 | 1 | 0.99999 | 0.9982
CA | 40001161 | 6082 | From KESS to YPSS | 6082_Farnborough Tee - Yeppoon 66 kV | Rating (A) | 212 | 296 | 246 | 212 | 296 | 246 | 212 | 296 | 246 | 212 | 296 | 246 | 212 | 296 | 246
CA | 40001163 | 6075 | KESS to FBSS | 6075_Keppel - Farnborough 66 kV
CA | 40001163 | 6075 | KESS to FBSS | 6075_Keppel - Farnborough 66 kV | % of Rated A | 0.30977 | 0.27816 | 0.35196 | 0.30968 | 0.27795 | 0.35187 | 0.30989 | 0.27829 | 0.35203 | 0.31147 | 0.27994 | 0.35297 | 0.31043 | 0.27903 | 0.35223
CA | 40001163 | 6075 | KESS to FBSS | 6075_Keppel - Farnborough 66 kV | Loading (A) | 1.1709 | 1.1544 | 1.1861 | 1.1706 | 1.1535 | 1.1858 | 1.1714 | 1.1549 | 1.1863 | 1.1773 | 1.1618 | 1.1895 | 1.1734 | 1.158 | 1.187
CA | 40001163 | 6075 | KESS to FBSS | 6075_Keppel - Farnborough 66 kV | Power Factor | 2.4918e-05 | 2.4919e-05 | 2.4919e-05 | 2.4918e-05 | 2.4918e-05 | 2.4918e-05 | 2.4918e-05 | 2.4918e-05 | 2.4919e-05 | 2.4917e-05 | 2.4918e-05 | 2.4918e-05 | 2.4918e-05 | 2.4918e-05 | 2.4919e-05
CA | 40001163 | 6075 | KESS to FBSS | 6075_Keppel - Farnborough 66 kV | Rating (A) | 378 | 415 | 337 | 378 | 415 | 337 | 378 | 415 | 337 | 378 | 415 | 337 | 378 | 415 | 337
CA | 40001218 | 6032 | Boyne Residental Tee to Awoonga | 6032_Boyne Residential Tee-Awoonga 66 kV
CA | 40001218 | 6032 | Boyne Residental Tee to Awoonga | 6032_Boyne Residential Tee-Awoonga 66 kV | % of Rated A | 26.3617 | 20.2604 | 21.7639 | 26.4004 | 20.2843 | 21.7786 | 26.401 | 20.2847 | 21.7791 | 26.4399 | 20.309 | 21.7937 | 26.4354 | 20.4948 | 21.9794
CA | 40001218 | 6032 | Boyne Residental Tee to Awoonga | 6032_Boyne Residential Tee-Awoonga 66 kV | Loading (A) | 55.6233 | 59.7681 | 53.3216 | 55.7049 | 59.8387 | 53.3576 | 55.7061 | 59.84 | 53.3588 | 55.7882 | 59.9115 | 53.3946 | 55.7787 | 60.4598 | 53.8495
CA | 40001218 | 6032 | Boyne Residental Tee to Awoonga | 6032_Boyne Residential Tee-Awoonga 66 kV | Power Factor | 0.99563 | 0.99608 | 0.99693 | 0.9956 | 0.99602 | 0.9969 | 0.99559 | 0.99602 | 0.9969 | 0.99556 | 0.99597 | 0.99686 | 0.99548 | 0.99616 | 0.99703
CA | 40001218 | 6032 | Boyne Residental Tee to Awoonga | 6032_Boyne Residential Tee-Awoonga 66 kV | Rating (A) | 211 | 295 | 245 | 211 | 295 | 245 | 211 | 295 | 245 | 211 | 295 | 245 | 211 | 295 | 245
CA | 40001219 | 6034 | Boyne Residental Tee to Boyne Residental | 6034_Boyne Residential Tee - BORE 66 kV
CA | 40001219 | 6034 | Boyne Residental Tee to Boyne Residental | 6034_Boyne Residential Tee - BORE 66 kV | % of Rated A | 52.3597 | 48.3693 | 36.1532 | 52.7952 | 48.7754 | 36.4514 | 52.7933 | 48.7735 | 36.4507 | 53.2309 | 49.1818 | 36.7497 | 53.2227 | 49.5979 | 37.0534
CA | 40001219 | 6034 | Boyne Residental Tee to Boyne Residental | 6034_Boyne Residential Tee - BORE 66 kV | Loading (A) | 86.3908 | 107.8608 | 66.5194 | 87.1094 | 108.7664 | 67.068 | 87.1062 | 108.7621 | 67.0668 | 87.8283 | 109.6725 | 67.6169 | 87.8148 | 110.6005 | 68.1757
CA | 40001219 | 6034 | Boyne Residental Tee to Boyne Residental | 6034_Boyne Residential Tee - BORE 66 kV | Power Factor | 0.98318 | 0.98122 | 0.98495 | 0.98311 | 0.98113 | 0.9849 | 0.98311 | 0.98113 | 0.9849 | 0.98304 | 0.98104 | 0.98485 | 0.98311 | 0.98095 | 0.9848
CA | 40001219 | 6034 | Boyne Residental Tee to Boyne Residental | 6034_Boyne Residential Tee - BORE 66 kV | Rating (A) | 165 | 223 | 184 | 165 | 223 | 184 | 165 | 223 | 184 | 165 | 223 | 184 | 165 | 223 | 184
CA | 40001229 | 6101 ICI-T4 | 6101 ICI-T4 | 6101_Boat Creek - Orica 66 kV
CA | 40001229 | 6101 ICI-T4 | 6101 ICI-T4 | 6101_Boat Creek - Orica 66 kV | % of Rated A | 6.152 | 5.0604 | 9.6764 | 6.152 | 5.0603 | 9.6763 | 6.1554 | 5.0635 | 9.6782 | 6.2485 | 5.1444 | 9.8051 | 6.2467 | 5.1424 | 9.8039
CA | 40001229 | 6101 ICI-T4 | 6101 ICI-T4 | 6101_Boat Creek - Orica 66 kV | Loading (A) | 45.5244 | 40.8377 | 64.0549 | 45.5248 | 40.8362 | 64.0544 | 45.5497 | 40.8627 | 64.0664 | 46.2388 | 41.5156 | 64.9066 | 46.2257 | 41.4989 | 64.8986
CA | 40001229 | 6101 ICI-T4 | 6101 ICI-T4 | 6101_Boat Creek - Orica 66 kV | Power Factor | 0.99412 | 0.99051 | 0.99479 | 0.99413 | 0.99052 | 0.99479 | 0.99402 | 0.9904 | 0.99477 | 0.99413 | 0.99064 | 0.9949 | 0.99441 | 0.99099 | 0.99502
CA | 40001229 | 6101 ICI-T4 | 6101 ICI-T4 | 6101_Boat Creek - Orica 66 kV | Rating (A) | 740 | 807 | 662 | 740 | 807 | 662 | 740 | 807 | 662 | 740 | 807 | 662 | 740 | 807 | 662
CA | 40001235 | 6102 | BOAT CREEK TO YARWUN | 6102_Boat Creek - Yarwun 66 kV
CA | 40001235 | 6102 | BOAT CREEK TO YARWUN | 6102_Boat Creek - Yarwun 66 kV | % of Rated A | 2.314 | 1.5283 | 1.8238 | 2.314 | 1.5283 | 1.8238 | 2.3139 | 1.5282 | 1.8238 | 2.3138 | 1.5282 | 1.8238 | 2.3141 | 1.5283 | 1.8239
CA | 40001235 | 6102 | BOAT CREEK TO YARWUN | 6102_Boat Creek - Yarwun 66 kV | Loading (A) | 17.1233 | 12.3331 | 12.0738 | 17.1233 | 12.3332 | 12.0738 | 17.1228 | 12.3327 | 12.0734 | 17.1224 | 12.3325 | 12.0733 | 17.124 | 12.3337 | 12.0743
CA | 40001235 | 6102 | BOAT CREEK TO YARWUN | 6102_Boat Creek - Yarwun 66 kV | Power Factor | 0.86278 | 0.8223 | 0.82004 | 0.86278 | 0.8223 | 0.82004 | 0.86278 | 0.8223 | 0.82004 | 0.86278 | 0.8223 | 0.82004 | 0.86278 | 0.82229 | 0.82003
CA | 40001235 | 6102 | BOAT CREEK TO YARWUN | 6102_Boat Creek - Yarwun 66 kV | Rating (A) | 740 | 807 | 662 | 740 | 807 | 662 | 740 | 807 | 662 | 740 | 807 | 662 | 740 | 807 | 662
CA | 40001238 | 6007 | From T26 to COSS | 6007_Biloela - Coominglah Tee 66 kV
CA | 40001238 | 6007 | From T26 to COSS | 6007_Biloela - Coominglah Tee 66 kV | % of Rated A | 41.173 | 38.4801 | 33.4848 | 41.1705 | 38.4782 | 33.4835 | 41.1667 | 38.4744 | 33.4816 | 41.166 | 38.4744 | 33.4817 | 41.1652 | 38.4735 | 33.4814
CA | 40001238 | 6007 | From T26 to COSS | 6007_Biloela - Coominglah Tee 66 kV | Loading (A) | 54.3484 | 64.2618 | 53.2408 | 54.345 | 64.2586 | 53.2388 | 54.34 | 64.2522 | 53.2357 | 54.3391 | 64.2522 | 53.2359 | 54.3381 | 64.2508 | 53.2354
CA | 40001238 | 6007 | From T26 to COSS | 6007_Biloela - Coominglah Tee 66 kV | Power Factor | 0.99151 | 0.99829 | 0.98993 | 0.99151 | 0.99829 | 0.98992 | 0.9915 | 0.99829 | 0.98991 | 0.99149 | 0.99829 | 0.98991 | 0.99149 | 0.99829 | 0.98991
CA | 40001238 | 6007 | From T26 to COSS | 6007_Biloela - Coominglah Tee 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
CA | 40001239 | 6008 | From T26 to WNSS | 6008_Biloela - Wowan 66 kV
CA | 40001239 | 6008 | From T26 to WNSS | 6008_Biloela - Wowan 66 kV | % of Rated A | 37.3644 | 33.6655 | 26.0985 | 37.3617 | 33.6637 | 26.0974 | 37.3577 | 33.6601 | 26.0956 | 37.357 | 33.6601 | 26.0958 | 37.3562 | 33.6593 | 26.0955
CA | 40001239 | 6008 | From T26 to WNSS | 6008_Biloela - Wowan 66 kV | Loading (A) | 49.2051 | 56.0955 | 41.3951 | 49.2016 | 56.0924 | 41.3933 | 49.1963 | 56.0864 | 41.3905 | 49.1954 | 56.0864 | 41.3907 | 49.1943 | 56.0851 | 41.3903
CA | 40001239 | 6008 | From T26 to WNSS | 6008_Biloela - Wowan 66 kV | Power Factor | 0.98615 | 0.98319 | 0.9899 | 0.98615 | 0.9832 | 0.9899 | 0.98615 | 0.9832 | 0.9899 | 0.98615 | 0.9832 | 0.9899 | 0.98616 | 0.9832 | 0.9899
CA | 40001239 | 6008 | From T26 to WNSS | 6008_Biloela - Wowan 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
CA | 40001243 | 6030 | From LMSS to MTSS | 6030_Littlemore - Monto 66 kV
CA | 40001243 | 6030 | From LMSS to MTSS | 6030_Littlemore - Monto 66 kV | % of Rated A | 5.5248 | 4.3309 | 4.5892 | 5.5247 | 4.3306 | 4.5891 | 5.5248 | 4.3306 | 4.5891 | 5.5245 | 4.3302 | 4.5889 | 5.5239 | 4.3294 | 4.5884
CA | 40001243 | 6030 | From LMSS to MTSS | 6030_Littlemore - Monto 66 kV | Loading (A) | 7.2927 | 7.2326 | 7.2969 | 7.2926 | 7.232 | 7.2966 | 7.2927 | 7.2322 | 7.2967 | 7.2924 | 7.2315 | 7.2964 | 7.2915 | 7.2301 | 7.2956
CA | 40001243 | 6030 | From LMSS to MTSS | 6030_Littlemore - Monto 66 kV | Power Factor | 0.34158 | 0.3353 | 0.33772 | 0.3416 | 0.33536 | 0.33775 | 0.34158 | 0.33535 | 0.33774 | 0.34161 | 0.33542 | 0.33778 | 0.3417 | 0.33556 | 0.33785
CA | 40001243 | 6030 | From LMSS to MTSS | 6030_Littlemore - Monto 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
CA | 40001244 | 6045 | From MTSS to COSS | 6045_Coominglah Tee - Monto 66 kV
CA | 40001244 | 6045 | From MTSS to COSS | 6045_Coominglah Tee - Monto 66 kV | % of Rated A | 32.996 | 30.3053 | 26.8706 | 32.994 | 30.3038 | 26.8696 | 32.991 | 30.3008 | 26.868 | 32.9904 | 30.3008 | 26.8681 | 32.9898 | 30.3001 | 26.8679
CA | 40001244 | 6045 | From MTSS to COSS | 6045_Coominglah Tee - Monto 66 kV | Loading (A) | 43.5547 | 50.6098 | 42.7242 | 43.5521 | 50.6073 | 42.7226 | 43.5481 | 50.6023 | 42.7202 | 43.5474 | 50.6023 | 42.7204 | 43.5465 | 50.6012 | 42.7199
CA | 40001244 | 6045 | From MTSS to COSS | 6045_Coominglah Tee - Monto 66 kV | Power Factor | 0.98174 | 0.99057 | 0.97983 | 0.98173 | 0.99057 | 0.97983 | 0.98171 | 0.99056 | 0.97982 | 0.98171 | 0.99056 | 0.97982 | 0.98171 | 0.99056 | 0.97981
CA | 40001244 | 6045 | From MTSS to COSS | 6045_Coominglah Tee - Monto 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
CA | 40216264 | 6080 | BBBS TO BKSS | 6080_Barcaldine - Blackall 66 kV
CA | 40216264 | 6080 | BBBS TO BKSS | 6080_Barcaldine - Blackall 66 kV | % of Rated A | 10.0431 | 11.0426 | 8.9155 | 10.0435 | 11.0412 | 8.915 | 10.0439 | 11.0398 | 8.9146 | 10.0439 | 11.0399 | 8.9147 | 9.8282 | 10.8101 | 8.7502
CA | 40216264 | 6080 | BBBS TO BKSS | 6080_Barcaldine - Blackall 66 kV | Loading (A) | 37.5613 | 42.9558 | 30.1342 | 37.5627 | 42.9503 | 30.1328 | 37.5641 | 42.9449 | 30.1314 | 37.5641 | 42.9451 | 30.1315 | 36.7573 | 42.0512 | 29.5756
CA | 40216264 | 6080 | BBBS TO BKSS | 6080_Barcaldine - Blackall 66 kV | Power Factor | 0.99405 | 0.98631 | 0.94647 | 0.99405 | 0.98629 | 0.94646 | 0.99405 | 0.98627 | 0.94644 | 0.99405 | 0.98627 | 0.94644 | 0.99339 | 0.98485 | 0.94316
CA | 40216264 | 6080 | BBBS TO BKSS | 6080_Barcaldine - Blackall 66 kV | Rating (A) | 374 | 389 | 338 | 374 | 389 | 338 | 374 | 389 | 338 | 374 | 389 | 338 | 374 | 389 | 338
CA | 40218335 | 6046 | MMLS-MMSS-WOWA | 6046_Mt Morgan - Wowan 66 kV
CA | 40218335 | 6046 | MMLS-MMSS-WOWA | 6046_Mt Morgan - Wowan 66 kV | % of Rated A | 6.39 | 4.5473 | 4.4951 | 6.39 | 4.5474 | 4.4951 | 6.3853 | 4.5452 | 4.4955 | 6.3864 | 4.5467 | 4.4957 | 6.3875 | 4.5451 | 4.4952
CA | 40218335 | 6046 | MMLS-MMSS-WOWA | 6046_Mt Morgan - Wowan 66 kV | Loading (A) | 8.4347 | 7.5939 | 7.1472 | 8.4348 | 7.5942 | 7.1472 | 8.4287 | 7.5905 | 7.1479 | 8.4301 | 7.5929 | 7.1482 | 8.4314 | 7.5904 | 7.1474
CA | 40218335 | 6046 | MMLS-MMSS-WOWA | 6046_Mt Morgan - Wowan 66 kV | Power Factor | 0.79371 | 0.73949 | 0.69331 | 0.79372 | 0.7397 | 0.69331 | 0.79205 | 0.73602 | 0.69172 | 0.79244 | 0.7385 | 0.69096 | 0.79281 | 0.73589 | 0.69282
CA | 40218335 | 6046 | MMLS-MMSS-WOWA | 6046_Mt Morgan - Wowan 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
CA | 82575918 | 6109 | 6109 CLINTON INDUSTRIAL 66KV FEEDER | 6109_Gladstone North - Clinton 66 kV
CA | 82575918 | 6109 | 6109 CLINTON INDUSTRIAL 66KV FEEDER | 6109_Gladstone North - Clinton 66 kV | % of Rated A | 93.0987 | 63.9738 | 60.2942 | 93.0312 | 63.9532 | 60.2687 | 92.9098 | 63.8902 | 60.2129 | 93.158 | 64.0613 | 60.3492 | 93.7192 | 64.2197 | 60.476
CA | 82575918 | 6109 | 6109 CLINTON INDUSTRIAL 66KV FEEDER | 6109_Gladstone North - Clinton 66 kV | Loading (A) | 337.9483 | 348.6141 | 277.914 | 337.7033 | 348.5019 | 277.7963 | 337.2625 | 348.1586 | 277.5387 | 338.1636 | 349.0909 | 278.1673 | 340.1554 | 349.9543 | 278.752
CA | 82575918 | 6109 | 6109 CLINTON INDUSTRIAL 66KV FEEDER | 6109_Gladstone North - Clinton 66 kV | Power Factor | 0.96881 | 0.9405 | 0.94215 | 0.96874 | 0.94047 | 0.94209 | 0.96859 | 0.94028 | 0.94193 | 0.9689 | 0.94084 | 0.94234 | 0.93416 | 0.94138 | 0.94274
CA | 82575918 | 6109 | 6109 CLINTON INDUSTRIAL 66KV FEEDER | 6109_Gladstone North - Clinton 66 kV | Rating (A) | 363 | 545 | 461 | 363 | 545 | 461 | 363 | 545 | 461 | 363 | 545 | 461 | 363 | 545 | 461
CA | 82588694 | 7290 | Boat Creek - Yarwun 132 kV | 7290_Boat Creek - Yarwun 132 kV
CA | 82588694 | 7290 | Boat Creek - Yarwun 132 kV | 7290_Boat Creek - Yarwun 132 kV | % of Rated A | 2.6422 | 2.1454 | 3.084 | 2.6422 | 2.1453 | 3.0839 | 2.6431 | 2.1461 | 3.0843 | 2.6612 | 2.1615 | 3.1079 | 2.6836 | 2.1811 | 3.1302
CA | 82588694 | 7290 | Boat Creek - Yarwun 132 kV | 7290_Boat Creek - Yarwun 132 kV | Loading (A) | 23.4894 | 21.1103 | 25.8744 | 23.4895 | 21.1098 | 25.8742 | 23.4971 | 21.1175 | 25.8775 | 23.6583 | 21.2693 | 26.0757 | 23.8571 | 21.462 | 26.2621
CA | 82588694 | 7290 | Boat Creek - Yarwun 132 kV | 7290_Boat Creek - Yarwun 132 kV | Power Factor | 0.94644 | 0.93974 | 0.96168 | 0.94644 | 0.93974 | 0.96168 | 0.94632 | 0.93963 | 0.96166 | 0.94694 | 0.94041 | 0.9622 | 0.9467 | 0.94016 | 0.96185
CA | 82588694 | 7290 | Boat Creek - Yarwun 132 kV | 7290_Boat Creek - Yarwun 132 kV | Rating (A) | 889 | 984 | 839 | 889 | 984 | 839 | 889 | 984 | 839 | 889 | 984 | 839 | 889 | 984 | 839
CA | 82588698 | 7291 | Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV
CA | 82588698 | 7291 | Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | % of Rated A | 2.6552 | 2.1559 | 3.0991 | 2.6552 | 2.1558 | 3.099 | 2.656 | 2.1566 | 3.0994 | 2.6743 | 2.1721 | 3.1232 | 2.6967 | 2.1918 | 3.1455
CA | 82588698 | 7291 | Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | Loading (A) | 23.6044 | 21.2137 | 26.0011 | 23.6045 | 21.2132 | 26.001 | 23.6122 | 21.2209 | 26.0043 | 23.7742 | 21.3735 | 26.2034 | 23.9739 | 21.5671 | 26.3907
CA | 82588698 | 7291 | Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | Power Factor | 0.94638 | 0.93967 | 0.96162 | 0.94638 | 0.93968 | 0.96163 | 0.94626 | 0.93957 | 0.9616 | 0.94688 | 0.94034 | 0.96215 | 0.94663 | 0.9401 | 0.9618
CA | 82588698 | 7291 | Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | Rating (A) | 889 | 984 | 839 | 889 | 984 | 839 | 889 | 984 | 839 | 889 | 984 | 839 | 889 | 984 | 839
CA | 82860724 | 6022 | GSBS TO CALLIOPE | 6022_Gladstone South - Calliope 66 kV
CA | 82860724 | 6022 | GSBS TO CALLIOPE | 6022_Gladstone South - Calliope 66 kV | % of Rated A | 26.081 | 27.086 | 23.2228 | 26.2007 | 27.215 | 23.3072 | 26.2001 | 27.2144 | 23.3071 | 26.3205 | 27.3444 | 23.3918 | 26.2679 | 27.5358 | 23.5347
CA | 82860724 | 6022 | GSBS TO CALLIOPE | 6022_Gladstone South - Calliope 66 kV | Loading (A) | 162.4833 | 179.8498 | 139.1035 | 163.2287 | 180.7063 | 139.6092 | 163.2251 | 180.7019 | 139.6083 | 163.9756 | 181.565 | 140.1159 | 163.6476 | 182.836 | 140.9714
CA | 82860724 | 6022 | GSBS TO CALLIOPE | 6022_Gladstone South - Calliope 66 kV | Power Factor | 0.98391 | 0.98081 | 0.98872 | 0.98376 | 0.98064 | 0.98861 | 0.98376 | 0.98064 | 0.98861 | 0.98361 | 0.98047 | 0.98851 | 0.98379 | 0.98022 | 0.98832
CA | 82860724 | 6022 | GSBS TO CALLIOPE | 6022_Gladstone South - Calliope 66 kV | Rating (A) | 623 | 664 | 599 | 623 | 664 | 599 | 623 | 664 | 599 | 623 | 664 | 599 | 623 | 664 | 599
CA | 82999218 | 6103 | FISHERMANS LANDING | 6103_Fisherman Landing-Boat Creek 66 kV
CA | 82999218 | 6103 | FISHERMANS LANDING | 6103_Fisherman Landing-Boat Creek 66 kV | % of Rated A | 0.096396 | 0.088376 | 0.10784 | 0.096397 | 0.088376 | 0.10784 | 0.096398 | 0.088379 | 0.10784 | 0.0964 | 0.08838 | 0.10784 | 0.096392 | 0.088372 | 0.10783
CA | 82999218 | 6103 | FISHERMANS LANDING | 6103_Fisherman Landing-Boat Creek 66 kV | Loading (A) | 0.71333 | 0.7132 | 0.7139 | 0.71333 | 0.71319 | 0.7139 | 0.71335 | 0.71322 | 0.71391 | 0.71336 | 0.71323 | 0.71392 | 0.7133 | 0.71317 | 0.71387
CA | 82999218 | 6103 | FISHERMANS LANDING | 6103_Fisherman Landing-Boat Creek 66 kV | Power Factor | 5.8252e-06 | 5.9011e-06 | 5.8637e-06 | 5.824e-06 | 5.8999e-06 | 5.863e-06 | 5.816e-06 | 5.8377e-06 | 5.8629e-06 | 5.8237e-06 | 5.8371e-06 | 5.8621e-06 | 5.8157e-06 | 5.9024e-06 | 5.8633e-06
CA | 82999218 | 6103 | FISHERMANS LANDING | 6103_Fisherman Landing-Boat Creek 66 kV | Rating (A) | 740 | 807 | 662 | 740 | 807 | 662 | 740 | 807 | 662 | 740 | 807 | 662 | 740 | 807 | 662
CA | 83009518 | 6112 | 66KV 6112 AGNES WATER FDR | 6112_Agnes Water 66 kV
CA | 83009518 | 6112 | 66KV 6112 AGNES WATER FDR | 6112_Agnes Water 66 kV | % of Rated A | 8.571 | 6.062 | 4.4925 | 8.5711 | 6.0638 | 4.4935 | 8.5728 | 6.0654 | 4.4942 | 8.5755 | 6.0688 | 4.4955 | 8.738 | 6.1864 | 4.5792
CA | 83009518 | 6112 | 66KV 6112 AGNES WATER FDR | 6112_Agnes Water 66 kV | Loading (A) | 24.3417 | 29.2188 | 21.6989 | 24.3419 | 29.2274 | 21.7035 | 24.3467 | 29.2354 | 21.7072 | 24.3546 | 29.2517 | 21.7134 | 24.8159 | 29.8185 | 22.1174
CA | 83009518 | 6112 | 66KV 6112 AGNES WATER FDR | 6112_Agnes Water 66 kV | Power Factor | 0.98703 | 0.99355 | 0.98053 | 0.98703 | 0.99357 | 0.98055 | 0.98705 | 0.99358 | 0.98058 | 0.98708 | 0.99362 | 0.98062 | 0.98795 | 0.99415 | 0.98178
CA | 83009518 | 6112 | 66KV 6112 AGNES WATER FDR | 6112_Agnes Water 66 kV | Rating (A) | 284 | 482 | 483 | 284 | 482 | 483 | 284 | 482 | 483 | 284 | 482 | 483 | 284 | 482 | 483
CA | 83878739 | 6298 | TANB to YPSS | 6298_Tanby - Yeppoon 66 kV
CA | 83878739 | 6298 | TANB to YPSS | 6298_Tanby - Yeppoon 66 kV | % of Rated A | 15.9465 | 11.0369 | 11.0035 | 16.1567 | 11.167 | 11.1593 | 16.3335 | 11.5674 | 11.2817 | 16.0389 | 11.2334 | 11.355 | 16.2528 | 11.3044 | 11.5607
CA | 83878739 | 6298 | TANB to YPSS | 6298_Tanby - Yeppoon 66 kV | Loading (A) | 60.2769 | 45.803 | 37.0819 | 61.0714 | 46.3432 | 37.6069 | 61.7397 | 48.0047 | 38.0193 | 60.6272 | 46.6185 | 38.2665 | 61.4355 | 46.9134 | 38.9594
CA | 83878739 | 6298 | TANB to YPSS | 6298_Tanby - Yeppoon 66 kV | Power Factor | 0.97858 | 0.97978 | 0.99243 | 0.97823 | 0.97921 | 0.99217 | 0.97828 | 0.97322 | 0.99231 | 0.99991 | 0.99523 | 0.99494 | 0.99878 | 0.98784 | 0.98884
CA | 83878739 | 6298 | TANB to YPSS | 6298_Tanby - Yeppoon 66 kV | Rating (A) | 378 | 415 | 337 | 378 | 415 | 337 | 378 | 415 | 337 | 378 | 415 | 337 | 378 | 415 | 337
CA | 83966216 | 6310 | LAKES CREEK | 6310_Lakes Creek - Berserker 66 kV
CA | 83966216 | 6310 | LAKES CREEK | 6310_Lakes Creek - Berserker 66 kV | % of Rated A | 27.9342 | 31.6165 | 22.4704 | 28.8021 | 31.9414 | 22.6413 | 27.4754 | 30.368 | 21.7848 | 27.7884 | 31.2318 | 22.1919 | 28.8405 | 31.9143 | 22.3139
CA | 83966216 | 6310 | LAKES CREEK | 6310_Lakes Creek - Berserker 66 kV | Loading (A) | 103.9152 | 117.6135 | 83.5901 | 107.1437 | 118.8219 | 84.2258 | 102.2083 | 112.9691 | 81.0394 | 103.3727 | 116.1824 | 82.554 | 107.2867 | 118.7211 | 83.0077
CA | 83966216 | 6310 | LAKES CREEK | 6310_Lakes Creek - Berserker 66 kV | Power Factor | 0.99992 | 0.9952 | 0.99727 | 0.99753 | 0.99485 | 0.99755 | 0.99803 | 0.991 | 0.9966 | 0.99983 | 0.9968 | 0.99146 | 0.97637 | 0.96742 | 0.99646
CA | 83966216 | 6310 | LAKES CREEK | 6310_Lakes Creek - Berserker 66 kV | Rating (A) | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372
CA | 84873218 | 7450 | ROLLESTON | 7450_Memooloo - Rolleston 132 kV
CA | 84873218 | 7450 | ROLLESTON | 7450_Memooloo - Rolleston 132 kV | % of Rated A | 12.3405 | 13.1097 | 12.9864 | 12.3406 | 13.1098 | 12.9864 | 12.3402 | 13.1094 | 12.9863 | 12.3941 | 13.1649 | 13.0449 | 12.3942 | 13.165 | 13.045
CA | 84873218 | 7450 | ROLLESTON | 7450_Memooloo - Rolleston 132 kV | Loading (A) | 87.0007 | 96.3559 | 84.6711 | 87.0009 | 96.3565 | 84.6715 | 86.9987 | 96.3538 | 84.6704 | 87.3784 | 96.7612 | 85.0525 | 87.3794 | 96.7624 | 85.0537
CA | 84873218 | 7450 | ROLLESTON | 7450_Memooloo - Rolleston 132 kV | Power Factor | 0.99884 | 0.99852 | 0.9985 | 0.99884 | 0.99852 | 0.9985 | 0.99884 | 0.99852 | 0.9985 | 0.99884 | 0.99853 | 0.99853 | 0.99884 | 0.99853 | 0.99853
CA | 84873218 | 7450 | ROLLESTON | 7450_Memooloo - Rolleston 132 kV | Rating (A) | 705 | 735 | 652 | 705 | 735 | 652 | 705 | 735 | 652 | 705 | 735 | 652 | 705 | 735 | 652
FN | 10020664 | 7200 | 7200 - CRAIGLIE NO 2 | 7200_Craiglie No 2 132 kV
FN | 10020664 | 7200 | 7200 - CRAIGLIE NO 2 | 7200_Craiglie No 2 132 kV | % of Rated A | 8.924 | 13.5238 | 13.8038 | 8.9703 | 13.5226 | 13.7805 | 8.9363 | 13.5475 | 13.7969 | 9.0468 | 13.5928 | 13.828 | 9.1011 | 13.6165 | 13.8422
FN | 10020664 | 7200 | 7200 - CRAIGLIE NO 2 | 7200_Craiglie No 2 132 kV | Loading (A) | 40.3364 | 64.3731 | 58.9422 | 40.5457 | 64.3676 | 58.8428 | 40.392 | 64.4859 | 58.913 | 40.8916 | 64.7019 | 59.0454 | 41.1368 | 64.8145 | 59.1063
FN | 10020664 | 7200 | 7200 - CRAIGLIE NO 2 | 7200_Craiglie No 2 132 kV | Power Factor | 0.82791 | 0.79818 | 0.67862 | 0.82388 | 0.79914 | 0.68527 | 0.83143 | 0.79958 | 0.68689 | 0.83049 | 0.80383 | 0.68976 | 0.82999 | 0.80561 | 0.69178
FN | 10020664 | 7200 | 7200 - CRAIGLIE NO 2 | 7200_Craiglie No 2 132 kV | Rating (A) | 452 | 476 | 427 | 452 | 476 | 427 | 452 | 476 | 427 | 452 | 476 | 427 | 452 | 476 | 427
FN | 10020665 | 7201 | 7201 - CRAIGLIE NO 1 | 7201_Craiglie No 1 132 kV
FN | 10020665 | 7201 | 7201 - CRAIGLIE NO 1 | 7201_Craiglie No 1 132 kV | % of Rated A | 7.5204 | 7.7405 | 7.7595 | 7.5121 | 7.7536 | 7.7658 | 7.5666 | 7.787 | 7.809 | 7.5655 | 7.8086 | 7.8197 | 7.6233 | 7.8597 | 7.8768
FN | 10020665 | 7201 | 7201 - CRAIGLIE NO 1 | 7201_Craiglie No 1 132 kV | Loading (A) | 28.5023 | 28.6398 | 24.9857 | 28.4709 | 28.6883 | 25.0059 | 28.6776 | 28.8121 | 25.145 | 28.6734 | 28.8919 | 25.1794 | 28.8925 | 29.0807 | 25.3632
FN | 10020665 | 7201 | 7201 - CRAIGLIE NO 1 | 7201_Craiglie No 1 132 kV | Power Factor | 0.99223 | 0.99267 | 0.98851 | 0.99385 | 0.99252 | 0.98842 | 0.99258 | 0.99293 | 0.98896 | 0.99419 | 0.99285 | 0.98895 | 0.99425 | 0.99305 | 0.98928
FN | 10020665 | 7201 | 7201 - CRAIGLIE NO 1 | 7201_Craiglie No 1 132 kV | Rating (A) | 379 | 370 | 322 | 379 | 370 | 322 | 379 | 370 | 322 | 379 | 370 | 322 | 379 | 370 | 322
FN | 10020666 | 7216 | 4GEO (GEORGETOWN) | 7216_4GEO (Georgetown) 132 kV
FN | 10020666 | 7216 | 4GEO (GEORGETOWN) | 7216_4GEO (Georgetown) 132 kV | % of Rated A | 10.7604 | 10.3177 | 8.6368 | 10.7604 | 10.3171 | 8.6359 | 10.7604 | 10.3161 | 8.6351 | 10.8661 | 10.3934 | 8.6808 | 10.8661 | 10.3922 | 8.6798
FN | 10020666 | 7216 | 4GEO (GEORGETOWN) | 7216_4GEO (Georgetown) 132 kV | Loading (A) | 32.0659 | 35.4928 | 29.5378 | 32.0659 | 35.4907 | 29.5347 | 32.0658 | 35.4872 | 29.532 | 32.3811 | 35.7533 | 29.6885 | 32.3811 | 35.7491 | 29.685
FN | 10020666 | 7216 | 4GEO (GEORGETOWN) | 7216_4GEO (Georgetown) 132 kV | Power Factor | 0.86352 | 0.83757 | 0.75884 | 0.86352 | 0.83763 | 0.75893 | 0.86352 | 0.83772 | 0.759 | 0.86755 | 0.84309 | 0.76505 | 0.86755 | 0.8432 | 0.76514
FN | 10020666 | 7216 | 4GEO (GEORGETOWN) | 7216_4GEO (Georgetown) 132 kV | Rating (A) | 298 | 344 | 342 | 298 | 344 | 342 | 298 | 344 | 342 | 298 | 344 | 342 | 298 | 344 | 342
FN | 10020667 | 3AT2 | ATHERTON NO 2 | 3AT2_Atherton No 2 66 kV
FN | 10020667 | 3AT2 | ATHERTON NO 2 | 3AT2_Atherton No 2 66 kV | % of Rated A | 17.4314 | 19.6397 | 14.5167 | 17.5544 | 19.7667 | 14.539 | 17.6501 | 19.8992 | 14.8683 | 17.8781 | 20.1536 | 14.8405 | 18.0204 | 20.3091 | 14.9723
FN | 10020667 | 3AT2 | ATHERTON NO 2 | 3AT2_Atherton No 2 66 kV | Loading (A) | 95.1056 | 109.9825 | 75.2703 | 95.7234 | 110.6934 | 75.3294 | 96.2495 | 111.4355 | 77.0302 | 97.4973 | 112.8603 | 76.9004 | 98.2767 | 113.7309 | 77.5859
FN | 10020667 | 3AT2 | ATHERTON NO 2 | 3AT2_Atherton No 2 66 kV | Power Factor | 0.99217 | 0.99225 | 0.99489 | 0.98976 | 0.99017 | 0.993 | 0.98985 | 0.98976 | 0.9921 | 0.98971 | 0.98959 | 0.99295 | 0.98963 | 0.98995 | 0.99287
FN | 10020667 | 3AT2 | ATHERTON NO 2 | 3AT2_Atherton No 2 66 kV | Rating (A) | 548 | 560 | 521 | 548 | 560 | 521 | 548 | 560 | 521 | 548 | 560 | 521 | 548 | 560 | 521
FN | 10020668 | 4KID | ROSS - KIDSTON | 4KID_Ross - Kidston 132 kV
FN | 10020668 | 4KID | ROSS - KIDSTON | 4KID_Ross - Kidston 132 kV | % of Rated A | 56.3338 | 39.3117 | 54.6638 | 56.3336 | 39.3108 | 54.6635 | 56.3329 | 39.3091 | 54.6628 | 56.2324 | 39.209 | 54.5776 | 56.2315 | 39.207 | 54.5767
FN | 10020668 | 4KID | ROSS - KIDSTON | 4KID_Ross - Kidston 132 kV | Loading (A) | 199.9849 | 151.35 | 189.6833 | 199.9841 | 151.3464 | 189.6823 | 199.9819 | 151.3401 | 189.68 | 199.6249 | 150.9548 | 189.3843 | 199.6218 | 150.9469 | 189.3811
FN | 10020668 | 4KID | ROSS - KIDSTON | 4KID_Ross - Kidston 132 kV | Power Factor | 0.89688 | 0.84008 | 0.88664 | 0.89688 | 0.8401 | 0.88665 | 0.89689 | 0.84013 | 0.88666 | 0.89657 | 0.8396 | 0.88638 | 0.89658 | 0.83964 | 0.88639
FN | 10020668 | 4KID | ROSS - KIDSTON | 4KID_Ross - Kidston 132 kV | Rating (A) | 355 | 385 | 347 | 355 | 385 | 347 | 355 | 385 | 347 | 355 | 385 | 347 | 355 | 385 | 347
FN | 10020672 | 3CRO | CROYDON | 3CRO_Croydon 66 kV
FN | 10020672 | 3CRO | CROYDON | 3CRO_Croydon 66 kV | % of Rated A | 10.8755 | 10.2927 | 8.7601 | 10.8755 | 10.2927 | 8.7601 | 10.8755 | 10.2928 | 8.7601 | 11.0388 | 10.4472 | 8.8818 | 11.0388 | 10.4472 | 8.8818
FN | 10020672 | 3CRO | CROYDON | 3CRO_Croydon 66 kV | Loading (A) | 49.7012 | 50.1257 | 41.3475 | 49.7012 | 50.1257 | 41.3475 | 49.7012 | 50.1257 | 41.3475 | 50.4475 | 50.8776 | 41.922 | 50.4475 | 50.8776 | 41.922
FN | 10020672 | 3CRO | CROYDON | 3CRO_Croydon 66 kV | Power Factor | 0.84395 | 0.8465 | 0.79378 | 0.84395 | 0.8465 | 0.79378 | 0.84395 | 0.8465 | 0.79378 | 0.84735 | 0.84983 | 0.79792 | 0.84735 | 0.84983 | 0.79792
FN | 10020672 | 3CRO | CROYDON | 3CRO_Croydon 66 kV | Rating (A) | 457 | 487 | 472 | 457 | 487 | 472 | 457 | 487 | 472 | 457 | 487 | 472 | 457 | 487 | 472
FN | 10020676 | 3NOR | NORMANTON | 3NOR_Normanton 66 kV
FN | 10020676 | 3NOR | NORMANTON | 3NOR_Normanton 66 kV | % of Rated A | 8.405 | 7.9365 | 6.4829 | 8.405 | 7.9365 | 6.4829 | 8.405 | 7.9365 | 6.4829 | 8.5798 | 8.1015 | 6.6169 | 8.5798 | 8.1015 | 6.6169
FN | 10020676 | 3NOR | NORMANTON | 3NOR_Normanton 66 kV | Loading (A) | 38.4106 | 38.6506 | 30.5994 | 38.4106 | 38.6506 | 30.5994 | 38.4106 | 38.6506 | 30.5994 | 39.2097 | 39.4545 | 31.232 | 39.2097 | 39.4545 | 31.232
FN | 10020676 | 3NOR | NORMANTON | 3NOR_Normanton 66 kV | Power Factor | 0.94439 | 0.94391 | 0.94732 | 0.94439 | 0.94391 | 0.94732 | 0.94439 | 0.94391 | 0.94732 | 0.94464 | 0.94417 | 0.94748 | 0.94464 | 0.94417 | 0.94748
FN | 10020676 | 3NOR | NORMANTON | 3NOR_Normanton 66 kV | Rating (A) | 457 | 487 | 472 | 457 | 487 | 472 | 457 | 487 | 472 | 457 | 487 | 472 | 457 | 487 | 472
FN | 10020678 | 3AT1 | ATHERTON NO 1 | 3AT1_Atherton No 1 66 kV
FN | 10020678 | 3AT1 | ATHERTON NO 1 | 3AT1_Atherton No 1 66 kV | % of Rated A | 17.4328 | 19.6413 | 14.5178 | 17.5557 | 19.7682 | 14.5401 | 17.6514 | 19.9007 | 14.8695 | 17.8795 | 20.1552 | 14.8416 | 18.0218 | 20.3107 | 14.9734
FN | 10020678 | 3AT1 | ATHERTON NO 1 | 3AT1_Atherton No 1 66 kV | Loading (A) | 95.113 | 109.991 | 75.2761 | 95.7308 | 110.7019 | 75.3353 | 96.2569 | 111.4441 | 77.0362 | 97.5049 | 112.8691 | 76.9064 | 98.2843 | 113.7397 | 77.5919
FN | 10020678 | 3AT1 | ATHERTON NO 1 | 3AT1_Atherton No 1 66 kV | Power Factor | 0.99217 | 0.99225 | 0.99489 | 0.98976 | 0.99017 | 0.993 | 0.98985 | 0.98976 | 0.9921 | 0.98971 | 0.98959 | 0.99295 | 0.98963 | 0.98995 | 0.99287
FN | 10020678 | 3AT1 | ATHERTON NO 1 | 3AT1_Atherton No 1 66 kV | Rating (A) | 548 | 560 | 521 | 548 | 560 | 521 | 548 | 560 | 521 | 548 | 560 | 521 | 548 | 560 | 521
FN | 10020733 | 3EVE | EVELYN | 3EVE_Evelyn 66 kV
FN | 10020733 | 3EVE | EVELYN | 3EVE_Evelyn 66 kV | % of Rated A | 48.3235 | 33.016 | 37.1564 | 48.2805 | 33.0981 | 37.1956 | 48.311 | 33.0204 | 37.1633 | 48.3314 | 33.047 | 37.179 | 48.2585 | 33.0955 | 37.1911
FN | 10020733 | 3EVE | EVELYN | 3EVE_Evelyn 66 kV | Loading (A) | 81.6666 | 79.5687 | 87.3177 | 81.5941 | 79.7665 | 87.4097 | 81.6456 | 79.5791 | 87.3338 | 81.68 | 79.6434 | 87.3707 | 81.5569 | 79.7601 | 87.3991
FN | 10020733 | 3EVE | EVELYN | 3EVE_Evelyn 66 kV | Power Factor | 0.98799 | 0.9859 | 0.99269 | 0.98818 | 0.98578 | 0.99266 | 0.988 | 0.9859 | 0.99269 | 0.98798 | 0.98585 | 0.99267 | 0.9882 | 0.98579 | 0.99266
FN | 10020733 | 3EVE | EVELYN | 3EVE_Evelyn 66 kV | Rating (A) | 169 | 241 | 235 | 169 | 241 | 235 | 169 | 241 | 235 | 169 | 241 | 235 | 169 | 241 | 235
FN | 10020762 | 3MTG | MT GARNET | 3MTG_Mt Garnet 66 kV
FN | 10020762 | 3MTG | MT GARNET | 3MTG_Mt Garnet 66 kV | % of Rated A | 51.5248 | 32.6567 | 36.7121 | 51.5972 | 32.7478 | 36.7542 | 51.5105 | 32.6709 | 36.7085 | 52.1126 | 33.0886 | 37.1351 | 52.1357 | 33.1234 | 37.1491
FN | 10020762 | 3MTG | MT GARNET | 3MTG_Mt Garnet 66 kV | Loading (A) | 87.0489 | 78.6752 | 86.244 | 87.1671 | 78.8946 | 86.3429 | 87.0246 | 78.7094 | 86.2356 | 88.0424 | 79.7162 | 87.2383 | 88.0774 | 79.7999 | 87.2711
FN | 10020762 | 3MTG | MT GARNET | 3MTG_Mt Garnet 66 kV | Power Factor | 0.99949 | 0.99954 | 0.99944 | 0.99931 | 0.99953 | 0.99944 | 0.99949 | 0.99954 | 0.99944 | 0.99949 | 0.99954 | 0.99944 | 0.99931 | 0.99954 | 0.99944
FN | 10020762 | 3MTG | MT GARNET | 3MTG_Mt Garnet 66 kV | Rating (A) | 169 | 241 | 235 | 169 | 241 | 235 | 169 | 241 | 235 | 169 | 241 | 235 | 169 | 241 | 235
FN | 10020819 | 7206 | 7206 CAIRNS CITY | 7206 Woree-Cairns Terminal-Cairns City
FN | 10020819 | 7206 | 7206 CAIRNS CITY | 7206 Woree-Cairns Terminal-Cairns City | % of Rated A | 22.7329 | 18.4429 | 20.1221 | 22.5803 | 18.3194 | 19.9874 | 22.5292 | 18.278 | 19.9422 | 22.5292 | 18.278 | 19.9422 | 22.4783 | 18.2369 | 19.8974
FN | 10020819 | 7206 | 7206 CAIRNS CITY | 7206 Woree-Cairns Terminal-Cairns City | Loading (A) | 94.9666 | 82.9473 | 82.0532 | 94.3293 | 82.3922 | 81.5042 | 94.1156 | 82.2061 | 81.3201 | 94.1156 | 82.2061 | 81.3201 | 93.9033 | 82.0212 | 81.1372
FN | 10020819 | 7206 | 7206 CAIRNS CITY | 7206 Woree-Cairns Terminal-Cairns City | Power Factor | 0.99692 | 0.9981 | 0.99817 | 0.99699 | 0.99815 | 0.99822 | 0.99701 | 0.99817 | 0.99824 | 0.99701 | 0.99817 | 0.99824 | 0.99703 | 0.99818 | 0.99826
FN | 10020819 | 7206 | 7206 CAIRNS CITY | 7206 Woree-Cairns Terminal-Cairns City | Rating (A) | 418 | 450 | 408 | 418 | 450 | 408 | 418 | 450 | 408 | 418 | 450 | 408 | 418 | 450 | 408
FN | 10020851 | 3MO2 | MOSSMAN NO 2 | 3MO2_Mossman No 2 66 kV
FN | 10020851 | 3MO2 | MOSSMAN NO 2 | 3MO2_Mossman No 2 66 kV | % of Rated A | 28.5438 | 22.4609 | 17.8121 | 28.5672 | 22.503 | 17.7379 | 28.8637 | 22.7174 | 18.1661 | 28.8796 | 22.7434 | 17.9214 | 28.8865 | 22.7511 | 17.9318
FN | 10020851 | 3MO2 | MOSSMAN NO 2 | 3MO2_Mossman No 2 66 kV | Loading (A) | 37.5832 | 37.4174 | 28.2656 | 37.6148 | 37.4873 | 28.1487 | 38.0041 | 37.8442 | 28.8246 | 38.025 | 37.8875 | 28.4391 | 38.0349 | 37.9002 | 28.4554
FN | 10020851 | 3MO2 | MOSSMAN NO 2 | 3MO2_Mossman No 2 66 kV | Power Factor | 0.99477 | 0.995 | 0.99865 | 0.99484 | 0.99494 | 0.99874 | 0.9946 | 0.99482 | 0.99835 | 0.99458 | 0.99478 | 0.99865 | 0.99467 | 0.99477 | 0.99864
FN | 10020851 | 3MO2 | MOSSMAN NO 2 | 3MO2_Mossman No 2 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
FN | 10020852 | 3MO1 | MOSSMAN NO 1 | 3MO1_Mossman No 1 66 kV
FN | 10020852 | 3MO1 | MOSSMAN NO 1 | 3MO1_Mossman No 1 66 kV | % of Rated A | 71.7139 | 57.6796 | 45.3981 | 72.0622 | 57.9757 | 45.4462 | 73.4101 | 59.0319 | 46.9038 | 74.0288 | 59.5327 | 46.8429 | 74.6392 | 60.0383 | 47.2053
FN | 10020852 | 3MO1 | MOSSMAN NO 1 | 3MO1_Mossman No 1 66 kV | Loading (A) | 94.6623 | 96.325 | 72.183 | 95.1221 | 96.8194 | 72.2594 | 96.9013 | 98.5833 | 74.577 | 97.718 | 99.4196 | 74.4803 | 98.5238 | 100.2639 | 75.0564
FN | 10020852 | 3MO1 | MOSSMAN NO 1 | 3MO1_Mossman No 1 66 kV | Power Factor | 0.97136 | 0.97324 | 0.93499 | 0.97192 | 0.97383 | 0.93449 | 0.96153 | 0.96367 | 0.92502 | 0.96253 | 0.96464 | 0.92243 | 0.96348 | 0.9656 | 0.92403
FN | 10020852 | 3MO1 | MOSSMAN NO 1 | 3MO1_Mossman No 1 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
FN | 10020859 | 3DIM | DIMBULAH | 3DIM_Dimbulah 66 kV
FN | 10020859 | 3DIM | DIMBULAH | 3DIM_Dimbulah 66 kV | % of Rated A | 47.5807 | 30.2197 | 33.9448 | 46.9918 | 30.3202 | 34.052 | 47.2167 | 30.0028 | 33.7482 | 46.8443 | 29.7739 | 33.4935 | 46.2101 | 29.7835 | 33.5035
FN | 10020859 | 3DIM | DIMBULAH | 3DIM_Dimbulah 66 kV | Loading (A) | 103.7201 | 81.2888 | 85.8796 | 102.4374 | 81.5595 | 86.1509 | 102.9275 | 80.7066 | 85.3829 | 102.1162 | 80.0917 | 84.7387 | 100.7346 | 80.1175 | 84.7639
FN | 10020859 | 3DIM | DIMBULAH | 3DIM_Dimbulah 66 kV | Power Factor | 0.99937 | 0.99993 | 0.99999 | 0.99961 | 0.99995 | 1 | 0.99957 | 0.99999 | 0.99998 | 0.99966 | 0.99995 | 0.99995 | 0.99979 | 0.99995 | 0.99995
FN | 10020859 | 3DIM | DIMBULAH | 3DIM_Dimbulah 66 kV | Rating (A) | 218 | 269 | 253 | 218 | 269 | 253 | 218 | 269 | 253 | 218 | 269 | 253 | 218 | 269 | 253
FN | 10129304 | 3RA1 | RAVENSHOE NO 1 | 3RA1_Ravenshoe No 1 66 kV
FN | 10129304 | 3RA1 | RAVENSHOE NO 1 | 3RA1_Ravenshoe No 1 66 kV | % of Rated A | 51.8061 | 36.4055 | 38.987 | 51.8422 | 36.4948 | 39.0285 | 51.7929 | 36.4103 | 38.995 | 51.8146 | 36.4393 | 39.0112 | 51.828 | 36.492 | 39.024
FN | 10129304 | 3RA1 | RAVENSHOE NO 1 | 3RA1_Ravenshoe No 1 66 kV | Loading (A) | 87.5524 | 87.7374 | 91.6195 | 87.6133 | 87.9526 | 91.7169 | 87.5301 | 87.7488 | 91.6383 | 87.5666 | 87.8186 | 91.6763 | 87.5893 | 87.9458 | 91.7064
FN | 10129304 | 3RA1 | RAVENSHOE NO 1 | 3RA1_Ravenshoe No 1 66 kV | Power Factor | 0.99183 | 0.99201 | 0.9945 | 0.99214 | 0.99195 | 0.99447 | 0.99183 | 0.99201 | 0.99449 | 0.99182 | 0.99199 | 0.99448 | 0.99215 | 0.99195 | 0.99448
FN | 10129304 | 3RA1 | RAVENSHOE NO 1 | 3RA1_Ravenshoe No 1 66 kV | Rating (A) | 169 | 241 | 235 | 169 | 241 | 235 | 169 | 241 | 235 | 169 | 241 | 235 | 169 | 241 | 235
FN | 10131933 | 3MA2 | 3MA2 | 3MA2_Mareeba No 2 66 kV
FN | 10131933 | 3MA2 | 3MA2 | 3MA2_Mareeba No 2 66 kV | % of Rated A | 57.4039 | 40.9246 | 31.4429 | 57.6776 | 41.1311 | 31.4732 | 58.6829 | 41.8309 | 32.4454 | 59.1675 | 42.1787 | 32.4014 | 59.6454 | 42.5298 | 32.6426
FN | 10131933 | 3MA2 | 3MA2 | 3MA2_Mareeba No 2 66 kV | Loading (A) | 97.0126 | 98.6284 | 73.8908 | 97.4751 | 99.1259 | 73.9621 | 99.1741 | 100.8124 | 76.2466 | 99.9931 | 101.6506 | 76.1433 | 100.8007 | 102.4968 | 76.7102
FN | 10131933 | 3MA2 | 3MA2 | 3MA2_Mareeba No 2 66 kV | Power Factor | 0.98116 | 0.98246 | 0.94884 | 0.9816 | 0.98292 | 0.94833 | 0.97333 | 0.97485 | 0.94035 | 0.97412 | 0.97561 | 0.93779 | 0.97486 | 0.97636 | 0.93921
FN | 10131933 | 3MA2 | 3MA2 | 3MA2_Mareeba No 2 66 kV | Rating (A) | 169 | 241 | 235 | 169 | 241 | 235 | 169 | 241 | 235 | 169 | 241 | 235 | 169 | 241 | 235
FN | 10132678 | 4LAK | 7285 LAKELAND 132kV | 7285_4LAK (Lakeland) 132kV
FN | 10132678 | 4LAK | 7285 LAKELAND 132kV | 7285_4LAK (Lakeland) 132kV | % of Rated A | 8.282 | 7.1504 | 7.6336 | 8.2465 | 7.1473 | 7.6133 | 8.3307 | 7.1501 | 7.6128 | 8.2583 | 7.1849 | 7.6363 | 8.2216 | 7.1834 | 7.6653
FN | 10132678 | 4LAK | 7285 LAKELAND 132kV | 7285_4LAK (Lakeland) 132kV | Loading (A) | 38.7596 | 38.8981 | 36.6414 | 38.5936 | 38.8815 | 36.5439 | 38.9876 | 38.8964 | 36.5414 | 38.6488 | 39.0859 | 36.6543 | 38.4769 | 39.0776 | 36.7935
FN | 10132678 | 4LAK | 7285 LAKELAND 132kV | 7285_4LAK (Lakeland) 132kV | Power Factor | 0.56662 | 0.74641 | 0.60852 | 0.56918 | 0.74757 | 0.61494 | 0.56313 | 0.74653 | 0.61504 | 0.56047 | 0.75467 | 0.62113 | 0.5631 | 0.75529 | 0.60412
FN | 10132678 | 4LAK | 7285 LAKELAND 132kV | 7285_4LAK (Lakeland) 132kV | Rating (A) | 468 | 544 | 480 | 468 | 544 | 480 | 468 | 544 | 480 | 468 | 544 | 480 | 468 | 544 | 480
FN | 80076156 | 3HLA | 3HLA | 3HLA_Helenvale 66 kV
FN | 80076156 | 3HLA | 3HLA | 3HLA_Helenvale 66 kV | % of Rated A | 11.5088 | 11.731 | 9.3848 | 11.5088 | 11.7451 | 9.3446 | 11.5088 | 11.7325 | 9.3455 | 11.7318 | 11.9707 | 9.5152 | 11.7318 | 11.9784 | 9.5206
FN | 80076156 | 3HLA | 3HLA | 3HLA_Helenvale 66 kV | Loading (A) | 43.4895 | 46.7828 | 34.7238 | 43.4896 | 46.8385 | 34.575 | 43.4895 | 46.7885 | 34.5784 | 44.3293 | 47.7358 | 35.2062 | 44.3294 | 47.7664 | 35.2262
FN | 80076156 | 3HLA | 3HLA | 3HLA_Helenvale 66 kV | Power Factor | 0.99978 | 0.99917 | 0.99437 | 0.99978 | 0.99914 | 0.99445 | 0.99978 | 0.99916 | 0.99445 | 0.99963 | 0.99888 | 0.99414 | 0.99963 | 0.99887 | 0.99412
FN | 80076156 | 3HLA | 3HLA | 3HLA_Helenvale 66 kV | Rating (A) | 378 | 399 | 370 | 378 | 399 | 370 | 378 | 399 | 370 | 378 | 399 | 370 | 378 | 399 | 370
FN | 83003861 | 3CHI | CHILLAGOE FDR | 3CHI_Chillagoe 66 kV
FN | 83003861 | 3CHI | CHILLAGOE FDR | 3CHI_Chillagoe 66 kV | % of Rated A | 8.8051 | 8.4061 | 8.5185 | 8.9968 | 8.6015 | 8.708 | 8.9834 | 8.5809 | 8.7505 | 8.9824 | 8.5887 | 8.6979 | 8.9838 | 8.5956 | 8.7004
FN | 83003861 | 3CHI | CHILLAGOE FDR | 3CHI_Chillagoe 66 kV | Loading (A) | 40.2391 | 40.9376 | 40.2075 | 41.1152 | 41.8891 | 41.1017 | 41.0543 | 41.7892 | 41.3023 | 41.0496 | 41.8268 | 41.054 | 41.0559 | 41.8604 | 41.066
FN | 83003861 | 3CHI | CHILLAGOE FDR | 3CHI_Chillagoe 66 kV | Power Factor | 0.99365 | 0.99388 | 0.99361 | 0.99402 | 0.99428 | 0.99399 | 0.99397 | 0.99421 | 0.99408 | 0.99396 | 0.99424 | 0.99395 | 0.99397 | 0.99426 | 0.99396
FN | 83003861 | 3CHI | CHILLAGOE FDR | 3CHI_Chillagoe 66 kV | Rating (A) | 457 | 487 | 472 | 457 | 487 | 472 | 457 | 487 | 472 | 457 | 487 | 472 | 457 | 487 | 472
FN | 83031299 | MUNGANA | MUNGANA | Mungana 66 kV
FN | 83031299 | MUNGANA | MUNGANA | Mungana 66 kV | % of Rated A | 8.7473 | 8.3527 | 8.4623 | 8.9407 | 8.55 | 8.6535 | 8.9271 | 8.529 | 8.6965 | 8.926 | 8.5369 | 8.6432 | 8.9275 | 8.5439 | 8.6458
FN | 83031299 | MUNGANA | MUNGANA | Mungana 66 kV | Loading (A) | 39.975 | 40.6776 | 39.9421 | 40.8591 | 41.6383 | 40.8447 | 40.7968 | 41.5361 | 41.0476 | 40.7919 | 41.5746 | 40.7959 | 40.7985 | 41.609 | 40.8082
FN | 83031299 | MUNGANA | MUNGANA | Mungana 66 kV | Power Factor | 0.99928 | 0.99931 | 0.99928 | 0.99933 | 0.99936 | 0.99932 | 0.99932 | 0.99935 | 0.99933 | 0.99932 | 0.99935 | 0.99932 | 0.99932 | 0.99935 | 0.99932
FN | 83031299 | MUNGANA | MUNGANA | Mungana 66 kV | Rating (A) | 457 | 487 | 472 | 457 | 487 | 472 | 457 | 487 | 472 | 457 | 487 | 472 | 457 | 487 | 472
FN | 83842085 | FDR 7333 | 132KV CANO 7333 FDR | 7333_Cairns North 132 kV
FN | 83842085 | FDR 7333 | 132KV CANO 7333 FDR | 7333_Cairns North 132 kV | % of Rated A | 25.6421 | 24.8903 | 26.1836 | 25.6966 | 24.9454 | 26.2347 | 25.7787 | 25.0282 | 26.3116 | 25.861 | 25.1113 | 26.3888 | 25.9436 | 25.1947 | 26.4662
FN | 83842085 | FDR 7333 | 132KV CANO 7333 FDR | 7333_Cairns North 132 kV | Loading (A) | 121.2873 | 123.7048 | 116.7789 | 121.5451 | 123.9785 | 117.0067 | 121.9331 | 124.3902 | 117.3498 | 122.3225 | 124.8033 | 117.694 | 122.7132 | 125.2177 | 118.0395
FN | 83842085 | FDR 7333 | 132KV CANO 7333 FDR | 7333_Cairns North 132 kV | Power Factor | 0.79416 | 0.80811 | 0.76461 | 0.79571 | 0.80961 | 0.76623 | 0.798 | 0.81185 | 0.76864 | 0.80028 | 0.81406 | 0.77102 | 0.80253 | 0.81625 | 0.77339
FN | 83842085 | FDR 7333 | 132KV CANO 7333 FDR | 7333_Cairns North 132 kV | Rating (A) | 473 | 497 | 446 | 473 | 497 | 446 | 473 | 497 | 446 | 473 | 497 | 446 | 473 | 497 | 446
FN | 83842089 | 7332 | Cairns North 132 kV | 7332_Cairns North 132 kV
FN | 83842089 | 7332 | Cairns North 132 kV | 7332_Cairns North 132 kV | % of Rated A | 26.6028 | 25.8377 | 27.1324 | 26.661 | 25.8965 | 27.1871 | 26.7486 | 25.9849 | 27.2694 | 26.8366 | 26.0736 | 27.3519 | 26.9248 | 26.1626 | 27.4348
FN | 83842089 | 7332 | Cairns North 132 kV | 7332_Cairns North 132 kV | Loading (A) | 125.8311 | 128.4132 | 121.0107 | 126.1065 | 128.7054 | 121.2545 | 126.5211 | 129.145 | 121.6215 | 126.937 | 129.5859 | 121.9897 | 127.3543 | 130.0282 | 122.3592
FN | 83842089 | 7332 | Cairns North 132 kV | 7332_Cairns North 132 kV | Power Factor | 0.80271 | 0.81636 | 0.77371 | 0.80423 | 0.81784 | 0.7753 | 0.80648 | 0.82002 | 0.77767 | 0.8087 | 0.82219 | 0.78001 | 0.81091 | 0.82432 | 0.78233
FN | 83842089 | 7332 | Cairns North 132 kV | 7332_Cairns North 132 kV | Rating (A) | 473 | 497 | 446 | 473 | 497 | 446 | 473 | 497 | 446 | 473 | 497 | 446 | 473 | 497 | 446
FN | 84463555 | 3COO | COOKTOWN FEEDER | 3COO_Cooktown 66 kV
FN | 84463555 | 3COO | COOKTOWN FEEDER | 3COO_Cooktown 66 kV | % of Rated A | 15.9724 | 16.6503 | 11.9747 | 15.9724 | 16.6703 | 11.9244 | 15.9724 | 16.6523 | 11.9249 | 16.3244 | 17.0434 | 12.1826 | 16.3244 | 17.0545 | 12.188
FN | 84463555 | 3COO | COOKTOWN FEEDER | 3COO_Cooktown 66 kV | Loading (A) | 39.6116 | 41.2927 | 29.6973 | 39.6117 | 41.3424 | 29.5725 | 39.6116 | 41.2978 | 29.5737 | 40.4844 | 42.2678 | 30.2129 | 40.4845 | 42.2951 | 30.2262
FN | 84463555 | 3COO | COOKTOWN FEEDER | 3COO_Cooktown 66 kV | Power Factor | 0.97087 | 0.97074 | 0.9722 | 0.97087 | 0.97072 | 0.97222 | 0.97087 | 0.97074 | 0.97223 | 0.97074 | 0.97059 | 0.97213 | 0.97074 | 0.97059 | 0.97214
FN | 84463555 | 3COO | COOKTOWN FEEDER | 3COO_Cooktown 66 kV | Rating (A) | 248 | 248 | 248 | 248 | 248 | 248 | 248 | 248 | 248 | 248 | 248 | 248 | 248 | 248 | 248
MK | 20010276 | ME-PR-1 | Merinda-Proserpine No.1 | ME-PR-1_Merinda - Proserpine No 1 66 kV
MK | 20010276 | ME-PR-1 | Merinda-Proserpine No.1 | ME-PR-1_Merinda - Proserpine No 1 66 kV | % of Rated A | 10.1389 | 8.9336 | 9.1086 | 10.2267 | 9.0161 | 9.1477 | 10.389 | 9.1719 | 9.2278 | 10.5105 | 9.26 | 9.2633 | 10.6656 | 9.3895 | 9.3212
MK | 20010276 | ME-PR-1 | Merinda-Proserpine No.1 | ME-PR-1_Merinda - Proserpine No 1 66 kV | Loading (A) | 19.5681 | 21.3512 | 19.8567 | 19.7376 | 21.5484 | 19.9419 | 20.0509 | 21.9208 | 20.1167 | 20.2852 | 22.1315 | 20.194 | 20.5847 | 22.441 | 20.3201
MK | 20010276 | ME-PR-1 | Merinda-Proserpine No.1 | ME-PR-1_Merinda - Proserpine No 1 66 kV | Power Factor | 0.88957 | 0.97942 | 0.96305 | 0.88895 | 0.97866 | 0.96406 | 0.88665 | 0.97639 | 0.96633 | 0.88569 | 0.97528 | 0.96731 | 0.88512 | 0.97423 | 0.9686
MK | 20010276 | ME-PR-1 | Merinda-Proserpine No.1 | ME-PR-1_Merinda - Proserpine No 1 66 kV | Rating (A) | 193 | 239 | 218 | 193 | 239 | 218 | 193 | 239 | 218 | 193 | 239 | 218 | 193 | 239 | 218
MK | 20011116 | NL-WR-1 | Newlands-Wirralie | NL-WR-1_Newlands-Wirralie 1 66 kV
MK | 20011116 | NL-WR-1 | Newlands-Wirralie | NL-WR-1_Newlands-Wirralie 1 66 kV | % of Rated A | 4.8777 | 4.3931 | 4.9835 | 4.8776 | 4.3929 | 4.9834 | 4.8772 | 4.3924 | 4.9831 | 4.8768 | 4.3919 | 4.9827 | 4.8763 | 4.3914 | 4.9822
MK | 20011116 | NL-WR-1 | Newlands-Wirralie | NL-WR-1_Newlands-Wirralie 1 66 kV | Loading (A) | 9.1701 | 9.0059 | 9.2195 | 9.1699 | 9.0054 | 9.2193 | 9.1692 | 9.0045 | 9.2187 | 9.1684 | 9.0034 | 9.2179 | 9.1675 | 9.0023 | 9.2171
MK | 20011116 | NL-WR-1 | Newlands-Wirralie | NL-WR-1_Newlands-Wirralie 1 66 kV | Power Factor | 0.21986 | 0.28376 | 0.20537 | 0.21987 | 0.28379 | 0.20538 | 0.2199 | 0.28385 | 0.2054 | 0.21994 | 0.28391 | 0.20544 | 0.21998 | 0.28398 | 0.20547
MK | 20011116 | NL-WR-1 | Newlands-Wirralie | NL-WR-1_Newlands-Wirralie 1 66 kV | Rating (A) | 188 | 205 | 185 | 188 | 205 | 185 | 188 | 205 | 185 | 188 | 205 | 185 | 188 | 205 | 185
MK | 20013617 | PR-BN-1 | Proserpine-Bowen No.1 | PR-BN-1_Proserpine - Bowen No 1 66 kV
MK | 20013617 | PR-BN-1 | Proserpine-Bowen No.1 | PR-BN-1_Proserpine - Bowen No 1 66 kV | % of Rated A | 6.2991 | 3.6655 | 5.0974 | 6.2967 | 3.6671 | 5.0936 | 6.3216 | 3.688 | 5.1116 | 6.312 | 3.6952 | 5.1092 | 6.2943 | 3.6971 | 5.0978
MK | 20013617 | PR-BN-1 | Proserpine-Bowen No.1 | PR-BN-1_Proserpine - Bowen No 1 66 kV | Loading (A) | 17.3854 | 11.583 | 14.8334 | 17.3789 | 11.5879 | 14.8225 | 17.4477 | 11.6542 | 14.8749 | 17.4211 | 11.677 | 14.8677 | 17.3722 | 11.6828 | 14.8346
MK | 20013617 | PR-BN-1 | Proserpine-Bowen No.1 | PR-BN-1_Proserpine - Bowen No 1 66 kV | Power Factor | 0.82283 | 0.46133 | 0.78886 | 0.82232 | 0.45968 | 0.78836 | 0.82089 | 0.44688 | 0.78675 | 0.81929 | 0.4431 | 0.78604 | 0.81689 | 0.4328 | 0.7839
MK | 20013617 | PR-BN-1 | Proserpine-Bowen No.1 | PR-BN-1_Proserpine - Bowen No 1 66 kV | Rating (A) | 276 | 316 | 291 | 276 | 316 | 291 | 276 | 316 | 291 | 276 | 316 | 291 | 276 | 316 | 291
MK | 30053760 | 118 | CANNONVALE NO 2 | 118_Cannonvale No 2 66 kV
MK | 30053760 | 118 | CANNONVALE NO 2 | 118_Cannonvale No 2 66 kV | % of Rated A | 85.4245 | 85.2924 | 61.776 | 85.8424 | 85.7131 | 61.9626 | 86.2837 | 86.1597 | 62.1516 | 87.1095 | 86.9876 | 62.528 | 87.5463 | 87.428 | 62.7194
MK | 30053760 | 118 | CANNONVALE NO 2 | 118_Cannonvale No 2 66 kV | Loading (A) | 164.8694 | 164.6144 | 119.2278 | 165.6758 | 165.4262 | 119.5877 | 166.5276 | 166.2882 | 119.9526 | 168.1213 | 167.886 | 120.6791 | 168.9643 | 168.736 | 121.0484
MK | 30053760 | 118 | CANNONVALE NO 2 | 118_Cannonvale No 2 66 kV | Power Factor | 0.976 | 0.97636 | 0.85475 | 0.97689 | 0.97725 | 0.85686 | 0.97784 | 0.97822 | 0.85906 | 0.97942 | 0.97979 | 0.86303 | 0.98026 | 0.98064 | 0.8651
MK | 30053760 | 118 | CANNONVALE NO 2 | 118_Cannonvale No 2 66 kV | Rating (A) | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193
MK | 30053761 | 119 | CANNONVALE NO 1 | 119_Cannonvale No 1 66 kV
MK | 30053761 | 119 | CANNONVALE NO 1 | 119_Cannonvale No 1 66 kV | % of Rated A | 84.2416 | 59.5759 | 48.9416 | 84.7066 | 59.9208 | 49.1624 | 85.7047 | 60.6378 | 49.6816 | 85.7528 | 60.6705 | 49.6943 | 86.2378 | 61.0265 | 49.921
MK | 30053761 | 119 | CANNONVALE NO 1 | 119_Cannonvale No 1 66 kV | Loading (A) | 155.843 | 154.2977 | 123.3302 | 156.7032 | 155.1909 | 123.8866 | 158.5496 | 157.048 | 125.1947 | 158.6387 | 157.1326 | 125.2269 | 159.536 | 158.0545 | 125.798
MK | 30053761 | 119 | CANNONVALE NO 1 | 119_Cannonvale No 1 66 kV | Power Factor | 0.98947 | 0.98984 | 0.99495 | 0.98936 | 0.98972 | 0.99489 | 0.98909 | 0.98944 | 0.99471 | 0.98905 | 0.98941 | 0.9947 | 0.98892 | 0.98931 | 0.99463
MK | 30053761 | 119 | CANNONVALE NO 1 | 119_Cannonvale No 1 66 kV | Rating (A) | 185 | 259 | 252 | 185 | 259 | 252 | 185 | 259 | 252 | 185 | 259 | 252 | 185 | 259 | 252
MK | 30053762 | 120 | Proserpine-Calen | 120_Prosperpine - Calen 66 kV
MK | 30053762 | 120 | Proserpine-Calen | 120_Prosperpine - Calen 66 kV | % of Rated A | 23.6461 | 34.298 | 30.6759 | 24.0012 | 34.8063 | 31.1238 | 24.3792 | 35.4023 | 31.6345 | 24.3925 | 35.4245 | 31.6459 | 24.4078 | 35.4507 | 31.6612
MK | 30053762 | 120 | Proserpine-Calen | 120_Prosperpine - Calen 66 kV | Loading (A) | 31.2129 | 60.7028 | 52.1448 | 31.6815 | 61.6025 | 52.9062 | 32.1805 | 62.6574 | 53.7743 | 32.1981 | 62.6966 | 53.7937 | 32.2183 | 62.743 | 53.8197
MK | 30053762 | 120 | Proserpine-Calen | 120_Prosperpine - Calen 66 kV | Power Factor | 0.98904 | 0.96295 | 0.97031 | 0.98886 | 0.96432 | 0.97033 | 0.98817 | 0.96181 | 0.96936 | 0.98814 | 0.96176 | 0.96934 | 0.9881 | 0.9617 | 0.9693
MK | 30053762 | 120 | Proserpine-Calen | 120_Prosperpine - Calen 66 kV | Rating (A) | 132 | 177 | 170 | 132 | 177 | 170 | 132 | 177 | 170 | 132 | 177 | 170 | 132 | 177 | 170
MK | 30053795 | 3045 | SARINA 1 | 3045_Sarina No 1 33 kV
MK | 30053795 | 3045 | SARINA 1 | 3045_Sarina No 1 33 kV | % of Rated A | 43.0569 | 56.0366 | 46.6586 | 43.1882 | 56.1853 | 46.6596 | 43.3214 | 56.3369 | 46.6613 | 43.453 | 56.4858 | 46.6623 | 43.9048 | 57.0723 | 47.1244
MK | 30053795 | 3045 | SARINA 1 | 3045_Sarina No 1 33 kV | Loading (A) | 269.1048 | 350.2133 | 142.3087 | 269.9254 | 351.1421 | 142.3119 | 270.7576 | 352.0894 | 142.317 | 271.5804 | 353.0199 | 142.3202 | 274.4037 | 356.6851 | 143.7294
MK | 30053795 | 3045 | SARINA 1 | 3045_Sarina No 1 33 kV | Power Factor | 0.99942 | 0.993 | 0.88241 | 0.99937 | 0.99288 | 0.88244 | 0.99932 | 0.99275 | 0.88247 | 0.99927 | 0.99263 | 0.88249 | 0.99913 | 0.99227 | 0.8859
MK | 30053795 | 3045 | SARINA 1 | 3045_Sarina No 1 33 kV | Rating (A) | 625 | 625 | 305 | 625 | 625 | 305 | 625 | 625 | 305 | 625 | 625 | 305 | 625 | 625 | 305
MK | 30053796 | 3046 | ROSELLA | 3046_Rosella 33 kV
MK | 30053796 | 3046 | ROSELLA | 3046_Rosella 33 kV | % of Rated A | 31.8329 | 35.3771 | 32.1471 | 31.8341 | 35.3787 | 32.148 | 32.2682 | 35.8668 | 32.5866 | 32.2695 | 35.8686 | 32.5876 | 32.2726 | 35.871 | 32.59
MK | 30053796 | 3046 | ROSELLA | 3046_Rosella 33 kV | Loading (A) | 130.1965 | 144.6922 | 131.4815 | 130.2016 | 144.699 | 131.4855 | 131.9769 | 146.6953 | 133.279 | 131.9821 | 146.7024 | 133.2831 | 131.995 | 146.7124 | 133.2931
MK | 30053796 | 3046 | ROSELLA | 3046_Rosella 33 kV | Power Factor | 0.93115 | 0.92819 | 0.93082 | 0.93115 | 0.92819 | 0.93082 | 0.93068 | 0.92766 | 0.93035 | 0.93068 | 0.92766 | 0.93035 | 0.93068 | 0.92765 | 0.93035
MK | 30053796 | 3046 | ROSELLA | 3046_Rosella 33 kV | Rating (A) | 409 | 409 | 409 | 409 | 409 | 409 | 409 | 409 | 409 | 409 | 409 | 409 | 409 | 409 | 409
MK | 30053797 | 3047 | SARINA 2 | 3047_Sarina No 2 33 kV
MK | 30053797 | 3047 | SARINA 2 | 3047_Sarina No 2 33 kV | % of Rated A | 43.316 | 47.6015 | 37.3062 | 43.5525 | 47.8388 | 37.4816 | 43.7911 | 48.0789 | 37.6588 | 44.0281 | 48.3165 | 37.8344 | 44.5323 | 48.8193 | 38.2073
MK | 30053797 | 3047 | SARINA 2 | 3047_Sarina No 2 33 kV | Loading (A) | 164.5952 | 198.9687 | 156.6804 | 165.4939 | 199.9603 | 157.4168 | 166.4006 | 200.9639 | 158.1611 | 167.3014 | 201.9571 | 158.8988 | 169.2171 | 204.0591 | 160.465
MK | 30053797 | 3047 | SARINA 2 | 3047_Sarina No 2 33 kV | Power Factor | 0.96393 | 0.95778 | 0.96026 | 0.96374 | 0.9576 | 0.96014 | 0.96354 | 0.95742 | 0.96001 | 0.96335 | 0.95724 | 0.95989 | 0.96301 | 0.95717 | 0.95969
MK | 30053797 | 3047 | SARINA 2 | 3047_Sarina No 2 33 kV | Rating (A) | 380 | 418 | 420 | 380 | 418 | 420 | 380 | 418 | 420 | 380 | 418 | 420 | 380 | 418 | 420
MK | 30053798 | 231 | Carmila | 231_Carmila 33 kV
MK | 30053798 | 231 | Carmila | 231_Carmila 33 kV | % of Rated A | 27.3244 | 52.7325 | 50.5316 | 27.3337 | 52.7484 | 50.546 | 27.344 | 52.763 | 50.5628 | 27.3534 | 52.7814 | 50.5772 | 27.3731 | 52.8156 | 50.608
MK | 30053798 | 231 | Carmila | 231_Carmila 33 kV | Loading (A) | 41.5207 | 80.1534 | 76.8081 | 41.5349 | 80.1775 | 76.8299 | 41.5504 | 80.1998 | 76.8555 | 41.5648 | 80.2278 | 76.8774 | 41.5947 | 80.2797 | 76.9242
MK | 30053798 | 231 | Carmila | 231_Carmila 33 kV | Power Factor | 0.92575 | 0.90755 | 0.90868 | 0.92573 | 0.90753 | 0.90867 | 0.92571 | 0.90752 | 0.90865 | 0.92569 | 0.9075 | 0.90863 | 0.92565 | 0.90746 | 0.9086
MK | 30053798 | 231 | Carmila | 231_Carmila 33 kV | Rating (A) | 152 | 152 | 152 | 152 | 152 | 152 | 152 | 152 | 152 | 152 | 152 | 152 | 152 | 152 | 152
MK | 30053799 | 232 | Newlands-Glenden | 232_Newlands-Glenden 66 kV
MK | 30053799 | 232 | Newlands-Glenden | 232_Newlands-Glenden 66 kV | % of Rated A | 12.0246 | 8.8767 | 6.4773 | 12.0233 | 8.8773 | 6.4774 | 12.0242 | 8.8784 | 6.4777 | 12.0256 | 8.8795 | 6.4782 | 12.0269 | 8.8806 | 6.4787
MK | 30053799 | 232 | Newlands-Glenden | 232_Newlands-Glenden 66 kV | Loading (A) | 13.9486 | 14.2027 | 10.1045 | 13.9471 | 14.2037 | 10.1048 | 13.9481 | 14.2055 | 10.1053 | 13.9496 | 14.2072 | 10.106 | 13.9512 | 14.209 | 10.1067
MK | 30053799 | 232 | Newlands-Glenden | 232_Newlands-Glenden 66 kV | Power Factor | 0.99438 | 0.99435 | 0.99005 | 0.99438 | 0.99435 | 0.99006 | 0.99438 | 0.99435 | 0.99006 | 0.99438 | 0.99435 | 0.99006 | 0.99438 | 0.99435 | 0.99007
MK | 30053799 | 232 | Newlands-Glenden | 232_Newlands-Glenden 66 kV | Rating (A) | 116 | 160 | 156 | 116 | 160 | 156 | 116 | 160 | 156 | 116 | 160 | 156 | 116 | 160 | 156
MK | 30053850 | 340 | MK3-1 Farleigh | 340_MK3-1 Farleigh 33 kV
MK | 30053850 | 340 | MK3-1 Farleigh | 340_MK3-1 Farleigh 33 kV | % of Rated A | 2.2347 | 1.6528 | 1.7199 | 2.2359 | 1.6533 | 1.7203 | 2.2362 | 1.6533 | 1.7204 | 2.2363 | 1.6529 | 1.7203 | 2.236 | 1.6524 | 1.7199
MK | 30053850 | 340 | MK3-1 Farleigh | 340_MK3-1 Farleigh 33 kV | Loading (A) | 3.8437 | 3.7188 | 3.8182 | 3.8457 | 3.7199 | 3.8191 | 3.8463 | 3.7199 | 3.8192 | 3.8464 | 3.719 | 3.819 | 3.846 | 3.7179 | 3.8182
MK | 30053850 | 340 | MK3-1 Farleigh | 340_MK3-1 Farleigh 33 kV | Power Factor | 0.018374 | 0.018588 | 0.018588 | 0.018374 | 0.018588 | 0.018588 | 0.018374 | 0.018588 | 0.018588 | 0.018374 | 0.018588 | 0.018588 | 0.018374 | 0.018588 | 0.018588
MK | 30053850 | 340 | MK3-1 Farleigh | 340_MK3-1 Farleigh 33 kV | Rating (A) | 172 | 225 | 222 | 172 | 225 | 222 | 172 | 225 | 222 | 172 | 225 | 222 | 172 | 225 | 222
MK | 30053851 | 341 | TENNYSON ST 2 | 341_Tennyson St No 2 33 kV
MK | 30053851 | 341 | TENNYSON ST 2 | 341_Tennyson St No 2 33 kV | % of Rated A | 19.5867 | 16.4262 | 16.289 | 19.3787 | 16.256 | 16.1164 | 19.2779 | 16.1731 | 16.0319 | 19.2813 | 16.177 | 16.033 | 19.1839 | 16.0947 | 15.9505
MK | 30053851 | 341 | TENNYSON ST 2 | 341_Tennyson St No 2 33 kV | Loading (A) | 68.5533 | 57.4916 | 57.0113 | 67.8254 | 56.8959 | 56.4075 | 67.4728 | 56.606 | 56.1118 | 67.4845 | 56.6195 | 56.1155 | 67.1435 | 56.3314 | 55.8268
MK | 30053851 | 341 | TENNYSON ST 2 | 341_Tennyson St No 2 33 kV | Power Factor | 0.92416 | 0.92576 | 0.92583 | 0.92428 | 0.92586 | 0.92594 | 0.92434 | 0.92591 | 0.92599 | 0.92434 | 0.9259 | 0.92599 | 0.92439 | 0.92595 | 0.92604
MK | 30053851 | 341 | TENNYSON ST 2 | 341_Tennyson St No 2 33 kV | Rating (A) | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350
MK | 30053852 | 342 | SOUTH MACKAY | 342_South Mackay 33 kV
MK | 30053852 | 342 | SOUTH MACKAY | 342_South Mackay 33 kV | % of Rated A | 104.4012 | 56.1324 | 66.8444 | 103.0468 | 55.6997 | 66.0772 | 101.7528 | 55.1712 | 65.3008 | 101.3316 | 54.9986 | 65.0468 | 100.4798 | 54.6502 | 64.5357
MK | 30053852 | 342 | SOUTH MACKAY | 342_South Mackay 33 kV | Loading (A) | 352.8761 | 275.0456 | 328.2059 | 348.2983 | 272.9254 | 324.4366 | 343.9243 | 270.3357 | 320.6244 | 342.5008 | 269.4901 | 319.3775 | 339.6219 | 267.7827 | 316.8679
MK | 30053852 | 342 | SOUTH MACKAY | 342_South Mackay 33 kV | Power Factor | 0.94859 | 0.85707 | 0.92761 | 0.94172 | 0.84676 | 0.91943 | 0.93848 | 0.84147 | 0.91557 | 0.93742 | 0.83983 | 0.9143 | 0.93518 | 0.83619 | 0.91164
MK | 30053852 | 342 | SOUTH MACKAY | 342_South Mackay 33 kV | Rating (A) | 338 | 490 | 491 | 338 | 490 | 491 | 338 | 490 | 491 | 338 | 490 | 491 | 338 | 490 | 491
MK | 30053853 | 343 | PLEYSTOWE | 343_Pleystowe 33 kV
MK | 30053853 | 343 | PLEYSTOWE | 343_Pleystowe 33 kV | % of Rated A | 42.4013 | 55.5181 | 43.7461 | 42.3779 | 55.5052 | 43.733 | 42.3727 | 55.5068 | 43.7331 | 42.3789 | 55.5216 | 43.7386 | 42.7024 | 56.0034 | 44.1309
MK | 30053853 | 343 | PLEYSTOWE | 343_Pleystowe 33 kV | Loading (A) | 93.2829 | 122.1397 | 96.2414 | 93.2315 | 122.1115 | 96.2127 | 93.2199 | 122.115 | 96.2129 | 93.2335 | 122.1475 | 96.2249 | 93.9453 | 123.2075 | 97.0881
MK | 30053853 | 343 | PLEYSTOWE | 343_Pleystowe 33 kV | Power Factor | 0.99626 | 0.99097 | 0.9954 | 0.99627 | 0.99097 | 0.9954 | 0.99627 | 0.99097 | 0.9954 | 0.99627 | 0.99096 | 0.9954 | 0.99614 | 0.99077 | 0.99524
MK | 30053853 | 343 | PLEYSTOWE | 343_Pleystowe 33 kV | Rating (A) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
MK | 30053854 | 344 | WEST MACKAY 2 | 344_West Mackay 2 33 kV
MK | 30053854 | 344 | WEST MACKAY 2 | 344_West Mackay 2 33 kV | % of Rated A | 28.8499 | 27.1822 | 23.2874 | 28.8347 | 27.1744 | 23.2752 | 28.8318 | 27.1742 | 23.2716 | 28.8369 | 27.1809 | 23.2732 | 28.8391 | 27.1816 | 23.2724
MK | 30053854 | 344 | WEST MACKAY 2 | 344_West Mackay 2 33 kV | Loading (A) | 180.3118 | 169.8891 | 145.5462 | 180.2166 | 169.8398 | 145.4699 | 180.1988 | 169.8389 | 145.4475 | 180.2307 | 169.8805 | 145.4573 | 180.2444 | 169.8852 | 145.4528
MK | 30053854 | 344 | WEST MACKAY 2 | 344_West Mackay 2 33 kV | Power Factor | 0.95468 | 0.95585 | 0.95838 | 0.9547 | 0.95586 | 0.9584 | 0.95471 | 0.95586 | 0.9584 | 0.9547 | 0.95586 | 0.9584 | 0.9547 | 0.95585 | 0.9584
MK | 30053854 | 344 | WEST MACKAY 2 | 344_West Mackay 2 33 kV | Rating (A) | 625 | 625 | 625 | 625 | 625 | 625 | 625 | 625 | 625 | 625 | 625 | 625 | 625 | 625 | 625
MK | 30053855 | 3053 | MT BASSETT | 3053_Mt Bassett 33 kV
MK | 30053855 | 3053 | MT BASSETT | 3053_Mt Bassett 33 kV | % of Rated A | 37.1657 | 25.7572 | 20.3543 | 37.0986 | 25.7267 | 20.3168 | 37.3355 | 25.9034 | 20.4416 | 37.6053 | 26.099 | 20.5844 | 37.5955 | 26.097 | 20.5776
MK | 30053855 | 3053 | MT BASSETT | 3053_Mt Bassett 33 kV | Loading (A) | 87.281 | 83.6536 | 65.6892 | 87.1234 | 83.5545 | 65.5682 | 87.6799 | 84.1288 | 65.9712 | 88.3139 | 84.7643 | 66.4322 | 88.2908 | 84.758 | 66.4102
MK | 30053855 | 3053 | MT BASSETT | 3053_Mt Bassett 33 kV | Power Factor | 0.93618 | 0.93875 | 0.94397 | 0.93631 | 0.93883 | 0.9441 | 0.93619 | 0.93867 | 0.944 | 0.936 | 0.93846 | 0.94384 | 0.93604 | 0.93847 | 0.94388
MK | 30053855 | 3053 | MT BASSETT | 3053_Mt Bassett 33 kV | Rating (A) | 235 | 325 | 323 | 235 | 325 | 323 | 235 | 325 | 323 | 235 | 325 | 323 | 235 | 325 | 323
MK | 30053856 | 346 | RITCHIES RD | 346_Ritchies Rd 33 kV
MK | 30053856 | 346 | RITCHIES RD | 346_Ritchies Rd 33 kV | % of Rated A | 31.6797 | 30.0235 | 23.7334 | 31.6623 | 30.0166 | 23.7263 | 31.6584 | 30.0174 | 23.7264 | 31.663 | 30.0254 | 23.7293 | 31.905 | 30.286 | 23.9424
MK | 30053856 | 346 | RITCHIES RD | 346_Ritchies Rd 33 kV | Loading (A) | 69.6951 | 91.2711 | 71.9119 | 69.6567 | 91.25 | 71.8904 | 69.6481 | 91.2527 | 71.8906 | 69.6583 | 91.2769 | 71.8996 | 70.1907 | 92.0692 | 72.5451
MK | 30053856 | 346 | RITCHIES RD | 346_Ritchies Rd 33 kV | Power Factor | 0.99528 | 0.98992 | 0.99435 | 0.99529 | 0.98992 | 0.99435 | 0.99529 | 0.98992 | 0.99435 | 0.99528 | 0.98992 | 0.99435 | 0.99515 | 0.98972 | 0.99419
MK | 30053856 | 346 | RITCHIES RD | 346_Ritchies Rd 33 kV | Rating (A) | 220 | 304 | 303 | 220 | 304 | 303 | 220 | 304 | 303 | 220 | 304 | 303 | 220 | 304 | 303
MK | 30053857 | 347 | MT BASSETT | 347_Mt Bassett 33 kV
MK | 30053857 | 347 | MT BASSETT | 347_Mt Bassett 33 kV | % of Rated A | 51.8665 | 51.7932 | 38.9101 | 51.8733 | 51.8128 | 38.9205 | 52.3413 | 52.2794 | 39.2647 | 52.8052 | 52.7436 | 39.5986 | 52.8147 | 52.7571 | 39.609
MK | 30053857 | 347 | MT BASSETT | 347_Mt Bassett 33 kV | Loading (A) | 132.2595 | 132.0725 | 99.2208 | 132.277 | 132.1225 | 99.2473 | 133.4703 | 133.3125 | 100.1249 | 134.6532 | 134.4962 | 100.9764 | 134.6775 | 134.5305 | 101.0028
MK | 30053857 | 347 | MT BASSETT | 347_Mt Bassett 33 kV | Power Factor | 0.95215 | 0.95092 | 0.95295 | 0.9521 | 0.95088 | 0.95291 | 0.95193 | 0.95072 | 0.95283 | 0.95178 | 0.95059 | 0.95285 | 0.95176 | 0.95057 | 0.95283
MK | 30053857 | 347 | MT BASSETT | 347_Mt Bassett 33 kV | Rating (A) | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255
MK | 30053858 | 348 | Farleigh | 348_Farleigh 33 kV
MK | 30053858 | 348 | Farleigh | 348_Farleigh 33 kV | % of Rated A | 26.546 | 19.4542 | 14.3044 | 26.5319 | 19.4492 | 14.2986 | 26.5277 | 19.4483 | 14.2963 | 26.5294 | 19.4513 | 14.2957 | 26.5346 | 19.4577 | 14.2962
MK | 30053858 | 348 | Farleigh | 348_Farleigh 33 kV | Loading (A) | 51.4993 | 50.5809 | 36.9053 | 51.4719 | 50.5679 | 36.8905 | 51.4636 | 50.5657 | 36.8845 | 51.467 | 50.5735 | 36.883 | 51.4771 | 50.5901 | 36.8843
MK | 30053858 | 348 | Farleigh | 348_Farleigh 33 kV | Power Factor | 0.96492 | 0.96143 | 0.87607 | 0.96489 | 0.96141 | 0.87601 | 0.96487 | 0.9614 | 0.87598 | 0.96487 | 0.96141 | 0.87595 | 0.96489 | 0.96143 | 0.87595
MK | 30053858 | 348 | Farleigh | 348_Farleigh 33 kV | Rating (A) | 194 | 260 | 258 | 194 | 260 | 258 | 194 | 260 | 258 | 194 | 260 | 258 | 194 | 260 | 258
MK | 30053859 | 349 | Pioneer Valley-Pinnacle(Marian) | 349_Pioneer Valley - Pinnacle 66 kV
MK | 30053859 | 349 | Pioneer Valley-Pinnacle(Marian) | 349_Pioneer Valley - Pinnacle 66 kV | % of Rated A | 45.5508 | 44.9656 | 41.922 | 45.8638 | 45.267 | 42.1856 | 46.1672 | 45.5736 | 42.4588 | 46.1725 | 45.5984 | 42.4703 | 46.4675 | 45.908 | 42.7667
MK | 30053859 | 349 | Pioneer Valley-Pinnacle(Marian) | 349_Pioneer Valley - Pinnacle 66 kV | Loading (A) | 100.2109 | 136.6943 | 127.0226 | 100.8996 | 137.6105 | 127.8214 | 101.5671 | 138.5426 | 128.6491 | 101.5788 | 138.6182 | 128.6841 | 102.2277 | 139.5593 | 129.582
MK | 30053859 | 349 | Pioneer Valley-Pinnacle(Marian) | 349_Pioneer Valley - Pinnacle 66 kV | Power Factor | 0.99073 | 0.98292 | 0.98447 | 0.99028 | 0.98235 | 0.98394 | 0.99022 | 0.98228 | 0.98389 | 0.99022 | 0.98225 | 0.98387 | 0.98982 | 0.9817 | 0.98332
MK | 30053859 | 349 | Pioneer Valley-Pinnacle(Marian) | 349_Pioneer Valley - Pinnacle 66 kV | Rating (A) | 220 | 304 | 303 | 220 | 304 | 303 | 220 | 304 | 303 | 220 | 304 | 303 | 220 | 304 | 303
MK | 30053869 | 360 | Pinnacle-Crediton/Eungella Dam | 360_Pinnacle-Crediton/Eungella Dam 66 kV
MK | 30053869 | 360 | Pinnacle-Crediton/Eungella Dam | 360_Pinnacle-Crediton/Eungella Dam 66 kV | % of Rated A | 5.4569 | 4.179 | 4.4243 | 5.4567 | 4.1769 | 4.4235 | 5.4565 | 4.1755 | 4.4233 | 5.4556 | 4.1734 | 4.4229 | 5.4539 | 4.1963 | 4.4211
MK | 30053869 | 360 | Pinnacle-Crediton/Eungella Dam | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Loading (A) | 5.0203 | 4.973 | 4.9994 | 5.0201 | 4.9705 | 4.9986 | 5.02 | 4.9688 | 4.9984 | 5.0192 | 4.9664 | 4.9978 | 5.0175 | 4.9936 | 4.9958
MK | 30053869 | 360 | Pinnacle-Crediton/Eungella Dam | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Power Factor | 0.001817 | 0.001817 | 0.001817 | 0.001817 | 0.001817 | 0.001817 | 0.0018171 | 0.001817 | 0.001817 | 0.0018171 | 0.001817 | 0.001817 | 0.0018168 | 0.001817 | 0.001817
MK | 30053869 | 360 | Pinnacle-Crediton/Eungella Dam | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Rating (A) | 92 | 119 | 113 | 92 | 119 | 113 | 92 | 119 | 113 | 92 | 119 | 113 | 92 | 119 | 113
MK | 30053873 | 364 | WEST MACKAY 1 | 364_West Mackay No 1 33 kV
MK | 30053873 | 364 | WEST MACKAY 1 | 364_West Mackay No 1 33 kV | % of Rated A | 62.2014 | 41.3509 | 35.5102 | 62.1685 | 41.3389 | 35.4916 | 62.1623 | 41.3387 | 35.4861 | 62.1733 | 41.3488 | 35.4885 | 62.1781 | 41.35 | 35.4874
MK | 30053873 | 364 | WEST MACKAY 1 | 364_West Mackay No 1 33 kV | Loading (A) | 180.3835 | 169.9519 | 145.5914 | 180.2881 | 169.9026 | 145.515 | 180.2703 | 169.9017 | 145.4926 | 180.3022 | 169.9433 | 145.5024 | 180.316 | 169.948 | 145.4979
MK | 30053873 | 364 | WEST MACKAY 1 | 364_West Mackay No 1 33 kV | Power Factor | 0.95465 | 0.95582 | 0.95836 | 0.95467 | 0.95583 | 0.95838 | 0.95467 | 0.95584 | 0.95838 | 0.95467 | 0.95583 | 0.95838 | 0.95466 | 0.95583 | 0.95838
MK | 30053873 | 364 | WEST MACKAY 1 | 364_West Mackay No 1 33 kV | Rating (A) | 290 | 411 | 410 | 290 | 411 | 410 | 290 | 411 | 410 | 290 | 411 | 410 | 290 | 411 | 410
MK | 30053874 | 365 | TENNYSTON ST 1 | 365_Tennyson St No 1 33 kV
MK | 30053874 | 365 | TENNYSTON ST 1 | 365_Tennyson St No 1 33 kV | % of Rated A | 9.506 | 8.3476 | 7.6554 | 9.439 | 8.2917 | 7.6011 | 9.4317 | 8.286 | 7.5928 | 9.4578 | 8.3092 | 7.6113 | 9.4438 | 8.2978 | 7.5996
MK | 30053874 | 365 | TENNYSTON ST 1 | 365_Tennyson St No 1 33 kV | Loading (A) | 63.2151 | 55.5114 | 50.9083 | 62.7692 | 55.1396 | 50.5472 | 62.7211 | 55.1022 | 50.4921 | 62.8945 | 55.2565 | 50.6154 | 62.8013 | 55.1802 | 50.5374
MK | 30053874 | 365 | TENNYSTON ST 1 | 365_Tennyson St No 1 33 kV | Power Factor | 0.85843 | 0.87758 | 0.88782 | 0.85945 | 0.87851 | 0.88887 | 0.85955 | 0.87858 | 0.88904 | 0.85914 | 0.87815 | 0.88869 | 0.85943 | 0.87842 | 0.88899
MK | 30053874 | 365 | TENNYSTON ST 1 | 365_Tennyson St No 1 33 kV | Rating (A) | 665 | 665 | 665 | 665 | 665 | 665 | 665 | 665 | 665 | 665 | 665 | 665 | 665 | 665 | 665
MK | 30053876 | 367 | Pioneer Valley-Greenmount | 367_Pioneer Valley - Greenmount 66 kV
MK | 30053876 | 367 | Pioneer Valley-Greenmount | 367_Pioneer Valley - Greenmount 66 kV | % of Rated A | 0.063942 | 0.046141 | 0.046332 | 0.063949 | 0.046129 | 0.04633 | 0.063949 | 0.046227 | 0.046327 | 0.063939 | 0.046209 | 0.046321 | 0.06393 | 0.046216 | 0.046314
MK | 30053876 | 367 | Pioneer Valley-Greenmount | 367_Pioneer Valley - Greenmount 66 kV | Loading (A) | 0.16113 | 0.16103 | 0.16123 | 0.16115 | 0.16099 | 0.16123 | 0.16115 | 0.16133 | 0.16122 | 0.16113 | 0.16127 | 0.1612 | 0.1611 | 0.16129 | 0.16117
MK | 30053876 | 367 | Pioneer Valley-Greenmount | 367_Pioneer Valley - Greenmount 66 kV | Power Factor | 4.0685e-06 | 4.0735e-06 | 4.0754e-06 | 4.07e-06 | 4.073e-06 | 4.0731e-06 | 4.0709e-06 | 4.0701e-06 | 4.0696e-06 | 4.0701e-06 | 4.0747e-06 | 4.0707e-06 | 4.076e-06 | 4.0744e-06 | 4.0704e-06
MK | 30053876 | 367 | Pioneer Valley-Greenmount | 367_Pioneer Valley - Greenmount 66 kV | Rating (A) | 252 | 349 | 348 | 252 | 349 | 348 | 252 | 349 | 348 | 252 | 349 | 348 | 252 | 349 | 348
MK | 30053881 | 372 | Pioneer Valley-MCKINLEY CREEK | 372_Pioneer Valley-McKinley Creek 33 kV
MK | 30053881 | 372 | Pioneer Valley-MCKINLEY CREEK | 372_Pioneer Valley-McKinley Creek 33 kV | % of Rated A | 12.9932 | 11.9871 | 7.9654 | 12.995 | 11.9908 | 7.9647 | 12.9978 | 11.994 | 7.966 | 13.336 | 12.3121 | 8.1741 | 13.3418 | 12.3152 | 8.1766
MK | 30053881 | 372 | Pioneer Valley-MCKINLEY CREEK | 372_Pioneer Valley-McKinley Creek 33 kV | Loading (A) | 25.3368 | 33.3243 | 21.5065 | 25.3403 | 33.3345 | 21.5047 | 25.3457 | 33.3434 | 21.5081 | 26.0052 | 34.2278 | 22.0699 | 26.0166 | 34.2362 | 22.0768
MK | 30053881 | 372 | Pioneer Valley-MCKINLEY CREEK | 372_Pioneer Valley-McKinley Creek 33 kV | Power Factor | 0.97553 | 0.97405 | 0.97625 | 0.97553 | 0.97404 | 0.97625 | 0.97553 | 0.97404 | 0.97625 | 0.9754 | 0.97386 | 0.97615 | 0.9754 | 0.97386 | 0.97614
MK | 30053881 | 372 | Pioneer Valley-MCKINLEY CREEK | 372_Pioneer Valley-McKinley Creek 33 kV | Rating (A) | 195 | 278 | 270 | 195 | 278 | 270 | 195 | 278 | 270 | 195 | 278 | 270 | 195 | 278 | 270
MK | 80001012 | PROS-KECR-1 | Proserpine No.1 66kV Feeder | PROS-KECR-1_Proserpine No 1 66 kV
MK | 80001012 | PROS-KECR-1 | Proserpine No.1 66kV Feeder | PROS-KECR-1_Proserpine No 1 66 kV | % of Rated A | 26.1162 | 24.0805 | 20.9529 | 26.1266 | 24.092 | 20.959 | 26.4133 | 24.3622 | 21.1769 | 26.5603 | 24.4992 | 21.2909 | 26.8435 | 24.7629 | 21.5146
MK | 80001012 | PROS-KECR-1 | Proserpine No.1 66kV Feeder | PROS-KECR-1_Proserpine No 1 66 kV | Loading (A) | 46.2256 | 56.83 | 47.3535 | 46.244 | 56.8571 | 47.3673 | 46.7516 | 57.4947 | 47.8599 | 47.0118 | 57.8181 | 48.1174 | 47.513 | 58.4404 | 48.623
MK | 80001012 | PROS-KECR-1 | Proserpine No.1 66kV Feeder | PROS-KECR-1_Proserpine No 1 66 kV | Power Factor | 0.9395 | 0.93624 | 0.93887 | 0.93949 | 0.93622 | 0.93886 | 0.93931 | 0.93599 | 0.93907 | 0.93921 | 0.93587 | 0.93898 | 0.93903 | 0.93565 | 0.93881
MK | 80001012 | PROS-KECR-1 | Proserpine No.1 66kV Feeder | PROS-KECR-1_Proserpine No 1 66 kV | Rating (A) | 177 | 236 | 226 | 177 | 236 | 226 | 177 | 236 | 226 | 177 | 236 | 226 | 177 | 236 | 226
MK | 80075847 | PROS-KECR-2 | Proserpine No.2 66kV Feeder | PROS-KECR-2_Proserpine No 2 66 kV
MK | 80075847 | PROS-KECR-2 | Proserpine No.2 66kV Feeder | PROS-KECR-2_Proserpine No 2 66 kV | % of Rated A | 52.3682 | 48.3134 | 41.9985 | 52.3892 | 48.3366 | 42.0108 | 52.9658 | 48.8806 | 42.4672 | 53.2615 | 49.1565 | 42.6964 | 53.831 | 49.6875 | 43.1463
MK | 80075847 | PROS-KECR-2 | Proserpine No.2 66kV Feeder | PROS-KECR-2_Proserpine No 2 66 kV | Loading (A) | 92.6895 | 114.0175 | 94.9145 | 92.7266 | 114.0722 | 94.9423 | 93.7473 | 115.3561 | 95.9737 | 94.2706 | 116.0072 | 96.4917 | 95.2786 | 117.2602 | 97.5084
MK | 80075847 | PROS-KECR-2 | Proserpine No.2 66kV Feeder | PROS-KECR-2_Proserpine No 2 66 kV | Power Factor | 0.93971 | 0.93648 | 0.93947 | 0.9397 | 0.93646 | 0.93946 | 0.93952 | 0.93623 | 0.93928 | 0.93942 | 0.93611 | 0.93919 | 0.93925 | 0.93589 | 0.93902
MK | 80075847 | PROS-KECR-2 | Proserpine No.2 66kV Feeder | PROS-KECR-2_Proserpine No 2 66 kV | Rating (A) | 177 | 236 | 226 | 177 | 236 | 226 | 177 | 236 | 226 | 177 | 236 | 226 | 177 | 236 | 226
MK | 82846747 | 351 | ALLIGATOR CREEK 33kV FDR | 351_Alligator Creek 33 kV
MK | 82846747 | 351 | ALLIGATOR CREEK 33kV FDR | 351_Alligator Creek 33 kV | % of Rated A | 0.23827 | 0.17297 | 0.17536 | 0.23848 | 0.17307 | 0.17545 | 0.23853 | 0.17309 | 0.17547 | 0.23853 | 0.17305 | 0.17545 | 0.23852 | 0.17303 | 0.17545
MK | 82846747 | 351 | ALLIGATOR CREEK 33kV FDR | 351_Alligator Creek 33 kV | Loading (A) | 0.6076 | 0.61059 | 0.61728 | 0.60812 | 0.61094 | 0.61757 | 0.60826 | 0.611 | 0.61764 | 0.60824 | 0.61088 | 0.61759 | 0.60824 | 0.61081 | 0.61757
MK | 82846747 | 351 | ALLIGATOR CREEK 33kV FDR | 351_Alligator Creek 33 kV | Power Factor | 0.0061737 | 0.0061751 | 0.0061808 | 0.0061737 | 0.006175 | 0.0061807 | 0.0061738 | 0.006175 | 0.0061806 | 0.0061747 | 0.006175 | 0.0061806 | 0.0061736 | 0.0061751 | 0.0061804
MK | 82846747 | 351 | ALLIGATOR CREEK 33kV FDR | 351_Alligator Creek 33 kV | Rating (A) | 255 | 353 | 352 | 255 | 353 | 352 | 255 | 353 | 352 | 255 | 353 | 352 | 255 | 353 | 352
MK | 82913608 | PV 6/5 | PV 6/5 GLENELLA NO 1 | PV 6/5_Glenella No 1 66 kV
MK | 82913608 | PV 6/5 | PV 6/5 GLENELLA NO 1 | PV 6/5_Glenella No 1 66 kV | % of Rated A | 57.1489 | 50.8936 | 50.9545 | 57.1737 | 50.922 | 50.9516 | 57.2022 | 50.9464 | 50.9555 | 57.2189 | 50.9912 | 50.9697 | 57.2692 | 50.9322 | 50.9839
MK | 82913608 | PV 6/5 | PV 6/5 GLENELLA NO 1 | PV 6/5_Glenella No 1 66 kV | Loading (A) | 473.7584 | 473.305 | 464.6997 | 473.9647 | 473.569 | 464.6727 | 474.2005 | 473.7955 | 464.7083 | 474.3395 | 474.2129 | 464.8381 | 474.7558 | 473.6638 | 464.9675
MK | 82913608 | PV 6/5 | PV 6/5 GLENELLA NO 1 | PV 6/5_Glenella No 1 66 kV | Power Factor | 0.69694 | 0.69523 | 0.69377 | 0.69697 | 0.69526 | 0.69377 | 0.69703 | 0.69532 | 0.6938 | 0.69711 | 0.69541 | 0.69387 | 0.69719 | 0.69942 | 0.69391
MK | 82913608 | PV 6/5 | PV 6/5 GLENELLA NO 1 | PV 6/5_Glenella No 1 66 kV | Rating (A) | 829 | 930 | 912 | 829 | 930 | 912 | 829 | 930 | 912 | 829 | 930 | 912 | 829 | 930 | 912
MK | 82913611 | PV 6/4 | PV 6/4 GLENELLA NO 2 | PV 6/4_Glenella No 2 66 kV
MK | 82913611 | PV 6/4 | PV 6/4 GLENELLA NO 2 | PV 6/4_Glenella No 2 66 kV | % of Rated A | 23.7123 | 23.6247 | 16.5102 | 23.9428 | 23.8937 | 16.527 | 24.1281 | 24.0877 | 16.6169 | 24.248 | 24.3691 | 16.7353 | 24.5427 | 24.5715 | 16.8743
MK | 82913611 | PV 6/4 | PV 6/4 GLENELLA NO 2 | PV 6/4_Glenella No 2 66 kV | Loading (A) | 191.8258 | 214.5056 | 147.0985 | 193.6906 | 216.9487 | 147.2478 | 195.19 | 218.7103 | 148.0485 | 196.1595 | 221.2655 | 149.1042 | 198.5437 | 223.1027 | 150.3428
MK | 82913611 | PV 6/4 | PV 6/4 GLENELLA NO 2 | PV 6/4_Glenella No 2 66 kV | Power Factor | 0.55028 | 0.61599 | 0.30432 | 0.55563 | 0.6202 | 0.31418 | 0.55979 | 0.62388 | 0.32093 | 0.56684 | 0.62773 | 0.32912 | 0.57279 | 0.63461 | 0.33845
MK | 82913611 | PV 6/4 | PV 6/4 GLENELLA NO 2 | PV 6/4_Glenella No 2 66 kV | Rating (A) | 809 | 908 | 891 | 809 | 908 | 891 | 809 | 908 | 891 | 809 | 908 | 891 | 809 | 908 | 891
MK | 83058752 | 395 | TEST-ALST | 395_Tennyson Street-Alfred Street 33 kV
MK | 83058752 | 395 | TEST-ALST | 395_Tennyson Street-Alfred Street 33 kV | % of Rated A | 30.9087 | 26.534 | 23.9366 | 30.7502 | 26.4332 | 23.8088 | 30.8271 | 26.5355 | 23.8584 | 30.9825 | 26.6919 | 23.9709 | 30.8944 | 26.6319 | 23.8967
MK | 83058752 | 395 | TEST-ALST | 395_Tennyson Street-Alfred Street 33 kV | Loading (A) | 207.7065 | 178.3084 | 160.8541 | 206.6415 | 177.631 | 159.9953 | 207.1579 | 178.3184 | 160.3285 | 208.2027 | 179.3694 | 161.0841 | 207.6106 | 178.9662 | 160.5859
MK | 83058752 | 395 | TEST-ALST | 395_Tennyson Street-Alfred Street 33 kV | Power Factor | 0.95457 | 0.95594 | 0.95317 | 0.9546 | 0.95591 | 0.95315 | 0.95462 | 0.9559 | 0.95321 | 0.95463 | 0.95591 | 0.95326 | 0.95471 | 0.95596 | 0.95333
MK | 83058752 | 395 | TEST-ALST | 395_Tennyson Street-Alfred Street 33 kV | Rating (A) | 672 | 672 | 672 | 672 | 672 | 672 | 672 | 672 | 672 | 672 | 672 | 672 | 672 | 672 | 672
MK | 84186116 | 423 | NORTH MACKAY NO 2 | 423_North Mackay No 2 33 kV
MK | 84186116 | 423 | NORTH MACKAY NO 2 | 423_North Mackay No 2 33 kV | % of Rated A | 33.0644 | 37.5385 | 30.554 | 33.2962 | 37.8203 | 30.7599 | 33.5289 | 38.0977 | 30.9659 | 33.7555 | 38.3878 | 30.8702 | 33.9988 | 38.6639 | 31.0773
MK | 84186116 | 423 | NORTH MACKAY NO 2 | 423_North Mackay No 2 33 kV | Loading (A) | 202.3544 | 229.7359 | 186.9907 | 203.7725 | 231.4602 | 188.2506 | 205.1966 | 233.1577 | 189.5113 | 206.5838 | 234.9333 | 188.9258 | 208.073 | 236.6232 | 190.1933
MK | 84186116 | 423 | NORTH MACKAY NO 2 | 423_North Mackay No 2 33 kV | Power Factor | 0.95464 | 0.97018 | 0.94504 | 0.95562 | 0.97097 | 0.94612 | 0.95659 | 0.97172 | 0.94718 | 0.95748 | 0.97251 | 0.94471 | 0.95849 | 0.97321 | 0.94581
MK | 84186116 | 423 | NORTH MACKAY NO 2 | 423_North Mackay No 2 33 kV | Rating (A) | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612
MK | 84186121 | 422 | NORTH MACKAY NO 1 | 422_North Mackay No 1 33 kV
MK | 84186121 | 422 | NORTH MACKAY NO 1 | 422_North Mackay No 1 33 kV | % of Rated A | 80.7378 | 84.8462 | 56.6685 | 82.104 | 86.3344 | 56.5915 | 83.0351 | 87.3195 | 57.1437 | 83.133 | 88.8135 | 58.0672 | 84.528 | 90.3629 | 58.9996
MK | 84186121 | 422 | NORTH MACKAY NO 1 | 422_North Mackay No 1 33 kV | Loading (A) | 296.3075 | 347.869 | 383.646 | 301.3212 | 353.9709 | 383.1247 | 304.7384 | 358.0098 | 228.5746 | 305.0976 | 364.1351 | 232.2684 | 310.2173 | 370.4874 | 235.9981
MK | 84186121 | 422 | NORTH MACKAY NO 1 | 422_North Mackay No 1 33 kV | Power Factor | 0.98909 | 0.9875 | 0.99749 | 0.98893 | 0.98729 | 0.99728 | 0.98882 | 0.98728 | 0.99079 | 0.9887 | 0.98721 | 0.99068 | 0.98853 | 0.98699 | 0.99057
MK | 84186121 | 422 | NORTH MACKAY NO 1 | 422_North Mackay No 1 33 kV | Rating (A) | 367 | 410 | 677 | 367 | 410 | 677 | 367 | 410 | 400 | 367 | 410 | 400 | 367 | 410 | 400
MK | 84211409 | 426 | MT ROOPER | 426_Mt Rooper 66 kV
MK | 84211409 | 426 | MT ROOPER | 426_Mt Rooper 66 kV | % of Rated A | 48.6153 | 41.9829 | 35.6125 | 48.6465 | 42.0125 | 35.6255 | 49.0682 | 42.3792 | 35.9058 | 49.0949 | 42.4022 | 35.9151 | 48.9607 | 42.44 | 35.9317
MK | 84211409 | 426 | MT ROOPER | 426_Mt Rooper 66 kV | Loading (A) | 121.0512 | 117.5521 | 99.715 | 121.129 | 117.6351 | 99.7514 | 122.1789 | 118.6618 | 100.5362 | 122.2453 | 118.7262 | 100.5624 | 121.9112 | 118.8319 | 100.6087
MK | 84211409 | 426 | MT ROOPER | 426_Mt Rooper 66 kV | Power Factor | 0.98091 | 0.97565 | 0.97756 | 0.98088 | 0.97563 | 0.97755 | 0.98079 | 0.9756 | 0.97754 | 0.98077 | 0.97559 | 0.97754 | 0.98087 | 0.97556 | 0.97752
MK | 84211409 | 426 | MT ROOPER | 426_Mt Rooper 66 kV | Rating (A) | 249 | 280 | 280 | 249 | 280 | 280 | 249 | 280 | 280 | 249 | 280 | 280 | 249 | 280 | 280
MK | 84216180 | 387 | ALFRED ST 1 | 387_Mackay-Alfred Street 1 33 kV
MK | 84216180 | 387 | ALFRED ST 1 | 387_Mackay-Alfred Street 1 33 kV | % of Rated A | 69.4251 | 62.3808 | 57.4313 | 68.9064 | 61.9405 | 57.0161 | 68.7671 | 61.8213 | 56.8928 | 68.8855 | 61.9278 | 56.9748 | 68.8245 | 61.8785 | 56.9242
MK | 84216180 | 387 | ALFRED ST 1 | 387_Mackay-Alfred Street 1 33 kV | Loading (A) | 299.2222 | 268.8614 | 247.5289 | 296.9867 | 266.9634 | 245.7393 | 296.3863 | 266.4499 | 245.208 | 296.8967 | 266.9089 | 245.5616 | 296.6336 | 266.6965 | 245.3431
MK | 84216180 | 387 | ALFRED ST 1 | 387_Mackay-Alfred Street 1 33 kV | Power Factor | 0.99504 | 0.98921 | 0.98348 | 0.99472 | 0.98874 | 0.98281 | 0.99463 | 0.98862 | 0.98262 | 0.99471 | 0.98875 | 0.98276 | 0.99466 | 0.98868 | 0.98265
MK | 84216180 | 387 | ALFRED ST 1 | 387_Mackay-Alfred Street 1 33 kV | Rating (A) | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431
MK | 84293483 | 6328 | BROADLEA-MOORVALE | 6328_Broadlea - Moorvale 66 kV
MK | 84293483 | 6328 | BROADLEA-MOORVALE | 6328_Broadlea - Moorvale 66 kV | % of Rated A | 12.138 | 13.2682 | 11.3487 | 12.1381 | 13.2686 | 11.3488 | 12.1387 | 13.2695 | 11.3493 | 12.1398 | 13.2704 | 11.35 | 12.1402 | 13.2709 | 11.3502
MK | 84293483 | 6328 | BROADLEA-MOORVALE | 6328_Broadlea - Moorvale 66 kV | Loading (A) | 46.8527 | 51.6135 | 38.3587 | 46.8532 | 51.6148 | 38.359 | 46.8555 | 51.6184 | 38.3608 | 46.8598 | 51.6218 | 38.3629 | 46.8612 | 51.6238 | 38.3638
MK | 84293483 | 6328 | BROADLEA-MOORVALE | 6328_Broadlea - Moorvale 66 kV | Power Factor | 0.96835 | 0.96725 | 0.97016 | 0.96834 | 0.96725 | 0.97016 | 0.96834 | 0.96725 | 0.97016 | 0.96834 | 0.96725 | 0.97016 | 0.96834 | 0.96725 | 0.97016
MK | 84293483 | 6328 | BROADLEA-MOORVALE | 6328_Broadlea - Moorvale 66 kV | Rating (A) | 386 | 389 | 338 | 386 | 389 | 338 | 386 | 389 | 338 | 386 | 389 | 338 | 386 | 389 | 338
MK | 84293489 | 6330 | BROADLEA-MILLENNIUM | 6330 Broadlea - Millennium 66 kV
MK | 84293489 | 6330 | BROADLEA-MILLENNIUM | 6330 Broadlea - Millennium 66 kV | % of Rated A | 25.4872 | 20.3783 | 26.0043 | 25.4874 | 20.3788 | 26.0045 | 25.5906 | 20.4924 | 26.1168 | 25.7103 | 20.5759 | 26.2354 | 25.711 | 20.5766 | 26.236
MK | 84293489 | 6330 | BROADLEA-MILLENNIUM | 6330 Broadlea - Millennium 66 kV | Loading (A) | 179.6848 | 149.7808 | 169.5479 | 179.6865 | 149.7845 | 169.5492 | 180.4135 | 150.6193 | 170.2812 | 181.2574 | 151.2326 | 171.0546 | 181.2627 | 151.2382 | 171.0588
MK | 84293489 | 6330 | BROADLEA-MILLENNIUM | 6330 Broadlea - Millennium 66 kV | Power Factor | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
MK | 84293489 | 6330 | BROADLEA-MILLENNIUM | 6330 Broadlea - Millennium 66 kV | Rating (A) | 705 | 735 | 652 | 705 | 735 | 652 | 705 | 735 | 652 | 705 | 735 | 652 | 705 | 735 | 652
MK | 84544397 | 7366 | 132KV MORA - BROD | 7366_Moranbah - Broadlea 132 kV
MK | 84544397 | 7366 | 132KV MORA - BROD | 7366_Moranbah - Broadlea 132 kV | % of Rated A | 20.9187 | 18.0528 | 22.2914 | 20.9189 | 18.0533 | 22.2916 | 20.9715 | 18.1116 | 22.3481 | 21.0327 | 18.1529 | 22.4079 | 21.0333 | 18.1536 | 22.4084
MK | 84544397 | 7366 | 132KV MORA - BROD | 7366_Moranbah - Broadlea 132 kV | Loading (A) | 147.4758 | 132.6872 | 145.3393 | 147.4772 | 132.6904 | 145.3405 | 147.8481 | 133.119 | 145.7092 | 148.2793 | 133.4227 | 146.0985 | 148.2837 | 133.4281 | 146.1021
MK | 84544397 | 7366 | 132KV MORA - BROD | 7366_Moranbah - Broadlea 132 kV | Power Factor | 0.99911 | 0.99908 | 0.99955 | 0.99911 | 0.99908 | 0.99955 | 0.9991 | 0.99908 | 0.99955 | 0.9991 | 0.99907 | 0.99954 | 0.9991 | 0.99907 | 0.99954
MK | 84544397 | 7366 | 132KV MORA - BROD | 7366_Moranbah - Broadlea 132 kV | Rating (A) | 705 | 735 | 652 | 705 | 735 | 652 | 705 | 735 | 652 | 705 | 735 | 652 | 705 | 735 | 652
MK | 84750025 | 430 | ALFRED ST 2 | 430_Mackay-Alfred Street 2 33 kV
MK | 84750025 | 430 | ALFRED ST 2 | 430_Mackay-Alfred Street 2 33 kV | % of Rated A | 50.2284 | 45.1344 | 41.5553 | 49.8533 | 44.816 | 41.2551 | 49.7526 | 44.7298 | 41.1659 | 49.8382 | 44.8068 | 41.2252 | 49.7941 | 44.7712 | 41.1886
MK | 84750025 | 430 | ALFRED ST 2 | 430_Mackay-Alfred Street 2 33 kV | Loading (A) | 290.8225 | 261.3283 | 240.6051 | 288.6507 | 259.4845 | 238.8668 | 288.0675 | 258.9857 | 238.3507 | 288.5633 | 259.4316 | 238.6942 | 288.3077 | 259.2253 | 238.482
MK | 84750025 | 430 | ALFRED ST 2 | 430_Mackay-Alfred Street 2 33 kV | Power Factor | 0.99496 | 0.98908 | 0.9833 | 0.99463 | 0.9886 | 0.98263 | 0.99454 | 0.98848 | 0.98244 | 0.99463 | 0.98862 | 0.98257 | 0.99458 | 0.98855 | 0.98247
MK | 84750025 | 430 | ALFRED ST 2 | 430_Mackay-Alfred Street 2 33 kV | Rating (A) | 579 | 579 | 579 | 579 | 579 | 579 | 579 | 579 | 579 | 579 | 579 | 579 | 579 | 579 | 579
NQ | 10132026 | 7182 | ROSS - MILLCHESTER | 7182 Ross - Milchester
NQ | 10132026 | 7182 | ROSS - MILLCHESTER | 7182 Ross - Milchester | % of Rated A | 16.3972 | 37.5332 | 33.0143 | 16.3958 | 37.539 | 33.0143 | 17.6408 | 37.8288 | 32.0206 | 17.6208 | 37.6511 | 31.9857 | 17.6556 | 37.6615 | 32.6501
NQ | 10132026 | 7182 | ROSS - MILLCHESTER | 7182 Ross - Milchester | Loading (A) | 51.1592 | 134.3651 | 108.6148 | 51.1549 | 134.3858 | 108.6148 | 55.0392 | 135.423 | 105.3464 | 54.9769 | 134.7866 | 105.2317 | 55.0855 | 134.824 | 107.4164
NQ | 10132026 | 7182 | ROSS - MILLCHESTER | 7182 Ross - Milchester | Power Factor | 0.91455 | 0.98908 | 0.99566 | 0.91475 | 0.98911 | 0.99568 | 0.88867 | 0.98454 | 0.99869 | 0.88757 | 0.9848 | 0.9987 | 0.88668 | 0.98468 | 0.9958
NQ | 10132026 | 7182 | ROSS - MILLCHESTER | 7182 Ross - Milchester | Rating (A) | 312 | 358 | 329 | 312 | 358 | 329 | 312 | 358 | 329 | 312 | 358 | 329 | 312 | 358 | 329
NQ | 20001222 | AV-CB-1 | Aitkenvale-Cranbrook | AV-CB-1_Aitkenvale-Cranbrook 66 kV
NQ | 20001222 | AV-CB-1 | Aitkenvale-Cranbrook | AV-CB-1_Aitkenvale-Cranbrook 66 kV | % of Rated A | 16.933 | 6.4105 | 13.5463 | 18.0843 | 6.4783 | 13.4492 | 18.2012 | 6.2143 | 13.3855 | 18.4237 | 6.2367 | 13.3524 | 18.3849 | 6.4185 | 13.3128
NQ | 20001222 | AV-CB-1 | Aitkenvale-Cranbrook | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Loading (A) | 56.3869 | 25.001 | 49.1731 | 60.2206 | 25.2652 | 48.8205 | 60.6099 | 24.2356 | 48.5893 | 61.351 | 24.3232 | 48.4691 | 61.2217 | 25.0322 | 48.3254
NQ | 20001222 | AV-CB-1 | Aitkenvale-Cranbrook | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Power Factor | 0.96821 | 0.52556 | 0.92516 | 0.77662 | 0.17048 | 0.92083 | 0.78169 | 0.31658 | 0.92008 | 0.80638 | 0.13813 | 0.91957 | 0.80505 | 0.21248 | 0.91875
NQ | 20001222 | AV-CB-1 | Aitkenvale-Cranbrook | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Rating (A) | 333 | 390 | 363 | 333 | 390 | 363 | 333 | 390 | 363 | 333 | 390 | 363 | 333 | 390 | 363
NQ | 20001857 | AY-HH-1 | AYR-HOMEHILL/JARVISFIELD | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV
NQ | 20001857 | AY-HH-1 | AYR-HOMEHILL/JARVISFIELD | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | % of Rated A | 44.6619 | 39.7299 | 43.2694 | 44.6933 | 39.7662 | 43.3086 | 44.4081 | 39.5709 | 43.0828 | 44.3617 | 39.5371 | 43.0259 | 44.3522 | 39.55 | 43.0299
NQ | 20001857 | AY-HH-1 | AYR-HOMEHILL/JARVISFIELD | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Loading (A) | 115.2277 | 117.2031 | 117.6928 | 115.3088 | 117.3102 | 117.7993 | 114.5729 | 116.7343 | 117.1852 | 114.4531 | 116.6345 | 117.0303 | 114.4288 | 116.6725 | 117.0413
NQ | 20001857 | AY-HH-1 | AYR-HOMEHILL/JARVISFIELD | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Power Factor | 0.99108 | 0.99187 | 0.99317 | 0.99121 | 0.992 | 0.99327 | 0.9919 | 0.9925 | 0.99367 | 0.99176 | 0.99271 | 0.99353 | 0.99174 | 0.99266 | 0.99352
NQ | 20001857 | AY-HH-1 | AYR-HOMEHILL/JARVISFIELD | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Rating (A) | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272
NQ | 20003134 | BO-DG-1 | Bohle-Dan Gleeson | BO-DG-1_Bohle-Dan Gleeson 66 kV
NQ | 20003134 | BO-DG-1 | Bohle-Dan Gleeson | BO-DG-1_Bohle-Dan Gleeson 66 kV | % of Rated A | 40.9828 | 37.8184 | 50.4915 | 40.6477 | 37.3106 | 50.1712 | 40.1611 | 38.3869 | 49.5967 | 39.8285 | 37.9445 | 49.2756 | 39.5181 | 37.5671 | 48.9802
NQ | 20003134 | BO-DG-1 | Bohle-Dan Gleeson | BO-DG-1_Bohle-Dan Gleeson 66 kV | Loading (A) | 183.1931 | 169.0481 | 225.6968 | 181.6952 | 166.7785 | 224.2652 | 179.5203 | 171.5895 | 221.6973 | 178.0335 | 169.6119 | 220.2619 | 176.6459 | 167.9251 | 218.9414
NQ | 20003134 | BO-DG-1 | Bohle-Dan Gleeson | BO-DG-1_Bohle-Dan Gleeson 66 kV | Power Factor | 0.92946 | 0.9006 | 0.95195 | 0.92834 | 0.8966 | 0.95123 | 0.9266 | 0.844 | 0.96907 | 0.92412 | 0.83701 | 0.96824 | 0.9218 | 0.82995 | 0.96745
NQ | 20003134 | BO-DG-1 | Bohle-Dan Gleeson | BO-DG-1_Bohle-Dan Gleeson 66 kV | Rating (A) | 447 | 447 | 447 | 447 | 447 | 447 | 447 | 447 | 447 | 447 | 447 | 447 | 447 | 447 | 447
NQ | 20003135 | 6127 | BOHLE-BLACK RIVER 1 | 6127_Bohle-Black River 1 66 kV
NQ | 20003135 | 6127 | BOHLE-BLACK RIVER 1 | 6127_Bohle-Black River 1 66 kV | % of Rated A | 42.8026 | 32.589 | 43.7223 | 42.6925 | 32.3487 | 43.6078 | 42.4167 | 32.1429 | 43.3282 | 42.3333 | 31.9192 | 43.2393 | 42.2614 | 31.7355 | 43.162
NQ | 20003135 | 6127 | BOHLE-BLACK RIVER 1 | 6127_Bohle-Black River 1 66 kV | Loading (A) | 312.0311 | 255.1718 | 310.4286 | 311.2283 | 253.2896 | 309.6154 | 309.2178 | 251.6783 | 307.63 | 308.6101 | 249.9269 | 306.999 | 308.0858 | 248.4885 | 306.4505
NQ | 20003135 | 6127 | BOHLE-BLACK RIVER 1 | 6127_Bohle-Black River 1 66 kV | Power Factor | 0.97704 | 0.94636 | 0.97678 | 0.97683 | 0.94463 | 0.97655 | 0.97683 | 0.9427 | 0.97653 | 0.97658 | 0.94095 | 0.97627 | 0.97636 | 0.9392 | 0.97603
NQ | 20003135 | 6127 | BOHLE-BLACK RIVER 1 | 6127_Bohle-Black River 1 66 kV | Rating (A) | 729 | 783 | 710 | 729 | 783 | 710 | 729 | 783 | 710 | 729 | 783 | 710 | 729 | 783 | 710
NQ | 20003596 | CH-CC-1 | CHUMVALE-CLONCURRY | CH-CC-1_Chumvale-Cloncurry 66 kV
NQ | 20003596 | CH-CC-1 | CHUMVALE-CLONCURRY | CH-CC-1_Chumvale-Cloncurry 66 kV | % of Rated A | 40.3733 | 37.8767 | 28.02 | 40.3766 | 37.8798 | 28.0222 | 40.3764 | 37.8796 | 28.0222 | 40.3847 | 37.8872 | 28.0273 | 40.3847 | 37.8872 | 28.0273
NQ | 20003596 | CH-CC-1 | CHUMVALE-CLONCURRY | CH-CC-1_Chumvale-Cloncurry 66 kV | Loading (A) | 65.7944 | 68.9217 | 48.1819 | 65.7997 | 68.9272 | 48.1858 | 65.7995 | 68.927 | 48.1857 | 65.8129 | 68.9408 | 48.1945 | 65.8129 | 68.9408 | 48.1945
NQ | 20003596 | CH-CC-1 | CHUMVALE-CLONCURRY | CH-CC-1_Chumvale-Cloncurry 66 kV | Power Factor | 0.97908 | 0.97963 | 0.98358 | 0.97908 | 0.97962 | 0.98358 | 0.97908 | 0.97962 | 0.98358 | 0.97908 | 0.97962 | 0.98359 | 0.97908 | 0.97962 | 0.98359
NQ | 20003596 | CH-CC-1 | CHUMVALE-CLONCURRY | CH-CC-1_Chumvale-Cloncurry 66 kV | Rating (A) | 163 | 182 | 172 | 163 | 182 | 172 | 163 | 182 | 172 | 163 | 182 | 172 | 163 | 182 | 172
NQ | 20003732 | CHTO | CLARESOUTH-CHARTERSTOWERS | CHTO_Clare South - Charters Towers 66 kV
NQ | 20003732 | CHTO | CLARESOUTH-CHARTERSTOWERS | CHTO_Clare South - Charters Towers 66 kV | % of Rated A | 54.2145 | 48.0649 | 46.393 | 54.2426 | 48.0838 | 46.4131 | 54.5033 | 48.3983 | 46.7775 | 54.5088 | 47.3631 | 46.7279 | 54.3022 | 47.3521 | 46.2233
NQ | 20003732 | CHTO | CLARESOUTH-CHARTERSTOWERS | CHTO_Clare South - Charters Towers 66 kV | Loading (A) | 107.8859 | 141.7915 | 126.1891 | 107.942 | 141.8471 | 126.2437 | 108.4606 | 142.7749 | 127.2348 | 108.4717 | 139.721 | 127.0999 | 108.0605 | 139.6887 | 125.7274
NQ | 20003732 | CHTO | CLARESOUTH-CHARTERSTOWERS | CHTO_Clare South - Charters Towers 66 kV | Power Factor | 0.99875 | 0.99912 | 0.99604 | 0.99874 | 0.99913 | 0.99605 | 0.99878 | 0.99916 | 0.99868 | 0.99878 | 0.99477 | 0.99867 | 0.99874 | 0.99481 | 0.99647
NQ | 20003732 | CHTO | CLARESOUTH-CHARTERSTOWERS | CHTO_Clare South - Charters Towers 66 kV | Rating (A) | 199 | 295 | 272 | 199 | 295 | 272 | 199 | 295 | 272 | 199 | 295 | 272 | 199 | 295 | 272
NQ | 20003733 | EAAY | CLARESOUTH-EASTAYR | EAAY_Clare South - East Ayr 66 kV
NQ | 20003733 | EAAY | CLARESOUTH-EASTAYR | EAAY_Clare South - East Ayr 66 kV | % of Rated A | 11.5572 | 8.6027 | 12.141 | 11.5759 | 8.6169 | 12.1805 | 10.9598 | 8.2832 | 12.0327 | 10.9359 | 8.2609 | 11.9942 | 10.8597 | 8.2271 | 11.9286
NQ | 20003733 | EAAY | CLARESOUTH-EASTAYR | EAAY_Clare South - East Ayr 66 kV | Loading (A) | 24.2702 | 27.0984 | 37.6372 | 24.3093 | 27.1434 | 37.7595 | 23.0155 | 26.092 | 37.3015 | 22.9654 | 26.0219 | 37.1821 | 22.8054 | 25.9153 | 36.9787
NQ | 20003733 | EAAY | CLARESOUTH-EASTAYR | EAAY_Clare South - East Ayr 66 kV | Power Factor | 0.86119 | 0.84188 | 0.99637 | 0.86313 | 0.84409 | 0.99807 | 0.88597 | 0.85932 | 0.99932 | 0.88301 | 0.85604 | 0.99928 | 0.88026 | 0.85434 | 0.99925
NQ | 20003733 | EAAY | CLARESOUTH-EASTAYR | EAAY_Clare South - East Ayr 66 kV | Rating (A) | 210 | 315 | 310 | 210 | 315 | 310 | 210 | 315 | 310 | 210 | 315 | 310 | 210 | 315 | 310
NQ | 20003734 | CLSO-HOHI-1 | CLARESOUTH-HOMEHILL NO.01 | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV
NQ | 20003734 | CLSO-HOHI-1 | CLARESOUTH-HOMEHILL NO.01 | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | % of Rated A | 7.7931 | 7.076 | 7.1364 | 8.0751 | 7.0597 | 7.2147 | 8.0413 | 6.6646 | 7.1185 | 7.8858 | 6.6801 | 7.0929 | 7.9296 | 6.693 | 7.055
NQ | 20003734 | CLSO-HOHI-1 | CLARESOUTH-HOMEHILL NO.01 | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Loading (A) | 24.3144 | 25.6857 | 24.0497 | 25.1942 | 25.6266 | 24.3134 | 25.089 | 24.1925 | 23.9895 | 24.6037 | 24.2488 | 23.9032 | 24.7405 | 24.2956 | 23.7753
NQ | 20003734 | CLSO-HOHI-1 | CLARESOUTH-HOMEHILL NO.01 | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Power Factor | 0.59307 | 0.3771 | 0.96843 | 0.57586 | 0.37504 | 0.97578 | 0.59907 | 0.4061 | 0.97976 | 0.60638 | 0.44023 | 0.9795 | 0.6119 | 0.44578 | 0.9792
NQ | 20003734 | CLSO-HOHI-1 | CLARESOUTH-HOMEHILL NO.01 | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Rating (A) | 312 | 363 | 337 | 312 | 363 | 337 | 312 | 363 | 337 | 312 | 363 | 337 | 312 | 363 | 337
NQ | 20003735 | CLSO-HOHI-2 | CLARESOUTH-HOMEHILL NO.02 | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV
NQ | 20003735 | CLSO-HOHI-2 | CLARESOUTH-HOMEHILL NO.02 | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | % of Rated A | 13.3149 | 9.925 | 9.87 | 13.8134 | 9.9009 | 9.9924 | 13.7674 | 9.3314 | 9.8672 | 13.4883 | 9.3589 | 9.831 | 13.5684 | 9.3788 | 9.7777
NQ | 20003735 | CLSO-HOHI-2 | CLARESOUTH-HOMEHILL NO.02 | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Loading (A) | 22.5022 | 23.7207 | 22.9972 | 23.3446 | 23.6632 | 23.2823 | 23.2669 | 22.3019 | 22.9905 | 22.7953 | 22.3677 | 22.9063 | 22.9306 | 22.4153 | 22.782
NQ | 20003735 | CLSO-HOHI-2 | CLARESOUTH-HOMEHILL NO.02 | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Power Factor | 0.65401 | 0.43875 | 0.96487 | 0.63642 | 0.4367 | 0.97255 | 0.65893 | 0.46858 | 0.97695 | 0.6666 | 0.50282 | 0.97671 | 0.67184 | 0.50834 | 0.97645
NQ | 20003735 | CLSO-HOHI-2 | CLARESOUTH-HOMEHILL NO.02 | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Rating (A) | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233
NQ | 20003736 | CS-ML-1 | CLARESOUTH-MILLAROO | CS-ML-1_Clare South - Millaroo 66 kV
NQ | 20003736 | CS-ML-1 | CLARESOUTH-MILLAROO | CS-ML-1_Clare South - Millaroo 66 kV | % of Rated A | 45.3257 | 44.4664 | 44.0009 | 44.8913 | 44.0189 | 43.5534 | 45.7589 | 43.9484 | 43.4263 | 45.7751 | 43.962 | 43.4355 | 45.346 | 43.9731 | 43.4422
NQ | 20003736 | CS-ML-1 | CLARESOUTH-MILLAROO | CS-ML-1_Clare South - Millaroo 66 kV | Loading (A) | 88.3805 | 96.9321 | 87.5572 | 87.5333 | 95.9564 | 86.6665 | 89.2252 | 95.8028 | 86.4137 | 89.2569 | 95.8325 | 86.4321 | 88.4201 | 95.8567 | 86.4453
NQ | 20003736 | CS-ML-1 | CLARESOUTH-MILLAROO | CS-ML-1_Clare South - Millaroo 66 kV | Power Factor | 0.84833 | 0.84337 | 0.84663 | 0.84884 | 0.84392 | 0.84717 | 0.84794 | 0.84405 | 0.84741 | 0.84791 | 0.84403 | 0.84739 | 0.84865 | 0.84401 | 0.84738
NQ | 20003736 | CS-ML-1 | CLARESOUTH-MILLAROO | CS-ML-1_Clare South - Millaroo 66 kV | Rating (A) | 195 | 218 | 199 | 195 | 218 | 199 | 195 | 218 | 199 | 195 | 218 | 199 | 195 | 218 | 199
NQ | 20003737 | MOPA | CLARESOUTH-MONAPARK | MOPA_Clare South - Mona Park 66 kV
NQ | 20003737 | MOPA | CLARESOUTH-MONAPARK | MOPA_Clare South - Mona Park 66 kV | % of Rated A | 32.3181 | 11.939 | 13.1363 | 32.3097 | 11.9364 | 13.2093 | 33.0383 | 11.6254 | 13.0006 | 33.0494 | 11.621 | 12.9791 | 32.91 | 11.6079 | 12.9421
NQ | 20003737 | MOPA | CLARESOUTH-MONAPARK | MOPA_Clare South - Mona Park 66 kV | Loading (A) | 43.3063 | 37.6079 | 40.7226 | 43.2949 | 37.5997 | 40.9489 | 44.2713 | 36.6199 | 40.3018 | 44.2862 | 36.6061 | 40.2352 | 44.0994 | 36.5649 | 40.1204
NQ | 20003737 | MOPA | CLARESOUTH-MONAPARK | MOPA_Clare South - Mona Park 66 kV | Power Factor | 0.82298 | 0.56955 | 0.89309 | 0.82299 | 0.58243 | 0.8977 | 0.8227 | 0.58765 | 0.90358 | 0.82268 | 0.58334 | 0.9021 | 0.8227 | 0.58162 | 0.90098
NQ | 20003737 | MOPA | CLARESOUTH-MONAPARK | MOPA_Clare South - Mona Park 66 kV | Rating (A) | 134 | 315 | 310 | 134 | 315 | 310 | 134 | 315 | 310 | 134 | 315 | 310 | 134 | 315 | 310
NQ | 20004005 | CR-HU-1 | CAPERIVER-HUGHENDEN NO.01 | CR-HU-1_Cape River-Hughenden No 1 66 kV
NQ | 20004005 | CR-HU-1 | CAPERIVER-HUGHENDEN NO.01 | CR-HU-1_Cape River-Hughenden No 1 66 kV | % of Rated A | 51.7376 | 32.0757 | 39.0671 | 51.743 | 32.0768 | 39.0683 | 51.8225 | 32.6543 | 39.4095 | 51.9634 | 32.1976 | 39.1938 | 52.0704 | 33.1059 | 39.2654
NQ | 20004005 | CR-HU-1 | CAPERIVER-HUGHENDEN NO.01 | CR-HU-1_Cape River-Hughenden No 1 66 kV | Loading (A) | 60.0156 | 51.3212 | 60.9446 | 60.0219 | 51.3229 | 60.9465 | 60.1141 | 52.2469 | 61.4788 | 60.2775 | 51.5161 | 61.1424 | 60.4017 | 52.9695 | 61.254
NQ | 20004005 | CR-HU-1 | CAPERIVER-HUGHENDEN NO.01 | CR-HU-1_Cape River-Hughenden No 1 66 kV | Power Factor | 0.82613 | 0.83269 | 0.87133 | 0.82596 | 0.83264 | 0.87127 | 0.82356 | 0.78651 | 0.83058 | 0.82432 | 0.83579 | 0.8697 | 0.82568 | 0.7846 | 0.87069
NQ | 20004005 | CR-HU-1 | CAPERIVER-HUGHENDEN NO.01 | CR-HU-1_Cape River-Hughenden No 1 66 kV | Rating (A) | 116 | 160 | 156 | 116 | 160 | 156 | 116 | 160 | 156 | 116 | 160 | 156 | 116 | 160 | 156
NQ | 20004647 | CT-CR-1 | CHARTERSTOWERS-CAPERIVER | CT-CR-1_Charters Towers-CARI No 1 66 kV
NQ | 20004647 | CT-CR-1 | CHARTERSTOWERS-CAPERIVER | CT-CR-1_Charters Towers-CARI No 1 66 kV | % of Rated A | 49.2999 | 40.3497 | 51.1275 | 49.3071 | 40.3527 | 51.1308 | 49.0253 | 39.9462 | 51.2079 | 49.2394 | 40.3943 | 51.2966 | 49.2947 | 40.8474 | 51.4609
NQ | 20004647 | CT-CR-1 | CHARTERSTOWERS-CAPERIVER | CT-CR-1_Charters Towers-CARI No 1 66 kV | Loading (A) | 90.7117 | 80.6995 | 92.0295 | 90.725 | 80.7055 | 92.0354 | 90.2066 | 79.8925 | 92.1742 | 90.6004 | 80.7886 | 92.3339 | 90.7023 | 81.6948 | 92.6297
NQ | 20004647 | CT-CR-1 | CHARTERSTOWERS-CAPERIVER | CT-CR-1_Charters Towers-CARI No 1 66 kV | Power Factor | 0.635 | 0.58384 | 0.65912 | 0.63481 | 0.58378 | 0.65904 | 0.64474 | 0.58762 | 0.65621 | 0.6339 | 0.58901 | 0.65698 | 0.63406 | 0.5849 | 0.64242
NQ | 20004647 | CT-CR-1 | CHARTERSTOWERS-CAPERIVER | CT-CR-1_Charters Towers-CARI No 1 66 kV | Rating (A) | 184 | 200 | 180 | 184 | 200 | 180 | 184 | 200 | 180 | 184 | 200 | 180 | 184 | 200 | 180
NQ | 20004649 | CT-MR-1 | MILLCHESTER-CHARTERSTOWERS | CT-MR-1_Millchester-CHTO No 1 66 kV
NQ | 20004649 | CT-MR-1 | MILLCHESTER-CHARTERSTOWERS | CT-MR-1_Millchester-CHTO No 1 66 kV | % of Rated A | 23.794 | 26.6966 | 22.5081 | 23.7875 | 26.694 | 22.4966 | 26.7252 | 27.6192 | 19.3216 | 26.7569 | 27.3266 | 19.3459 | 27.2058 | 27.3073 | 21.8826
NQ | 20004649 | CT-MR-1 | MILLCHESTER-CHARTERSTOWERS | CT-MR-1_Millchester-CHTO No 1 66 kV | Loading (A) | 66.1472 | 83.0195 | 63.923 | 66.1293 | 83.0114 | 63.8904 | 74.2962 | 85.8884 | 54.8735 | 74.3841 | 84.9786 | 54.9423 | 75.632 | 84.9185 | 62.1464
NQ | 20004649 | CT-MR-1 | MILLCHESTER-CHARTERSTOWERS | CT-MR-1_Millchester-CHTO No 1 66 kV | Power Factor | 0.73676 | 0.73257 | 0.68054 | 0.73715 | 0.73317 | 0.68111 | 0.69811 | 0.68916 | 0.70697 | 0.69924 | 0.68964 | 0.70858 | 0.69919 | 0.69032 | 0.67136
NQ | 20004649 | CT-MR-1 | MILLCHESTER-CHARTERSTOWERS | CT-MR-1_Millchester-CHTO No 1 66 kV | Rating (A) | 278 | 311 | 284 | 278 | 311 | 284 | 278 | 311 | 284 | 278 | 311 | 284 | 278 | 311 | 284
NQ | 20005445 | DR-CC-1 | DUCHESSRD-CLONCURRY | DR-CC-1_Duchess Road-Cloncurry 1 66 kV
NQ | 20005445 | DR-CC-1 | DUCHESSRD-CLONCURRY | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | % of Rated A | 14.7994 | 9.0224 | 8.7323 | 14.7995 | 9.0225 | 8.7324 | 14.7998 | 9.0227 | 8.7325 | 14.7994 | 9.0225 | 8.7322 | 14.7994 | 9.0225 | 8.7322
NQ | 20005445 | DR-CC-1 | DUCHESSRD-CLONCURRY | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Loading (A) | 12.2835 | 12.2704 | 12.3126 | 12.2836 | 12.2706 | 12.3126 | 12.2838 | 12.2709 | 12.3128 | 12.2835 | 12.2706 | 12.3125 | 12.2835 | 12.2706 | 12.3125
NQ | 20005445 | DR-CC-1 | DUCHESSRD-CLONCURRY | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Power Factor | 0.0056514 | 0.0056514 | 0.0056514 | 0.0056514 | 0.0056514 | 0.0056514 | 0.0056514 | 0.0056514 | 0.0056514 | 0.0056514 | 0.0056514 | 0.0056514 | 0.0056514 | 0.0056514 | 0.0056514
NQ | 20005445 | DR-CC-1 | DUCHESSRD-CLONCURRY | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Rating (A) | 83 | 136 | 141 | 83 | 136 | 141 | 83 | 136 | 141 | 83 | 136 | 141 | 83 | 136 | 141
NQ | 20006056 | GA-BO-1 | GARBUTT-BOHLE | GA-BO-1_Garbutt-Bohle No 1 66 kV
NQ | 20006056 | GA-BO-1 | GARBUTT-BOHLE | GA-BO-1_Garbutt-Bohle No 1 66 kV | % of Rated A | 49.9913 | 35.9639 | 51.1668 | 49.5966 | 35.5092 | 50.744 | 49.0533 | 33.9219 | 50.1615 | 48.7276 | 33.4587 | 49.8066 | 48.4125 | 33.0596 | 49.4653
NQ | 20006056 | GA-BO-1 | GARBUTT-BOHLE | GA-BO-1_Garbutt-Bohle No 1 66 kV | Loading (A) | 275.4523 | 209.3078 | 268.1142 | 273.2774 | 206.6616 | 265.8987 | 270.2838 | 197.4235 | 262.8461 | 268.4892 | 194.7279 | 260.9866 | 266.7529 | 192.4052 | 259.1983
NQ | 20006056 | GA-BO-1 | GARBUTT-BOHLE | GA-BO-1_Garbutt-Bohle No 1 66 kV | Power Factor | 0.94038 | 0.85934 | 0.93328 | 0.93814 | 0.85147 | 0.93077 | 0.93765 | 0.88379 | 0.93005 | 0.93592 | 0.87769 | 0.92799 | 0.93418 | 0.87153 | 0.92593
NQ | 20006056 | GA-BO-1 | GARBUTT-BOHLE | GA-BO-1_Garbutt-Bohle No 1 66 kV | Rating (A) | 551 | 582 | 524 | 551 | 582 | 524 | 551 | 582 | 524 | 551 | 582 | 524 | 551 | 582 | 524
NQ | 20006058 | GA-HP-1 | GARBUTT-HERMITPARK | GA-HP-1_Garbutt-Hermit Park No 1 66 kV
NQ | 20006058 | GA-HP-1 | GARBUTT-HERMITPARK | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | % of Rated A | 68.1135 | 65.4683 | 62.0694 | 68.4136 | 65.7662 | 62.3542 | 66.7374 | 60.2449 | 57.6028 | 67.0116 | 61.1784 | 57.8305 | 66.1329 | 60.9932 | 58.0408
NQ | 20006058 | GA-HP-1 | GARBUTT-HERMITPARK | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Loading (A) | 234.9668 | 235.0086 | 198.6008 | 236.0042 | 236.0781 | 199.5123 | 230.2185 | 216.256 | 184.3068 | 231.1645 | 219.6082 | 185.0353 | 228.133 | 218.9422 | 185.7084
NQ | 20006058 | GA-HP-1 | GARBUTT-HERMITPARK | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Power Factor | 0.78902 | 0.82228 | 0.8472 | 0.82082 | 0.82271 | 0.84759 | 0.77236 | 0.81202 | 0.83274 | 0.7733 | 0.82802 | 0.83333 | 0.77388 | 0.81305 | 0.83387
NQ | 20006058 | GA-HP-1 | GARBUTT-HERMITPARK | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Rating (A) | 345 | 359 | 320 | 345 | 359 | 320 | 345 | 359 | 320 | 345 | 359 | 320 | 345 | 359 | 320
NQ | 20006059 | GA-NS-1 | GARBUTT-NEILSMITH | GA-NS-1_Garbutt-Neil Smith No 1 66 kV
NQ | 20006059 | GA-NS-1 | GARBUTT-NEILSMITH | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | % of Rated A | 41.077 | 28.1903 | 25.1539 | 41.0727 | 28.1895 | 25.1503 | 40.9566 | 28.1593 | 25.0944 | 41.2285 | 28.3514 | 25.2546 | 41.3215 | 28.3648 | 25.26
NQ | 20006059 | GA-NS-1 | GARBUTT-NEILSMITH | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Loading (A) | 69.4193 | 67.3741 | 58.6081 | 69.4121 | 67.3722 | 58.5997 | 69.216 | 67.3001 | 58.4693 | 69.6754 | 67.759 | 58.8426 | 69.8325 | 67.7911 | 58.8552
NQ | 20006059 | GA-NS-1 | GARBUTT-NEILSMITH | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Power Factor | 0.99284 | 0.99334 | 0.99553 | 0.99284 | 0.99335 | 0.99554 | 0.99283 | 0.99338 | 0.99553 | 0.9927 | 0.99326 | 0.99543 | 0.99274 | 0.99324 | 0.99542
NQ | 20006059 | GA-NS-1 | GARBUTT-NEILSMITH | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Rating (A) | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233
NQ | 20006060 | GA-TP-1 | GARBUTT-TOWNSVILLEPORT | GA-TP-1_Garbutt-Townsville Port 1 66 kV
NQ | 20006060 | GA-TP-1 | GARBUTT-TOWNSVILLEPORT | GA-TP-1_Garbutt-Townsville Port 1 66 kV | % of Rated A | 26.5259 | 20.5689 | 33.0018 | 24.771 | 19.7643 | 32.6605 | 22.9791 | 16.8705 | 31.3724 | 20.4623 | 18.2428 | 31.1089 | 20.2305 | 17.9935 | 30.887
NQ | 20006060 | GA-TP-1 | GARBUTT-TOWNSVILLEPORT | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Loading (A) | 68.4368 | 60.6784 | 89.7587 | 63.9093 | 58.3046 | 88.8304 | 59.286 | 49.7679 | 85.3268 | 52.7927 | 53.8163 | 84.61 | 52.1947 | 53.0807 | 84.0064
NQ | 20006060 | GA-TP-1 | GARBUTT-TOWNSVILLEPORT | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Power Factor | 0.90478 | 0.45124 | 0.92923 | 0.57445 | 0.44636 | 0.93187 | 0.92712 | 0.14386 | 0.93144 | 0.54537 | 0.35182 | 0.93185 | 0.53386 | 0.32967 | 0.93024
NQ | 20006060 | GA-TP-1 | GARBUTT-TOWNSVILLEPORT | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Rating (A) | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272
NQ | 20007825 | HU-WI-1 | HUGHENDEN-WINTON | HU-WI-1 Hughenden-Winton No 1 66 kV
NQ | 20007825 | HU-WI-1 | HUGHENDEN-WINTON | HU-WI-1 Hughenden-Winton No 1 66 kV | % of Rated A | 14.1596 | 13.4087 | 11.868 | 14.1595 | 13.4087 | 11.868 | 14.1623 | 13.4099 | 11.867 | 13.923 | 13.1628 | 11.726 | 13.9212 | 13.1605 | 11.7284
NQ | 20007825 | HU-WI-1 | HUGHENDEN-WINTON | HU-WI-1 Hughenden-Winton No 1 66 kV | Loading (A) | 37.0981 | 39.0193 | 31.3316 | 37.0979 | 39.0193 | 31.3316 | 37.1052 | 39.0227 | 31.3289 | 36.4783 | 38.3038 | 30.9567 | 36.4736 | 38.297 | 30.9629
NQ | 20007825 | HU-WI-1 | HUGHENDEN-WINTON | HU-WI-1 Hughenden-Winton No 1 66 kV | Power Factor | 0.88262 | 0.90844 | 0.78656 | 0.88261 | 0.90844 | 0.78654 | 0.88305 | 0.90857 | 0.78783 | 0.87443 | 0.90116 | 0.77746 | 0.87408 | 0.90087 | 0.77555
NQ | 20007825 | HU-WI-1 | HUGHENDEN-WINTON | HU-WI-1 Hughenden-Winton No 1 66 kV | Rating (A) | 262 | 291 | 264 | 262 | 291 | 264 | 262 | 291 | 264 | 262 | 291 | 264 | 262 | 291 | 264
NQ | 20007826 | HU-RI-1 | HUGHENDEN-RICHMOND | HU-RI-1_Hughenden-Richmond No 1 66 kV
NQ | 20007826 | HU-RI-1 | HUGHENDEN-RICHMOND | HU-RI-1_Hughenden-Richmond No 1 66 kV | % of Rated A | 17.4481 | 14.7417 | 11.842 | 17.4479 | 14.7417 | 11.8419 | 17.4552 | 14.7329 | 11.8444 | 17.4539 | 14.73 | 11.8441 | 17.2075 | 14.4948 | 11.7278
NQ | 20007826 | HU-RI-1 | HUGHENDEN-RICHMOND | HU-RI-1_Hughenden-Richmond No 1 66 kV | Loading (A) | 49.7271 | 53.5124 | 39.3153 | 49.7265 | 53.5122 | 39.3152 | 49.7473 | 53.4804 | 39.3234 | 49.7436 | 53.4698 | 39.3224 | 49.0415 | 52.6163 | 38.9363
NQ | 20007826 | HU-RI-1 | HUGHENDEN-RICHMOND | HU-RI-1_Hughenden-Richmond No 1 66 kV | Power Factor | 0.9532 | 0.97145 | 0.85343 | 0.95319 | 0.97145 | 0.85341 | 0.95348 | 0.97118 | 0.85458 | 0.95343 | 0.97109 | 0.85444 | 0.9487 | 0.96697 | 0.8449
NQ | 20007826 | HU-RI-1 | HUGHENDEN-RICHMOND | HU-RI-1_Hughenden-Richmond No 1 66 kV | Rating (A) | 285 | 363 | 332 | 285 | 363 | 332 | 285 | 363 | 332 | 285 | 363 | 332 | 285 | 363 | 332
NQ | 20008181 | IN-LA-1 | INGHAM-LANNERCOST | IN-LA-1_Ingham-Lannercost No 1 66 kV
NQ | 20008181 | IN-LA-1 | INGHAM-LANNERCOST | IN-LA-1_Ingham-Lannercost No 1 66 kV | % of Rated A | 11.1293 | 10.0975 | 5.8691 | 11.1266 | 10.138 | 5.8679 | 11.1149 | 10.0845 | 5.864 | 11.1167 | 10.1105 | 5.8647 | 11.1193 | 10.2149 | 5.8646
NQ | 20008181 | IN-LA-1 | INGHAM-LANNERCOST | IN-LA-1_Ingham-Lannercost No 1 66 kV | Loading (A) | 14.9133 | 18.2765 | 10.2709 | 14.9096 | 18.3499 | 10.2688 | 14.894 | 18.2529 | 10.2621 | 14.8964 | 18.3 | 10.2632 | 14.8998 | 18.489 | 10.263
NQ | 20008181 | IN-LA-1 | INGHAM-LANNERCOST | IN-LA-1_Ingham-Lannercost No 1 66 kV | Power Factor | 0.99254 | 0.99004 | 0.99677 | 0.99255 | 0.99002 | 0.99677 | 0.99251 | 0.99007 | 0.99679 | 0.99251 | 0.98997 | 0.99679 | 0.99256 | 0.98983 | 0.99679
NQ | 20008181 | IN-LA-1 | INGHAM-LANNERCOST | IN-LA-1_Ingham-Lannercost No 1 66 kV | Rating (A) | 134 | 181 | 175 | 134 | 181 | 175 | 134 | 181 | 175 | 134 | 181 | 175 | 134 | 181 | 175
NQ | 20008182 | IN-VC-1 | INGHAM-VICTORIA | IN-VC-1_Ingham-Victoria No 1 66 kV
NQ | 20008182 | IN-VC-1 | INGHAM-VICTORIA | IN-VC-1_Ingham-Victoria No 1 66 kV | % of Rated A | 12.2953 | 12.9735 | 13.3567 | 12.4157 | 12.7142 | 13.507 | 12.2313 | 12.6456 | 13.3173 | 12.2385 | 12.8698 | 13.3234 | 12.2442 | 12.8729 | 13.3288
NQ | 20008182 | IN-VC-1 | INGHAM-VICTORIA | IN-VC-1_Ingham-Victoria No 1 66 kV | Loading (A) | 24.4676 | 28.9309 | 27.2477 | 24.7072 | 28.3526 | 27.5543 | 24.3403 | 28.1997 | 27.1674 | 24.3546 | 28.6996 | 27.1798 | 24.3659 | 28.7066 | 27.1908
NQ | 20008182 | IN-VC-1 | INGHAM-VICTORIA | IN-VC-1_Ingham-Victoria No 1 66 kV | Power Factor | 0.86624 | 0.30365 | 0.94698 | 0.8718 | 0.28044 | 0.94971 | 0.86824 | 0.29213 | 0.9484 | 0.86834 | 0.3137 | 0.94842 | 0.86842 | 0.28974 | 0.94844
NQ | 20008182 | IN-VC-1 | INGHAM-VICTORIA | IN-VC-1_Ingham-Victoria No 1 66 kV | Rating (A) | 199 | 223 | 204 | 199 | 223 | 204 | 199 | 223 | 204 | 199 | 223 | 204 | 199 | 223 | 204
NQ | 20008540 | JA-EA-1 | JARVISFIELD-EASTAYR | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV
NQ | 20008540 | JA-EA-1 | JARVISFIELD-EASTAYR | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | % of Rated A | 18.9 | 14.9864 | 15.7746 | 18.9155 | 14.993 | 15.7805 | 19.6947 | 15.4486 | 15.9306 | 19.6676 | 15.4341 | 15.9219 | 19.6024 | 15.392 | 15.8907
NQ | 20008540 | JA-EA-1 | JARVISFIELD-EASTAYR | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Loading (A) | 31.9411 | 35.9674 | 36.9126 | 31.9672 | 35.9833 | 36.9264 | 33.284 | 37.0767 | 37.2775 | 33.2382 | 37.0419 | 37.2573 | 33.1281 | 36.9408 | 37.1842
NQ | 20008540 | JA-EA-1 | JARVISFIELD-EASTAYR | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Power Factor | 0.55662 | 0.59629 | 0.70605 | 0.5567 | 0.59646 | 0.70616 | 0.53612 | 0.62521 | 0.67559 | 0.53613 | 0.62495 | 0.67538 | 0.53277 | 0.62257 | 0.67347
NQ | 20008540 | JA-EA-1 | JARVISFIELD-EASTAYR | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Rating (A) | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234
NQ | 20010431 | MICB - DURO 1 | MICA CK B - DUCHESS ROAD NO.01 | MICB-DURO 1_Mica Creek B-DURO 1 132 kV
NQ | 20010431 | MICB - DURO 1 | MICA CK B - DUCHESS ROAD NO.01 | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | % of Rated A | 19.6376 | 16.1164 | 13.2746 | 19.5836 | 16.072 | 13.2381 | 19.5294 | 16.0276 | 13.2014 | 19.5299 | 16.028 | 13.2018 | 19.5299 | 16.028 | 13.2018
NQ | 20010431 | MICB - DURO 1 | MICA CK B - DUCHESS ROAD NO.01 | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Loading (A) | 75.4085 | 79.1315 | 61.3288 | 75.2011 | 78.9137 | 61.1599 | 74.993 | 78.6953 | 60.9906 | 74.995 | 78.6973 | 60.9921 | 74.995 | 78.6973 | 60.9921
NQ | 20010431 | MICB - DURO 1 | MICA CK B - DUCHESS ROAD NO.01 | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Power Factor | 0.98642 | 0.98617 | 0.99127 | 0.98643 | 0.98618 | 0.99129 | 0.98645 | 0.9862 | 0.99131 | 0.98645 | 0.9862 | 0.99131 | 0.98645 | 0.9862 | 0.99131
NQ | 20010431 | MICB - DURO 1 | MICA CK B - DUCHESS ROAD NO.01 | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Rating (A) | 384 | 491 | 462 | 384 | 491 | 462 | 384 | 491 | 462 | 384 | 491 | 462 | 384 | 491 | 462
NQ | 20010432 | MICB - DURO 2 | MICA CREEKB-DUCHESSRD NO.02 | MICB-DURO 2_Mica Creek B-DURO 2 132 kV
NQ | 20010432 | MICB - DURO 2 | MICA CREEKB-DUCHESSRD NO.02 | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | % of Rated A | 26.763 | 22.7156 | 18.1406 | 26.6891 | 22.6529 | 18.0906 | 26.615 | 22.5899 | 18.0406 | 26.6157 | 22.5905 | 18.041 | 26.6157 | 22.5905 | 18.041
NQ | 20010432 | MICB - DURO 2 | MICA CREEKB-DUCHESSRD NO.02 | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Loading (A) | 74.6687 | 78.369 | 60.9523 | 74.4625 | 78.1524 | 60.7846 | 74.2558 | 77.9353 | 60.6163 | 74.2577 | 77.9373 | 60.6179 | 74.2577 | 77.9373 | 60.6179
NQ | 20010432 | MICB - DURO 2 | MICA CREEKB-DUCHESSRD NO.02 | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Power Factor | 0.99651 | 0.99605 | 0.99824 | 0.99654 | 0.99607 | 0.99826 | 0.99656 | 0.9961 | 0.99828 | 0.99656 | 0.9961 | 0.99828 | 0.99656 | 0.9961 | 0.99828
NQ | 20010432 | MICB - DURO 2 | MICA CREEKB-DUCHESSRD NO.02 | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Rating (A) | 279 | 345 | 336 | 279 | 345 | 336 | 279 | 345 | 336 | 279 | 345 | 336 | 279 | 345 | 336
NQ | 20010433 | CHUM | MICC - CHUM 220KV FDR 7018 | 7018_Mica Creek C - Chumvale 220 kV
NQ | 20010433 | CHUM | MICC - CHUM 220KV FDR 7018 | 7018_Mica Creek C - Chumvale 220 kV | % of Rated A | 15.3975 | 12.9471 | 13.8649 | 15.4306 | 12.9739 | 13.8961 | 15.4306 | 12.9738 | 13.8961 | 15.4976 | 13.0274 | 13.9603 | 15.4976 | 13.0274 | 13.9603
NQ | 20010433 | CHUM | MICC - CHUM 220KV FDR 7018 | 7018_Mica Creek C - Chumvale 220 kV | Loading (A) | 131.6484 | 120.4082 | 120.9022 | 131.9319 | 120.6569 | 121.1738 | 131.9315 | 120.6565 | 121.1737 | 132.5047 | 121.1546 | 121.7337 | 132.5047 | 121.1546 | 121.7337
NQ | 20010433 | CHUM | MICC - CHUM 220KV FDR 7018 | 7018_Mica Creek C - Chumvale 220 kV | Power Factor | 0.96104 | 0.96813 | 0.96198 | 0.96089 | 0.968 | 0.96185 | 0.96089 | 0.968 | 0.96185 | 0.96059 | 0.96774 | 0.96153 | 0.96059 | 0.96774 | 0.96153
NQ | 20010433 | CHUM | MICC - CHUM 220KV FDR 7018 | 7018_Mica Creek C - Chumvale 220 kV | Rating (A) | 855 | 930 | 872 | 855 | 930 | 872 | 855 | 930 | 872 | 855 | 930 | 872 | 855 | 930 | 872
NQ | 20010916 | MP-AY-1 | MONAPARK-AYR | MP-AY-1 Mona Park - Ayr No 1 66 kV
NQ | 20010916 | MP-AY-1 | MONAPARK-AYR | MP-AY-1 Mona Park - Ayr No 1 66 kV | % of Rated A | 31.3588 | 21.9901 | 24.9765 | 31.2561 | 21.917 | 25.15 | 30.9396 | 21.7435 | 25.0447 | 30.8828 | 21.6936 | 24.9912 | 30.8145 | 21.6675 | 24.9317
NQ | 20010916 | MP-AY-1 | MONAPARK-AYR | MP-AY-1 Mona Park - Ayr No 1 66 kV | Loading (A) | 62.4039 | 64.6509 | 72.1817 | 62.1995 | 64.4359 | 72.6831 | 61.5699 | 63.9259 | 72.3789 | 61.4567 | 63.7791 | 72.2241 | 61.3209 | 63.7024 | 72.0523
NQ | 20010916 | MP-AY-1 | MONAPARK-AYR | MP-AY-1 Mona Park - Ayr No 1 66 kV | Power Factor | 0.99853 | 0.99787 | 0.99767 | 0.99838 | 0.99768 | 0.99685 | 0.99925 | 0.99851 | 0.99597 | 0.99918 | 0.99839 | 0.99602 | 0.99916 | 0.99838 | 0.99601
NQ | 20010916 | MP-AY-1 | MONAPARK-AYR | MP-AY-1 Mona Park - Ayr No 1 66 kV | Rating (A) | 199 | 294 | 289 | 199 | 294 | 289 | 199 | 294 | 289 | 199 | 294 | 289 | 199 | 294 | 289
NQ | 20010918 | MR-LE-1 | MILLCHESTER-MOUNTLEYSHON | MR-LE-1_Millchester-Mt Leyshon 1 66 kV
NQ | 20010918 | MR-LE-1 | MILLCHESTER-MOUNTLEYSHON | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | % of Rated A | 42.6061 | 38.9003 | 44.1179 | 42.6005 | 38.8975 | 44.1026 | 42.6669 | 38.8533 | 44.0991 | 42.5126 | 38.8595 | 44.1051 | 42.528 | 38.8744 | 44.1187
NQ | 20010918 | MR-LE-1 | MILLCHESTER-MOUNTLEYSHON | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Loading (A) | 78.401 | 78.0536 | 79.9355 | 78.3903 | 78.0478 | 79.9073 | 78.5255 | 77.9558 | 79.894 | 78.2234 | 77.9688 | 79.9054 | 78.2526 | 77.9998 | 79.9309
NQ | 20010918 | MR-LE-1 | MILLCHESTER-MOUNTLEYSHON | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Power Factor | 0.86689 | 0.86693 | 0.86616 | 0.86691 | 0.86694 | 0.86621 | 0.86645 | 0.86705 | 0.86546 | 0.86712 | 0.86703 | 0.86545 | 0.86709 | 0.867 | 0.86542
NQ | 20010918 | MR-LE-1 | MILLCHESTER-MOUNTLEYSHON | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Rating (A) | 188 | 205 | 185 | 188 | 205 | 185 | 188 | 205 | 185 | 188 | 205 | 185 | 188 | 205 | 185
NQ | 20012877 | ST-GI-1 | Stuart-Giru | ST-GI-1_Stuart-Giru 66 kV
NQ | 20012877 | ST-GI-1 | Stuart-Giru | ST-GI-1_Stuart-Giru 66 kV | % of Rated A | 14.1392 | 16.137 | 16.5583 | 14.139 | 16.1387 | 16.5578 | 14.1147 | 16.0368 | 16.4604 | 14.8431 | 16.8901 | 17.3113 | 14.8485 | 16.898 | 17.2955
NQ | 20012877 | ST-GI-1 | Stuart-Giru | ST-GI-1_Stuart-Giru 66 kV | Loading (A) | 13.8564 | 17.2666 | 15.896 | 13.8562 | 17.2684 | 15.8955 | 13.8324 | 17.1594 | 15.802 | 14.5462 | 18.0298 | 16.6189 | 14.5516 | 18.0382 | 16.6037
NQ | 20012877 | ST-GI-1 | Stuart-Giru | ST-GI-1_Stuart-Giru 66 kV | Power Factor | 0.99182 | 0.9909 | 0.99127 | 0.99182 | 0.9909 | 0.99127 | 0.99184 | 0.99096 | 0.99132 | 0.99165 | 0.99299 | 0.9911 | 0.99164 | 0.99299 | 0.99111
NQ | 20012877 | ST-GI-1 | Stuart-Giru | ST-GI-1_Stuart-Giru 66 kV | Rating (A) | 98 | 107 | 96 | 98 | 107 | 96 | 98 | 107 | 96 | 98 | 107 | 96 | 98 | 107 | 96
NQ | 20012878 | HP-OO | HERMIT PARK - OONOONBA | HP-OO_Hermit park - Oonoonba 66 kV
NQ | 20012878 | HP-OO | HERMIT PARK - OONOONBA | HP-OO_Hermit park - Oonoonba 66 kV | % of Rated A | 26.8532 | 26.5166 | 31.5257 | 27.3852 | 26.7377 | 31.735 | 25.7644 | 22.7701 | 27.2752 | 25.8652 | 22.9271 | 27.4653 | 25.6771 | 23.0587 | 27.8262
NQ | 20012878 | HP-OO | HERMIT PARK - OONOONBA | HP-OO_Hermit park - Oonoonba 66 kV | Loading (A) | 92.6435 | 93.8427 | 98.3399 | 94.4481 | 94.6254 | 98.9929 | 88.887 | 80.606 | 85.0764 | 89.2348 | 81.162 | 85.6697 | 88.5859 | 81.6276 | 86.7959
NQ | 20012878 | HP-OO | HERMIT PARK - OONOONBA | HP-OO_Hermit park - Oonoonba 66 kV | Power Factor | 0.22997 | 0.57911 | 0.76999 | 0.24609 | 0.58279 | 0.77124 | 0.063524 | 0.42503 | 0.71868 | 0.073057 | 0.39334 | 0.72123 | 0.084274 | 0.43646 | 0.72726
NQ | 20012878 | HP-OO | HERMIT PARK - OONOONBA | HP-OO_Hermit park - Oonoonba 66 kV | Rating (A) | 345 | 354 | 312 | 345 | 354 | 312 | 345 | 354 | 312 | 345 | 354 | 312 | 345 | 354 | 312
NQ | 20012879 | ST-RM-1 | Stuart-Rasmussen | ST-RM-1_Stuart-Rasmussen 66 kV
NQ | 20012879 | ST-RM-1 | Stuart-Rasmussen | ST-RM-1_Stuart-Rasmussen 66 kV | % of Rated A | 9.9394 | 10.611 | 8.3917 | 9.9762 | 10.666 | 8.3843 | 11.1685 | 11.6923 | 8.4733 | 11.2302 | 11.7964 | 8.5245 | 11.0013 | 11.9042 | 8.5768
NQ | 20012879 | ST-RM-1 | Stuart-Rasmussen | ST-RM-1_Stuart-Rasmussen 66 kV | Loading (A) | 54.7664 | 61.7563 | 43.9725 | 54.9686 | 62.0759 | 43.9339 | 61.5383 | 68.049 | 44.4002 | 61.8782 | 68.6548 | 44.6683 | 60.6173 | 69.2823 | 44.9422
NQ | 20012879 | ST-RM-1 | Stuart-Rasmussen | ST-RM-1_Stuart-Rasmussen 66 kV | Power Factor | 0.75033 | 0.83625 | 0.22092 | 0.75392 | 0.83956 | 0.21798 | 0.69639 | 0.89999 | 0.63163 | 0.70102 | 0.90303 | 0.63854 | 0.84746 | 0.90412 | 0.65313
NQ | 20012879 | ST-RM-1 | Stuart-Rasmussen | ST-RM-1_Stuart-Rasmussen 66 kV | Rating (A) | 551 | 582 | 524 | 551 | 582 | 524 | 551 | 582 | 524 | 551 | 582 | 524 | 551 | 582 | 524
NQ | 20012880 | ST-RP-1 | Stuart-RossPlains | ST-RP-1_Stuart-Ross Plains 66 kV
NQ | 20012880 | ST-RP-1 | Stuart-RossPlains | ST-RP-1_Stuart-Ross Plains 66 kV | % of Rated A | 18.4466 | 19.5734 | 12.3417 | 18.5317 | 19.6834 | 12.4174 | 20.3265 | 21.5306 | 14.7935 | 20.4407 | 21.6673 | 14.8717 | 20.4873 | 21.7646 | 14.9643
NQ | 20012880 | ST-RP-1 | Stuart-RossPlains | ST-RP-1_Stuart-Ross Plains 66 kV | Loading (A) | 125.2525 | 142.8856 | 81.8257 | 125.8299 | 143.6889 | 82.3275 | 138.0167 | 157.1734 | 98.0811 | 138.7925 | 158.171 | 98.5994 | 139.1091 | 158.8814 | 99.2136
NQ | 20012880 | ST-RP-1 | Stuart-RossPlains | ST-RP-1_Stuart-Ross Plains 66 kV | Power Factor | 0.90792 | 0.94461 | 0.88825 | 0.90995 | 0.94623 | 0.89136 | 0.94645 | 0.96894 | 0.84779 | 0.94771 | 0.96998 | 0.85056 | 0.94694 | 0.96989 | 0.85622
NQ | 20012880 | ST-RP-1 | Stuart-RossPlains | ST-RP-1_Stuart-Ross Plains 66 kV | Rating (A) | 679 | 730 | 663 | 679 | 730 | 663 | 679 | 730 | 663 | 679 | 730 | 663 | 679 | 730 | 663
NQ | 20012881 | ST-TOPO-1 | Stuart-TOPO | ST-TOPO-1_Stuart-Townsville Port 66 kV
NQ | 20012881 | ST-TOPO-1 | Stuart-TOPO | ST-TOPO-1_Stuart-Townsville Port 66 kV | % of Rated A | 27.729 | 21.283 | 23.4035 | 28.1994 | 21.7229 | 23.7821 | 28.0182 | 20.9531 | 22.7589 | 28.0033 | 19.5126 | 22.7424 | 27.9748 | 19.853 | 22.7239
NQ | 20012881 | ST-TOPO-1 | Stuart-TOPO | ST-TOPO-1_Stuart-Townsville Port 66 kV | Loading (A) | 69.5997 | 66.8286 | 65.9978 | 70.7804 | 68.2099 | 67.0656 | 70.3256 | 65.7927 | 64.1801 | 70.2884 | 61.2696 | 64.1335 | 70.2167 | 62.3385 | 64.0815
NQ | 20012881 | ST-TOPO-1 | Stuart-TOPO | ST-TOPO-1_Stuart-Townsville Port 66 kV | Power Factor | 0.13137 | 0.015589 | 0.35674 | 0.11596 | 0.029237 | 0.36078 | 0.30641 | 0.20928 | 0.34774 | 0.30107 | 0.091002 | 0.3406 | 0.29572 | 0.086964 | 0.3341
NQ | 20012881 | ST-TOPO-1 | Stuart-TOPO | ST-TOPO-1_Stuart-Townsville Port 66 kV | Rating (A) | 251 | 314 | 282 | 251 | 314 | 282 | 251 | 314 | 282 | 251 | 314 | 282 | 251 | 314 | 282
NQ | 20012883 | ST-WO-1 | STUA-WOSO | ST-WO-1_Stuart-Woodstock South 1 66 kV
NQ | 20012883 | ST-WO-1 | STUA-WOSO | ST-WO-1_Stuart-Woodstock South 1 66 kV | % of Rated A | 14.8211 | 33.0887 | 29.4904 | 15.8938 | 33.0072 | 29.4265 | 18.8576 | 34.5228 | 31.1283 | 16.8017 | 34.5741 | 30.9513 | 16.6425 | 34.4545 | 30.5463
NQ | 20012883 | ST-WO-1 | STUA-WOSO | ST-WO-1_Stuart-Woodstock South 1 66 kV | Loading (A) | 19.5639 | 55.2581 | 46.8897 | 20.9798 | 55.1221 | 46.7881 | 24.8921 | 57.6531 | 49.494 | 22.1783 | 57.7387 | 49.2125 | 21.968 | 57.539 | 48.5687
NQ | 20012883 | ST-WO-1 | STUA-WOSO | ST-WO-1_Stuart-Woodstock South 1 66 kV | Power Factor | 0.93916 | 0.93346 | 0.94588 | 0.9209 | 0.93353 | 0.94602 | 0.93711 | 0.92482 | 0.95696 | 0.93961 | 0.9306 | 0.95705 | 0.95163 | 0.93081 | 0.95126
NQ | 20012883 | ST-WO-1 | STUA-WOSO | ST-WO-1_Stuart-Woodstock South 1 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
NQ | 20012969 | TP-NS-1 | TP-NeilSmith | TP-NS-1_Townsville Port-NESM No 1 66 kV
NQ | 20012969 | TP-NS-1 | TP-NeilSmith | TP-NS-1_Townsville Port-NESM No 1 66 kV | % of Rated A | 26.9302 | 22.8537 | 21.5777 | 26.9198 | 22.8481 | 21.5711 | 26.8464 | 22.8706 | 21.5156 | 27.021 | 23.0251 | 21.6519 | 27.1284 | 23.0335 | 21.6558
NQ | 20012969 | TP-NS-1 | TP-NeilSmith | TP-NS-1_Townsville Port-NESM No 1 66 kV | Loading (A) | 69.4793 | 67.4179 | 58.6909 | 69.4525 | 67.4014 | 58.673 | 69.2632 | 67.4677 | 58.5219 | 69.7137 | 67.9236 | 58.8927 | 69.9907 | 67.9482 | 58.9033
NQ | 20012969 | TP-NS-1 | TP-NeilSmith | TP-NS-1_Townsville Port-NESM No 1 66 kV | Power Factor | 0.99315 | 0.99369 | 0.99578 | 0.99316 | 0.9937 | 0.99579 | 0.99325 | 0.99367 | 0.99579 | 0.99314 | 0.99355 | 0.9957 | 0.99305 | 0.99353 | 0.99569
NQ | 20012969 | TP-NS-1 | TP-NeilSmith | TP-NS-1_Townsville Port-NESM No 1 66 kV | Rating (A) | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272
NQ | 20013599 | DG-CB-1 | DANGLEESON-CRANBROOK | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV
NQ | 20013599 | DG-CB-1 | DANGLEESON-CRANBROOK | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | % of Rated A | 74.8845 | 45.6485 | 41.988 | 74.7049 | 45.2813 | 41.7364 | 73.9949 | 45.1506 | 41.4172 | 73.9282 | 45.086 | 41.3897 | 73.8307 | 45.004 | 41.3527
NQ | 20013599 | DG-CB-1 | DANGLEESON-CRANBROOK | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Loading (A) | 187.9602 | 175.7467 | 159.5542 | 187.5092 | 174.3331 | 158.5984 | 185.7271 | 173.8299 | 157.3853 | 185.5598 | 173.5811 | 157.2807 | 185.3152 | 173.2652 | 157.1402
NQ | 20013599 | DG-CB-1 | DANGLEESON-CRANBROOK | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Power Factor | 0.97923 | 0.99484 | 0.97772 | 0.99674 | 0.9943 | 0.97664 | 0.97884 | 0.99671 | 0.9774 | 0.97884 | 0.9967 | 0.97738 | 0.97873 | 0.99665 | 0.97732
NQ | 20013599 | DG-CB-1 | DANGLEESON-CRANBROOK | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Rating (A) | 251 | 385 | 380 | 251 | 385 | 380 | 251 | 385 | 380 | 251 | 385 | 380 | 251 | 385 | 380
NQ | 20013608 | GI-AY-1 | GIRU-AYR | GI-AY-1_Giru - Ayr 1 66 kV
NQ | 20013608 | GI-AY-1 | GIRU-AYR | GI-AY-1_Giru - Ayr 1 66 kV | % of Rated A | 19.5698 | 18.6222 | 19.7384 | 19.5648 | 18.6201 | 19.7341 | 19.7414 | 18.7825 | 19.6692 | 20.1026 | 19.236 | 19.9868 | 19.8657 | 19.2348 | 19.9913
NQ | 20013608 | GI-AY-1 | GIRU-AYR | GI-AY-1_Giru - Ayr 1 66 kV | Loading (A) | 36.9869 | 38.3618 | 36.7134 | 36.9774 | 38.3574 | 36.7055 | 37.3112 | 38.6919 | 36.5847 | 37.9939 | 39.6261 | 37.1754 | 37.5462 | 39.6237 | 37.1839
NQ | 20013608 | GI-AY-1 | GIRU-AYR | GI-AY-1_Giru - Ayr 1 66 kV | Power Factor | 0.89788 | 0.90388 | 0.89653 | 0.89791 | 0.90389 | 0.89655 | 0.89892 | 0.90328 | 0.8969 | 0.89862 | 0.9027 | 0.8967 | 0.89963 | 0.90271 | 0.89667
NQ | 20013608 | GI-AY-1 | GIRU-AYR | GI-AY-1_Giru - Ayr 1 66 kV | Rating (A) | 189 | 206 | 186 | 189 | 206 | 186 | 189 | 206 | 186 | 189 | 206 | 186 | 189 | 206 | 186
NQ | 20013609 | IN-GR | INGHAM-BLACKRIVER/GREENVALE | IN-GR_Ingham-Black River/Greenvale 66 kV
NQ | 20013609 | IN-GR | INGHAM-BLACKRIVER/GREENVALE | IN-GR_Ingham-Black River/Greenvale 66 kV | % of Rated A | 22.6709 | 17.8721 | 19.1446 | 22.6747 | 17.8563 | 19.1467 | 22.6937 | 17.8936 | 19.1479 | 22.6918 | 17.8759 | 19.1463 | 22.6906 | 17.8511 | 19.1439
NQ | 20013609 | IN-GR | INGHAM-BLACKRIVER/GREENVALE | IN-GR_Ingham-Black River/Greenvale 66 kV | Loading (A) | 15.6429 | 15.5487 | 15.6986 | 15.6455 | 15.5349 | 15.7003 | 15.6587 | 15.5675 | 15.7013 | 15.6574 | 15.552 | 15.7 | 15.6565 | 15.5305 | 15.698
NQ | 20013609 | IN-GR | INGHAM-BLACKRIVER/GREENVALE | IN-GR_Ingham-Black River/Greenvale 66 kV | Power Factor | 0.13558 | 0.3116 | 0.12349 | 0.13553 | 0.25362 | 0.12346 | 0.13532 | 0.31085 | 0.10555 | 0.13534 | 0.32248 | 0.10557 | 0.13535 | 0.2874 | 0.10559
NQ | 20013609 | IN-GR | INGHAM-BLACKRIVER/GREENVALE | IN-GR_Ingham-Black River/Greenvale 66 kV | Rating (A) | 69 | 87 | 82 | 69 | 87 | 82 | 69 | 87 | 82 | 69 | 87 | 82 | 69 | 87 | 82
NQ | 20013610 | MR-CR-1 | MILLCHESTER-CAPERIVER | MR-CR-1_Millchester-Cape River 1 66 kV
NQ | 20013610 | MR-CR-1 | MILLCHESTER-CAPERIVER | MR-CR-1_Millchester-Cape River 1 66 kV | % of Rated A | 83.3597 | 49.9122 | 57.7886 | 83.367 | 49.9133 | 57.7881 | 83.0518 | 49.5225 | 57.9113 | 83.2384 | 50.0523 | 57.9793 | 83.4506 | 50.6407 | 58.2407
NQ | 20013610 | MR-CR-1 | MILLCHESTER-CAPERIVER | MR-CR-1_Millchester-Cape River 1 66 kV | Loading (A) | 129.2076 | 114.2989 | 130.6022 | 129.2189 | 114.3014 | 130.6011 | 128.7302 | 113.4066 | 130.8796 | 129.0196 | 114.6198 | 131.0331 | 129.3485 | 115.9673 | 131.624
NQ | 20013610 | MR-CR-1 | MILLCHESTER-CAPERIVER | MR-CR-1_Millchester-Cape River 1 66 kV | Power Factor | 0.87167 | 0.84613 | 0.8779 | 0.87155 | 0.84609 | 0.87786 | 0.87714 | 0.84478 | 0.88215 | 0.87762 | 0.8482 | 0.87662 | 0.87915 | 0.84712 | 0.87509
NQ | 20013610 | MR-CR-1 | MILLCHESTER-CAPERIVER | MR-CR-1_Millchester-Cape River 1 66 kV | Rating (A) | 155 | 229 | 226 | 155 | 229 | 226 | 155 | 229 | 226 | 155 | 229 | 226 | 155 | 229 | 226
NQ | 20013612 | WO-CT-1 | Woodstock-Charters Towers | WO-CT-1_Woodstock-CHTO No 1 66 kV
NQ | 20013612 | WO-CT-1 | Woodstock-Charters Towers | WO-CT-1_Woodstock-CHTO No 1 66 kV | % of Rated A | 10.4676 | 22.2982 | 22.2652 | 10.8166 | 22.2314 | 22.2065 | 11.6379 | 23.2177 | 23.3841 | 11.0862 | 23.2743 | 23.2176 | 10.8934 | 23.1677 | 23.0092
NQ | 20013612 | WO-CT-1 | Woodstock-Charters Towers | WO-CT-1_Woodstock-CHTO No 1 66 kV | Loading (A) | 18.737 | 42.1437 | 37.4055 | 19.3616 | 42.0173 | 37.3069 | 20.8319 | 43.8814 | 39.2853 | 19.8443 | 43.9884 | 39.0055 | 19.4992 | 43.787 | 38.6555
NQ | 20013612 | WO-CT-1 | Woodstock-Charters Towers | WO-CT-1_Woodstock-CHTO No 1 66 kV | Power Factor | 0.27726 | 0.94174 | 0.96094 | 0.56393 | 0.94209 | 0.9612 | 0.63718 | 0.90231 | 0.968 | 0.6257 | 0.91128 | 0.96833 | 0.20346 | 0.91167 | 0.96366
NQ | 20013612 | WO-CT-1 | Woodstock-Charters Towers | WO-CT-1_Woodstock-CHTO No 1 66 kV | Rating (A) | 179 | 189 | 168 | 179 | 189 | 168 | 179 | 189 | 168 | 179 | 189 | 168 | 179 | 189 | 168
NQ | 20013621 | MF-TP-2 | Max Fulton-TPSS No.02 | MF-TP-2_Max Fulton-TOPO No 2 66 kV
NQ | 20013621 | MF-TP-2 | Max Fulton-TPSS No.02 | MF-TP-2_Max Fulton-TOPO No 2 66 kV | % of Rated A | 27.9338 | 23.8023 | 23.8617 | 28.1692 | 24.0085 | 24.0849 | 28.1248 | 24.0189 | 24.0808 | 28.1305 | 24.0259 | 24.0835 | 28.3597 | 24.1785 | 24.0598
NQ | 20013621 | MF-TP-2 | Max Fulton-TPSS No.02 | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Loading (A) | 72.0693 | 70.2168 | 64.904 | 72.6767 | 70.8252 | 65.511 | 72.5619 | 70.8558 | 65.4998 | 72.5767 | 70.8763 | 65.5071 | 73.1679 | 71.3264 | 65.4425
NQ | 20013621 | MF-TP-2 | Max Fulton-TPSS No.02 | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Power Factor | 0.89403 | 0.8859 | 0.85833 | 0.88148 | 0.87332 | 0.84541 | 0.87997 | 0.87377 | 0.84516 | 0.88016 | 0.87407 | 0.84533 | 0.87713 | 0.86884 | 0.84454
NQ | 20013621 | MF-TP-2 | Max Fulton-TPSS No.02 | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Rating (A) | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272
NQ | 20013622 | ST-TS-1 | TownsvilleSouth-Stuart No.1 (607) | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV
NQ | 20013622 | ST-TS-1 | TownsvilleSouth-Stuart No.1 (607) | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | % of Rated A | 28.33 | 28.5996 | 21.6165 | 28.511 | 28.8057 | 21.7809 | 26.0376 | 26.4265 | 19.8192 | 26.3387 | 26.7725 | 20.0613 | 26.5669 | 27.0237 | 20.4909
NQ | 20013622 | ST-TS-1 | TownsvilleSouth-Stuart No.1 (607) | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Loading (A) | 260.9197 | 287.1403 | 198.4392 | 262.5862 | 289.2091 | 199.9484 | 239.8026 | 265.3185 | 181.9347 | 242.5753 | 268.7922 | 184.1573 | 244.6783 | 271.3148 | 188.1003
NQ | 20013622 | ST-TS-1 | TownsvilleSouth-Stuart No.1 (607) | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Power Factor | 0.97735 | 0.98032 | 0.96378 | 0.97783 | 0.98092 | 0.96447 | 0.95354 | 0.97205 | 0.92213 | 0.95609 | 0.96379 | 0.92609 | 0.97085 | 0.97521 | 0.90469
NQ | 20013622 | ST-TS-1 | TownsvilleSouth-Stuart No.1 (607) | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Rating (A) | 921 | 1003.9999 | 918 | 921 | 1003.9999 | 918 | 921 | 1003.9999 | 918 | 921 | 1003.9999 | 918 | 921 | 1003.9999 | 918
NQ | 20013640 | AY-EA-1 | AYR-EASTAYR | AY-EA-1_Ayr - East Ayr No 1 66 kV
NQ | 20013640 | AY-EA-1 | AYR-EASTAYR | AY-EA-1_Ayr - East Ayr No 1 66 kV | % of Rated A | 55.5927 | 44.3654 | 50.2566 | 55.5316 | 44.3934 | 50.2809 | 56.4796 | 44.8992 | 50.2787 | 56.4459 | 44.8411 | 50.2487 | 56.5793 | 44.9463 | 50.3407
NQ | 20013640 | AY-EA-1 | AYR-EASTAYR | AY-EA-1_Ayr - East Ayr No 1 66 kV | Loading (A) | 143.9852 | 131.3215 | 137.7031 | 143.8268 | 131.4046 | 137.7697 | 146.2822 | 132.9016 | 137.7636 | 146.1949 | 132.7296 | 137.6815 | 146.5405 | 133.0412 | 137.9334
NQ | 20013640 | AY-EA-1 | AYR-EASTAYR | AY-EA-1_Ayr - East Ayr No 1 66 kV | Power Factor | 0.98689 | 0.9842 | 0.98858 | 0.98947 | 0.98432 | 0.98867 | 0.98716 | 0.9825 | 0.98685 | 0.98702 | 0.98226 | 0.98673 | 0.98713 | 0.98239 | 0.98681
NQ | 20013640 | AY-EA-1 | AYR-EASTAYR | AY-EA-1_Ayr - East Ayr No 1 66 kV | Rating (A) | 259 | 296 | 274 | 259 | 296 | 274 | 259 | 296 | 274 | 259 | 296 | 274 | 259 | 296 | 274
NQ | 20013643 | ME-BN-1 | Merinda-Bowen | ME-BN-1_Merinda - Bowen No 1 66 kV
NQ | 20013643 | ME-BN-1 | Merinda-Bowen | ME-BN-1_Merinda - Bowen No 1 66 kV | % of Rated A | 53.712 | 53.5244 | 42.4568 | 54.0698 | 53.9062 | 42.6743 | 54.4663 | 54.3451 | 42.8988 | 54.8463 | 54.7312 | 43.1171 | 55.2555 | 55.1569 | 43.3621
NQ | 20013643 | ME-BN-1 | Merinda-Bowen | ME-BN-1_Merinda - Bowen No 1 66 kV | Loading (A) | 104.7385 | 116.6831 | 84.4891 | 105.4362 | 117.5154 | 84.9218 | 106.2092 | 118.4723 | 85.3686 | 106.9503 | 119.314 | 85.803 | 107.7483 | 120.242 | 86.2905
NQ | 20013643 | ME-BN-1 | Merinda-Bowen | ME-BN-1_Merinda - Bowen No 1 66 kV | Power Factor | 0.96811 | 0.98236 | 0.85316 | 0.96918 | 0.9831 | 0.85608 | 0.97055 | 0.98411 | 0.85979 | 0.97166 | 0.98485 | 0.86268 | 0.97279 | 0.98559 | 0.86586
NQ | 20013643 | ME-BN-1 | Merinda-Bowen | ME-BN-1_Merinda - Bowen No 1 66 kV | Rating (A) | 195 | 218 | 199 | 195 | 218 | 199 | 195 | 218 | 199 | 195 | 218 | 199 | 195 | 218 | 199
NQ | 20013651 | AV-GA-1 | GARBUTT-AITKENVALE | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV
NQ | 20013651 | AV-GA-1 | GARBUTT-AITKENVALE | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | % of Rated A | 37.026 | 35.1615 | 25.8717 | 36.9954 | 35.1395 | 25.862 | 36.7435 | 34.9094 | 25.057 | 36.8419 | 34.8182 | 25.1222 | 36.7401 | 34.9129 | 25.195
NQ | 20013651 | AV-GA-1 | GARBUTT-AITKENVALE | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Loading (A) | 170.3195 | 181.4324 | 122.6315 | 170.1786 | 181.3191 | 122.5856 | 169.0198 | 180.1317 | 118.7704 | 169.4726 | 179.6617 | 119.0794 | 169.0045 | 180.1504 | 119.4243
NQ | 20013651 | AV-GA-1 | GARBUTT-AITKENVALE | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Power Factor | 0.99997 | 0.99962 | 0.99992 | 0.99995 | 0.99957 | 0.99988 | 0.99999 | 0.99969 | 0.97606 | 0.99999 | 1 | 0.97631 | 0.99989 | 1 | 0.98389
NQ | 20013651 | AV-GA-1 | GARBUTT-AITKENVALE | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Rating (A) | 460 | 516 | 474 | 460 | 516 | 474 | 460 | 516 | 474 | 460 | 516 | 474 | 460 | 516 | 474
NQ | 20013655 | DG-RM-1 | DANGLEESON-RASMUSSEN | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV
NQ | 20013655 | DG-RM-1 | DANGLEESON-RASMUSSEN | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | % of Rated A | 52.008 | 39.0268 | 33.6203 | 52.1578 | 39.1265 | 33.7065 | 48.3465 | 36.6141 | 32.5915 | 48.7275 | 36.8941 | 32.8217 | 49.3381 | 37.0801 | 32.8976
NQ | 20013655 | DG-RM-1 | DANGLEESON-RASMUSSEN | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Loading (A) | 130.5401 | 150.2529 | 127.7572 | 130.9161 | 150.6368 | 128.0845 | 121.3495 | 140.9641 | 123.8475 | 122.3059 | 142.0421 | 124.7225 | 123.8386 | 142.7585 | 125.0106
NQ | 20013655 | DG-RM-1 | DANGLEESON-RASMUSSEN | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Power Factor | 0.97115 | 0.97404 | 0.99022 | 0.97123 | 0.97412 | 0.99024 | 0.97488 | 0.97753 | 0.97812 | 0.97486 | 0.9775 | 0.97809 | 0.9743 | 0.9775 | 0.97847
NQ | 20013655 | DG-RM-1 | DANGLEESON-RASMUSSEN | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Rating (A) | 251 | 385 | 380 | 251 | 385 | 380 | 251 | 385 | 380 | 251 | 385 | 380 | 251 | 385 | 380
NQ | 20013660 | MF-TP-1 | Max Fulton-TPSS No.01 | MF-TP-1_Max Fulton-TOPO No 1 66 kV
NQ | 20013660 | MF-TP-1 | Max Fulton-TPSS No.01 | MF-TP-1_Max Fulton-TOPO No 1 66 kV | % of Rated A | 25.0041 | 21.1094 | 20.4925 | 24.8198 | 20.959 | 20.3511 | 24.7379 | 20.9775 | 20.339 | 24.7485 | 20.9901 | 20.3453 | 24.865 | 20.9974 | 20.3063
NQ | 20013660 | MF-TP-1 | Max Fulton-TPSS No.01 | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Loading (A) | 64.5101 | 62.2723 | 55.7391 | 64.035 | 61.829 | 55.3551 | 63.8236 | 61.8836 | 55.3222 | 63.8511 | 61.9206 | 55.3392 | 64.1517 | 61.9423 | 55.2332
NQ | 20013660 | MF-TP-1 | Max Fulton-TPSS No.01 | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Power Factor | 0.99843 | 0.99856 | 0.99895 | 0.99994 | 0.99996 | 1 | 0.99995 | 0.99996 | 1 | 0.99995 | 0.99996 | 1 | 0.99994 | 0.99996 | 1
NQ | 20013660 | MF-TP-1 | Max Fulton-TPSS No.01 | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Rating (A) | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272
NQ | 20013662 | ST-TS-2 | TownsvilleSouth-Stuart No.2 (608) | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV
NQ | 20013662 | ST-TS-2 | TownsvilleSouth-Stuart No.2 (608) | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | % of Rated A | 28.7901 | 29.0641 | 21.9675 | 28.974 | 29.2735 | 22.1346 | 26.4605 | 26.8556 | 20.141 | 26.7664 | 27.2073 | 20.3871 | 26.9984 | 27.4625 | 20.8236
NQ | 20013662 | ST-TS-2 | TownsvilleSouth-Stuart No.2 (608) | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Loading (A) | 265.1571 | 291.8035 | 201.6619 | 266.8506 | 293.9059 | 203.1956 | 243.6972 | 269.6274 | 184.8896 | 246.5149 | 273.1576 | 187.1483 | 248.6521 | 275.724 | 191.1553
NQ | 20013662 | ST-TS-2 | TownsvilleSouth-Stuart No.2 (608) | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Power Factor | 0.97911 | 0.98196 | 0.966 | 0.97957 | 0.98253 | 0.96667 | 0.95605 | 0.97401 | 0.92537 | 0.95854 | 0.96602 | 0.92924 | 0.97284 | 0.97709 | 0.90826
NQ | 20013662 | ST-TS-2 | TownsvilleSouth-Stuart No.2 (608) | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Rating (A) | 921 | 1003.9999 | 918 | 921 | 1003.9999 | 918 | 921 | 1003.9999 | 918 | 921 | 1003.9999 | 918 | 921 | 1003.9999 | 918
NQ | 25267806 | DG-PA-1 | DANGLEESON-PETERARLETT | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV
NQ | 25267806 | DG-PA-1 | DANGLEESON-PETERARLETT | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | % of Rated A | 34.4513 | 37.5824 | 34.7289 | 36.0947 | 37.7304 | 34.8641 | 33.7918 | 34.9548 | 34.1267 | 33.9708 | 37.1947 | 34.2885 | 33.7539 | 37.2401 | 34.1505
NQ | 25267806 | DG-PA-1 | DANGLEESON-PETERARLETT | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Loading (A) | 189.8215 | 218.7246 | 181.9756 | 198.8758 | 219.5863 | 182.6843 | 186.1868 | 203.4322 | 178.819 | 187.1731 | 216.4676 | 179.6669 | 185.978 | 216.7318 | 178.944
NQ | 25267806 | DG-PA-1 | DANGLEESON-PETERARLETT | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Power Factor | 0.88602 | 0.906 | 0.94144 | 0.84636 | 0.90585 | 0.94136 | 0.84077 | 0.90954 | 0.90412 | 0.84062 | 0.87272 | 0.90388 | 0.84087 | 0.8724 | 0.90412
NQ | 25267806 | DG-PA-1 | DANGLEESON-PETERARLETT | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Rating (A) | 551 | 582 | 524 | 551 | 582 | 524 | 551 | 582 | 524 | 551 | 582 | 524 | 551 | 582 | 524
NQ | 25267807 | PA-RP-1 | PETERARLETT-ROSSPLAINS | PA-RP-1_Peter Arlett-Ross Plains 66 kV
NQ | 25267807 | PA-RP-1 | PETERARLETT-ROSSPLAINS | PA-RP-1_Peter Arlett-Ross Plains 66 kV | % of Rated A | 18.6134 | 18.9905 | 23.934 | 23.1371 | 18.7477 | 23.804 | 17.3568 | 8.7673 | 17.6156 | 17.2931 | 13.0743 | 17.5146 | 17.2596 | 12.9644 | 17.7766
NQ | 25267807 | PA-RP-1 | PETERARLETT-ROSSPLAINS | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Loading (A) | 48.0226 | 56.0218 | 65.1006 | 59.6937 | 55.3057 | 64.7469 | 44.7805 | 25.8635 | 47.9144 | 44.6163 | 38.5693 | 47.6398 | 44.5297 | 38.2451 | 48.3522
NQ | 25267807 | PA-RP-1 | PETERARLETT-ROSSPLAINS | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Power Factor | 0.5544 | 0.50432 | 0.73372 | 0.38372 | 0.49518 | 0.7317 | 0.0024045 | 0.43385 | 0.6032 | 0.018384 | 0.16822 | 0.59778 | 0.031158 | 0.14992 | 0.59919
NQ | 25267807 | PA-RP-1 | PETERARLETT-ROSSPLAINS | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Rating (A) | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272
NQ | 25273587 | RI-JC-1 | Richmond-Julia Creek No.1 66kV feeder | RI-JC-1_Richmond-Julia Creek No 1 66 kV
NQ | 25273587 | RI-JC-1 | Richmond-Julia Creek No.1 66kV feeder | RI-JC-1_Richmond-Julia Creek No 1 66 kV | % of Rated A | 7.5477 | 7.56 | 5.1245 | 7.5477 | 7.56 | 5.1245 | 7.551 | 7.5603 | 5.1259 | 7.5504 | 7.559 | 5.1257 | 7.3508 | 7.2876 | 5.0282
NQ | 25273587 | RI-JC-1 | Richmond-Julia Creek No.1 66kV feeder | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Loading (A) | 26.7945 | 29.3328 | 21.5229 | 26.7942 | 29.3328 | 21.5228 | 26.8059 | 29.3339 | 21.5288 | 26.8038 | 29.3288 | 21.5281 | 26.0954 | 28.2759 | 21.1184
NQ | 25273587 | RI-JC-1 | Richmond-Julia Creek No.1 66kV feeder | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Power Factor | 0.94826 | 0.9624 | 0.85815 | 0.94825 | 0.9624 | 0.85814 | 0.94857 | 0.96239 | 0.85934 | 0.94851 | 0.9624 | 0.8592 | 0.94034 | 0.96276 | 0.84445
NQ | 25273587 | RI-JC-1 | Richmond-Julia Creek No.1 66kV feeder | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Rating (A) | 355 | 388 | 420 | 355 | 388 | 420 | 355 | 388 | 420 | 355 | 388 | 420 | 355 | 388 | 420
NQ | 25275522 | 6266 | BOHLE-BLACK RIVER 2 | 6266_Bohle-Black River No 2 66 kV
NQ | 25275522 | 6266 | BOHLE-BLACK RIVER 2 | 6266_Bohle-Black River No 2 66 kV | % of Rated A | 43.2777 | 32.9511 | 44.2076 | 43.1664 | 32.7081 | 44.0918 | 42.8875 | 32.5 | 43.8091 | 42.8032 | 32.2738 | 43.7193 | 42.7305 | 32.0881 | 43.6411
NQ | 25275522 | 6266 | BOHLE-BLACK RIVER 2 | 6266_Bohle-Black River No 2 66 kV | Loading (A) | 315.4945 | 258.0022 | 313.8742 | 314.6828 | 256.0992 | 313.0521 | 312.6501 | 254.47 | 311.0447 | 312.0356 | 252.6992 | 310.4067 | 311.5055 | 251.2448 | 309.8521
NQ | 25275522 | 6266 | BOHLE-BLACK RIVER 2 | 6266_Bohle-Black River No 2 66 kV | Power Factor | 0.97598 | 0.94467 | 0.97572 | 0.97576 | 0.94292 | 0.97548 | 0.97576 | 0.94096 | 0.97546 | 0.9755 | 0.93918 | 0.97519 | 0.97528 | 0.9374 | 0.97495
NQ | 25275522 | 6266 | BOHLE-BLACK RIVER 2 | 6266_Bohle-Black River No 2 66 kV | Rating (A) | 729 | 783 | 710 | 729 | 783 | 710 | 729 | 783 | 710 | 729 | 783 | 710 | 729 | 783 | 710
NQ | 25275871 | KA-AY-01 | AYR-KALAMIA | KA-AY-01_Ayr - Kalamia No 1 66 kV
NQ | 25275871 | KA-AY-01 | AYR-KALAMIA | KA-AY-01_Ayr - Kalamia No 1 66 kV | % of Rated A | 9.2124 | 5.1119 | 5.7428 | 9.2098 | 5.1111 | 5.7392 | 9.4038 | 5.149 | 5.729 | 9.2896 | 5.151 | 5.728 | 9.4015 | 5.1553 | 5.7288
NQ | 25275871 | KA-AY-01 | AYR-KALAMIA | KA-AY-01_Ayr - Kalamia No 1 66 kV | Loading (A) | 18.3328 | 11.3995 | 11.7153 | 18.3274 | 11.3978 | 11.708 | 18.7136 | 11.4822 | 11.6871 | 18.4863 | 11.4867 | 11.6852 | 18.7089 | 11.4963 | 11.6867
NQ | 25275871 | KA-AY-01 | AYR-KALAMIA | KA-AY-01_Ayr - Kalamia No 1 66 kV | Power Factor | 0.52868 | 0.058823 | 0.1449 | 0.52862 | 0.058508 | 0.14476 | 0.52956 | 0.06194 | 0.14775 | 0.5296 | 0.061215 | 0.14733 | 0.52913 | 0.06058 | 0.14697
NQ | 25275871 | KA-AY-01 | AYR-KALAMIA | KA-AY-01_Ayr - Kalamia No 1 66 kV | Rating (A) | 199 | 223 | 204 | 199 | 223 | 204 | 199 | 223 | 204 | 199 | 223 | 204 | 199 | 223 | 204
NQ | 25279916 | BC-IN-1 | Black River - Ingham | BC-IN-1_Black River - Ingham No 1 66 kV
NQ | 25279916 | BC-IN-1 | Black River - Ingham | BC-IN-1_Black River - Ingham No 1 66 kV | % of Rated A | 23.6449 | 28.2416 | 21.7653 | 24.0058 | 28.6835 | 22.0728 | 23.9355 | 28.6456 | 21.9523 | 23.9555 | 28.6326 | 21.9662 | 24.0129 | 28.7001 | 21.945
NQ | 25279916 | BC-IN-1 | Black River - Ingham | BC-IN-1_Black River - Ingham No 1 66 kV | Loading (A) | 44.686 | 58.1741 | 40.4809 | 45.3681 | 59.0845 | 41.0528 | 45.2353 | 59.0065 | 40.8286 | 45.273 | 58.9797 | 40.8544 | 45.3815 | 59.1186 | 40.815
NQ | 25279916 | BC-IN-1 | Black River - Ingham | BC-IN-1_Black River - Ingham No 1 66 kV | Power Factor | 0.99281 | 0.98852 | 0.99371 | 0.99262 | 0.98828 | 0.99356 | 0.9927 | 0.98833 | 0.99368 | 0.99268 | 0.98834 | 0.99366 | 0.99261 | 0.98826 | 0.99369
NQ | 25279916 | BC-IN-1 | Black River - Ingham | BC-IN-1_Black River - Ingham No 1 66 kV | Rating (A) | 189 | 206 | 186 | 189 | 206 | 186 | 189 | 206 | 186 | 189 | 206 | 186 | 189 | 206 | 186
NQ | 82903972 | 7307 | King Creek - Blue Valley 132 kV | 7307_King Creek - Blue Valley 132 kV
NQ | 82903972 | 7307 | King Creek - Blue Valley 132 kV | 7307_King Creek - Blue Valley 132 kV | % of Rated A | 2.7531 | 2.598 | 2.915 | 2.753 | 2.598 | 2.915 | 2.7496 | 2.5961 | 2.9115 | 2.7514 | 2.5957 | 2.9118 | 2.7517 | 2.5961 | 2.912
NQ | 82903972 | 7307 | King Creek - Blue Valley 132 kV | 7307_King Creek - Blue Valley 132 kV | Loading (A) | 12.4442 | 12.3667 | 12.4472 | 12.4435 | 12.3665 | 12.4468 | 12.4284 | 12.3576 | 12.4321 | 12.4364 | 12.3555 | 12.4334 | 12.4376 | 12.3575 | 12.4344
NQ | 82903972 | 7307 | King Creek - Blue Valley 132 kV | 7307_King Creek - Blue Valley 132 kV | Power Factor | 0.95678 | 0.95682 | 0.95679 | 0.95679 | 0.95682 | 0.95679 | 0.95679 | 0.95681 | 0.9568 | 0.95679 | 0.95681 | 0.9568 | 0.95678 | 0.95681 | 0.9568
NQ | 82903972 | 7307 | King Creek - Blue Valley 132 kV | 7307_King Creek - Blue Valley 132 kV | Rating (A) | 452 | 476 | 427 | 452 | 476 | 427 | 452 | 476 | 427 | 452 | 476 | 427 | 452 | 476 | 427
NQ | 82908830 | 7308 | Stony Creek - Havilah 132 kV | 7308_Stony Creek - Havilah 132 kV
NQ | 82908830 | 7308 | Stony Creek - Havilah 132 kV | 7308_Stony Creek - Havilah 132 kV | % of Rated A | 1.5855 | 1.5979 | 1.6554 | 1.5853 | 1.5979 | 1.6554 | 1.5845 | 1.597 | 1.6549 | 1.5846 | 1.597 | 1.6549 | 1.5847 | 1.5971 | 1.655
NQ | 82908830 | 7308 | Stony Creek - Havilah 132 kV | 7308_Stony Creek - Havilah 132 kV | Loading (A) | 6.9287 | 7.1268 | 6.4725 | 6.9277 | 7.1268 | 6.4725 | 6.9244 | 7.1226 | 6.4707 | 6.9248 | 7.1226 | 6.4708 | 6.925 | 7.123 | 6.471
NQ | 82908830 | 7308 | Stony Creek - Havilah 132 kV | 7308_Stony Creek - Havilah 132 kV | Power Factor | 0.95149 | 0.95718 | 0.93667 | 0.95142 | 0.95718 | 0.93667 | 0.95116 | 0.9569 | 0.93646 | 0.95119 | 0.9569 | 0.93648 | 0.95121 | 0.95693 | 0.9365
NQ | 82908830 | 7308 | Stony Creek - Havilah 132 kV | 7308_Stony Creek - Havilah 132 kV | Rating (A) | 437 | 446 | 391 | 437 | 446 | 391 | 437 | 446 | 391 | 437 | 446 | 391 | 437 | 446 | 391
NQ | 82908833 | 7309 | Stony Creek - Fig Tree 132 kV | 7309_Stony Creek - Fig Tree 132 kV
NQ | 82908833 | 7309 | Stony Creek - Fig Tree 132 kV | 7309_Stony Creek - Fig Tree 132 kV | % of Rated A | 1.2246 | 1.1639 | 1.3103 | 1.2247 | 1.1639 | 1.3103 | 1.2253 | 1.1639 | 1.3102 | 1.2248 | 1.1639 | 1.3102 | 1.2248 | 1.1639 | 1.3102
NQ | 82908833 | 7309 | Stony Creek - Fig Tree 132 kV | 7309_Stony Creek - Fig Tree 132 kV | Loading (A) | 5.5353 | 5.54 | 5.5949 | 5.5358 | 5.54 | 5.5949 | 5.5385 | 5.5402 | 5.5945 | 5.536 | 5.5401 | 5.5946 | 5.536 | 5.5402 | 5.5945
NQ | 82908833 | 7309 | Stony Creek - Fig Tree 132 kV | 7309_Stony Creek - Fig Tree 132 kV | Power Factor | 0.80037 | 0.80179 | 0.80887 | 0.80002 | 0.80178 | 0.80886 | 0.80362 | 0.80201 | 0.8085 | 0.79985 | 0.80196 | 0.80852 | 0.79989 | 0.80202 | 0.80844
NQ | 82908833 | 7309 | Stony Creek - Fig Tree 132 kV | 7309_Stony Creek - Fig Tree 132 kV | Rating (A) | 452 | 476 | 427 | 452 | 476 | 427 | 452 | 476 | 427 | 452 | 476 | 427 | 452 | 476 | 427
NQ | 82912295 | BEGA 2 | GARBUTT-BELGIANGARDENS NO.02 | BEGA 2_Garbutt-Belgian Gardens No2 66 kV
NQ | 82912295 | BEGA 2 | GARBUTT-BELGIANGARDENS NO.02 | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | % of Rated A | 7.3131 | 8.6204 | 6.7172 | 7.353 | 8.6707 | 6.7527 | 7.4169 | 8.762 | 6.8089 | 7.4603 | 8.8032 | 6.8467 | 7.5554 | 8.92 | 6.9114
NQ | 82912295 | BEGA 2 | GARBUTT-BELGIANGARDENS NO.02 | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | Loading (A) | 58.0664 | 68.4463 | 53.3343 | 58.3828 | 68.8452 | 53.6167 | 58.8905 | 69.5704 | 54.0625 | 59.2348 | 69.8972 | 54.3631 | 59.9899 | 70.8245 | 54.8764
NQ | 82912295 | BEGA 2 | GARBUTT-BELGIANGARDENS NO.02 | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | Power Factor | 0.97374 | 0.98764 | 0.96344 | 0.97431 | 0.98801 | 0.96415 | 0.97491 | 0.98859 | 0.96484 | 0.97556 | 0.9888 | 0.96562 | 0.97705 | 0.98969 | 0.96665
NQ | 82912295 | BEGA 2 | GARBUTT-BELGIANGARDENS NO.02 | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | Rating (A) | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794
NQ | 82912298 | BEGA 1 | GARBUTT-BELGIANGARDENS NO.01 | BEGA 1_Garbutt-Belgian Gardens No1 66 kV
NQ | 82912298 | BEGA 1 | GARBUTT-BELGIANGARDENS NO.01 | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | % of Rated A | 7.3195 | 8.6262 | 6.724 | 7.3593 | 8.6764 | 6.7595 | 7.4233 | 8.7678 | 6.8156 | 7.4666 | 8.8089 | 6.8535 | 7.5616 | 8.9256 | 6.9181
NQ | 82912298 | BEGA 1 | GARBUTT-BELGIANGARDENS NO.01 | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | Loading (A) | 58.1171 | 68.4922 | 53.3882 | 58.4332 | 68.8909 | 53.6704 | 58.9409 | 69.616 | 54.1162 | 59.285 | 69.9427 | 54.4165 | 60.0395 | 70.8696 | 54.9296
NQ | 82912298 | BEGA 1 | GARBUTT-BELGIANGARDENS NO.01 | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | Power Factor | 0.97331 | 0.9874 | 0.96289 | 0.97388 | 0.98778 | 0.9636 | 0.9745 | 0.98836 | 0.9643 | 0.97516 | 0.98858 | 0.96509 | 0.97667 | 0.98948 | 0.96614
NQ | 82912298 | BEGA 1 | GARBUTT-BELGIANGARDENS NO.01 | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | Rating (A) | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794
NQ | 83878913 | 6299 | TOPO FDR | 6299_Townsville Port 66 kV
NQ | 83878913 | 6299 | TOPO FDR | 6299_Townsville Port 66 kV | % of Rated A | 24.2604 | 22.4116 | 17.3322 | 24.3509 | 22.532 | 17.4097 | 23.3252 | 21.3912 | 15.4694 | 23.5395 | 21.8415 | 15.6089 | 22.6838 | 21.7492 | 16.4084
NQ | 83878913 | 6299 | TOPO FDR | 6299_Townsville Port 66 kV | Loading (A) | 264.922 | 270.0581 | 191.8647 | 265.9104 | 271.5094 | 192.7226 | 254.7098 | 257.7624 | 171.2429 | 257.0498 | 263.1886 | 172.7868 | 247.707 | 262.076 | 181.6385
NQ | 83878913 | 6299 | TOPO FDR | 6299_Townsville Port 66 kV | Power Factor | 0.98645 | 0.99041 | 0.97318 | 0.98754 | 0.99121 | 0.97538 | 0.98802 | 0.98996 | 0.96197 | 0.98794 | 0.99148 | 0.96223 | 0.99978 | 0.99135 | 0.9845
NQ | 83878913 | 6299 | TOPO FDR | 6299_Townsville Port 66 kV | Rating (A) | 1092 | 1205 | 1107 | 1092 | 1205 | 1107 | 1092 | 1205 | 1107 | 1092 | 1205 | 1107 | 1092 | 1205 | 1107
NQ | 83969140 | 6312 | MERINDA-HOMEHILL | 6312_Merinda - Home Hill 66 kV
NQ | 83969140 | 6312 | MERINDA-HOMEHILL | 6312_Merinda - Home Hill 66 kV | % of Rated A | 4.2651 | 3.5765 | 3.7668 | 4.2668 | 3.5766 | 3.7379 | 4.2726 | 3.5679 | 3.7478 | 4.2685 | 3.567 | 3.7469 | 4.2685 | 3.5667 | 3.7463
NQ | 83969140 | 6312 | MERINDA-HOMEHILL | 6312_Merinda - Home Hill 66 kV | Loading (A) | 11.0039 | 10.2645 | 9.8691 | 11.0083 | 10.2649 | 9.7932 | 11.0234 | 10.2399 | 9.8192 | 11.0127 | 10.2374 | 9.8169 | 11.0128 | 10.2363 | 9.8152
NQ | 83969140 | 6312 | MERINDA-HOMEHILL | 6312_Merinda - Home Hill 66 kV | Power Factor | 0.88396 | 0.80117 | 0.32148 | 0.89164 | 0.80105 | 0.34242 | 0.89932 | 0.80993 | 0.34071 | 0.88933 | 0.81083 | 0.34086 | 0.88937 | 0.8112 | 0.34097
NQ | 83969140 | 6312 | MERINDA-HOMEHILL | 6312_Merinda - Home Hill 66 kV | Rating (A) | 258 | 287 | 262 | 258 | 287 | 262 | 258 | 287 | 262 | 258 | 287 | 262 | 258 | 287 | 262
NQ | 84212381 | 6321 | 66kV LUCINDA FDR | 6321_Lucinda 66 kV
NQ | 84212381 | 6321 | 66kV LUCINDA FDR | 6321_Lucinda 66 kV | % of Rated A | 24.4592 | 27.2454 | 24.0365 | 24.1097 | 26.8382 | 23.7128 | 24.095 | 26.6917 | 23.7035 | 24.0977 | 27.0377 | 23.7051 | 24.0983 | 27.0447 | 23.7037
NQ | 84212381 | 6321 | 66kV LUCINDA FDR | 6321_Lucinda 66 kV | Loading (A) | 48.6738 | 60.7364 | 49.0345 | 47.9783 | 59.8283 | 48.3741 | 47.9491 | 59.5016 | 48.3552 | 47.9543 | 60.2734 | 48.3585 | 47.9557 | 60.2891 | 48.3555
NQ | 84212381 | 6321 | 66kV LUCINDA FDR | 6321_Lucinda 66 kV | Power Factor | 0.90138 | 0.9065 | 0.89761 | 0.90085 | 0.90618 | 0.89702 | 0.90078 | 0.90653 | 0.89711 | 0.90076 | 0.90626 | 0.89709 | 0.90092 | 0.90623 | 0.89708
NQ | 84212381 | 6321 | 66kV LUCINDA FDR | 6321_Lucinda 66 kV | Rating (A) | 199 | 223 | 204 | 199 | 223 | 204 | 199 | 223 | 204 | 199 | 223 | 204 | 199 | 223 | 204
NQ | 84253050 | 6325 | OONOONBA-STUART | 6325_Oonoonba-Stuart 66 kV
NQ | 84253050 | 6325 | OONOONBA-STUART | 6325_Oonoonba-Stuart 66 kV | % of Rated A | 34.3161 | 33.3266 | 22.5993 | 34.4406 | 33.4741 | 22.6406 | 38.9525 | 37.9496 | 26.0516 | 39.2751 | 38.2439 | 26.2159 | 39.6051 | 38.629 | 26.3901
NQ | 84253050 | 6325 | OONOONBA-STUART | 6325_Oonoonba-Stuart 66 kV | Loading (A) | 111.5274 | 110.6445 | 66.2159 | 111.932 | 111.1341 | 66.3369 | 126.5957 | 125.9926 | 76.3311 | 127.6442 | 126.9697 | 76.8126 | 128.7167 | 128.2482 | 77.323
NQ | 84253050 | 6325 | OONOONBA-STUART | 6325_Oonoonba-Stuart 66 kV | Power Factor | 0.87905 | 0.87395 | 0.69836 | 0.87943 | 0.87476 | 0.69679 | 0.85032 | 0.93301 | 0.82017 | 0.92599 | 0.9336 | 0.8232 | 0.93727 | 0.93566 | 0.82642
NQ | 84253050 | 6325 | OONOONBA-STUART | 6325_Oonoonba-Stuart 66 kV | Rating (A) | 325 | 332 | 293 | 325 | 332 | 293 | 325 | 332 | 293 | 325 | 332 | 293 | 325 | 332 | 293
NQ | 84431571 | MICC-MICB 1 | MICA CREEK 'C' TO MICA CREEK 'B' 1 | MICC-MICB No 1 132 kV
NQ | 84431571 | MICC-MICB 1 | MICA CREEK 'C' TO MICA CREEK 'B' 1 | MICC-MICB No 1 132 kV | % of Rated A | 20.5373 | 13.8658 | 14.4484 | 20.574 | 13.8895 | 14.4728 | 20.5787 | 13.8929 | 14.4745 | 20.6692 | 13.9511 | 14.5381 | 20.6692 | 13.9511 | 14.5381
NQ | 84431571 | MICC-MICB 1 | MICA CREEK 'C' TO MICA CREEK 'B' 1 | MICC-MICB No 1 132 kV | Loading (A) | 107.2047 | 99.6954 | 104.0286 | 107.3965 | 99.8653 | 104.204 | 107.4207 | 99.8898 | 104.2161 | 107.8932 | 100.3084 | 104.6744 | 107.8932 | 100.3084 | 104.6744
NQ | 84431571 | MICC-MICB 1 | MICA CREEK 'C' TO MICA CREEK 'B' 1 | MICC-MICB No 1 132 kV | Power Factor | 0.99516 | 0.98922 | 0.99329 | 0.99526 | 0.98937 | 0.9934 | 0.99527 | 0.98939 | 0.99341 | 0.99554 | 0.9898 | 0.99373 | 0.99554 | 0.9898 | 0.99373
NQ | 84431571 | MICC-MICB 1 | MICA CREEK 'C' TO MICA CREEK 'B' 1 | MICC-MICB No 1 132 kV | Rating (A) | 522 | 719 | 720 | 522 | 719 | 720 | 522 | 719 | 720 | 522 | 719 | 720 | 522 | 719 | 720
NQ | 84431576 | MICC-MICB 2 | MICA CREEK 'C' TO MICA CREEK 'B' 2 | MICC-MICB No 2 132 kV
NQ | 84431576 | MICC-MICB 2 | MICA CREEK 'C' TO MICA CREEK 'B' 2 | MICC-MICB No 2 132 kV | % of Rated A | 20.6089 | 13.9141 | 14.4988 | 20.6458 | 13.9379 | 14.5232 | 20.6504 | 13.9413 | 14.5249 | 20.7412 | 13.9997 | 14.5888 | 20.7412 | 13.9997 | 14.5888
NQ | 84431576 | MICC-MICB 2 | MICA CREEK 'C' TO MICA CREEK 'B' 2 | MICC-MICB No 2 132 kV | Loading (A) | 107.5783 | 100.0426 | 104.3911 | 107.7708 | 100.2132 | 104.5671 | 107.7951 | 100.2377 | 104.5793 | 108.2692 | 100.6578 | 105.0391 | 108.2692 | 100.6578 | 105.0391
NQ | 84431576 | MICC-MICB 2 | MICA CREEK 'C' TO MICA CREEK 'B' 2 | MICC-MICB No 2 132 kV | Power Factor | 0.99517 | 0.98923 | 0.9933 | 0.99527 | 0.98938 | 0.99341 | 0.99527 | 0.98939 | 0.99341 | 0.99554 | 0.9898 | 0.99373 | 0.99554 | 0.9898 | 0.99373
NQ | 84431576 | MICC-MICB 2 | MICA CREEK 'C' TO MICA CREEK 'B' 2 | MICC-MICB No 2 132 kV | Rating (A) | 522 | 719 | 720 | 522 | 719 | 720 | 522 | 719 | 720 | 522 | 719 | 720 | 522 | 719 | 720
NQ | 111543431 | 6382 | JACR - HUGH FDR 6382 | 6382 JACR-HUGH 132kV
NQ | 111543431 | 6382 | JACR - HUGH FDR 6382 | 6382 JACR-HUGH 132kV | % of Rated A | 77.9008 | 72.3176 | 75.1006 | 75.0468 | 72.3282 | 75.1114 | 75.1499 | 75.0263 | 74.1605 | 75.1801 | 74.6218 | 75.6663 | 75.7507 | 74.7801 | 75.5508
NQ | 111543431 | 6382 | JACR - HUGH FDR 6382 | 6382 JACR-HUGH 132kV | Loading (A) | 90.365 | 83.8884 | 87.1167 | 87.0543 | 83.9007 | 87.1292 | 87.1738 | 85.6302 | 86.0262 | 87.2089 | 85.1488 | 87.7729 | 87.8708 | 86.7449 | 87.6389
NQ | 111543431 | 6382 | JACR - HUGH FDR 6382 | 6382 JACR-HUGH 132kV | Power Factor | 0.073875 | 0.02888 | 0.21673 | 0.089825 | 0.028867 | 0.2167 | 0.13587 | 0.85224 | 0.22804 | 0.14127 | 0.84953 | 0.21897 | 0.055289 | 0.46864 | 0.22271
NQ | 111543431 | 6382 | JACR - HUGH FDR 6382 | 6382 JACR-HUGH 132kV | Rating (A) | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116
NQ | 111675890 | 7460 | CPRE-JACR FDR | 6383 CARI-CPRE 66kV
NQ | 111675890 | 7460 | CPRE-JACR FDR | 6383 CARI-CPRE 66kV | % of Rated A | 54.2268 | 43.1836 | 51.8468 | 54.2338 | 43.1856 | 51.8485 | 53.7057 | 42.4332 | 51.8605 | 54.1594 | 43.2406 | 52.0168 | 54.2253 | 43.2435 | 52.2736
NQ | 111675890 | 7460 | CPRE-JACR FDR | 6383 CARI-CPRE 66kV | Loading (A) | 169.18 | 154.5893 | 170.5684 | 169.2018 | 154.5964 | 170.5741 | 167.5541 | 151.9109 | 170.6136 | 168.9698 | 154.7933 | 171.1276 | 169.1753 | 154.8039 | 171.9725
NQ | 111675890 | 7460 | CPRE-JACR FDR | 6383 CARI-CPRE 66kV | Power Factor | 0.74068 | 0.70574 | 0.75079 | 0.74054 | 0.7057 | 0.75075 | 0.73137 | 0.72415 | 0.75647 | 0.73977 | 0.70904 | 0.74945 | 0.74126 | 0.7266 | 0.74753
NQ | 111675890 | 7460 | CPRE-JACR FDR | 6383 CARI-CPRE 66kV | Rating (A) | 312 | 358 | 329 | 312 | 358 | 329 | 312 | 358 | 329 | 312 | 358 | 329 | 312 | 358 | 329
NQ | 111675890 | 7460 | CPRE-JACR FDR | 7460 CPRE-JACR 132kV
NQ | 111675890 | 7460 | CPRE-JACR FDR | 7460 CPRE-JACR 132kV | % of Rated A | 58.2623 | 54.761 | 59.0484 | 58.2709 | 54.7636 | 59.0509 | 57.956 | 54.2662 | 58.9558 | 58.2184 | 54.7665 | 59.23 | 58.2496 | 54.5179 | 59.2509
NQ | 111675890 | 7460 | CPRE-JACR FDR | 7460 CPRE-JACR 132kV | Loading (A) | 100.7937 | 94.7364 | 102.1537 | 100.8086 | 94.7411 | 102.158 | 100.2639 | 93.8805 | 101.9935 | 100.7178 | 94.7461 | 102.4679 | 100.7718 | 94.316 | 102.504
NQ | 111675890 | 7460 | CPRE-JACR FDR | 7460 CPRE-JACR 132kV | Power Factor | 0.65281 | 0.60558 | 0.66569 | 0.65269 | 0.60555 | 0.66565 | 0.64257 | 0.62142 | 0.67128 | 0.65176 | 0.60886 | 0.66491 | 0.65338 | 0.62494 | 0.66628
NQ | 111675890 | 7460 | CPRE-JACR FDR | 7460 CPRE-JACR 132kV | Rating (A) | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173
SW | 60026645 | F008D | CENTRAL DALBY 2 | F008D_Central Dalby 2 33 kV
SW | 60026645 | F008D | CENTRAL DALBY 2 | F008D_Central Dalby 2 33 kV | % of Rated A | 36.4666 | 35.7838 | 22.3422 | 36.2509 | 35.5731 | 22.2181 | 36.2413 | 35.5637 | 22.2126 | 36.244 | 35.5664 | 22.2132 | 36.2534 | 35.5758 | 22.2165
SW | 60026645 | F008D | CENTRAL DALBY 2 | F008D_Central Dalby 2 33 kV | Loading (A) | 182.333 | 178.9188 | 107.1 | 181.2547 | 177.8656 | 106.5047 | 181.2065 | 177.8185 | 106.478 | 181.2199 | 177.8319 | 106.481 | 181.2672 | 177.8792 | 106.4968
SW | 60026645 | F008D | CENTRAL DALBY 2 | F008D_Central Dalby 2 33 kV | Power Factor | 0.90435 | 0.90541 | 0.92584 | 0.9047 | 0.90575 | 0.92606 | 0.90473 | 0.90578 | 0.92608 | 0.90472 | 0.90577 | 0.92608 | 0.90469 | 0.90574 | 0.92607
SW | 60026645 | F008D | CENTRAL DALBY 2 | F008D_Central Dalby 2 33 kV | Rating (A) | 500 | 500 | 480 | 500 | 500 | 480 | 500 | 500 | 480 | 500 | 500 | 480 | 500 | 500 | 480
SW | 60026646 | F019D | WEST DALBY NO 1 | F019D_West Dalby No 1 33 kV
SW | 60026646 | F019D | WEST DALBY NO 1 | F019D_West Dalby No 1 33 kV | % of Rated A | 61.7779 | 53.1065 | 51.1868 | 61.7625 | 53.0947 | 51.181 | 61.3263 | 52.7038 | 50.7469 | 61.3298 | 52.7076 | 50.7484 | 61.8396 | 53.115 | 51.0902
SW | 60026646 | F019D | WEST DALBY NO 1 | F019D_West Dalby No 1 33 kV | Loading (A) | 231.6388 | 217.1784 | 188.3416 | 231.5811 | 217.13 | 188.3201 | 229.9457 | 215.5319 | 186.723 | 229.9588 | 215.5471 | 186.7285 | 231.8704 | 217.2132 | 187.9863
SW | 60026646 | F019D | WEST DALBY NO 1 | F019D_West Dalby No 1 33 kV | Power Factor | 0.94934 | 0.95371 | 0.95812 | 0.94936 | 0.9537 | 0.95812 | 0.95069 | 0.95507 | 0.95967 | 0.95068 | 0.95506 | 0.95967 | 0.95017 | 0.95461 | 0.95929
SW | 60026646 | F019D | WEST DALBY NO 1 | F019D_West Dalby No 1 33 kV | Rating (A) | 375 | 409 | 368 | 375 | 409 | 368 | 375 | 409 | 368 | 375 | 409 | 368 | 375 | 409 | 368
SW | 60026664 | F039D | WEST DALBY NO 2 | F039D_West Dalby No 2 33 kV
SW | 60026664 | F039D | WEST DALBY NO 2 | F039D_West Dalby No 2 33 kV | % of Rated A | 0.48082 | 0.48514 | 0.48723 | 0.4809 | 0.4852 | 0.48728 | 0.48102 | 0.4853 | 0.4859 | 0.48101 | 0.48528 | 0.48589 | 0.48094 | 0.48521 | 0.48731
SW | 60026664 | F039D | WEST DALBY NO 2 | F039D_West Dalby No 2 33 kV | Loading (A) | 1.3655 | 1.3778 | 1.3837 | 1.3658 | 1.378 | 1.3839 | 1.3661 | 1.3783 | 1.38 | 1.3661 | 1.3782 | 1.3799 | 1.3659 | 1.378 | 1.384
SW | 60026664 | F039D | WEST DALBY NO 2 | F039D_West Dalby No 2 33 kV | Power Factor | 0.018852 | 0.018852 | 0.018852 | 0.018852 | 0.018852 | 0.018852 | 0.018852 | 0.018852 | 0.018852 | 0.018852 | 0.018852 | 0.018852 | 0.018852 | 0.018852 | 0.018852
SW | 60026664 | F039D | WEST DALBY NO 2 | F039D_West Dalby No 2 33 kV | Rating (A) | 284 | 284 | 284 | 284 | 284 | 284 | 284 | 284 | 284 | 284 | 284 | 284 | 284 | 284 | 284
SW | 60026667 | F060T | TARA | F060T_Tara 33 kV
SW | 60026667 | F060T | TARA | F060T_Tara 33 kV | % of Rated A | 36.5597 | 26.3207 | 20.097 | 36.5649 | 26.325 | 20.0999 | 36.5649 | 26.325 | 20.0999 | 36.5834 | 26.3387 | 20.1077 | 36.5836 | 26.3362 | 20.1078
SW | 60026667 | F060T | TARA | F060T_Tara 33 kV | Loading (A) | 33.9994 | 32.1103 | 23.5135 | 34.0042 | 32.1156 | 23.5168 | 34.0043 | 32.1156 | 23.5169 | 34.0214 | 32.1323 | 23.526 | 34.0216 | 32.1292 | 23.5261
SW | 60026667 | F060T | TARA | F060T_Tara 33 kV | Power Factor | 0.9917 | 0.99423 | 0.99988 | 0.99169 | 0.99421 | 0.99988 | 0.99169 | 0.99421 | 0.99988 | 0.99165 | 0.99418 | 0.99989 | 0.99165 | 0.99419 | 0.99989
SW | 60026667 | F060T | TARA | F060T_Tara 33 kV | Rating (A) | 93 | 122 | 117 | 93 | 122 | 117 | 93 | 122 | 117 | 93 | 122 | 117 | 93 | 122 | 117
SW | 60026669 | F067C | KOGAN | F067C_Kogan 33 kV
SW | 60026669 | F067C | KOGAN | F067C_Kogan 33 kV | % of Rated A | 55.1997 | 38.3881 | 29.8009 | 55.1985 | 38.3943 | 29.8051 | 55.1985 | 38.3943 | 29.8051 | 55.2202 | 38.4134 | 29.8168 | 55.2204 | 38.4108 | 29.8169
SW | 60026669 | F067C | KOGAN | F067C_Kogan 33 kV | Loading (A) | 51.3338 | 46.8318 | 34.8665 | 51.3327 | 46.8393 | 34.8714 | 51.3327 | 46.8393 | 34.8714 | 51.3528 | 46.8627 | 34.885 | 51.353 | 46.8595 | 34.8851
SW | 60026669 | F067C | KOGAN | F067C_Kogan 33 kV | Power Factor | 0.98677 | 0.98955 | 0.99883 | 0.98683 | 0.98954 | 0.99882 | 0.98683 | 0.98954 | 0.99882 | 0.98679 | 0.98949 | 0.99881 | 0.98679 | 0.9895 | 0.99881
SW | 60026669 | F067C | KOGAN | F067C_Kogan 33 kV | Rating (A) | 93 | 122 | 117 | 93 | 122 | 117 | 93 | 122 | 117 | 93 | 122 | 117 | 93 | 122 | 117
SW | 60026670 | F069C | BRIGALOW | F069C_Brigalow 33 kV
SW | 60026670 | F069C | BRIGALOW | F069C_Brigalow 33 kV | % of Rated A | 43.4483 | 38.2606 | 21.5416 | 43.4537 | 38.2668 | 21.5444 | 43.4537 | 38.2669 | 21.5444 | 46.4432 | 40.9103 | 22.9647 | 46.4434 | 40.9043 | 22.9647
SW | 60026670 | F069C | BRIGALOW | F069C_Brigalow 33 kV | Loading (A) | 26.5031 | 29.4603 | 15.7252 | 26.5064 | 29.4651 | 15.7272 | 26.5065 | 29.4651 | 15.7272 | 28.33 | 31.5005 | 16.764 | 28.3301 | 31.496 | 16.764
SW | 60026670 | F069C | BRIGALOW | F069C_Brigalow 33 kV | Power Factor | 0.98719 | 0.98504 | 0.99627 | 0.98719 | 0.98503 | 0.99627 | 0.98719 | 0.98503 | 0.99627 | 0.98584 | 0.98375 | 0.9953 | 0.98584 | 0.98375 | 0.9953
SW | 60026670 | F069C | BRIGALOW | F069C_Brigalow 33 kV | Rating (A) | 61 | 77 | 73 | 61 | 77 | 73 | 61 | 77 | 73 | 61 | 77 | 73 | 61 | 77 | 73
SW | 60026673 | F073C | FAIRYMEADOW | F073C_Fairymeadow 33 kV
SW | 60026673 | F073C | FAIRYMEADOW | F073C_Fairymeadow 33 kV | % of Rated A | 99.4636 | 62.7603 | 114.0962 | 99.4399 | 62.6765 | 114.0698 | 99.4397 | 62.6758 | 114.0696 | 99.3317 | 62.4126 | 113.9747 | 99.3312 | 62.4112 | 113.974
SW | 60026673 | F073C | FAIRYMEADOW | F073C_Fairymeadow 33 kV | Loading (A) | 332.2063 | 211.4998 | 333.1587 | 332.1272 | 211.2175 | 333.0816 | 332.1266 | 211.215 | 333.081 | 331.7659 | 210.3281 | 332.8039 | 331.764 | 210.3233 | 332.8018
SW | 60026673 | F073C | FAIRYMEADOW | F073C_Fairymeadow 33 kV | Power Factor | 0.73925 | 0.69233 | 0.73598 | 0.73944 | 0.69327 | 0.73615 | 0.73944 | 0.69328 | 0.73615 | 0.74026 | 0.69626 | 0.73673 | 0.74027 | 0.69627 | 0.73673
SW | 60026673 | F073C | FAIRYMEADOW | F073C_Fairymeadow 33 kV | Rating (A) | 334 | 337 | 292 | 334 | 337 | 292 | 334 | 337 | 292 | 334 | 337 | 292 | 334 | 337 | 292
SW | 60026674 | F075S | ST GEORGE TOWN | F075S_St George Town 33 kV
SW | 60026674 | F075S | ST GEORGE TOWN | F075S_St George Town 33 kV | % of Rated A | 63.0407 | 63.8316 | 49.9935 | 63.0407 | 63.8315 | 49.9935 | 63.0407 | 63.8315 | 49.9935 | 63.0396 | 63.8304 | 49.9929 | 63.0396 | 63.8304 | 49.9929
SW | 60026674 | F075S | ST GEORGE TOWN | F075S_St George Town 33 kV | Loading (A) | 103.3868 | 104.6838 | 81.9622 | 103.3868 | 104.6837 | 81.9622 | 103.3868 | 104.6837 | 81.9622 | 103.3849 | 104.6818 | 81.9612 | 103.3849 | 104.6819 | 81.9612
SW | 60026674 | F075S | ST GEORGE TOWN | F075S_St George Town 33 kV | Power Factor | 0.94499 | 0.94478 | 0.94895 | 0.94499 | 0.94478 | 0.94895 | 0.94499 | 0.94478 | 0.94895 | 0.94499 | 0.94478 | 0.94895 | 0.94499 | 0.94478 | 0.94895
SW | 60026674 | F075S | ST GEORGE TOWN | F075S_St George Town 33 kV | Rating (A) | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164
SW | 60026675 | F077S | MAIN CAMP | F077S_Main Camp 33 kV
SW | 60026675 | F077S | MAIN CAMP | F077S_Main Camp 33 kV | % of Rated A | 79.9043 | 59.962 | 72.3254 | 79.9043 | 59.962 | 72.3253 | 79.9044 | 59.962 | 72.3253 | 79.903 | 59.9608 | 72.3245 | 79.9029 | 59.9608 | 72.3245
SW | 60026675 | F077S | MAIN CAMP | F077S_Main Camp 33 kV | Loading (A) | 79.9043 | 59.962 | 72.3254 | 79.9043 | 59.962 | 72.3253 | 79.9044 | 59.962 | 72.3253 | 79.903 | 59.9608 | 72.3245 | 79.9029 | 59.9608 | 72.3245
SW | 60026675 | F077S | MAIN CAMP | F077S_Main Camp 33 kV | Power Factor | 0.88812 | 0.91404 | 0.89714 | 0.88812 | 0.91404 | 0.89714 | 0.88812 | 0.91404 | 0.89714 | 0.88812 | 0.91404 | 0.89714 | 0.88812 | 0.91404 | 0.89714
SW | 60026675 | F077S | MAIN CAMP | F077S_Main Camp 33 kV | Rating (A) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
SW | 60026676 | F079S | ST GEORGE MEATWORKS | F079S_St George Meatworks 33 kV
SW | 60026676 | F079S | ST GEORGE MEATWORKS | F079S_St George Meatworks 33 kV | % of Rated A | 46.96 | 49.8697 | 40.5685 | 46.96 | 49.8697 | 40.5685 | 46.96 | 49.8696 | 40.5685 | 46.9591 | 49.8687 | 40.568 | 46.9591 | 49.8687 | 40.568
SW | 60026676 | F079S | ST GEORGE MEATWORKS | F079S_St George Meatworks 33 kV | Loading (A) | 46.96 | 49.8697 | 40.5685 | 46.96 | 49.8697 | 40.5685 | 46.96 | 49.8696 | 40.5685 | 46.9591 | 49.8687 | 40.568 | 46.9591 | 49.8687 | 40.568
SW | 60026676 | F079S | ST GEORGE MEATWORKS | F079S_St George Meatworks 33 kV | Power Factor | 0.96993 | 0.96752 | 0.97768 | 0.96993 | 0.96752 | 0.97768 | 0.96993 | 0.96752 | 0.97768 | 0.96993 | 0.96752 | 0.97768 | 0.96993 | 0.96752 | 0.97768
SW | 60026676 | F079S | ST GEORGE MEATWORKS | F079S_St George Meatworks 33 kV | Rating (A) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
SW | 60026679 | F083C | CHINCHILLA | F083C_Chinchilla 33 kV
SW | 60026679 | F083C | CHINCHILLA | F083C_Chinchilla 33 kV | % of Rated A | 76.5693 | 77.565 | 52.6902 | 77.0464 | 78.1164 | 53.088 | 77.0464 | 78.1165 | 53.088 | 78.0836 | 79.1906 | 53.8123 | 78.0838 | 79.1908 | 53.8124
SW | 60026679 | F083C | CHINCHILLA | F083C_Chinchilla 33 kV | Loading (A) | 255.7388 | 261.3914 | 153.853 | 257.3323 | 263.2497 | 155.0146 | 257.3325 | 263.25 | 155.0147 | 260.7967 | 266.8697 | 157.1295 | 260.7974 | 266.8704 | 157.1299
SW | 60026679 | F083C | CHINCHILLA | F083C_Chinchilla 33 kV | Power Factor | 0.95519 | 0.95547 | 0.9656 | 0.9551 | 0.95532 | 0.96551 | 0.9551 | 0.95532 | 0.96551 | 0.9548 | 0.95499 | 0.9653 | 0.9548 | 0.95499 | 0.9653
SW | 60026679 | F083C | CHINCHILLA | F083C_Chinchilla 33 kV | Rating (A) | 334 | 337 | 292 | 334 | 337 | 292 | 334 | 337 | 292 | 334 | 337 | 292 | 334 | 337 | 292
SW | 60026682 | F095D | KAIMKILLENBUN | F095D_Kaimkillenbun 33 kV
SW | 60026682 | F095D | KAIMKILLENBUN | F095D_Kaimkillenbun 33 kV | % of Rated A | 23.9494 | 26.3396 | 17.6497 | 23.9431 | 26.334 | 17.6482 | 23.9372 | 26.3279 | 17.6444 | 23.9388 | 26.3302 | 17.645 | 23.9446 | 26.5885 | 17.6473
SW | 60026682 | F095D | KAIMKILLENBUN | F095D_Kaimkillenbun 33 kV | Loading (A) | 22.2621 | 26.3396 | 17.6497 | 22.2562 | 26.334 | 17.6482 | 22.2507 | 26.3279 | 17.6444 | 22.2522 | 26.3302 | 17.645 | 22.2576 | 26.5885 | 17.6473
SW | 60026682 | F095D | KAIMKILLENBUN | F095D_Kaimkillenbun 33 kV | Power Factor | 0.99551 | 0.99384 | 0.99986 | 0.99552 | 0.99385 | 0.99986 | 0.99553 | 0.99386 | 0.99986 | 0.99552 | 0.99385 | 0.99986 | 0.99551 | 0.9932 | 0.99986
SW | 60026682 | F095D | KAIMKILLENBUN | F095D_Kaimkillenbun 33 kV | Rating (A) | 93 | 100 | 100 | 93 | 100 | 100 | 93 | 100 | 100 | 93 | 100 | 100 | 93 | 100 | 100
SW | 60026684 | F106R | ROMA EAST | F106R_Roma East 33 kV
SW | 60026684 | F106R | ROMA EAST | F106R_Roma East 33 kV | % of Rated A | 90.6578 | 89.8346 | 63.4559 | 90.6581 | 89.8348 | 63.456 | 90.6581 | 89.8349 | 63.456 | 89.5002 | 89.855 | 63.4639 | 89.5001 | 89.8549 | 63.4638
SW | 60026684 | F106R | ROMA EAST | F106R_Roma East 33 kV | Loading (A) | 202.1667 | 196.7374 | 118.6623 | 202.1672 | 196.738 | 118.6624 | 202.1672 | 196.738 | 118.6624 | 199.585 | 196.7821 | 118.6771 | 199.5849 | 196.782 | 118.6771
SW | 60026684 | F106R | ROMA EAST | F106R_Roma East 33 kV | Power Factor | 0.94153 | 0.94161 | 0.94956 | 0.94153 | 0.94161 | 0.94956 | 0.94153 | 0.94161 | 0.94956 | 0.94155 | 0.9416 | 0.94956 | 0.94155 | 0.9416 | 0.94956
SW | 60026684 | F106R | ROMA EAST | F106R_Roma East 33 kV | Rating (A) | 223 | 219 | 187 | 223 | 219 | 187 | 223 | 219 | 187 | 223 | 219 | 187 | 223 | 219 | 187
SW | 60026689 | F127R | ROMA WEST | F127R_Roma West 33 kV
SW | 60026689 | F127R | ROMA WEST | F127R_Roma West 33 kV | % of Rated A | 82.23 | 55.879 | 42.8788 | 82.2302 | 55.8791 | 42.879 | 82.2291 | 55.8792 | 42.879 | 83.8798 | 56.9963 | 43.7222 | 83.8798 | 56.9962 | 43.7222
SW | 60026689 | F127R | ROMA WEST | F127R_Roma West 33 kV | Loading (A) | 95.3865 | 89.4061 | 66.8908 | 95.3867 | 89.4064 | 66.891 | 95.3856 | 89.4064 | 66.891 | 97.3003 | 91.1938 | 68.2065 | 97.3003 | 91.1938 | 68.2065
SW | 60026689 | F127R | ROMA WEST | F127R_Roma West 33 kV | Power Factor | 0.94743 | 0.94835 | 0.95206 | 0.94743 | 0.94835 | 0.95206 | 0.94743 | 0.94835 | 0.95206 | 0.94708 | 0.94802 | 0.95182 | 0.94708 | 0.94802 | 0.95182
SW | 60026689 | F127R | ROMA WEST | F127R_Roma West 33 kV | Rating (A) | 116 | 160 | 156 | 116 | 160 | 156 | 116 | 160 | 156 | 116 | 160 | 156 | 116 | 160 | 156
SW | 60026700 | F2060 | SLADEVALE 1 | F2060_Sladevale 1 33kV
SW | 60026700 | F2060 | SLADEVALE 1 | F2060_Sladevale 1 33kV | % of Rated A | 80.1083 | 65.5245 | 78.9935 | 80.125 | 65.5187 | 79.0118 | 80.1233 | 65.5197 | 79.0101 | 80.0268 | 65.282 | 78.886 | 80.0204 | 65.2857 | 78.8792
SW | 60026700 | F2060 | SLADEVALE 1 | F2060_Sladevale 1 33kV | Loading (A) | 508.6879 | 416.0804 | 501.6087 | 508.7935 | 416.0433 | 501.7248 | 508.7828 | 416.0497 | 501.7143 | 508.1704 | 414.5403 | 500.9259 | 508.1297 | 414.564 | 500.883
SW | 60026700 | F2060 | SLADEVALE 1 | F2060_Sladevale 1 33kV | Power Factor | 0.99028 | 0.99945 | 0.98662 | 0.99007 | 0.99954 | 0.98638 | 0.99009 | 0.99953 | 0.9864 | 0.99013 | 0.99947 | 0.98643 | 0.99021 | 0.99941 | 0.98652
SW | 60026700 | F2060 | SLADEVALE 1 | F2060_Sladevale 1 33kV | Rating (A) | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635
SW | 60026708 | F217R | ST GEORGE | F217R_St George 66 kV
SW | 60026708 | F217R | ST GEORGE | F217R_St George 66 kV | % of Rated A | 27.2251 | 26.0121 | 24.7382 | 27.2253 | 26.0123 | 24.7383 | 27.225 | 26.0123 | 24.7383 | 27.2325 | 26.019 | 24.7422 | 27.2325 | 26.019 | 24.7422
SW | 60026708 | F217R | ST GEORGE | F217R_St George 66 kV | Loading (A) | 121.6964 | 118.0949 | 97.9634 | 121.697 | 118.0957 | 97.9636 | 121.6957 | 118.0957 | 97.9635 | 121.7292 | 118.1262 | 97.979 | 121.7292 | 118.126 | 97.9791
SW | 60026708 | F217R | ST GEORGE | F217R_St George 66 kV | Power Factor | 0.95709 | 0.95748 | 0.95966 | 0.95709 | 0.95748 | 0.95966 | 0.9571 | 0.95748 | 0.95966 | 0.95699 | 0.95738 | 0.95959 | 0.95699 | 0.95738 | 0.95959
SW | 60026708 | F217R | ST GEORGE | F217R_St George 66 kV | Rating (A) | 447 | 454 | 396 | 447 | 454 | 396 | 447 | 454 | 396 | 447 | 454 | 396 | 447 | 454 | 396
SW | 60026714 | F2325 | BROXBURN | F2325_Broxburn 33 kV
SW | 60026714 | F2325 | BROXBURN | F2325_Broxburn 33 kV | % of Rated A | 58.5027 | 60.5607 | 38.2823 | 58.5027 | 60.5608 | 38.2823 | 58.5146 | 60.5733 | 38.7481 | 58.5168 | 60.5884 | 38.7487 | 59.1385 | 61.2392 | 39.0646
SW | 60026714 | F2325 | BROXBURN | F2325_Broxburn 33 kV | Loading (A) | 195.3988 | 204.0892 | 130.155 | 195.3985 | 204.0896 | 130.1549 | 195.4383 | 204.1316 | 131.7387 | 195.4457 | 204.1825 | 131.7406 | 197.5223 | 206.3756 | 132.8146
SW | 60026714 | F2325 | BROXBURN | F2325_Broxburn 33 kV | Power Factor | 0.93366 | 0.93324 | 0.92442 | 0.93366 | 0.93324 | 0.92442 | 0.93365 | 0.93323 | 0.92343 | 0.93365 | 0.9332 | 0.92343 | 0.93341 | 0.93295 | 0.92332
SW | 60026714 | F2325 | BROXBURN | F2325_Broxburn 33 kV | Rating (A) | 334 | 337 | 340 | 334 | 337 | 340 | 334 | 337 | 340 | 334 | 337 | 340 | 334 | 337 | 340
SW | 60026720 | F2450 | CARRINGTON ROAD | F2450_Carrington Road 33 kV
SW | 60026720 | F2450 | CARRINGTON ROAD | F2450_Carrington Road 33 kV | % of Rated A | 35.0454 | 30.5035 | 30.7635 | 35.0449 | 30.506 | 30.7636 | 35.0541 | 30.5183 | 30.7689 | 35.069 | 30.536 | 30.7778 | 35.0831 | 30.5543 | 30.7865
SW | 60026720 | F2450 | CARRINGTON ROAD | F2450_Carrington Road 33 kV | Loading (A) | 75.3477 | 65.5826 | 66.1416 | 75.3465 | 65.5879 | 66.1417 | 75.3664 | 65.6143 | 66.153 | 75.3983 | 65.6525 | 66.1724 | 75.4286 | 65.6917 | 66.1909
SW | 60026720 | F2450 | CARRINGTON ROAD | F2450_Carrington Road 33 kV | Power Factor | 0.83958 | 0.84257 | 0.84191 | 0.83958 | 0.84257 | 0.84191 | 0.83957 | 0.84255 | 0.8419 | 0.83955 | 0.84253 | 0.84189 | 0.83954 | 0.84251 | 0.84188
SW | 60026720 | F2450 | CARRINGTON ROAD | F2450_Carrington Road 33 kV | Rating (A) | 215 | 215 | 215 | 215 | 215 | 215 | 215 | 215 | 215 | 215 | 215 | 215 | 215 | 215 | 215
SW | 60026721 | F2460 | CECIL PLAINS | F2460_Cecil Plains 33 kV
SW | 60026721 | F2460 | CECIL PLAINS | F2460_Cecil Plains 33 kV | % of Rated A | 31.5436 | 20.6598 | 19.9033 | 31.5436 | 20.6598 | 19.9033 | 31.5426 | 20.6587 | 19.9022 | 31.5424 | 20.6585 | 19.9021 | 31.541 | 20.6849 | 19.9011
SW | 60026721 | F2460 | CECIL PLAINS | F2460_Cecil Plains 33 kV | Loading (A) | 45.1074 | 43.5923 | 41.3988 | 45.1074 | 43.5923 | 41.3988 | 45.106 | 43.5899 | 41.3967 | 45.1056 | 43.5894 | 41.3964 | 45.1036 | 43.6451 | 41.3944
SW | 60026721 | F2460 | CECIL PLAINS | F2460_Cecil Plains 33 kV | Power Factor | 0.65064 | 0.60878 | 0.5582 | 0.65064 | 0.60878 | 0.5582 | 0.65075 | 0.60891 | 0.5583 | 0.65077 | 0.60894 | 0.55831 | 0.65092 | 0.61048 | 0.55839
SW | 60026721 | F2460 | CECIL PLAINS | F2460_Cecil Plains 33 kV | Rating (A) | 143 | 211 | 208 | 143 | 211 | 208 | 143 | 211 | 208 | 143 | 211 | 208 | 143 | 211 | 208
SW | 60026723 | F2520 | CLIFTON | F2520_Clifton 33 kV
SW | 60026723 | F2520 | CLIFTON | F2520_Clifton 33 kV | % of Rated A | 61.77 | 68.0508 | 42.8426 | 61.8239 | 68.2585 | 43.0927 | 61.8297 | 68.2649 | 43.0943 | 61.8503 | 68.2918 | 43.0985 | 61.8608 | 68.3122 | 43.1019
SW | 60026723 | F2520 | CLIFTON | F2520_Clifton 33 kV | Loading (A) | 75.3594 | 83.022 | 52.268 | 75.4251 | 83.2754 | 52.5731 | 75.4323 | 83.2832 | 52.575 | 75.4574 | 83.316 | 52.5802 | 75.4702 | 83.3408 | 52.5843
SW | 60026723 | F2520 | CLIFTON | F2520_Clifton 33 kV | Power Factor | 0.96171 | 0.97241 | 0.89737 | 0.96197 | 0.97046 | 0.89254 | 0.962 | 0.97048 | 0.89257 | 0.9621 | 0.97058 | 0.89266 | 0.96215 | 0.97065 | 0.89273
SW | 60026723 | F2520 | CLIFTON | F2520_Clifton 33 kV | Rating (A) | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122
SW | 60026736 | F2695 | SPARE 02 | F2695_Dent Street 33 kV
SW | 60026736 | F2695 | SPARE 02 | F2695_Dent Street 33 kV | % of Rated A | 0.20172 | 0.2014 | 0.20155 | 0.20172 | 0.20139 | 0.20155 | 0.20171 | 0.20136 | 0.20154 | 0.20165 | 0.20183 | 0.20151 | 0.20181 | 0.20179 | 0.20148
SW | 60026736 | F2695 | SPARE 02 | F2695_Dent Street 33 kV | Loading (A) | 1.0086 | 1.007 | 1.0078 | 1.0086 | 1.0069 | 1.0078 | 1.0085 | 1.0068 | 1.0077 | 1.0083 | 1.0091 | 1.0075 | 1.0091 | 1.0089 | 1.0074
SW | 60026736 | F2695 | SPARE 02 | F2695_Dent Street 33 kV | Power Factor | 0.019996 | 0.019996 | 0.019996 | 0.019996 | 0.019996 | 0.019996 | 0.019996 | 0.019996 | 0.019996 | 0.019996 | 0.019996 | 0.019996 | 0.019996 | 0.019996 | 0.019996
SW | 60026736 | F2695 | SPARE 02 | F2695_Dent Street 33 kV | Rating (A) | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500
SW | 60026737 | F2777 | EAST STANTHORPE | F2777_East Stanthorpe 33 kV
SW | 60026737 | F2777 | EAST STANTHORPE | F2777_East Stanthorpe 33 kV | % of Rated A | 1.6141 | 1.195 | 1.2413 | 1.6142 | 1.1951 | 1.2413 | 1.6142 | 1.1951 | 1.2413 | 1.6142 | 1.195 | 1.2414 | 1.6141 | 1.195 | 1.2413
SW | 60026737 | F2777 | EAST STANTHORPE | F2777_East Stanthorpe 33 kV | Loading (A) | 2.4856 | 2.4856 | 2.4951 | 2.4858 | 2.4858 | 2.4951 | 2.4858 | 2.4857 | 2.4951 | 2.4858 | 2.4857 | 2.4951 | 2.4858 | 2.4856 | 2.4951
SW | 60026737 | F2777 | EAST STANTHORPE | F2777_East Stanthorpe 33 kV | Power Factor | 0.00047551 | 0.00047551 | 0.00047551 | 0.00047551 | 0.00047551 | 0.00047551 | 0.00047551 | 0.00047551 | 0.00047551 | 0.00047551 | 0.00047551 | 0.00047551 | 0.00047551 | 0.00047551 | 0.00047551
SW | 60026737 | F2777 | EAST STANTHORPE | F2777_East Stanthorpe 33 kV | Rating (A) | 154 | 208 | 201 | 154 | 208 | 201 | 154 | 208 | 201 | 154 | 208 | 201 | 154 | 208 | 201
SW | 60026738 | F2780 | WARWICK EAST 1 | F2780_East Warwick No 1 33 kV
SW | 60026738 | F2780 | WARWICK EAST 1 | F2780_East Warwick No 1 33 kV | % of Rated A | 33.9189 | 33.0311 | 24.372 | 33.5998 | 32.7205 | 24.1611 | 33.6002 | 32.7208 | 24.1612 | 33.6007 | 32.7214 | 24.1616 | 33.6019 | 32.7227 | 24.1622
SW | 60026738 | F2780 | WARWICK EAST 1 | F2780_East Warwick No 1 33 kV | Loading (A) | 179.7701 | 179.3586 | 116.2546 | 178.0789 | 177.6721 | 115.2484 | 178.0808 | 177.6741 | 115.2491 | 178.0837 | 177.6771 | 115.2507 | 178.09 | 177.6842 | 115.2536
SW | 60026738 | F2780 | WARWICK EAST 1 | F2780_East Warwick No 1 33 kV | Power Factor | 0.99999 | 0.99998 | 0.98528 | 0.99997 | 0.99996 | 0.98456 | 0.99997 | 0.99996 | 0.98456 | 0.99997 | 0.99996 | 0.98456 | 0.99997 | 0.99996 | 0.98457
SW | 60026738 | F2780 | WARWICK EAST 1 | F2780_East Warwick No 1 33 kV | Rating (A) | 530 | 543 | 477 | 530 | 543 | 477 | 530 | 543 | 477 | 530 | 543 | 477 | 530 | 543 | 477
SW | 60026739 | F2785 | WARWICK EAST 2 | F2785_East Warwick No 2 33 kV
SW | 60026739 | F2785 | WARWICK EAST 2 | F2785_East Warwick No 2 33 kV | % of Rated A | 33.7512 | 32.8678 | 24.2516 | 33.4337 | 32.5587 | 24.0417 | 33.4341 | 32.5591 | 24.0418 | 33.4346 | 32.5597 | 24.0422 | 33.4358 | 32.5609 | 24.0428
SW | 60026739 | F2785 | WARWICK EAST 2 | F2785_East Warwick No 2 33 kV | Loading (A) | 178.8815 | 178.4721 | 115.6801 | 177.1987 | 176.7938 | 114.6788 | 177.2006 | 176.7959 | 114.6795 | 177.2034 | 176.7989 | 114.6812 | 177.2097 | 176.8059 | 114.684
SW | 60026739 | F2785 | WARWICK EAST 2 | F2785_East Warwick No 2 33 kV | Power Factor | 0.99999 | 0.99999 | 0.98535 | 0.99997 | 0.99996 | 0.98463 | 0.99997 | 0.99996 | 0.98463 | 0.99997 | 0.99996 | 0.98463 | 0.99997 | 0.99997 | 0.98464
SW | 60026739 | F2785 | WARWICK EAST 2 | F2785_East Warwick No 2 33 kV | Rating (A) | 530 | 543 | 477 | 530 | 543 | 477 | 530 | 543 | 477 | 530 | 543 | 477 | 530 | 543 | 477
SW | 60026753 | F3040 | HAMPTON STREET | F3040 Hampton Street
SW | 60026753 | F3040 | HAMPTON STREET | F3040 Hampton Street | % of Rated A | 0.30911 | 0.3086 | 0.30884 | 0.30911 | 0.30859 | 0.30885 | 0.30908 | 0.30855 | 0.30883 | 0.309 | 0.30927 | 0.30877 | 0.30924 | 0.30921 | 0.30873
SW | 60026753 | F3040 | HAMPTON STREET | F3040 Hampton Street | Loading (A) | 1.5455 | 1.543 | 1.5442 | 1.5455 | 1.543 | 1.5442 | 1.5454 | 1.5428 | 1.5441 | 1.545 | 1.5463 | 1.5439 | 1.5462 | 1.546 | 1.5437
SW | 60026753 | F3040 | HAMPTON STREET | F3040 Hampton Street | Power Factor | 0.014093 | 0.014093 | 0.014093 | 0.014093 | 0.014093 | 0.014093 | 0.014093 | 0.014093 | 0.014093 | 0.014093 | 0.014093 | 0.014093 | 0.014093 | 0.014093 | 0.014093
SW | 60026753 | F3040 | HAMPTON STREET | F3040 Hampton Street | Rating (A) | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500
SW | 60026769 | F3255 | JENNINGS STREET | F3255_Jennings Street 33 kV
SW | 60026769 | F3255 | JENNINGS STREET | F3255_Jennings Street 33 kV | % of Rated A | 38.4089 | 38.2683 | 24.5167 | 38.1077 | 37.97 | 24.3291 | 37.9607 | 37.8251 | 24.2361 | 38.1261 | 37.9478 | 24.3345 | 38.1338 | 37.9597 | 24.3368
SW | 60026769 | F3255 | JENNINGS STREET | F3255_Jennings Street 33 kV | Loading (A) | 236.983 | 236.1157 | 151.268 | 235.1246 | 234.2749 | 150.1102 | 234.2176 | 233.3806 | 149.5367 | 235.238 | 234.1381 | 150.1437 | 235.2857 | 234.2111 | 150.1578
SW | 60026769 | F3255 | JENNINGS STREET | F3255_Jennings Street 33 kV | Power Factor | 0.95128 | 0.95157 | 0.96314 | 0.95156 | 0.95184 | 0.96329 | 0.9517 | 0.95197 | 0.96337 | 0.95153 | 0.95269 | 0.96328 | 0.95152 | 0.95267 | 0.96328
SW | 60026769 | F3255 | JENNINGS STREET | F3255_Jennings Street 33 kV | Rating (A) | 617 | 617 | 617 | 617 | 617 | 617 | 617 | 617 | 617 | 617 | 617 | 617 | 617 | 617 | 617
SW | 60026772 | F3315 | SLADEVALE 2 | F3315_Sladevale 2 33kV
SW | 60026772 | F3315 | SLADEVALE 2 | F3315_Sladevale 2 33kV | % of Rated A | 82.9174 | 73.1501 | 82.1423 | 82.7842 | 72.9271 | 81.9597 | 82.7823 | 72.9255 | 81.9578 | 82.6265 | 72.691 | 81.753 | 82.6192 | 72.6859 | 81.7453
SW | 60026772 | F3315 | SLADEVALE 2 | F3315_Sladevale 2 33kV | Loading (A) | 526.5254 | 464.5028 | 521.6036 | 525.6798 | 463.087 | 520.4443 | 525.6676 | 463.0769 | 520.4323 | 524.678 | 461.5878 | 519.1317 | 524.6318 | 461.5554 | 519.0828
SW | 60026772 | F3315 | SLADEVALE 2 | F3315_Sladevale 2 33kV | Power Factor | 0.98027 | 0.99867 | 0.97895 | 0.98004 | 0.99858 | 0.97872 | 0.98006 | 0.99861 | 0.97874 | 0.9801 | 0.99867 | 0.97878 | 0.98019 | 0.99874 | 0.97887
SW | 60026772 | F3315 | SLADEVALE 2 | F3315_Sladevale 2 33kV | Rating (A) | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635
SW | 60026789 | F3530 | MILLMERRAN | F3530_Millmerran 33 kV
SW | 60026789 | F3530 | MILLMERRAN | F3530_Millmerran 33 kV | % of Rated A | 59.3024 | 33.4861 | 31.788 | 59.3022 | 33.4862 | 31.7881 | 59.3112 | 33.5017 | 31.7986 | 59.3127 | 33.5049 | 31.8016 | 59.3359 | 33.5345 | 31.819
SW | 60026789 | F3530 | MILLMERRAN | F3530_Millmerran 33 kV | Loading (A) | 75.2245 | 60.2104 | 55.5724 | 75.2243 | 60.2107 | 55.5725 | 75.2356 | 60.2384 | 55.591 | 75.2375 | 60.2442 | 55.5962 | 75.2669 | 60.2975 | 55.6264
SW | 60026789 | F3530 | MILLMERRAN | F3530_Millmerran 33 kV | Power Factor | 0.99784 | 0.99904 | 0.99932 | 0.99784 | 0.99904 | 0.99932 | 0.99783 | 0.99904 | 0.99932 | 0.99783 | 0.99904 | 0.99932 | 0.99783 | 0.99903 | 0.99931
SW | 60026789 | F3530 | MILLMERRAN | F3530_Millmerran 33 kV | Rating (A) | 127 | 180 | 175 | 127 | 180 | 175 | 127 | 180 | 175 | 127 | 180 | 175 | 127 | 180 | 175
SW | 60026795 | F3820 | BOUNDARY ROAD | F3820_Boundary Road 33 kV
SW | 60026795 | F3820 | BOUNDARY ROAD | F3820_Boundary Road 33 kV | % of Rated A | 52.3551 | 52.2152 | 43.7304 | 52.3581 | 52.2207 | 43.7319 | 52.6631 | 52.5267 | 43.974 | 52.9796 | 52.8328 | 44.2245 | 52.5694 | 53.1515 | 44.4767
SW | 60026795 | F3820 | BOUNDARY ROAD | F3820_Boundary Road 33 kV | Loading (A) | 361.2502 | 360.2846 | 301.7398 | 361.2707 | 360.3225 | 301.7501 | 363.3755 | 362.4342 | 303.4204 | 365.5591 | 364.5461 | 305.1492 | 362.7288 | 366.745 | 306.8889
SW | 60026795 | F3820 | BOUNDARY ROAD | F3820_Boundary Road 33 kV | Power Factor | 0.81856 | 0.81887 | 0.82772 | 0.81855 | 0.81886 | 0.82772 | 0.81821 | 0.81851 | 0.82742 | 0.81785 | 0.81817 | 0.82711 | 0.81815 | 0.81781 | 0.8268
SW | 60026795 | F3820 | BOUNDARY ROAD | F3820_Boundary Road 33 kV | Rating (A) | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690
SW | 60026796 | F3830 | NORWIN | F3830_Norwin 33 kV
SW | 60026796 | F3830 | NORWIN | F3830_Norwin 33 kV | % of Rated A | 29.4061 | 34.2804 | 29.0096 | 29.4061 | 34.2806 | 29.0097 | 29.4111 | 34.2978 | 29.0679 | 29.4121 | 34.3016 | 29.0704 | 30.8109 | 35.9565 | 30.4598
SW | 60026796 | F3830 | NORWIN | F3830_Norwin 33 kV | Loading (A) | 34.1111 | 39.7653 | 33.6511 | 34.1111 | 39.7655 | 33.6512 | 34.1169 | 39.7855 | 33.7187 | 34.118 | 39.7899 | 33.7217 | 35.7406 | 41.7096 | 35.3334
SW | 60026796 | F3830 | NORWIN | F3830_Norwin 33 kV | Power Factor | 0.86177 | 0.86053 | 0.86175 | 0.86177 | 0.86053 | 0.86175 | 0.86176 | 0.86052 | 0.86172 | 0.86176 | 0.86052 | 0.86172 | 0.86954 | 0.86843 | 0.86949
SW | 60026796 | F3830 | NORWIN | F3830_Norwin 33 kV | Rating (A) | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116
SW | 60026800 | F3855 | O'MARAS ROAD | F3855 Omaras Road 33 kV
SW | 60026800 | F3855 | O'MARAS ROAD | F3855 Omaras Road 33 kV | % of Rated A | 21.1975 | 19.9911 | 21.3793 | 21.1974 | 19.9926 | 21.3798 | 21.2035 | 20.0003 | 21.3842 | 21.2134 | 20.0113 | 21.3907 | 21.2183 | 20.0227 | 21.3971
SW | 60026800 | F3855 | O'MARAS ROAD | F3855 Omaras Road 33 kV | Loading (A) | 49.3901 | 46.5792 | 49.8138 | 49.3899 | 46.5828 | 49.815 | 49.4043 | 46.6006 | 49.8251 | 49.4272 | 46.6264 | 49.8402 | 49.4386 | 46.653 | 49.8553
SW | 60026800 | F3855 | O'MARAS ROAD | F3855 Omaras Road 33 kV | Power Factor | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998
SW | 60026800 | F3855 | O'MARAS ROAD | F3855 Omaras Road 33 kV | Rating (A) | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233
SW | 60026810 | F3970 | POZIERES | F3970_Pozieres 33 kV
SW | 60026810 | F3970 | POZIERES | F3970_Pozieres 33 kV | % of Rated A | 36.1399 | 20.6853 | 20.2951 | 34.8218 | 19.9419 | 19.5596 | 34.8228 | 19.9429 | 19.5599 | 34.8197 | 19.9459 | 19.561 | 34.8368 | 19.9519 | 19.5656
SW | 60026810 | F3970 | POZIERES | F3970_Pozieres 33 kV | Loading (A) | 51.6793 | 43.0161 | 40.784 | 49.7943 | 41.4699 | 39.3056 | 49.7958 | 41.472 | 39.3061 | 49.7914 | 41.4782 | 39.3084 | 49.8159 | 41.4908 | 39.3176
SW | 60026810 | F3970 | POZIERES | F3970_Pozieres 33 kV | Power Factor | 0.85636 | 0.86178 | 0.86245 | 0.85673 | 0.86215 | 0.86303 | 0.85673 | 0.86215 | 0.86303 | 0.85674 | 0.86214 | 0.86303 | 0.85673 | 0.86233 | 0.86302
SW | 60026810 | F3970 | POZIERES | F3970_Pozieres 33 kV | Rating (A) | 143 | 208 | 201 | 143 | 208 | 201 | 143 | 208 | 201 | 143 | 208 | 201 | 143 | 208 | 201
SW | 60026811 | F3980 | PURRAWUNDA | F3980_Purrawunda 33 kV
SW | 60026811 | F3980 | PURRAWUNDA | F3980_Purrawunda 33 kV | % of Rated A | 56.1357 | 58.3156 | 52.5616 | 56.1377 | 58.3194 | 52.5626 | 56.1521 | 58.4731 | 52.7601 | 56.1739 | 58.4969 | 52.771 | 55.4964 | 58.5246 | 52.7829
SW | 60026811 | F3980 | PURRAWUNDA | F3980_Purrawunda 33 kV | Loading (A) | 118.4462 | 123.0459 | 110.9049 | 118.4505 | 123.0538 | 110.9072 | 118.481 | 123.3782 | 111.3237 | 118.5269 | 123.4284 | 111.3469 | 117.0973 | 123.487 | 111.3719
SW | 60026811 | F3980 | PURRAWUNDA | F3980_Purrawunda 33 kV | Power Factor | 0.95599 | 0.96168 | 0.9465 | 0.95601 | 0.96171 | 0.94651 | 0.95611 | 0.961 | 0.94332 | 0.95627 | 0.96115 | 0.94343 | 0.95544 | 0.96132 | 0.94354
SW | 60026811 | F3980 | PURRAWUNDA | F3980_Purrawunda 33 kV | Rating (A) | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211
SW | 60026813 | F4005 | RACECOURSE | F4005_Racecourse 33 kV
SW | 60026813 | F4005 | RACECOURSE | F4005_Racecourse 33 kV | % of Rated A | 29.9727 | 27.2957 | 17.5337 | 29.836 | 27.1725 | 17.4542 | 29.8471 | 27.1835 | 17.4571 | 29.8421 | 27.1994 | 17.4621 | 29.4789 | 27.2157 | 17.4669
SW | 60026813 | F4005 | RACECOURSE | F4005_Racecourse 33 kV | Loading (A) | 211.6073 | 192.7073 | 123.7878 | 210.6422 | 191.838 | 123.2267 | 210.7202 | 191.9154 | 123.2473 | 210.6851 | 192.0275 | 123.2825 | 208.1208 | 192.1427 | 123.3163
SW | 60026813 | F4005 | RACECOURSE | F4005_Racecourse 33 kV | Power Factor | 0.94783 | 0.95001 | 0.9564 | 0.94793 | 0.9501 | 0.95645 | 0.94791 | 0.95008 | 0.95645 | 0.94845 | 0.95006 | 0.95644 | 0.94843 | 0.95004 | 0.95643
SW | 60026813 | F4005 | RACECOURSE | F4005_Racecourse 33 kV | Rating (A) | 706 | 706 | 706 | 706 | 706 | 706 | 706 | 706 | 706 | 706 | 706 | 706 | 706 | 706 | 706
SW | 60026814 | F4015 | RAMSAY STREET | F4015_Ramsay Street 33 kV
SW | 60026814 | F4015 | RAMSAY STREET | F4015_Ramsay Street 33 kV | % of Rated A | 38.8998 | 38.7574 | 24.8347 | 38.5947 | 38.4553 | 24.6446 | 38.4458 | 38.3085 | 24.5505 | 38.6133 | 38.4253 | 24.6501 | 38.6212 | 38.4373 | 24.6524
SW | 60026814 | F4015 | RAMSAY STREET | F4015_Ramsay Street 33 kV | Loading (A) | 233.3987 | 232.5444 | 149.0082 | 231.5683 | 230.7315 | 147.8677 | 230.675 | 229.8508 | 147.3028 | 231.68 | 230.552 | 147.9007 | 231.7271 | 230.6238 | 147.9146
SW | 60026814 | F4015 | RAMSAY STREET | F4015_Ramsay Street 33 kV | Power Factor | 0.95314 | 0.95342 | 0.96467 | 0.95342 | 0.95369 | 0.96482 | 0.95355 | 0.95382 | 0.96489 | 0.95339 | 0.95455 | 0.96481 | 0.95337 | 0.95453 | 0.96481
SW | 60026814 | F4015 | RAMSAY STREET | F4015_Ramsay Street 33 kV | Rating (A) | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600
SW | 60026827 | F4245 | STANTHORPE | F4245_Stanthorpe 33 kV
SW | 60026827 | F4245 | STANTHORPE | F4245_Stanthorpe 33 kV | % of Rated A | 55.0864 | 57.6416 | 39.5265 | 55.0606 | 57.6147 | 39.516 | 55.0626 | 57.6172 | 39.5167 | 55.0689 | 57.6195 | 39.5192 | 55.6222 | 58.2099 | 39.8464
SW | 60026827 | F4245 | STANTHORPE | F4245_Stanthorpe 33 kV | Loading (A) | 160.8523 | 168.3135 | 115.4173 | 160.7769 | 168.235 | 115.3868 | 160.7828 | 168.2422 | 115.3887 | 160.8013 | 168.249 | 115.396 | 162.4168 | 169.973 | 116.3516
SW | 60026827 | F4245 | STANTHORPE | F4245_Stanthorpe 33 kV | Power Factor | 0.99693 | 0.99858 | 0.96147 | 0.99689 | 0.99855 | 0.96132 | 0.9969 | 0.99855 | 0.96133 | 0.99691 | 0.99856 | 0.96137 | 0.99732 | 0.99883 | 0.9632
SW | 60026827 | F4245 | STANTHORPE | F4245_Stanthorpe 33 kV | Rating (A) | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292
SW | 60026834 | F4470 | VACY STREET | F4470 Vacy Street
SW | 60026834 | F4470 | VACY STREET | F4470 Vacy Street | % of Rated A | 0.45409 | 0.45335 | 0.45371 | 0.45409 | 0.45334 | 0.45371 | 0.45406 | 0.45328 | 0.45368 | 0.45393 | 0.45433 | 0.4536 | 0.45429 | 0.45424 | 0.45354
SW | 60026834 | F4470 | VACY STREET | F4470 Vacy Street | Loading (A) | 2.2705 | 2.2668 | 2.2686 | 2.2705 | 2.2667 | 2.2686 | 2.2703 | 2.2664 | 2.2684 | 2.2697 | 2.2717 | 2.268 | 2.2714 | 2.2712 | 2.2677
SW | 60026834 | F4470 | VACY STREET | F4470 Vacy Street | Power Factor | 0.017383 | 0.017383 | 0.017383 | 0.017383 | 0.017383 | 0.017383 | 0.017383 | 0.017383 | 0.017383 | 0.017383 | 0.017383 | 0.017383 | 0.017383 | 0.017383 | 0.017383
SW | 60026834 | F4470 | VACY STREET | F4470 Vacy Street | Rating (A) | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500
SW | 60026835 | F4475 | SPARE 01 | F4475_Victoria Street 33 kV
SW | 60026835 | F4475 | SPARE 01 | F4475_Victoria Street 33 kV | % of Rated A | 0.11005 | 0.10987 | 0.10996 | 0.11005 | 0.10987 | 0.10996 | 0.11005 | 0.10986 | 0.10995 | 0.11001 | 0.11011 | 0.10993 | 0.1101 | 0.11009 | 0.10992
SW | 60026835 | F4475 | SPARE 01 | F4475_Victoria Street 33 kV | Loading (A) | 0.55027 | 0.54937 | 0.5498 | 0.55027 | 0.54935 | 0.5498 | 0.55023 | 0.54928 | 0.54977 | 0.55007 | 0.55056 | 0.54967 | 0.55051 | 0.55045 | 0.5496
SW | 60026835 | F4475 | SPARE 01 | F4475_Victoria Street 33 kV | Power Factor | 0.019244 | 0.019244 | 0.019244 | 0.019244 | 0.019244 | 0.019244 | 0.019244 | 0.019244 | 0.019244 | 0.019244 | 0.019244 | 0.019244 | 0.019244 | 0.019244 | 0.019244
SW | 60026835 | F4475 | SPARE 01 | F4475_Victoria Street 33 kV | Rating (A) | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500
SW | 60026843 | F4605 | WEST WARWICK | F4605_West Warwick 33 kV
SW | 60026843 | F4605 | WEST WARWICK | F4605_West Warwick 33 kV | % of Rated A | 57.6039 | 55.0554 | 44.006 | 57.5996 | 55.0514 | 44.0037 | 57.6003 | 55.0522 | 44.0041 | 57.6013 | 55.0532 | 44.0049 | 57.6036 | 55.0556 | 44.0062
SW | 60026843 | F4605 | WEST WARWICK | F4605_West Warwick 33 kV | Loading (A) | 224.0773 | 215.8153 | 149.6185 | 224.0605 | 215.7997 | 149.6109 | 224.0632 | 215.8025 | 149.612 | 224.0672 | 215.8065 | 149.6147 | 224.0761 | 215.816 | 149.6194
SW | 60026843 | F4605 | WEST WARWICK | F4605_West Warwick 33 kV | Power Factor | 0.92538 | 0.92669 | 0.93703 | 0.92539 | 0.9267 | 0.93703 | 0.92539 | 0.9267 | 0.93703 | 0.92539 | 0.9267 | 0.93703 | 0.92538 | 0.92669 | 0.93703
SW | 60026843 | F4605 | WEST WARWICK | F4605_West Warwick 33 kV | Rating (A) | 389 | 392 | 340 | 389 | 392 | 340 | 389 | 392 | 340 | 389 | 392 | 340 | 389 | 392 | 340
SW | 60026846 | F4685 | WYALLA STREET | F4685_Wyalla Street 33 kV
SW | 60026846 | F4685 | WYALLA STREET | F4685_Wyalla Street 33 kV | % of Rated A | 27.0746 | 24.6569 | 15.8403 | 26.9511 | 24.5457 | 15.7686 | 26.9611 | 24.5556 | 15.7712 | 26.9566 | 24.5699 | 15.7757 | 26.6286 | 24.5846 | 15.78
SW | 60026846 | F4685 | WYALLA STREET | F4685_Wyalla Street 33 kV | Loading (A) | 186.8147 | 170.1324 | 109.2984 | 185.9628 | 169.3651 | 108.8031 | 186.0317 | 169.4333 | 108.8214 | 186.0004 | 169.5323 | 108.8524 | 183.7375 | 169.634 | 108.8822
SW | 60026846 | F4685 | WYALLA STREET | F4685_Wyalla Street 33 kV | Power Factor | 0.94653 | 0.94872 | 0.95507 | 0.94663 | 0.94881 | 0.95513 | 0.94662 | 0.94879 | 0.95512 | 0.94716 | 0.94877 | 0.95512 | 0.94714 | 0.94875 | 0.95511
SW | 60026846 | F4685 | WYALLA STREET | F4685_Wyalla Street 33 kV | Rating (A) | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690
SW | 60026848 | 790 | 790 WARWICK - STANTHORPE | 790_Warwick-Stanthorpe 110 kV
SW | 60026848 | 790 | 790 WARWICK - STANTHORPE | 790_Warwick-Stanthorpe 110 kV | % of Rated A | 46.3628 | 33.7782 | 24.2627 | 46.0191 | 33.5424 | 24.0715 | 46.0211 | 33.5439 | 24.072 | 46.027 | 33.5454 | 24.0742 | 46.4305 | 33.8469 | 24.257
SW | 60026848 | 790 | 790 WARWICK - STANTHORPE | 790_Warwick-Stanthorpe 110 kV | Loading (A) | 58.8797 | 60.7995 | 42.4598 | 58.4434 | 60.3751 | 42.1251 | 58.4458 | 60.378 | 42.126 | 58.4533 | 60.3807 | 42.1298 | 58.9658 | 60.9233 | 42.4498
SW | 60026848 | 790 | 790 WARWICK - STANTHORPE | 790_Warwick-Stanthorpe 110 kV | Power Factor | 0.99752 | 0.99651 | 0.99698 | 0.99783 | 0.99686 | 0.99645 | 0.99783 | 0.99685 | 0.99645 | 0.99782 | 0.99685 | 0.99646 | 0.99756 | 0.99654 | 0.99682
SW | 60026848 | 790 | 790 WARWICK - STANTHORPE | 790_Warwick-Stanthorpe 110 kV | Rating (A) | 127 | 180 | 175 | 127 | 180 | 175 | 127 | 180 | 175 | 127 | 180 | 175 | 127 | 180 | 175
SW | 60026891 | F074C | MILES - CONDAMINE | F074C_Miles-Condamine 33 kV
SW | 60026891 | F074C | MILES - CONDAMINE | F074C_Miles-Condamine 33 kV | % of Rated A | 15.3501 | 12.5659 | 11.4342 | 15.3502 | 12.566 | 11.4342 | 15.3502 | 12.566 | 11.4342 | 15.3504 | 12.5663 | 11.4345 | 15.3505 | 12.5663 | 11.4345
SW | 60026891 | F074C | MILES - CONDAMINE | F074C_Miles-Condamine 33 kV | Loading (A) | 21.9507 | 37.0694 | 30.0719 | 21.9507 | 37.0696 | 30.072 | 21.9507 | 37.0696 | 30.072 | 21.9511 | 37.0705 | 30.0728 | 21.9512 | 37.0707 | 30.0727
SW | 60026891 | F074C | MILES - CONDAMINE | F074C_Miles-Condamine 33 kV | Power Factor | 0.99996 | 0.99999 | 0.99869 | 0.99996 | 0.99999 | 0.99869 | 0.99996 | 0.99999 | 0.99869 | 0.99996 | 0.99999 | 0.99869 | 0.99996 | 0.99999 | 0.99869
SW | 60026891 | F074C | MILES - CONDAMINE | F074C_Miles-Condamine 33 kV | Rating (A) | 143 | 295 | 263 | 143 | 295 | 263 | 143 | 295 | 263 | 143 | 295 | 263 | 143 | 295 | 263
SW | 60026893 | F077C | WANDOAN | F077C_Wandoan 33 kV
SW | 60026893 | F077C | WANDOAN | F077C_Wandoan 33 kV | % of Rated A | 34.9246 | 22.8058 | 17.3933 | 34.9247 | 22.8059 | 17.3933 | 34.9247 | 22.8059 | 17.3933 | 34.9254 | 22.8066 | 17.3934 | 34.9255 | 22.8067 | 17.3935
SW | 60026893 | F077C | WANDOAN | F077C_Wandoan 33 kV | Loading (A) | 60.4188 | 63.3994 | 48.3525 | 60.4189 | 63.3997 | 48.3525 | 60.419 | 63.3999 | 48.3526 | 60.4202 | 63.4015 | 48.353 | 60.4203 | 63.4018 | 48.3531
SW | 60026893 | F077C | WANDOAN | F077C_Wandoan 33 kV | Power Factor | 0.98515 | 0.98942 | 0.9871 | 0.98515 | 0.98942 | 0.9871 | 0.98515 | 0.98942 | 0.9871 | 0.98515 | 0.98942 | 0.9871 | 0.98515 | 0.98942 | 0.9871
SW | 60026893 | F077C | WANDOAN | F077C_Wandoan 33 kV | Rating (A) | 173 | 278 | 278 | 173 | 278 | 278 | 173 | 278 | 278 | 173 | 278 | 278 | 173 | 278 | 278
SW | 60026994 | F083S | Dirrabandi Town 33 kV | F083S_Dirrabandi Town 33 kV
SW | 60026994 | F083S | Dirrabandi Town 33 kV | F083S_Dirrabandi Town 33 kV | % of Rated A | 12.2782 | 11.0426 | 11.3325 | 12.2782 | 11.0426 | 11.3325 | 12.2782 | 11.0426 | 11.3325 | 12.2779 | 11.0425 | 11.3324 | 12.278 | 11.0425 | 11.3324
SW | 60026994 | F083S | Dirrabandi Town 33 kV | F083S_Dirrabandi Town 33 kV | Loading (A) | 8.9631 | 10.0488 | 9.746 | 8.9631 | 10.0488 | 9.746 | 8.9631 | 10.0488 | 9.746 | 8.9629 | 10.0487 | 9.7459 | 8.9629 | 10.0487 | 9.7459
SW | 60026994 | F083S | Dirrabandi Town 33 kV | F083S_Dirrabandi Town 33 kV | Power Factor | 0.88673 | 0.99228 | 0.98978 | 0.88673 | 0.99228 | 0.98978 | 0.88673 | 0.99228 | 0.98978 | 0.88673 | 0.99228 | 0.98978 | 0.88673 | 0.99228 | 0.98978
SW | 60026994 | F083S | Dirrabandi Town 33 kV | F083S_Dirrabandi Town 33 kV | Rating (A) | 73 | 91 | 86 | 73 | 91 | 86 | 73 | 91 | 86 | 73 | 91 | 86 | 73 | 91 | 86
SW | 60027002 | F097D | JANDOWAE | F097D_Jandowae 33 kV
SW | 60027002 | F097D | JANDOWAE | F097D_Jandowae 33 kV | % of Rated A | 60.5935 | 40.4695 | 39.8129 | 60.5795 | 40.4596 | 39.8092 | 59.6537 | 39.8295 | 39.174 | 59.6574 | 39.8322 | 39.1755 | 59.6838 | 39.8502 | 39.1852
SW | 60027002 | F097D | JANDOWAE | F097D_Jandowae 33 kV | Loading (A) | 86.6354 | 85.7813 | 83.1951 | 86.6154 | 85.7604 | 83.1874 | 85.2933 | 84.4263 | 81.8617 | 85.2985 | 84.4322 | 81.8647 | 85.3363 | 84.4702 | 81.885
SW | 60027002 | F097D | JANDOWAE | F097D_Jandowae 33 kV | Power Factor | 0.99445 | 0.9939 | 0.99404 | 0.99446 | 0.99391 | 0.99404 | 0.99584 | 0.99537 | 0.99553 | 0.99584 | 0.99537 | 0.99553 | 0.99583 | 0.99537 | 0.99553
SW | 60027002 | F097D | JANDOWAE | F097D_Jandowae 33 kV | Rating (A) | 143 | 212 | 209 | 143 | 212 | 209 | 143 | 212 | 209 | 143 | 212 | 209 | 143 | 212 | 209
SW | 60027003 | F099D | WARRA | F099D_Warra 33 kV
SW | 60027003 | F099D | WARRA | F099D_Warra 33 kV | % of Rated A | 22.0536 | 21.2084 | 21.2178 | 22.0479 | 21.2037 | 21.2153 | 22.0351 | 21.1921 | 21.2033 | 22.0364 | 21.194 | 21.2039 | 22.0482 | 21.3918 | 21.211
SW | 60027003 | F099D | WARRA | F099D_Warra 33 kV | Loading (A) | 36.384 | 37.5346 | 33.3077 | 36.3746 | 37.5264 | 33.3037 | 36.3534 | 37.5058 | 33.2849 | 36.3556 | 37.5091 | 33.2859 | 36.3752 | 37.8592 | 33.2969
SW | 60027003 | F099D | WARRA | F099D_Warra 33 kV | Power Factor | 0.95512 | 0.95861 | 0.95812 | 0.95514 | 0.95862 | 0.95813 | 0.95519 | 0.95866 | 0.95817 | 0.95519 | 0.95866 | 0.95817 | 0.95514 | 0.95813 | 0.95814
SW | 60027003 | F099D | WARRA | F099D_Warra 33 kV | Rating (A) | 165 | 177 | 157 | 165 | 177 | 157 | 165 | 177 | 157 | 165 | 177 | 157 | 165 | 177 | 157
SW | 60300324 | F5530 | 728 MR - South Toowo | 728_Middle Ridge-South Toowoomba 110 kV
SW | 60300324 | F5530 | 728 MR - South Toowo | 728_Middle Ridge-South Toowoomba 110 kV | % of Rated A | 23.6566 | 22.1299 | 17.1037 | 23.6281 | 22.1066 | 17.0872 | 23.6779 | 22.155 | 17.1001 | 23.8177 | 22.2848 | 17.1743 | 23.8924 | 22.3563 | 17.2021
SW | 60300324 | F5530 | 728 MR - South Toowo | 728_Middle Ridge-South Toowoomba 110 kV | Loading (A) | 243.4264 | 235.0192 | 162.9986 | 243.133 | 234.7719 | 162.8412 | 243.6459 | 235.2861 | 162.9635 | 245.0841 | 236.6647 | 163.6715 | 245.8526 | 237.4235 | 163.9364
SW | 60300324 | F5530 | 728 MR - South Toowo | 728_Middle Ridge-South Toowoomba 110 kV | Power Factor | 0.99968 | 0.99884 | 0.97115 | 0.99968 | 0.99883 | 0.97107 | 0.99969 | 0.99887 | 0.97115 | 0.99976 | 0.99901 | 0.97188 | 0.99979 | 0.99908 | 0.97213
SW | 60300324 | F5530 | 728 MR - South Toowo | 728_Middle Ridge-South Toowoomba 110 kV | Rating (A) | 1029 | 1062 | 953 | 1029 | 1062 | 953 | 1029 | 1062 | 953 | 1029 | 1062 | 953 | 1029 | 1062 | 953
SW | 60300325 | F5555 | 734 MR - Yarranlea | F5555_734(Middle Ridge-Yarranlea) 110 kV
SW | 60300325 | F5555 | 734 MR - Yarranlea | F5555_734(Middle Ridge-Yarranlea) 110 kV | % of Rated A | 104.7457 | 35.7098 | 116.6648 | 104.7471 | 35.7086 | 116.6656 | 104.6861 | 35.6211 | 116.5922 | 104.6674 | 35.5423 | 116.5689 | 104.5442 | 35.3381 | 116.4251
SW | 60300325 | F5555 | 734 MR - Yarranlea | F5555_734(Middle Ridge-Yarranlea) 110 kV | Loading (A) | 300.6201 | 102.1301 | 288.1621 | 300.6241 | 102.1267 | 288.1639 | 300.4491 | 101.8763 | 287.9827 | 300.3955 | 101.6509 | 287.9251 | 300.0418 | 101.0669 | 287.5699
SW | 60300325 | F5555 | 734 MR - Yarranlea | F5555_734(Middle Ridge-Yarranlea) 110 kV | Power Factor | 0.80156 | 0.48163 | 0.79366 | 0.80155 | 0.48165 | 0.79365 | 0.80148 | 0.48086 | 0.79357 | 0.80166 | 0.48197 | 0.79375 | 0.80155 | 0.47952 | 0.79364
SW | 60300325 | F5555 | 734 MR - Yarranlea | F5555_734(Middle Ridge-Yarranlea) 110 kV | Rating (A) | 287 | 286 | 247 | 287 | 286 | 247 | 287 | 286 | 247 | 287 | 286 | 247 | 287 | 286 | 247
SW | 60300326 | F5560 | 735 MR - Warwick | F5560_735(Middle Ridge-Warwick) 110 kV
SW | 60300326 | F5560 | 735 MR - Warwick | F5560_735(Middle Ridge-Warwick) 110 kV | % of Rated A | 30.0266 | 35.9365 | 29.9007 | 30.14 | 35.8121 | 29.8007 | 30.1395 | 35.8228 | 29.8044 | 30.0507 | 35.9802 | 29.9416 | 30.0102 | 36.0627 | 29.9987
SW | 60300326 | F5560 | 735 MR - Warwick | F5560_735(Middle Ridge-Warwick) 110 kV | Loading (A) | 77.1684 | 114.9969 | 87.908 | 77.4598 | 114.5989 | 87.614 | 77.4586 | 114.6331 | 87.6251 | 77.2302 | 115.1366 | 88.0284 | 77.1263 | 115.4007 | 88.1963
SW | 60300326 | F5560 | 735 MR - Warwick | F5560_735(Middle Ridge-Warwick) 110 kV | Power Factor | 0.93307 | 0.90894 | 0.90689 | 0.9334 | 0.90826 | 0.90626 | 0.93348 | 0.90797 | 0.90612 | 0.93387 | 0.90774 | 0.90603 | 0.9339 | 0.90765 | 0.90602
SW | 60300326 | F5560 | 735 MR - Warwick | F5560_735(Middle Ridge-Warwick) 110 kV | Rating (A) | 257 | 320 | 294 | 257 | 320 | 294 | 257 | 320 | 294 | 257 | 320 | 294 | 257 | 320 | 294
SW | 60306799 | F3095 | Highfields | F3095_Highfields 33 kV
SW | 60306799 | F3095 | Highfields | F3095_Highfields 33 kV | % of Rated A | 62.7981 | 46.5689 | 34.7491 | 62.7977 | 46.569 | 34.7504 | 62.0113 | 45.9878 | 34.5469 | 63.3718 | 47.0094 | 34.949 | 64.1703 | 47.5927 | 35.157
SW | 60306799 | F3095 | Highfields | F3095_Highfields 33 kV | Loading (A) | 106.1184 | 111.7551 | 81.2996 | 106.1179 | 111.7554 | 81.3026 | 104.7886 | 110.3601 | 80.8263 | 107.0878 | 112.8119 | 81.7673 | 108.4374 | 114.2121 | 82.254
SW | 60306799 | F3095 | Highfields | F3095_Highfields 33 kV | Power Factor | 0.95596 | 0.9554 | 0.9264 | 0.95596 | 0.9554 | 0.9264 | 0.95393 | 0.95337 | 0.92471 | 0.95368 | 0.95309 | 0.92517 | 0.95572 | 0.95525 | 0.92686
SW | 60306799 | F3095 | Highfields | F3095_Highfields 33 kV | Rating (A) | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234
SW | 60306800 | F3815 | North Street No 1 | F3815 North Street No 1 33 kV
SW | 60306800 | F3815 | North Street No 1 | F3815 North Street No 1 33 kV | % of Rated A | 1.3114 | 0.9868 | 1.0306 | 1.3114 | 0.98679 | 1.0306 | 1.3114 | 0.98669 | 1.0306 | 1.3113 | 0.98646 | 1.0306 | 1.3113 | 0.98629 | 1.0306
SW | 60306800 | F3815 | North Street No 1 | F3815 North Street No 1 33 kV | Loading (A) | 2.3213 | 2.3288 | 2.3292 | 2.3213 | 2.3288 | 2.3292 | 2.3212 | 2.3286 | 2.3291 | 2.321 | 2.328 | 2.3292 | 2.3209 | 2.3276 | 2.3291
SW | 60306800 | F3815 | North Street No 1 | F3815 North Street No 1 33 kV | Power Factor | 0.0031927 | 0.0031927 | 0.0031927 | 0.0031927 | 0.0031927 | 0.0031927 | 0.0031927 | 0.0031927 | 0.0031927 | 0.0031927 | 0.0031927 | 0.0031927 | 0.0031927 | 0.0031927 | 0.0031927
SW | 60306800 | F3815 | North Street No 1 | F3815 North Street No 1 33 kV | Rating (A) | 177 | 236 | 226 | 177 | 236 | 226 | 177 | 236 | 226 | 177 | 236 | 226 | 177 | 236 | 226
SW | 60306801 | F3910 | Perseverence Creek 1 | F3910_Perseverence Creek 1 33 kV
SW | 60306801 | F3910 | Perseverence Creek 1 | F3910_Perseverence Creek 1 33 kV | % of Rated A | 49.7856 | 36.8057 | 42.4905 | 49.7853 | 36.8058 | 42.4927 | 49.5839 | 36.664 | 42.4448 | 50.4094 | 37.2837 | 42.7068 | 50.6201 | 37.4311 | 42.7602
SW | 60306801 | F3910 | Perseverence Creek 1 | F3910_Perseverence Creek 1 33 kV | Loading (A) | 84.1376 | 88.3336 | 99.4277 | 84.1371 | 88.3338 | 99.4327 | 83.7966 | 87.9934 | 99.3207 | 85.1918 | 89.4806 | 99.9338 | 85.5479 | 89.8344 | 100.0586
SW | 60306801 | F3910 | Perseverence Creek 1 | F3910_Perseverence Creek 1 33 kV | Power Factor | 0.96414 | 0.96459 | 0.92584 | 0.96414 | 0.96459 | 0.92584 | 0.96339 | 0.94266 | 0.92539 | 0.96359 | 0.96402 | 0.92589 | 0.96434 | 0.96491 | 0.92633
SW | 60306801 | F3910 | Perseverence Creek 1 | F3910_Perseverence Creek 1 33 kV | Rating (A) | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234
SW | 60306802 | F7233 | 7233 MR - Torrington | 7233_Middle Ridge-Torrington 110 kV
SW | 60306802 | F7233 | 7233 MR - Torrington | 7233_Middle Ridge-Torrington 110 kV | % of Rated A | 26.0705 | 22.2089 | 17.7859 | 26.0907 | 22.2347 | 17.7922 | 26.235 | 22.3598 | 17.8793 | 26.4445 | 22.5277 | 18.0049 | 26.6844 | 22.7225 | 18.1425
SW | 60306802 | F7233 | 7233 MR - Torrington | 7233_Middle Ridge-Torrington 110 kV | Loading (A) | 228.3103 | 213.5154 | 151.3953 | 228.4879 | 213.7636 | 151.4489 | 229.7532 | 214.9676 | 152.1912 | 231.5909 | 216.5839 | 153.2625 | 233.695 | 218.4599 | 154.4352
SW | 60306802 | F7233 | 7233 MR - Torrington | 7233_Middle Ridge-Torrington 110 kV | Power Factor | 0.91831 | 0.92142 | 0.94389 | 0.9182 | 0.92126 | 0.94385 | 0.91779 | 0.9207 | 0.94347 | 0.91722 | 0.92005 | 0.94301 | 0.91648 | 0.91936 | 0.94255
SW | 60306802 | F7233 | 7233 MR - Torrington | 7233_Middle Ridge-Torrington 110 kV | Rating (A) | 878 | 964 | 854 | 878 | 964 | 854 | 878 | 964 | 854 | 878 | 964 | 854 | 878 | 964 | 854
SW | 60306803 | F5535 | 730 MR - South Toowo | 730_Middle Ridge-South Toowoomba 110 kV
SW | 60306803 | F5535 | 730 MR - South Toowo | 730_Middle Ridge-South Toowoomba 110 kV | % of Rated A | 23.6623 | 22.1353 | 17.1056 | 23.6337 | 22.112 | 17.0891 | 23.6836 | 22.1605 | 17.102 | 23.8235 | 22.2903 | 17.1763 | 23.8982 | 22.3618 | 17.2041
SW | 60306803 | F5535 | 730 MR - South Toowo | 730_Middle Ridge-South Toowoomba 110 kV | Loading (A) | 243.485 | 235.0771 | 163.0166 | 243.1913 | 234.8296 | 162.8592 | 243.7047 | 235.3443 | 162.9817 | 245.1435 | 236.7234 | 163.6899 | 245.9124 | 237.4827 | 163.9549
SW | 60306803 | F5535 | 730 MR - South Toowo | 730_Middle Ridge-South Toowoomba 110 kV | Power Factor | 0.99968 | 0.99884 | 0.97115 | 0.99968 | 0.99883 | 0.97107 | 0.99969 | 0.99888 | 0.97115 | 0.99976 | 0.99901 | 0.97189 | 0.99979 | 0.99908 | 0.97213
SW | 60306803 | F5535 | 730 MR - South Toowo | 730_Middle Ridge-South Toowoomba 110 kV | Rating (A) | 1029 | 1062 | 953 | 1029 | 1062 | 953 | 1029 | 1062 | 953 | 1029 | 1062 | 953 | 1029 | 1062 | 953
SW | 60306804 | F5550 | 733 MR - Yarranlea | F5550_733(Middle Ridge-Yarranlea) 110 kV
SW | 60306804 | F5550 | 733 MR - Yarranlea | F5550_733(Middle Ridge-Yarranlea) 110 kV | % of Rated A | 104.8462 | 35.7289 | 116.7758 | 104.8476 | 35.7277 | 116.7765 | 104.7866 | 35.64 | 116.7031 | 104.7679 | 35.5611 | 116.6797 | 104.6445 | 35.3567 | 116.5358
SW | 60306804 | F5550 | 733 MR - Yarranlea | F5550_733(Middle Ridge-Yarranlea) 110 kV | Loading (A) | 300.9086 | 102.1846 | 288.4362 | 300.9126 | 102.1811 | 288.438 | 300.7375 | 101.9304 | 288.2566 | 300.6838 | 101.7048 | 288.1989 | 300.3297 | 101.1202 | 287.8433
SW | 60306804 | F5550 | 733 MR - Yarranlea | F5550_733(Middle Ridge-Yarranlea) 110 kV | Power Factor | 0.80321 | 0.4841 | 0.79534 | 0.8032 | 0.48412 | 0.79534 | 0.80313 | 0.48333 | 0.79525 | 0.80331 | 0.48444 | 0.79543 | 0.8032 | 0.48199 | 0.79532
SW | 60306804 | F5550 | 733 MR - Yarranlea | F5550_733(Middle Ridge-Yarranlea) 110 kV | Rating (A) | 287 | 286 | 247 | 287 | 286 | 247 | 287 | 286 | 247 | 287 | 286 | 247 | 287 | 286 | 247
SW | 60306805 | F5565 | 736 MR - Warwick | F5565_736(Middle Ridge-Warwick) 110 kV
SW | 60306805 | F5565 | 736 MR - Warwick | F5565_736(Middle Ridge-Warwick) 110 kV | % of Rated A | 12.7958 | 17.5989 | 15.2315 | 12.8398 | 17.5365 | 15.1791 | 12.8392 | 17.5417 | 15.1811 | 12.8012 | 17.6203 | 15.2527 | 12.7847 | 17.6616 | 15.2825
SW | 60306805 | F5565 | 736 MR - Warwick | F5565_736(Middle Ridge-Warwick) 110 kV | Loading (A) | 97.6323 | 137.0954 | 104.3359 | 97.9678 | 136.6091 | 103.977 | 97.963 | 136.6501 | 103.9903 | 97.6733 | 137.2622 | 104.4809 | 97.5476 | 137.5836 | 104.6852
SW | 60306805 | F5565 | 736 MR - Warwick | F5565_736(Middle Ridge-Warwick) 110 kV | Power Factor | 0.98983 | 0.99643 | 0.99616 | 0.99005 | 0.99629 | 0.99603 | 0.99008 | 0.99623 | 0.996 | 0.99015 | 0.99618 | 0.99598 | 0.99012 | 0.99616 | 0.99597
SW | 60306805 | F5565 | 736 MR - Warwick | F5565_736(Middle Ridge-Warwick) 110 kV | Rating (A) | 763 | 779 | 685 | 763 | 779 | 685 | 763 | 779 | 685 | 763 | 779 | 685 | 763 | 779 | 685
SW | 60306930 | F3867 | PAMPAS | F3867_Pampas 33 kV
SW | 60306930 | F3867 | PAMPAS | F3867_Pampas 33 kV | % of Rated A | 73.1435 | 71.9595 | 65.1679 | 73.1433 | 71.96 | 65.1679 | 73.156 | 71.9531 | 65.1782 | 73.1587 | 71.9626 | 65.1793 | 73.1761 | 72.0465 | 65.1896
SW | 60306930 | F3867 | PAMPAS | F3867_Pampas 33 kV | Loading (A) | 219.4306 | 215.8786 | 191.5934 | 219.43 | 215.8799 | 191.5933 | 219.468 | 215.8594 | 191.6236 | 219.476 | 215.8878 | 191.6269 | 219.5283 | 216.1395 | 191.6572
SW | 60306930 | F3867 | PAMPAS | F3867_Pampas 33 kV | Power Factor | 0.84529 | 0.85662 | 0.85472 | 0.84529 | 0.85662 | 0.85472 | 0.84528 | 0.85703 | 0.85471 | 0.84528 | 0.85703 | 0.85471 | 0.84527 | 0.85696 | 0.8547
SW | 60306930 | F3867 | PAMPAS | F3867_Pampas 33 kV | Rating (A) | 300 | 300 | 294 | 300 | 300 | 294 | 300 | 300 | 294 | 300 | 300 | 294 | 300 | 300 | 294
SW | 60320796 | F5540 | 7244 TANGKAM - DALBY | F5540_7244 Tangkam-Dalby 110 kV
SW | 60320796 | F5540 | 7244 TANGKAM - DALBY | F5540_7244 Tangkam-Dalby 110 kV | % of Rated A | 23.9119 | 23.1376 | 23.9895 | 23.8439 | 23.0746 | 24.0065 | 23.7616 | 22.9936 | 23.9946 | 23.7544 | 22.9864 | 23.9947 | 23.8042 | 23.0325 | 23.9833
SW | 60320796 | F5540 | 7244 TANGKAM - DALBY | F5540_7244 Tangkam-Dalby 110 kV | Loading (A) | 63.1274 | 62.2402 | 56.3752 | 62.948 | 62.0707 | 56.4152 | 62.7306 | 61.8527 | 56.3874 | 62.7117 | 61.8334 | 56.3876 | 62.8432 | 61.9574 | 56.3607
SW | 60320796 | F5540 | 7244 TANGKAM - DALBY | F5540_7244 Tangkam-Dalby 110 kV | Power Factor | 0.21966 | 0.20437 | 0.5846 | 0.21628 | 0.20094 | 0.58551 | 0.21418 | 0.19875 | 0.58859 | 0.21403 | 0.1986 | 0.58871 | 0.21686 | 0.20148 | 0.58773
SW | 60320796 | F5540 | 7244 TANGKAM - DALBY | F5540_7244 Tangkam-Dalby 110 kV | Rating (A) | 264 | 269 | 235 | 264 | 269 | 235 | 264 | 269 | 235 | 264 | 269 | 235 | 264 | 269 | 235
SW | 60320797 | F5545 | 7245 TANGKAM - DALBY | F5545_7245 Tangkam-Dalby 110 kV
SW | 60320797 | F5545 | 7245 TANGKAM - DALBY | F5545_7245 Tangkam-Dalby 110 kV | % of Rated A | 51.5509 | 35.8553 | 33.4224 | 51.4027 | 35.7565 | 33.4465 | 51.2233 | 35.6296 | 33.4306 | 51.2077 | 35.6185 | 33.4307 | 51.3164 | 35.6907 | 33.4144
SW | 60320797 | F5545 | 7245 TANGKAM - DALBY | F5545_7245 Tangkam-Dalby 110 kV | Loading (A) | 65.4696 | 64.5396 | 58.4892 | 65.2814 | 64.3617 | 58.5314 | 65.0536 | 64.1334 | 58.5035 | 65.0338 | 64.1132 | 58.5038 | 65.1719 | 64.2433 | 58.4753
SW | 60320797 | F5545 | 7245 TANGKAM - DALBY | F5545_7245 Tangkam-Dalby 110 kV | Power Factor | 0.20289 | 0.18745 | 0.60431 | 0.19948 | 0.18398 | 0.60521 | 0.19736 | 0.18178 | 0.60826 | 0.1972 | 0.18162 | 0.60838 | 0.20006 | 0.18454 | 0.60741
SW | 60320797 | F5545 | 7245 TANGKAM - DALBY | F5545_7245 Tangkam-Dalby 110 kV | Rating (A) | 127 | 180 | 175 | 127 | 180 | 175 | 127 | 180 | 175 | 127 | 180 | 175 | 127 | 180 | 175
SW | 60322637 | F3253 | JELLICOE STREET | F3253_Jellicoe Street 33 kV
SW | 60322637 | F3253 | JELLICOE STREET | F3253_Jellicoe Street 33 kV | % of Rated A | 0.95602 | 0.67555 | 0.58593 | 0.95602 | 0.67551 | 0.58592 | 0.95574 | 0.67529 | 0.58574 | 0.95696 | 0.67496 | 0.58552 | 0.9566 | 0.67461 | 0.58529
SW | 60322637 | F3253 | JELLICOE STREET | F3253_Jellicoe Street 33 kV | Loading (A) | 2.1128 | 2.1077 | 2.1152 | 2.1128 | 2.1076 | 2.1152 | 2.1122 | 2.1069 | 2.1145 | 2.1149 | 2.1059 | 2.1137 | 2.1141 | 2.1048 | 2.1129
SW | 60322637 | F3253 | JELLICOE STREET | F3253_Jellicoe Street 33 kV | Power Factor | 0.017714 | 0.017714 | 0.017714 | 0.017714 | 0.017714 | 0.017714 | 0.017714 | 0.017714 | 0.017714 | 0.017714 | 0.017714 | 0.017714 | 0.017714 | 0.017714 | 0.017714
SW | 60322637 | F3253 | JELLICOE STREET | F3253_Jellicoe Street 33 kV | Rating (A) | 221 | 312 | 361 | 221 | 312 | 361 | 221 | 312 | 361 | 221 | 312 | 361 | 221 | 312 | 361
SW | 60327274 | F4132 | SHIRLEY ROAD FEEDER | F4132_Shirley Road 33 kV
SW | 60327274 | F4132 | SHIRLEY ROAD FEEDER | F4132_Shirley Road 33 kV | % of Rated A | 75.1792 | 60.3043 | 25.9751 | 76.0564 | 61.023 | 26.2704 | 76.9601 | 61.7365 | 26.5692 | 77.8796 | 62.4846 | 26.8728 | 78.5674 | 63.9385 | 27.4645
SW | 60327274 | F4132 | SHIRLEY ROAD FEEDER | F4132_Shirley Road 33 kV | Loading (A) | 140.5843 | 162.8209 | 81.0415 | 142.2247 | 164.7614 | 81.9629 | 143.9147 | 166.6877 | 82.8951 | 145.6341 | 168.7077 | 83.8424 | 146.9203 | 172.633 | 85.6887
SW | 60327274 | F4132 | SHIRLEY ROAD FEEDER | F4132_Shirley Road 33 kV | Power Factor | 0.98395 | 0.98263 | 0.98705 | 0.98385 | 0.98251 | 0.987 | 0.98374 | 0.98263 | 0.98695 | 0.98364 | 0.9825 | 0.9869 | 0.98366 | 0.98225 | 0.98691
SW | 60327274 | F4132 | SHIRLEY ROAD FEEDER | F4132_Shirley Road 33 kV | Rating (A) | 187 | 270 | 312 | 187 | 270 | 312 | 187 | 270 | 312 | 187 | 270 | 312 | 187 | 270 | 312
SW | 60330365 | 7235 | Bulli Creek - Waggamba 132 kV | 7235_Bulli Creek - Waggamba 132 kV
SW | 60330365 | 7235 | Bulli Creek - Waggamba 132 kV | 7235_Bulli Creek - Waggamba 132 kV | % of Rated A | 13.7687 | 14.7361 | 13.523 | 13.7687 | 14.7361 | 13.523 | 13.8251 | 14.7963 | 13.577 | 13.825 | 14.7966 | 13.5771 | 13.8252 | 14.7968 | 13.5772
SW | 60330365 | 7235 | Bulli Creek - Waggamba 132 kV | 7235_Bulli Creek - Waggamba 132 kV | Loading (A) | 89.4968 | 97.111 | 77.7573 | 89.4967 | 97.1109 | 77.7573 | 89.8634 | 97.5078 | 78.0678 | 89.8625 | 97.5094 | 78.0684 | 89.8635 | 97.5108 | 78.0691
SW | 60330365 | 7235 | Bulli Creek - Waggamba 132 kV | 7235_Bulli Creek - Waggamba 132 kV | Power Factor | 0.96922 | 0.97701 | 0.95221 | 0.96922 | 0.97701 | 0.95221 | 0.96963 | 0.97734 | 0.9528 | 0.96966 | 0.97735 | 0.9528 | 0.96966 | 0.97735 | 0.9528
SW | 60330365 | 7235 | Bulli Creek - Waggamba 132 kV | 7235_Bulli Creek - Waggamba 132 kV | Rating (A) | 650 | 659 | 575 | 650 | 659 | 575 | 650 | 659 | 575 | 650 | 659 | 575 | 650 | 659 | 575
SW | 60330908 | F7234 | 7234 MR - Torrington | 7234_Middle Ridge-Torrington 110 kV
SW | 60330908 | F7234 | 7234 MR - Torrington | 7234_Middle Ridge-Torrington 110 kV | % of Rated A | 27.0106 | 23.0098 | 18.4267 | 27.0316 | 23.0365 | 18.4332 | 27.181 | 23.1661 | 18.5235 | 27.3981 | 23.34 | 18.6537 | 27.6467 | 23.5419 | 18.7962
SW | 60330908 | F7234 | 7234 MR - Torrington | 7234_Middle Ridge-Torrington 110 kV | Loading (A) | 236.5711 | 221.2422 | 156.8744 | 236.7551 | 221.4994 | 156.9299 | 238.0661 | 222.7468 | 157.699 | 239.9701 | 224.4215 | 158.8089 | 242.1502 | 226.3653 | 160.024
SW | 60330908 | F7234 | 7234 MR - Torrington | 7234_Middle Ridge-Torrington 110 kV | Power Factor | 0.91939 | 0.92247 | 0.9448 | 0.91928 | 0.92231 | 0.94476 | 0.91887 | 0.92175 | 0.94438 | 0.91832 | 0.92111 | 0.94393 | 0.91758 | 0.92042 | 0.94347
SW | 60330908 | F7234 | 7234 MR - Torrington | 7234_Middle Ridge-Torrington 110 kV | Rating (A) | 878 | 964 | 854 | 878 | 964 | 854 | 878 | 964 | 854 | 878 | 964 | 854 | 878 | 964 | 854
SW | 82639691 | 3900 | PERANGA | 3900_Peranga 33 kV
SW | 82639691 | 3900 | PERANGA | 3900_Peranga 33 kV | % of Rated A | 24.8171 | 30.6343 | 21.5527 | 24.8157 | 30.6328 | 21.5518 | 24.8153 | 30.6339 | 21.5514 | 24.8161 | 30.6348 | 21.5517 | 24.8161 | 30.6351 | 21.5516
SW | 82639691 | 3900 | PERANGA | 3900_Peranga 33 kV | Loading (A) | 24.8171 | 30.6343 | 21.5527 | 24.8157 | 30.6328 | 21.5518 | 24.8153 | 30.6339 | 21.5514 | 24.8161 | 30.6348 | 21.5517 | 24.8161 | 30.6351 | 21.5516
SW | 82639691 | 3900 | PERANGA | 3900_Peranga 33 kV | Power Factor | 0.94475 | 0.93393 | 0.95203 | 0.94476 | 0.93393 | 0.95204 | 0.94476 | 0.93393 | 0.95204 | 0.94476 | 0.93393 | 0.95204 | 0.94476 | 0.93392 | 0.95204
SW | 82639691 | 3900 | PERANGA | 3900_Peranga 33 kV | Rating (A) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
SW | 82640976 | EB10 | ACLAND | EB10_Acland 33 kV
SW | 82640976 | EB10 | ACLAND | EB10_Acland 33 kV | % of Rated A | 12.3796 | 8.9533 | 11.0884 | 12.379 | 8.9528 | 11.0879 | 12.3787 | 8.9527 | 11.0877 | 12.3789 | 8.953 | 11.0878 | 12.3789 | 8.953 | 11.0877
SW | 82640976 | EB10 | ACLAND | EB10_Acland 33 kV | Loading (A) | 11.5131 | 8.3266 | 10.3122 | 11.5125 | 8.3261 | 10.3117 | 11.5122 | 8.326 | 10.3115 | 11.5124 | 8.3263 | 10.3117 | 11.5123 | 8.3263 | 10.3116
SW | 82640976 | EB10 | ACLAND | EB10_Acland 33 kV | Power Factor | 0.83863 | 0.85435 | 0.84411 | 0.83863 | 0.85436 | 0.84411 | 0.83864 | 0.85436 | 0.84412 | 0.83863 | 0.85436 | 0.84411 | 0.83864 | 0.85436 | 0.84411
SW | 82640976 | EB10 | ACLAND | EB10_Acland 33 kV | Rating (A) | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93
SW | 83015720 | 7174 | 7174 FDR | 7174_Roma-Columboola 2 132 kV
SW | 83015720 | 7174 | 7174 FDR | 7174_Roma-Columboola 2 132 kV | % of Rated A | 27.4316 | 16.2577 | 11.7289 | 27.4342 | 16.2592 | 11.7299 | 27.4322 | 16.2578 | 11.7293 | 27.5342 | 16.3158 | 11.7634 | 27.5283 | 16.312 | 11.7616
SW | 83015720 | 7174 | 7174 FDR | 7174_Roma-Columboola 2 132 kV | Loading (A) | 47.4567 | 45.1965 | 32.6064 | 47.4611 | 45.2005 | 32.6091 | 47.4578 | 45.1966 | 32.6075 | 47.6341 | 45.3581 | 32.7021 | 47.6239 | 45.3473 | 32.6972
SW | 83015720 | 7174 | 7174 FDR | 7174_Roma-Columboola 2 132 kV | Power Factor | 0.9216 | 0.91727 | 0.80519 | 0.9216 | 0.91727 | 0.8052 | 0.92155 | 0.91725 | 0.80519 | 0.92248 | 0.91817 | 0.80678 | 0.92246 | 0.91814 | 0.80673
SW | 83015720 | 7174 | 7174 FDR | 7174_Roma-Columboola 2 132 kV | Rating (A) | 173 | 278 | 278 | 173 | 278 | 278 | 173 | 278 | 278 | 173 | 278 | 278 | 173 | 278 | 278
SW | 83015723 | 7164 | 7164 FDR | 7164_Roma-Columboola 1 132 kV
SW | 83015723 | 7164 | 7164 FDR | 7164_Roma-Columboola 1 132 kV | % of Rated A | 27.4316 | 16.2577 | 11.7289 | 27.4341 | 16.2592 | 11.7299 | 27.4322 | 16.2578 | 11.7293 | 27.5342 | 16.3158 | 11.7634 | 27.5283 | 16.312 | 11.7616
SW | 83015723 | 7164 | 7164 FDR | 7164_Roma-Columboola 1 132 kV | Loading (A) | 47.4567 | 45.1965 | 32.6064 | 47.4611 | 45.2005 | 32.6091 | 47.4578 | 45.1966 | 32.6075 | 47.6341 | 45.358 | 32.7021 | 47.6239 | 45.3473 | 32.6972
SW | 83015723 | 7164 | 7164 FDR | 7164_Roma-Columboola 1 132 kV | Power Factor | 0.9216 | 0.91727 | 0.80518 | 0.9216 | 0.91727 | 0.8052 | 0.92155 | 0.91725 | 0.80519 | 0.92248 | 0.91817 | 0.80678 | 0.92246 | 0.91814 | 0.80673
SW | 83015723 | 7164 | 7164 FDR | 7164_Roma-Columboola 1 132 kV | Rating (A) | 173 | 278 | 278 | 173 | 278 | 278 | 173 | 278 | 278 | 173 | 278 | 278 | 173 | 278 | 278
SW | 83921739 | 3153 | CECIL PLAINS ROAD | 3153_Cecil Plains Road 33 kV
SW | 83921739 | 3153 | CECIL PLAINS ROAD | 3153_Cecil Plains Road 33 kV | % of Rated A | 18.2547 | 15.6826 | 17.5444 | 18.2512 | 15.6793 | 17.5421 | 18.2464 | 15.6757 | 17.5376 | 18.2472 | 15.6771 | 17.5381 | 18.2508 | 15.7276 | 17.5408
SW | 83921739 | 3153 | CECIL PLAINS ROAD | 3153_Cecil Plains Road 33 kV | Loading (A) | 16.9769 | 15.6826 | 17.5444 | 16.9736 | 15.6793 | 17.5421 | 16.9692 | 15.6757 | 17.5376 | 16.9699 | 15.6771 | 17.5381 | 16.9732 | 15.7276 | 17.5408
SW | 83921739 | 3153 | CECIL PLAINS ROAD | 3153_Cecil Plains Road 33 kV | Power Factor | 0.96138 | 0.98234 | 0.97395 | 0.96141 | 0.98236 | 0.97397 | 0.96145 | 0.98238 | 0.974 | 0.96144 | 0.98238 | 0.97399 | 0.96141 | 0.98167 | 0.97398
SW | 83921739 | 3153 | CECIL PLAINS ROAD | 3153_Cecil Plains Road 33 kV | Rating (A) | 93 | 100 | 100 | 93 | 100 | 100 | 93 | 100 | 100 | 93 | 100 | 100 | 93 | 100 | 100
SW | 83921742 | 3154 | CENTRAL DALBY 1 | 3154_Central Dalby 1 33 kV
SW | 83921742 | 3154 | CENTRAL DALBY 1 | 3154_Central Dalby 1 33 kV | % of Rated A | 38.1982 | 37.4824 | 24.6743 | 37.9722 | 37.2616 | 24.5373 | 37.9621 | 37.2518 | 24.5311 | 37.9649 | 37.2546 | 24.5318 | 37.9748 | 37.2645 | 24.5354
SW | 83921742 | 3154 | CENTRAL DALBY 1 | 3154_Central Dalby 1 33 kV | Loading (A) | 171.8921 | 168.671 | 101.1644 | 170.8747 | 167.6773 | 100.6025 | 170.8292 | 167.6329 | 100.5774 | 170.8419 | 167.6455 | 100.5802 | 170.8865 | 167.6902 | 100.5951
SW | 83921742 | 3154 | CENTRAL DALBY 1 | 3154_Central Dalby 1 33 kV | Power Factor | 0.94299 | 0.94382 | 0.9608 | 0.94326 | 0.94408 | 0.96095 | 0.94328 | 0.9441 | 0.96096 | 0.94327 | 0.9441 | 0.96096 | 0.94325 | 0.94408 | 0.96095
SW | 83921742 | 3154 | CENTRAL DALBY 1 | 3154_Central Dalby 1 33 kV | Rating (A) | 450 | 450 | 410 | 450 | 450 | 410 | 450 | 450 | 410 | 450 | 450 | 410 | 450 | 450 | 410
SW | 84000793 | 3178 | WILKIE CREEK | 3178_Wilkie Creek 33 kV
SW | 84000793 | 3178 | WILKIE CREEK | 3178_Wilkie Creek 33 kV | % of Rated A | 4.1367 | 4.1229 | 4.145 | 4.1367 | 4.1229 | 4.145 | 4.1367 | 4.1229 | 4.145 | 4.1367 | 4.1229 | 4.145 | 4.1367 | 4.1229 | 4.145
SW | 84000793 | 3178 | WILKIE CREEK | 3178_Wilkie Creek 33 kV | Loading (A) | 3.8472 | 3.8343 | 3.8548 | 3.8472 | 3.8343 | 3.8548 | 3.8472 | 3.8343 | 3.8548 | 3.8472 | 3.8343 | 3.8548 | 3.8472 | 3.8343 | 3.8548
SW | 84000793 | 3178 | WILKIE CREEK | 3178_Wilkie Creek 33 kV | Power Factor | 0.03626 | 0.047899 | 0.02963 | 0.03626 | 0.047899 | 0.02963 | 0.03626 | 0.047899 | 0.02963 | 0.03626 | 0.047899 | 0.02963 | 0.03626 | 0.047899 | 0.02963
SW | 84000793 | 3178 | WILKIE CREEK | 3178_Wilkie Creek 33 kV | Rating (A) | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93
SW | 84109456 | 7314 | 7314 DALBY EAST | 7314_Dalby East 110 kV
SW | 84109456 | 7314 | 7314 DALBY EAST | 7314_Dalby East 110 kV | % of Rated A | 56.8675 | 55.0734 | 62.0401 | 56.8773 | 55.0766 | 62.0452 | 56.8898 | 55.0894 | 62.199 | 56.8958 | 55.0922 | 62.2015 | 56.8913 | 55.0863 | 62.1963
SW | 84109456 | 7314 | 7314 DALBY EAST | 7314_Dalby East 110 kV | Loading (A) | 157.523 | 162.4666 | 163.1654 | 157.5501 | 162.4758 | 163.1789 | 157.5848 | 162.5138 | 163.5834 | 157.6014 | 162.5221 | 163.5901 | 157.5888 | 162.5047 | 163.5763
SW | 84109456 | 7314 | 7314 DALBY EAST | 7314_Dalby East 110 kV | Power Factor | 0.93147 | 0.89828 | 0.88866 | 0.93117 | 0.89818 | 0.88854 | 0.93094 | 0.89794 | 0.88422 | 0.93107 | 0.89805 | 0.8843 | 0.93138 | 0.8983 | 0.88449
SW | 84109456 | 7314 | 7314 DALBY EAST | 7314_Dalby East 110 kV | Rating (A) | 277 | 295 | 263 | 277 | 295 | 263 | 277 | 295 | 263 | 277 | 295 | 263 | 277 | 295 | 263
SW | 84170804 | 3196 | TARA | 3196_Tara 33 kV
SW | 84170804 | 3196 | TARA | 3196_Tara 33 kV | % of Rated A | 1.081 | 0.72811 | 0.73725 | 1.081 | 0.72811 | 0.73725 | 1.081 | 0.72811 | 0.73725 | 1.081 | 0.72811 | 0.73725 | 1.081 | 0.72811 | 0.73725
SW | 84170804 | 3196 | TARA | 3196_Tara 33 kV | Loading (A) | 1.762 | 1.762 | 1.762 | 1.762 | 1.762 | 1.762 | 1.762 | 1.762 | 1.762 | 1.762 | 1.762 | 1.762 | 1.762 | 1.762 | 1.762
SW | 84170804 | 3196 | TARA | 3196_Tara 33 kV | Power Factor | 0.00023722 | 0.00023722 | 0.00023722 | 0.00023722 | 0.00023722 | 0.00023722 | 0.00023722 | 0.00023722 | 0.00023722 | 0.00023722 | 0.00023722 | 0.00023722 | 0.00023722 | 0.00023722 | 0.00023722
SW | 84170804 | 3196 | TARA | 3196_Tara 33 kV | Rating (A) | 163 | 242 | 239 | 163 | 242 | 239 | 163 | 242 | 239 | 163 | 242 | 239 | 163 | 242 | 239
SW | 84301618 | 3203 | MILES | 3203_Miles 33 kV
SW | 84301618 | 3203 | MILES | 3203_Miles 33 kV | % of Rated A | 86.9649 | 93.6694 | 69.2009 | 86.9652 | 93.6698 | 69.2013 | 86.9653 | 93.6701 | 69.2013 | 86.9668 | 93.6725 | 69.2045 | 86.9671 | 93.6729 | 69.203
SW | 84301618 | 3203 | MILES | 3203_Miles 33 kV | Loading (A) | 157.4065 | 169.5416 | 125.2537 | 157.407 | 169.5424 | 125.2543 | 157.4072 | 169.5428 | 125.2544 | 157.4099 | 169.5472 | 125.2601 | 157.4104 | 169.5479 | 125.2574
SW | 84301618 | 3203 | MILES | 3203_Miles 33 kV | Power Factor | 0.99089 | 0.99137 | 0.99581 | 0.99089 | 0.99137 | 0.99581 | 0.99089 | 0.99137 | 0.99581 | 0.99089 | 0.99137 | 0.9958 | 0.99089 | 0.99137 | 0.99581
SW | 84301618 | 3203 | MILES | 3203_Miles 33 kV | Rating (A) | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181
SW | 84976334 | 7448 | 7448 SOTO - TOCE 110KV | 7448_South Toowoomba-TWCE 110 kV
SW | 84976334 | 7448 | 7448 SOTO - TOCE 110KV | 7448_South Toowoomba-TWCE 110 kV | % of Rated A | 20.3125 | 14.3562 | 15.7122 | 20.2279 | 14.2974 | 15.6476 | 20.1444 | 14.2396 | 15.5833 | 20.1468 | 14.2421 | 15.5846 | 20.0638 | 14.185 | 15.5207
SW | 84976334 | 7448 | 7448 SOTO - TOCE 110KV | 7448_South Toowoomba-TWCE 110 kV | Loading (A) | 85.3126 | 60.296 | 65.9914 | 84.9572 | 60.049 | 65.7199 | 84.6064 | 59.8062 | 65.45 | 84.6166 | 59.8167 | 65.4551 | 84.2681 | 59.577 | 65.1868
SW | 84976334 | 7448 | 7448 SOTO - TOCE 110KV | 7448_South Toowoomba-TWCE 110 kV | Power Factor | 0.9404 | 0.94883 | 0.94691 | 0.94054 | 0.94892 | 0.94701 | 0.94067 | 0.949 | 0.94711 | 0.94066 | 0.949 | 0.9471 | 0.94079 | 0.94908 | 0.9472
SW | 84976334 | 7448 | 7448 SOTO - TOCE 110KV | 7448_South Toowoomba-TWCE 110 kV | Rating (A) | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420
SW | 84976560 | 7449 | SOTO - TWCE 110KV 7449 FDR | 7449 South Toowoomba-TWCE 110 kV
SW | 84976560 | 7449 | SOTO - TWCE 110KV 7449 FDR | 7449 South Toowoomba-TWCE 110 kV | % of Rated A | 10.6561 | 8.7844 | 9.1912 | 10.6271 | 8.7684 | 9.1724 | 10.5984 | 8.7524 | 9.1537 | 10.5988 | 8.7522 | 9.1537 | 10.5702 | 8.7362 | 9.135
SW | 84976560 | 7449 | SOTO - TWCE 110KV 7449 FDR | 7449 South Toowoomba-TWCE 110 kV | Loading (A) | 44.7557 | 36.8943 | 38.6032 | 44.6339 | 36.8271 | 38.5243 | 44.5131 | 36.76 | 38.4456 | 44.5149 | 36.7594 | 38.4456 | 44.3948 | 36.6922 | 38.3672
SW | 84976560 | 7449 | SOTO - TWCE 110KV 7449 FDR | 7449 South Toowoomba-TWCE 110 kV | Power Factor | 0.90887 | 0.79136 | 0.82461 | 0.90775 | 0.7897 | 0.82306 | 0.90664 | 0.78808 | 0.82151 | 0.9067 | 0.78822 | 0.82156 | 0.90559 | 0.78663 | 0.82002
SW | 84976560 | 7449 | SOTO - TWCE 110KV 7449 FDR | 7449 South Toowoomba-TWCE 110 kV | Rating (A) | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420
SW | 85177784 | 7374 | Roma Power Station 132 kV | 7374_Roma Power Station 132 kV
SW | 85177784 | 7374 | Roma Power Station 132 kV | 7374_Roma Power Station 132 kV | % of Rated A | 0.0075994 | 0.0076063 | 0.0076748 | 0.0075994 | 0.0076063 | 0.0076748 | 0.0075994 | 0.0076063 | 0.0076748 | 0.0075992 | 0.0076056 | 0.0076745 | 0.0075992 | 0.0076056 | 0.0076745
SW | 85177784 | 7374 | Roma Power Station 132 kV | 7374_Roma Power Station 132 kV | Loading (A) | 0.033133 | 0.033164 | 0.033462 | 0.033133 | 0.033164 | 0.033462 | 0.033133 | 0.033164 | 0.033462 | 0.033132 | 0.033161 | 0.033461 | 0.033132 | 0.033161 | 0.033461
SW | 85177784 | 7374 | Roma Power Station 132 kV | 7374_Roma Power Station 132 kV | Power Factor | 3.0185e-06 | 3.0199e-06 | 3.013e-06 | 3.0196e-06 | 3.0091e-06 | 3.0128e-06 | 3.0182e-06 | 3.0216e-06 | 3.0216e-06 | 3.0162e-06 | 3.0187e-06 | 3.0173e-06 | 3.0173e-06 | 3.0197e-06 | 3.0137e-06
SW | 85177784 | 7374 | Roma Power Station 132 kV | 7374_Roma Power Station 132 kV | Rating (A) | 436 | 436 | 436 | 436 | 436 | 436 | 436 | 436 | 436 | 436 | 436 | 436 | 436 | 436 | 436
WB | 40001217 | 7188 | Gin Gin - Korenan QR | 7188_Gin Gin - Korenan QR 132 kV
WB | 40001217 | 7188 | Gin Gin - Korenan QR | 7188_Gin Gin - Korenan QR 132 kV | % of Rated A | 6.1001 | 5.5503 | 5.5634 | 6.1001 | 5.5504 | 5.5633 | 6.1002 | 5.5505 | 5.5632 | 6.1002 | 5.5508 | 5.563 | 6.1401 | 5.5958 | 5.5853
WB | 40001217 | 7188 | Gin Gin - Korenan QR | 7188_Gin Gin - Korenan QR 132 kV | Loading (A) | 23.0585 | 23.4223 | 21.4748 | 23.0585 | 23.4228 | 21.4745 | 23.0586 | 23.4232 | 21.4741 | 23.0588 | 23.4242 | 21.4733 | 23.2097 | 23.6145 | 21.5593
WB | 40001217 | 7188 | Gin Gin - Korenan QR | 7188_Gin Gin - Korenan QR 132 kV | Power Factor | 0.75753 | 0.78039 | 0.67443 | 0.75754 | 0.78062 | 0.6745 | 0.75769 | 0.78082 | 0.67458 | 0.75795 | 0.78125 | 0.67474 | 0.76298 | 0.78696 | 0.67898
WB | 40001217 | 7188 | Gin Gin - Korenan QR | 7188_Gin Gin - Korenan QR 132 kV | Rating (A) | 378 | 422 | 386 | 378 | 422 | 386 | 378 | 422 | 386 | 378 | 422 | 386 | 378 | 422 | 386
WB | 50000001 | 7187 | 7187 GIN GIN - BUNDABERG T/LINE | 7187_Gin Gin - Bundaberg 132 kV
WB | 50000001 | 7187 | 7187 GIN GIN - BUNDABERG T/LINE | 7187_Gin Gin - Bundaberg 132 kV | % of Rated A | 25.9921 | 38.9639 | 30.9114 | 26.7533 | 39.8406 | 31.6511 | 27.2928 | 40.4527 | 32.0763 | 27.6672 | 40.921 | 32.3647 | 27.8629 | 41.1509 | 32.5222
WB | 50000001 | 7187 | 7187 GIN GIN - BUNDABERG T/LINE | 7187_Gin Gin - Bundaberg 132 kV | Loading (A) | 176.4863 | 284.7171 | 204.9426 | 181.6547 | 291.1372 | 209.847 | 185.3184 | 295.5707 | 212.666 | 187.8601 | 298.8614 | 214.5782 | 189.189 | 300.5147 | 215.6221
WB | 50000001 | 7187 | 7187 GIN GIN - BUNDABERG T/LINE | 7187_Gin Gin - Bundaberg 132 kV | Power Factor | 0.99884 | 0.99972 | 0.99301 | 0.9987 | 0.99972 | 0.99397 | 0.99913 | 0.9996 | 0.99482 | 0.99968 | 0.99916 | 0.99609 | 0.99976 | 0.99905 | 0.99636
WB | 50000001 | 7187 | 7187 GIN GIN - BUNDABERG T/LINE | 7187_Gin Gin - Bundaberg 132 kV | Rating (A) | 679 | 731 | 663 | 679 | 731 | 663 | 679 | 731 | 663 | 679 | 731 | 663 | 679 | 731 | 663
WB | 50000002 | 7190 | 7190 WOOLOOGA - MUNGAR T/LINE | 7190_Woolooga-Mungar 132 kV
WB | 50000002 | 7190 | 7190 WOOLOOGA - MUNGAR T/LINE | 7190_Woolooga-Mungar 132 kV | % of Rated A | 2.9778 | 2.5211 | 2.9375 | 2.978 | 2.5208 | 2.9374 | 2.9781 | 2.5207 | 2.9373 | 2.9782 | 2.5205 | 2.9373 | 2.9782 | 2.5204 | 2.9372
WB | 50000002 | 7190 | 7190 WOOLOOGA - MUNGAR T/LINE | 7190_Woolooga-Mungar 132 kV | Loading (A) | 7.4147 | 15.1265 | 15.9212 | 7.4153 | 15.1249 | 15.9205 | 7.4154 | 15.1241 | 15.9203 | 7.4157 | 15.1228 | 15.9199 | 7.4158 | 15.1224 | 15.9198
WB | 50000002 | 7190 | 7190 WOOLOOGA - MUNGAR T/LINE | 7190_Woolooga-Mungar 132 kV | Power Factor | 1 | 0.16163 | 0.34614 | 1 | 0.16166 | 0.34617 | 1 | 0.16168 | 0.34618 | 1 | 0.16171 | 0.3462 | 1 | 0.16172 | 0.34621
WB | 50000002 | 7190 | 7190 WOOLOOGA - MUNGAR T/LINE | 7190_Woolooga-Mungar 132 kV | Rating (A) | 249 | 600 | 542 | 249 | 600 | 542 | 249 | 600 | 542 | 249 | 600 | 542 | 249 | 600 | 542
WB | 50000003 | 7215 | 7215 BUNDABERG - ISIS NO.1 | 7215_Bundaberg - ISIS No 1 132 kV
WB | 50000003 | 7215 | 7215 BUNDABERG - ISIS NO.1 | 7215_Bundaberg - ISIS No 1 132 kV | % of Rated A | 48.0137 | 13.8515 | 29.6838 | 47.4322 | 12.9682 | 29.2593 | 47.3315 | 12.9239 | 29.2187 | 47.4431 | 13.0721 | 29.3038 | 47.4548 | 13.0948 | 29.2957
WB | 50000003 | 7215 | 7215 BUNDABERG - ISIS NO.1 | 7215_Bundaberg - ISIS No 1 132 kV | Loading (A) | 119.074 | 54.8518 | 116.6575 | 117.6318 | 51.3542 | 114.9891 | 117.3822 | 51.1788 | 114.8295 | 117.6588 | 51.7656 | 115.1641 | 117.6879 | 51.8556 | 115.1321
WB | 50000003 | 7215 | 7215 BUNDABERG - ISIS NO.1 | 7215_Bundaberg - ISIS No 1 132 kV | Power Factor | 0.98747 | 0.87377 | 0.98431 | 0.98587 | 0.88112 | 0.982 | 0.98582 | 0.87877 | 0.98187 | 0.98682 | 0.8778 | 0.98162 | 0.98698 | 0.87615 | 0.98178
WB | 50000003 | 7215 | 7215 BUNDABERG - ISIS NO.1 | 7215_Bundaberg - ISIS No 1 132 kV | Rating (A) | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393
WB | 50000006 | 786 | 786 GIN GIN - BUNDABERG T/LINE | 786_Gin Gin - Bundaberg 132 kV
WB | 50000006 | 786 | 786 GIN GIN - BUNDABERG T/LINE | 786_Gin Gin - Bundaberg 132 kV | % of Rated A | 62.4533 | 59.2975 | 42.5808 | 64.2822 | 60.631 | 43.5998 | 65.5786 | 61.5634 | 44.1855 | 66.478 | 62.2801 | 44.5828 | 66.9483 | 62.6306 | 44.7997
WB | 50000006 | 786 | 786 GIN GIN - BUNDABERG T/LINE | 786_Gin Gin - Bundaberg 132 kV | Loading (A) | 176.7427 | 285.2033 | 205.2397 | 181.9185 | 291.6314 | 210.1511 | 185.5875 | 296.0886 | 212.9741 | 188.1328 | 299.4354 | 214.8891 | 189.4637 | 301.102 | 215.9344
WB | 50000006 | 786 | 786 GIN GIN - BUNDABERG T/LINE | 786_Gin Gin - Bundaberg 132 kV | Power Factor | 0.99882 | 0.99992 | 0.99296 | 0.99868 | 0.99993 | 0.99392 | 0.99912 | 0.99987 | 0.99478 | 0.99967 | 0.9996 | 0.99605 | 0.99975 | 0.99952 | 0.99633
WB | 50000006 | 786 | 786 GIN GIN - BUNDABERG T/LINE | 786_Gin Gin - Bundaberg 132 kV | Rating (A) | 283 | 481 | 482 | 283 | 481 | 482 | 283 | 481 | 482 | 283 | 481 | 482 | 283 | 481 | 482
WB | 50000008 | M029 | BUNDABERG - FARNSFIELD T/LINE | M029_Bundaberg - Farnsfield 66 kV
WB | 50000008 | M029 | BUNDABERG - FARNSFIELD T/LINE | M029_Bundaberg - Farnsfield 66 kV | % of Rated A | 43.0672 | 31.3247 | 31.4792 | 43.0177 | 31.3213 | 31.4793 | 43.0756 | 31.1352 | 31.3064 | 43.6967 | 31.6235 | 31.7615 | 43.7223 | 31.4106 | 31.7766
WB | 50000008 | M029 | BUNDABERG - FARNSFIELD T/LINE | M029_Bundaberg - Farnsfield 66 kV | Loading (A) | 82.9791 | 85.6891 | 83.9092 | 82.8834 | 85.6797 | 83.9096 | 82.9953 | 85.1696 | 83.4475 | 84.194 | 86.5078 | 84.6627 | 84.2435 | 85.9234 | 84.703
WB | 50000008 | M029 | BUNDABERG - FARNSFIELD T/LINE | M029_Bundaberg - Farnsfield 66 kV | Power Factor | 0.8334 | 0.83196 | 0.83275 | 0.83349 | 0.83197 | 0.83275 | 0.83339 | 0.83232 | 0.83308 | 0.83272 | 0.83153 | 0.83248 | 0.83267 | 0.83216 | 0.83245
WB | 50000008 | M029 | BUNDABERG - FARNSFIELD T/LINE | M029_Bundaberg - Farnsfield 66 kV | Rating (A) | 193 | 274 | 267 | 193 | 274 | 267 | 193 | 274 | 267 | 193 | 274 | 267 | 193 | 274 | 267
WB | 50000009 | M036 | BBERG - STH BUNDABERG T/LINE | M036_Bundaberg-South Bundaberg 66 kV
WB | 50000009 | M036 | BBERG - STH BUNDABERG T/LINE | M036_Bundaberg-South Bundaberg 66 kV | % of Rated A | 53.0755 | 55.8087 | 46.0548 | 54.1515 | 56.9351 | 47.1926 | 55.3752 | 57.5344 | 48.2303 | 56.1668 | 58.4791 | 48.807 | 56.5948 | 58.9692 | 49.1659
WB | 50000009 | M036 | BBERG - STH BUNDABERG T/LINE | M036_Bundaberg-South Bundaberg 66 kV | Loading (A) | 233.0016 | 267.8819 | 179.1533 | 237.725 | 273.2887 | 183.5791 | 243.0972 | 276.1649 | 187.6157 | 246.5722 | 280.6998 | 189.8591 | 248.4514 | 283.052 | 191.2553
WB | 50000009 | M036 | BBERG - STH BUNDABERG T/LINE | M036_Bundaberg-South Bundaberg 66 kV | Power Factor | 0.98235 | 0.99151 | 0.95859 | 0.97452 | 0.98539 | 0.94837 | 0.97647 | 0.98618 | 0.95163 | 0.98001 | 0.98895 | 0.95722 | 0.98064 | 0.98945 | 0.95825
WB | 50000009 | M036 | BBERG - STH BUNDABERG T/LINE | M036_Bundaberg-South Bundaberg 66 kV | Rating (A) | 439 | 480 | 389 | 439 | 480 | 389 | 439 | 480 | 389 | 439 | 480 | 389 | 439 | 480 | 389
WB | 50000018 | M046 | TARONG-CABOONBAH T/LINE | M046_Tarong-Caboonbah 66 kV
WB | 50000018 | M046 | TARONG-CABOONBAH T/LINE | M046_Tarong-Caboonbah 66 kV | % of Rated A | 28.7078 | 16.9583 | 19.3067 | 28.7328 | 16.9784 | 19.3237 | 28.733 | 16.9786 | 19.3238 | 28.7357 | 16.9815 | 19.3253 | 28.7362 | 16.9824 | 19.3255
WB | 50000018 | M046 | TARONG-CABOONBAH T/LINE | M046_Tarong-Caboonbah 66 kV | Loading (A) | 71.4825 | 64.7806 | 71.4348 | 71.5447 | 64.8574 | 71.4976 | 71.5451 | 64.8582 | 71.498 | 71.5519 | 64.8694 | 71.5036 | 71.5533 | 64.8726 | 71.5045
WB | 50000018 | M046 | TARONG-CABOONBAH T/LINE | M046_Tarong-Caboonbah 66 kV | Power Factor | 0.89013 | 0.89424 | 0.89024 | 0.89005 | 0.89413 | 0.89017 | 0.89005 | 0.89413 | 0.89017 | 0.89004 | 0.89411 | 0.89016 | 0.89004 | 0.89411 | 0.89016
WB | 50000018 | M046 | TARONG-CABOONBAH T/LINE | M046_Tarong-Caboonbah 66 kV | Rating (A) | 249 | 382 | 370 | 249 | 382 | 370 | 249 | 382 | 370 | 249 | 382 | 370 | 249 | 382 | 370
WB | 50000048 | M030 | FARNSFIELD - CHILDERS T/LINE | M030_Farnsfield - Childers 66 kV
WB | 50000048 | M030 | FARNSFIELD - CHILDERS T/LINE | M030_Farnsfield - Childers 66 kV | % of Rated A | 50.5619 | 59.9919 | 59.143 | 50.6894 | 59.2188 | 59.3435 | 50.8199 | 59.3562 | 59.4831 | 51.3668 | 60.0834 | 59.9341 | 51.3946 | 60.1338 | 59.965
WB | 50000048 | M030 | FARNSFIELD - CHILDERS T/LINE | M030_Farnsfield - Childers 66 kV | Loading (A) | 66.6535 | 100.0681 | 93.9212 | 66.8215 | 98.7775 | 94.2397 | 66.9935 | 99.0069 | 94.4617 | 67.7144 | 100.2205 | 95.18 | 67.751 | 100.3046 | 95.2292
WB | 50000048 | M030 | FARNSFIELD - CHILDERS T/LINE | M030_Farnsfield - Childers 66 kV | Power Factor | 0.95924 | 0.92171 | 0.92706 | 0.95879 | 0.92403 | 0.92645 | 0.95833 | 0.92361 | 0.92603 | 0.95715 | 0.92216 | 0.92759 | 0.95706 | 0.92201 | 0.9275
WB | 50000048 | M030 | FARNSFIELD - CHILDERS T/LINE | M030_Farnsfield - Childers 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
WB | 50000069 | M024 | GAYNDAH - MUNDUBBERA T/LINE | M024_Gayndah - Mundubbera 66 kV
WB | 50000069 | M024 | GAYNDAH - MUNDUBBERA T/LINE | M024_Gayndah - Mundubbera 66 kV | % of Rated A | 68.282 | 51.9177 | 41.1355 | 68.4174 | 52.0522 | 41.1258 | 67.6584 | 52.2753 | 41.2234 | 67.7535 | 51.9432 | 41.2326 | 67.7845 | 51.9724 | 41.2387
WB | 50000069 | M024 | GAYNDAH - MUNDUBBERA T/LINE | M024_Gayndah - Mundubbera 66 kV | Loading (A) | 90.1322 | 91.8943 | 69.9304 | 90.311 | 92.1324 | 69.9139 | 89.3091 | 92.5273 | 70.0798 | 89.4346 | 91.9395 | 70.0954 | 89.4755 | 91.9911 | 70.1057
WB | 50000069 | M024 | GAYNDAH - MUNDUBBERA T/LINE | M024_Gayndah - Mundubbera 66 kV | Power Factor | 0.98669 | 0.98774 | 0.96351 | 0.98768 | 0.98876 | 0.9648 | 0.98666 | 0.98862 | 0.96417 | 0.98685 | 0.9878 | 0.96423 | 0.98692 | 0.98787 | 0.96428
WB | 50000069 | M024 | GAYNDAH - MUNDUBBERA T/LINE | M024_Gayndah - Mundubbera 66 kV | Rating (A) | 132 | 177 | 170 | 132 | 177 | 170 | 132 | 177 | 170 | 132 | 177 | 170 | 132 | 177 | 170
WB | 50000077 | M021 | 66KV HOWA-PIAL TEE MARY FDR | M021_Hoawrd-Pialba Tee Mary 66 kV
WB | 50000077 | M021 | 66KV HOWA-PIAL TEE MARY FDR | M021_Hoawrd-Pialba Tee Mary 66 kV | % of Rated A | 0.53898 | 0.48425 | 0.59595 | 0.53998 | 0.48359 | 0.59555 | 0.53964 | 0.48289 | 0.59525 | 0.54045 | 0.48235 | 0.59493 | 0.54034 | 0.48217 | 0.59482
WB | 50000077 | M021 | 66KV HOWA-PIAL TEE MARY FDR | M021_Hoawrd-Pialba Tee Mary 66 kV | Loading (A) | 3.2609 | 3.2348 | 3.2599 | 3.2669 | 3.2304 | 3.2577 | 3.2649 | 3.2257 | 3.256 | 3.2697 | 3.2221 | 3.2543 | 3.2691 | 3.2209 | 3.2537
WB | 50000077 | M021 | 66KV HOWA-PIAL TEE MARY FDR | M021_Hoawrd-Pialba Tee Mary 66 kV | Power Factor | 9.6633e-05 | 9.6633e-05 | 9.6633e-05 | 9.6633e-05 | 9.6633e-05 | 9.6633e-05 | 9.6633e-05 | 9.6633e-05 | 9.6633e-05 | 9.6633e-05 | 9.6633e-05 | 9.6633e-05 | 9.6633e-05 | 9.6633e-05 | 9.6633e-05
WB | 50000077 | M021 | 66KV HOWA-PIAL TEE MARY FDR | M021_Hoawrd-Pialba Tee Mary 66 kV | Rating (A) | 605 | 668 | 547 | 605 | 668 | 547 | 605 | 668 | 547 | 605 | 668 | 547 | 605 | 668 | 547
WB | 50000078 | M026 | ISIS - BUNDABERG 66KV FDR | M026_ISIS - Bundaberg 66 kV
WB | 50000078 | M026 | ISIS - BUNDABERG 66KV FDR | M026_ISIS - Bundaberg 66 kV | % of Rated A | 12.9307 | 22.5421 | 13.9693 | 13.4493 | 23.4924 | 14.5422 | 13.4656 | 23.5386 | 14.5592 | 13.4806 | 23.5896 | 14.5751 | 13.4853 | 23.605 | 14.5801
WB | 50000078 | M026 | ISIS - BUNDABERG 66KV FDR | M026_ISIS - Bundaberg 66 kV | Loading (A) | 12.9307 | 22.5421 | 13.9693 | 13.4493 | 23.4924 | 14.5422 | 13.4656 | 23.5386 | 14.5592 | 13.4806 | 23.5896 | 14.5751 | 13.4853 | 23.605 | 14.5801
WB | 50000078 | M026 | ISIS - BUNDABERG 66KV FDR | M026_ISIS - Bundaberg 66 kV | Power Factor | 0.9787 | 0.97529 | 0.97844 | 0.97851 | 0.9749 | 0.97823 | 0.9785 | 0.97487 | 0.97821 | 0.97849 | 0.97483 | 0.9782 | 0.97848 | 0.97482 | 0.9782
WB | 50000078 | M026 | ISIS - BUNDABERG 66KV FDR | M026_ISIS - Bundaberg 66 kV | Rating (A) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
WB | 50000079 | M027 | ISIS - CHILDERS 66KV FDR | M027_ISIS - Childers 66 kV
WB | 50000079 | M027 | ISIS - CHILDERS 66KV FDR | M027_ISIS - Childers 66 kV | % of Rated A | 21.1104 | 20.3271 | 31.4526 | 19.8078 | 22.6991 | 29.946 | 18.3595 | 25.4724 | 28.3019 | 18.2875 | 25.6439 | 28.1869 | 18.1708 | 25.9659 | 28.0384
WB | 50000079 | M027 | ISIS - CHILDERS 66KV FDR | M027_ISIS - Childers 66 kV | Loading (A) | 54.465 | 53.8669 | 73.599 | 51.104 | 60.1527 | 70.0735 | 47.3674 | 67.5018 | 66.2264 | 47.1817 | 67.9562 | 65.9573 | 46.8806 | 68.8098 | 65.6098
WB | 50000079 | M027 | ISIS - CHILDERS 66KV FDR | M027_ISIS - Childers 66 kV | Power Factor | 0.96031 | 0.28831 | 0.99259 | 0.9436 | 0.38542 | 0.98885 | 0.92397 | 0.46619 | 0.98303 | 0.91982 | 0.47292 | 0.98181 | 0.91678 | 0.4785 | 0.98101
WB | 50000079 | M027 | ISIS - CHILDERS 66KV FDR | M027_ISIS - Childers 66 kV | Rating (A) | 258 | 265 | 234 | 258 | 265 | 234 | 258 | 265 | 234 | 258 | 265 | 234 | 258 | 265 | 234
WB | 50000080 | M049 | ISIS - GAYNDAH 66KV FDR | M049_ISIS - Gayndah 66 kV
WB | 50000080 | M049 | ISIS - GAYNDAH 66KV FDR | M049_ISIS - Gayndah 66 kV | % of Rated A | 32.0224 | 30.9749 | 26.9641 | 32.3954 | 31.3684 | 27.1534 | 32.6455 | 31.6668 | 27.2877 | 32.6992 | 31.4556 | 27.3 | 32.7212 | 31.4805 | 27.3091
WB | 50000080 | M049 | ISIS - GAYNDAH 66KV FDR | M049_ISIS - Gayndah 66 kV | Loading (A) | 174.9536 | 178.7954 | 140.1998 | 176.9816 | 181.0568 | 141.1739 | 178.3529 | 182.7796 | 141.8719 | 178.646 | 181.5633 | 141.9355 | 178.7656 | 181.7064 | 141.9825
WB | 50000080 | M049 | ISIS - GAYNDAH 66KV FDR | M049_ISIS - Gayndah 66 kV | Power Factor | 0.98452 | 0.983 | 0.99572 | 0.98348 | 0.98181 | 0.99533 | 0.98344 | 0.98136 | 0.99527 | 0.98328 | 0.98203 | 0.99524 | 0.98323 | 0.98196 | 0.99523
WB | 50000080 | M049 | ISIS - GAYNDAH 66KV FDR | M049_ISIS - Gayndah 66 kV | Rating (A) | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521
WB | 50000081 | M022 | HOWARD TEE ISIS RIVER 66KV FDR | M022_Howard - ISIS 66 kV
WB | 50000081 | M022 | HOWARD TEE ISIS RIVER 66KV FDR | M022_Howard - ISIS 66 kV | % of Rated A | 83.0085 | 39.0433 | 87.9138 | 83.0491 | 39.0861 | 87.9588 | 83.0871 | 39.1312 | 87.9966 | 83.0994 | 39.1656 | 88.0336 | 83.1028 | 39.1752 | 88.0443
WB | 50000081 | M022 | HOWARD TEE ISIS RIVER 66KV FDR | M022_Howard - ISIS 66 kV | Loading (A) | 454.8638 | 225.9836 | 458.0085 | 455.0865 | 226.2314 | 458.2429 | 455.2945 | 226.4924 | 458.4403 | 455.3618 | 226.6919 | 458.6327 | 455.3807 | 226.7471 | 458.6887
WB | 50000081 | M022 | HOWARD TEE ISIS RIVER 66KV FDR | M022_Howard - ISIS 66 kV | Power Factor | 0.97693 | 0.69108 | 0.97783 | 0.97697 | 0.69117 | 0.97787 | 0.977 | 0.69128 | 0.9779 | 0.97702 | 0.69135 | 0.97794 | 0.97702 | 0.69138 | 0.97795
WB | 50000081 | M022 | HOWARD TEE ISIS RIVER 66KV FDR | M022_Howard - ISIS 66 kV | Rating (A) | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521
WB | 50000088 | M001 | TARONG - KINGAROY EAST T/LINE | M001_Tarong-Kingaroy East 66 kV
WB | 50000088 | M001 | TARONG - KINGAROY EAST T/LINE | M001_Tarong-Kingaroy East 66 kV | % of Rated A | 34.7343 | 36.1875 | 24.8471 | 37.2112 | 38.7548 | 27.062 | 37.2116 | 38.7554 | 27.0623 | 37.4755 | 39.0261 | 27.2477 | 37.5651 | 39.1151 | 27.2934
WB | 50000088 | M001 | TARONG - KINGAROY EAST T/LINE | M001_Tarong-Kingaroy East 66 kV | Loading (A) | 189.3054 | 208.4541 | 128.5267 | 202.865 | 223.3083 | 140.0434 | 202.8673 | 223.3113 | 140.0446 | 204.3103 | 224.8757 | 141.0072 | 204.801 | 225.3912 | 141.245
WB | 50000088 | M001 | TARONG - KINGAROY EAST T/LINE | M001_Tarong-Kingaroy East 66 kV | Power Factor | 0.94171 | 0.93651 | 0.95762 | 0.93916 | 0.93416 | 0.95459 | 0.93916 | 0.93416 | 0.95459 | 0.9387 | 0.93368 | 0.95418 | 0.9386 | 0.93365 | 0.95414
WB | 50000088 | M001 | TARONG - KINGAROY EAST T/LINE | M001_Tarong-Kingaroy East 66 kV | Rating (A) | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521
WB | 50000089 | M002 | TARONG - KINGAROY WEST T/LINE | M002_Tarong-Kingaroy West 66 kV
WB | 50000089 | M002 | TARONG - KINGAROY WEST T/LINE | M002_Tarong-Kingaroy West 66 kV | % of Rated A | 34.7548 | 36.2089 | 24.8617 | 37.2332 | 38.7778 | 27.0779 | 37.2336 | 38.7783 | 27.0782 | 37.4977 | 39.0492 | 27.2637 | 37.5873 | 39.1383 | 27.3094
WB | 50000089 | M002 | TARONG - KINGAROY WEST T/LINE | M002_Tarong-Kingaroy West 66 kV | Loading (A) | 190.4541 | 209.6475 | 129.5273 | 204.0356 | 224.5211 | 141.074 | 204.038 | 224.5242 | 141.0752 | 205.4849 | 226.0925 | 142.0418 | 205.9764 | 226.6082 | 142.28
WB | 50000089 | M002 | TARONG - KINGAROY WEST T/LINE | M002_Tarong-Kingaroy West 66 kV | Power Factor | 0.95 | 0.94694 | 0.95897 | 0.94891 | 0.94615 | 0.9573 | 0.94891 | 0.94615 | 0.9573 | 0.94862 | 0.94585 | 0.95701 | 0.94857 | 0.94587 | 0.95699
WB | 50000089 | M002 | TARONG - KINGAROY WEST T/LINE | M002_Tarong-Kingaroy West 66 kV | Rating (A) | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521
WB | 50000091 | M005 | KINGAROY - BOONDOOMA T/LINE | M005_Kingaroy-Boondooma 66 kV
WB | 50000091 | M005 | KINGAROY - BOONDOOMA T/LINE | M005_Kingaroy-Boondooma 66 kV | % of Rated A | 26.8094 | 21.5957 | 19.6112 | 45.1231 | 36.4182 | 32.9957 | 45.1236 | 36.4187 | 32.9959 | 45.1546 | 36.4461 | 33.0103 | 45.1623 | 36.4521 | 33.0118
WB | 50000091 | M005 | KINGAROY - BOONDOOMA T/LINE | M005_Kingaroy-Boondooma 66 kV | Loading (A) | 35.9245 | 39.0882 | 34.3196 | 60.4245 | 65.8764 | 57.7008 | 60.4252 | 65.8772 | 57.7012 | 60.4668 | 65.9269 | 57.7264 | 60.477 | 65.9378 | 57.7291
WB | 50000091 | M005 | KINGAROY - BOONDOOMA T/LINE | M005_Kingaroy-Boondooma 66 kV | Power Factor | 0.92376 | 0.92319 | 0.92416 | 0.93298 | 0.93161 | 0.93301 | 0.93297 | 0.93161 | 0.93301 | 0.93296 | 0.93159 | 0.933 | 0.93295 | 0.93158 | 0.933
WB | 50000091 | M005 | KINGAROY - BOONDOOMA T/LINE | M005_Kingaroy-Boondooma 66 kV | Rating (A) | 134 | 181 | 175 | 134 | 181 | 175 | 134 | 181 | 175 | 134 | 181 | 175 | 134 | 181 | 175
WB | 50000099 | M015 | MARYBOROUGH-HOWARD No 1 | M015_Maryborough-Howard No 1 66 kV
WB | 50000099 | M015 | MARYBOROUGH-HOWARD No 1 | M015_Maryborough-Howard No 1 66 kV | % of Rated A | 1.9328 | 1.5155 | 1.6041 | 1.9364 | 1.5135 | 1.603 | 1.9352 | 1.5113 | 1.6022 | 1.9381 | 1.5096 | 1.6014 | 1.9377 | 1.509 | 1.6011
WB | 50000099 | M015 | MARYBOROUGH-HOWARD No 1 | M015_Maryborough-Howard No 1 66 kV | Loading (A) | 2.5513 | 2.5309 | 2.5506 | 2.556 | 2.5275 | 2.5488 | 2.5544 | 2.5238 | 2.5475 | 2.5582 | 2.521 | 2.5462 | 2.5578 | 2.5201 | 2.5457
WB | 50000099 | M015 | MARYBOROUGH-HOWARD No 1 | M015_Maryborough-Howard No 1 66 kV | Power Factor | 0.0030456 | 0.0030456 | 0.0030456 | 0.0030456 | 0.0030456 | 0.0030456 | 0.0030456 | 0.0030456 | 0.0030456 | 0.0030456 | 0.0030456 | 0.0030456 | 0.0030456 | 0.0030456 | 0.0030456
WB | 50000099 | M015 | MARYBOROUGH-HOWARD No 1 | M015_Maryborough-Howard No 1 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
WB | 50000100 | T014 | 66KV MARY-PIAL TEE HOWA FDR | T014_Maryborough-Pialba Tee Howard 66 kV
WB | 50000100 | T014 | 66KV MARY-PIAL TEE HOWA FDR | T014_Maryborough-Pialba Tee Howard 66 kV | % of Rated A | 36.9811 | 39.7296 | 31.8556 | 37.1135 | 39.8949 | 32.0906 | 37.3194 | 40.1174 | 32.2737 | 37.5706 | 40.3516 | 31.9946 | 37.8989 | 40.6769 | 32.2399
WB | 50000100 | T014 | 66KV MARY-PIAL TEE HOWA FDR | T014_Maryborough-Pialba Tee Howard 66 kV | Loading (A) | 223.7355 | 265.3934 | 174.2504 | 224.5367 | 266.4978 | 175.5356 | 225.7825 | 267.984 | 176.5371 | 227.302 | 269.5484 | 175.0104 | 229.2886 | 271.7218 | 176.352
WB | 50000100 | T014 | 66KV MARY-PIAL TEE HOWA FDR | T014_Maryborough-Pialba Tee Howard 66 kV | Power Factor | 0.99774 | 0.99358 | 0.96563 | 0.99731 | 0.99197 | 0.96564 | 0.99723 | 0.99193 | 0.96641 | 0.99813 | 0.99382 | 0.97061 | 0.99822 | 0.99401 | 0.97151
WB | 50000100 | T014 | 66KV MARY-PIAL TEE HOWA FDR | T014_Maryborough-Pialba Tee Howard 66 kV | Rating (A) | 605 | 668 | 547 | 605 | 668 | 547 | 605 | 668 | 547 | 605 | 668 | 547 | 605 | 668 | 547
WB | 50000102 | M012 | MARYBOROUGH- ROCKY ST T/LINE | M012_Maryborough-Rocky St 66 kV
WB | 50000102 | M012 | MARYBOROUGH- ROCKY ST T/LINE | M012_Maryborough-Rocky St 66 kV | % of Rated A | 36.957 | 33.6192 | 30.8412 | 39.1996 | 36.2648 | 33.0197 | 39.4865 | 36.5746 | 33.2356 | 39.672 | 36.7814 | 33.3852 | 39.7029 | 36.7743 | 33.425
WB | 50000102 | M012 | MARYBOROUGH- ROCKY ST T/LINE | M012_Maryborough-Rocky St 66 kV | Loading (A) | 202.5243 | 194.6551 | 160.6828 | 214.8136 | 209.9733 | 172.0325 | 216.386 | 211.7668 | 173.1576 | 217.4025 | 212.9644 | 173.9368 | 217.5716 | 212.923 | 174.1444
WB | 50000102 | M012 | MARYBOROUGH- ROCKY ST T/LINE | M012_Maryborough-Rocky St 66 kV | Power Factor | 0.99496 | 0.99723 | 0.98762 | 0.99854 | 0.99989 | 0.99531 | 0.99912 | 1 | 0.99596 | 0.99917 | 1 | 0.99608 | 0.99921 | 1 | 0.9962
WB | 50000102 | M012 | MARYBOROUGH- ROCKY ST T/LINE | M012_Maryborough-Rocky St 66 kV | Rating (A) | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521
WB | 50000103 | TORQUAY TEE | 66KV TORQUAY TEE FDR T015 | M020_Maryborough-Torquay 66 kV
WB | 50000103 | TORQUAY TEE | 66KV TORQUAY TEE FDR T015 | M020_Maryborough-Torquay 66 kV | % of Rated A | 74.2235 | 55.0541 | 69.5476 | 74.1269 | 55.2785 | 69.0094 | 74.2506 | 55.6097 | 68.8291 | 74.1799 | 55.8964 | 68.6021 | 74.4221 | 56.3507 | 68.415
WB | 50000103 | TORQUAY TEE | 66KV TORQUAY TEE FDR T015 | M020_Maryborough-Torquay 66 kV | Loading (A) | 341.4281 | 369.9635 | 363.8616 | 340.9835 | 371.4715 | 361.07 | 341.5525 | 373.697 | 360.1297 | 341.2276 | 375.6238 | 359.475 | 342.3419 | 378.6767 | 358.4944
WB | 50000103 | TORQUAY TEE | 66KV TORQUAY TEE FDR T015 | M020_Maryborough-Torquay 66 kV | Power Factor | 0.96136 | 0.98486 | 0.91045 | 0.96443 | 0.98605 | 0.91891 | 0.96559 | 0.98673 | 0.92025 | 0.97032 | 0.98985 | 0.93738 | 0.97113 | 0.99039 | 0.93772
WB | 50000103 | TORQUAY TEE | 66KV TORQUAY TEE FDR T015 | M020_Maryborough-Torquay 66 kV | Rating (A) | 460 | 672 | 524 | 460 | 672 | 524 | 460 | 672 | 524 | 460 | 672 | 524 | 460 | 672 | 524
WB | 50000104 | M019 | MBOROUGH CITY-WALKERS T/LINE | M019_Maryborough City-Walkers 66 kV
WB | 50000104 | M019 | MBOROUGH CITY-WALKERS T/LINE | M019_Maryborough City-Walkers 66 kV | % of Rated A | 13.2751 | 0.25188 | 8.5919 | 13.3053 | 0.25178 | 8.6132 | 13.3125 | 0.2519 | 8.616 | 13.2558 | 0.25191 | 8.6197 | 13.414 | 0.26148 | 8.7221
WB | 50000104 | M019 | MBOROUGH CITY-WALKERS T/LINE | M019_Maryborough City-Walkers 66 kV | Loading (A) | 72.7472 | 1.4584 | 44.7636 | 72.9129 | 1.4578 | 44.8743 | 72.9522 | 1.4585 | 44.889 | 72.6417 | 1.4585 | 44.9084 | 73.5084 | 1.514 | 45.4419
WB | 50000104 | M019 | MBOROUGH CITY-WALKERS T/LINE | M019_Maryborough City-Walkers 66 kV | Power Factor | 0.99876 | 0.099444 | 0.99876 | 0.99874 | 0.099456 | 0.99876 | 0.99874 | 0.099442 | 0.99876 | 0.99876 | 0.099441 | 0.99876 | 0.99875 | 0.099247 | 0.99877
WB | 50000104 | M019 | MBOROUGH CITY-WALKERS T/LINE | M019_Maryborough City-Walkers 66 kV | Rating (A) | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521
WB | 50000122 | M008 | KILKIVAN - MURGON NO1 T/LINE | M008_Kilkivan-Murgon No 1 66 kV
WB | 50000122 | M008 | KILKIVAN - MURGON NO1 T/LINE | M008_Kilkivan-Murgon No 1 66 kV | % of Rated A | 39.2943 | 30.9313 | 25.4647 | 40.8346 | 32.138 | 26.4528 | 41.0994 | 32.3456 | 26.6213 | 41.3653 | 32.5549 | 26.7906 | 41.6302 | 32.76 | 26.9594
WB | 50000122 | M008 | KILKIVAN - MURGON NO1 T/LINE | M008_Kilkivan-Murgon No 1 66 kV | Loading (A) | 71.0747 | 77.8968 | 62.3441 | 73.8616 | 80.9369 | 64.7639 | 74.3406 | 81.46 | 65.1768 | 74.8218 | 81.987 | 65.5911 | 75.3009 | 82.5038 | 66.0046
WB | 50000122 | M008 | KILKIVAN - MURGON NO1 T/LINE | M008_Kilkivan-Murgon No 1 66 kV | Power Factor | 0.95725 | 0.95317 | 0.9635 | 0.9552 | 0.95107 | 0.96152 | 0.95479 | 0.95065 | 0.96113 | 0.95438 | 0.95022 | 0.96075 | 0.95397 | 0.94985 | 0.96035
WB | 50000122 | M008 | KILKIVAN - MURGON NO1 T/LINE | M008_Kilkivan-Murgon No 1 66 kV | Rating (A) | 181 | 252 | 245 | 181 | 252 | 245 | 181 | 252 | 245 | 181 | 252 | 245 | 181 | 252 | 245
WB | 50000123 | M009 | KILKIVAN - MURGON NO2 T/LINE | M009_Kilkivan-Murgon No 2 66 kV
WB | 50000123 | M009 | KILKIVAN - MURGON NO2 T/LINE | M009_Kilkivan-Murgon No 2 66 kV | % of Rated A | 38.4 | 29.422 | 24.2255 | 40.0775 | 30.7102 | 25.2821 | 40.3665 | 30.9319 | 25.4625 | 40.6567 | 31.1552 | 25.6435 | 40.9435 | 31.3741 | 25.8239
WB | 50000123 | M009 | KILKIVAN - MURGON NO2 T/LINE | M009_Kilkivan-Murgon No 2 66 kV | Loading (A) | 63.4962 | 68.8782 | 56.4453 | 66.3026 | 71.9336 | 57.5775 | 66.786 | 72.4587 | 57.9925 | 67.2714 | 72.9875 | 58.4089 | 67.7516 | 73.5067 | 58.8242
WB | 50000123 | M009 | KILKIVAN - MURGON NO2 T/LINE | M009_Kilkivan-Murgon No 2 66 kV | Power Factor | 0.96319 | 0.95904 | 0.953 | 0.96069 | 0.95667 | 0.96783 | 0.96024 | 0.9562 | 0.96741 | 0.95978 | 0.95572 | 0.96698 | 0.95936 | 0.9553 | 0.96656
WB | 50000123 | M009 | KILKIVAN - MURGON NO2 T/LINE | M009_Kilkivan-Murgon No 2 66 kV | Rating (A) | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233
WB | 50000131 | M004 | MURGON - KINGAROY T/LINE | M004_Murgon-Kingaroy 66 kV
WB | 50000131 | M004 | MURGON - KINGAROY T/LINE | M004_Murgon-Kingaroy 66 kV | % of Rated A | 7.5791 | 6.0913 | 4.555 | 7.596 | 6.1091 | 4.5577 | 7.5988 | 6.1124 | 4.5582 | 7.6016 | 6.1158 | 4.5587 | 7.6044 | 6.1178 | 4.5592
WB | 50000131 | M004 | MURGON - KINGAROY T/LINE | M004_Murgon-Kingaroy 66 kV | Loading (A) | 12.8087 | 14.5582 | 10.6133 | 12.8372 | 14.6007 | 10.6195 | 12.8419 | 14.6086 | 10.6207 | 12.8468 | 14.6168 | 10.6219 | 12.8514 | 14.6216 | 10.623
WB | 50000131 | M004 | MURGON - KINGAROY T/LINE | M004_Murgon-Kingaroy 66 kV | Power Factor | 0.92928 | 0.96114 | 0.84874 | 0.93049 | 0.96246 | 0.85091 | 0.9308 | 0.9627 | 0.85131 | 0.93112 | 0.96295 | 0.85172 | 0.93142 | 0.96309 | 0.85211
WB | 50000131 | M004 | MURGON - KINGAROY T/LINE | M004_Murgon-Kingaroy 66 kV | Rating (A) | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233
WB | 50000146 | M003 | KINGAROY - YARRAMAN T/LINE | M003_Kingaroy- Yarraman 66 kV
WB | 50000146 | M003 | KINGAROY - YARRAMAN T/LINE | M003_Kingaroy- Yarraman 66 kV | % of Rated A | 78.0207 | 70.1485 | 45.264 | 79.0671 | 71.1291 | 45.7206 | 79.068 | 71.1302 | 45.721 | 79.8012 | 71.7766 | 46.023 | 80.5044 | 72.361 | 46.3123
WB | 50000146 | M003 | KINGAROY - YARRAMAN T/LINE | M003_Kingaroy- Yarraman 66 kV | Loading (A) | 102.9865 | 117.1472 | 71.9691 | 104.3678 | 118.7849 | 72.6949 | 104.3691 | 118.7866 | 72.6956 | 105.3368 | 119.8662 | 73.1758 | 106.2651 | 120.8422 | 73.6358
WB | 50000146 | M003 | KINGAROY - YARRAMAN T/LINE | M003_Kingaroy- Yarraman 66 kV | Power Factor | 0.96336 | 0.96069 | 0.96715 | 0.96316 | 0.96033 | 0.96695 | 0.96316 | 0.96033 | 0.96695 | 0.96299 | 0.96016 | 0.96688 | 0.96283 | 0.96025 | 0.96682
WB | 50000146 | M003 | KINGAROY - YARRAMAN T/LINE | M003_Kingaroy- Yarraman 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
WB | 50000176 | M037 | SOUTH - EAST BUNDABERG T/LINE | M037_South - East Bundaberg 66 kV
WB | 50000176 | M037 | SOUTH - EAST BUNDABERG T/LINE | M037_South - East Bundaberg 66 kV | % of Rated A | 19.4526 | 12.6127 | 12.5332 | 18.9869 | 10.0508 | 11.6371 | 19.661 | 10.4214 | 11.9838 | 19.71 | 10.0075 | 11.8734 | 19.7064 | 9.9573 | 11.8461
WB | 50000176 | M037 | SOUTH - EAST BUNDABERG T/LINE | M037_South - East Bundaberg 66 kV | Loading (A) | 43.9628 | 39.2256 | 32.3356 | 42.9104 | 31.2581 | 30.0237 | 44.4339 | 32.4105 | 30.9182 | 44.5445 | 31.1233 | 30.6333 | 44.5365 | 30.9673 | 30.5628
WB | 50000176 | M037 | SOUTH - EAST BUNDABERG T/LINE | M037_South - East Bundaberg 66 kV | Power Factor | 0.81083 | 0.13165 | 0.56787 | 0.85073 | 0.46192 | 0.63294 | 0.86058 | 0.52342 | 0.65227 | 0.88595 | 0.57998 | 0.68434 | 0.88578 | 0.57071 | 0.68128
WB | 50000176 | M037 | SOUTH - EAST BUNDABERG T/LINE | M037_South - East Bundaberg 66 kV | Rating (A) | 226 | 311 | 258 | 226 | 311 | 258 | 226 | 311 | 258 | 226 | 311 | 258 | 226 | 311 | 258
WB | 50000182 | M035 | BBERG - STH KOLAN NO2 T/LINE | M035_Bundaberg-South Kolan No 2 66 kV
WB | 50000182 | M035 | BBERG - STH KOLAN NO2 T/LINE | M035_Bundaberg-South Kolan No 2 66 kV | % of Rated A | 12.1545 | 14.4453 | 14.3249 | 12.4053 | 14.7718 | 14.6141 | 12.4207 | 14.8049 | 14.6127 | 12.575 | 15.024 | 14.7831 | 12.6546 | 14.8938 | 14.864
WB | 50000182 | M035 | BBERG - STH KOLAN NO2 T/LINE | M035_Bundaberg-South Kolan No 2 66 kV | Loading (A) | 66.4772 | 83.45 | 74.4519 | 67.8462 | 85.3351 | 75.9538 | 67.9308 | 85.5263 | 75.9509 | 68.7723 | 86.7912 | 76.8354 | 69.2066 | 86.0355 | 77.2558
WB | 50000182 | M035 | BBERG - STH KOLAN NO2 T/LINE | M035_Bundaberg-South Kolan No 2 66 kV | Power Factor | 0.99213 | 0.98242 | 0.98423 | 0.99141 | 0.98135 | 0.98337 | 0.99138 | 0.98118 | 0.98414 | 0.99077 | 0.98029 | 0.98344 | 0.9905 | 0.98043 | 0.98318
WB | 50000182 | M035 | BBERG - STH KOLAN NO2 T/LINE | M035_Bundaberg-South Kolan No 2 66 kV | Rating (A) | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521
WB | 50000183 | M032 | BBERG - STH KOLAN NO1 T/LINE | M032_Bundaberg-South Kolan No 1 66 kV
WB | 50000183 | M032 | BBERG - STH KOLAN NO1 T/LINE | M032_Bundaberg-South Kolan No 1 66 kV | % of Rated A | 70.0223 | 63.5723 | 59.3592 | 70.5713 | 64.1334 | 59.8246 | 70.6644 | 63.6922 | 59.8128 | 71.3234 | 64.4797 | 60.3541 | 71.9755 | 64.586 | 60.8451
WB | 50000183 | M032 | BBERG - STH KOLAN NO1 T/LINE | M032_Bundaberg-South Kolan No 1 66 kV | Loading (A) | 92.3843 | 112.388 | 100.7562 | 93.1055 | 113.3773 | 101.5443 | 93.2272 | 112.5973 | 101.5333 | 94.0906 | 113.9838 | 102.4483 | 94.9468 | 114.1767 | 103.2798
WB | 50000183 | M032 | BBERG - STH KOLAN NO1 T/LINE | M032_Bundaberg-South Kolan No 1 66 kV | Power Factor | 0.99943 | 0.9944 | 0.99307 | 0.99933 | 0.99407 | 0.99279 | 0.99929 | 0.99419 | 0.99358 | 0.99909 | 0.99349 | 0.99307 | 0.99892 | 0.99402 | 0.99276
WB | 50000183 | M032 | BBERG - STH KOLAN NO1 T/LINE | M032_Bundaberg-South Kolan No 1 66 kV | Rating (A) | 132 | 177 | 170 | 132 | 177 | 170 | 132 | 177 | 170 | 132 | 177 | 170 | 132 | 177 | 170
WB | 50000197 | M014 | TORQUAY - PIALBA T/LINE | M014_Torquay-Pialba 66 kV
WB | 50000197 | M014 | TORQUAY - PIALBA T/LINE | M014_Torquay-Pialba 66 kV | % of Rated A | 24.1456 | 15.1819 | 23.1412 | 23.9427 | 14.8961 | 22.9271 | 23.7683 | 14.6095 | 22.7488 | 23.7341 | 14.4747 | 22.7234 | 23.6395 | 14.3152 | 22.6467
WB | 50000197 | M014 | TORQUAY - PIALBA T/LINE | M014_Torquay-Pialba 66 kV | Loading (A) | 146.8052 | 102.0221 | 127.5079 | 145.5715 | 100.1015 | 126.3285 | 144.5113 | 98.1756 | 125.3458 | 144.3036 | 97.2697 | 125.206 | 143.7281 | 96.1984 | 124.7835
WB | 50000197 | M014 | TORQUAY - PIALBA T/LINE | M014_Torquay-Pialba 66 kV | Power Factor | 0.98733 | 0.99798 | 0.97833 | 0.98799 | 0.99878 | 0.97966 | 0.98803 | 0.99892 | 0.97955 | 0.986 | 0.99661 | 0.97655 | 0.9867 | 0.99658 | 0.97646
WB | 50000197 | M014 | TORQUAY - PIALBA T/LINE | M014_Torquay-Pialba 66 kV | Rating (A) | 608 | 672 | 551 | 608 | 672 | 551 | 608 | 672 | 551 | 608 | 672 | 551 | 608 | 672 | 551
WB | 50000200 | M039 | BBERG - WST BBERG NO1 T/LINE | M039_Bundaberg-West Bundaberg No 1 66 kV
WB | 50000200 | M039 | BBERG - WST BBERG NO1 T/LINE | M039_Bundaberg-West Bundaberg No 1 66 kV | % of Rated A | 39.0908 | 37.0214 | 30.1964 | 39.3765 | 37.3478 | 30.5194 | 39.9428 | 37.5327 | 30.9717 | 40.4431 | 38.0617 | 31.3049 | 40.6325 | 38.2557 | 31.4456
WB | 50000200 | M039 | BBERG - WST BBERG NO1 T/LINE | M039_Bundaberg-West Bundaberg No 1 66 kV | Loading (A) | 315.0718 | 334.3034 | 224.9634 | 317.3748 | 337.2503 | 227.3697 | 321.9393 | 338.9204 | 230.7393 | 325.9717 | 343.6972 | 233.2218 | 327.4981 | 345.4487 | 234.2698
WB | 50000200 | M039 | BBERG - WST BBERG NO1 T/LINE | M039_Bundaberg-West Bundaberg No 1 66 kV | Power Factor | 0.99801 | 0.99941 | 0.98297 | 0.99726 | 0.99907 | 0.9812 | 0.99755 | 0.99896 | 0.98226 | 0.99842 | 0.99952 | 0.9851 | 0.99851 | 0.99957 | 0.98545
WB | 50000200 | M039 | BBERG - WST BBERG NO1 T/LINE | M039_Bundaberg-West Bundaberg No 1 66 kV | Rating (A) | 806 | 903 | 745 | 806 | 903 | 745 | 806 | 903 | 745 | 806 | 903 | 745 | 806 | 903 | 745
WB | 50000201 | M040 | B'BERG - WEST B'BERG NO2 T/LINE | M040_Bundaberg-West Bundaberg No 2 66 kV
WB | 50000201 | M040 | B'BERG - WEST B'BERG NO2 T/LINE | M040_Bundaberg-West Bundaberg No 2 66 kV | % of Rated A | 37.6374 | 35.6448 | 29.0743 | 37.9125 | 35.959 | 29.3853 | 38.4577 | 36.1371 | 29.8208 | 38.9394 | 36.6464 | 30.1416 | 39.1217 | 36.8331 | 30.277
WB | 50000201 | M040 | B'BERG - WEST B'BERG NO2 T/LINE | M040_Bundaberg-West Bundaberg No 2 66 kV | Loading (A) | 303.3571 | 321.8725 | 216.6037 | 305.5748 | 324.7101 | 218.9208 | 309.9694 | 326.3182 | 222.1649 | 313.8514 | 330.9169 | 224.5546 | 315.321 | 332.6031 | 225.5635
WB | 50000201 | M040 | B'BERG - WEST B'BERG NO2 T/LINE | M040_Bundaberg-West Bundaberg No 2 66 kV | Power Factor | 0.99799 | 0.9994 | 0.98292 | 0.99724 | 0.99906 | 0.98114 | 0.99753 | 0.99895 | 0.98221 | 0.9984 | 0.99951 | 0.98505 | 0.9985 | 0.99957 | 0.98541
WB | 50000201 | M040 | B'BERG - WEST B'BERG NO2 T/LINE | M040_Bundaberg-West Bundaberg No 2 66 kV | Rating (A) | 806 | 903 | 745 | 806 | 903 | 745 | 806 | 903 | 745 | 806 | 903 | 745 | 806 | 903 | 745
WB | 50016424 | 764 | 764 WOOLOOGA - KILKIVAN NO1 T/LINE | 764_Woolooga-Kilkivan No 1 132 kV
WB | 50016424 | 764 | 764 WOOLOOGA - KILKIVAN NO1 T/LINE | 764_Woolooga-Kilkivan No 1 132 kV | % of Rated A | 13.5653 | 9.2659 | 7.3811 | 14.1291 | 9.6508 | 7.6861 | 14.2259 | 9.717 | 7.7382 | 14.3232 | 9.7837 | 7.7904 | 14.4201 | 9.8491 | 7.8425
WB | 50016424 | 764 | 764 WOOLOOGA - KILKIVAN NO1 T/LINE | 764_Woolooga-Kilkivan No 1 132 kV | Loading (A) | 33.6419 | 36.6931 | 29.0077 | 35.0401 | 38.2172 | 30.2066 | 35.2802 | 38.4793 | 30.411 | 35.5215 | 38.7433 | 30.6162 | 35.7618 | 39.0023 | 30.8208
WB | 50016424 | 764 | 764 WOOLOOGA - KILKIVAN NO1 T/LINE | 764_Woolooga-Kilkivan No 1 132 kV | Power Factor | 0.93635 | 0.92877 | 0.94791 | 0.93258 | 0.92475 | 0.94448 | 0.93185 | 0.92398 | 0.94383 | 0.93113 | 0.9232 | 0.94319 | 0.9304 | 0.92249 | 0.94254
WB | 50016424 | 764 | 764 WOOLOOGA - KILKIVAN NO1 T/LINE | 764_Woolooga-Kilkivan No 1 132 kV | Rating (A) | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393
WB | 50016425 | 765 | 765 WOOLOOGA - KILKIVAN NO2 T/LINE | 765_Woolooga-Kilkivan No 2 132 kV
WB | 50016425 | 765 | 765 WOOLOOGA - KILKIVAN NO2 T/LINE | 765_Woolooga-Kilkivan No 2 132 kV | % of Rated A | 13.5644 | 9.2653 | 7.3806 | 14.1282 | 9.6502 | 7.6857 | 14.225 | 9.7164 | 7.7377 | 14.3223 | 9.783 | 7.7899 | 14.4192 | 9.8484 | 7.842
WB | 50016425 | 765 | 765 WOOLOOGA - KILKIVAN NO2 T/LINE | 765_Woolooga-Kilkivan No 2 132 kV | Loading (A) | 33.6397 | 36.6908 | 29.0059 | 35.0378 | 38.2147 | 30.2046 | 35.278 | 38.4768 | 30.4091 | 35.5192 | 38.7408 | 30.6142 | 35.7595 | 38.9998 | 30.8189
WB | 50016425 | 765 | 765 WOOLOOGA - KILKIVAN NO2 T/LINE | 765_Woolooga-Kilkivan No 2 132 kV | Power Factor | 0.93635 | 0.92876 | 0.94791 | 0.93258 | 0.92475 | 0.94447 | 0.93185 | 0.92398 | 0.94383 | 0.93112 | 0.9232 | 0.94319 | 0.9304 | 0.92249 | 0.94254
WB | 50016425 | 765 | 765 WOOLOOGA - KILKIVAN NO2 T/LINE | 765_Woolooga-Kilkivan No 2 132 kV | Rating (A) | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393
WB | 50021248 | 7204 | 7204 BUNDABERG - CLAYTON T/LINE | 7204_Bundaberg - Clayton 132 kV
WB | 50021248 | 7204 | 7204 BUNDABERG - CLAYTON T/LINE | 7204_Bundaberg - Clayton 132 kV | % of Rated A | 1.0094 | 0.52003 | 0.44058 | 1.0095 | 0.52035 | 0.44059 | 1.0097 | 0.5205 | 0.44063 | 1.0103 | 0.52115 | 0.44072 | 1.0104 | 0.5213 | 0.44074
WB | 50021248 | 7204 | 7204 BUNDABERG - CLAYTON T/LINE | 7204_Bundaberg - Clayton 132 kV | Loading (A) | 8.9434 | 5.1015 | 3.6965 | 8.9439 | 5.1046 | 3.6965 | 8.946 | 5.1061 | 3.6969 | 8.9513 | 5.1125 | 3.6976 | 8.9524 | 5.114 | 3.6978
WB | 50021248 | 7204 | 7204 BUNDABERG - CLAYTON T/LINE | 7204_Bundaberg - Clayton 132 kV | Power Factor | 0.97262 | 0.91634 | 0.82661 | 0.97263 | 0.9166 | 0.82663 | 0.97266 | 0.91672 | 0.82677 | 0.97273 | 0.91726 | 0.82705 | 0.97274 | 0.91738 | 0.82711
WB | 50021248 | 7204 | 7204 BUNDABERG - CLAYTON T/LINE | 7204_Bundaberg - Clayton 132 kV | Rating (A) | 886 | 981 | 839 | 886 | 981 | 839 | 886 | 981 | 839 | 886 | 981 | 839 | 886 | 981 | 839
WB | 50021251 | M045 | TARONG - PACIFIC COAL T/LINE | M045_Tarong-Pacific Coal 66 kV
WB | 50021251 | M045 | TARONG - PACIFIC COAL T/LINE | M045_Tarong-Pacific Coal 66 kV | % of Rated A | 26.6006 | 39.1326 | 41.2244 | 26.619 | 39.1621 | 41.2547 | 26.6191 | 39.1624 | 41.255 | 26.9266 | 39.6165 | 41.7331 | 26.927 | 39.6173 | 41.7339
WB | 50021251 | M045 | TARONG - PACIFIC COAL T/LINE | M045_Tarong-Pacific Coal 66 kV | Loading (A) | 35.6449 | 70.83 | 72.1427 | 35.6694 | 70.8834 | 72.1956 | 35.6696 | 70.884 | 72.1962 | 36.0817 | 71.7059 | 73.033 | 36.0822 | 71.7073 | 73.0343
WB | 50021251 | M045 | TARONG - PACIFIC COAL T/LINE | M045_Tarong-Pacific Coal 66 kV | Power Factor | 0.99999 | 1 | 1 | 0.99999 | 1 | 1 | 0.99999 | 1 | 1 | 0.99999 | 1 | 1 | 0.99999 | 1 | 1
WB | 50021251 | M045 | TARONG - PACIFIC COAL T/LINE | M045_Tarong-Pacific Coal 66 kV | Rating (A) | 134 | 181 | 175 | 134 | 181 | 175 | 134 | 181 | 175 | 134 | 181 | 175 | 134 | 181 | 175
WB | 50078755 | M028 | CHILDERS - GAYNDAH T/LINE | M028_Childers - Gayndah 66 kV
WB | 50078755 | M028 | CHILDERS - GAYNDAH T/LINE | M028_Childers - Gayndah 66 kV | % of Rated A | 75.7196 | 61.3651 | 48.7083 | 77.7576 | 63.12 | 49.5071 | 79.4892 | 64.6715 | 50.196 | 79.5914 | 64.2419 | 50.2015 | 79.6089 | 64.2615 | 50.1995
WB | 50078755 | M028 | CHILDERS - GAYNDAH T/LINE | M028_Childers - Gayndah 66 kV | Loading (A) | 99.9498 | 102.4797 | 77.4461 | 102.64 | 105.4104 | 78.7163 | 104.9258 | 108.0015 | 79.8117 | 105.0606 | 107.284 | 79.8204 | 105.0838 | 107.3168 | 79.8171
WB | 50078755 | M028 | CHILDERS - GAYNDAH T/LINE | M028_Childers - Gayndah 66 kV | Power Factor | 0.98596 | 0.98755 | 0.9588 | 0.98857 | 0.99013 | 0.96209 | 0.99007 | 0.99185 | 0.96418 | 0.99017 | 0.99129 | 0.96417 | 0.99019 | 0.99131 | 0.96415
WB | 50078755 | M028 | CHILDERS - GAYNDAH T/LINE | M028_Childers - Gayndah 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
WB | 50078756 | 6205 | EAST B'BERG - B'BERG CENTRAL | 6205_East Bundaberg-BUCE 66 kV
WB | 50078756 | 6205 | EAST B'BERG - B'BERG CENTRAL | 6205_East Bundaberg-BUCE 66 kV | % of Rated A | 35.4221 | 42.6554 | 34.8435 | 36.8778 | 44.1344 | 36.1913 | 39.1677 | 46.0669 | 38.1318 | 40.4335 | 47.5606 | 39.1435 | 40.9264 | 48.1257 | 39.5696
WB | 50078756 | 6205 | EAST B'BERG - B'BERG CENTRAL | 6205_East Bundaberg-BUCE 66 kV | Loading (A) | 140.6243 | 185.975 | 124.0428 | 146.4047 | 192.4251 | 128.8409 | 155.4955 | 200.8501 | 135.7492 | 160.5195 | 207.3616 | 139.3509 | 162.4763 | 209.8251 | 140.8677
WB | 50078756 | 6205 | EAST B'BERG - B'BERG CENTRAL | 6205_East Bundaberg-BUCE 66 kV | Power Factor | 0.99926 | 0.99725 | 0.99977 | 0.99998 | 0.99963 | 0.99821 | 0.99999 | 0.99916 | 0.99888 | 0.9992 | 0.99722 | 0.99995 | 0.99911 | 0.99705 | 0.99997
WB | 50078756 | 6205 | EAST B'BERG - B'BERG CENTRAL | 6205_East Bundaberg-BUCE 66 kV | Rating (A) | 397 | 436 | 356 | 397 | 436 | 356 | 397 | 436 | 356 | 397 | 436 | 356 | 397 | 436 | 356
WB | 50079711 | M010 | MARYBOROUGH - OWANYILLA T/LINE | M010_Maryborough - Owanyilla 66 kV
WB | 50079711 | M010 | MARYBOROUGH - OWANYILLA T/LINE | M010_Maryborough - Owanyilla 66 kV | % of Rated A | 56.8712 | 42.0306 | 30.969 | 56.6455 | 41.6376 | 30.9643 | 57.038 | 41.933 | 31.2203 | 57.4202 | 42.2086 | 31.0712 | 57.4386 | 42.2272 | 31.0902
WB | 50079711 | M010 | MARYBOROUGH - OWANYILLA T/LINE | M010_Maryborough - Owanyilla 66 kV | Loading (A) | 141.601 | 160.5483 | 114.5762 | 141.0389 | 159.047 | 114.5588 | 142.0164 | 160.1753 | 115.5058 | 142.968 | 161.2283 | 114.9542 | 143.0137 | 161.2992 | 115.0247
WB | 50079711 | M010 | MARYBOROUGH - OWANYILLA T/LINE | M010_Maryborough - Owanyilla 66 kV | Power Factor | 0.9406 | 0.93435 | 0.94814 | 0.94062 | 0.93483 | 0.94824 | 0.94017 | 0.93426 | 0.94762 | 0.93974 | 0.93429 | 0.94788 | 0.93971 | 0.93425 | 0.94782
WB | 50079711 | M010 | MARYBOROUGH - OWANYILLA T/LINE | M010_Maryborough - Owanyilla 66 kV | Rating (A) | 249 | 382 | 370 | 249 | 382 | 370 | 249 | 382 | 370 | 249 | 382 | 370 | 249 | 382 | 370
WB | 50079712 | M011 | KILKIVAN-MARYBOROUGH | M011_Kilkivan-Maryborough 66 kV
WB | 50079712 | M011 | KILKIVAN-MARYBOROUGH | M011_Kilkivan-Maryborough 66 kV | % of Rated A | 31.2466 | 27.734 | 17.3271 | 30.6447 | 27.0417 | 17.0467 | 30.6773 | 27.0747 | 17.0732 | 30.0527 | 26.5297 | 16.513 | 30.0624 | 26.5416 | 16.523
WB | 50079712 | M011 | KILKIVAN-MARYBOROUGH | M011_Kilkivan-Maryborough 66 kV | Loading (A) | 41.2456 | 46.3152 | 27.5501 | 40.451 | 45.1591 | 27.1043 | 40.494 | 45.2143 | 27.1464 | 39.6696 | 44.304 | 26.2557 | 39.6824 | 44.3239 | 26.2715
WB | 50079712 | M011 | KILKIVAN-MARYBOROUGH | M011_Kilkivan-Maryborough 66 kV | Power Factor | 0.94823 | 0.94644 | 0.95304 | 0.94852 | 0.94696 | 0.95343 | 0.94849 | 0.94692 | 0.9534 | 0.94879 | 0.94725 | 0.95359 | 0.94878 | 0.94723 | 0.95358
WB | 50079712 | M011 | KILKIVAN-MARYBOROUGH | M011_Kilkivan-Maryborough 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
WB | 50079714 | M017 | ROCKY ST - MBOROUGH CITY T/LINE | M017_Rocky St - Maryborough City 66 kV
WB | 50079714 | M017 | ROCKY ST - MBOROUGH CITY T/LINE | M017_Rocky St - Maryborough City 66 kV | % of Rated A | 6.6965 | 1.712 | 3.4019 | 8.7467 | 5.1139 | 6.0204 | 8.891 | 5.1658 | 6.1226 | 8.8772 | 5.169 | 6.1424 | 8.9294 | 5.2027 | 6.1945
WB | 50079714 | M017 | ROCKY ST - MBOROUGH CITY T/LINE | M017_Rocky St - Maryborough City 66 kV | Loading (A) | 36.6967 | 9.9125 | 17.7238 | 47.932 | 29.6092 | 31.3661 | 48.7226 | 29.9098 | 31.8989 | 48.6472 | 29.9284 | 32.0018 | 48.933 | 30.1236 | 32.2736
WB | 50079714 | M017 | ROCKY ST - MBOROUGH CITY T/LINE | M017_Rocky St - Maryborough City 66 kV | Power Factor | 0.99679 | 0.57501 | 0.97419 | 0.97927 | 0.69699 | 0.92294 | 0.98341 | 0.72245 | 0.93062 | 0.98385 | 0.727 | 0.93118 | 0.9834 | 0.72141 | 0.92991
WB | 50079714 | M017 | ROCKY ST - MBOROUGH CITY T/LINE | M017_Rocky St - Maryborough City 66 kV | Rating (A) | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521
WB | 50079715 | M018 | MBOROUGH - MBOROUGH CITY T/TUAN | M018_Maryborough-Maryborough City 66 kV
WB | 50079715 | M018 | MBOROUGH - MBOROUGH CITY T/TUAN | M018_Maryborough-Maryborough City 66 kV | % of Rated A | 25.7926 | 21.4933 | 20.9385 | 28.1829 | 24.4573 | 23.2996 | 28.457 | 24.7261 | 23.5035 | 28.5901 | 24.8721 | 23.6086 | 28.6237 | 24.883 | 23.653
WB | 50079715 | M018 | MBOROUGH - MBOROUGH CITY T/TUAN | M018_Maryborough-Maryborough City 66 kV | Loading (A) | 141.3435 | 124.4462 | 109.0896 | 154.4425 | 141.6073 | 121.391 | 155.9442 | 143.1637 | 122.4535 | 156.674 | 144.0091 | 123.0007 | 156.8579 | 144.0721 | 123.2324
WB | 50079715 | M018 | MBOROUGH - MBOROUGH CITY T/TUAN | M018_Maryborough-Maryborough City 66 kV | Power Factor | 0.99656 | 0.99822 | 0.99087 | 0.99986 | 0.99796 | 0.99891 | 0.99996 | 0.99761 | 0.99912 | 0.99997 | 0.9976 | 0.99916 | 0.99998 | 0.99743 | 0.99923
WB | 50079715 | M018 | MBOROUGH - MBOROUGH CITY T/TUAN | M018_Maryborough-Maryborough City 66 kV | Rating (A) | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521
WB | 50079735 | M007 | PROSTON T/LINE | M007_Proston 66 kV
WB | 50079735 | M007 | PROSTON T/LINE | M007_Proston 66 kV | % of Rated A | 12.4538 | 11.433 | 7.6891 | 12.4947 | 11.4835 | 7.7137 | 12.5036 | 11.4928 | 7.7182 | 12.5129 | 11.5025 | 7.7229 | 12.5216 | 11.5082 | 7.7273
WB | 50079735 | M007 | PROSTON T/LINE | M007_Proston 66 kV | Loading (A) | 12.3292 | 14.52 | 9.3038 | 12.3697 | 14.5841 | 9.3335 | 12.3786 | 14.5958 | 9.339 | 12.3877 | 14.6082 | 9.3447 | 12.3964 | 14.6154 | 9.3501
WB | 50079735 | M007 | PROSTON T/LINE | M007_Proston 66 kV | Power Factor | 0.96563 | 0.9641 | 0.96807 | 0.96587 | 0.96399 | 0.96803 | 0.96586 | 0.96397 | 0.96802 | 0.96584 | 0.96395 | 0.96801 | 0.96583 | 0.96394 | 0.968
WB | 50079735 | M007 | PROSTON T/LINE | M007_Proston 66 kV | Rating (A) | 99 | 127 | 121 | 99 | 127 | 121 | 99 | 127 | 121 | 99 | 127 | 121 | 99 | 127 | 121
WB | 50079738 | M051 | TARONG TIE 66KV T/LINE | M051_Tarong Tie 66 kV
WB | 50079738 | M051 | TARONG TIE 66KV T/LINE | M051_Tarong Tie 66 kV | % of Rated A | 34.3749 | 32.9899 | 29.0629 | 34.5347 | 33.1848 | 29.1796 | 34.5352 | 33.1853 | 29.1799 | 34.5681 | 33.2204 | 29.1957 | 34.5874 | 33.2409 | 29.2031
WB | 50079738 | M051 | TARONG TIE 66KV T/LINE | M051_Tarong Tie 66 kV | Loading (A) | 36.7811 | 45.3723 | 38.3631 | 36.9522 | 45.6418 | 38.5171 | 36.9526 | 45.6425 | 38.5174 | 36.9879 | 45.691 | 38.5383 | 37.0085 | 45.7193 | 38.3914
WB | 50079738 | M051 | TARONG TIE 66KV T/LINE | M051_Tarong Tie 66 kV | Power Factor | 0.952 | 0.95189 | 0.951 | 0.95226 | 0.95164 | 0.95087 | 0.95226 | 0.95164 | 0.95087 | 0.95223 | 0.95159 | 0.95085 | 0.95222 | 0.95157 | 0.95439
WB | 50079738 | M051 | TARONG TIE 66KV T/LINE | M051_Tarong Tie 66 kV | Rating (A) | 107 | 138 | 132 | 107 | 138 | 132 | 107 | 138 | 132 | 107 | 138 | 132 | 107 | 138 | 132
WB | 50079742 | M033 | WALLAVILLE T/LINE | M033_Wallaville 66 kV
WB | 50079742 | M033 | WALLAVILLE T/LINE | M033_Wallaville 66 kV | % of Rated A | 27.7947 | 31.8203 | 33.416 | 28.0672 | 32.1737 | 33.7403 | 28.1003 | 31.7655 | 33.7501 | 28.1743 | 31.8857 | 33.8355 | 28.4842 | 32.2615 | 34.1746
WB | 50079742 | M033 | WALLAVILLE T/LINE | M033_Wallaville 66 kV | Loading (A) | 71.7103 | 84.3238 | 78.1729 | 72.4133 | 85.2602 | 78.9282 | 72.4989 | 84.1786 | 78.9601 | 72.6896 | 84.4972 | 79.1578 | 73.4892 | 85.493 | 79.9475
WB | 50079742 | M033 | WALLAVILLE T/LINE | M033_Wallaville 66 kV | Power Factor | 0.9957 | 0.99978 | 0.99982 | 0.99612 | 0.99988 | 0.99975 | 0.99623 | 0.99985 | 0.99991 | 0.99646 | 0.99972 | 0.99988 | 0.99694 | 0.99984 | 0.9998
WB | 50079742 | M033 | WALLAVILLE T/LINE | M033_Wallaville 66 kV | Rating (A) | 258 | 265 | 234 | 258 | 265 | 234 | 258 | 265 | 234 | 258 | 265 | 234 | 258 | 265 | 234
WB | 50079743 | M034 | MONDURAN DAM T/LINE | M034_Monduran Dam 66 kV
WB | 50079743 | M034 | MONDURAN DAM T/LINE | M034_Monduran Dam 66 kV | % of Rated A | 1.6405 | 9.1646 | 12.2881 | 1.6398 | 9.1722 | 12.2868 | 1.6406 | 9.184 | 12.2934 | 1.6375 | 9.2067 | 12.309 | 1.6366 | 9.2175 | 12.3142
WB | 50079743 | M034 | MONDURAN DAM T/LINE | M034_Monduran Dam 66 kV | Loading (A) | 2.1654 | 16.2213 | 20.8898 | 2.1646 | 16.2349 | 20.8876 | 2.1656 | 16.2556 | 20.8988 | 2.1615 | 16.2959 | 20.9253 | 2.1603 | 16.3149 | 20.9341
WB | 50079743 | M034 | MONDURAN DAM T/LINE | M034_Monduran Dam 66 kV | Power Factor | 0.39104 | 0.80709 | 0.79361 | 0.41933 | 0.80705 | 0.79362 | 0.39098 | 0.80699 | 0.7936 | 0.39242 | 0.80685 | 0.79358 | 0.39285 | 0.8068 | 0.79355
WB | 50079743 | M034 | MONDURAN DAM T/LINE | M034_Monduran Dam 66 kV | Rating (A) | 132 | 177 | 170 | 132 | 177 | 170 | 132 | 177 | 170 | 132 | 177 | 170 | 132 | 177 | 170
WB | 50079744 | M041 | WST BBERG - MEADOWVALE T/LINE | M041_West Bundaberg-Meadowvale 66 kV
WB | 50079744 | M041 | WST BBERG - MEADOWVALE T/LINE | M041_West Bundaberg-Meadowvale 66 kV | % of Rated A | 56.2493 | 51.697 | 50.9579 | 56.1879 | 51.6733 | 50.9489 | 56.2575 | 51.0224 | 50.9963 | 56.8333 | 51.5328 | 51.3937 | 56.8524 | 51.5661 | 51.4226
WB | 50079744 | M041 | WST BBERG - MEADOWVALE T/LINE | M041_West Bundaberg-Meadowvale 66 kV | Loading (A) | 126.9927 | 160.6528 | 131.3394 | 126.8537 | 160.579 | 131.3161 | 127.0112 | 158.5534 | 131.4387 | 128.3124 | 160.1417 | 132.4644 | 128.3559 | 160.2452 | 132.5392
WB | 50079744 | M041 | WST BBERG - MEADOWVALE T/LINE | M041_West Bundaberg-Meadowvale 66 kV | Power Factor | 0.87894 | 0.88798 | 0.87922 | 0.87881 | 0.88797 | 0.87922 | 0.87895 | 0.88817 | 0.87933 | 0.87807 | 0.88875 | 0.88002 | 0.87814 | 0.88879 | 0.88006
WB | 50079744 | M041 | WST BBERG - MEADOWVALE T/LINE | M041_West Bundaberg-Meadowvale 66 kV | Rating (A) | 226 | 311 | 258 | 226 | 311 | 258 | 226 | 311 | 258 | 226 | 311 | 258 | 226 | 311 | 258
WB | 50079745 | M042 | MEADOWVALE - GOOBURRUM T/LINE | M042_Meadowvale-Gooburrum 66 kV
WB | 50079745 | M042 | MEADOWVALE - GOOBURRUM T/LINE | M042_Meadowvale-Gooburrum 66 kV | % of Rated A | 37.4945 | 34.7908 | 37.3041 | 37.4499 | 34.7782 | 37.3015 | 37.5056 | 34.3322 | 37.3428 | 37.6294 | 34.4909 | 37.4428 | 37.6457 | 34.5161 | 37.4623
WB | 50079745 | M042 | MEADOWVALE - GOOBURRUM T/LINE | M042_Meadowvale-Gooburrum 66 kV | Loading (A) | 41.3159 | 50.4909 | 44.0839 | 41.266 | 50.4724 | 44.0809 | 41.3282 | 49.8174 | 44.1302 | 41.4664 | 50.0502 | 44.2499 | 41.4848 | 50.0873 | 44.2732
WB | 50079745 | M042 | MEADOWVALE - GOOBURRUM T/LINE | M042_Meadowvale-Gooburrum 66 kV | Power Factor | 0.90179 | 0.89804 | 0.90042 | 0.90182 | 0.89806 | 0.90042 | 0.90178 | 0.89818 | 0.90038 | 0.90166 | 0.898 | 0.90028 | 0.90165 | 0.89797 | 0.90026
WB | 50079745 | M042 | MEADOWVALE - GOOBURRUM T/LINE | M042_Meadowvale-Gooburrum 66 kV | Rating (A) | 111 | 146 | 119 | 111 | 146 | 119 | 111 | 146 | 119 | 111 | 146 | 119 | 111 | 146 | 119
WB | 50079747 | M025 | 66kV EIDSVOLD T/LINE | M025_Eidsvold 66 kV
WB | 50079747 | M025 | 66kV EIDSVOLD T/LINE | M025_Eidsvold 66 kV | % of Rated A | 18.3157 | 14.6227 | 12.9183 | 18.4567 | 14.7277 | 12.9672 | 18.225 | 14.7695 | 12.9765 | 18.2419 | 14.5799 | 12.9953 | 18.2457 | 14.5948 | 12.7938
WB | 50079747 | M025 | 66kV EIDSVOLD T/LINE | M025_Eidsvold 66 kV | Loading (A) | 19.5978 | 20.1793 | 17.0522 | 19.7487 | 20.3242 | 17.1167 | 19.5007 | 20.3819 | 17.129 | 19.5189 | 20.1203 | 17.1538 | 19.5229 | 20.1409 | 16.8878
WB | 50079747 | M025 | 66kV EIDSVOLD T/LINE | M025_Eidsvold 66 kV | Power Factor | 0.97536 | 0.97504 | 0.97666 | 0.97118 | 0.97085 | 0.97301 | 0.97542 | 0.97477 | 0.97686 | 0.9754 | 0.97512 | 0.97682 | 0.97539 | 0.97509 | 0.97717
WB | 50079747 | M025 | 66kV EIDSVOLD T/LINE | M025_Eidsvold 66 kV | Rating (A) | 107 | 138 | 132 | 107 | 138 | 132 | 107 | 138 | 132 | 107 | 138 | 132 | 107 | 138 | 132
WB | 82554175 | M023 | 6242 PIALBA - POINT VERNON | M023_6242 (Pialba-Point Vernon) 66 kV
WB | 82554175 | M023 | 6242 PIALBA - POINT VERNON | M023_6242 (Pialba-Point Vernon) 66 kV | % of Rated A | 33.6841 | 30.2993 | 21.8136 | 33.6016 | 30.2305 | 21.75 | 33.4855 | 30.1287 | 21.6733 | 33.5513 | 30.2126 | 21.693 | 33.5678 | 30.2285 | 21.697
WB | 82554175 | M023 | 6242 PIALBA - POINT VERNON | M023_6242 (Pialba-Point Vernon) 66 kV | Loading (A) | 203.7887 | 202.3993 | 119.3203 | 203.2895 | 201.9395 | 118.9728 | 202.5873 | 201.2596 | 118.553 | 202.9854 | 201.8202 | 118.6608 | 203.0854 | 201.9262 | 118.6826
WB | 82554175 | M023 | 6242 PIALBA - POINT VERNON | M023_6242 (Pialba-Point Vernon) 66 kV | Power Factor | 0.98834 | 0.98812 | 0.946 | 0.98831 | 0.98811 | 0.94576 | 0.98821 | 0.98801 | 0.94534 | 0.98837 | 0.98728 | 0.94562 | 0.98841 | 0.98733 | 0.94567
WB | 82554175 | M023 | 6242 PIALBA - POINT VERNON | M023_6242 (Pialba-Point Vernon) 66 kV | Rating (A) | 605 | 668 | 547 | 605 | 668 | 547 | 605 | 668 | 547 | 605 | 668 | 547 | 605 | 668 | 547
WB | 82624538 | SOBU-BARG-1 | STH BUNDABERG-BARGARA 66KV FDR | SOBU-BARG-1_SOBU-Bargara-1 66 kV
WB | 82624538 | SOBU-BARG-1 | STH BUNDABERG-BARGARA 66KV FDR | SOBU-BARG-1_SOBU-Bargara-1 66 kV | % of Rated A | 26.2944 | 21.7063 | 14.7903 | 26.0129 | 21.3165 | 14.686 | 26.4016 | 21.6493 | 14.8999 | 26.8343 | 22.0198 | 15.1334 | 27.201 | 22.3244 | 15.3374
WB | 82624538 | SOBU-BARG-1 | STH BUNDABERG-BARGARA 66KV FDR | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Loading (A) | 107.7809 | 137.3736 | 79.6949 | 106.6476 | 134.9265 | 79.1534 | 108.2415 | 137.0335 | 80.3062 | 110.0154 | 139.3785 | 81.5653 | 111.5186 | 141.3063 | 82.6644
WB | 82624538 | SOBU-BARG-1 | STH BUNDABERG-BARGARA 66KV FDR | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Power Factor | 0.97848 | 0.97624 | 0.98069 | 0.99913 | 0.99859 | 0.99954 | 0.99915 | 0.9986 | 0.99952 | 0.99911 | 0.99854 | 0.99952 | 0.99908 | 0.9985 | 0.99951
WB | 82624538 | SOBU-BARG-1 | STH BUNDABERG-BARGARA 66KV FDR | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Rating (A) | 410 | 633 | 539 | 410 | 633 | 539 | 410 | 633 | 539 | 410 | 633 | 539 | 410 | 633 | 539
WB | 83859989 | 785 | 785 ISIS 132KV | 785_ISIS 132 kV
WB | 83859989 | 785 | 785 ISIS 132KV | 785_ISIS 132 kV | % of Rated A | 24.0236 | 20.5623 | 13.7733 | 23.9725 | 20.3489 | 13.325 | 24.6967 | 20.9688 | 13.705 | 24.9974 | 21.6305 | 13.9472 | 25.1235 | 21.7516 | 14.0177
WB | 83859989 | 785 | 785 ISIS 132KV | 785_ISIS 132 kV | Loading (A) | 59.5786 | 81.4268 | 54.1291 | 59.4518 | 80.5818 | 52.3672 | 61.2478 | 83.0363 | 53.8607 | 61.9936 | 85.6568 | 54.8126 | 62.3062 | 86.1362 | 55.0896
WB | 83859989 | 785 | 785 ISIS 132KV | 785_ISIS 132 kV | Power Factor | 0.99477 | 0.81774 | 0.88393 | 0.99295 | 0.8222 | 0.89582 | 0.99514 | 0.82555 | 0.89827 | 0.9972 | 0.98928 | 0.89636 | 0.99766 | 0.9886 | 0.8968
WB | 83859989 | 785 | 785 ISIS 132KV | 785_ISIS 132 kV | Rating (A) | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393
WB | 83859994 | 784 | 784 ISIS 132KV | 784_ISIS 132 kV
WB | 83859994 | 784 | 784 ISIS 132KV | 784_ISIS 132 kV | % of Rated A | 24.1027 | 20.2726 | 14.2794 | 24.0964 | 20.0622 | 14.2774 | 24.7508 | 20.673 | 14.396 | 24.9805 | 21.3198 | 14.4964 | 25.0866 | 21.4392 | 14.4959
WB | 83859994 | 784 | 784 ISIS 132KV | 784_ISIS 132 kV | Loading (A) | 59.7748 | 80.2794 | 56.1182 | 59.759 | 79.4462 | 56.1102 | 61.3821 | 81.8651 | 56.5762 | 61.9517 | 84.4266 | 56.971 | 62.2148 | 84.8993 | 56.9688
WB | 83859994 | 784 | 784 ISIS 132KV | 784_ISIS 132 kV | Power Factor | 0.97852 | 0.81772 | 0.69715 | 0.97505 | 0.82217 | 0.68725 | 0.97994 | 0.82553 | 0.70123 | 0.98459 | 0.98926 | 0.70472 | 0.98576 | 0.98858 | 0.7078
WB | 83859994 | 784 | 784 ISIS 132KV | 784_ISIS 132 kV | Rating (A) | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393
WB | 83859997 | 7330 | 7330 MBH 132KV | 7330_Maryborough 132 kV
WB | 83859997 | 7330 | 7330 MBH 132KV | 7330_Maryborough 132 kV | % of Rated A | 30.3677 | 44.5287 | 32.8288 | 31.8408 | 46.2066 | 34.2576 | 32.1736 | 46.5559 | 34.5075 | 32.4782 | 46.8988 | 34.7102 | 32.6864 | 47.1411 | 34.8778
WB | 83859997 | 7330 | 7330 MBH 132KV | 7330_Maryborough 132 kV | Loading (A) | 170.254 | 266.9943 | 177.9323 | 178.5264 | 276.9984 | 185.6762 | 180.4097 | 279.0973 | 187.0305 | 182.1225 | 281.1401 | 188.1291 | 183.304 | 282.5944 | 189.0379
WB | 83859997 | 7330 | 7330 MBH 132KV | 7330_Maryborough 132 kV | Power Factor | 0.98883 | 0.99941 | 0.99101 | 0.98772 | 0.99897 | 0.9959 | 0.9878 | 0.99898 | 0.99654 | 0.9876 | 0.99886 | 0.99731 | 0.98775 | 0.99886 | 0.99755
WB | 83859997 | 7330 | 7330 MBH 132KV | 7330_Maryborough 132 kV | Rating (A) | 564 | 600 | 542 | 564 | 600 | 542 | 564 | 600 | 542 | 564 | 600 | 542 | 564 | 600 | 542
WB | 83860000 | 7331 | 7331 132KV KILKIVAN | 7331_Kilkivan 132 kV
WB | 83860000 | 7331 | 7331 132KV KILKIVAN | 7331_Kilkivan 132 kV | % of Rated A | 88.6074 | 48.6081 | 53.0319 | 88.6006 | 48.6553 | 53.0583 | 88.6226 | 48.6874 | 53.0687 | 88.6072 | 48.7246 | 53.0783 | 88.619 | 48.7339 | 53.0819
WB | 83860000 | 7331 | 7331 132KV KILKIVAN | 7331_Kilkivan 132 kV | Loading (A) | 209.1135 | 192.4705 | 208.4062 | 209.0974 | 192.6575 | 208.5104 | 209.1492 | 192.785 | 208.5512 | 209.1131 | 192.9324 | 208.5891 | 209.1409 | 192.9694 | 208.6032
WB | 83860000 | 7331 | 7331 132KV KILKIVAN | 7331_Kilkivan 132 kV | Power Factor | 0.99838 | 0.99979 | 0.99994 | 0.99838 | 0.99979 | 0.99995 | 0.99838 | 0.9998 | 0.99995 | 0.99838 | 0.9998 | 0.99995 | 0.99838 | 0.9998 | 0.99995
WB | 83860000 | 7331 | 7331 132KV KILKIVAN | 7331_Kilkivan 132 kV | Rating (A) | 236 | 396 | 393 | 236 | 396 | 393 | 236 | 396 | 393 | 236 | 396 | 393 | 236 | 396 | 393
WB | 83860003 | 7329 | 7329 MBH 132KV | 7329_Maryborough 132 kV
WB | 83860003 | 7329 | 7329 MBH 132KV | 7329_Maryborough 132 kV | % of Rated A | 30.3811 | 44.5487 | 32.8436 | 31.8549 | 46.2272 | 34.273 | 32.1879 | 46.5768 | 34.523 | 32.4926 | 46.9197 | 34.7258 | 32.7008 | 47.1621 | 34.8935
WB | 83860003 | 7329 | 7329 MBH 132KV | 7329_Maryborough 132 kV | Loading (A) | 170.3307 | 267.1143 | 178.0125 | 178.6068 | 277.1229 | 185.7598 | 180.491 | 279.2227 | 187.1147 | 182.2046 | 281.2665 | 188.2138 | 183.3866 | 282.7214 | 189.123
WB | 83860003 | 7329 | 7329 MBH 132KV | 7329_Maryborough 132 kV | Power Factor | 0.98884 | 0.99941 | 0.991 | 0.98772 | 0.99898 | 0.99589 | 0.98781 | 0.99898 | 0.99654 | 0.98761 | 0.99887 | 0.9973 | 0.98776 | 0.99886 | 0.99754
WB | 83860003 | 7329 | 7329 MBH 132KV | 7329_Maryborough 132 kV | Rating (A) | 564 | 600 | 542 | 564 | 600 | 542 | 564 | 600 | 542 | 564 | 600 | 542 | 564 | 600 | 542
WB | 83860136 | 7316 | Aramara 132 kV | 7316_Aramara 132 kV
WB | 83860136 | 7316 | Aramara 132 kV | 7316_Aramara 132 kV | % of Rated A | 11.6343 | 26.9987 | 20.2889 | 12.3458 | 27.8089 | 20.9429 | 12.6952 | 28.1793 | 21.1967 | 12.935 | 28.4617 | 21.3634 | 13.0763 | 28.6207 | 21.4709
WB | 83860136 | 7316 | Aramara 132 kV | 7316_Aramara 132 kV | Loading (A) | 127.0468 | 325.3306 | 224.5982 | 134.8166 | 335.094 | 231.8384 | 138.6314 | 339.5564 | 234.6475 | 141.2497 | 342.9589 | 236.4933 | 142.793 | 344.8749 | 237.6825
WB | 83860136 | 7316 | Aramara 132 kV | 7316_Aramara 132 kV | Power Factor | 0.99649 | 0.99159 | 0.99796 | 0.99582 | 0.99107 | 0.99927 | 0.99518 | 0.99085 | 0.99955 | 0.99394 | 0.99002 | 0.99982 | 0.99375 | 0.98993 | 0.99987
WB | 83860136 | 7316 | Aramara 132 kV | 7316_Aramara 132 kV | Rating (A) | 1092 | 1205 | 1107 | 1092 | 1205 | 1107 | 1092 | 1205 | 1107 | 1092 | 1205 | 1107 | 1092 | 1205 | 1107
WB | 83860139 | 7315 | Aramara 132 kV | 7315_Aramara 132 kV
WB | 83860139 | 7315 | Aramara 132 kV | 7315_Aramara 132 kV | % of Rated A | 11.636 | 27.0025 | 20.2918 | 12.3476 | 27.8129 | 20.9459 | 12.697 | 28.1832 | 21.1997 | 12.9368 | 28.4656 | 21.3665 | 13.0781 | 28.6247 | 21.4739
WB | 83860139 | 7315 | Aramara 132 kV | 7315_Aramara 132 kV | Loading (A) | 127.0646 | 325.3763 | 224.6298 | 134.8355 | 335.1411 | 231.871 | 138.6508 | 339.6041 | 234.6805 | 141.2695 | 343.007 | 236.5266 | 142.813 | 344.9233 | 237.7159
WB | 83860139 | 7315 | Aramara 132 kV | 7315_Aramara 132 kV | Power Factor | 0.99649 | 0.99159 | 0.99796 | 0.99582 | 0.99107 | 0.99927 | 0.99518 | 0.99085 | 0.99955 | 0.99394 | 0.99002 | 0.99982 | 0.99375 | 0.98993 | 0.99987
WB | 83860139 | 7315 | Aramara 132 kV | 7315_Aramara 132 kV | Rating (A) | 1092 | 1205 | 1107 | 1092 | 1205 | 1107 | 1092 | 1205 | 1107 | 1092 | 1205 | 1107 | 1092 | 1205 | 1107
WB | 83901293 | 6302 | BUNDABERG CENTRAL-WEST BUNDABERG | 6302_Bundaberg Central - WEBU 66 kV
WB | 83901293 | 6302 | BUNDABERG CENTRAL-WEST BUNDABERG | 6302_Bundaberg Central - WEBU 66 kV | % of Rated A | 58.7658 | 58.7188 | 48.1165 | 60.2615 | 60.3938 | 49.7043 | 62.2898 | 61.9684 | 51.2872 | 63.1727 | 63.003 | 51.634 | 63.629 | 63.514 | 51.9848
WB | 83901293 | 6302 | BUNDABERG CENTRAL-WEST BUNDABERG | 6302_Bundaberg Central - WEBU 66 kV | Loading (A) | 233.3002 | 256.0141 | 171.2947 | 239.2383 | 263.3168 | 176.9474 | 247.2906 | 270.1821 | 182.5824 | 250.7957 | 274.6932 | 183.8169 | 252.6072 | 276.9209 | 185.0657
WB | 83901293 | 6302 | BUNDABERG CENTRAL-WEST BUNDABERG | 6302_Bundaberg Central - WEBU 66 kV | Power Factor | 0.97278 | 0.98227 | 0.90056 | 0.96686 | 0.97661 | 0.89318 | 0.97019 | 0.97884 | 0.90222 | 0.97682 | 0.98478 | 0.9167 | 0.97766 | 0.98551 | 0.91878
WB | 83901293 | 6302 | BUNDABERG CENTRAL-WEST BUNDABERG | 6302_Bundaberg Central - WEBU 66 kV | Rating (A) | 397 | 436 | 356 | 397 | 436 | 356 | 397 | 436 | 356 | 397 | 436 | 356 | 397 | 436 | 356
WB | 84050534 | 7328 | 7328 BBERG-ISIS NO.2 | 7328_Bundaberg - ISIS No 2 132 kV
WB | 84050534 | 7328 | 7328 BBERG-ISIS NO.2 | 7328_Bundaberg - ISIS No 2 132 kV | % of Rated A | 47.9104 | 13.828 | 29.6201 | 47.3303 | 12.9465 | 29.1965 | 47.2298 | 12.9024 | 29.156 | 47.3411 | 13.0503 | 29.241 | 47.3528 | 13.073 | 29.2328
WB | 84050534 | 7328 | 7328 BBERG-ISIS NO.2 | 7328_Bundaberg - ISIS No 2 132 kV | Loading (A) | 118.8179 | 54.759 | 116.4069 | 117.379 | 51.2683 | 114.7424 | 117.1299 | 51.0935 | 114.5831 | 117.4058 | 51.679 | 114.917 | 117.4348 | 51.769 | 114.8851
WB | 84050534 | 7328 | 7328 BBERG-ISIS NO.2 | 7328_Bundaberg - ISIS No 2 132 kV | Power Factor | 0.98751 | 0.87321 | 0.98436 | 0.98592 | 0.88055 | 0.98205 | 0.98587 | 0.87819 | 0.98192 | 0.98686 | 0.87722 | 0.98167 | 0.98703 | 0.87557 | 0.98184
WB | 84050534 | 7328 | 7328 BBERG-ISIS NO.2 | 7328_Bundaberg - ISIS No 2 132 kV | Rating (A) | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393
WB | 84575625 | M016 | MARYBOROUGH-HOWARD No 2 | M016_Maryborough-Howard No 2 66 kV
WB | 84575625 | M016 | MARYBOROUGH-HOWARD No 2 | M016_Maryborough-Howard No 2 66 kV | % of Rated A | 1.9672 | 1.5425 | 1.6326 | 1.9708 | 1.5403 | 1.6315 | 1.9696 | 1.5381 | 1.6307 | 1.9725 | 1.5364 | 1.6298 | 1.9721 | 1.5358 | 1.6295
WB | 84575625 | M016 | MARYBOROUGH-HOWARD No 2 | M016_Maryborough-Howard No 2 66 kV | Loading (A) | 2.5967 | 2.5759 | 2.5959 | 2.6014 | 2.5724 | 2.5941 | 2.5998 | 2.5687 | 2.5928 | 2.6037 | 2.5658 | 2.5914 | 2.6032 | 2.5648 | 2.5909
WB | 84575625 | M016 | MARYBOROUGH-HOWARD No 2 | M016_Maryborough-Howard No 2 66 kV | Power Factor | 0.00262 | 0.00262 | 0.00262 | 0.00262 | 0.00262 | 0.00262 | 0.00262 | 0.00262 | 0.00262 | 0.00262 | 0.00262 | 0.00262 | 0.00262 | 0.00262 | 0.00262
WB | 84575625 | M016 | MARYBOROUGH-HOWARD No 2 | M016_Maryborough-Howard No 2 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
WB | 85251782 | 6366 | 6366 66kV GOOTCHIE FDR | 6366_Gootchie 33 kV
WB | 85251782 | 6366 | 6366 66kV GOOTCHIE FDR | 6366_Gootchie 33 kV | % of Rated A | 55.1578 | 50.1648 | 32.7419 | 54.6081 | 49.4036 | 32.5449 | 54.6574 | 49.4638 | 32.5962 | 54.6696 | 49.5089 | 32.2317 | 54.6874 | 49.5312 | 32.2514
WB | 85251782 | 6366 | 6366 66kV GOOTCHIE FDR | 6366_Gootchie 33 kV | Loading (A) | 72.805 | 83.7718 | 52.0568 | 72.0794 | 82.5006 | 51.7435 | 72.1445 | 82.6012 | 51.8252 | 72.1607 | 82.6765 | 51.2455 | 72.1841 | 82.7137 | 51.2769
WB | 85251782 | 6366 | 6366 66kV GOOTCHIE FDR | 6366_Gootchie 33 kV | Power Factor | 0.9662 | 0.96257 | 0.97537 | 0.9665 | 0.96302 | 0.97564 | 0.96657 | 0.96296 | 0.97556 | 0.96669 | 0.96321 | 0.97603 | 0.96668 | 0.96318 | 0.976
WB | 85251782 | 6366 | 6366 66kV GOOTCHIE FDR | 6366_Gootchie 33 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159