{"text_format":"1","workbook":"xlsx","n_sheets":292,"sheets":["Disclaimer","Introduction & Notes","INDEX","AGWA","AITK","ALLO","ALSH","ALST","ATHE","AWOO","AYRZ","BALB","BAMB","BARC","BARG","BARR","BEGA","BERS","BEWE","BILO","BING","BLAC","BLAK","BLRI","BLUE","BODA","BOHL","BORE","BOWE","BROX","BUCE","BULL","CACI","CAFE","CALE","CALL","CANN","CANO","CARI","CARM","CAST","CAUP","CAWD","CEPL","CHAL","CHAR","CHIA","CHIL","CHTO","CHTW","CHUM","CLER","CLIF","CLIN","CLON","CLSO","COME","COOK","COOM","CRAI","CRAN","CRED","CRNE","CROY","CUNN","DACE","DAGL","DEGI","DIMB","DURO","DYSA","EAAY","EABU","EATO","EDMO","EIDS","ELRO","EMER","ETON","EUDA","EVEL","FARL","FARN","FREN","GARB","GAYN","GEOR","GEOR1","GIRU","GIVE","GLEE","GLEL","GLEN","GLFS","GLSO","GOOB","GOOT","Gracem","GRCR","GREN","GUML","GUTH","HAPU","HELE","HEPA","HIGH","HILL","HOHI","HOWA","HUGH","ILBI","INGH","JAND","JARV","JUCR","JUPO","KAIM","KALA","KECE","KESP","KIDS","KILL","KING","KIRK","KITO","KOCR","KOUM","LACR","LAKE","LANN","LAQU","LARO","LITT","LOCR","LONG","LUCI","LYLA","MACI","MACN","MAFU","MALC","MARE","MASO","MCCR","MEAD","MEAN","MERI","MERN","MICO","MIDD","MILC","MILE","MILL","MILM","MING","MIRA","MITC","MIVA","MLEP","MOBA","MODA","MOFO","MOGA","MOMO","MOMR","MOMW","MONT","MOOR","MOPA","MORA","MORO","MOSI","MOSK","MOSS","MOUR","MUND","MURG","MUTA","NANA","NAND","NEBO","NESM","NOCL","NOMA","NORM","NORW","NOST","OAKE","OONN","OWAN","PAMP","PAND","PARK","PEAR","PERA","PIAL","PINN","PIRR","PLAN","PLEY","POVE","POZI","PROT","PURR","QUIL","RAGL","RASM","RAVE","RAVN","RICH","ROEA","ROGL","ROLE","ROLL","ROPL","ROSE","ROSO","ROST","ROWE","ROWO","SAGE","SAGT","SARI","SAUN","SHUT","SKIE","SOBL","SOBU","SOKO","SOMA","SOTO","STAM","STTO","STUA","T002","T010","T012","T013","T019","T020","T043","T058","T059","T060","T065","T071","T072","T074","T083","T0831","T095","T116","T130","T131","T159","T163","T166","T176","T188","T189","T194","T198","TANB","TARA","TEST","THAL","THEO","TIER","TOPO","TORQ","TORR","TUAN","TWCE","VERM","VICT","WAEA","WALL","WAND","WEBU","WEDA","WEMA","WETO","WEWA","WINT","WOOD","WOOG","WOOL","WOSO","WOWA","YARR","YASO","YEPP"],"not_rendered":{"charts":0,"images":0,"macros":1,"external_links":0,"defined_names":1,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Disclaimer","index":0,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":"Introduction & Notes","index":1,"n_rows":0,"n_cols":0,"rows_kept":0,"cut":false,"hidden":false,"merged":[]}

{"sheet":"INDEX","index":2,"n_rows":292,"n_cols":23,"rows_kept":292,"cut":false,"hidden":false,"merged":[[1,4,2,13],[3,4,3,8],[3,9,3,13]]}
[]
[null,null,null,null,"NCC Rating (MVA)"]
[]
[null,null,null,null,"SUMMER",null,null,null,null,"WINTER"]
[null,"Substation List","Substation \nType",null,"2019/20","2020/21","2021/22","2022/23","2023/24",2019,2020,2021,2022,2023,null,"Sub Brief","Substation","Summer Range Dates","Winter Range Dates",{"$f":"\"Summer \"&$E$2&\" Range Results\"","v":"Summer NCC Rating (MVA) Range Results"},{"$f":"\"Winter \"&$E$2&\" Range Results\"","v":"Winter NCC Rating (MVA) Range Results"},null,"Title"]
[null,"Agnes Water (66/22kV)","Zone Substation",null,{"$f":"IF(AND($R6<>\"\", $T6<>\"\", $E$2<>\"\", $E$2<>\"-\"), IF(INDEX(INDIRECT($T6), MATCH(E$5, INDIRECT($R6), 0))<>\"\", IF(ISNUMBER(INDEX(INDIRECT($T6), MATCH(E$5, INDIRECT($R6), 0))), ROUND(INDEX(INDIRECT($T6), MATCH(E$5, INDIRECT($R6), 0)), 1), IF($E$2=\"Meets Security Standard\", PROPER(INDEX(INDIRECT($T6), MATCH(E$5, INDIRECT($R6), 0))), INDEX(INDIRECT($T6), MATCH(E$5, INDIRECT($R6), 0)))), \"\"), \"\")","v":48},{"$f":"IF(AND($R6<>\"\", $T6<>\"\", $E$2<>\"\", $E$2<>\"-\"), IF(INDEX(INDIRECT($T6), MATCH(F$5, INDIRECT($R6), 0))<>\"\", IF(ISNUMBER(INDEX(INDIRECT($T6), MATCH(F$5, INDIRECT($R6), 0))), ROUND(INDEX(INDIRECT($T6), MATCH(F$5, INDIRECT($R6), 0)), 1), IF($E$2=\"Meets Security Standard\", PROPER(INDEX(INDIRECT($T6), MATCH(F$5, INDIRECT($R6), 0))), INDEX(INDIRECT($T6), MATCH(F$5, INDIRECT($R6), 0)))), \"\"), \"\")","v":48},48,48,48,{"$f":"IF(AND($S6<>\"\", $U6<>\"\", $E$2<>\"\", $E$2<>\"-\"), IF(INDEX(INDIRECT($U6), MATCH(TEXT(J$5, \"????\"), INDIRECT($S6), 0))<>\"\", IF(INDEX(INDIRECT($U6), MATCH(TEXT(J$5, \"????\"), INDIRECT($S6), 0))<>\"\", IF(ISNUMBER(INDEX(INDIRECT($U6), MATCH(TEXT(J$5, \"????\"), INDIRECT($S6), 0))), ROUND(INDEX(INDIRECT($U6), MATCH(TEXT(J$5, \"????\"), INDIRECT($S6), 0)), 1), IF($E$2=\"Meets Security Standard\", PROPER(INDEX(INDIRECT($U6), MATCH(TEXT(J$5, \"????\"), INDIRECT($S6), 0))), INDEX(INDIRECT($U6), MATCH(TEXT(J$5, \"????\"), INDIRECT($S6), 0)))), \"\"), \"\"), \"\")","v":55.6},{"$f":"IF(AND($S6<>\"\", $U6<>\"\", $E$2<>\"\", $E$2<>\"-\"), IF(INDEX(INDIRECT($U6), MATCH(TEXT(K$5, \"????\"), INDIRECT($S6), 0))<>\"\", IF(INDEX(INDIRECT($U6), MATCH(TEXT(K$5, \"????\"), INDIRECT($S6), 0))<>\"\", IF(ISNUMBER(INDEX(INDIRECT($U6), MATCH(TEXT(K$5, \"????\"), INDIRECT($S6), 0))), ROUND(INDEX(INDIRECT($U6), MATCH(TEXT(K$5, \"????\"), INDIRECT($S6), 0)), 1), IF($E$2=\"Meets Security Standard\", PROPER(INDEX(INDIRECT($U6), MATCH(TEXT(K$5, \"????\"), INDIRECT($S6), 0))), INDEX(INDIRECT($U6), MATCH(TEXT(K$5, \"????\"), INDIRECT($S6), 0)))), \"\"), \"\"), \"\")","v":55.6},55.6,55.6,55.6,null,"Agnes Water","AGWA",{"$f":"IF(ISERROR(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q6&\"!$e$1:$e$55\"), 0))=FALSE, ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q6&\"!$e$1:$e$55\"), 0)+1, MATCH(\"SUMMER\", INDIRECT(ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q6&\"!$e$1:$e$55\"), 0), 1, 1, TRUE, $Q6)&\":$AQ\"&MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q6&\"!$e$1:$e$55\"), 0)), 0), 1, TRUE, $Q6)&\":\"&ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q6&\"!$e$1:$e$55\"), 0)+1, MATCH(\"WINTER\", INDIRECT(ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q6&\"!$e$1:$e$55\"), 0), 1, 1, TRUE, $Q6)&\":$AQ\"&MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q6&\"!$e$1:$e$55\"), 0)), 0)-1, 1, TRUE),\nIF(ISERROR(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q6&\"!$D$1:$D$55\"), 0))=FALSE, ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q6&\"!$D$1:$D$55\"), 0)+1, MATCH(\"SUMMER\", INDIRECT(ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q6&\"!$D$1:$D$55\"), 0), 1, 1, TRUE, $Q6)&\":$AQ\"&MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q6&\"!$D$1:$D$55\"), 0)), 0), 1, TRUE, $Q6)&\":\"&ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q6&\"!$D$1:$D$55\"), 0)+1, MATCH(\"WINTER\", INDIRECT(ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q6&\"!$D$1:$D$55\"), 0), 1, 1, TRUE, $Q6)&\":$AQ\"&MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q6&\"!$D$1:$D$55\"), 0)), 0)-1, 1, TRUE), \"\"))","v":"AGWA!$K$25:$W$25"},{"$f":"IF(ISERROR(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q6&\"!$e$1:$e$55\"), 0))=FALSE, ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q6&\"!$e$1:$e$55\"), 0)+1, MATCH(\"WINTER\", INDIRECT(ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q6&\"!$e$1:$e$55\"), 0), 1, 1, TRUE, $Q6)&\":$AQ\"&MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q6&\"!$e$1:$e$55\"), 0)), 0), 1, TRUE, $Q6)&\":\"&ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q6&\"!$e$1:$e$55\"), 0)+1, 43, 1, TRUE),\nIF(ISERROR(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q6&\"!$D$1:$D$55\"), 0))=FALSE, ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q6&\"!$D$1:$D$55\"), 0)+1, MATCH(\"WINTER\", INDIRECT(ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q6&\"!$D$1:$D$55\"), 0), 1, 1, TRUE, $Q6)&\":$AQ\"&MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q6&\"!$D$1:$D$55\"), 0)), 0), 1, TRUE, $Q6)&\":\"&ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q6&\"!$D$1:$D$55\"), 0)+1, 43, 1, TRUE), \"\"))","v":"AGWA!$X$25:$AQ$25"},{"$f":"IF(ISERROR(MATCH($E$2, INDIRECT($Q6&\"!$E$1:$E$55\"), 0))=FALSE, ADDRESS(MATCH($E$2, INDIRECT($Q6&\"!$E$1:$E$55\"), 0), MATCH(\"SUMMER\", INDIRECT(ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q6&\"!$E$1:$E$55\"), 0), 1, 1, TRUE, $Q6)&\":$AQ\"&MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q6&\"!$E$1:$E$55\"), 0)), 0), 1, TRUE, $Q6)&\":\"&\nADDRESS(MATCH($E$2, INDIRECT($Q6&\"!$E$1:$E$55\"), 0), MATCH(\"WINTER\", INDIRECT(ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q6&\"!$E$1:$E$55\"), 0), 1, 1, TRUE, $Q6)&\":$AQ\"&MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q6&\"!$E$1:$E$55\"), 0)), 0)-1, 1, TRUE),\nIF(ISERROR(MATCH($E$2, INDIRECT($Q6&\"!$d$1:$d$55\"), 0))=FALSE, ADDRESS(MATCH($E$2, INDIRECT($Q6&\"!$d$1:$d$55\"), 0), MATCH(\"SUMMER\", INDIRECT(ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q6&\"!$d$1:$d$55\"), 0), 1, 1, TRUE, $Q6)&\":$AQ\"&MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q6&\"!$d$1:$d$55\"), 0)), 0), 1, TRUE, $Q6)&\":\"&\nADDRESS(MATCH($E$2, INDIRECT($Q6&\"!$d$1:$d$55\"), 0), MATCH(\"WINTER\", INDIRECT(ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q6&\"!$d$1:$d$55\"), 0), 1, 1, TRUE, $Q6)&\":$AQ\"&MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q6&\"!$d$1:$d$55\"), 0)), 0)-1, 1, TRUE), \"\"))","v":"AGWA!$K$26:$W$26"},{"$f":"IF(ISERROR(MATCH($E$2, INDIRECT($Q6&\"!$E$1:$E$55\"), 0))=FALSE, ADDRESS(MATCH($E$2, INDIRECT($Q6&\"!$E$1:$E$55\"), 0), MATCH(\"WINTER\", INDIRECT(ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q6&\"!$E$1:$E$55\"), 0), 1, 1, TRUE, $Q6)&\":$AQ\"&MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q6&\"!$E$1:$E$55\"), 0)), 0), 1, TRUE, $Q6)&\":\"&\nADDRESS(MATCH($E$2, INDIRECT($Q6&\"!$E$1:$E$55\"), 0), 43, 1, TRUE),\nIF(ISERROR(MATCH($E$2, INDIRECT($Q6&\"!$d$1:$d$55\"), 0))=FALSE, ADDRESS(MATCH($E$2, INDIRECT($Q6&\"!$d$1:$d$55\"), 0), MATCH(\"WINTER\", INDIRECT(ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q6&\"!$d$1:$d$55\"), 0), 1, 1, TRUE, $Q6)&\":$AQ\"&MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q6&\"!$d$1:$d$55\"), 0)), 0), 1, TRUE, $Q6)&\":\"&\nADDRESS(MATCH($E$2, INDIRECT($Q6&\"!$d$1:$d$55\"), 0), 43, 1, TRUE), \"\"))","v":"AGWA!$X$26:$AQ$26"},null,"NCC Rating (MVA)"]
[null,"Aitkenvale (66/11kV)","Zone Substation",null,{"$f":"IF(AND($R7<>\"\", $T7<>\"\", $E$2<>\"\", $E$2<>\"-\"), IF(INDEX(INDIRECT($T7), MATCH(E$5, INDIRECT($R7), 0))<>\"\", IF(ISNUMBER(INDEX(INDIRECT($T7), MATCH(E$5, INDIRECT($R7), 0))), ROUND(INDEX(INDIRECT($T7), MATCH(E$5, INDIRECT($R7), 0)), 1), IF($E$2=\"Meets Security Standard\", PROPER(INDEX(INDIRECT($T7), MATCH(E$5, INDIRECT($R7), 0))), INDEX(INDIRECT($T7), MATCH(E$5, INDIRECT($R7), 0)))), \"\"), \"\")","v":61.6},61.6,61.6,61.6,61.6,64.7,64.7,64.7,64.7,64.7,null,"Aitkenvale","AITK",{"$f":"IF(ISERROR(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q7&\"!$e$1:$e$55\"), 0))=FALSE, ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q7&\"!$e$1:$e$55\"), 0)+1, MATCH(\"SUMMER\", INDIRECT(ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q7&\"!$e$1:$e$55\"), 0), 1, 1, TRUE, $Q7)&\":$AQ\"&MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q7&\"!$e$1:$e$55\"), 0)), 0), 1, TRUE, $Q7)&\":\"&ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q7&\"!$e$1:$e$55\"), 0)+1, MATCH(\"WINTER\", INDIRECT(ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q7&\"!$e$1:$e$55\"), 0), 1, 1, TRUE, $Q7)&\":$AQ\"&MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q7&\"!$e$1:$e$55\"), 0)), 0)-1, 1, TRUE),\nIF(ISERROR(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q7&\"!$D$1:$D$55\"), 0))=FALSE, ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q7&\"!$D$1:$D$55\"), 0)+1, MATCH(\"SUMMER\", INDIRECT(ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q7&\"!$D$1:$D$55\"), 0), 1, 1, TRUE, $Q7)&\":$AQ\"&MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q7&\"!$D$1:$D$55\"), 0)), 0), 1, TRUE, $Q7)&\":\"&ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q7&\"!$D$1:$D$55\"), 0)+1, MATCH(\"WINTER\", INDIRECT(ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q7&\"!$D$1:$D$55\"), 0), 1, 1, TRUE, $Q7)&\":$AQ\"&MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q7&\"!$D$1:$D$55\"), 0)), 0)-1, 1, TRUE), \"\"))","v":"AITK!$K$25:$W$25"},{"$f":"IF(ISERROR(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q7&\"!$e$1:$e$55\"), 0))=FALSE, ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q7&\"!$e$1:$e$55\"), 0)+1, MATCH(\"WINTER\", INDIRECT(ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q7&\"!$e$1:$e$55\"), 0), 1, 1, TRUE, $Q7)&\":$AQ\"&MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q7&\"!$e$1:$e$55\"), 0)), 0), 1, TRUE, $Q7)&\":\"&ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q7&\"!$e$1:$e$55\"), 0)+1, 43, 1, TRUE),\nIF(ISERROR(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q7&\"!$D$1:$D$55\"), 0))=FALSE, ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q7&\"!$D$1:$D$55\"), 0)+1, MATCH(\"WINTER\", INDIRECT(ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q7&\"!$D$1:$D$55\"), 0), 1, 1, TRUE, $Q7)&\":$AQ\"&MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q7&\"!$D$1:$D$55\"), 0)), 0), 1, TRUE, $Q7)&\":\"&ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q7&\"!$D$1:$D$55\"), 0)+1, 43, 1, TRUE), \"\"))","v":"AITK!$X$25:$AQ$25"},"AITK!$K$26:$W$26","AITK!$X$26:$AQ$26",null,"Contracted non-network (MVA)"]
[null,"Alan Sherriff (132/11kV)","Zone Substation",null,70,70,70,70,70,73.5,73.5,73.5,73.5,73.5,null,"Alan Sherriff","ALSH","ALSH!$K$25:$W$25","ALSH!$X$25:$AQ$25","ALSH!$K$26:$W$26","ALSH!$X$26:$AQ$26",null,"10 PoE Load (MVA)"]
[null,"Alfred Street (33/11kV)","Zone Substation",null,90.7,90.7,90.7,90.7,90.7,93.7,93.7,93.7,93.7,93.7,null,"Alfred Street","ALST","ALST!$K$25:$W$25","ALST!$X$25:$AQ$25","ALST!$K$26:$W$26","ALST!$X$26:$AQ$26",null,"LARn (MVA)"]
[null,"Alligator Creek BSP (132/33kV)","Bulk Supply",null,200,200,200,200,200,200,200,200,200,200,null,"Alligator Creek BSP","T065","'T065'!$J$23:$V$23","'T065'!$W$23:$AQ$23","'T065'!$J$24:$V$24","'T065'!$W$24:$AQ$24",null,"LARn (MW)"]
[null,"Allora (33/11kV)","Zone Substation",null,7.3,7.3,7.3,7.3,7.3,7.9,7.9,7.9,7.9,7.9,null,"Allora","ALLO","ALLO!$K$25:$W$25","ALLO!$X$25:$AQ$25","ALLO!$K$26:$W$26","ALLO!$X$26:$AQ$26",null,"Power Factor at Peak Load"]
[null,"Atherton (66/22kV)","Zone Substation",null,88.1,88.1,88.1,88.1,88.1,97.4,97.4,97.4,97.4,97.4,null,"Atherton","ATHE","ATHE!$K$25:$W$25","ATHE!$X$25:$AQ$25","ATHE!$K$26:$W$26","ATHE!$X$26:$AQ$26",null,"ECC Rating (MVA)"]
[null,"Awoonga (66/11kV)","Zone Substation",null,24.4,24.4,24.4,24.4,24.4,25.7,25.7,25.7,25.7,25.7,null,"Awoonga","AWOO","AWOO!$K$25:$W$25","AWOO!$X$25:$AQ$25","AWOO!$K$26:$W$26","AWOO!$X$26:$AQ$26",null,"50 PoE Load (MVA)"]
[null,"Ayr (66/11kV)","Zone Substation",null,23.9,23.9,23.9,23.9,23.9,25.4,25.4,25.4,25.4,25.4,null,"Ayr","AYRZ","AYRZ!$K$25:$W$25","AYRZ!$X$25:$AQ$25","AYRZ!$K$26:$W$26","AYRZ!$X$26:$AQ$26",null,"50 PoE Load >  95%  (MVA)"]
[null,"Balberra (33/11kV)","Zone Substation",null,7,7,7,7,7,7.5,7.5,7.5,7.5,7.5,null,"Balberra","BALB","BALB!$K$25:$W$25","BALB!$X$25:$AQ$25","BALB!$K$26:$W$26","BALB!$X$26:$AQ$26",null,"Hours PA >  95%  Peak Load"]
[null,"Bambaroo (66/11kV)","Zone Substation",null,2.2000000000000002,2.2000000000000002,2.2000000000000002,2.2000000000000002,2.2000000000000002,2.2000000000000002,2.2000000000000002,2.2000000000000002,2.2000000000000002,2.2000000000000002,null,"Bambaroo","BAMB","BAMB!$K$25:$W$25","BAMB!$X$25:$AQ$25","BAMB!$K$26:$W$26","BAMB!$X$26:$AQ$26",null,"Raw LAR (MVA)"]
[null,"Barcaldine (66/22kV)","Zone Substation",null,4,4,4,4,4,4,4,4,4,4,null,"Barcaldine","BARR","BARR!$K$25:$W$25","BARR!$X$25:$AQ$25","BARR!$K$26:$W$26","BARR!$X$26:$AQ$26",null,"Auto Trans Avail (MVA)"]
[null,"Barcaldine BSP (132/66kV)","Bulk Supply",null,26.6,26.6,26.6,26.6,26.6,26.6,26.6,26.6,26.6,26.6,null,"Barcaldine BSP","T072","'T072'!$J$23:$V$23","'T072'!$W$23:$AQ$23","'T072'!$J$24:$V$24","'T072'!$W$24:$AQ$24",null,"Remote Trans Avail (MVA)"]
[null,"Bargara (66/11kV)","Zone Substation",null,69.900000000000006,69.900000000000006,69.900000000000006,69.900000000000006,69.900000000000006,74.8,74.8,74.8,74.8,74.8,null,"Bargara","BARG","BARG!$K$25:$W$25","BARG!$X$25:$AQ$25","BARG!$K$26:$W$26","BARG!$X$26:$AQ$26",null,"Manual Trans Avail (MVA)"]
[null,"Barratta (66/11kV)","Zone Substation",null,25.8,25.8,25.8,25.8,25.8,30,30,30,30,30,null,"Barratta","BARC","BARC!$K$25:$W$25","BARC!$X$25:$AQ$25","BARC!$K$26:$W$26","BARC!$X$26:$AQ$26",null,"Mobile Plant Avail (MVA)"]
[null,"Bedford Weir (66/22kV)","Zone Substation",null,20.9,20.9,20.9,20.9,20.9,23.3,23.3,23.3,23.3,23.3,null,"Bedford Weir","BEWE","BEWE!$K$25:$W$25","BEWE!$X$25:$AQ$25","BEWE!$K$26:$W$26","BEWE!$X$26:$AQ$26",null,"Shed(30min)"]
[null,"Belgian Gardens (66/11kV)","Zone Substation",null,73.900000000000006,73.900000000000006,73.900000000000006,73.900000000000006,73.900000000000006,76.599999999999994,76.599999999999994,76.599999999999994,76.599999999999994,76.599999999999994,null,"Belgian Gardens","BEGA","BEGA!$K$25:$W$25","BEGA!$X$25:$AQ$25","BEGA!$K$26:$W$26","BEGA!$X$26:$AQ$26",null,"Shed(4Hour)"]
[null,"Berserker (66/11kV)","Zone Substation",null,78.5,78.5,78.5,78.5,78.5,88,88,88,88,88,null,"Berserker","BERS","BERS!$K$25:$W$25","BERS!$X$25:$AQ$25","BERS!$K$26:$W$26","BERS!$X$26:$AQ$26",null,"LARc (MVA)"]
[null,"Biloela (66/11kV)","Zone Substation",null,47.3,47.3,47.3,47.3,47.3,55,55,55,55,55,null,"Biloela","BILO","BILO!$K$25:$W$25","BILO!$X$25:$AQ$25","BILO!$K$26:$W$26","BILO!$X$26:$AQ$26",null,"LARc (MW)"]
[null,"Bingegang (66/22kV)","Zone Substation",null,10,10,10,10,10,12,12,12,12,12,null,"Bingegang","BING","BING!$K$25:$W$25","BING!$X$25:$AQ$25","BING!$K$26:$W$26","BING!$X$26:$AQ$26",null,"Substation Category"]
[null,"Black River (66/11kV)","Zone Substation",null,56,56,56,56,56,59.1,59.1,59.1,59.1,59.1,null,"Black River","BLRI","BLRI!$K$25:$W$25","BLRI!$X$25:$AQ$25","BLRI!$K$26:$W$26","BLRI!$X$26:$AQ$26",null,"Meets Security Standard"]
[null,"Blackall (66/22kV)","Zone Substation",null,13.9,13.9,13.9,13.9,13.9,16.5,16.5,16.5,16.5,16.5,null,"Blackall","BLAK","BLAK!$K$25:$W$25","BLAK!$X$25:$AQ$25","BLAK!$K$26:$W$26","BLAK!$X$26:$AQ$26"]
[null,"Blackwater (11/22kV)","Zone Substation",null,{"$f":"IF(AND($R28<>\"\", $T28<>\"\", $E$2<>\"\", $E$2<>\"-\"), IF(INDEX(INDIRECT($T28), MATCH(E$5, INDIRECT($R28), 0))<>\"\", IF(ISNUMBER(INDEX(INDIRECT($T28), MATCH(E$5, INDIRECT($R28), 0))), ROUND(INDEX(INDIRECT($T28), MATCH(E$5, INDIRECT($R28), 0)), 1), IF($E$2=\"Meets Security Standard\", PROPER(INDEX(INDIRECT($T28), MATCH(E$5, INDIRECT($R28), 0))), INDEX(INDIRECT($T28), MATCH(E$5, INDIRECT($R28), 0)))), \"\"), \"\")","v":20},20,20,20,20,{"$f":"IF(AND($S28<>\"\", $U28<>\"\", $E$2<>\"\", $E$2<>\"-\"), IF(INDEX(INDIRECT($U28), MATCH(TEXT(J$5, \"????\"), INDIRECT($S28), 0))<>\"\", IF(INDEX(INDIRECT($U28), MATCH(TEXT(J$5, \"????\"), INDIRECT($S28), 0))<>\"\", IF(ISNUMBER(INDEX(INDIRECT($U28), MATCH(TEXT(J$5, \"????\"), INDIRECT($S28), 0))), ROUND(INDEX(INDIRECT($U28), MATCH(TEXT(J$5, \"????\"), INDIRECT($S28), 0)), 1), IF($E$2=\"Meets Security Standard\", PROPER(INDEX(INDIRECT($U28), MATCH(TEXT(J$5, \"????\"), INDIRECT($S28), 0))), INDEX(INDIRECT($U28), MATCH(TEXT(J$5, \"????\"), INDIRECT($S28), 0)))), \"\"), \"\"), \"\")","v":20},20,20,20,20,null,"Blackwater","BLAC","BLAC!$K$25:$W$25","BLAC!$X$25:$AQ$25","BLAC!$K$26:$W$26","BLAC!$X$26:$AQ$26"]
[null,"Bluewater (66/11kV)","Zone Substation",null,5.3,5.3,5.3,5.3,5.3,5.5,5.5,5.5,5.5,5.5,null,"Bluewater","BLUE","BLUE!$K$25:$W$25","BLUE!$X$25:$AQ$25","BLUE!$K$26:$W$26","BLUE!$X$26:$AQ$26"]
[null,"Boat Creek BSP (132/66kV)","Bulk Supply",null,151.19999999999999,151.19999999999999,151.19999999999999,151.19999999999999,151.19999999999999,162,162,162,162,162,null,"Boat Creek BSP","T130","'T130'!$J$23:$V$23","'T130'!$W$23:$AQ$23","'T130'!$J$24:$V$24","'T130'!$W$24:$AQ$24"]
[null,"Bohle (66/11kV)","Zone Substation",null,52.7,52.7,52.7,52.7,52.7,55.3,55.3,55.3,55.3,55.3,null,"Bohle","BOHL","BOHL!$K$25:$W$25","BOHL!$X$25:$AQ$25","BOHL!$K$26:$W$26","BOHL!$X$26:$AQ$26"]
[null,"Boondooma Dam (66/11kV)","Zone Substation",null,5.2,5.2,5.2,5.2,5.2,5.5,5.5,5.5,5.5,5.5,null,"Boondooma Dam","BODA","BODA!$K$25:$W$25","BODA!$X$25:$AQ$25","BODA!$K$26:$W$26","BODA!$X$26:$AQ$26"]
[null,"Bowen (66/11kV)","Zone Substation",null,39.799999999999997,39.799999999999997,39.799999999999997,39.799999999999997,39.799999999999997,44.4,44.4,44.4,44.4,44.4,null,"Bowen","BOWE","BOWE!$K$25:$W$25","BOWE!$X$25:$AQ$25","BOWE!$K$26:$W$26","BOWE!$X$26:$AQ$26"]
[null,"Boyne Residential (66/11kV)","Zone Substation",null,26,26,26,26,26,29.9,29.9,29.9,29.9,29.9,null,"Boyne Residential","BORE","BORE!$K$25:$W$25","BORE!$X$25:$AQ$25","BORE!$K$26:$W$26","BORE!$X$26:$AQ$26"]
[null,"Broadlea BSP (132/66kV)","Bulk Supply",null,223.1,223.1,223.1,223.1,223.1,241.4,241.4,241.4,241.4,241.4,null,"Broadlea BSP","T198","'T198'!$J$23:$V$23","'T198'!$W$23:$AQ$23","'T198'!$J$24:$V$24","'T198'!$W$24:$AQ$24"]
[null,"Broxburn (33/11kV)","Zone Substation",null,11,11,11,11,11,11,11,11,11,11,null,"Broxburn","BROX","BROX!$K$25:$W$25","BROX!$X$25:$AQ$25","BROX!$K$26:$W$26","BROX!$X$26:$AQ$26"]
[null,"Bullyard (66/11kV)","Zone Substation",null,14.2,14.2,14.2,14.2,14.2,15,15,15,15,15,null,"Bullyard","BULL","BULL!$K$25:$W$25","BULL!$X$25:$AQ$25","BULL!$K$26:$W$26","BULL!$X$26:$AQ$26"]
[null,"Bundaberg BSP (132/66kV)","Bulk Supply",null,226.4,226.4,226.4,226.4,226.4,250.8,250.8,250.8,250.8,250.8,null,"Bundaberg BSP","T020","'T020'!$J$23:$V$23","'T020'!$W$23:$AQ$23","'T020'!$J$24:$V$24","'T020'!$W$24:$AQ$24"]
[null,"Bundaberg Central (66/11kV)","Zone Substation",null,80.3,80.3,80.3,80.3,80.3,87.4,87.4,87.4,87.4,87.4,null,"Bundaberg Central","BUCE","BUCE!$K$25:$W$25","BUCE!$X$25:$AQ$25","BUCE!$K$26:$W$26","BUCE!$X$26:$AQ$26"]
[null,"Cairns City (132/22kV)","Zone Substation",null,182.3,182.3,182.3,182.3,182.3,187.9,187.9,187.9,187.9,187.9,null,"Cairns City","CACI","CACI!$K$25:$W$25","CACI!$X$25:$AQ$25","CACI!$K$26:$W$26","CACI!$X$26:$AQ$26"]
[null,"Cairns North (132/22kV)","Zone Substation",null,142.80000000000001,142.80000000000001,142.80000000000001,142.80000000000001,142.80000000000001,147.1,147.1,147.1,147.1,147.1,null,"Cairns North","CANO","CANO!$K$25:$W$25","CANO!$X$25:$AQ$25","CANO!$K$26:$W$26","CANO!$X$26:$AQ$26"]
[null,"Calen (66/11kV)","Zone Substation",null,11,11,11,11,11,12,12,12,12,12,null,"Calen","CALE","CALE!$K$25:$W$25","CALE!$X$25:$AQ$25","CALE!$K$26:$W$26","CALE!$X$26:$AQ$26"]
[null,"Calliope (66/11kV)","Zone Substation",null,26.7,26.7,26.7,26.7,26.7,29.9,29.9,29.9,29.9,29.9,null,"Calliope","CALL","CALL!$K$25:$W$25","CALL!$X$25:$AQ$25","CALL!$K$26:$W$26","CALL!$X$26:$AQ$26"]
[null,"Canning Street (66/11kV)","Zone Substation",null,46.3,46.3,46.3,46.3,46.3,54.2,54.2,54.2,54.2,54.2,null,"Canning Street","CAST","CAST!$K$25:$W$25","CAST!$X$25:$AQ$25","CAST!$K$26:$W$26","CAST!$X$26:$AQ$26"]
[null,"Cannonvale (66/11kV)","Zone Substation",null,34.9,34.9,34.9,34.9,34.9,37.799999999999997,37.799999999999997,37.799999999999997,37.799999999999997,37.799999999999997,null,"Cannonvale","CANN","CANN!$K$25:$W$25","CANN!$X$25:$AQ$25","CANN!$K$26:$W$26","CANN!$X$26:$AQ$26"]
[null,"Cape Ferguson (66/11kV)","Zone Substation",null,4.4000000000000004,4.4000000000000004,4.4000000000000004,4.4000000000000004,4.4000000000000004,4.7,4.7,4.7,4.7,4.7,null,"Cape Ferguson","CAFE","CAFE!$K$25:$W$25","CAFE!$X$25:$AQ$25","CAFE!$K$26:$W$26","CAFE!$X$26:$AQ$26"]
[null,"Cape River (66/11kV)","Zone Substation",null,1,1,1,1,1,1.1000000000000001,1.1000000000000001,1.1000000000000001,1.1000000000000001,1.1000000000000001,null,"Cape River","CARI","CARI!$K$25:$W$25","CARI!$X$25:$AQ$25","CARI!$K$26:$W$26","CARI!$X$26:$AQ$26"]
[null,"Cape Upstart (66/11kV)","Zone Substation",null,"","",10,10,10,"","",10,10,10,null,"Cape Upstart","CAUP","CAUP!$K$25:$W$25","CAUP!$X$25:$AQ$25","CAUP!$K$26:$W$26","CAUP!$X$26:$AQ$26"]
[null,"Carmila (33/11kV)","Zone Substation",null,1.3,1.3,1.3,1.3,1.3,1.4,1.4,1.4,1.4,1.4,null,"Carmila","CARM","CARM!$K$25:$W$25","CARM!$X$25:$AQ$25","CARM!$K$26:$W$26","CARM!$X$26:$AQ$26"]
[null,"Cawdor (33/11kV)","Zone Substation",null,10,10,10,10,10,10,10,10,10,10,null,"Cawdor","CAWD","CAWD!$K$25:$W$25","CAWD!$X$25:$AQ$25","CAWD!$K$26:$W$26","CAWD!$X$26:$AQ$26"]
[null,"Cecil Plains (33/11kV)","Zone Substation",null,10,10,10,10,10,10,10,10,10,10,null,"Cecil Plains","CEPL","CEPL!$K$25:$W$25","CEPL!$X$25:$AQ$25","CEPL!$K$26:$W$26","CEPL!$X$26:$AQ$26"]
[null,"Charleville (66/2211kV)","Zone Substation",null,18.600000000000001,18.600000000000001,18.600000000000001,18.600000000000001,18.600000000000001,18.600000000000001,18.600000000000001,18.600000000000001,18.600000000000001,18.600000000000001,null,"Charleville","CHAR","CHAR!$K$25:$W$25","CHAR!$X$25:$AQ$25","CHAR!$K$26:$W$26","CHAR!$X$26:$AQ$26"]
[null,"Charlton (33/11kV)","Zone Substation",null,11,11,11,11,11,11,11,11,11,11,null,"Charlton","CHAL","CHAL!$K$25:$W$25","CHAL!$X$25:$AQ$25","CHAL!$K$26:$W$26","CHAL!$X$26:$AQ$26"]
[null,"Charters Towers (66/11kV)","Zone Substation",null,21,21,21,21,21,23,23,23,23,23,null,"Charters Towers","CHTO","CHTO!$K$25:$W$25","CHTO!$X$25:$AQ$25","CHTO!$K$26:$W$26","CHTO!$X$26:$AQ$26"]
[null,"Childers (66/11kV)","Zone Substation",null,20.9,20.9,20.9,20.9,20.9,22.4,22.4,22.4,22.4,22.4,null,"Childers","CHIL","CHIL!$K$25:$W$25","CHIL!$X$25:$AQ$25","CHIL!$K$26:$W$26","CHIL!$X$26:$AQ$26"]
[null,"Chillagoe (66/22kV)","Zone Substation",null,8.9,8.9,8.9,8.9,8.9,9.1999999999999993,9.1999999999999993,9.1999999999999993,9.1999999999999993,9.1999999999999993,null,"Chillagoe","CHIA","CHIA!$K$25:$W$25","CHIA!$X$25:$AQ$25","CHIA!$K$26:$W$26","CHIA!$X$26:$AQ$26"]
[null,"Chinchilla BSP (132/33kV)","Bulk Supply",null,66,66,66,66,66,66,66,66,66,66,null,"Chinchilla BSP","T013","'T013'!$J$23:$V$23","'T013'!$W$23:$AQ$23","'T013'!$J$24:$V$24","'T013'!$W$24:$AQ$24"]
[null,"Chinchilla Skid (33/11kV)","Zone Substation",null,7.5,7.5,7.5,7.5,7.5,7.5,7.5,7.5,7.5,7.5,null,"Chinchilla Skid","SKIE","SKIE!$K$25:$W$25","SKIE!$X$25:$AQ$25","SKIE!$K$26:$W$26","SKIE!$X$26:$AQ$26"]
[null,"Chinchilla Town (33/11kV)","Zone Substation",null,13.7,13.7,13.7,13.7,13.7,15,15,15,15,15,null,"Chinchilla Town","CHTW","CHTW!$K$25:$W$25","CHTW!$X$25:$AQ$25","CHTW!$K$26:$W$26","CHTW!$X$26:$AQ$26"]
[null,"Chumvale BSP (220/66kV)","Bulk Supply",null,49.8,49.8,49.8,49.8,49.8,49.8,49.8,49.8,49.8,49.8,null,"Chumvale BSP","CHUM","CHUM!$J$23:$V$23","CHUM!$W$23:$AQ$23","CHUM!$J$24:$V$24","CHUM!$W$24:$AQ$24"]
[null,"Clare South (66/11kV)","Zone Substation",null,7.5,7.5,7.5,7.5,7.5,8.3000000000000007,8.3000000000000007,8.3000000000000007,8.3000000000000007,8.3000000000000007,null,"Clare South","CLSO","CLSO!$K$25:$W$25","CLSO!$X$25:$AQ$25","CLSO!$K$26:$W$26","CLSO!$X$26:$AQ$26"]
[null,"Clermont (66/22kV)","Zone Substation",null,20,20,20,20,20,20,20,20,20,20,null,"Clermont","CLER","CLER!$K$25:$W$25","CLER!$X$25:$AQ$25","CLER!$K$26:$W$26","CLER!$X$26:$AQ$26"]
[null,"Clermont BSP (132/66kV)","Bulk Supply",null,80.900000000000006,80.900000000000006,80.900000000000006,80.900000000000006,80.900000000000006,86.9,86.9,86.9,86.9,86.9,null,"Clermont BSP","T071","'T071'!$J$23:$V$23","'T071'!$W$23:$AQ$23","'T071'!$J$24:$V$24","'T071'!$W$24:$AQ$24"]
[null,"Clifton (33/11kV)","Zone Substation",null,8,8,8,8,8,8.6999999999999993,8.6999999999999993,8.6999999999999993,8.6999999999999993,8.6999999999999993,null,"Clifton","CLIF","CLIF!$K$25:$W$25","CLIF!$X$25:$AQ$25","CLIF!$K$26:$W$26","CLIF!$X$26:$AQ$26"]
[null,"Clinton (66/11kV)","Zone Substation",null,70.599999999999994,70.599999999999994,70.599999999999994,70.599999999999994,70.599999999999994,74.8,74.8,74.8,74.8,74.8,null,"Clinton","CLIN","CLIN!$K$25:$W$25","CLIN!$X$25:$AQ$25","CLIN!$K$26:$W$26","CLIN!$X$26:$AQ$26"]
[null,"Cloncurry (66/11kV)","Zone Substation",null,6.7,6.7,6.7,6.7,6.7,6.9,6.9,6.9,6.9,6.9,null,"Cloncurry","CLON","CLON!$K$25:$W$25","CLON!$X$25:$AQ$25","CLON!$K$26:$W$26","CLON!$X$26:$AQ$26"]
[null,"Columboola BSP (132/33kV)","Bulk Supply",null,40.200000000000003,40.200000000000003,40.200000000000003,40.200000000000003,40.200000000000003,47.4,47.4,47.4,47.4,47.4,null,"Columboola BSP","T194","'T194'!$J$23:$V$23","'T194'!$W$23:$AQ$23","'T194'!$J$24:$V$24","'T194'!$W$24:$AQ$24"]
[null,"Comet (66/22kV)","Zone Substation",null,5.5,5.5,5.5,5.5,5.5,6.4,6.4,6.4,6.4,6.4,null,"Comet","COME","COME!$K$25:$W$25","COME!$X$25:$AQ$25","COME!$K$26:$W$26","COME!$X$26:$AQ$26"]
[null,"Cooktown (66/22kV)","Zone Substation",null,21.5,21.5,21.5,21.5,21.5,24.6,24.6,24.6,24.6,24.6,null,"Cooktown","COOK","COOK!$K$25:$W$25","COOK!$X$25:$AQ$25",{"$f":"IF(ISERROR(MATCH($E$2, INDIRECT($Q69&\"!$E$1:$E$55\"), 0))=FALSE, ADDRESS(MATCH($E$2, INDIRECT($Q69&\"!$E$1:$E$55\"), 0), MATCH(\"SUMMER\", INDIRECT(ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q69&\"!$E$1:$E$55\"), 0), 1, 1, TRUE, $Q69)&\":$AQ\"&MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q69&\"!$E$1:$E$55\"), 0)), 0), 1, TRUE, $Q69)&\":\"&\nADDRESS(MATCH($E$2, INDIRECT($Q69&\"!$E$1:$E$55\"), 0), MATCH(\"WINTER\", INDIRECT(ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q69&\"!$E$1:$E$55\"), 0), 1, 1, TRUE, $Q69)&\":$AQ\"&MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q69&\"!$E$1:$E$55\"), 0)), 0)-1, 1, TRUE),\nIF(ISERROR(MATCH($E$2, INDIRECT($Q69&\"!$d$1:$d$55\"), 0))=FALSE, ADDRESS(MATCH($E$2, INDIRECT($Q69&\"!$d$1:$d$55\"), 0), MATCH(\"SUMMER\", INDIRECT(ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q69&\"!$d$1:$d$55\"), 0), 1, 1, TRUE, $Q69)&\":$AQ\"&MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q69&\"!$d$1:$d$55\"), 0)), 0), 1, TRUE, $Q69)&\":\"&\nADDRESS(MATCH($E$2, INDIRECT($Q69&\"!$d$1:$d$55\"), 0), MATCH(\"WINTER\", INDIRECT(ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q69&\"!$d$1:$d$55\"), 0), 1, 1, TRUE, $Q69)&\":$AQ\"&MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q69&\"!$d$1:$d$55\"), 0)), 0)-1, 1, TRUE), \"\"))","v":"COOK!$K$26:$W$26"},{"$f":"IF(ISERROR(MATCH($E$2, INDIRECT($Q69&\"!$E$1:$E$55\"), 0))=FALSE, ADDRESS(MATCH($E$2, INDIRECT($Q69&\"!$E$1:$E$55\"), 0), MATCH(\"WINTER\", INDIRECT(ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q69&\"!$E$1:$E$55\"), 0), 1, 1, TRUE, $Q69)&\":$AQ\"&MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q69&\"!$E$1:$E$55\"), 0)), 0), 1, TRUE, $Q69)&\":\"&\nADDRESS(MATCH($E$2, INDIRECT($Q69&\"!$E$1:$E$55\"), 0), 43, 1, TRUE),\nIF(ISERROR(MATCH($E$2, INDIRECT($Q69&\"!$d$1:$d$55\"), 0))=FALSE, ADDRESS(MATCH($E$2, INDIRECT($Q69&\"!$d$1:$d$55\"), 0), MATCH(\"WINTER\", INDIRECT(ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q69&\"!$d$1:$d$55\"), 0), 1, 1, TRUE, $Q69)&\":$AQ\"&MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q69&\"!$d$1:$d$55\"), 0)), 0), 1, TRUE, $Q69)&\":\"&\nADDRESS(MATCH($E$2, INDIRECT($Q69&\"!$d$1:$d$55\"), 0), 43, 1, TRUE), \"\"))","v":"COOK!$X$26:$AQ$26"}]
[null,"Coominglah (66/22kV)","Zone Substation",null,2.6,2.6,2.6,2.6,2.6,3,3,3,3,3,null,"Coominglah","COOM",{"$f":"IF(ISERROR(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q70&\"!$e$1:$e$55\"), 0))=FALSE, ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q70&\"!$e$1:$e$55\"), 0)+1, MATCH(\"SUMMER\", INDIRECT(ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q70&\"!$e$1:$e$55\"), 0), 1, 1, TRUE, $Q70)&\":$AQ\"&MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q70&\"!$e$1:$e$55\"), 0)), 0), 1, TRUE, $Q70)&\":\"&ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q70&\"!$e$1:$e$55\"), 0)+1, MATCH(\"WINTER\", INDIRECT(ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q70&\"!$e$1:$e$55\"), 0), 1, 1, TRUE, $Q70)&\":$AQ\"&MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q70&\"!$e$1:$e$55\"), 0)), 0)-1, 1, TRUE),\nIF(ISERROR(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q70&\"!$D$1:$D$55\"), 0))=FALSE, ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q70&\"!$D$1:$D$55\"), 0)+1, MATCH(\"SUMMER\", INDIRECT(ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q70&\"!$D$1:$D$55\"), 0), 1, 1, TRUE, $Q70)&\":$AQ\"&MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q70&\"!$D$1:$D$55\"), 0)), 0), 1, TRUE, $Q70)&\":\"&ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q70&\"!$D$1:$D$55\"), 0)+1, MATCH(\"WINTER\", INDIRECT(ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q70&\"!$D$1:$D$55\"), 0), 1, 1, TRUE, $Q70)&\":$AQ\"&MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q70&\"!$D$1:$D$55\"), 0)), 0)-1, 1, TRUE), \"\"))","v":"COOM!$K$25:$W$25"},{"$f":"IF(ISERROR(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q70&\"!$e$1:$e$55\"), 0))=FALSE, ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q70&\"!$e$1:$e$55\"), 0)+1, MATCH(\"WINTER\", INDIRECT(ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q70&\"!$e$1:$e$55\"), 0), 1, 1, TRUE, $Q70)&\":$AQ\"&MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q70&\"!$e$1:$e$55\"), 0)), 0), 1, TRUE, $Q70)&\":\"&ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q70&\"!$e$1:$e$55\"), 0)+1, 43, 1, TRUE),\nIF(ISERROR(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q70&\"!$D$1:$D$55\"), 0))=FALSE, ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q70&\"!$D$1:$D$55\"), 0)+1, MATCH(\"WINTER\", INDIRECT(ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q70&\"!$D$1:$D$55\"), 0), 1, 1, TRUE, $Q70)&\":$AQ\"&MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q70&\"!$D$1:$D$55\"), 0)), 0), 1, TRUE, $Q70)&\":\"&ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q70&\"!$D$1:$D$55\"), 0)+1, 43, 1, TRUE), \"\"))","v":"COOM!$X$25:$AQ$25"},"COOM!$K$26:$W$26","COOM!$X$26:$AQ$26"]
[null,"Craiglie (132/22kV)","Zone Substation",null,47.1,47.1,47.1,47.1,47.1,53.4,53.4,53.4,53.4,53.4,null,"Craiglie","CRAI","CRAI!$K$25:$W$25","CRAI!$X$25:$AQ$25","CRAI!$K$26:$W$26","CRAI!$X$26:$AQ$26"]
[null,"Cranbrook (66/11kV)","Zone Substation",null,55.6,55.6,55.6,55.6,55.6,57.9,57.9,57.9,57.9,57.9,null,"Cranbrook","CRAN","CRAN!$K$25:$W$25","CRAN!$X$25:$AQ$25","CRAN!$K$26:$W$26","CRAN!$X$26:$AQ$26"]
[null,"Crediton (66/11kV)","Zone Substation",null,1.1000000000000001,1.1000000000000001,1.1000000000000001,1.1000000000000001,1.1000000000000001,1.1000000000000001,1.1000000000000001,1.1000000000000001,1.1000000000000001,1.1000000000000001,null,"Crediton","CRED","CRED!$K$25:$W$25","CRED!$X$25:$AQ$25","CRED!$K$26:$W$26","CRED!$X$26:$AQ$26"]
[null,"Crows Nest (33/11kV)","Zone Substation",null,8.3000000000000007,8.3000000000000007,8.3000000000000007,8.3000000000000007,8.3000000000000007,9.4,9.4,9.4,9.4,9.4,null,"Crows Nest","CRNE","CRNE!$K$25:$W$25","CRNE!$X$25:$AQ$25","CRNE!$K$26:$W$26","CRNE!$X$26:$AQ$26"]
[null,"Croydon (66/22kV)","Zone Substation",null,5.0999999999999996,5.0999999999999996,5.0999999999999996,5.0999999999999996,5.0999999999999996,5.4,5.4,5.4,5.4,5.4,null,"Croydon","CROY","CROY!$K$25:$W$25","CROY!$X$25:$AQ$25","CROY!$K$26:$W$26","CROY!$X$26:$AQ$26"]
[null,"Cunnamulla (66/22kV)","Zone Substation",null,11.3,11.3,11.3,11.3,11.3,13.9,13.9,13.9,13.9,13.9,null,"Cunnamulla","CUNN","CUNN!$K$25:$W$25","CUNN!$X$25:$AQ$25","CUNN!$K$26:$W$26","CUNN!$X$26:$AQ$26"]
[null,"Daandine BSP (110/33kV)","Bulk Supply",null,37.299999999999997,37.299999999999997,37.299999999999997,37.299999999999997,37.299999999999997,40.5,40.5,40.5,40.5,40.5,null,"Daandine BSP","T188","'T188'!$J$23:$V$23","'T188'!$W$23:$AQ$23","'T188'!$J$24:$V$24","'T188'!$W$24:$AQ$24"]
[null,"Dalby Central (33/11kV)","Zone Substation",null,{"$f":"IF(AND($R78<>\"\", $T78<>\"\", $E$2<>\"\", $E$2<>\"-\"), IF(INDEX(INDIRECT($T78), MATCH(E$5, INDIRECT($R78), 0))<>\"\", IF(ISNUMBER(INDEX(INDIRECT($T78), MATCH(E$5, INDIRECT($R78), 0))), ROUND(INDEX(INDIRECT($T78), MATCH(E$5, INDIRECT($R78), 0)), 1), IF($E$2=\"Meets Security Standard\", PROPER(INDEX(INDIRECT($T78), MATCH(E$5, INDIRECT($R78), 0))), INDEX(INDIRECT($T78), MATCH(E$5, INDIRECT($R78), 0)))), \"\"), \"\")","v":47.6},47.6,47.6,47.6,47.6,{"$f":"IF(AND($S78<>\"\", $U78<>\"\", $E$2<>\"\", $E$2<>\"-\"), IF(INDEX(INDIRECT($U78), MATCH(TEXT(J$5, \"????\"), INDIRECT($S78), 0))<>\"\", IF(INDEX(INDIRECT($U78), MATCH(TEXT(J$5, \"????\"), INDIRECT($S78), 0))<>\"\", IF(ISNUMBER(INDEX(INDIRECT($U78), MATCH(TEXT(J$5, \"????\"), INDIRECT($S78), 0))), ROUND(INDEX(INDIRECT($U78), MATCH(TEXT(J$5, \"????\"), INDIRECT($S78), 0)), 1), IF($E$2=\"Meets Security Standard\", PROPER(INDEX(INDIRECT($U78), MATCH(TEXT(J$5, \"????\"), INDIRECT($S78), 0))), INDEX(INDIRECT($U78), MATCH(TEXT(J$5, \"????\"), INDIRECT($S78), 0)))), \"\"), \"\"), \"\")","v":50.9},50.9,50.9,50.9,50.9,null,"Dalby Central","DACE","DACE!$K$25:$W$25","DACE!$X$25:$AQ$25","DACE!$K$26:$W$26","DACE!$X$26:$AQ$26"]
[null,"Dalby East BSP (110/33kV)","Bulk Supply",null,130.30000000000001,130.30000000000001,130.30000000000001,130.30000000000001,130.30000000000001,149.69999999999999,149.69999999999999,149.69999999999999,149.69999999999999,149.69999999999999,null,"Dalby East BSP","T002","'T002'!$J$23:$V$23","'T002'!$W$23:$AQ$23","'T002'!$J$24:$V$24","'T002'!$W$24:$AQ$24"]
[null,"Dan Gleeson (66/11kV)","Zone Substation",null,42.6,42.6,42.6,42.6,42.6,39.799999999999997,39.799999999999997,39.799999999999997,39.799999999999997,39.799999999999997,null,"Dan Gleeson","DAGL","DAGL!$K$25:$W$25","DAGL!$X$25:$AQ$25","DAGL!$K$26:$W$26","DAGL!$X$26:$AQ$26"]
[null,"Degilbo (66/11kV)","Zone Substation",null,5.0999999999999996,5.0999999999999996,5.0999999999999996,5.0999999999999996,5.0999999999999996,5.9,5.9,5.9,5.9,5.9,null,"Degilbo","DEGI","DEGI!$K$25:$W$25","DEGI!$X$25:$AQ$25","DEGI!$K$26:$W$26","DEGI!$X$26:$AQ$26"]
[null,"Dimbulah (66/22kV)","Zone Substation",null,24.2,24.2,24.2,24.2,24.2,25.9,25.9,25.9,25.9,25.9,null,"Dimbulah","DIMB","DIMB!$K$25:$W$25","DIMB!$X$25:$AQ$25","DIMB!$K$26:$W$26","DIMB!$X$26:$AQ$26"]
[null,"Duchess Road (132/66kV)","Zone Substation",null,129.30000000000001,129.30000000000001,129.30000000000001,129.30000000000001,129.30000000000001,151,151,151,151,151,null,"Duchess Road","DURO","DURO!$K$25:$W$25","DURO!$X$25:$AQ$25","DURO!$K$26:$W$26","DURO!$X$26:$AQ$26"]
[null,"Dysart (66/22kV)","Zone Substation",null,44,44,44,44,44,20,44,44,44,44,null,"Dysart","DYSA","DYSA!$K$25:$W$25","DYSA!$X$25:$AQ$25","DYSA!$K$26:$W$26","DYSA!$X$26:$AQ$26"]
[null,"East Ayr (66/11kV)","Zone Substation",null,64.900000000000006,64.900000000000006,64.900000000000006,64.900000000000006,64.900000000000006,69.900000000000006,69.900000000000006,69.900000000000006,69.900000000000006,69.900000000000006,null,"East Ayr","EAAY","EAAY!$K$25:$W$25","EAAY!$X$25:$AQ$25","EAAY!$K$26:$W$26","EAAY!$X$26:$AQ$26"]
[null,"East Bundaberg (66/11kV)","Zone Substation",null,34.700000000000003,34.700000000000003,34.700000000000003,34.700000000000003,34.700000000000003,40.799999999999997,40.799999999999997,40.799999999999997,40.799999999999997,40.799999999999997,null,"East Bundaberg","EABU","EABU!$K$25:$W$25","EABU!$X$25:$AQ$25","EABU!$K$26:$W$26","EABU!$X$26:$AQ$26"]
[null,"East Toowoomba (33/11kV)","Zone Substation",null,56.3,56.3,56.3,56.3,56.3,66.099999999999994,66.099999999999994,66.099999999999994,66.099999999999994,66.099999999999994,null,"East Toowoomba","EATO","EATO!$K$25:$W$25","EATO!$X$25:$AQ$25","EATO!$K$26:$W$26","EATO!$X$26:$AQ$26"]
[null,"Edmonton (132/22kV)","Zone Substation",null,75,75,75,75,75,75,75,75,75,75,null,"Edmonton","EDMO","EDMO!$K$25:$W$25","EDMO!$X$25:$AQ$25","EDMO!$K$26:$W$26","EDMO!$X$26:$AQ$26"]
[null,"Eidsvold (66/11kV)","Zone Substation",null,4.5,4.5,4.5,4.5,4.5,5.3,5.3,5.3,5.3,5.3,null,"Eidsvold","EIDS","EIDS!$K$25:$W$25","EIDS!$X$25:$AQ$25","EIDS!$K$26:$W$26","EIDS!$X$26:$AQ$26"]
[null,"Ellwoods Road (66/11kV)","Zone Substation",null,5,5,5,5,5,6.1,6.1,6.1,6.1,6.1,null,"Ellwoods Road","ELRO","ELRO!$K$25:$W$25","ELRO!$X$25:$AQ$25","ELRO!$K$26:$W$26","ELRO!$X$26:$AQ$26"]
[null,"Emerald (66/22kV)","Zone Substation",null,69.599999999999994,69.599999999999994,69.599999999999994,69.599999999999994,69.599999999999994,81.099999999999994,81.099999999999994,81.099999999999994,81.099999999999994,81.099999999999994,null,"Emerald","EMER","EMER!$K$25:$W$25","EMER!$X$25:$AQ$25","EMER!$K$26:$W$26","EMER!$X$26:$AQ$26"]
[null,"Eton (33/11kV)","Zone Substation",null,14.1,14.1,14.1,14.1,14.1,15,15,15,15,15,null,"Eton","ETON","ETON!$K$25:$W$25","ETON!$X$25:$AQ$25","ETON!$K$26:$W$26","ETON!$X$26:$AQ$26"]
[null,"Eungella Dam (66/11kV)","Zone Substation",null,6.6,6.6,6.6,6.6,6.6,6.6,6.6,6.6,6.6,6.6,null,"Eungella Dam","EUDA","EUDA!$K$25:$W$25","EUDA!$X$25:$AQ$25","EUDA!$K$26:$W$26","EUDA!$X$26:$AQ$26"]
[null,"Evelyn (66/22kV)","Zone Substation",null,6.3,6.3,6.3,6.3,6.3,6.3,6.3,6.3,6.3,6.3,null,"Evelyn","EVEL","EVEL!$K$25:$W$25","EVEL!$X$25:$AQ$25","EVEL!$K$26:$W$26","EVEL!$X$26:$AQ$26"]
[null,"Farleigh (33/11kV)","Zone Substation",null,16.5,16.5,16.5,16.5,16.5,18,18,18,18,18,null,"Farleigh","FARL","FARL!$K$25:$W$25","FARL!$X$25:$AQ$25","FARL!$K$26:$W$26","FARL!$X$26:$AQ$26"]
[null,"Farnsfield (66/11kV)","Zone Substation",null,28.9,28.9,28.9,28.9,28.9,37.4,37.4,37.4,37.4,37.4,null,"Farnsfield","FARN","FARN!$K$25:$W$25","FARN!$X$25:$AQ$25","FARN!$K$26:$W$26","FARN!$X$26:$AQ$26"]
[null,"Frenchville (66/11kV)","Zone Substation",null,48,48,48,48,48,48,48,48,48,48,null,"Frenchville","FREN","FREN!$K$25:$W$25","FREN!$X$25:$AQ$25","FREN!$K$26:$W$26","FREN!$X$26:$AQ$26"]
[null,"Friend Street (66/11kV)","Zone Substation",null,47.4,47.4,47.4,47.4,47.4,53.3,53.3,53.3,53.3,53.3,null,"Friend Street","GLFS","GLFS!$K$25:$W$25","GLFS!$X$25:$AQ$25","GLFS!$K$26:$W$26","GLFS!$X$26:$AQ$26"]
[null,"Garbutt (66/11kV)","Zone Substation",null,53.8,53.8,53.8,53.8,53.8,54,54,54,54,54,null,"Garbutt","GARB","GARB!$K$25:$W$25","GARB!$X$25:$AQ$25","GARB!$K$26:$W$26","GARB!$X$26:$AQ$26"]
[null,"Gayndah (66/11kV)","Zone Substation",null,24.6,24.6,24.6,24.6,24.6,27.1,27.1,27.1,27.1,27.1,null,"Gayndah","GAYN","GAYN!$K$25:$W$25","GAYN!$X$25:$AQ$25","GAYN!$K$26:$W$26","GAYN!$X$26:$AQ$26"]
[null,"Georgetown (66/22kV)","Zone Substation",null,5.5,5.5,5.5,5.5,5.5,6,6,6,6,6,null,"Georgetown","GEOR","GEOR!$K$25:$W$25","GEOR!$X$25:$AQ$25","GEOR!$K$26:$W$26","GEOR!$X$26:$AQ$26"]
[null,"Georgetown BSP (132/66kV)","Bulk Supply",null,16.7,16.7,16.7,16.7,16.7,18,18,18,18,18,null,"Georgetown ","GEOR1","GEOR1!$J$23:$V$23","GEOR1!$W$23:$AQ$23","GEOR1!$J$24:$V$24","GEOR1!$W$24:$AQ$24"]
[null,"Giru (66/11kV)","Zone Substation",null,9.5,9.5,9.5,9.5,9.5,10.5,10.5,10.5,10.5,10.5,null,"Giru","GIRU","GIRU!$K$25:$W$25","GIRU!$X$25:$AQ$25","GIRU!$K$26:$W$26","GIRU!$X$26:$AQ$26"]
[null,"Givelda (66/11kV)","Zone Substation",null,24.4,24.4,24.4,24.4,24.4,29.6,29.6,29.6,29.6,29.6,null,"Givelda","GIVE","GIVE!$K$25:$W$25","GIVE!$X$25:$AQ$25","GIVE!$K$26:$W$26","GIVE!$X$26:$AQ$26"]
[null,"Gladstone North BSP (132/66kV)","Bulk Supply",null,184,184,184,184,184,208.8,208.8,208.8,208.8,208.8,null,"Gladstone North ","T074","'T074'!$J$23:$V$23","'T074'!$W$23:$AQ$23","'T074'!$J$24:$V$24","'T074'!$W$24:$AQ$24"]
[null,"Gladstone South (66/11kV)","Zone Substation",null,54.7,54.7,54.7,54.7,54.7,59.8,59.8,59.8,59.8,59.8,null,"Gladstone South","GLSO","GLSO!$K$25:$W$25","GLSO!$X$25:$AQ$25","GLSO!$K$26:$W$26","GLSO!$X$26:$AQ$26"]
[null,"Glenden (66/11kV)","Zone Substation",null,15,15,15,15,15,16.7,16.7,16.7,16.7,16.7,null,"Glenden","GLEN","GLEN!$K$25:$W$25","GLEN!$X$25:$AQ$25","GLEN!$K$26:$W$26","GLEN!$X$26:$AQ$26"]
[null,"Glenelg (66/33kV)","Zone Substation",null,0.6,0.6,0.6,0.6,0.6,0.6,0.6,0.6,0.6,0.6,null,"Glenelg","GLEE","GLEE!$K$25:$W$25","GLEE!$X$25:$AQ$25","GLEE!$K$26:$W$26","GLEE!$X$26:$AQ$26"]
[null,"Glenella 11kV (66/11kV)","Zone Substation",null,75.2,75.2,75.2,75.2,75.2,83.8,83.8,83.8,83.8,83.8,null,"Glenella 11kV","GLEL","GLEL!$K$25:$W$25","GLEL!$X$25:$AQ$25","GLEL!$K$26:$W$26","GLEL!$X$26:$AQ$26"]
[null,"Gooburrum (66/11kV)","Zone Substation",null,14.3,14.3,14.3,14.3,14.3,15,15,15,15,15,null,"Gooburrum","GOOB","GOOB!$K$25:$W$25","GOOB!$X$25:$AQ$25","GOOB!$K$26:$W$26","GOOB!$X$26:$AQ$26"]
[null,"Gootchie (66/11kV)","Zone Substation",null,5,5,5,5,5,5.8,5.8,5.8,5.8,5.8,null,"Gootchie","GOOT","GOOT!$K$25:$W$25","GOOT!$X$25:$AQ$25","GOOT!$K$26:$W$26","GOOT!$X$26:$AQ$26"]
[null,"Gracemere (66/11kV)","Zone Substation",null,"","",11,11,11,"","",11,11,11,null,"Gracemere","Gracem","Gracem!$K$22:$T$22","Gracem!$U$22:$AQ$22","Gracem!$K$23:$T$23","Gracem!$U$23:$AQ$23"]
[null,"Granite Creek (66/22kV)","Zone Substation",null,3.8,3.8,3.8,3.8,3.8,3.8,3.8,3.8,3.8,3.8,null,"Granite Creek","GRCR","GRCR!$K$25:$W$25","GRCR!$X$25:$AQ$25","GRCR!$K$26:$W$26","GRCR!$X$26:$AQ$26"]
[null,"Granite Creek BSP (132/66kV)","Bulk Supply",null,32,32,32,32,32,32,32,32,32,32,null,"Granite Creek ","T166","'T166'!$J$23:$V$23","'T166'!$W$23:$AQ$23","'T166'!$J$24:$V$24","'T166'!$W$24:$AQ$24"]
[null,"Greenvale (66/11kV)","Zone Substation",null,0.7,0.7,0.7,0.7,0.7,0.7,0.7,0.7,0.7,0.7,null,"Greenvale","GREN","GREN!$K$25:$W$25","GREN!$X$25:$AQ$25","GREN!$K$26:$W$26","GREN!$X$26:$AQ$26"]
[null,"Gumlu (66/11kV)","Zone Substation",null,1.7,1.7,1.7,1.7,1.7,1.7,1.7,1.7,1.7,1.7,null,"Gumlu","GUML","GUML!$K$25:$W$25","GUML!$X$25:$AQ$25","GUML!$K$26:$W$26","GUML!$X$26:$AQ$26"]
[null,"Guthalungra (66/11kV)","Zone Substation",null,0.6,0.6,0.6,0.6,0.6,0.6,0.6,0.6,0.6,0.6,null,"Guthalungra","GUTH","GUTH!$K$25:$W$25","GUTH!$X$25:$AQ$25","GUTH!$K$26:$W$26","GUTH!$X$26:$AQ$26"]
[null,"Haughton (66/11kV)","Zone Substation",null,6.2,6.2,6.2,6.2,6.2,6.7,6.7,6.7,6.7,6.7,null,"Haughton","HAPU","HAPU!$K$25:$W$25","HAPU!$X$25:$AQ$25","HAPU!$K$26:$W$26","HAPU!$X$26:$AQ$26"]
[null,"Helenvale (66/22kV)","Zone Substation",null,5.7,5.7,5.7,5.7,5.7,6.3,6.3,6.3,6.3,6.3,null,"Helenvale","HELE","HELE!$K$25:$W$25","HELE!$X$25:$AQ$25","HELE!$K$26:$W$26","HELE!$X$26:$AQ$26"]
[null,"Hermit Park (66/11kV)","Zone Substation",null,56.6,56.6,56.6,56.6,56.6,58.6,58.6,58.6,58.6,58.6,null,"Hermit Park","HEPA","HEPA!$K$25:$W$25","HEPA!$X$25:$AQ$25","HEPA!$K$26:$W$26","HEPA!$X$26:$AQ$26"]
[null,"Highfields (33/11kV)","Zone Substation",null,5.5,5.5,5.5,5.5,5.5,5.5,5.5,5.5,5.5,5.5,null,"Highfields","HIGH","HIGH!$K$25:$W$25","HIGH!$X$25:$AQ$25","HIGH!$K$26:$W$26","HIGH!$X$26:$AQ$26"]
[null,"Hillsborough (66/11kV)","Zone Substation",null,0.1,0.1,0.1,0.1,0.1,0.1,0.1,0.1,0.1,0.1,null,"Hillsborough","HILL","HILL!$K$25:$W$25","HILL!$X$25:$AQ$25","HILL!$K$26:$W$26","HILL!$X$26:$AQ$26"]
[null,"Home Hill (66/11kV)","Zone Substation",null,59.3,59.3,59.3,59.3,59.3,65.099999999999994,65.099999999999994,65.099999999999994,65.099999999999994,65.099999999999994,null,"Home Hill","HOHI","HOHI!$K$25:$W$25","HOHI!$X$25:$AQ$25","HOHI!$K$26:$W$26","HOHI!$X$26:$AQ$26"]
[null,"Howard (66/11kV)","Zone Substation",null,16.100000000000001,16.100000000000001,16.100000000000001,16.100000000000001,16.100000000000001,16.100000000000001,16.100000000000001,16.100000000000001,16.100000000000001,16.100000000000001,null,"Howard","HOWA","HOWA!$K$25:$W$25","HOWA!$X$25:$AQ$25","HOWA!$K$26:$W$26","HOWA!$X$26:$AQ$26"]
[null,"Hughenden (66/33kV)","Zone Substation",null,20,20,20,20,20,22.9,22.9,22.9,22.9,22.9,null,"Hughenden","HUGH","HUGH!$K$25:$W$25","HUGH!$X$25:$AQ$25","HUGH!$K$26:$W$26","HUGH!$X$26:$AQ$26"]
[null,"Ilbilbie (33/11kV)","Zone Substation",null,1.2,1.2,1.2,1.2,1.2,1.4,1.4,1.4,1.4,1.4,null,"Ilbilbie","ILBI","ILBI!$K$25:$W$25","ILBI!$X$25:$AQ$25","ILBI!$K$26:$W$26","ILBI!$X$26:$AQ$26"]
[null,"Ingham (66/11kV)","Zone Substation",null,26.7,26.7,26.7,26.7,26.7,28.1,28.1,28.1,28.1,28.1,null,"Ingham","INGH","INGH!$K$25:$W$25","INGH!$X$25:$AQ$25","INGH!$K$26:$W$26","INGH!$X$26:$AQ$26"]
[null,"Isis BSP (132/66kV)","Bulk Supply",null,134,134,134,134,134,145,145,145,145,145,null,"Isis ","T131","'T131'!$J$23:$V$23","'T131'!$W$23:$AQ$23","'T131'!$J$24:$V$24","'T131'!$W$24:$AQ$24"]
[null,"Jandowae (33/11kV)","Zone Substation",null,{"$f":"IF(AND($R129<>\"\", $T129<>\"\", $E$2<>\"\", $E$2<>\"-\"), IF(INDEX(INDIRECT($T129), MATCH(E$5, INDIRECT($R129), 0))<>\"\", IF(ISNUMBER(INDEX(INDIRECT($T129), MATCH(E$5, INDIRECT($R129), 0))), ROUND(INDEX(INDIRECT($T129), MATCH(E$5, INDIRECT($R129), 0)), 1), IF($E$2=\"Meets Security Standard\", PROPER(INDEX(INDIRECT($T129), MATCH(E$5, INDIRECT($R129), 0))), INDEX(INDIRECT($T129), MATCH(E$5, INDIRECT($R129), 0)))), \"\"), \"\")","v":3.2},3.2,3.2,3.2,3.2,{"$f":"IF(AND($S129<>\"\", $U129<>\"\", $E$2<>\"\", $E$2<>\"-\"), IF(INDEX(INDIRECT($U129), MATCH(TEXT(J$5, \"????\"), INDIRECT($S129), 0))<>\"\", IF(INDEX(INDIRECT($U129), MATCH(TEXT(J$5, \"????\"), INDIRECT($S129), 0))<>\"\", IF(ISNUMBER(INDEX(INDIRECT($U129), MATCH(TEXT(J$5, \"????\"), INDIRECT($S129), 0))), ROUND(INDEX(INDIRECT($U129), MATCH(TEXT(J$5, \"????\"), INDIRECT($S129), 0)), 1), IF($E$2=\"Meets Security Standard\", PROPER(INDEX(INDIRECT($U129), MATCH(TEXT(J$5, \"????\"), INDIRECT($S129), 0))), INDEX(INDIRECT($U129), MATCH(TEXT(J$5, \"????\"), INDIRECT($S129), 0)))), \"\"), \"\"), \"\")","v":3.2},3.2,3.2,3.2,3.2,null,"Jandowae","JAND","JAND!$K$25:$W$25","JAND!$X$25:$AQ$25","JAND!$K$26:$W$26","JAND!$X$26:$AQ$26"]
[null,"Jarvisfield (66/11kV)","Zone Substation",null,12.1,12.1,12.1,12.1,12.1,12.4,12.4,12.4,12.4,12.4,null,"Jarvisfield","JARV","JARV!$K$25:$W$25","JARV!$X$25:$AQ$25","JARV!$K$26:$W$26","JARV!$X$26:$AQ$26"]
[null,"Jubilee Pocket (66/11kV)","Zone Substation",null,39.6,39.6,39.6,39.6,39.6,43.4,43.4,43.4,43.4,43.4,null,"Jubilee Pocket","JUPO","JUPO!$K$25:$W$25","JUPO!$X$25:$AQ$25","JUPO!$K$26:$W$26","JUPO!$X$26:$AQ$26"]
[null,"Julia Creek (66/33kV)","Zone Substation",null,7.4,7.4,7.4,7.4,7.4,8.8000000000000007,8.8000000000000007,8.8000000000000007,8.8000000000000007,8.8000000000000007,null,"Julia Creek","JUCR","JUCR!$K$25:$W$25","JUCR!$X$25:$AQ$25","JUCR!$K$26:$W$26","JUCR!$X$26:$AQ$26"]
[null,"Kaimkillenbun (33/11kV)","Zone Substation",null,1,1,1,1,1,1,1,1,1,1,null,"Kaimkillenbun","KAIM","KAIM!$K$25:$W$25","KAIM!$X$25:$AQ$25",{"$f":"IF(ISERROR(MATCH($E$2, INDIRECT($Q133&\"!$E$1:$E$55\"), 0))=FALSE, ADDRESS(MATCH($E$2, INDIRECT($Q133&\"!$E$1:$E$55\"), 0), MATCH(\"SUMMER\", INDIRECT(ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q133&\"!$E$1:$E$55\"), 0), 1, 1, TRUE, $Q133)&\":$AQ\"&MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q133&\"!$E$1:$E$55\"), 0)), 0), 1, TRUE, $Q133)&\":\"&\nADDRESS(MATCH($E$2, INDIRECT($Q133&\"!$E$1:$E$55\"), 0), MATCH(\"WINTER\", INDIRECT(ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q133&\"!$E$1:$E$55\"), 0), 1, 1, TRUE, $Q133)&\":$AQ\"&MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q133&\"!$E$1:$E$55\"), 0)), 0)-1, 1, TRUE),\nIF(ISERROR(MATCH($E$2, INDIRECT($Q133&\"!$d$1:$d$55\"), 0))=FALSE, ADDRESS(MATCH($E$2, INDIRECT($Q133&\"!$d$1:$d$55\"), 0), MATCH(\"SUMMER\", INDIRECT(ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q133&\"!$d$1:$d$55\"), 0), 1, 1, TRUE, $Q133)&\":$AQ\"&MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q133&\"!$d$1:$d$55\"), 0)), 0), 1, TRUE, $Q133)&\":\"&\nADDRESS(MATCH($E$2, INDIRECT($Q133&\"!$d$1:$d$55\"), 0), MATCH(\"WINTER\", INDIRECT(ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q133&\"!$d$1:$d$55\"), 0), 1, 1, TRUE, $Q133)&\":$AQ\"&MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q133&\"!$d$1:$d$55\"), 0)), 0)-1, 1, TRUE), \"\"))","v":"KAIM!$K$26:$W$26"},{"$f":"IF(ISERROR(MATCH($E$2, INDIRECT($Q133&\"!$E$1:$E$55\"), 0))=FALSE, ADDRESS(MATCH($E$2, INDIRECT($Q133&\"!$E$1:$E$55\"), 0), MATCH(\"WINTER\", INDIRECT(ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q133&\"!$E$1:$E$55\"), 0), 1, 1, TRUE, $Q133)&\":$AQ\"&MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q133&\"!$E$1:$E$55\"), 0)), 0), 1, TRUE, $Q133)&\":\"&\nADDRESS(MATCH($E$2, INDIRECT($Q133&\"!$E$1:$E$55\"), 0), 43, 1, TRUE),\nIF(ISERROR(MATCH($E$2, INDIRECT($Q133&\"!$d$1:$d$55\"), 0))=FALSE, ADDRESS(MATCH($E$2, INDIRECT($Q133&\"!$d$1:$d$55\"), 0), MATCH(\"WINTER\", INDIRECT(ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q133&\"!$d$1:$d$55\"), 0), 1, 1, TRUE, $Q133)&\":$AQ\"&MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q133&\"!$d$1:$d$55\"), 0)), 0), 1, TRUE, $Q133)&\":\"&\nADDRESS(MATCH($E$2, INDIRECT($Q133&\"!$d$1:$d$55\"), 0), 43, 1, TRUE), \"\"))","v":"KAIM!$X$26:$AQ$26"}]
[null,"Kalamia (66/11kV)","Zone Substation",null,13,13,13,13,13,14.2,14.2,14.2,14.2,14.2,null,"Kalamia","KALA",{"$f":"IF(ISERROR(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q134&\"!$e$1:$e$55\"), 0))=FALSE, ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q134&\"!$e$1:$e$55\"), 0)+1, MATCH(\"SUMMER\", INDIRECT(ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q134&\"!$e$1:$e$55\"), 0), 1, 1, TRUE, $Q134)&\":$AQ\"&MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q134&\"!$e$1:$e$55\"), 0)), 0), 1, TRUE, $Q134)&\":\"&ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q134&\"!$e$1:$e$55\"), 0)+1, MATCH(\"WINTER\", INDIRECT(ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q134&\"!$e$1:$e$55\"), 0), 1, 1, TRUE, $Q134)&\":$AQ\"&MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q134&\"!$e$1:$e$55\"), 0)), 0)-1, 1, TRUE),\nIF(ISERROR(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q134&\"!$D$1:$D$55\"), 0))=FALSE, ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q134&\"!$D$1:$D$55\"), 0)+1, MATCH(\"SUMMER\", INDIRECT(ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q134&\"!$D$1:$D$55\"), 0), 1, 1, TRUE, $Q134)&\":$AQ\"&MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q134&\"!$D$1:$D$55\"), 0)), 0), 1, TRUE, $Q134)&\":\"&ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q134&\"!$D$1:$D$55\"), 0)+1, MATCH(\"WINTER\", INDIRECT(ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q134&\"!$D$1:$D$55\"), 0), 1, 1, TRUE, $Q134)&\":$AQ\"&MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q134&\"!$D$1:$D$55\"), 0)), 0)-1, 1, TRUE), \"\"))","v":"KALA!$K$25:$W$25"},{"$f":"IF(ISERROR(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q134&\"!$e$1:$e$55\"), 0))=FALSE, ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q134&\"!$e$1:$e$55\"), 0)+1, MATCH(\"WINTER\", INDIRECT(ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q134&\"!$e$1:$e$55\"), 0), 1, 1, TRUE, $Q134)&\":$AQ\"&MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q134&\"!$e$1:$e$55\"), 0)), 0), 1, TRUE, $Q134)&\":\"&ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q134&\"!$e$1:$e$55\"), 0)+1, 43, 1, TRUE),\nIF(ISERROR(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q134&\"!$D$1:$D$55\"), 0))=FALSE, ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q134&\"!$D$1:$D$55\"), 0)+1, MATCH(\"WINTER\", INDIRECT(ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q134&\"!$D$1:$D$55\"), 0), 1, 1, TRUE, $Q134)&\":$AQ\"&MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q134&\"!$D$1:$D$55\"), 0)), 0), 1, TRUE, $Q134)&\":\"&ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q134&\"!$D$1:$D$55\"), 0)+1, 43, 1, TRUE), \"\"))","v":"KALA!$X$25:$AQ$25"},"KALA!$K$26:$W$26","KALA!$X$26:$AQ$26"]
[null,"Kearneys Spring (110/11kV)","Zone Substation",null,79.099999999999994,79.099999999999994,79.099999999999994,79.099999999999994,79.099999999999994,89.8,89.8,89.8,89.8,89.8,null,"Kearneys Spring","KESP","KESP!$K$25:$W$25","KESP!$X$25:$AQ$25","KESP!$K$26:$W$26","KESP!$X$26:$AQ$26"]
[null,"Kelsey Creek East (66/11kV)","Zone Substation",null,36.799999999999997,36.799999999999997,36.799999999999997,36.799999999999997,36.799999999999997,38.4,38.4,38.4,38.4,38.4,null,"Kelsey Creek East","KECE","KECE!$K$25:$W$25","KECE!$X$25:$AQ$25","KECE!$K$26:$W$26","KECE!$X$26:$AQ$26"]
[null,"Kidston (132/6.6kV)","Zone Substation",null,42.5,42.5,42.5,42.5,42.5,44.9,44.9,44.9,44.9,44.9,null,"Kidston","KIDS","KIDS!$K$25:$W$25","KIDS!$X$25:$AQ$25","KIDS!$K$26:$W$26","KIDS!$X$26:$AQ$26"]
[null,"Kilkivan BSP (132/66kV)","Bulk Supply",null,34,34,34,34,34,34,34,34,34,34,null,"Kilkivan ","T012","'T012'!$J$23:$V$23","'T012'!$W$23:$AQ$23","'T012'!$J$24:$V$24","'T012'!$W$24:$AQ$24"]
[null,"Kilkivan Town (66/11kV)","Zone Substation",null,2,2,2,2,2,2,2,2,2,2,null,"Kilkivan Town","KITO","KITO!$K$25:$W$25","KITO!$X$25:$AQ$25","KITO!$K$26:$W$26","KITO!$X$26:$AQ$26"]
[null,"Killarney (33/11kV)","Zone Substation",null,7.5,7.5,7.5,7.5,7.5,8.9,8.9,8.9,8.9,8.9,null,"Killarney","KILL","KILL!$K$25:$W$25","KILL!$X$25:$AQ$25","KILL!$K$26:$W$26","KILL!$X$26:$AQ$26"]
[null,"Kingaroy (66/11kV)","Zone Substation",null,57.4,57.4,57.4,57.4,57.4,64.7,64.7,64.7,64.7,64.7,null,"Kingaroy","KING","KING!$K$25:$W$25","KING!$X$25:$AQ$25","KING!$K$26:$W$26","KING!$X$26:$AQ$26"]
[null,"Kirknie (66/11kV)","Zone Substation",null,9.6999999999999993,9.6999999999999993,9.6999999999999993,9.6999999999999993,9.6999999999999993,10.9,10.9,10.9,10.9,10.9,null,"Kirknie","KIRK","KIRK!$K$25:$W$25","KIRK!$X$25:$AQ$25","KIRK!$K$26:$W$26","KIRK!$X$26:$AQ$26"]
[null,"Kogan Creek (33/11kV)","Zone Substation",null,5,5,5,5,5,5,5,5,5,5,null,"Kogan Creek","KOCR","KOCR!$K$25:$W$25","KOCR!$X$25:$AQ$25","KOCR!$K$26:$W$26","KOCR!$X$26:$AQ$26"]
[null,"Koumala (33/11kV)","Zone Substation",null,7,7,7,7,7,7.5,7.5,7.5,7.5,7.5,null,"Koumala","KOUM","KOUM!$K$25:$W$25","KOUM!$X$25:$AQ$25","KOUM!$K$26:$W$26","KOUM!$X$26:$AQ$26"]
[null,"Laguna Quays (66/11kV)","Zone Substation",null,17.600000000000001,17.600000000000001,17.600000000000001,17.600000000000001,17.600000000000001,19,19,19,19,19,null,"Laguna Quays","LAQU","LAQU!$K$25:$W$25","LAQU!$X$25:$AQ$25","LAQU!$K$26:$W$26","LAQU!$X$26:$AQ$26"]
[null,"Lakeland (66/22kV)","Zone Substation",null,16,16,16,16,16,16,16,16,16,16,null,"Lakeland","LAKE","LAKE!$K$25:$W$25","LAKE!$X$25:$AQ$25","LAKE!$K$26:$W$26","LAKE!$X$26:$AQ$26"]
[null,"Lakeland BSP (132/66kV)","Bulk Supply",null,49.8,49.8,49.8,49.8,49.8,55.8,55.8,55.8,55.8,55.8,null,"Lakeland ","T159","'T159'!$J$23:$V$23","'T159'!$W$23:$AQ$23","'T159'!$J$24:$V$24","'T159'!$W$24:$AQ$24"]
[null,"Lakes Creek (66/11kV)","Zone Substation",null,45.9,45.9,45.9,45.9,45.9,50.9,50.9,50.9,50.9,50.9,null,"Lakes Creek","LACR","LACR!$K$25:$W$25","LACR!$X$25:$AQ$25","LACR!$K$26:$W$26","LACR!$X$26:$AQ$26"]
[null,"Landing Road (66/11kV)","Zone Substation",null,10,10,10,10,10,10,10,10,10,10,null,"Landing Road","LARO","LARO!$K$25:$W$25","LARO!$X$25:$AQ$25","LARO!$K$26:$W$26","LARO!$X$26:$AQ$26"]
[null,"Lannercost (66/11kV)","Zone Substation",null,8.1999999999999993,8.1999999999999993,8.1999999999999993,8.1999999999999993,8.1999999999999993,8.6999999999999993,8.6999999999999993,8.6999999999999993,8.6999999999999993,8.6999999999999993,null,"Lannercost","LANN","LANN!$K$25:$W$25","LANN!$X$25:$AQ$25","LANN!$K$26:$W$26","LANN!$X$26:$AQ$26"]
[null,"Littlemore (66/11kV)","Zone Substation",null,2.2000000000000002,2.2000000000000002,2.2000000000000002,2.2000000000000002,2.2000000000000002,2.2000000000000002,2.2000000000000002,2.2000000000000002,2.2000000000000002,2.2000000000000002,null,"Littlemore","LITT","LITT!$K$25:$W$25","LITT!$X$25:$AQ$25","LITT!$K$26:$W$26","LITT!$X$26:$AQ$26"]
[null,"Longreach (66/22kV)","Zone Substation",null,24.4,24.4,24.4,24.4,24.4,28.6,28.6,28.6,28.6,28.6,null,"Longreach","LONG","LONG!$K$25:$W$25","LONG!$X$25:$AQ$25","LONG!$K$26:$W$26","LONG!$X$26:$AQ$26"]
[null,"Louisa Creek (33/11kV)","Zone Substation",null,7.4,7.4,7.4,7.4,7.4,7.8,7.8,7.8,7.8,7.8,null,"Louisa Creek","LOCR","LOCR!$K$25:$W$25","LOCR!$X$25:$AQ$25","LOCR!$K$26:$W$26","LOCR!$X$26:$AQ$26"]
[null,"Louisa Creek BSP (132/33kV)","Bulk Supply",null,175.8,175.8,175.8,175.8,175.8,185.2,185.2,185.2,185.2,185.2,null,"Louisa Creek ","T176","'T176'!$J$23:$V$23","'T176'!$W$23:$AQ$23","'T176'!$J$24:$V$24","'T176'!$W$24:$AQ$24"]
[null,"Lucinda (66/11kV)","Zone Substation",null,5.9,5.9,5.9,5.9,5.9,6,6,6,6,6,null,"Lucinda","LUCI","LUCI!$K$25:$W$25","LUCI!$X$25:$AQ$25","LUCI!$K$26:$W$26","LUCI!$X$26:$AQ$26"]
[null,"Lyndley Lane (33/22kV)","Zone Substation",null,1.1000000000000001,1.1000000000000001,1.1000000000000001,1.1000000000000001,1.1000000000000001,1.1000000000000001,1.1000000000000001,1.1000000000000001,1.1000000000000001,1.1000000000000001,null,"Lyndley Lane","LYLA","LYLA!$K$25:$W$25","LYLA!$X$25:$AQ$25","LYLA!$K$26:$W$26","LYLA!$X$26:$AQ$26"]
[null,"Macknade (66/11kV)","Zone Substation",null,13.9,13.9,13.9,13.9,13.9,13.9,13.9,13.9,13.9,13.9,null,"Macknade","MACN","MACN!$K$25:$W$25","MACN!$X$25:$AQ$25","MACN!$K$26:$W$26","MACN!$X$26:$AQ$26"]
[null,"Malchi (66/11kV)","Zone Substation",null,23.8,23.8,23.8,23.8,23.8,28.7,28.7,28.7,28.7,28.7,null,"Malchi","MALC","MALC!$L$25:$W$25","MALC!$X$25:$AQ$25","MALC!$L$26:$W$26","MALC!$X$26:$AQ$26"]
[null,"Mareeba (66/22kV)","Zone Substation",null,54.8,54.8,54.8,54.8,54.8,57.5,57.5,57.5,57.5,57.5,null,"Mareeba","MARE","MARE!$K$25:$W$25","MARE!$X$25:$AQ$25","MARE!$K$26:$W$26","MARE!$X$26:$AQ$26"]
[null,"Marian South (66/11kV)","Zone Substation",null,15,15,15,15,15,15,15,15,15,15,null,"Marian South","MASO","MASO!$K$25:$W$25","MASO!$X$25:$AQ$25","MASO!$K$26:$W$26","MASO!$X$26:$AQ$26"]
[null,"Maryborough BSP (132/66kV)","Bulk Supply",null,356.1,356.1,356.1,356.1,356.1,403.7,403.7,403.7,403.7,403.7,null,"Maryborough ","T059","'T059'!$J$23:$V$23","'T059'!$W$23:$AQ$23","'T059'!$J$24:$V$24","'T059'!$W$24:$AQ$24"]
[null,"Maryborough City (66/11kV)","Zone Substation",null,39.6,39.6,39.6,39.6,39.6,42.7,42.7,42.7,42.7,42.7,null,"Maryborough City","MACI","MACI!$K$25:$W$25","MACI!$X$25:$AQ$25","MACI!$K$26:$W$26","MACI!$X$26:$AQ$26"]
[null,"Max Fulton (66/11kV)","Zone Substation",null,76.3,76.3,76.3,76.3,76.3,77.7,77.7,77.7,77.7,77.7,null,"Max Fulton","MAFU","MAFU!$K$25:$W$25","MAFU!$X$25:$AQ$25","MAFU!$K$26:$W$26","MAFU!$X$26:$AQ$26"]
[null,"McKinley Creek (66/11kV)","Zone Substation",null,15.1,15.1,15.1,15.1,15.1,15.1,15.1,15.1,15.1,15.1,null,"McKinley Creek","MCCR","MCCR!$K$25:$W$25","MCCR!$X$25:$AQ$25","MCCR!$K$26:$W$26","MCCR!$X$26:$AQ$26"]
[null,"Meadowvale (66/11kV)","Zone Substation",null,14,14,14,14,14,15.2,15.2,15.2,15.2,15.2,null,"Meadowvale","MEAD","MEAD!$K$25:$W$25","MEAD!$X$25:$AQ$25","MEAD!$K$26:$W$26","MEAD!$X$26:$AQ$26"]
[null,"Meandarra (33/22kV)","Zone Substation",null,1,1,1,1,1,1.1000000000000001,1.1000000000000001,1.1000000000000001,1.1000000000000001,1.1000000000000001,null,"Meandarra","MEAN","MEAN!$K$25:$W$25","MEAN!$X$25:$AQ$25","MEAN!$K$26:$W$26","MEAN!$X$26:$AQ$26"]
[null,"Merinda (66/11kV)","Zone Substation",null,8.1,8.1,8.1,8.1,8.1,8.3000000000000007,8.3000000000000007,8.3000000000000007,8.3000000000000007,8.3000000000000007,null,"Merinda","MERI","MERI!$K$25:$W$25","MERI!$X$25:$AQ$25","MERI!$K$26:$W$26","MERI!$X$26:$AQ$26"]
[null,"Meringandan (33/11kV)","Zone Substation",null,16.899999999999999,16.899999999999999,16.899999999999999,16.899999999999999,16.899999999999999,18.5,18.5,18.5,18.5,18.5,null,"Meringandan","MERN","MERN!$K$25:$W$25","MERN!$X$25:$AQ$25","MERN!$K$26:$W$26","MERN!$X$26:$AQ$26"]
[null,"Middlemount (66/22kV)","Zone Substation",null,15.3,15.3,15.3,15.3,15.3,18.600000000000001,18.600000000000001,18.600000000000001,18.600000000000001,18.600000000000001,null,"Middlemount","MIDD","MIDD!$K$25:$W$25","MIDD!$X$25:$AQ$25","MIDD!$K$26:$W$26","MIDD!$X$26:$AQ$26"]
[null,"Miles (33/11kV)","Zone Substation",null,8.1,8.1,8.1,8.1,8.1,9.4,9.4,9.4,9.4,9.4,null,"Miles","MILE","MILE!$K$25:$W$25","MILE!$X$25:$AQ$25","MILE!$K$26:$W$26","MILE!$X$26:$AQ$26"]
[null,"Miles-Condamine (33/22kV)","Zone Substation",null,1.6,1.6,1.6,1.6,1.6,1.6,1.6,1.6,1.6,1.6,null,"Miles-Condamine","MICO","MICO!$K$25:$W$25","MICO!$X$25:$AQ$25","MICO!$K$26:$W$26","MICO!$X$26:$AQ$26"]
[null,"Millaroo (66/11kV)","Zone Substation",null,5.6,5.6,5.6,5.6,5.6,6.5,6.5,6.5,6.5,6.5,null,"Millaroo","MILL","MILL!$K$25:$W$25","MILL!$X$25:$AQ$25","MILL!$K$26:$W$26","MILL!$X$26:$AQ$26"]
[null,"Millchester (66/11kV)","Zone Substation",null,10.6,10.6,10.6,10.6,10.6,12.2,12.2,12.2,12.2,12.2,null,"Millchester","MILC","MILC!$K$25:$W$25","MILC!$X$25:$AQ$25","MILC!$K$26:$W$26","MILC!$X$26:$AQ$26"]
[null,"Millchester BSP (132/66kV)","Bulk Supply",null,68,68,68,68,68,68,68,68,68,68,null,"Millchester ","T095","'T095'!$J$23:$V$23","'T095'!$W$23:$AQ$23","'T095'!$J$24:$V$24","'T095'!$W$24:$AQ$24"]
[null,"Millmerran (33/11kV)","Zone Substation",null,7.6,7.6,7.6,7.6,7.6,8.5,8.5,8.5,8.5,8.5,null,"Millmerran","MILM","MILM!$K$25:$W$25","MILM!$X$25:$AQ$25","MILM!$K$26:$W$26","MILM!$X$26:$AQ$26"]
[null,"Mingela (66/11kV)","Zone Substation",null,0.3,0.3,0.3,0.3,0.3,0.3,0.3,0.3,0.3,0.3,null,"Mingela","MING","MING!$K$25:$W$25","MING!$X$25:$AQ$25","MING!$K$26:$W$26","MING!$X$26:$AQ$26"]
[null,"Mirani (66/11kV)","Zone Substation",null,6.1,6.1,6.1,6.1,6.1,7,7,7,7,7,null,"Mirani","MIRA","MIRA!$K$25:$W$25","MIRA!$X$25:$AQ$25","MIRA!$K$26:$W$26","MIRA!$X$26:$AQ$26"]
[null,"Miriam Vale (66/22kV)","Zone Substation",null,9.1,9.1,9.1,9.1,9.1,9.4,9.4,9.4,9.4,9.4,null,"Miriam Vale","MIVA","MIVA!$K$25:$W$25","MIVA!$X$25:$AQ$25","MIVA!$K$26:$W$26","MIVA!$X$26:$AQ$26"]
[null,"Mitchell (33/11kV)","Zone Substation",null,2.2999999999999998,2.2999999999999998,2.2999999999999998,2.2999999999999998,2.2999999999999998,2.2999999999999998,2.2999999999999998,2.2999999999999998,2.2999999999999998,2.2999999999999998,null,"Mitchell","MITC","MITC!$K$25:$W$25","MITC!$X$25:$AQ$25","MITC!$K$26:$W$26","MITC!$X$26:$AQ$26"]
[null,"Mona Park (66/11kV)","Zone Substation",null,{"$f":"IF(AND($R180<>\"\", $T180<>\"\", $E$2<>\"\", $E$2<>\"-\"), IF(INDEX(INDIRECT($T180), MATCH(E$5, INDIRECT($R180), 0))<>\"\", IF(ISNUMBER(INDEX(INDIRECT($T180), MATCH(E$5, INDIRECT($R180), 0))), ROUND(INDEX(INDIRECT($T180), MATCH(E$5, INDIRECT($R180), 0)), 1), IF($E$2=\"Meets Security Standard\", PROPER(INDEX(INDIRECT($T180), MATCH(E$5, INDIRECT($R180), 0))), INDEX(INDIRECT($T180), MATCH(E$5, INDIRECT($R180), 0)))), \"\"), \"\")","v":7.6},7.6,7.6,7.6,7.6,{"$f":"IF(AND($S180<>\"\", $U180<>\"\", $E$2<>\"\", $E$2<>\"-\"), IF(INDEX(INDIRECT($U180), MATCH(TEXT(J$5, \"????\"), INDIRECT($S180), 0))<>\"\", IF(INDEX(INDIRECT($U180), MATCH(TEXT(J$5, \"????\"), INDIRECT($S180), 0))<>\"\", IF(ISNUMBER(INDEX(INDIRECT($U180), MATCH(TEXT(J$5, \"????\"), INDIRECT($S180), 0))), ROUND(INDEX(INDIRECT($U180), MATCH(TEXT(J$5, \"????\"), INDIRECT($S180), 0)), 1), IF($E$2=\"Meets Security Standard\", PROPER(INDEX(INDIRECT($U180), MATCH(TEXT(J$5, \"????\"), INDIRECT($S180), 0))), INDEX(INDIRECT($U180), MATCH(TEXT(J$5, \"????\"), INDIRECT($S180), 0)))), \"\"), \"\"), \"\")","v":8},8,8,8,8,null,"Mona Park","MOPA","MOPA!$K$25:$W$25","MOPA!$X$25:$AQ$25","MOPA!$K$26:$W$26","MOPA!$X$26:$AQ$26"]
[null,"Monduran Dam (66/11kV)","Zone Substation",null,1.5,1.5,1.5,1.5,1.5,1.5,1.5,1.5,1.5,1.5,null,"Monduran Dam","MODA","MODA!$K$25:$W$25","MODA!$X$25:$AQ$25","MODA!$K$26:$W$26","MODA!$X$26:$AQ$26"]
[null,"Monto (66/11kV)","Zone Substation",null,14,14,14,14,14,16.7,16.7,16.7,16.7,16.7,null,"Monto","MONT","MONT!$K$25:$W$25","MONT!$X$25:$AQ$25","MONT!$K$26:$W$26","MONT!$X$26:$AQ$26"]
[null,"Moorvale (66/11kV)","Zone Substation",null,10.5,10.5,10.5,10.5,10.5,11,11,11,11,11,null,"Moorvale","MOOR","MOOR!$K$25:$W$25","MOOR!$X$25:$AQ$25","MOOR!$K$26:$W$26","MOOR!$X$26:$AQ$26"]
[null,"Moranbah Skid J (66/11kV)","Zone Substation",null,10,10,10,10,10,10,10,10,10,10,null,"Moranbah Skid J","MOSK","MOSK!$K$25:$W$25","MOSK!$X$25:$AQ$25","MOSK!$K$26:$W$26","MOSK!$X$26:$AQ$26"]
[null,"Moranbah Town (132/11kV)","Zone Substation",null,40,40,40,40,40,40,40,40,40,40,null,"Moranbah Town","MORA","MORA!$K$25:$W$25","MORA!$X$25:$AQ$25","MORA!$K$26:$W$26","MORA!$X$26:$AQ$26"]
[null,"Mossman (66/22kV)","Zone Substation",null,18.5,18.5,18.5,18.5,18.5,20.6,20.6,20.6,20.6,20.6,null,"Mossman","MOSS","MOSS!$K$25:$W$25","MOSS!$X$25:$AQ$25","MOSS!$K$26:$W$26","MOSS!$X$26:$AQ$26"]
[null,"Mount Fox (66/33kV)","Zone Substation",null,0.7,0.7,0.7,0.7,0.7,0.7,0.7,0.7,0.7,0.7,null,"Mt Fox","MOFO","MOFO!$K$25:$W$25","MOFO!$X$25:$AQ$25","MOFO!$K$26:$W$26","MOFO!$X$26:$AQ$26"]
[null,"Mount Leyshon Pump (66/11kV)","Zone Substation",null,0.6,0.6,0.6,0.6,0.6,0.6,0.6,0.6,0.6,0.6,null,"Mount Leyshon Pump","MLEP","MLEP!$K$25:$W$25","MLEP!$X$25:$AQ$25","MLEP!$K$26:$W$26","MLEP!$X$26:$AQ$26"]
[null,"Mount Rooper (66/11kV)","Zone Substation",null,5.8,5.8,5.8,5.8,5.8,6.4,6.4,6.4,6.4,6.4,null,"Mt Rooper","MORO","MORO!$K$25:$W$25","MORO!$X$25:$AQ$25","MORO!$K$26:$W$26","MORO!$X$26:$AQ$26"]
[null,"Moura (66/22kV)","Zone Substation",null,20,20,20,20,20,20,20,20,20,20,null,"Moura","MOUR","MOUR!$L$25:$W$25","MOUR!$X$25:$AQ$25","MOUR!$L$26:$W$26","MOUR!$X$26:$AQ$26"]
[null,"Mt Bassett (33/11kV)","Zone Substation",null,39,39,39,39,39,42,42,42,42,42,null,"Mt Bassett","MOBA","MOBA!$K$25:$W$25","MOBA!$X$25:$AQ$25","MOBA!$K$26:$W$26","MOBA!$X$26:$AQ$26"]
[null,"Mt Garnet (66/22kV)","Zone Substation",null,8,8,8,8,8,9.3000000000000007,9.3000000000000007,9.3000000000000007,9.3000000000000007,9.3000000000000007,null,"Mt Garnet","MOGA","MOGA!$K$25:$W$25","MOGA!$X$25:$AQ$25","MOGA!$K$26:$W$26","MOGA!$X$26:$AQ$26"]
[null,"Mt Molloy (66/22kV)","Zone Substation",null,16.399999999999999,16.399999999999999,16.399999999999999,16.399999999999999,16.399999999999999,18,18,18,18,18,null,"Mt Molloy","MOMO","MOMO!$K$25:$W$25","MOMO!$X$25:$AQ$25","MOMO!$K$26:$W$26","MOMO!$X$26:$AQ$26"]
[null,"Mt Morgan (66/11kV)","Zone Substation",null,15.8,15.8,15.8,15.8,15.8,18,18,18,18,18,null,"Mt Morgan","MOMR","MOMR!$K$25:$W$25","MOMR!$X$25:$AQ$25","MOMR!$K$26:$W$26","MOMR!$X$26:$AQ$26"]
[null,"Mt Mowbullan (33/11kV)","Zone Substation",null,1,1,1,1,1,1,1,1,1,1,null,"Mt Mowbullan","MOMW","MOMW!$K$25:$W$25","MOMW!$X$25:$AQ$25","MOMW!$K$26:$W$26","MOMW!$X$26:$AQ$26"]
[null,"Mt Sibley (33/11kV)","Zone Substation",null,6.3,6.3,6.3,6.3,6.3,6.3,6.3,6.3,6.3,6.3,null,"Mt Sibley","MOSI","MOSI!$K$25:$W$25","MOSI!$X$25:$AQ$25","MOSI!$K$26:$W$26","MOSI!$X$26:$AQ$26"]
[null,"Mundubbera Town (66/11kV)","Zone Substation",null,49.4,49.4,49.4,49.4,49.4,54.6,54.6,54.6,54.6,54.6,null,"Mundubbera Town","MUND","MUND!$K$25:$W$25","MUND!$X$25:$AQ$25",{"$f":"IF(ISERROR(MATCH($E$2, INDIRECT($Q197&\"!$E$1:$E$55\"), 0))=FALSE, ADDRESS(MATCH($E$2, INDIRECT($Q197&\"!$E$1:$E$55\"), 0), MATCH(\"SUMMER\", INDIRECT(ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q197&\"!$E$1:$E$55\"), 0), 1, 1, TRUE, $Q197)&\":$AQ\"&MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q197&\"!$E$1:$E$55\"), 0)), 0), 1, TRUE, $Q197)&\":\"&\nADDRESS(MATCH($E$2, INDIRECT($Q197&\"!$E$1:$E$55\"), 0), MATCH(\"WINTER\", INDIRECT(ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q197&\"!$E$1:$E$55\"), 0), 1, 1, TRUE, $Q197)&\":$AQ\"&MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q197&\"!$E$1:$E$55\"), 0)), 0)-1, 1, TRUE),\nIF(ISERROR(MATCH($E$2, INDIRECT($Q197&\"!$d$1:$d$55\"), 0))=FALSE, ADDRESS(MATCH($E$2, INDIRECT($Q197&\"!$d$1:$d$55\"), 0), MATCH(\"SUMMER\", INDIRECT(ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q197&\"!$d$1:$d$55\"), 0), 1, 1, TRUE, $Q197)&\":$AQ\"&MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q197&\"!$d$1:$d$55\"), 0)), 0), 1, TRUE, $Q197)&\":\"&\nADDRESS(MATCH($E$2, INDIRECT($Q197&\"!$d$1:$d$55\"), 0), MATCH(\"WINTER\", INDIRECT(ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q197&\"!$d$1:$d$55\"), 0), 1, 1, TRUE, $Q197)&\":$AQ\"&MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q197&\"!$d$1:$d$55\"), 0)), 0)-1, 1, TRUE), \"\"))","v":"MUND!$K$26:$W$26"},{"$f":"IF(ISERROR(MATCH($E$2, INDIRECT($Q197&\"!$E$1:$E$55\"), 0))=FALSE, ADDRESS(MATCH($E$2, INDIRECT($Q197&\"!$E$1:$E$55\"), 0), MATCH(\"WINTER\", INDIRECT(ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q197&\"!$E$1:$E$55\"), 0), 1, 1, TRUE, $Q197)&\":$AQ\"&MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q197&\"!$E$1:$E$55\"), 0)), 0), 1, TRUE, $Q197)&\":\"&\nADDRESS(MATCH($E$2, INDIRECT($Q197&\"!$E$1:$E$55\"), 0), 43, 1, TRUE),\nIF(ISERROR(MATCH($E$2, INDIRECT($Q197&\"!$d$1:$d$55\"), 0))=FALSE, ADDRESS(MATCH($E$2, INDIRECT($Q197&\"!$d$1:$d$55\"), 0), MATCH(\"WINTER\", INDIRECT(ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q197&\"!$d$1:$d$55\"), 0), 1, 1, TRUE, $Q197)&\":$AQ\"&MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q197&\"!$d$1:$d$55\"), 0)), 0), 1, TRUE, $Q197)&\":\"&\nADDRESS(MATCH($E$2, INDIRECT($Q197&\"!$d$1:$d$55\"), 0), 43, 1, TRUE), \"\"))","v":"MUND!$X$26:$AQ$26"}]
[null,"Murgon (66/11kV)","Zone Substation",null,29.6,29.6,29.6,29.6,29.6,35.4,35.4,35.4,35.4,35.4,null,"Murgon","MURG",{"$f":"IF(ISERROR(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q198&\"!$e$1:$e$55\"), 0))=FALSE, ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q198&\"!$e$1:$e$55\"), 0)+1, MATCH(\"SUMMER\", INDIRECT(ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q198&\"!$e$1:$e$55\"), 0), 1, 1, TRUE, $Q198)&\":$AQ\"&MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q198&\"!$e$1:$e$55\"), 0)), 0), 1, TRUE, $Q198)&\":\"&ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q198&\"!$e$1:$e$55\"), 0)+1, MATCH(\"WINTER\", INDIRECT(ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q198&\"!$e$1:$e$55\"), 0), 1, 1, TRUE, $Q198)&\":$AQ\"&MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q198&\"!$e$1:$e$55\"), 0)), 0)-1, 1, TRUE),\nIF(ISERROR(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q198&\"!$D$1:$D$55\"), 0))=FALSE, ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q198&\"!$D$1:$D$55\"), 0)+1, MATCH(\"SUMMER\", INDIRECT(ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q198&\"!$D$1:$D$55\"), 0), 1, 1, TRUE, $Q198)&\":$AQ\"&MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q198&\"!$D$1:$D$55\"), 0)), 0), 1, TRUE, $Q198)&\":\"&ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q198&\"!$D$1:$D$55\"), 0)+1, MATCH(\"WINTER\", INDIRECT(ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q198&\"!$D$1:$D$55\"), 0), 1, 1, TRUE, $Q198)&\":$AQ\"&MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q198&\"!$D$1:$D$55\"), 0)), 0)-1, 1, TRUE), \"\"))","v":"MURG!$K$25:$W$25"},{"$f":"IF(ISERROR(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q198&\"!$e$1:$e$55\"), 0))=FALSE, ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q198&\"!$e$1:$e$55\"), 0)+1, MATCH(\"WINTER\", INDIRECT(ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q198&\"!$e$1:$e$55\"), 0), 1, 1, TRUE, $Q198)&\":$AQ\"&MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q198&\"!$e$1:$e$55\"), 0)), 0), 1, TRUE, $Q198)&\":\"&ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q198&\"!$e$1:$e$55\"), 0)+1, 43, 1, TRUE),\nIF(ISERROR(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q198&\"!$D$1:$D$55\"), 0))=FALSE, ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q198&\"!$D$1:$D$55\"), 0)+1, MATCH(\"WINTER\", INDIRECT(ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q198&\"!$D$1:$D$55\"), 0), 1, 1, TRUE, $Q198)&\":$AQ\"&MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q198&\"!$D$1:$D$55\"), 0)), 0), 1, TRUE, $Q198)&\":\"&ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q198&\"!$D$1:$D$55\"), 0)+1, 43, 1, TRUE), \"\"))","v":"MURG!$X$25:$AQ$25"},"MURG!$K$26:$W$26","MURG!$X$26:$AQ$26"]
[null,"Mutarnee (66/11kV)","Zone Substation",null,1.1000000000000001,1.1000000000000001,1.1000000000000001,1.1000000000000001,1.1000000000000001,1.1000000000000001,1.1000000000000001,1.1000000000000001,1.1000000000000001,1.1000000000000001,null,"Mutarnee","MUTA","MUTA!$K$25:$W$25","MUTA!$X$25:$AQ$25","MUTA!$K$26:$W$26","MUTA!$X$26:$AQ$26"]
[null,"Nanango (66/11kV)","Zone Substation",null,13.7,13.7,13.7,13.7,13.7,15.6,15.6,15.6,15.6,15.6,null,"Nanango","NANA","NANA!$K$25:$W$25","NANA!$X$25:$AQ$25","NANA!$K$26:$W$26","NANA!$X$26:$AQ$26"]
[null,"Nandi (33/11kV)","Zone Substation",null,2,2,2,2,2,2,2,2,2,2,null,"Nandi","NAND","NAND!$K$25:$W$25","NAND!$X$25:$AQ$25","NAND!$K$26:$W$26","NAND!$X$26:$AQ$26"]
[null,"Nebo (132/11kV)","Zone Substation",null,10,10,10,10,10,10,10,10,10,10,null,"Nebo","NEBO","NEBO!$K$25:$W$25","NEBO!$X$25:$AQ$25","NEBO!$K$26:$W$26","NEBO!$X$26:$AQ$26"]
[null,"Neil Smith (66/11kV)","Zone Substation",null,65.5,65.5,65.5,65.5,65.5,68,68,68,68,68,null,"Neil Smith","NESM","NESM!$K$25:$W$25","NESM!$X$25:$AQ$25","NESM!$K$26:$W$26","NESM!$X$26:$AQ$26"]
[null,"Normanton (66/22kV)","Zone Substation",null,8.1999999999999993,8.1999999999999993,8.1999999999999993,8.1999999999999993,8.1999999999999993,9.5,9.5,9.5,9.5,9.5,null,"Normanton","NORM","NORM!$K$25:$W$25","NORM!$X$25:$AQ$25","NORM!$K$26:$W$26","NORM!$X$26:$AQ$26"]
[null,"North Cloncurry (66/11kV)","Zone Substation",null,10,10,10,10,10,13.1,13.1,13.1,13.1,13.1,null,"North Cloncurry","NOCL","NOCL!$K$25:$W$25","NOCL!$X$25:$AQ$25","NOCL!$K$26:$W$26","NOCL!$X$26:$AQ$26"]
[null,"North Mackay (33/11kV)","Zone Substation",null,47.7,47.7,47.7,47.7,47.7,53.1,53.1,53.1,53.1,53.1,null,"North Mackay","NOMA","NOMA!$K$25:$W$25","NOMA!$X$25:$AQ$25","NOMA!$K$26:$W$26","NOMA!$X$26:$AQ$26"]
[null,"North Street (33/11kV)","Zone Substation",null,30,30,30,30,30,34.5,34.5,34.5,34.5,34.5,null,"North St","NOST","NOST!$K$25:$W$25","NOST!$X$25:$AQ$25","NOST!$K$26:$W$26","NOST!$X$26:$AQ$26"]
[null,"Norwin (33/11kV)","Zone Substation",null,6,6,6,6,6,7.9,7.9,7.9,7.9,7.9,null,"Norwin","NORW","NORW!$K$25:$W$25","NORW!$X$25:$AQ$25","NORW!$K$26:$W$26","NORW!$X$26:$AQ$26"]
[null,"Oakey (33/11kV)","Zone Substation",null,49.7,49.7,49.7,49.7,49.7,56.3,56.3,56.3,56.3,56.3,null,"Oakey","OAKE","OAKE!$K$25:$W$25","OAKE!$X$25:$AQ$25","OAKE!$K$26:$W$26","OAKE!$X$26:$AQ$26"]
[null,"Oakey BSP (110/33kV)","Bulk Supply",null,147.19999999999999,147.19999999999999,147.19999999999999,147.19999999999999,147.19999999999999,165.2,165.2,165.2,165.2,165.2,null,"Oakey BSP","T189","'T189'!$J$23:$V$23","'T189'!$W$23:$AQ$23","'T189'!$J$24:$V$24","'T189'!$W$24:$AQ$24"]
[null,"Oonoonba (66/11kV)","Zone Substation",null,74.2,74.2,74.2,74.2,74.2,77.599999999999994,77.599999999999994,77.599999999999994,77.599999999999994,77.599999999999994,null,"Oonoonba","OONN","OONN!$K$25:$W$25","OONN!$X$25:$AQ$25","OONN!$K$26:$W$26","OONN!$X$26:$AQ$26"]
[null,"Owanyilla (66/11kV)","Zone Substation",null,{"$f":"IF(AND($R212<>\"\", $T212<>\"\", $E$2<>\"\", $E$2<>\"-\"), IF(INDEX(INDIRECT($T212), MATCH(E$5, INDIRECT($R212), 0))<>\"\", IF(ISNUMBER(INDEX(INDIRECT($T212), MATCH(E$5, INDIRECT($R212), 0))), ROUND(INDEX(INDIRECT($T212), MATCH(E$5, INDIRECT($R212), 0)), 1), IF($E$2=\"Meets Security Standard\", PROPER(INDEX(INDIRECT($T212), MATCH(E$5, INDIRECT($R212), 0))), INDEX(INDIRECT($T212), MATCH(E$5, INDIRECT($R212), 0)))), \"\"), \"\")","v":22},22,22,22,22,{"$f":"IF(AND($S212<>\"\", $U212<>\"\", $E$2<>\"\", $E$2<>\"-\"), IF(INDEX(INDIRECT($U212), MATCH(TEXT(J$5, \"????\"), INDIRECT($S212), 0))<>\"\", IF(INDEX(INDIRECT($U212), MATCH(TEXT(J$5, \"????\"), INDIRECT($S212), 0))<>\"\", IF(ISNUMBER(INDEX(INDIRECT($U212), MATCH(TEXT(J$5, \"????\"), INDIRECT($S212), 0))), ROUND(INDEX(INDIRECT($U212), MATCH(TEXT(J$5, \"????\"), INDIRECT($S212), 0)), 1), IF($E$2=\"Meets Security Standard\", PROPER(INDEX(INDIRECT($U212), MATCH(TEXT(J$5, \"????\"), INDIRECT($S212), 0))), INDEX(INDIRECT($U212), MATCH(TEXT(J$5, \"????\"), INDIRECT($S212), 0)))), \"\"), \"\"), \"\")","v":22},22,22,22,22,null,"Owanyilla","OWAN","OWAN!$K$25:$W$25","OWAN!$X$25:$AQ$25","OWAN!$K$26:$W$26","OWAN!$X$26:$AQ$26"]
[null,"Pampas (33/11kV)","Zone Substation",null,10,10,10,10,10,10,10,10,10,10,null,"Pampas","PAMP","PAMP!$K$25:$W$25","PAMP!$X$25:$AQ$25","PAMP!$K$26:$W$26","PAMP!$X$26:$AQ$26"]
[null,"Pandoin (66/22kV)","Zone Substation",null,23.2,23.2,23.2,23.2,23.2,26.6,26.6,26.6,26.6,26.6,null,"Pandoin","PAND","PAND!$K$25:$W$25","PAND!$X$25:$AQ$25","PAND!$K$26:$W$26","PAND!$X$26:$AQ$26"]
[null,"Parkhurst (66/11kV)","Zone Substation",null,48.3,48.3,48.3,48.3,48.3,55.4,55.4,55.4,55.4,55.4,null,"Parkhurst","PARK","PARK!$K$25:$W$25","PARK!$X$25:$AQ$25","PARK!$K$26:$W$26","PARK!$X$26:$AQ$26"]
[null,"Peranga (33/11kV)","Zone Substation",null,4.7,4.7,4.7,4.7,4.7,5.0999999999999996,5.0999999999999996,5.0999999999999996,5.0999999999999996,5.0999999999999996,null,"Peranga","PERA","PERA!$K$25:$W$25","PERA!$X$25:$AQ$25","PERA!$K$26:$W$26","PERA!$X$26:$AQ$26"]
[null,"Peter Arlett (66/11kV)","Zone Substation",null,78.900000000000006,78.900000000000006,78.900000000000006,78.900000000000006,78.900000000000006,87.4,87.4,87.4,87.4,87.4,null,"Peter Arlett","PEAR","PEAR!$K$25:$W$25","PEAR!$X$25:$AQ$25","PEAR!$K$26:$W$26","PEAR!$X$26:$AQ$26"]
[null,"Pialba (66/11kV)","Zone Substation",null,33.200000000000003,33.200000000000003,33.200000000000003,33.200000000000003,33.200000000000003,37.200000000000003,37.200000000000003,37.200000000000003,37.200000000000003,37.200000000000003,null,"Pialba","PIAL","PIAL!$K$25:$W$25","PIAL!$X$25:$AQ$25","PIAL!$K$26:$W$26","PIAL!$X$26:$AQ$26"]
[null,"Pinnacle (66/11kV)","Zone Substation",null,11,11,11,11,11,12,12,12,12,12,null,"Pinnacle","PINN","PINN!$K$25:$W$25","PINN!$X$25:$AQ$25","PINN!$K$26:$W$26","PINN!$X$26:$AQ$26"]
[null,"Pirrinuan (33/11kV)","Zone Substation",null,3.5,3.5,3.5,3.5,3.5,3.5,3.5,3.5,3.5,3.5,null,"Pirrinuan","PIRR","PIRR!$K$25:$W$25","PIRR!$X$25:$AQ$25","PIRR!$K$26:$W$26","PIRR!$X$26:$AQ$26"]
[null,"Planella (66/11kV)","Zone Substation",null,30,30,30,30,30,30.6,30.6,30.6,30.6,30.6,null,"Planella","PLAN","PLAN!$K$25:$W$25","PLAN!$X$25:$AQ$25","PLAN!$K$26:$W$26","PLAN!$X$26:$AQ$26"]
[null,"Pleystowe (33/11kV)","Zone Substation",null,13.5,13.5,13.5,13.5,13.5,13.5,13.5,13.5,13.5,13.5,null,"Pleystowe","PLEY","PLEY!$K$25:$W$25","PLEY!$X$25:$AQ$25","PLEY!$K$26:$W$26","PLEY!$X$26:$AQ$26"]
[null,"Point Vernon (66/11kV)","Zone Substation",null,84.6,84.6,84.6,84.6,84.6,95.7,95.7,95.7,95.7,95.7,null,"Point Vernon","POVE","POVE!$K$25:$W$25","POVE!$X$25:$AQ$25","POVE!$K$26:$W$26","POVE!$X$26:$AQ$26"]
[null,"Pozieres (33/11kV)","Zone Substation",null,7.1,7.1,7.1,7.1,7.1,7.5,7.5,7.5,7.5,7.5,null,"Pozieres","POZI","POZI!$K$25:$W$25","POZI!$X$25:$AQ$25","POZI!$K$26:$W$26","POZI!$X$26:$AQ$26"]
[null,"Proston (66/11kV)","Zone Substation",null,5.4,5.4,5.4,5.4,5.4,6,6,6,6,6,null,"Proston","PROT","PROT!$K$25:$W$25","PROT!$X$25:$AQ$25","PROT!$K$26:$W$26","PROT!$X$26:$AQ$26"]
[null,"Purrawunda (33/11kV)","Zone Substation",null,14,14,14,14,14,15.5,15.5,15.5,15.5,15.5,null,"Purrawunda","PURR","PURR!$K$25:$W$25","PURR!$X$25:$AQ$25","PURR!$K$26:$W$26","PURR!$X$26:$AQ$26"]
[null,"Quilpie (66/11kV)","Zone Substation",null,6,6,6,6,6,7.4,7.4,7.4,7.4,7.4,null,"Quilpie","QUIL","QUIL!$K$25:$W$25","QUIL!$X$25:$AQ$25","QUIL!$K$26:$W$26","QUIL!$X$26:$AQ$26"]
[null,"Raglan (66/22kV)","Zone Substation",null,12.5,12.5,12.5,12.5,12.5,14,14,14,14,14,null,"Raglan","RAGL","RAGL!$K$25:$W$25","RAGL!$X$25:$AQ$25","RAGL!$K$26:$W$26","RAGL!$X$26:$AQ$26"]
[null,"Rasmussen (66/11kV)","Zone Substation",null,80.400000000000006,80.400000000000006,80.400000000000006,80.400000000000006,80.400000000000006,84.4,84.4,84.4,84.4,84.4,null,"Rasmussen","RASM","RASM!$K$25:$W$25","RASM!$X$25:$AQ$25","RASM!$K$26:$W$26","RASM!$X$26:$AQ$26"]
[null,"Ravenshoe (66/22kV)","Zone Substation",null,19.600000000000001,19.600000000000001,19.600000000000001,19.600000000000001,19.600000000000001,22.3,22.3,22.3,22.3,22.3,null,"Ravenshoe","RAVE","RAVE!$K$25:$W$25","RAVE!$X$25:$AQ$25","RAVE!$K$26:$W$26","RAVE!$X$26:$AQ$26"]
[null,"Ravenswood (66/11kV)","Zone Substation",null,2.5,2.5,2.5,2.5,2.5,2.5,2.5,2.5,2.5,2.5,null,"Ravenswood","RAVN","RAVN!$K$25:$W$25","RAVN!$X$25:$AQ$25","RAVN!$K$26:$W$26","RAVN!$X$26:$AQ$26"]
[null,"Richmond (66/33kV)","Zone Substation",null,{"$f":"IF(AND($R232<>\"\", $T232<>\"\", $E$2<>\"\", $E$2<>\"-\"), IF(INDEX(INDIRECT($T232), MATCH(E$5, INDIRECT($R232), 0))<>\"\", IF(ISNUMBER(INDEX(INDIRECT($T232), MATCH(E$5, INDIRECT($R232), 0))), ROUND(INDEX(INDIRECT($T232), MATCH(E$5, INDIRECT($R232), 0)), 1), IF($E$2=\"Meets Security Standard\", PROPER(INDEX(INDIRECT($T232), MATCH(E$5, INDIRECT($R232), 0))), INDEX(INDIRECT($T232), MATCH(E$5, INDIRECT($R232), 0)))), \"\"), \"\")","v":14.6},14.6,14.6,14.6,14.6,{"$f":"IF(AND($S232<>\"\", $U232<>\"\", $E$2<>\"\", $E$2<>\"-\"), IF(INDEX(INDIRECT($U232), MATCH(TEXT(J$5, \"????\"), INDIRECT($S232), 0))<>\"\", IF(INDEX(INDIRECT($U232), MATCH(TEXT(J$5, \"????\"), INDIRECT($S232), 0))<>\"\", IF(ISNUMBER(INDEX(INDIRECT($U232), MATCH(TEXT(J$5, \"????\"), INDIRECT($S232), 0))), ROUND(INDEX(INDIRECT($U232), MATCH(TEXT(J$5, \"????\"), INDIRECT($S232), 0)), 1), IF($E$2=\"Meets Security Standard\", PROPER(INDEX(INDIRECT($U232), MATCH(TEXT(J$5, \"????\"), INDIRECT($S232), 0))), INDEX(INDIRECT($U232), MATCH(TEXT(J$5, \"????\"), INDIRECT($S232), 0)))), \"\"), \"\"), \"\")","v":16.3},16.3,16.3,16.3,16.3,null,"Richmond","RICH","RICH!$K$25:$W$25","RICH!$X$25:$AQ$25","RICH!$K$26:$W$26","RICH!$X$26:$AQ$26"]
[null,"Rockhampton Glenmore (66/11kV)","Zone Substation",null,54.3,54.3,54.3,54.3,54.3,55,55,55,55,55,null,"Rockhampton Glenmore","ROGL","ROGL!$K$25:$W$25","ROGL!$X$25:$AQ$25","ROGL!$K$26:$W$26","ROGL!$X$26:$AQ$26"]
[null,"Rockhampton South (66/11kV)","Zone Substation",null,32.700000000000003,32.700000000000003,32.700000000000003,32.700000000000003,32.700000000000003,32.700000000000003,32.700000000000003,32.700000000000003,32.700000000000003,32.700000000000003,null,"Rockhampton South","ROSO","ROSO!$K$25:$W$25","ROSO!$X$25:$AQ$25","ROSO!$K$26:$W$26","ROSO!$X$26:$AQ$26"]
[null,"Rocky Street (66/11kV)","Zone Substation",null,57.5,57.5,57.5,57.5,57.5,64.3,64.3,64.3,64.3,64.3,null,"Rocky Street","ROST","ROST!$K$25:$W$25","ROST!$X$25:$AQ$25","ROST!$K$26:$W$26","ROST!$X$26:$AQ$26"]
[null,"Rolleston (66/22kV)","Zone Substation",null,25,25,25,25,25,25,25,25,25,25,null,"Rolleston","ROLE","ROLE!$K$25:$W$25","ROLE!$X$25:$AQ$25","ROLE!$K$26:$W$26","ROLE!$X$26:$AQ$26"]
[null,"Rolleston BSP (132/66kV)","Bulk Supply",null,89.3,89.3,89.3,89.3,89.3,97.7,97.7,97.7,97.7,97.7,null,"Rolleston ","T163","'T163'!$J$23:$V$23","'T163'!$W$23:$AQ$23","'T163'!$J$24:$V$24","'T163'!$W$24:$AQ$24"]
[null,"Rollingstone (66/11kV)","Zone Substation",null,3.8,3.8,3.8,3.8,3.8,3.8,3.8,3.8,3.8,3.8,null,"Rollingstone","ROLL","ROLL!$K$25:$W$25","ROLL!$X$25:$AQ$25","ROLL!$K$26:$W$26","ROLL!$X$26:$AQ$26"]
[null,"Roma 33kV BSP (132/33kV)","Bulk Supply",null,97.8,97.8,97.8,97.8,97.8,115.2,115.2,115.2,115.2,115.2,null,"Roma 33kV ","T083","'T083'!$J$23:$V$23","'T083'!$W$23:$AQ$23","'T083'!$J$24:$V$24","'T083'!$W$24:$AQ$24"]
[null,"Roma 66kV BSP (132/66kV)","Bulk Supply",null,101.4,101.4,101.4,101.4,101.4,119.6,119.6,119.6,119.6,119.6,null,"Roma 66kV","T0831","'T0831'!$J$23:$V$23","'T0831'!$W$23:$AQ$23","'T0831'!$J$24:$V$24","'T0831'!$W$24:$AQ$24"]
[null,"Roma East (33/11kV)","Zone Substation",null,14,14,14,14,14,17.5,17.5,17.5,17.5,17.5,null,"Roma East","ROEA","ROEA!$K$25:$W$25","ROEA!$X$25:$AQ$25","ROEA!$K$26:$W$26","ROEA!$X$26:$AQ$26"]
[null,"Roma West (33/11kV)","Zone Substation",null,6.3,6.3,6.3,6.3,6.3,6.3,6.3,6.3,6.3,6.3,null,"Roma West","ROWE","ROWE!$K$25:$W$25","ROWE!$X$25:$AQ$25","ROWE!$K$26:$W$26","ROWE!$X$26:$AQ$26"]
[null,"Roo Works (33/11kV)","Zone Substation",null,2.4,2.4,2.4,2.4,2.4,2.4,2.4,2.4,2.4,2.4,null,"Roo Works","ROWO","ROWO!$K$25:$W$25","ROWO!$X$25:$AQ$25","ROWO!$K$26:$W$26","ROWO!$X$26:$AQ$26"]
[null,"Rosella (33/11kV)","Zone Substation",null,11.5,11.5,11.5,11.5,11.5,12.3,12.3,12.3,12.3,12.3,null,"Rosella","ROSE","ROSE!$K$25:$W$25","ROSE!$X$25:$AQ$25","ROSE!$K$26:$W$26","ROSE!$X$26:$AQ$26"]
[null,"Ross Plains (66/11kV)","Zone Substation",null,33,33,33,33,33,37.799999999999997,37.799999999999997,37.799999999999997,37.799999999999997,37.799999999999997,null,"Ross Plains","ROPL","ROPL!$K$25:$W$25","ROPL!$X$25:$AQ$25","ROPL!$K$26:$W$26","ROPL!$X$26:$AQ$26"]
[null,"Sarina (33/11kV)","Zone Substation",null,24,24,24,24,24,26.8,26.8,26.8,26.8,26.8,null,"Sarina","SARI","SARI!$K$25:$W$25","SARI!$X$25:$AQ$25","SARI!$K$26:$W$26","SARI!$X$26:$AQ$26"]
[null,"Saunders (66/11kV)","Zone Substation",null,5.0999999999999996,5.0999999999999996,5.0999999999999996,5.0999999999999996,5.0999999999999996,5.4,5.4,5.4,5.4,5.4,null,"Saunders","SAUN","SAUN!$K$25:$W$25","SAUN!$X$25:$AQ$25","SAUN!$K$26:$W$26","SAUN!$X$26:$AQ$26"]
[null,"Shutehaven (66/22kV)","Zone Substation",null,30.4,30.4,30.4,30.4,30.4,33.200000000000003,33.200000000000003,33.200000000000003,33.200000000000003,33.200000000000003,null,"Shutehaven","SHUT","SHUT!$K$25:$W$25","SHUT!$X$25:$AQ$25","SHUT!$K$26:$W$26","SHUT!$X$26:$AQ$26"]
[null,"South Blackwater (66/22kV)","Zone Substation",null,0.4,0.4,0.4,0.4,0.4,0.4,0.4,0.4,0.4,0.4,null,"South Blackwater","SOBL","SOBL!$K$25:$W$25","SOBL!$X$25:$AQ$25","SOBL!$K$26:$W$26","SOBL!$X$26:$AQ$26"]
[null,"South Bundaberg (66/11kV)","Zone Substation",null,42.4,42.4,42.4,42.4,42.4,46.6,46.6,46.6,46.6,46.6,null,"South Bundaberg","SOBU","SOBU!$K$25:$W$25","SOBU!$X$25:$AQ$25","SOBU!$K$26:$W$26","SOBU!$X$26:$AQ$26"]
[null,"South Kolan (66/11kV)","Zone Substation",null,27.5,27.5,27.5,27.5,27.5,29.9,29.9,29.9,29.9,29.9,null,"South Kolan","SOKO","SOKO!$K$25:$W$25","SOKO!$X$25:$AQ$25","SOKO!$K$26:$W$26","SOKO!$X$26:$AQ$26"]
[null,"South Mackay (33/11kV)","Zone Substation",null,40,40,40,40,40,40,40,40,40,40,null,"South Mackay","SOMA","SOMA!$K$25:$W$25","SOMA!$X$25:$AQ$25","SOMA!$K$26:$W$26","SOMA!$X$26:$AQ$26"]
[null,"South Toowoomba (33/11kV)","Zone Substation",null,37.4,37.4,37.4,37.4,37.4,42.4,42.4,42.4,42.4,42.4,null,"South Toowoomba","SOTO","SOTO!$K$25:$W$25","SOTO!$X$25:$AQ$25","SOTO!$K$26:$W$26","SOTO!$X$26:$AQ$26"]
[null,"South Toowoomba BSP (110/33kV)","Bulk Supply",null,144.9,144.9,144.9,144.9,144.9,163.6,163.6,163.6,163.6,163.6,null,"South Toowoomba ","T043","'T043'!$J$23:$V$23","'T043'!$W$23:$AQ$23","'T043'!$J$24:$V$24","'T043'!$W$24:$AQ$24"]
[null,"St. George (66/33kV)","Zone Substation",null,48.7,48.7,48.7,48.7,48.7,55.9,55.9,55.9,55.9,55.9,null,"St George","SAGE","SAGE!$K$25:$W$25","SAGE!$X$25:$AQ$25","SAGE!$K$26:$W$26","SAGE!$X$26:$AQ$26"]
[null,"St. George Town (33/11kV)","Zone Substation",null,6.6,6.6,6.6,6.6,6.6,6.6,6.6,6.6,6.6,6.6,null,"St George Town","SAGT","SAGT!$K$25:$W$25","SAGT!$X$25:$AQ$25","SAGT!$K$26:$W$26","SAGT!$X$26:$AQ$26"]
[null,"Stamford (66/33kV)","Zone Substation",null,0.6,0.6,0.6,0.6,0.6,0.6,0.6,0.6,0.6,0.6,null,"Stamford","STAM","STAM!$K$25:$W$25","STAM!$X$25:$AQ$25","STAM!$K$26:$W$26","STAM!$X$26:$AQ$26"]
[null,"Stanthorpe BSP (110/33kV)","Bulk Supply",null,71.3,71.3,71.3,71.3,71.3,80.400000000000006,80.400000000000006,80.400000000000006,80.400000000000006,80.400000000000006,null,"Stanthorpe ","T060","'T060'!$J$23:$V$23","'T060'!$W$23:$AQ$23","'T060'!$J$24:$V$24","'T060'!$W$24:$AQ$24"]
[null,"Stanthorpe Town (33/11kV)","Zone Substation",null,27.1,27.1,27.1,27.1,27.1,29.2,29.2,29.2,29.2,29.2,null,"Stanthorpe Town","STTO","STTO!$K$25:$W$25","STTO!$X$25:$AQ$25","STTO!$K$26:$W$26","STTO!$X$26:$AQ$26"]
[null,"Stuart (66/11kV)","Zone Substation",null,76.7,76.7,76.7,76.7,76.7,81.599999999999994,81.599999999999994,81.599999999999994,81.599999999999994,81.599999999999994,null,"Stuart","STUA","STUA!$K$25:$W$25","STUA!$X$25:$AQ$25","STUA!$K$26:$W$26","STUA!$X$26:$AQ$26"]
[null,"Tanby (66/22kV)","Zone Substation",null,50.4,50.4,50.4,50.4,50.4,56.6,56.6,56.6,56.6,56.6,null,"Tanby","TANB","TANB!$K$25:$W$25","TANB!$X$25:$AQ$25","TANB!$K$26:$W$26","TANB!$X$26:$AQ$26"]
[null,"Tara (33/11kV)","Zone Substation",null,2,2,2,2,2,2,2,2,2,2,null,"Tara","TARA","TARA!$K$25:$W$25","TARA!$X$25:$AQ$25",{"$f":"IF(ISERROR(MATCH($E$2, INDIRECT($Q262&\"!$E$1:$E$55\"), 0))=FALSE, ADDRESS(MATCH($E$2, INDIRECT($Q262&\"!$E$1:$E$55\"), 0), MATCH(\"SUMMER\", INDIRECT(ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q262&\"!$E$1:$E$55\"), 0), 1, 1, TRUE, $Q262)&\":$AQ\"&MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q262&\"!$E$1:$E$55\"), 0)), 0), 1, TRUE, $Q262)&\":\"&\nADDRESS(MATCH($E$2, INDIRECT($Q262&\"!$E$1:$E$55\"), 0), MATCH(\"WINTER\", INDIRECT(ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q262&\"!$E$1:$E$55\"), 0), 1, 1, TRUE, $Q262)&\":$AQ\"&MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q262&\"!$E$1:$E$55\"), 0)), 0)-1, 1, TRUE),\nIF(ISERROR(MATCH($E$2, INDIRECT($Q262&\"!$d$1:$d$55\"), 0))=FALSE, ADDRESS(MATCH($E$2, INDIRECT($Q262&\"!$d$1:$d$55\"), 0), MATCH(\"SUMMER\", INDIRECT(ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q262&\"!$d$1:$d$55\"), 0), 1, 1, TRUE, $Q262)&\":$AQ\"&MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q262&\"!$d$1:$d$55\"), 0)), 0), 1, TRUE, $Q262)&\":\"&\nADDRESS(MATCH($E$2, INDIRECT($Q262&\"!$d$1:$d$55\"), 0), MATCH(\"WINTER\", INDIRECT(ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q262&\"!$d$1:$d$55\"), 0), 1, 1, TRUE, $Q262)&\":$AQ\"&MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q262&\"!$d$1:$d$55\"), 0)), 0)-1, 1, TRUE), \"\"))","v":"TARA!$K$26:$W$26"},{"$f":"IF(ISERROR(MATCH($E$2, INDIRECT($Q262&\"!$E$1:$E$55\"), 0))=FALSE, ADDRESS(MATCH($E$2, INDIRECT($Q262&\"!$E$1:$E$55\"), 0), MATCH(\"WINTER\", INDIRECT(ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q262&\"!$E$1:$E$55\"), 0), 1, 1, TRUE, $Q262)&\":$AQ\"&MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q262&\"!$E$1:$E$55\"), 0)), 0), 1, TRUE, $Q262)&\":\"&\nADDRESS(MATCH($E$2, INDIRECT($Q262&\"!$E$1:$E$55\"), 0), 43, 1, TRUE),\nIF(ISERROR(MATCH($E$2, INDIRECT($Q262&\"!$d$1:$d$55\"), 0))=FALSE, ADDRESS(MATCH($E$2, INDIRECT($Q262&\"!$d$1:$d$55\"), 0), MATCH(\"WINTER\", INDIRECT(ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q262&\"!$d$1:$d$55\"), 0), 1, 1, TRUE, $Q262)&\":$AQ\"&MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q262&\"!$d$1:$d$55\"), 0)), 0), 1, TRUE, $Q262)&\":\"&\nADDRESS(MATCH($E$2, INDIRECT($Q262&\"!$d$1:$d$55\"), 0), 43, 1, TRUE), \"\"))","v":"TARA!$X$26:$AQ$26"}]
[null,"Tennyson Street (33/11kV)","Zone Substation",null,25,25,25,25,25,25,25,25,25,25,null,"Tennyson St","TEST",{"$f":"IF(ISERROR(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q263&\"!$e$1:$e$55\"), 0))=FALSE, ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q263&\"!$e$1:$e$55\"), 0)+1, MATCH(\"SUMMER\", INDIRECT(ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q263&\"!$e$1:$e$55\"), 0), 1, 1, TRUE, $Q263)&\":$AQ\"&MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q263&\"!$e$1:$e$55\"), 0)), 0), 1, TRUE, $Q263)&\":\"&ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q263&\"!$e$1:$e$55\"), 0)+1, MATCH(\"WINTER\", INDIRECT(ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q263&\"!$e$1:$e$55\"), 0), 1, 1, TRUE, $Q263)&\":$AQ\"&MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q263&\"!$e$1:$e$55\"), 0)), 0)-1, 1, TRUE),\nIF(ISERROR(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q263&\"!$D$1:$D$55\"), 0))=FALSE, ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q263&\"!$D$1:$D$55\"), 0)+1, MATCH(\"SUMMER\", INDIRECT(ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q263&\"!$D$1:$D$55\"), 0), 1, 1, TRUE, $Q263)&\":$AQ\"&MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q263&\"!$D$1:$D$55\"), 0)), 0), 1, TRUE, $Q263)&\":\"&ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q263&\"!$D$1:$D$55\"), 0)+1, MATCH(\"WINTER\", INDIRECT(ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q263&\"!$D$1:$D$55\"), 0), 1, 1, TRUE, $Q263)&\":$AQ\"&MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q263&\"!$D$1:$D$55\"), 0)), 0)-1, 1, TRUE), \"\"))","v":"TEST!$K$25:$W$25"},{"$f":"IF(ISERROR(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q263&\"!$e$1:$e$55\"), 0))=FALSE, ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q263&\"!$e$1:$e$55\"), 0)+1, MATCH(\"WINTER\", INDIRECT(ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q263&\"!$e$1:$e$55\"), 0), 1, 1, TRUE, $Q263)&\":$AQ\"&MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q263&\"!$e$1:$e$55\"), 0)), 0), 1, TRUE, $Q263)&\":\"&ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q263&\"!$e$1:$e$55\"), 0)+1, 43, 1, TRUE),\nIF(ISERROR(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q263&\"!$D$1:$D$55\"), 0))=FALSE, ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q263&\"!$D$1:$D$55\"), 0)+1, MATCH(\"WINTER\", INDIRECT(ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q263&\"!$D$1:$D$55\"), 0), 1, 1, TRUE, $Q263)&\":$AQ\"&MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q263&\"!$D$1:$D$55\"), 0)), 0), 1, TRUE, $Q263)&\":\"&ADDRESS(MATCH(\"PEAK LOAD FORECAST AND CAPACITY\", INDIRECT($Q263&\"!$D$1:$D$55\"), 0)+1, 43, 1, TRUE), \"\"))","v":"TEST!$X$25:$AQ$25"},"TEST!$K$26:$W$26","TEST!$X$26:$AQ$26"]
[null,"Theodore (66/22kV)","Zone Substation",null,16.600000000000001,16.600000000000001,16.600000000000001,16.600000000000001,16.600000000000001,18.2,18.2,18.2,18.2,18.2,null,"Theodore","THEO","THEO!$K$25:$W$25","THEO!$X$25:$AQ$25","THEO!$K$26:$W$26","THEO!$X$26:$AQ$26"]
[null,"Tieri (66/22kV)","Zone Substation",null,10,10,10,10,10,10,10,10,10,10,null,"Tieri","TIER","TIER!$K$25:$W$25","TIER!$X$25:$AQ$25","TIER!$K$26:$W$26","TIER!$X$26:$AQ$26"]
[null,"Toowoomba Central (110/11kV)","Zone Substation",null,84,84,84,84,84,84,84,84,84,84,null,"Toowoomba Central","TWCE","TWCE!$K$25:$W$25","TWCE!$X$25:$AQ$25","TWCE!$K$26:$W$26","TWCE!$X$26:$AQ$26"]
[null,"Torquay (66/11kV)","Zone Substation",null,91.1,91.1,91.1,91.1,91.1,99,99,99,99,99,null,"Torquay","TORQ","TORQ!$K$25:$W$25","TORQ!$X$25:$AQ$25","TORQ!$K$26:$W$26","TORQ!$X$26:$AQ$26"]
[null,"Torrington (33/11kV)","Zone Substation",null,56.7,56.7,56.7,56.7,56.7,67.5,67.5,67.5,67.5,67.5,null,"Torrington","TORR","TORR!$K$25:$W$25","TORR!$X$25:$AQ$25","TORR!$K$26:$W$26","TORR!$X$26:$AQ$26"]
[null,"Torrington BSP (110/33kV)","Bulk Supply",null,239,239,239,239,239,286.2,286.2,286.2,286.2,286.2,null,"Torrington ","T116","'T116'!$J$23:$V$23","'T116'!$W$23:$AQ$23","'T116'!$J$24:$V$24","'T116'!$W$24:$AQ$24"]
[null,"Townsville Port (66/11kV)","Zone Substation",null,83.2,83.2,83.2,83.2,83.2,83.2,83.2,83.2,83.2,83.2,null,"Townsville Port","TOPO","TOPO!$K$25:$W$25","TOPO!$X$25:$AQ$25","TOPO!$K$26:$W$26","TOPO!$X$26:$AQ$26"]
[null,"Tuan (66/11kV)","Zone Substation",null,10.8,10.8,10.8,10.8,10.8,11.4,11.4,11.4,11.4,11.4,null,"Tuan","TUAN","TUAN!$K$25:$W$25","TUAN!$X$25:$AQ$25","TUAN!$K$26:$W$26","TUAN!$X$26:$AQ$26"]
[null,"Vermont (66/22kV)","Zone Substation",null,22.1,22.1,22.1,22.1,22.1,24.3,24.3,24.3,24.3,24.3,null,"Vermont","VERM","VERM!$K$25:$W$25","VERM!$X$25:$AQ$25","VERM!$K$26:$W$26","VERM!$X$26:$AQ$26"]
[null,"Victoria (66/11kV)","Zone Substation",null,0,0,7.6,7.6,7.6,7.6,7.6,7.6,7.6,7.6,null,"Victoria","VICT","VICT!$K$25:$W$25","VICT!$X$25:$AQ$25","VICT!$K$26:$W$26","VICT!$X$26:$AQ$26"]
[null,"Wallaville (66/11kV)","Zone Substation",null,25.6,25.6,25.6,25.6,25.6,27,27,27,27,27,null,"Wallaville","WALL","WALL!$K$25:$W$25","WALL!$X$25:$AQ$25","WALL!$K$26:$W$26","WALL!$X$26:$AQ$26"]
[null,"Wandoan (33/22kV)","Zone Substation",null,12.2,12.2,12.2,12.2,12.2,14.5,14.5,14.5,14.5,14.5,null,"Wandoan","WAND","WAND!$K$25:$W$25","WAND!$X$25:$AQ$25","WAND!$K$26:$W$26","WAND!$X$26:$AQ$26"]
[null,"Warwick BSP (110/33kV)","Bulk Supply",null,118.5,118.5,118.5,118.5,118.5,135.6,135.6,135.6,135.6,135.6,null,"Warwick ","T058","'T058'!$J$23:$V$23","'T058'!$W$23:$AQ$23","'T058'!$J$24:$V$24","'T058'!$W$24:$AQ$24"]
[null,"Warwick East (33/11kV)","Zone Substation",null,69.599999999999994,69.599999999999994,69.599999999999994,69.599999999999994,69.599999999999994,79.2,79.2,79.2,79.2,79.2,null,"Warwick East","WAEA","WAEA!$K$25:$W$25","WAEA!$X$25:$AQ$25","WAEA!$K$26:$W$26","WAEA!$X$26:$AQ$26"]
[null,"West Bundaberg (66/11kV)","Zone Substation",null,61.3,61.3,61.3,61.3,61.3,65,65,65,65,65,null,"West Bundaberg","WEBU","WEBU!$K$25:$W$25","WEBU!$X$25:$AQ$25","WEBU!$K$26:$W$26","WEBU!$X$26:$AQ$26"]
[null,"West Dalby (33/11kV)","Zone Substation",null,14.6,14.6,14.6,14.6,14.6,17.5,17.5,17.5,17.5,17.5,null,"West Dalby","WEDA","WEDA!$K$25:$W$25","WEDA!$X$25:$AQ$25","WEDA!$K$26:$W$26","WEDA!$X$26:$AQ$26"]
[null,"West Mackay (33/11kV)","Zone Substation",null,38.700000000000003,38.700000000000003,38.700000000000003,38.700000000000003,38.700000000000003,40.9,40.9,40.9,40.9,40.9,null,"West Mackay","WEMA","WEMA!$K$25:$W$25","WEMA!$X$25:$AQ$25","WEMA!$K$26:$W$26","WEMA!$X$26:$AQ$26"]
[null,"West Toowoomba (33/11kV)","Zone Substation",null,30,30,30,30,30,36.200000000000003,36.200000000000003,36.200000000000003,36.200000000000003,36.200000000000003,null,"West Toowoomba","WETO","WETO!$K$25:$W$25","WETO!$X$25:$AQ$25","WETO!$K$26:$W$26","WETO!$X$26:$AQ$26"]
[null,"West Warwick (33/11kV)","Zone Substation",null,27,27,27,27,27,30,30,30,30,30,null,"West Warwick","WEWA","WEWA!$K$25:$W$25","WEWA!$X$25:$AQ$25","WEWA!$K$26:$W$26","WEWA!$X$26:$AQ$26"]
[null,"Winton (66/11kV)","Zone Substation",null,{"$f":"IF(AND($R283<>\"\", $T283<>\"\", $E$2<>\"\", $E$2<>\"-\"), IF(INDEX(INDIRECT($T283), MATCH(E$5, INDIRECT($R283), 0))<>\"\", IF(ISNUMBER(INDEX(INDIRECT($T283), MATCH(E$5, INDIRECT($R283), 0))), ROUND(INDEX(INDIRECT($T283), MATCH(E$5, INDIRECT($R283), 0)), 1), IF($E$2=\"Meets Security Standard\", PROPER(INDEX(INDIRECT($T283), MATCH(E$5, INDIRECT($R283), 0))), INDEX(INDIRECT($T283), MATCH(E$5, INDIRECT($R283), 0)))), \"\"), \"\")","v":9.4},9.4,9.4,9.4,9.4,{"$f":"IF(AND($S283<>\"\", $U283<>\"\", $E$2<>\"\", $E$2<>\"-\"), IF(INDEX(INDIRECT($U283), MATCH(TEXT(J$5, \"????\"), INDIRECT($S283), 0))<>\"\", IF(INDEX(INDIRECT($U283), MATCH(TEXT(J$5, \"????\"), INDIRECT($S283), 0))<>\"\", IF(ISNUMBER(INDEX(INDIRECT($U283), MATCH(TEXT(J$5, \"????\"), INDIRECT($S283), 0))), ROUND(INDEX(INDIRECT($U283), MATCH(TEXT(J$5, \"????\"), INDIRECT($S283), 0)), 1), IF($E$2=\"Meets Security Standard\", PROPER(INDEX(INDIRECT($U283), MATCH(TEXT(J$5, \"????\"), INDIRECT($S283), 0))), INDEX(INDIRECT($U283), MATCH(TEXT(J$5, \"????\"), INDIRECT($S283), 0)))), \"\"), \"\"), \"\")","v":10.9},10.9,10.9,10.9,10.9,null,"Winton","WINT","WINT!$K$25:$W$25","WINT!$X$25:$AQ$25","WINT!$K$26:$W$26","WINT!$X$26:$AQ$26"]
[null,"Woodgate (66/11kV)","Zone Substation",null,5.3,5.3,5.3,5.3,5.3,5.3,5.3,5.3,5.3,5.3,null,"Woodgate","WOOG","WOOG!$K$25:$W$25","WOOG!$X$25:$AQ$25","WOOG!$K$26:$W$26","WOOG!$X$26:$AQ$26"]
[null,"Woodhouse Station (66/11kV)","Zone Substation",null,0.3,0.3,0.3,0.3,0.3,0.3,0.3,0.3,0.3,0.3,null,"Woodhouse Station","WOOD","WOOD!$K$25:$W$25","WOOD!$X$25:$AQ$25","WOOD!$K$26:$W$26","WOOD!$X$26:$AQ$26"]
[null,"Woodstock South (66/11kV)","Zone Substation",null,8.6,8.6,8.6,8.6,8.6,9.4,9.4,9.4,9.4,9.4,null,"Woodstock South","WOSO","WOSO!$K$25:$W$25","WOSO!$X$25:$AQ$25","WOSO!$K$26:$W$26","WOSO!$X$26:$AQ$26"]
[null,"Woolooga (66/11kV)","Zone Substation",null,17.7,17.7,17.7,17.7,17.7,18.7,18.7,18.7,18.7,18.7,null,"Woolooga","WOOL","WOOL!$K$25:$W$25","WOOL!$X$25:$AQ$25","WOOL!$K$26:$W$26","WOOL!$X$26:$AQ$26"]
[null,"Wowan (66/22kV)","Zone Substation",null,16.100000000000001,16.100000000000001,16.100000000000001,16.100000000000001,16.100000000000001,18,18,18,18,18,null,"Wowan","WOWA","WOWA!$K$25:$W$25","WOWA!$X$25:$AQ$25","WOWA!$K$26:$W$26","WOWA!$X$26:$AQ$26"]
[null,"Yarraman (66/11kV)","Zone Substation",null,15.5,15.5,15.5,15.5,15.5,17.899999999999999,17.899999999999999,17.899999999999999,17.899999999999999,17.899999999999999,null,"Yarraman","YARR","YARR!$K$25:$W$25","YARR!$X$25:$AQ$25","YARR!$K$26:$W$26","YARR!$X$26:$AQ$26"]
[null,"Yarranlea BSP (110/33kV)","Bulk Supply",null,30,30,30,30,30,30,30,30,30,30,null,"Yarranlea ","T010","'T010'!$J$23:$V$23","'T010'!$W$23:$AQ$23","'T010'!$J$24:$V$24","'T010'!$W$24:$AQ$24"]
[null,"Yarranlea South (33/11kV)","Zone Substation",null,2.8,2.8,2.8,2.8,2.8,2.8,2.8,2.8,2.8,2.8,null,"Yarranlea South","YASO","YASO!$K$25:$W$25","YASO!$X$25:$AQ$25","YASO!$K$26:$W$26","YASO!$X$26:$AQ$26"]
[null,"Yeppoon (66/11kV)","Zone Substation",null,59,59,59,59,59,67.8,67.8,67.8,67.8,67.8,null,"Yeppoon","YEPP","YEPP!$K$25:$W$25","YEPP!$X$25:$AQ$25","YEPP!$K$26:$W$26","YEPP!$X$26:$AQ$26"]

{"sheet":"AGWA","index":3,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"AGWA - Agnes Water (66/22kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T166 - Granite Creek BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Capricornia"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/22kV 15/20MVA ONAN/ONAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.0%, 2020 S 0.2% W 0.2%, 2021 S 0.2% W 0.2%, 2022 S 0.1% W 0.1%, 2023 S -0.0% W -0.0"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"4.9 MVA on 29/12/2018 at 19:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,48,null,48,null,48,null,48,null,null,null,null,48,null,55.599998474121094,null,55.599998474121094,null,null,null,null,null,55.599998474121094,55.599998474121094,null,null,55.599998474121094]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,4.9000000953674316,null,4.9000000953674316,null,4.8000001907348633,null,4.8000001907348633,null,null,null,null,4.9000000953674316,null,4.3000001907348633,null,4.3000001907348633,null,null,null,null,null,4.3000001907348633,4.3000001907348633,null,null,4.3000001907348633]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.995,null,0.995,null,0.995,null,0.995,null,null,null,null,0.995,null,0.999,null,0.999,null,null,null,null,null,0.999,0.999,null,null,0.999]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,24,null,24,null,24,null,24,null,null,null,null,24,null,27.799999237060547,null,27.799999237060547,null,null,null,null,null,27.799999237060547,27.799999237060547,null,null,27.799999237060547]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,4.5999999046325684,null,4.5999999046325684,null,4.5999999046325684,null,4.5999999046325684,null,null,null,null,4.5999999046325684,null,4.0999999046325684,null,4.0999999046325684,null,null,null,null,null,4.0999999046325684,4.0999999046325684,null,null,4.0999999046325684]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.2,null,0.2,null,0.2,null,0.2,null,null,null,null,0.2,null,0.2,null,0.2,null,null,null,null,null,0.2,0.2,null,null,0.2]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"24.5",null,"24.5",null,"24.5",null,"24.5",null,null,null,null,"24.5",null,"24.5",null,"24.5",null,null,null,null,null,"24.5","24.5",null,null,"24.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,2.5,null,2.5,null,2.5,null,2.5,null,null,null,null,2.5,null,2.5,null,2.5,null,null,null,null,null,2.5,2.5,null,null,2.5]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,10,null,10,null,10,null,10,null,null,null,null,10,null,10,null,10,null,null,null,null,null,10,10,null,null,10]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"AITK","index":4,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"AITK - Aitkenvale (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"TMES - Townsville Mesh"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Nth Queensland"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/11kV 15/20/25MVA ONAN/ONAF/ODAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.3%, 2020 S -0.1% W -0.1%2021 S -0.2% W -0.2%2022 S -0.7% W -0.7%2023 S -1.1% W -1.1"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"22.4 MVA on 20/02/2019 at 16:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,61.599998474121094,null,61.599998474121094,null,61.599998474121094,null,61.599998474121094,null,null,null,null,61.599998474121094,null,64.699996948242188,null,64.699996948242188,null,null,null,null,null,64.699996948242188,64.699996948242188,null,null,64.699996948242188]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,23.700000762939453,null,23.5,null,23.100000381469727,null,22.899999618530273,null,null,null,null,22.799999237060547,null,12.5,null,12.5,null,null,null,null,null,12.399999618530273,12.300000190734863,null,null,12.199999809265137]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.998,null,0.998,null,0.998,null,0.998,null,null,null,null,0.998,null,0.999,null,0.999,null,null,null,null,null,0.999,0.999,null,null,1]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,34.299999237060547,null,34.299999237060547,null,34.299999237060547,null,34.299999237060547,null,null,null,null,34.299999237060547,null,35.799999237060547,null,35.799999237060547,null,null,null,null,null,35.799999237060547,35.799999237060547,null,null,35.799999237060547]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,20.700000762939453,null,20.5,null,20.200000762939453,null,20,null,null,null,null,19.899999618530273,null,12,null,12,null,null,null,null,null,11.899999618530273,11.800000190734863,null,null,11.699999809265137]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,1,null,1,null,1,null,1,null,null,null,null,1,null,0.6,null,0.6,null,null,null,null,null,0.6,0.6,null,null,0.6]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"8.5",null,"8.5",null,"8.5",null,"8.5",null,null,null,null,"8.5",null,"8.5",null,"8.5",null,null,null,null,null,"8.5","8.5",null,null,"8.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"ALLO","index":5,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"ALLO - Allora (33/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T058 - Warwick BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is South West"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x33/11kV 3MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.4%, 2020 S -0.0% W -0.0%2021 S -0.1% W -0.1%2022 S 0.3% W 0.3%, 2023 S 0.0% W 0.0%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"4.9 MVA on 19/01/2019 at 19:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,7.3000001907348633,null,7.3000001907348633,null,7.3000001907348633,null,7.3000001907348633,null,null,null,null,7.3000001907348633,null,7.9000000953674316,null,7.9000000953674316,null,null,null,null,null,7.9000000953674316,7.9000000953674316,null,null,7.9000000953674316]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,6,null,5.9000000953674316,null,5.9000000953674316,null,5.9000000953674316,null,null,null,null,6,null,5,null,5,null,null,null,null,null,4.9000000953674316,4.9000000953674316,null,null,5]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.91400000000000003,null,0.91400000000000003,null,0.91400000000000003,null,0.91400000000000003,null,null,null,null,0.91400000000000003,null,0.95199999999999996,null,0.95199999999999996,null,null,null,null,null,0.95199999999999996,0.95199999999999996,null,null,0.95199999999999996]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,4.1999998092651367,null,4.1999998092651367,null,4.1999998092651367,null,4.1999998092651367,null,null,null,null,4.1999998092651367,null,4.4000000953674316,null,4.4000000953674316,null,null,null,null,null,4.4000000953674316,4.4000000953674316,null,null,4.4000000953674316]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,5.1999998092651367,null,5.1999998092651367,null,5.1999998092651367,null,5.1999998092651367,null,null,null,null,5.1999998092651367,null,4.6999998092651367,null,4.6999998092651367,null,null,null,null,null,4.5999999046325684,4.6999998092651367,null,null,4.6999998092651367]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.3,null,0.3,null,0.3,null,0.3,null,null,null,null,0.3,null,0.2,null,0.2,null,null,null,null,null,0.2,0.2,null,null,0.2]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"10",null,"10",null,"10",null,"10",null,null,null,null,"10",null,"10",null,"10",null,null,null,null,null,"10","10",null,null,"10"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,1,null,1,null,1,null,1,null,null,null,null,1,null,0.3,null,0.3,null,null,null,null,null,0.2,0.3,null,null,0.3]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,10,null,10,null,10,null,10,null,null,null,null,10,null,10,null,10,null,null,null,null,null,10,10,null,null,10]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"ALSH","index":6,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"ALSH - Alan Sherriff (132/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"QASF - Alan Sherriff TCP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Nth Queensland"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x132/11kV 18/22.5/30MVA ONAN/OFAF/ODAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.2%, 2020 S -0.0% W -0.0%2021 S -0.2% W -0.2%2022 S -0.5% W -0.5%2023 S -1.0% W -1.0"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"33.1 MVA on 27/11/2018 at 16:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,70,null,70,null,70,null,70,null,null,null,null,70,null,73.5,null,73.5,null,null,null,null,null,73.5,73.5,null,null,73.5]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,37.200000762939453,null,36.900001525878906,null,36.400001525878906,null,36,null,null,null,null,35.900001525878906,null,16.899999618530273,null,16.899999618530273,null,null,null,null,null,16.700000762939453,16.600000381469727,null,null,16.5]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.95199999999999996,null,0.95199999999999996,null,0.95199999999999996,null,0.95199999999999996,null,null,null,null,0.95199999999999996,null,0.95699999999999996,null,0.95699999999999996,null,null,null,null,null,0.95699999999999996,0.95699999999999996,null,null,0.95699999999999996]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,38.5,null,38.5,null,38.5,null,38.5,null,null,null,null,38.5,null,40.299999237060547,null,40.299999237060547,null,null,null,null,null,40.299999237060547,40.299999237060547,null,null,40.299999237060547]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,31.299999237060547,null,31.100000381469727,null,30.600000381469727,null,30.299999237060547,null,null,null,null,30.299999237060547,null,16.100000381469727,null,16.100000381469727,null,null,null,null,null,16,15.899999618530273,null,null,15.800000190734863]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,1.6,null,1.6,null,1.5,null,1.5,null,null,null,null,1.5,null,0.8,null,0.8,null,null,null,null,null,0.8,0.8,null,null,0.8]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"4",null,"4",null,"4",null,"4",null,null,null,null,"4",null,"4",null,"4",null,null,null,null,null,"4","4",null,null,"4"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"ALST","index":7,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"ALST - Alfred Street (33/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T038 - Mackay BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Mackay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x33/11kV 35/40MVA ONAN/ONAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -1.6%, 2020 S -0.8% W -0.8%2021 S -0.8% W -0.8%2022 S -0.7% W -0.7%2023 S -1.0% W -1.0"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"22.9 MVA on 28/11/2018 at 15:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,90.699996948242188,null,90.699996948242188,null,90.699996948242188,null,90.699996948242188,null,null,null,null,90.699996948242188,null,93.699996948242188,null,93.699996948242188,null,null,null,null,null,93.699996948242188,93.699996948242188,null,null,93.699996948242188]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,24.100000381469727,null,23.799999237060547,null,23.399999618530273,null,23.200000762939453,null,null,null,null,23.200000762939453,null,14.100000381469727,null,14,null,null,null,null,null,13.800000190734863,13.699999809265137,null,null,13]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.998,null,0.998,null,0.997,null,0.997,null,null,null,null,0.997,null,0.999,null,1,null,null,null,null,null,1,1,null,null,1]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,48,null,48,null,48,null,48,null,null,null,null,48,null,50.400001525878906,null,50.400001525878906,null,null,null,null,null,50.400001525878906,50.400001525878906,null,null,50.400001525878906]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,22.399999618530273,null,22.100000381469727,null,21.700000762939453,null,21.600000381469727,null,null,null,null,21.5,null,13.5,null,13.399999618530273,null,null,null,null,null,13.199999809265137,13.100000381469727,null,null,13.399999618530273]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,1.1000000000000001,null,1.1000000000000001,null,1.1000000000000001,null,1.1000000000000001,null,null,null,null,1.1000000000000001,null,0.7,null,0.7,null,null,null,null,null,0.7,0.7,null,null,0.7]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"18",null,"18",null,"18",null,"18",null,null,null,null,"18",null,"18",null,"18",null,null,null,null,null,"18","18",null,null,"18"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"ATHE","index":8,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"ATHE - Atherton (66/22kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T055 - Turkinje 66kV BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Far North"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/22kV 24/30/40MVA ONAN/ODAN/ODAF;1x66/22kV 24/30/40MVA ONAN/ONAF/ONAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 1.7 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.2%, 2020 S 0.5% W 0.5%, 2021 S 0.4% W 0.4%, 2022 S 0.4% W 0.4%, 2023 S 0.2% W 0.2%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"25.5 MVA on 19/06/2018 at 18:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,88.099998474121094,null,88.099998474121094,null,88.099998474121094,null,88.099998474121094,null,null,null,null,88.099998474121094,null,97.400001525878906,null,97.400001525878906,null,null,null,null,null,97.400001525878906,97.400001525878906,null,null,97.400001525878906]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0.80000001192092896,null,0.80000001192092896,null,0.80000001192092896,null,0.80000001192092896,null,null,null,null,0.80000001192092896,null,1,null,1,null,null,null,null,null,1,1,null,null,1]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,24.799999237060547,null,24.799999237060547,null,24.600000381469727,null,24.700000762939453,null,null,null,null,24.899999618530273,null,25.399999618530273,null,25.5,null,null,null,null,null,25.5,25.5,null,null,25.700000762939453]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,1,null,1,null,0.999,null,1,null,null,null,null,1,null,1,null,1,null,null,null,null,null,1,1,null,null,1]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,50.799999237060547,null,50.799999237060547,null,50.799999237060547,null,50.799999237060547,null,null,null,null,50.799999237060547,null,53.5,null,53.5,null,null,null,null,null,53.5,53.5,null,null,53.5]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,23.799999237060547,null,23.799999237060547,null,23.700000762939453,null,23.799999237060547,null,null,null,null,24,null,24.399999618530273,null,24.5,null,null,null,null,null,24.5,24.600000381469727,null,null,24.799999237060547]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,1.2,null,1.2,null,1.2,null,1.2,null,null,null,null,1.2,null,1.2,null,1.2,null,null,null,null,null,1.2,1.2,null,null,1.2]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"10.5",null,"10.5",null,"10.5",null,"10.5",null,null,null,null,"10.5",null,"10.5",null,"10.5",null,null,null,null,null,"10.5","10.5",null,null,"10.5"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"AWOO","index":9,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"AWOO - Awoonga (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T019 - Gladstone South BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Capricornia"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/11kV 7.5/10MVA ON/OB"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 1.1 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.0%, 2020 S 0.2% W 0.2%, 2021 S 0.2% W 0.2%, 2022 S 0.3% W 0.3%, 2023 S 0.2% W 0.2%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"7 MVA on 02/12/2018 at 19:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,24.399999618530273,null,24.399999618530273,null,24.399999618530273,null,24.399999618530273,null,null,null,null,24.399999618530273,null,25.700000762939453,null,25.700000762939453,null,null,null,null,null,25.700000762939453,25.700000762939453,null,null,25.700000762939453]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,1.1000000238418579,null,1.1000000238418579,null,1.1000000238418579,null,1.1000000238418579,null,null,null,null,1.1000000238418579,null,1.1000000238418579,null,1.1000000238418579,null,null,null,null,null,1.1000000238418579,1.1000000238418579,null,null,1.1000000238418579]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,7.6999998092651367,null,7.5999999046325684,null,7.5999999046325684,null,7.5999999046325684,null,null,null,null,7.6999998092651367,null,5.9000000953674316,null,5.9000000953674316,null,null,null,null,null,5.9000000953674316,5.9000000953674316,null,null,6]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.94499999999999995,null,0.94499999999999995,null,0.94499999999999995,null,0.94499999999999995,null,null,null,null,0.94499999999999995,null,0.93600000000000005,null,0.93600000000000005,null,null,null,null,null,0.93600000000000005,0.93600000000000005,null,null,0.93600000000000005]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,14,null,14,null,14,null,14,null,null,null,null,14,null,14.5,null,14.5,null,null,null,null,null,14.5,14.5,null,null,14.5]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,7.5,null,7.5,null,7.4000000953674316,null,7.4000000953674316,null,null,null,null,7.5,null,5.8000001907348633,null,5.8000001907348633,null,null,null,null,null,5.8000001907348633,5.8000001907348633,null,null,5.9000000953674316]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.4,null,0.4,null,0.4,null,0.4,null,null,null,null,0.4,null,0.3,null,0.3,null,null,null,null,null,0.3,0.3,null,null,0.3]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"2",null,"2",null,"2",null,"2",null,null,null,null,"2",null,"2",null,"2",null,null,null,null,null,"2","2",null,null,"2"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"AYRZ","index":10,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"AYRZ - Ayr (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T193 - Clare South BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Nth Queensland"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/11kV 7.5/10MVA ON/OB;1x66/11kV 7.5/10MVA ONAN/ONAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.4%, 2020 S -0.0% W -0.0%2021 S -0.2% W -0.2%2022 S -0.3% W -0.3%2023 S -0.5% W -0.5"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"9.3 MVA on 24/03/2019 at 11:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,23.899999618530273,null,23.899999618530273,null,23.899999618530273,null,23.899999618530273,null,null,null,null,23.899999618530273,null,25.399999618530273,null,25.399999618530273,null,null,null,null,null,25.399999618530273,25.399999618530273,null,null,25.399999618530273]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,9.6000003814697266,null,9.6000003814697266,null,9.3999996185302734,null,9.3999996185302734,null,null,null,null,9.3999996185302734,null,5.4000000953674316,null,5.4000000953674316,null,null,null,null,null,5.4000000953674316,5.3000001907348633,null,null,5.3000001907348633]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.98599999999999999,null,0.98599999999999999,null,0.98699999999999999,null,0.98699999999999999,null,null,null,null,0.98699999999999999,null,0.89,null,0.89,null,null,null,null,null,0.89,0.89,null,null,0.89]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,13.600000381469727,null,13.600000381469727,null,13.600000381469727,null,13.600000381469727,null,null,null,null,13.600000381469727,null,14.199999809265137,null,14.199999809265137,null,null,null,null,null,14.199999809265137,14.199999809265137,null,null,14.199999809265137]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,9.3999996185302734,null,9.3000001907348633,null,9.1999998092651367,null,9.1999998092651367,null,null,null,null,9.1999998092651367,null,5.0999999046325684,null,5.0999999046325684,null,null,null,null,null,5,5,null,null,5]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.5,null,0.5,null,0.5,null,0.5,null,null,null,null,0.5,null,0.3,null,0.3,null,null,null,null,null,0.3,0.3,null,null,0.3]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"8",null,"8",null,"8",null,"8",null,null,null,null,"8",null,"8",null,"8",null,null,null,null,null,"8","8",null,null,"8"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"BALB","index":11,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"BALB - Balberra (33/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T065 - Alligator Creek BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Mackay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x33/11kV 5MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.0%, 2020 S 0.2% W 0.2%, 2021 S 0.2% W 0.2%, 2022 S 0.0% W 0.0%, 2023 S 0.0% W 0.0%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"2.8 MVA on 26/11/2018 at 19:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,7,null,7,null,7,null,7,null,null,null,null,7,null,7.5,null,7.5,null,null,null,null,null,7.5,7.5,null,null,7.5]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,3.4000000953674316,null,3.4000000953674316,null,3.4000000953674316,null,3.4000000953674316,null,null,null,null,3.4000000953674316,null,2.0999999046325684,null,2.0999999046325684,null,null,null,null,null,2.0999999046325684,2.0999999046325684,null,null,2.0999999046325684]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.93100000000000005,null,0.93100000000000005,null,0.93100000000000005,null,0.93100000000000005,null,null,null,null,0.93100000000000005,null,0.93600000000000005,null,0.93600000000000005,null,null,null,null,null,0.93600000000000005,0.93600000000000005,null,null,0.93600000000000005]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,2.7000000476837158,null,2.7000000476837158,null,2.7000000476837158,null,2.7000000476837158,null,null,null,null,2.7000000476837158,null,1.8999999761581421,null,1.8999999761581421,null,null,null,null,null,1.8999999761581421,1.8999999761581421,null,null,1.8999999761581421]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.1,null,0.1,null,0.1,null,0.1,null,null,null,null,0.1,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"3.5",null,"3.5",null,"3.5",null,"3.5",null,null,null,null,"3.5",null,"3.5",null,"3.5",null,null,null,null,null,"3.5","3.5",null,null,"3.5"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,2.7,null,2.7,null,2.7,null,2.7,null,null,null,null,2.7,null,1.9,null,1.9,null,null,null,null,null,1.9,1.9,null,null,1.9]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,1.8999999761581421,null,1.8999999761581421,null,1.8999999761581421,null,1.8999999761581421,null,null,null,null,1.8999999761581421,null,1.8999999761581421,null,1.8999999761581421,null,null,null,null,null,1.8999999761581421,1.8999999761581421,null,null,1.8999999761581421]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,2,null,2,null,2,null,2,null,null,null,null,2,null,2,null,2,null,null,null,null,null,2,2,null,null,2]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"BAMB","index":12,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"BAMB - Bambaroo (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T047 - Ingham BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Nth Queensland"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/11kV 1.5MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.3%, 2020 S -0.2% W -0.2%2021 S -0.2% W -0.2%2022 S -0.4% W -0.4%2023 S -0.4% W -0.4"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"0.7 MVA on 28/08/2018 at 18:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,2.2000000476837158,null,2.2000000476837158,null,2.2000000476837158,null,2.2000000476837158,null,null,null,null,2.2000000476837158,null,2.2000000476837158,null,2.2000000476837158,null,null,null,null,null,2.2000000476837158,2.2000000476837158,null,null,2.2000000476837158]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,0.5,null,0.5,null,0.5,null,0.5,null,null,null,null,0.5,null,0.69999998807907104,null,0.69999998807907104,null,null,null,null,null,0.60000002384185791,0.60000002384185791,null,null,0.60000002384185791]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.94599999999999995,null,0.94599999999999995,null,0.94599999999999995,null,0.94599999999999995,null,null,null,null,0.94599999999999995,null,0.91700000000000004,null,0.91700000000000004,null,null,null,null,null,0.91700000000000004,0.91700000000000004,null,null,0.91700000000000004]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,0.40000000596046448,null,0.40000000596046448,null,0.40000000596046448,null,0.40000000596046448,null,null,null,null,0.40000000596046448,null,0.60000002384185791,null,0.60000002384185791,null,null,null,null,null,0.60000002384185791,0.60000002384185791,null,null,0.60000002384185791]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"23.5",null,"23.5",null,"23.5",null,"23.5",null,null,null,null,"23.5",null,"23.5",null,"23.5",null,null,null,null,null,"23.5","23.5",null,null,"23.5"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,0.4,null,0.4,null,0.4,null,0.4,null,null,null,null,0.4,null,0.6,null,0.6,null,null,null,null,null,0.6,0.6,null,null,0.6]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,1,null,1,null,1,null,1,null,null,null,null,1,null,1,null,1,null,null,null,null,null,1,1,null,null,1]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"BARC","index":13,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"BARC - Barcaldine (66/22kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T072 - Barcaldine BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Capricornia"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/22kV 8/10MVA ONAN/ONAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 28.4 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.9%, 2020 S -0.7% W -0.7%2021 S -0.9% W -0.9%2022 S -0.4% W -0.4%2023 S -0.6% W -0.6"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"7.1 MVA on 11/03/2019 at 19:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,25.799999237060547,null,25.799999237060547,null,25.799999237060547,null,25.799999237060547,null,null,null,null,25.799999237060547,null,30,null,30,null,null,null,null,null,30,30,null,null,30]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0.10000000149011612,null,0.10000000149011612,null,0.10000000149011612,null,0.10000000149011612,null,null,null,null,0.10000000149011612,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,7.5,null,7.4000000953674316,null,7.3000001907348633,null,7.1999998092651367,null,null,null,null,7.1999998092651367,null,6.1999998092651367,null,6.0999999046325684,null,null,null,null,null,6,6,null,null,6]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,1,null,1,null,1,null,1,null,null,null,null,1,null,0.997,null,0.997,null,null,null,null,null,0.997,0.997,null,null,0.997]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,14.199999809265137,null,14.199999809265137,null,14.199999809265137,null,14.199999809265137,null,null,null,null,14.199999809265137,null,15,null,15,null,null,null,null,null,15,15,null,null,15]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,7.3000001907348633,null,7.1999998092651367,null,7.0999999046325684,null,7,null,null,null,null,7,null,5.5999999046325684,null,5.5999999046325684,null,null,null,null,null,5.5,5.5,null,null,5.5]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.4,null,0.4,null,0.4,null,0.4,null,null,null,null,0.4,null,0.3,null,0.3,null,null,null,null,null,0.3,0.3,null,null,0.3]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"7",null,"7",null,"7",null,"7",null,null,null,null,"7",null,"7",null,"7",null,null,null,null,null,"7","7",null,null,"7"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"BARG","index":14,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"BARG - Bargara (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T020 - Bundaberg BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Wide Bay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/11kV 15/18/25MVA ONAN/ODAN/ODAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 1.8%, 2020 S 1.9% W 1.9%, 2021 S 1.8% W 1.8%, 2022 S 1.5% W 1.5%, 2023 S 1.2% W 1.2%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"13 MVA on 12/02/2019 at 18:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,69.900001525878906,null,69.900001525878906,null,69.900001525878906,null,69.900001525878906,null,null,null,null,69.900001525878906,null,74.800003051757813,null,74.800003051757813,null,null,null,null,null,74.800003051757813,74.800003051757813,null,null,74.800003051757813]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,14.899999618530273,null,15.100000381469727,null,15.199999809265137,null,15.399999618530273,null,null,null,null,15.699999809265137,null,13.699999809265137,null,13.899999618530273,null,null,null,null,null,14.100000381469727,14.300000190734863,null,null,14.600000381469727]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.999,null,0.999,null,0.999,null,0.999,null,null,null,null,0.999,null,0.99,null,0.99,null,null,null,null,null,0.99,0.99,null,null,0.99]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,37.400001525878906,null,37.400001525878906,null,37.400001525878906,null,37.400001525878906,null,null,null,null,37.400001525878906,null,37.400001525878906,null,37.400001525878906,null,null,null,null,null,37.400001525878906,37.400001525878906,null,null,37.400001525878906]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,14,null,14.199999809265137,null,14.199999809265137,null,14.399999618530273,null,null,null,null,14.699999809265137,null,12.800000190734863,null,13,null,null,null,null,null,13.199999809265137,13.399999618530273,null,null,13.600000381469727]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.7,null,0.7,null,0.7,null,0.7,null,null,null,null,0.7,null,0.6,null,0.7,null,null,null,null,null,0.7,0.7,null,null,0.7]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"19.5",null,"19.5",null,"19.5",null,"19.5",null,null,null,null,"19.5",null,"19.5",null,"19.5",null,null,null,null,null,"19.5","19.5",null,null,"19.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"BARR","index":15,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"BARR - Barratta (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T193 - Clare South BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Nth Queensland"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1xBARR TX NO 1-66/11KV TRANSF 1"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -1.4%, 2020 S -0.0% W -0.0%2021 S -0.2% W -0.2%2022 S -0.3% W -0.3%2023 S -0.4% W -0.4"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"2.7 MVA on 22/11/2018 at 17:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,4,null,4,null,4,null,4,null,null,null,null,4,null,4,null,4,null,null,null,null,null,4,4,null,null,4]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,2.7999999523162842,null,2.9000000953674316,null,2.7999999523162842,null,2.7999999523162842,null,null,null,null,2.7999999523162842,null,1.3999999761581421,null,1.3999999761581421,null,null,null,null,null,1.3999999761581421,1.3999999761581421,null,null,1.3999999761581421]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.86,null,0.86,null,0.86,null,0.86,null,null,null,null,0.86,null,0.86599999999999999,null,0.86599999999999999,null,null,null,null,null,0.86599999999999999,0.86599999999999999,null,null,0.86599999999999999]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,2.7999999523162842,null,2.7999999523162842,null,2.7999999523162842,null,2.7999999523162842,null,null,null,null,2.7999999523162842,null,1.2999999523162842,null,1.2999999523162842,null,null,null,null,null,1.2999999523162842,1.2999999523162842,null,null,1.2999999523162842]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.1,null,0.1,null,0.1,null,0.1,null,null,null,null,0.1,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"41.5",null,"41.5",null,"41.5",null,"41.5",null,null,null,null,"41.5",null,"41.5",null,"41.5",null,null,null,null,null,"41.5","41.5",null,null,"41.5"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,2.8,null,2.8,null,2.8,null,2.8,null,null,null,null,2.8,null,1.3,null,1.3,null,null,null,null,null,1.3,1.3,null,null,1.3]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0.5,null,0.5,null,0.5,null,0.5,null,null,null,null,0.5,null,0.5,null,0.5,null,null,null,null,null,0.5,0.5,null,null,0.5]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,2.4000000953674316,null,2.4000000953674316,null,2.4000000953674316,null,2.4000000953674316,null,null,null,null,2.4000000953674316,null,2.4000000953674316,null,2.4000000953674316,null,null,null,null,null,2.4000000953674316,2.4000000953674316,null,null,2.4000000953674316]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"BEGA","index":16,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"BEGA - Belgian Gardens (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"TMES - Townsville Mesh"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Nth Queensland"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/11kV 19/26/32MVA ONAN/ODAN/ODAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.9%, 2020 S 1.0% W 1.0%, 2021 S 1.0% W 1.0%, 2022 S 0.9% W 0.9%, 2023 S 0.8% W 0.8%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"15.5 MVA on 20/02/2019 at 19:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,73.900001525878906,null,73.900001525878906,null,73.900001525878906,null,73.900001525878906,null,null,null,null,73.900001525878906,null,76.599998474121094,null,76.599998474121094,null,null,null,null,null,76.599998474121094,76.599998474121094,null,null,76.599998474121094]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,17,null,17.100000381469727,null,17.100000381469727,null,17.200000762939453,null,null,null,null,17.5,null,7,null,7,null,null,null,null,null,7.0999999046325684,7.0999999046325684,null,null,7.1999998092651367]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.98799999999999999,null,0.98799999999999999,null,0.98799999999999999,null,0.98799999999999999,null,null,null,null,0.98799999999999999,null,0.98699999999999999,null,0.98699999999999999,null,null,null,null,null,0.98699999999999999,0.98699999999999999,null,null,0.98699999999999999]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,40.900001525878906,null,40.900001525878906,null,40.900001525878906,null,40.900001525878906,null,null,null,null,40.900001525878906,null,42.200000762939453,null,42.200000762939453,null,null,null,null,null,42.200000762939453,42.200000762939453,null,null,42.200000762939453]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,15.300000190734863,null,15.300000190734863,null,15.300000190734863,null,15.5,null,null,null,null,15.699999809265137,null,6.6999998092651367,null,6.6999998092651367,null,null,null,null,null,6.8000001907348633,6.8000001907348633,null,null,6.9000000953674316]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.8,null,0.8,null,0.8,null,0.8,null,null,null,null,0.8,null,0.3,null,0.3,null,null,null,null,null,0.3,0.3,null,null,0.3]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"8",null,"8",null,"8",null,"8",null,null,null,null,"8",null,"8",null,"8",null,null,null,null,null,"8","8",null,null,"8"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"BERS","index":17,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"BERS - Berserker (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"RMES - Rockhampton Mesh"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Capricornia"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/11kV 19/26/32MVA ONAN/ODAN/ODAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.3%, 2020 S -0.2% W -0.2%2021 S -0.3% W -0.3%2022 S -0.5% W -0.5%2023 S -0.8% W -0.8"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"21.5 MVA on 03/12/2018 at 15:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,78.5,null,78.5,null,78.5,null,78.5,null,null,null,null,78.5,null,88,null,88,null,null,null,null,null,88,88,null,null,88]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,23.600000381469727,null,23.5,null,23.100000381469727,null,22.899999618530273,null,null,null,null,22.899999618530273,null,11.199999809265137,null,11.100000381469727,null,null,null,null,null,11.100000381469727,11,null,null,10.899999618530273]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.99099999999999999,null,0.99099999999999999,null,0.99099999999999999,null,0.99199999999999999,null,null,null,null,0.99199999999999999,null,0.997,null,0.997,null,null,null,null,null,0.996,0.996,null,null,0.996]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,42.700000762939453,null,42.700000762939453,null,42.700000762939453,null,42.700000762939453,null,null,null,null,42.700000762939453,null,46.5,null,46.5,null,null,null,null,null,46.5,46.5,null,null,46.5]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,21.600000381469727,null,21.5,null,21.100000381469727,null,21,null,null,null,null,21,null,10.800000190734863,null,10.800000190734863,null,null,null,null,null,10.699999809265137,10.699999809265137,null,null,10.600000381469727]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,1.1000000000000001,null,1.1000000000000001,null,1.1000000000000001,null,1.1000000000000001,null,null,null,null,1.1000000000000001,null,0.5,null,0.5,null,null,null,null,null,0.5,0.5,null,null,0.5]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"7.5",null,"7.5",null,"7.5",null,"7.5",null,null,null,null,"7.5",null,"7.5",null,"7.5",null,null,null,null,null,"7.5","7.5",null,null,"7.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"BEWE","index":18,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"BEWE - Bedford Weir (66/22kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T032 - Blackwater BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Capricornia"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/22kV 10MVA ONAN;1x66/22kV 7.5/10MVA ON/OB"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.6%, 2020 S -0.5% W -0.5%2021 S -0.6% W -0.6%2022 S -0.5% W -0.5%2023 S -0.6% W -0.6"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"8 MVA on 13/02/2019 at 19:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,20.899999618530273,null,20.899999618530273,null,20.899999618530273,null,20.899999618530273,null,null,null,null,20.899999618530273,null,23.299999237060547,null,23.299999237060547,null,null,null,null,null,23.299999237060547,23.299999237060547,null,null,23.299999237060547]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,8.6999998092651367,null,8.6000003814697266,null,8.5,null,8.5,null,null,null,null,8.5,null,6.1999998092651367,null,6.1999998092651367,null,null,null,null,null,6.0999999046325684,6.0999999046325684,null,null,6.0999999046325684]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.95899999999999996,null,0.95899999999999996,null,0.95899999999999996,null,0.95899999999999996,null,null,null,null,0.95899999999999996,null,0.95199999999999996,null,0.95199999999999996,null,null,null,null,null,0.95199999999999996,0.95199999999999996,null,null,0.95199999999999996]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,12,null,12,null,12,null,12,null,null,null,null,12,null,12.899999618530273,null,12.899999618530273,null,null,null,null,null,12.899999618530273,12.899999618530273,null,null,12.899999618530273]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,8.1000003814697266,null,8,null,7.9000000953674316,null,7.8000001907348633,null,null,null,null,7.8000001907348633,null,5.8000001907348633,null,5.8000001907348633,null,null,null,null,null,5.6999998092651367,5.6999998092651367,null,null,5.6999998092651367]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.4,null,0.4,null,0.4,null,0.4,null,null,null,null,0.4,null,0.3,null,0.3,null,null,null,null,null,0.3,0.3,null,null,0.3]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"5.5",null,"5.5",null,"5.5",null,"5.5",null,null,null,null,"5.5",null,"5.5",null,"5.5",null,null,null,null,null,"5.5","5.5",null,null,"5.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"BILO","index":19,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"BILO - Biloela (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T026 - Biloela BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Capricornia"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/11kV 15/20MVA ONAN/ONAF;1x66/11kV 25/32MVA ONAN/ONAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -2.3%, 2020 S -1.2% W -1.2%2021 S -1.5% W -1.5%2022 S -1.3% W -1.3%2023 S -1.8% W -1.8"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"17.5 MVA on 20/02/2019 at 16:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,47.299999237060547,null,47.299999237060547,null,47.299999237060547,null,47.299999237060547,null,null,null,null,47.299999237060547,null,55,null,55,null,null,null,null,null,55,55,null,null,55]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,19.200000762939453,null,18.899999618530273,null,18.399999618530273,null,18.100000381469727,null,null,null,null,18,null,11.699999809265137,null,11.600000381469727,null,null,null,null,null,11.399999618530273,11.199999809265137,null,null,11.100000381469727]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.94499999999999995,null,0.94499999999999995,null,0.94499999999999995,null,0.94499999999999995,null,null,null,null,0.94499999999999995,null,0.96399999999999997,null,0.96399999999999997,null,null,null,null,null,0.96499999999999997,0.96499999999999997,null,null,0.96499999999999997]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,27.200000762939453,null,27.200000762939453,null,27.200000762939453,null,27.200000762939453,null,null,null,null,27.200000762939453,null,29.899999618530273,null,29.899999618530273,null,null,null,null,null,29.899999618530273,29.899999618530273,null,null,29.899999618530273]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,17.299999237060547,null,16.899999618530273,null,16.5,null,16.299999237060547,null,null,null,null,16.200000762939453,null,11.199999809265137,null,11.100000381469727,null,null,null,null,null,10.899999618530273,10.699999809265137,null,null,10.600000381469727]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.9,null,0.8,null,0.8,null,0.8,null,null,null,null,0.8,null,0.6,null,0.6,null,null,null,null,null,0.5,0.5,null,null,0.5]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"9.5",null,"9.5",null,"9.5",null,"9.5",null,null,null,null,"9.5",null,"9.5",null,"9.5",null,null,null,null,null,"9.5","9.5",null,null,"9.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,6.0999999046325684,null,6.0999999046325684,null,6.0999999046325684,null,6.0999999046325684,null,null,null,null,6.0999999046325684,null,6.0999999046325684,null,6.0999999046325684,null,null,null,null,null,6.0999999046325684,6.0999999046325684,null,null,6.0999999046325684]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,3.2999999523162842,null,3.2999999523162842,null,3.2999999523162842,null,3.2999999523162842,null,null,null,null,3.2999999523162842,null,3.2999999523162842,null,3.2999999523162842,null,null,null,null,null,3.2999999523162842,3.2999999523162842,null,null,3.2999999523162842]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,1.8999999761581421,null,1.8999999761581421,null,1.8999999761581421,null,1.8999999761581421,null,null,null,null,1.8999999761581421,null,1.8999999761581421,null,1.8999999761581421,null,null,null,null,null,1.8999999761581421,1.8999999761581421,null,null,1.8999999761581421]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"BING","index":20,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"BING - Bingegang (66/22kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T032 - Blackwater BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Capricornia"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/22kV 5MVA ON"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -1.7%, 2020 S -0.7% W -0.7%2021 S -0.8% W -0.8%2022 S -0.4% W -0.4%2023 S -0.5% W -0.5"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"2.2 MVA on 03/12/2018 at 14:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,10,null,10,null,10,null,10,null,null,null,null,10,null,12,null,12,null,null,null,null,null,12,12,null,null,12]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,2.2999999523162842,null,2.2999999523162842,null,2.2000000476837158,null,2.2000000476837158,null,null,null,null,2.2000000476837158,null,1.2000000476837158,null,1.1000000238418579,null,null,null,null,null,1.1000000238418579,1.2000000476837158,null,null,1.2000000476837158]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.96899999999999997,null,0.96899999999999997,null,0.96899999999999997,null,0.96899999999999997,null,null,null,null,0.96899999999999997,null,0.98599999999999999,null,0.98699999999999999,null,null,null,null,null,0.98699999999999999,0.98599999999999999,null,null,0.98599999999999999]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,6.5999999046325684,null,6.5999999046325684,null,6.5999999046325684,null,6.5999999046325684,null,null,null,null,6.5999999046325684,null,7.0999999046325684,null,7.0999999046325684,null,null,null,null,null,7.0999999046325684,7.0999999046325684,null,null,7.0999999046325684]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,2.2000000476837158,null,2.2000000476837158,null,2.2000000476837158,null,2.2000000476837158,null,null,null,null,2.2000000476837158,null,1.2000000476837158,null,1.1000000238418579,null,null,null,null,null,1.1000000238418579,1.1000000238418579,null,null,1.1000000238418579]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.1,null,0.1,null,0.1,null,0.1,null,null,null,null,0.1,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"26.5",null,"26.5",null,"26.5",null,"26.5",null,null,null,null,"26.5",null,"26.5",null,"26.5",null,null,null,null,null,"26.5","26.5",null,null,"26.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"BLAC","index":21,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"BLAC - Blackwater (11/22kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T032 - Blackwater BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Capricornia"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x11/22kV 7.5/10MVA ONAN/ONAF;2x132/22kV 160 MVA"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.5%, 2020 S -0.4% W -0.4%2021 S -0.4% W -0.4%2022 S -0.4% W -0.4%2023 S -0.4% W -0.4"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"10.3 MVA on 03/12/2018 at 19:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,20,null,20,null,20,null,20,null,20,null,20,20,null,20,null,20,null,20,null,20,null,20,20,null,20,20]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,11.5,null,11.399999618530273,null,11.300000190734863,null,11.199999809265137,null,null,null,null,11.300000190734863,null,7.1999998092651367,null,7.1999998092651367,null,null,null,null,null,7.0999999046325684,7.0999999046325684,null,null,7.0999999046325684]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.95599999999999996,null,0.95599999999999996,null,0.95599999999999996,null,0.95599999999999996,null,null,null,null,0.95599999999999996,null,0.97199999999999998,null,0.97199999999999998,null,null,null,null,null,0.97199999999999998,0.97199999999999998,null,null,0.97199999999999998]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,11,null,11,null,11,null,11,null,11,null,11,11,null,11,null,11,null,11,null,11,null,11,11,null,11,11]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,10.399999618530273,null,10.300000190734863,null,10.199999809265137,null,10.100000381469727,null,null,null,null,10.199999809265137,null,6.6999998092651367,null,6.6999998092651367,null,null,null,null,null,6.6999998092651367,6.5999999046325684,null,null,6.5999999046325684]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.5,null,0.5,null,0.5,null,0.5,null,null,null,null,0.5,null,0.3,null,0.3,null,null,null,null,null,0.3,0.3,null,null,0.3]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"3.5",null,"3.5",null,"3.5",null,"3.5",null,null,null,null,"3.5",null,"3.5",null,"3.5",null,null,null,null,null,"3.5","3.5",null,null,"3.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"BLAK","index":22,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"BLAK - Blackall (66/22kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T072 - Barcaldine BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Capricornia"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/22kV 5/6.25MVA ONAN/ONAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -1.1%, 2020 S -0.9% W -0.9%2021 S -1.0% W -1.0%2022 S -0.5% W -0.5%2023 S -0.7% W -0.7"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"4.1 MVA on 19/02/2019 at 18:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,13.899999618530273,null,13.899999618530273,null,13.899999618530273,null,13.899999618530273,null,null,null,null,13.899999618530273,null,16.5,null,16.5,null,null,null,null,null,16.5,16.5,null,null,16.5]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,4.9000000953674316,null,4.8000001907348633,null,4.8000001907348633,null,4.6999998092651367,null,null,null,null,4.6999998092651367,null,3.5999999046325684,null,3.5999999046325684,null,null,null,null,null,3.5,3.5,null,null,3.5]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.999,null,0.999,null,0.999,null,0.999,null,null,null,null,0.999,null,0.99,null,0.99,null,null,null,null,null,0.99,0.99,null,null,0.99]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,8.1000003814697266,null,8.1000003814697266,null,8.1000003814697266,null,8.1000003814697266,null,null,null,null,8.1000003814697266,null,9.3000001907348633,null,9.3000001907348633,null,null,null,null,null,9.3000001907348633,9.3000001907348633,null,null,9.3000001907348633]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,4.4000000953674316,null,4.3000001907348633,null,4.1999998092651367,null,4.1999998092651367,null,null,null,null,4.1999998092651367,null,3.2000000476837158,null,3.0999999046325684,null,null,null,null,null,3.0999999046325684,3.0999999046325684,null,null,3.0999999046325684]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.2,null,0.2,null,0.2,null,0.2,null,null,null,null,0.2,null,0.2,null,0.2,null,null,null,null,null,0.2,0.2,null,null,0.2]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"6",null,"6",null,"6",null,"6",null,null,null,null,"6",null,"6",null,"6",null,null,null,null,null,"6","6",null,null,"6"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"BLRI","index":23,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"BLRI - Black River (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"TMES - Townsville Mesh"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Nth Queensland"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/11kV 16/20MVA ONAN/ONAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 1.6%, 2020 S 1.6% W 1.6%, 2021 S 1.6% W 1.6%, 2022 S 2.4% W 2.4%, 2023 S 2.2% W 2.2%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"22.6 MVA on 21/02/2019 at 19:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,56,null,56,null,56,null,56,null,null,null,null,56,null,59.099998474121094,null,59.099998474121094,null,null,null,null,null,59.099998474121094,59.099998474121094,null,null,59.099998474121094]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,24.799999237060547,null,25.100000381469727,null,25.399999618530273,null,26,null,null,null,null,26.700000762939453,null,11.800000190734863,null,12,null,null,null,null,null,12.100000381469727,12.399999618530273,null,null,12.699999809265137]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.99399999999999999,null,0.99399999999999999,null,0.99399999999999999,null,0.99399999999999999,null,null,null,null,0.99399999999999999,null,0.996,null,0.996,null,null,null,null,null,0.996,0.996,null,null,0.996]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,29.899999618530273,null,29.899999618530273,null,29.899999618530273,null,29.899999618530273,null,null,null,null,29.899999618530273,null,29.899999618530273,null,29.899999618530273,null,null,null,null,null,29.899999618530273,29.899999618530273,null,null,29.899999618530273]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,21,null,21.200000762939453,null,21.5,null,22,null,null,null,null,22.600000381469727,null,11.100000381469727,null,11.300000190734863,null,null,null,null,null,11.399999618530273,11.699999809265137,null,null,12]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,1.1000000000000001,null,1.1000000000000001,null,1.1000000000000001,null,1.1000000000000001,null,null,null,null,1.1000000000000001,null,0.6,null,0.6,null,null,null,null,null,0.6,0.6,null,null,0.6]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"2",null,"2",null,"2",null,"2",null,null,null,null,"2",null,"2",null,"2",null,null,null,null,null,"2","2",null,null,"2"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"BLUE","index":24,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"BLUE - Bluewater (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"TMES - Townsville Mesh"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Nth Queensland"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/11kV 5MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 1.1%, 2020 S 1.1% W 1.1%, 2021 S 1.1% W 1.1%, 2022 S 0.3% W 0.3%, 2023 S 0.2% W 0.2%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"4 MVA on 26/11/2018 at 19:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,5.3000001907348633,null,5.3000001907348633,null,5.3000001907348633,null,5.3000001907348633,null,null,null,null,5.3000001907348633,null,5.5,null,5.5,null,null,null,null,null,5.5,5.5,null,null,5.5]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,4.5999999046325684,null,4.5999999046325684,null,4.5,null,4.5999999046325684,null,null,null,null,4.5999999046325684,null,2.7000000476837158,null,2.7000000476837158,null,null,null,null,null,2.7999999523162842,2.7999999523162842,null,null,2.7999999523162842]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.98799999999999999,null,0.98799999999999999,null,0.98799999999999999,null,0.98799999999999999,null,null,null,null,0.98799999999999999,null,0.98699999999999999,null,0.98699999999999999,null,null,null,null,null,0.98699999999999999,0.98699999999999999,null,null,0.98699999999999999]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,4,null,4,null,4,null,4,null,null,null,null,4,null,2.5999999046325684,null,2.5999999046325684,null,null,null,null,null,2.5999999046325684,2.5999999046325684,null,null,2.5999999046325684]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.2,null,0.2,null,0.2,null,0.2,null,null,null,null,0.2,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"7.5",null,"7.5",null,"7.5",null,"7.5",null,null,null,null,"7.5",null,"7.5",null,"7.5",null,null,null,null,null,"7.5","7.5",null,null,"7.5"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,4,null,4,null,4,null,4,null,null,null,null,4,null,2.6,null,2.6,null,null,null,null,null,2.6,2.6,null,null,2.6]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,3.5,null,3.5,null,3.5,null,3.5,null,null,null,null,3.5,null,3.5,null,3.5,null,null,null,null,null,3.5,3.5,null,null,3.5]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0.60000002384185791,null,0.60000002384185791,null,0.60000002384185791,null,0.60000002384185791,null,null,null,null,0.60000002384185791,null,0.60000002384185791,null,0.60000002384185791,null,null,null,null,null,0.60000002384185791,0.60000002384185791,null,null,0.60000002384185791]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"BODA","index":25,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"BODA - Boondooma Dam (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"H018 - Tarong BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Wide Bay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/11kV 4.1MVA ONAN;1x66/11kV 1MVA ONAN(Standby)"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.0%, 2020 S 0.0% W 0.0%, 2021 S 0.0% W 0.0%, 2022 S 0.0% W 0.0%, 2023 S 0.0% W 0.0%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"2.2 MVA on 14/07/2018 at 20:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,5.1999998092651367,null,5.1999998092651367,null,5.1999998092651367,null,5.1999998092651367,null,null,null,null,5.1999998092651367,null,5.5,null,5.5,null,null,null,null,null,5.5,5.5,null,null,5.5]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,2.2999999523162842,null,2.2999999523162842,null,2.2000000476837158,null,2.2000000476837158,null,null,null,null,2.2000000476837158,null,2.0999999046325684,null,2.0999999046325684,null,null,null,null,null,2.0999999046325684,2.0999999046325684,null,null,2.0999999046325684]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.91,null,0.91,null,0.91,null,0.91,null,null,null,null,0.91,null,0.89300000000000002,null,0.89300000000000002,null,null,null,null,null,0.89300000000000002,0.89300000000000002,null,null,0.89300000000000002]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,2.2000000476837158,null,2.2000000476837158,null,2.2000000476837158,null,2.2000000476837158,null,null,null,null,2.2000000476837158,null,2.0999999046325684,null,2.0999999046325684,null,null,null,null,null,2.0999999046325684,2.0999999046325684,null,null,2.0999999046325684]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.1,null,0.1,null,0.1,null,0.1,null,null,null,null,0.1,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"2794",null,"2794",null,"2794",null,"2794",null,null,null,null,"2794",null,"2794",null,"2794",null,null,null,null,null,"2794","2794",null,null,"2794"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,2.2000000000000002,null,2.2000000000000002,null,2.2000000000000002,null,2.2000000000000002,null,null,null,null,2.2000000000000002,null,2.1,null,2.1,null,null,null,null,null,2.1,2.1,null,null,2.1]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,1.1000000238418579,null,1.1000000238418579,null,1.1000000238418579,null,1.1000000238418579,null,null,null,null,1.1000000238418579,null,1.1000000238418579,null,1.1000000238418579,null,null,null,null,null,1.1000000238418579,1.1000000238418579,null,null,1.1000000238418579]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,2.0999999046325684,null,2.0999999046325684,null,2.0999999046325684,null,2.0999999046325684,null,null,null,null,2.0999999046325684,null,2.0999999046325684,null,2.0999999046325684,null,null,null,null,null,2.0999999046325684,2.0999999046325684,null,null,2.0999999046325684]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"BOHL","index":26,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"BOHL - Bohle (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"TMES - Townsville Mesh"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Nth Queensland"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/11kV 15/20/25MVA ODAN/ONAF/ODAF;1x66/11kV 15/20/25MVA ONAN/ONAF/ODAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 1.0%, 2020 S 0.8% W 0.8%, 2021 S 0.5% W 0.5%, 2022 S 0.3% W 0.3%, 2023 S 0.5% W 0.5%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"26.6 MVA on 28/11/2018 at 14:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,52.700000762939453,null,52.700000762939453,null,52.700000762939453,null,52.700000762939453,null,null,null,null,52.700000762939453,null,55.299999237060547,null,55.299999237060547,null,null,null,null,null,55.299999237060547,55.299999237060547,null,null,55.299999237060547]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,29.799999237060547,null,29.799999237060547,null,29.600000381469727,null,29.799999237060547,null,null,null,null,30.399999618530273,null,19.399999618530273,null,19.5,null,null,null,null,null,19.600000381469727,19.600000381469727,null,null,19.799999237060547]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.97699999999999998,null,0.97699999999999998,null,0.97699999999999998,null,0.97699999999999998,null,null,null,null,0.97699999999999998,null,0.96099999999999997,null,0.96099999999999997,null,null,null,null,null,0.96099999999999997,0.96099999999999997,null,null,0.96099999999999997]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,26.399999618530273,null,26.399999618530273,null,26.399999618530273,null,26.399999618530273,null,null,null,null,26.399999618530273,null,27.799999237060547,null,27.799999237060547,null,null,null,null,null,27.799999237060547,27.799999237060547,null,null,27.799999237060547]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,26.100000381469727,null,26.100000381469727,null,25.899999618530273,null,26,null,null,null,null,26.600000381469727,null,17.5,null,17.600000381469727,null,null,null,null,null,17.600000381469727,17.700000762939453,null,null,17.799999237060547]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,1.3,null,1.3,null,1.3,null,1.3,null,null,null,null,1.3,null,0.9,null,0.9,null,null,null,null,null,0.9,0.9,null,null,0.9]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"8.5",null,"8.5",null,"8.5",null,"8.5",null,null,null,null,"8.5",null,"8.5",null,"8.5",null,null,null,null,null,"8.5","8.5",null,null,"8.5"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.2]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0.80000001192092896,null,0.80000001192092896,null,0.80000001192092896,null,0.80000001192092896,null,null,null,null,0.80000001192092896,null,0.80000001192092896,null,0.80000001192092896,null,null,null,null,null,0.80000001192092896,0.80000001192092896,null,null,0.80000001192092896]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"BORE","index":27,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"BORE - Boyne Residential (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T019 - Gladstone South BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Capricornia"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/11kV 7.5/10MVA ONAN/ONAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.6%, 2020 S -0.4% W -0.4%2021 S -0.3% W -0.3%2022 S 0.5% W 0.5%, 2023 S 0.3% W 0.3%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"10.7 MVA on 13/02/2019 at 19:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,26,null,26,null,26,null,26,null,null,null,null,26,null,29.899999618530273,null,29.899999618530273,null,null,null,null,null,29.899999618530273,29.899999618530273,null,null,29.899999618530273]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,11.600000381469727,null,11.5,null,11.5,null,11.5,null,null,null,null,11.600000381469727,null,8.8000001907348633,null,8.6999998092651367,null,null,null,null,null,8.6999998092651367,8.6999998092651367,null,null,8.8000001907348633]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.98399999999999999,null,0.98399999999999999,null,0.98399999999999999,null,0.98399999999999999,null,null,null,null,0.98399999999999999,null,0.99399999999999999,null,0.99399999999999999,null,null,null,null,null,0.99399999999999999,0.99399999999999999,null,null,0.99399999999999999]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,14.300000190734863,null,14.300000190734863,null,14.300000190734863,null,14.300000190734863,null,null,null,null,14.300000190734863,null,15,null,15,null,null,null,null,null,15,15,null,null,15]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,10.800000190734863,null,10.699999809265137,null,10.600000381469727,null,10.699999809265137,null,null,null,null,10.800000190734863,null,8.3999996185302734,null,8.3999996185302734,null,null,null,null,null,8.3000001907348633,8.3999996185302734,null,null,8.3999996185302734]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.5,null,0.5,null,0.5,null,0.5,null,null,null,null,0.5,null,0.4,null,0.4,null,null,null,null,null,0.4,0.4,null,null,0.4]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"4",null,"4",null,"4",null,"4",null,null,null,null,"4",null,"4",null,"4",null,null,null,null,null,"4","4",null,null,"4"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"BOWE","index":28,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"BOWE - Bowen (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T181 - Bowen North BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Nth Queensland"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/11kV 15/16MVA ONAN/OFDAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.5%, 2020 S -0.1% W -0.1%2021 S -0.1% W -0.1%2022 S 0.5% W 0.5%, 2023 S 0.3% W 0.3%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"12.3 MVA on 13/02/2019 at 19:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,39.799999237060547,null,39.799999237060547,null,39.799999237060547,null,39.799999237060547,null,null,null,null,39.799999237060547,null,44.400001525878906,null,44.400001525878906,null,null,null,null,null,44.400001525878906,44.400001525878906,null,null,44.400001525878906]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,13.5,null,13.399999618530273,null,13.399999618530273,null,13.399999618530273,null,null,null,null,13.600000381469727,null,9.6000003814697266,null,9.6000003814697266,null,null,null,null,null,9.5,9.6000003814697266,null,null,9.6000003814697266]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,1,null,1,null,1,null,1,null,null,null,null,1,null,0.96899999999999997,null,0.96899999999999997,null,null,null,null,null,0.96899999999999997,0.96899999999999997,null,null,0.96899999999999997]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,22.399999618530273,null,22.399999618530273,null,22.399999618530273,null,22.399999618530273,null,null,null,null,22.399999618530273,null,23.899999618530273,null,23.899999618530273,null,null,null,null,null,23.899999618530273,23.899999618530273,null,null,23.899999618530273]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,12.300000190734863,null,12.199999809265137,null,12.199999809265137,null,12.300000190734863,null,null,null,null,12.399999618530273,null,9.3000001907348633,null,9.3000001907348633,null,null,null,null,null,9.3000001907348633,9.3000001907348633,null,null,9.3999996185302734]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.6,null,0.6,null,0.6,null,0.6,null,null,null,null,0.6,null,0.5,null,0.5,null,null,null,null,null,0.5,0.5,null,null,0.5]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"8",null,"8",null,"8",null,"8",null,null,null,null,"8",null,"8",null,"8",null,null,null,null,null,"8","8",null,null,"8"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"BROX","index":29,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"BROX - Broxburn (33/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T010 - Yarranlea BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is South West"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x33/11kV 5MVA ON"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.3%, 2020 S 0.4% W 0.4%, 2021 S 0.4% W 0.4%, 2022 S 0.1% W 0.1%, 2023 S -0.3% W -0.3"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"8.4 MVA on 19/02/2019 at 19:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,11,null,11,null,11,null,11,null,null,null,null,11,null,11,null,11,null,null,null,null,null,11,11,null,null,11]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,9.6000003814697266,null,9.6000003814697266,null,10.899999618530273,null,10.899999618530273,null,null,null,null,10.899999618530273,null,8,null,8.1000003814697266,null,null,null,null,null,9.3000001907348633,9.3000001907348633,null,null,9.3000001907348633]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.94199999999999995,null,0.94199999999999995,null,0.94199999999999995,null,0.94199999999999995,null,null,null,null,0.94199999999999995,null,0.97399999999999998,null,0.97399999999999998,null,null,null,null,null,0.97399999999999998,0.97399999999999998,null,null,0.97399999999999998]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,5.8000001907348633,null,5.8000001907348633,null,5.8000001907348633,null,5.8000001907348633,null,null,null,null,5.8000001907348633,null,6,null,6,null,null,null,null,null,6,6,null,null,6]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,8.5,null,8.5,null,9.8000001907348633,null,9.6999998092651367,null,null,null,null,9.8000001907348633,null,7.5,null,7.5,null,null,null,null,null,8.6999998092651367,8.6999998092651367,null,null,8.8000001907348633]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.4,null,0.4,null,0.5,null,0.5,null,null,null,null,0.5,null,0.4,null,0.4,null,null,null,null,null,0.4,0.4,null,null,0.4]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"13.5",null,"13.5",null,"13.5",null,"13.5",null,null,null,null,"13.5",null,"13.5",null,"13.5",null,null,null,null,null,"13.5","13.5",null,null,"13.5"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,2.7,null,2.7,null,4,null,3.9,null,null,null,null,4,null,1.5,null,1.5,null,null,null,null,null,2.7,2.7,null,null,2.8]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0.5,null,0.5,null,0.5,null,0.5,null,null,null,null,0.5,null,0.5,null,0.5,null,null,null,null,null,0.5,0.5,null,null,0.5]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,3.2999999523162842,null,3.2999999523162842,null,3.2999999523162842,null,3.2999999523162842,null,null,null,null,3.2999999523162842,null,3.2999999523162842,null,3.2999999523162842,null,null,null,null,null,3.2999999523162842,3.2999999523162842,null,null,3.2999999523162842]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)",null,null,null,null,null,null,null,null,null,0.20000000298023224,null,0.10000000149011612,null,null,null,null,0.20000000298023224]
[null,null,null,null,"LARc (MW)",null,null,null,null,null,null,null,null,null,0.2,null,0.1,null,null,null,null,0.2]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"No",null,"No",null,null,null,null,"No",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"BUCE","index":30,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"BUCE - Bundaberg Central (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T020 - Bundaberg BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Wide Bay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/11kV 19/26/32MVA ONAN/ODAN/ODAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -1.4%, 2020 S -1.0% W -1.0%2021 S -1.0% W -1.0%2022 S -0.9% W -0.9%2023 S -1.2% W -1.2"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"20.3 MVA on 20/03/2019 at 14:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,80.300003051757813,null,80.300003051757813,null,80.300003051757813,null,80.300003051757813,null,null,null,null,80.300003051757813,null,87.400001525878906,null,87.400001525878906,null,null,null,null,null,87.400001525878906,87.400001525878906,null,null,87.400001525878906]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,18.700000762939453,null,18.5,null,18.200000762939453,null,18,null,null,null,null,17.899999618530273,null,12.600000381469727,null,12.5,null,null,null,null,null,12.300000190734863,11.600000381469727,null,null,11.5]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.997,null,0.997,null,0.996,null,0.995,null,null,null,null,0.995,null,0.998,null,0.999,null,null,null,null,null,0.999,1,null,null,1]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,43.099998474121094,null,43.099998474121094,null,43.099998474121094,null,43.099998474121094,null,null,null,null,43.099998474121094,null,45.799999237060547,null,45.799999237060547,null,null,null,null,null,45.799999237060547,45.799999237060547,null,null,45.799999237060547]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,17.5,null,17.299999237060547,null,17,null,16.799999237060547,null,null,null,null,16.700000762939453,null,11.699999809265137,null,11.600000381469727,null,null,null,null,null,11.399999618530273,11.800000190734863,null,null,11.699999809265137]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.9,null,0.9,null,0.9,null,0.8,null,null,null,null,0.8,null,0.6,null,0.6,null,null,null,null,null,0.6,0.6,null,null,0.6]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"5",null,"5",null,"5",null,"5",null,null,null,null,"5",null,"5",null,"5",null,null,null,null,null,"5","5",null,null,"5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"BULL","index":31,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"BULL - Bullyard (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T020 - Bundaberg BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Wide Bay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/11kV 5MVA ON;1x66/11kV 5MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.1%, 2020 S 0.3% W 0.3%, 2021 S 0.2% W 0.2%, 2022 S 0.1% W 0.1%, 2023 S -0.0% W -0.0"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"3.4 MVA on 11/03/2019 at 18:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,14.199999809265137,null,14.199999809265137,null,14.199999809265137,null,14.199999809265137,null,null,null,null,14.199999809265137,null,15,null,15,null,null,null,null,null,15,15,null,null,15]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,3.7000000476837158,null,3.7000000476837158,null,3.7000000476837158,null,3.7000000476837158,null,null,null,null,3.7000000476837158,null,1.7000000476837158,null,1.7000000476837158,null,null,null,null,null,1.7000000476837158,1.7000000476837158,null,null,1.7000000476837158]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.90100000000000002,null,0.90100000000000002,null,0.90100000000000002,null,0.90100000000000002,null,null,null,null,0.90100000000000002,null,0.91200000000000003,null,0.91200000000000003,null,null,null,null,null,0.91200000000000003,0.91200000000000003,null,null,0.91200000000000003]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,7.5,null,7.5,null,7.5,null,7.5,null,null,null,null,7.5,null,7.5,null,7.5,null,null,null,null,null,7.5,7.5,null,null,7.5]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,3.5999999046325684,null,3.5999999046325684,null,3.5999999046325684,null,3.5999999046325684,null,null,null,null,3.5999999046325684,null,1.5,null,1.5,null,null,null,null,null,1.5,1.5,null,null,1.6000000238418579]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.2,null,0.2,null,0.2,null,0.2,null,null,null,null,0.2,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"5",null,"5",null,"5",null,"5",null,null,null,null,"5",null,"5",null,"5",null,null,null,null,null,"5","5",null,null,"5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"CACI","index":32,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"CACI - Cairns City (132/22kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"QCNS - Cairns 132kV TCP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Far North"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x132/22kV 55/80MVA ONAN/ODAN;1x132/22kV 64/80MVA ONAN/ODAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.2%, 2020 S 0.3% W 0.3%, 2021 S 0.2% W 0.2%, 2022 S -0.2% W -0.2%2023 S -0.5% W -0.5"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"47.6 MVA on 29/11/2018 at 12:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,182.30000305175781,null,182.30000305175781,null,182.30000305175781,null,182.30000305175781,null,null,null,null,182.30000305175781,null,187.89999389648438,null,187.89999389648438,null,null,null,null,null,187.89999389648438,187.89999389648438,null,null,187.89999389648438]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,54,null,53.799999237060547,null,53.200000762939453,null,53,null,null,null,null,53.200000762939453,null,29.799999237060547,null,29.899999618530273,null,null,null,null,null,29.799999237060547,29.700000762939453,null,null,29.700000762939453]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,1,null,1,null,0.999,null,0.999,null,null,null,null,0.999,null,0.996,null,0.996,null,null,null,null,null,0.996,0.996,null,null,0.996]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,101.59999847412109,null,101.59999847412109,null,101.59999847412109,null,101.59999847412109,null,null,null,null,101.59999847412109,null,103.80000305175781,null,103.80000305175781,null,null,null,null,null,103.80000305175781,103.80000305175781,null,null,103.80000305175781]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,50.900001525878906,null,50.700000762939453,null,50.099998474121094,null,50,null,null,null,null,50.099998474121094,null,29.100000381469727,null,29.200000762939453,null,null,null,null,null,29.100000381469727,29,null,null,29]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,2.5,null,2.5,null,2.5,null,2.5,null,null,null,null,2.5,null,1.5,null,1.5,null,null,null,null,null,1.5,1.5,null,null,1.5]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"42",null,"42",null,"42",null,"42",null,null,null,null,"42",null,"42",null,"42",null,null,null,null,null,"42","42",null,null,"42"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"CAFE","index":33,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"CAFE - Cape Ferguson (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"TMES - Townsville Mesh"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Nth Queensland"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/11kV 2.3MVA ONAN;1x66/11kV 2MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.9%, 2020 S 0.9% W 0.9%, 2021 S 0.9% W 0.9%, 2022 S 2.0% W 2.0%, 2023 S 1.8% W 1.8%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"2.1 MVA on 27/11/2018 at 19:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,4.4000000953674316,null,4.4000000953674316,null,4.4000000953674316,null,4.4000000953674316,null,null,null,null,4.4000000953674316,null,4.6999998092651367,null,4.6999998092651367,null,null,null,null,null,4.6999998092651367,4.6999998092651367,null,null,4.6999998092651367]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,2.0999999046325684,null,2.0999999046325684,null,2.0999999046325684,null,2.2000000476837158,null,null,null,null,2.2000000476837158,null,1.7000000476837158,null,1.7000000476837158,null,null,null,null,null,1.7000000476837158,1.7999999523162842,null,null,1.7999999523162842]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.98799999999999999,null,0.98799999999999999,null,0.98799999999999999,null,0.98799999999999999,null,null,null,null,0.98799999999999999,null,0.99099999999999999,null,0.99099999999999999,null,null,null,null,null,0.99099999999999999,0.99099999999999999,null,null,0.99099999999999999]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,2.5999999046325684,null,2.5999999046325684,null,2.5999999046325684,null,2.5999999046325684,null,null,null,null,2.5999999046325684,null,2.7000000476837158,null,2.7000000476837158,null,null,null,null,null,2.7000000476837158,2.7000000476837158,null,null,2.7000000476837158]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,2,null,2,null,2.0999999046325684,null,2.0999999046325684,null,null,null,null,2.0999999046325684,null,1.6000000238418579,null,1.6000000238418579,null,null,null,null,null,1.6000000238418579,1.7000000476837158,null,null,1.7000000476837158]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.1,null,0.1,null,0.1,null,0.1,null,null,null,null,0.1,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"50.5",null,"50.5",null,"50.5",null,"50.5",null,null,null,null,"50.5",null,"50.5",null,"50.5",null,null,null,null,null,"50.5","50.5",null,null,"50.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"CALE","index":34,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"CALE - Calen (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T039 - Proserpine BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Mackay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/11kV 5MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.0%, 2020 S 0.3% W 0.3%, 2021 S 0.3% W 0.3%, 2022 S 0.4% W 0.4%, 2023 S 0.3% W 0.3%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"4.4 MVA on 26/11/2018 at 19:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,11,null,11,null,11,null,11,null,null,null,null,11,null,12,null,12,null,null,null,null,null,12,12,null,null,12]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,5.8000001907348633,null,5.8000001907348633,null,5.8000001907348633,null,5.8000001907348633,null,null,null,null,5.9000000953674316,null,4.3000001907348633,null,4.3000001907348633,null,null,null,null,null,4.3000001907348633,4.3000001907348633,null,null,4.3000001907348633]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.92900000000000005,null,0.92900000000000005,null,0.92900000000000005,null,0.92900000000000005,null,null,null,null,0.92900000000000005,null,0.93700000000000006,null,0.93700000000000006,null,null,null,null,null,0.93700000000000006,0.93700000000000006,null,null,0.93700000000000006]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,6.3000001907348633,null,6.3000001907348633,null,6.3000001907348633,null,6.3000001907348633,null,null,null,null,6.3000001907348633,null,6.5,null,6.5,null,null,null,null,null,6.5,6.5,null,null,6.5]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,4.5999999046325684,null,4.5999999046325684,null,4.5,null,4.5999999046325684,null,null,null,null,4.5999999046325684,null,3.7000000476837158,null,3.7000000476837158,null,null,null,null,null,3.7000000476837158,3.7000000476837158,null,null,3.7000000476837158]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.2,null,0.2,null,0.2,null,0.2,null,null,null,null,0.2,null,0.2,null,0.2,null,null,null,null,null,0.2,0.2,null,null,0.2]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"5",null,"5",null,"5",null,"5",null,null,null,null,"5",null,"5",null,"5",null,null,null,null,null,"5","5",null,null,"5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"CALL","index":35,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"CALL - Calliope (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T019 - Gladstone South BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Capricornia"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/11kV 7.5/10MVA ON/OB;1x66/11kV 7.5/10MVA ONAN/ONAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.1%, 2020 S 0.3% W 0.3%, 2021 S 0.3% W 0.3%, 2022 S 0.8% W 0.8%, 2023 S 0.4% W 0.4%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"9.4 MVA on 28/11/2018 at 18:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,26.700000762939453,null,26.700000762939453,null,26.700000762939453,null,26.700000762939453,null,null,null,null,26.700000762939453,null,29.899999618530273,null,29.899999618530273,null,null,null,null,null,29.899999618530273,29.899999618530273,null,null,29.899999618530273]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,9.3999996185302734,null,9.3999996185302734,null,9.3999996185302734,null,9.3999996185302734,null,null,null,null,9.5,null,6.5,null,6.5,null,null,null,null,null,6.5,6.5,null,null,6.5999999046325684]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.98199999999999998,null,0.98199999999999998,null,0.98199999999999998,null,0.98199999999999998,null,null,null,null,0.98199999999999998,null,0.99299999999999999,null,0.99299999999999999,null,null,null,null,null,0.99299999999999999,0.99299999999999999,null,null,0.99299999999999999]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,14.699999809265137,null,14.699999809265137,null,14.699999809265137,null,14.699999809265137,null,null,null,null,14.699999809265137,null,15,null,15,null,null,null,null,null,15,15,null,null,15]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,8.5,null,8.5,null,8.5,null,8.5,null,null,null,null,8.6000003814697266,null,6.1999998092651367,null,6.1999998092651367,null,null,null,null,null,6.1999998092651367,6.1999998092651367,null,null,6.3000001907348633]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.4,null,0.4,null,0.4,null,0.4,null,null,null,null,0.4,null,0.3,null,0.3,null,null,null,null,null,0.3,0.3,null,null,0.3]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"7",null,"7",null,"7",null,"7",null,null,null,null,"7",null,"7",null,"7",null,null,null,null,null,"7","7",null,null,"7"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"CANN","index":36,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"CANN - Cannonvale (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T039 - Proserpine BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Mackay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/11kV 15MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.5%, 2020 S 0.9% W 0.9%, 2021 S 0.9% W 0.9%, 2022 S 0.9% W 0.9%, 2023 S 0.5% W 0.5%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"16 MVA on 13/02/2019 at 16:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,34.900001525878906,null,34.900001525878906,null,34.900001525878906,null,34.900001525878906,null,null,null,null,34.900001525878906,null,37.799999237060547,null,37.799999237060547,null,null,null,null,null,37.799999237060547,37.799999237060547,null,null,37.799999237060547]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,19.100000381469727,null,19.200000762939453,null,19.200000762939453,null,19.399999618530273,null,null,null,null,19.600000381469727,null,11.199999809265137,null,11.300000190734863,null,null,null,null,null,11.300000190734863,11.399999618530273,null,null,11.5]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.97799999999999998,null,0.97799999999999998,null,0.97799999999999998,null,0.97799999999999998,null,null,null,null,0.97799999999999998,null,0.97799999999999998,null,0.97799999999999998,null,null,null,null,null,0.97799999999999998,0.97799999999999998,null,null,0.97799999999999998]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,20,null,20,null,20,null,20,null,null,null,null,20,null,21.899999618530273,null,21.899999618530273,null,null,null,null,null,21.899999618530273,21.899999618530273,null,null,21.899999618530273]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,16.899999618530273,null,16.899999618530273,null,16.899999618530273,null,17,null,null,null,null,17.299999237060547,null,10.600000381469727,null,10.699999809265137,null,null,null,null,null,10.699999809265137,10.800000190734863,null,null,10.899999618530273]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.8,null,0.8,null,0.8,null,0.9,null,null,null,null,0.9,null,0.5,null,0.5,null,null,null,null,null,0.5,0.5,null,null,0.5]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"20.5",null,"20.5",null,"20.5",null,"20.5",null,null,null,null,"20.5",null,"20.5",null,"20.5",null,null,null,null,null,"20.5","20.5",null,null,"20.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"CANO","index":37,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"CANO - Cairns North (132/22kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"QWRE - Woree TCP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Far North"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x132/22kV 50/63MVA ONAN/ODAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.7%, 2020 S 0.9% W 0.9%, 2021 S 0.8% W 0.8%, 2022 S 0.5% W 0.5%, 2023 S 0.2% W 0.2%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"48 MVA on 21/02/2019 at 19:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,142.80000305175781,null,142.80000305175781,null,142.80000305175781,null,142.80000305175781,null,null,null,null,142.80000305175781,null,147.10000610351563,null,147.10000610351563,null,null,null,null,null,147.10000610351563,147.10000610351563,null,null,147.10000610351563]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,50.700000762939453,null,50.900001525878906,null,50.599998474121094,null,50.799999237060547,null,null,null,null,51.299999237060547,null,30.899999618530273,null,31.100000381469727,null,null,null,null,null,31.299999237060547,31.399999618530273,null,null,31.600000381469727]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.998,null,0.998,null,0.998,null,0.998,null,null,null,null,0.999,null,0.999,null,0.999,null,null,null,null,null,0.999,0.999,null,null,0.999]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,79.400001525878906,null,79.400001525878906,null,79.400001525878906,null,79.400001525878906,null,null,null,null,79.400001525878906,null,81.099998474121094,null,81.099998474121094,null,null,null,null,null,81.099998474121094,81.099998474121094,null,null,81.099998474121094]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,46.200000762939453,null,46.400001525878906,null,46.200000762939453,null,46.400001525878906,null,null,null,null,46.799999237060547,null,30.200000762939453,null,30.5,null,null,null,null,null,30.600000381469727,30.700000762939453,null,null,30.899999618530273]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,2.2999999999999998,null,2.2999999999999998,null,2.2999999999999998,null,2.2999999999999998,null,null,null,null,2.2999999999999998,null,1.5,null,1.5,null,null,null,null,null,1.5,1.5,null,null,1.5]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"18.5",null,"18.5",null,"18.5",null,"18.5",null,null,null,null,"18.5",null,"18.5",null,"18.5",null,null,null,null,null,"18.5","18.5",null,null,"18.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"CARI","index":38,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"CARI - Cape River (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T095 - Millchester BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Nth Queensland"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/11kV 1MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.1%, 2020 S 0.3% W 0.3%, 2021 S 0.2% W 0.2%, 2022 S 0.0% W 0.0%, 2023 S -0.2% W -0.2"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"0.7 MVA on 04/12/2018 at 19:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,1,null,1,null,1,null,1,null,null,null,null,1,null,1.1000000238418579,null,1.1000000238418579,null,null,null,null,null,1.1000000238418579,1.1000000238418579,null,null,1.1000000238418579]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,0.89999997615814209,null,0.89999997615814209,null,0.89999997615814209,null,0.89999997615814209,null,null,null,null,0.89999997615814209,null,0.69999998807907104,null,0.69999998807907104,null,null,null,null,null,0.69999998807907104,0.69999998807907104,null,null,0.69999998807907104]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.96699999999999997,null,0.96699999999999997,null,0.96699999999999997,null,0.96699999999999997,null,null,null,null,0.96699999999999997,null,0.95699999999999996,null,0.95699999999999996,null,null,null,null,null,0.95699999999999996,0.95699999999999996,null,null,0.95699999999999996]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,0.80000001192092896,null,0.80000001192092896,null,0.80000001192092896,null,0.80000001192092896,null,null,null,null,0.80000001192092896,null,0.69999998807907104,null,0.69999998807907104,null,null,null,null,null,0.69999998807907104,0.69999998807907104,null,null,0.69999998807907104]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"3",null,"3",null,"3",null,"3",null,null,null,null,"3",null,"3",null,"3",null,null,null,null,null,"3","3",null,null,"3"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,0.8,null,0.8,null,0.8,null,0.8,null,null,null,null,0.8,null,0.7,null,0.7,null,null,null,null,null,0.7,0.7,null,null,0.7]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,1,null,1,null,1,null,1,null,null,null,null,1,null,1,null,1,null,null,null,null,null,1,1,null,null,1]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"CARM","index":39,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"CARM - Carmila (33/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T065 - Alligator Creek BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Mackay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x33/11kV 1MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -2.0%, 2020 S -1.5% W -1.5%2021 S -1.5% W -1.5%2022 S -0.5% W -0.5%2023 S -0.5% W -0.5"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"0.8 MVA on 14/08/2018 at 19:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,1.2999999523162842,null,1.2999999523162842,null,1.2999999523162842,null,1.2999999523162842,null,null,null,null,1.2999999523162842,null,1.3999999761581421,null,1.3999999761581421,null,null,null,null,null,1.3999999761581421,1.3999999761581421,null,null,1.3999999761581421]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,0.60000002384185791,null,0.60000002384185791,null,0.60000002384185791,null,0.60000002384185791,null,null,null,null,0.60000002384185791,null,0.80000001192092896,null,0.80000001192092896,null,null,null,null,null,0.80000001192092896,0.80000001192092896,null,null,0.80000001192092896]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.94899999999999995,null,0.94899999999999995,null,0.94899999999999995,null,0.94899999999999995,null,null,null,null,0.94899999999999995,null,0.95299999999999996,null,0.95299999999999996,null,null,null,null,null,0.95299999999999996,0.95299999999999996,null,null,0.95299999999999996]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,0.60000002384185791,null,0.60000002384185791,null,0.5,null,0.5,null,null,null,null,0.5,null,0.69999998807907104,null,0.69999998807907104,null,null,null,null,null,0.69999998807907104,0.69999998807907104,null,null,0.69999998807907104]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"4",null,"4",null,"4",null,"4",null,null,null,null,"4",null,"4",null,"4",null,null,null,null,null,"4","4",null,null,"4"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,0.6,null,0.6,null,0.5,null,0.5,null,null,null,null,0.5,null,0.7,null,0.7,null,null,null,null,null,0.7,0.7,null,null,0.7]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0.10000000149011612,null,0.10000000149011612,null,0.10000000149011612,null,0.10000000149011612,null,null,null,null,0.10000000149011612,null,0.10000000149011612,null,0.10000000149011612,null,null,null,null,null,0.10000000149011612,0.10000000149011612,null,null,0.10000000149011612]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,1,null,1,null,1,null,1,null,null,null,null,1,null,1,null,1,null,null,null,null,null,1,1,null,null,1]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"CAST","index":40,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"CAST - Canning Street (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"RMES - Rockhampton Mesh"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Capricornia"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x16/20 MVA 66/11 ONAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -1.0%, 2020 S -0.8% W -0.8%2021 S -0.8% W -0.8%2022 S -0.8% W -0.8%2023 S -1.2% W -1.2"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"22.7 MVA on 03/12/2018 at 15:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,46.299999237060547,null,46.299999237060547,null,46.299999237060547,null,46.299999237060547,null,null,null,null,46.299999237060547,null,54.200000762939453,null,54.200000762939453,null,null,null,null,null,54.200000762939453,54.200000762939453,null,null,54.200000762939453]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,25.700000762939453,null,25.399999618530273,null,24.899999618530273,null,24.700000762939453,null,null,null,null,24.600000381469727,null,13.399999618530273,null,13.300000190734863,null,null,null,null,null,13.100000381469727,13,null,null,12.899999618530273]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,1,null,1,null,1,null,1,null,null,null,null,1,null,0.96899999999999997,null,0.96899999999999997,null,null,null,null,null,0.96899999999999997,0.96899999999999997,null,null,0.96899999999999997]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,26.899999618530273,null,26.899999618530273,null,26.899999618530273,null,26.899999618530273,null,null,null,null,26.899999618530273,null,29.899999618530273,null,29.899999618530273,null,null,null,null,null,29.899999618530273,29.899999618530273,null,null,29.899999618530273]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,22.899999618530273,null,22.600000381469727,null,22.700000762939453,null,22.5,null,null,null,null,22.5,null,13,null,12.899999618530273,null,null,null,null,null,12.699999809265137,12.600000381469727,null,null,12.5]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,1.1000000000000001,null,1.1000000000000001,null,1.1000000000000001,null,1.1000000000000001,null,null,null,null,1.1000000000000001,null,0.7,null,0.6,null,null,null,null,null,0.6,0.6,null,null,0.6]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"15.5",null,"15.5",null,"15.5",null,"15.5",null,null,null,null,"15.5",null,"15.5",null,"15.5",null,null,null,null,null,"15.5","15.5",null,null,"15.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"CAUP","index":41,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[49,2,49,39],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[45,23,45,24],[45,25,45,30],[45,32,45,34],[44,4,44,9],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[44,21,44,22],[44,23,44,24],[44,25,44,30],[44,32,44,34],[43,4,43,9],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[43,21,43,22],[43,23,43,24],[43,25,43,30],[43,32,43,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[42,21,42,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[41,23,41,24],[41,25,41,30],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"CAUP - Cape Upstart (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T193 - Clare South BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Nth Queensland"]
[]
[]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2021 W 0.0%, 2022 S 0.0% W 0.0%, 2023 S 0.0% W 0.0%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"No current information, due to be commissioned Winter 2021 "]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,null,null,null,null,10,null,10,null,null,null,null,10,null,null,null,null,null,null,null,null,null,10,10,null,null,10]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,null,null,null,null,0,null,0,null,null,null,null,0,null,null,null,null,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,null,null,null,null,2.5,null,4.9000000000000004,null,null,null,null,5,null,null,null,null,null,null,null,null,null,1.3,2.5,null,null,2.5]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,null,null,null,null,0.85,null,0.85,null,null,null,null,0.85,null,null,null,null,null,null,null,null,null,0.85,0.85,null,null,0.85]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,null,null,null,null,0,null,0,null,null,null,null,0,null,null,null,null,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,null,null,null,null,2.4,null,4.9000000000000004,null,null,null,null,4.9000000000000004,null,null,null,null,null,null,null,null,null,1.3,2.5,null,null,2.5]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,null,null,null,null,0.1,null,0.2,null,null,null,null,0.2,null,null,null,null,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,null,null,null,null,"N/A",null,"N/A",null,null,null,null,"N/A",null,null,null,null,null,null,null,null,null,"N/A","N/A",null,null,"N/A"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,null,null,null,null,2.4,null,4.9000000000000004,null,null,null,null,4.9000000000000004,null,null,null,null,null,null,null,null,null,1.3,2.5,null,null,2.5]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,null,null,null,null,0,null,0,null,null,null,null,0,null,null,null,null,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,null,null,null,null,0,null,0,null,null,null,null,0,null,null,null,null,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,null,null,null,null,6,null,6,null,null,null,null,6,null,null,null,null,null,null,null,null,null,6,6,null,null,6]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,null,null,null,null,4,null,4,null,null,null,null,4,null,null,null,null,null,null,null,null,null,4,4,null,null,4]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,null,null,null,null,0,null,0,null,null,null,null,0,null,null,null,null,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,null,null,null,null,0,null,0,null,null,null,null,0,null,null,null,null,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,null,null,null,null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"CAWD","index":42,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"CAWD - Cawdor (33/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T116 - Torrington BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is South West"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x10MVA Skid transformer"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.0%, 2020 S 0.0% W 0.0%, 2021 S 0.0% W 0.0%, 2022 S 0.0% W 0.0%, 2023 S 0.0% W 0.0%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"4.9 MVA on 13/02/2019 at 18:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,10,null,10,null,10,null,10,null,null,null,null,10,null,10,null,10,null,null,null,null,null,10,10,null,null,10]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,5.3000001907348633,null,5.3000001907348633,null,5.1999998092651367,null,5.1999998092651367,null,null,null,null,5.1999998092651367,null,5.5,null,5.5,null,null,null,null,null,5.4000000953674316,5.4000000953674316,null,null,5.4000000953674316]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.82199999999999995,null,0.82199999999999995,null,0.82199999999999995,null,0.82199999999999995,null,null,null,null,0.82199999999999995,null,0.86199999999999999,null,0.86199999999999999,null,null,null,null,null,0.86199999999999999,0.86199999999999999,null,null,0.86199999999999999]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,4.3000001907348633,null,4.3000001907348633,null,4.3000001907348633,null,4.3000001907348633,null,null,null,null,4.3000001907348633,null,5,null,5,null,null,null,null,null,5,5,null,null,5]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.2,null,0.2,null,0.2,null,0.2,null,null,null,null,0.2,null,0.3,null,0.3,null,null,null,null,null,0.3,0.3,null,null,0.3]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"4",null,"4",null,"4",null,"4",null,null,null,null,"4",null,"4",null,"4",null,null,null,null,null,"4","4",null,null,"4"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,4.3,null,4.3,null,4.3,null,4.3,null,null,null,null,4.3,null,5,null,5,null,null,null,null,null,5,5,null,null,5]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,3.5999999046325684,null,3.5999999046325684,null,3.5999999046325684,null,3.5999999046325684,null,null,null,null,3.5999999046325684,null,3.5999999046325684,null,3.5999999046325684,null,null,null,null,null,3.5999999046325684,3.5999999046325684,null,null,3.5999999046325684]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,10,null,10,null,10,null,10,null,null,null,null,10,null,10,null,10,null,null,null,null,null,10,10,null,null,10]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"CEPL","index":43,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"CEPL - Cecil Plains (33/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T010 - Yarranlea BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is South West"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x33/11kV 5MVA ON"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -4.4%, 2020 S -2.4% W -2.4%2021 S -2.3% W -2.3%2022 S -1.7% W -1.7%2023 S -2.0% W -2.0"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"4.2 MVA on 18/06/2018 at 20:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,10,null,10,null,10,null,10,null,null,null,null,10,null,10,null,10,null,null,null,null,null,10,10,null,null,10]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,2.2999999523162842,null,2.2000000476837158,null,2.0999999046325684,null,2.0999999046325684,null,null,null,null,2.0999999046325684,null,3.9000000953674316,null,3.7999999523162842,null,null,null,null,null,3.7000000476837158,3.5999999046325684,null,null,3.5]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.95099999999999996,null,0.95399999999999996,null,0.95699999999999996,null,0.95899999999999996,null,null,null,null,0.96099999999999997,null,0.96699999999999997,null,0.96899999999999997,null,null,null,null,null,0.97,0.97099999999999997,null,null,0.97199999999999998]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,5,null,5,null,5,null,5,null,null,null,null,5,null,5,null,5,null,null,null,null,null,5,5,null,null,5]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,1.7999999523162842,null,1.7999999523162842,null,1.7000000476837158,null,1.7000000476837158,null,null,null,null,1.7000000476837158,null,3.7999999523162842,null,3.7000000476837158,null,null,null,null,null,3.5999999046325684,3.5,null,null,3.4000000953674316]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.1,null,0.1,null,0.1,null,0.1,null,null,null,null,0.1,null,0.2,null,0.2,null,null,null,null,null,0.2,0.2,null,null,0.2]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"62.5",null,"62.5",null,"62.5",null,"62.5",null,null,null,null,"62.5",null,"62.5",null,"62.5",null,null,null,null,null,"62.5","62.5",null,null,"62.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"CHAL","index":44,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"CHAL - Charlton (33/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T116 - Torrington BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is South West"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x7.5/10MVA ONAN/ONAF 33/11kV"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.9%, 2020 S -0.5% W -0.5%2021 S -0.4% W -0.4%2022 S 0.0% W 0.0%, 2023 S -0.3% W -0.3"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"4.8 MVA on 08/08/2018 at 07:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,11,null,11,null,11,null,11,null,null,null,null,11,null,11,null,11,null,null,null,null,null,11,11,null,null,11]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,4.9000000953674316,null,4.9000000953674316,null,4.8000001907348633,null,4.8000001907348633,null,null,null,null,4.8000001907348633,null,4.8000001907348633,null,4.8000001907348633,null,null,null,null,null,4.8000001907348633,4.8000001907348633,null,null,4.8000001907348633]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.85399999999999998,null,0.85399999999999998,null,0.85399999999999998,null,0.85399999999999998,null,null,null,null,0.85399999999999998,null,0.86499999999999999,null,0.86499999999999999,null,null,null,null,null,0.88300000000000001,0.88300000000000001,null,null,0.88300000000000001]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,4.8000001907348633,null,4.8000001907348633,null,4.6999998092651367,null,4.6999998092651367,null,null,null,null,4.6999998092651367,null,4.5999999046325684,null,4.5999999046325684,null,null,null,null,null,4.5999999046325684,4.5999999046325684,null,null,4.5999999046325684]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.2,null,0.2,null,0.2,null,0.2,null,null,null,null,0.2,null,0.2,null,0.2,null,null,null,null,null,0.2,0.2,null,null,0.2]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"N/A",null,"N/A",null,"N/A",null,"N/A",null,null,null,null,"N/A",null,"N/A",null,"N/A",null,null,null,null,null,"N/A","N/A",null,null,"N/A"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,4.8,null,4.8,null,4.7,null,4.7,null,null,null,null,4.7,null,4.5999999999999996,null,4.5999999999999996,null,null,null,null,null,4.5999999999999996,4.5999999999999996,null,null,4.5999999999999996]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,4.8,null,4.8,null,4.8,null,4.8,null,null,null,null,4.8,null,4.8,null,4.8,null,null,null,null,null,4.8,4.8,null,null,4.8]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"YES",null,"YES",null,"YES",null,"YES",null,null,null,null,"YES",null,"YES",null,"YES",null,null,null,null,null,"YES","YES",null,null,"YES"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"CHAR","index":45,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"CHAR - Charleville (66/2211kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T083 - Roma 66kV BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is South West"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/11kV 7.5MVA ONAN;1x66/22kV 7.5MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.0%, 2020 S 0.0% W 0.0%, 2021 S 0.0% W 0.0%, 2022 S 0.0% W 0.0%, 2023 S 0.0% W 0.0%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"10 MVA on 24/01/2019 at 18:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,18.600000381469727,null,18.600000381469727,null,18.600000381469727,null,18.600000381469727,null,null,null,null,18.600000381469727,null,18.600000381469727,null,18.600000381469727,null,null,null,null,null,18.600000381469727,18.600000381469727,null,null,18.600000381469727]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,13.800000190734863,null,13.699999809265137,null,13.5,null,13.600000381469727,null,null,null,null,13.6,null,10.199999809265137,null,10.199999809265137,null,null,null,null,null,10.100000381469727,10.100000381469727,null,null,10.199999809265137]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.83699999999999997,null,0.83799999999999997,null,0.83799999999999997,null,0.83799999999999997,null,null,null,null,0.83799999999999997,null,0.88700000000000001,null,0.88700000000000001,null,null,null,null,null,0.88700000000000001,0.88700000000000001,null,null,0.88700000000000001]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,9.3000001907348633,null,9.3000001907348633,null,9.3000001907348633,null,9.3000001907348633,null,null,null,null,9.3000001907348633,null,9.3000001907348633,null,9.3000001907348633,null,null,null,null,null,9.3000001907348633,9.3000001907348633,null,null,9.3000001907348633]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,12.5,null,12.4,null,12.300000190734863,null,12.3,null,null,null,null,12.399999618530273,null,9.6000003814697266,null,9.5,null,null,null,null,null,9.5,9.5,null,null,9.5]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.6,null,0.6,null,0.6,null,0.6,null,null,null,null,0.6,null,0.5,null,0.5,null,null,null,null,null,0.5,0.5,null,null,0.5]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"11.5",null,"11.5",null,"11.5",null,"11.5",null,null,null,null,"11.5",null,"11.5",null,"11.5",null,null,null,null,null,"11.5","11.5",null,null,"11.5"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,3.2,null,3.1,null,3,null,3,null,null,null,null,3.1,null,0.3,null,0.2,null,null,null,null,null,0.2,0.2,null,null,0.2]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,3.2,null,3.2,null,3.2,null,3.2,null,null,null,null,3.2,null,3.2,null,3.2,null,null,null,null,null,3.2,3.2,null,null,3.2]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"CHIA","index":46,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"CHIA - Chillagoe (66/22kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T055 - Turkinje 66kV BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Far North"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/22kV 6.3MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -10.7%, 2020 S 5.0% W 5.0%, 2021 S -0.8% W -0.8%2022 S -2.3% W -2.3%2023 S -5.4% W -5.4"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"0.6 MVA on 27/11/2018 at 13:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,8.8999996185302734,null,8.8999996185302734,null,8.8999996185302734,null,8.8999996185302734,null,null,null,null,8.8999996185302734,null,9.1999998092651367,null,9.1999998092651367,null,null,null,null,null,9.1999998092651367,9.1999998092651367,null,null,9.1999998092651367]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,0.69999998807907104,null,0.60000002384185791,null,0.60000002384185791,null,0.60000002384185791,null,null,null,null,0.60000002384185791,null,0.5,null,0.5,null,null,null,null,null,0.5,0.5,null,null,0.5]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.99299999999999999,null,0.99299999999999999,null,0.99299999999999999,null,0.99299999999999999,null,null,null,null,0.99299999999999999,null,0.92600000000000005,null,0.92600000000000005,null,null,null,null,null,0.92600000000000005,0.92600000000000005,null,null,0.92600000000000005]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,0.60000002384185791,null,0.60000002384185791,null,0.60000002384185791,null,0.60000002384185791,null,null,null,null,0.60000002384185791,null,0.5,null,0.5,null,null,null,null,null,0.5,0.5,null,null,0.5]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"10",null,"10",null,"10",null,"10",null,null,null,null,"10",null,"10",null,"10",null,null,null,null,null,"10","10",null,null,"10"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,0.6,null,0.6,null,0.6,null,0.6,null,null,null,null,0.6,null,0.5,null,0.5,null,null,null,null,null,0.5,0.5,null,null,0.5]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0.20000000298023224,null,0.20000000298023224,null,0.20000000298023224,null,0.20000000298023224,null,null,null,null,0.20000000298023224,null,0.20000000298023224,null,0.20000000298023224,null,null,null,null,null,0.20000000298023224,0.20000000298023224,null,null,0.20000000298023224]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,1,null,1,null,1,null,1,null,null,null,null,1,null,1,null,1,null,null,null,null,null,1,1,null,null,1]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"CHIL","index":47,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"CHIL - Childers (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T131 - Isis BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Wide Bay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/11kV 10/7.5MVA ONB/ON;1x66/11kV 7.5/10MVA ON/ONB"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.4%, 2020 S 0.6% W 0.6%, 2021 S 0.5% W 0.5%, 2022 S 0.5% W 0.5%, 2023 S 0.3% W 0.3%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"7.6 MVA on 24/01/2019 at 19:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,20.899999618530273,null,20.899999618530273,null,20.899999618530273,null,20.899999618530273,null,null,null,null,20.899999618530273,null,22.399999618530273,null,22.399999618530273,null,null,null,null,null,22.399999618530273,22.399999618530273,null,null,22.399999618530273]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,11.100000381469727,null,11.100000381469727,null,11.100000381469727,null,11.100000381469727,null,null,null,null,11.199999809265137,null,5.6999998092651367,null,5.6999998092651367,null,null,null,null,null,5.6999998092651367,5.6999998092651367,null,null,5.8000001907348633]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.92800000000000005,null,0.92800000000000005,null,0.92800000000000005,null,0.92800000000000005,null,null,null,null,0.92800000000000005,null,0.93400000000000005,null,0.93400000000000005,null,null,null,null,null,0.93400000000000005,0.93400000000000005,null,null,0.93400000000000005]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,11.199999809265137,null,11.199999809265137,null,11.199999809265137,null,11.199999809265137,null,null,null,null,11.199999809265137,null,11.199999809265137,null,11.199999809265137,null,null,null,null,null,11.199999809265137,11.199999809265137,null,null,11.199999809265137]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,9.1999998092651367,null,9.1999998092651367,null,9.1999998092651367,null,9.1999998092651367,null,null,null,null,9.3000001907348633,null,5.4000000953674316,null,5.4000000953674316,null,null,null,null,null,5.4000000953674316,5.4000000953674316,null,null,5.5]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.5,null,0.5,null,0.5,null,0.5,null,null,null,null,0.5,null,0.3,null,0.3,null,null,null,null,null,0.3,0.3,null,null,0.3]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"3.5",null,"3.5",null,"3.5",null,"3.5",null,null,null,null,"3.5",null,"3.5",null,"3.5",null,null,null,null,null,"3.5","3.5",null,null,"3.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"CHTO","index":48,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"CHTO - Charters Towers (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T095 - Millchester BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Nth Queensland"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/11kV 7.5/10MVA ONAN/ONAF;1x66/11kV 8/10MVA ONAN/ONAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.5%, 2020 S -0.2% W -0.2%2021 S -0.4% W -0.4%2022 S -0.6% W -0.6%2023 S -0.6% W -0.6"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"10.9 MVA on 03/12/2018 at 15:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,21,null,21,null,21,null,21,null,null,null,null,21,null,23,null,23,null,null,null,null,null,23,23,null,null,23]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,11.800000190734863,null,11.699999809265137,null,11.5,null,11.399999618530273,null,null,null,null,11.5,null,7.8000001907348633,null,7.8000001907348633,null,null,null,null,null,7.8000001907348633,7.6999998092651367,null,null,7.6999998092651367]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.97299999999999998,null,0.97399999999999998,null,0.97499999999999998,null,0.97499999999999998,null,null,null,null,0.97499999999999998,null,0.97899999999999998,null,0.97899999999999998,null,null,null,null,null,0.98,0.98,null,null,0.98]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,10.5,null,10.5,null,10.5,null,10.5,null,null,null,null,10.5,null,11.5,null,11.5,null,null,null,null,null,11.5,11.5,null,null,11.5]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,10.699999809265137,null,10.600000381469727,null,10.399999618530273,null,10.399999618530273,null,null,null,null,10.399999618530273,null,7.4000000953674316,null,7.4000000953674316,null,null,null,null,null,7.4000000953674316,7.3000001907348633,null,null,7.3000001907348633]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.5,null,0.5,null,0.5,null,0.5,null,null,null,null,0.5,null,0.4,null,0.4,null,null,null,null,null,0.4,0.4,null,null,0.4]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"6.5",null,"6.5",null,"6.5",null,"6.5",null,null,null,null,"6.5",null,"6.5",null,"6.5",null,null,null,null,null,"6.5","6.5",null,null,"6.5"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,0.2,null,0.1]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,1,null,1,null,1,null,1,null,null,null,null,1,null,1,null,1,null,null,null,null,null,1,1,null,null,1]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"CHTW","index":49,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"CHTW - Chinchilla Town (33/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T013 - Chinchilla BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is South West"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x33/11kV 5MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.3%, 2020 S 0.1% W 0.1%, 2021 S 0.0% W 0.0%, 2022 S 0.0% W 0.0%, 2023 S -0.3% W -0.3"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"7.9 MVA on 13/02/2019 at 16:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,13.699999809265137,null,13.699999809265137,null,13.699999809265137,null,13.699999809265137,null,null,null,null,13.699999809265137,null,15,null,15,null,null,null,null,null,15,15,null,null,15]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,9.1999998092651367,null,9.1000003814697266,null,9.1000003814697266,null,9.1000003814697266,null,null,null,null,9.1000003814697266,null,6.1999998092651367,null,6.1999998092651367,null,null,null,null,null,6.1999998092651367,6.1999998092651367,null,null,6.1999998092651367]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.95499999999999996,null,0.95499999999999996,null,0.95499999999999996,null,0.95499999999999996,null,null,null,null,0.95499999999999996,null,0.96599999999999997,null,0.96599999999999997,null,null,null,null,null,0.96599999999999997,0.96599999999999997,null,null,0.96599999999999997]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,7.5,null,7.5,null,7.5,null,7.5,null,null,null,null,7.5,null,7.5,null,7.5,null,null,null,null,null,7.5,7.5,null,null,7.5]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,8.1999998092651367,null,8.1999998092651367,null,8.1000003814697266,null,8.1000003814697266,null,null,null,null,8.1000003814697266,null,5.8000001907348633,null,5.8000001907348633,null,null,null,null,null,5.8000001907348633,5.8000001907348633,null,null,5.8000001907348633]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.4,null,0.4,null,0.4,null,0.4,null,null,null,null,0.4,null,0.3,null,0.3,null,null,null,null,null,0.3,0.3,null,null,0.3]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"12",null,"12",null,"12",null,"12",null,null,null,null,"12",null,"12",null,"12",null,null,null,null,null,"12","12",null,null,"12"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,0.7,null,0.7,null,0.6,null,0.6,null,null,null,null,0.6]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0.69999998807907104,null,0.69999998807907104,null,0.69999998807907104,null,0.69999998807907104,null,null,null,null,0.69999998807907104,null,0.69999998807907104,null,0.69999998807907104,null,null,null,null,null,0.69999998807907104,0.69999998807907104,null,null,0.69999998807907104]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,2.5,null,2.5,null,2.5,null,2.5,null,null,null,null,2.5,null,2.5,null,2.5,null,null,null,null,null,2.5,2.5,null,null,2.5]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"CHUM","index":50,"n_rows":48,"n_cols":35,"rows_kept":48,"cut":false,"hidden":false,"merged":[[0,2,0,40],[2,1,2,5],[2,8,4,20],[2,23,3,24],[2,26,4,37],[6,1,8,5],[6,8,6,36],[8,8,9,36],[11,8,11,36],[13,3,14,11],[13,14,13,26],[16,17,17,31],[17,3,18,11],[17,14,18,15],[21,4,22,8],[21,9,21,21],[21,22,21,34],[22,9,22,10],[22,11,22,12],[22,13,22,14],[22,15,22,19],[22,20,22,21],[22,22,22,23],[22,24,22,29],[22,31,22,33],[23,4,23,8],[23,9,23,10],[23,11,23,12],[23,13,23,14],[23,15,23,19],[23,20,23,21],[23,22,23,23],[23,24,23,29],[23,31,23,33],[24,4,24,8],[24,9,24,10],[24,11,24,12],[24,13,24,14],[24,15,24,19],[24,20,24,21],[24,22,24,23],[24,24,24,29],[24,31,24,33],[25,4,25,8],[25,9,25,10],[25,11,25,12],[25,13,25,14],[25,15,25,19],[25,20,25,21],[25,22,25,23],[25,24,25,29],[25,31,25,33],[26,4,26,8],[26,9,26,10],[26,11,26,12],[26,13,26,14],[26,15,26,19],[26,20,26,21],[26,22,26,23],[26,24,26,29],[26,31,26,33],[27,4,27,8],[27,9,27,10],[27,11,27,12],[27,13,27,14],[27,15,27,19],[27,20,27,21],[27,22,27,23],[27,24,27,29],[27,31,27,33],[28,4,28,8],[28,9,28,10],[28,11,28,12],[28,13,28,14],[28,15,28,19],[28,20,28,21],[28,22,28,23],[28,24,28,29],[28,31,28,33],[29,4,29,8],[29,9,29,10],[29,11,29,12],[29,13,29,14],[29,15,29,19],[29,20,29,21],[29,22,29,23],[29,24,29,29],[29,31,29,33],[30,4,30,8],[30,9,30,10],[30,11,30,12],[30,13,30,14],[30,15,30,19],[30,20,30,21],[30,22,30,23],[30,24,30,29],[30,31,30,33],[31,4,31,8],[31,9,31,10],[31,11,31,12],[31,13,31,14],[31,15,31,19],[31,20,31,21],[31,22,31,23],[31,24,31,29],[31,31,31,33],[32,4,32,8],[32,9,32,10],[32,11,32,12],[32,13,32,14],[32,15,32,19],[32,20,32,21],[32,22,32,23],[32,24,32,29],[32,31,32,33],[33,4,33,8],[33,9,33,10],[33,11,33,12],[33,13,33,14],[33,15,33,19],[33,20,33,21],[33,22,33,23],[33,24,33,29],[33,31,33,33],[34,4,34,8],[34,9,34,10],[34,11,34,12],[34,13,34,14],[34,15,34,19],[34,20,34,21],[34,22,34,23],[34,24,34,29],[34,31,34,33],[35,4,35,8],[35,9,35,10],[35,11,35,12],[35,13,35,14],[35,15,35,19],[35,20,35,21],[35,22,35,23],[35,24,35,29],[35,31,35,33],[36,4,36,8],[36,9,36,10],[36,11,36,12],[36,13,36,14],[36,15,36,19],[36,20,36,21],[36,22,36,23],[36,24,36,29],[36,31,36,33],[37,4,37,8],[37,9,37,10],[37,11,37,12],[37,13,37,14],[37,15,37,19],[37,20,37,21],[37,22,37,23],[37,24,37,29],[37,31,37,33],[39,31,39,33],[38,4,38,8],[38,9,38,10],[38,11,38,12],[38,13,38,14],[38,15,38,19],[38,20,38,21],[38,22,38,23],[38,24,38,29],[38,31,38,33],[40,4,40,8],[40,9,40,10],[40,11,40,12],[40,13,40,14],[40,15,40,19],[39,22,39,23],[39,24,39,29],[39,4,39,8],[39,9,39,10],[39,11,39,12],[39,13,39,14],[39,15,39,19],[39,20,39,21],[40,22,40,23],[40,24,40,29],[40,31,40,33],[42,20,42,21],[42,22,42,23],[40,20,40,21],[42,9,42,10],[42,11,42,12],[42,13,42,14],[42,15,42,19],[41,9,41,10],[41,11,41,12],[41,13,41,14],[41,15,41,19],[43,31,43,33],[41,20,41,21],[43,22,43,23],[43,24,43,29],[41,22,41,23],[41,24,41,29],[47,2,47,38],[42,24,42,29],[42,31,42,33],[43,4,43,8],[43,9,43,10],[43,11,43,12],[43,13,43,14],[43,15,43,19],[43,20,43,21],[42,4,42,8],[41,31,41,33],[41,4,41,8]]}
[null,null,"Bulk Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,"CHUM - Chumvale BSP (220/66kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"QMCH - Mica Creek 220kV TCP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,"Region is Nth Queensland"]
[]
[null,null,null,null,null,null,null,null,"Transformer size is 1x220/66kV 30/40MVA ONAN/ONAF"]
[]
[]
[null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,"7.1 MVA on 03/12/2018 at 18:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,49.799999237060547,null,49.799999237060547,null,49.799999237060547,null,49.799999237060547,null,null,null,null,49.799999237060547,null,49.799999237060547,null,49.799999237060547,null,null,null,null,null,49.799999237060547,49.799999237060547,null,null,49.799999237060547]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,8.6999998092651367,null,8.6000003814697266,null,8.5,null,8.3999996185302734,null,null,null,null,8.3999996185302734,null,6,null,5.9000000953674316,null,null,null,null,null,5.9000000953674316,5.8000001907348633,null,null,5.8000001907348633]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,0.98199999999999998,null,0.98199999999999998,null,0.98199999999999998,null,0.98199999999999998,null,null,null,null,0.98199999999999998,null,0.98599999999999999,null,0.98599999999999999,null,null,null,null,null,0.98599999999999999,0.98599999999999999,null,null,0.98599999999999999]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,8,null,7.9000000953674316,null,7.8000001907348633,null,7.6999998092651367,null,null,null,null,7.6999998092651367,null,5.5999999046325684,null,5.5999999046325684,null,null,null,null,null,5.5,5.5,null,null,5.5]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,0.4,null,0.4,null,0.4,null,0.4,null,null,null,null,0.4,null,0.3,null,0.3,null,null,null,null,null,0.3,0.3,null,null,0.3]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,"16.5",null,"16.5",null,"16.5",null,"16.5",null,null,null,null,"16.5",null,"16.5",null,"16.5",null,null,null,null,null,"16.5","16.5",null,null,"16.5"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,8,null,7.9,null,7.8,null,7.7,null,null,null,null,7.7,null,5.6,null,5.6,null,null,null,null,null,5.5,5.5,null,null,5.5]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,6.8000001907348633,null,6.8000001907348633,null,6.8000001907348633,null,6.8000001907348633,null,null,null,null,6.8000001907348633,null,6.8000001907348633,null,6.8000001907348633,null,null,null,null,null,6.8000001907348633,6.8000001907348633,null,null,6.8000001907348633]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,1.2999999523162842,null,1.2999999523162842,null,1.2999999523162842,null,1.2999999523162842,null,null,null,null,1.2999999523162842,null,1.2999999523162842,null,1.2999999523162842,null,null,null,null,null,1.2999999523162842,1.2999999523162842,null,null,1.2999999523162842]
[null,null,null,null,"Shed(30min)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[null,null,null,null,null,"Note: Transfer capacity under review as part of the Cloncurry Supply Reinforcement project."]
[]
[]
[null,null,"Return to Index"]

{"sheet":"CLER","index":51,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"CLER - Clermont (66/22kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T071 - Clermont BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Capricornia"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1xCLERSS CL-T6 11KV TRANSF 6 TRANSF CL-T6;1xCLERSS TRANSF 5 TRANSFORMER"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -2.9%, 2020 S -0.9% W -0.9%2021 S -1.2% W -1.2%2022 S 0.7% W 0.7%, 2023 S 0.4% W 0.4%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"10.1 MVA on 03/12/2018 at 19:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,20,null,20,null,20,null,20,null,null,null,null,20,null,20,null,20,null,null,null,null,null,20,20,null,null,20]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,11.399999618530273,null,11.199999809265137,null,11.199999809265137,null,11.199999809265137,null,null,null,null,11.399999618530273,null,7.8000001907348633,null,7.6999998092651367,null,null,null,null,null,7.5999999046325684,7.5999999046325684,null,null,7.6999998092651367]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.99,null,0.99099999999999999,null,0.99099999999999999,null,0.99099999999999999,null,null,null,null,0.99,null,0.999,null,0.999,null,null,null,null,null,0.999,0.999,null,null,0.999]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,10,null,10,null,10,null,10,null,null,null,null,10,null,10,null,10,null,null,null,null,null,10,10,null,null,10]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,10.100000381469727,null,9.8999996185302734,null,9.8999996185302734,null,9.8999996185302734,null,null,null,null,10.100000381469727,null,7.0999999046325684,null,7,null,null,null,null,null,6.9000000953674316,7,null,null,7]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.5,null,0.5,null,0.5,null,0.5,null,null,null,null,0.5,null,0.4,null,0.4,null,null,null,null,null,0.3,0.4,null,null,0.4]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"13.5",null,"13.5",null,"13.5",null,"13.5",null,null,null,null,"13.5",null,"13.5",null,"13.5",null,null,null,null,null,"13.5","13.5",null,null,"13.5"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,0.1,null,null,null,null,null,null,null,null,null,null,0.1]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0.20000000298023224,null,0.20000000298023224,null,0.20000000298023224,null,0.20000000298023224,null,null,null,null,0.20000000298023224,null,0.20000000298023224,null,0.20000000298023224,null,null,null,null,null,0.20000000298023224,0.20000000298023224,null,null,0.20000000298023224]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"CLIF","index":52,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"CLIF - Clifton (33/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T043 - South Toowoomba BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is South West"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x33/11kV 3MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.3%, 2020 S 0.6% W 0.6%, 2021 S 0.5% W 0.5%, 2022 S 0.3% W 0.3%, 2023 S 0.1% W 0.1%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"4 MVA on 19/02/2019 at 18:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,8,null,8,null,8,null,8,null,null,null,null,8,null,8.6999998092651367,null,8.6999998092651367,null,null,null,null,null,8.6999998092651367,8.6999998092651367,null,null,8.6999998092651367]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,4.4000000953674316,null,4.4000000953674316,null,4.3000001907348633,null,4.3000001907348633,null,null,null,null,4.4000000953674316,null,4,null,4,null,null,null,null,null,4,4,null,null,4]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.999,null,0.999,null,0.999,null,0.999,null,null,null,null,0.999,null,0.999,null,0.999,null,null,null,null,null,0.999,0.999,null,null,0.999]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,4.4000000953674316,null,4.4000000953674316,null,4.4000000953674316,null,4.4000000953674316,null,null,null,null,4.4000000953674316,null,4.5,null,4.5,null,null,null,null,null,4.5,4.5,null,null,4.5]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,3.9000000953674316,null,3.9000000953674316,null,3.9000000953674316,null,3.9000000953674316,null,null,null,null,3.9000000953674316,null,3.7000000476837158,null,3.7000000476837158,null,null,null,null,null,3.7000000476837158,3.7000000476837158,null,null,3.7000000476837158]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.2,null,0.2,null,0.2,null,0.2,null,null,null,null,0.2,null,0.2,null,0.2,null,null,null,null,null,0.2,0.2,null,null,0.2]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"71",null,"71",null,"71",null,"71",null,null,null,null,"71",null,"71",null,"71",null,null,null,null,null,"71","71",null,null,"71"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0.60000002384185791,null,0.60000002384185791,null,0.60000002384185791,null,0.60000002384185791,null,null,null,null,0.60000002384185791,null,0.60000002384185791,null,0.60000002384185791,null,null,null,null,null,0.60000002384185791,0.60000002384185791,null,null,0.60000002384185791]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"CLIN","index":53,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"CLIN - Clinton (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T074 - Gladstone North BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Capricornia"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/11kV 16/20/25MVA ONAN/ONAF/ODAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.6%, 2020 S -0.3% W -0.3%2021 S -0.1% W -0.1%2022 S 0.0% W 0.0%, 2023 S -0.3% W -0.3"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"14.6 MVA on 28/11/2018 at 13:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,70.599998474121094,null,70.599998474121094,null,70.599998474121094,null,70.599998474121094,null,null,null,null,70.599998474121094,null,74.800003051757813,null,74.800003051757813,null,null,null,null,null,74.800003051757813,74.800003051757813,null,null,74.800003051757813]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,16,null,15.899999618530273,null,15.699999809265137,null,15.699999809265137,null,null,null,null,15.800000190734863,null,9.3999996185302734,null,9.3999996185302734,null,null,null,null,null,9.3000001907348633,9.3000001907348633,null,null,9.3000001907348633]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.998,null,0.998,null,0.999,null,0.999,null,null,null,null,0.998,null,0.92600000000000005,null,0.92600000000000005,null,null,null,null,null,0.92600000000000005,0.92600000000000005,null,null,0.92600000000000005]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,37.400001525878906,null,37.400001525878906,null,37.400001525878906,null,37.400001525878906,null,null,null,null,37.400001525878906,null,37.400001525878906,null,37.400001525878906,null,null,null,null,null,37.400001525878906,37.400001525878906,null,null,37.400001525878906]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,14.800000190734863,null,14.699999809265137,null,14.600000381469727,null,14.600000381469727,null,null,null,null,14.600000381469727,null,9.1999998092651367,null,9.1000003814697266,null,null,null,null,null,9.1000003814697266,9.1000003814697266,null,null,9.1000003814697266]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.7,null,0.7,null,0.7,null,0.7,null,null,null,null,0.7,null,0.5,null,0.5,null,null,null,null,null,0.5,0.5,null,null,0.5]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"6.5",null,"6.5",null,"6.5",null,"6.5",null,null,null,null,"6.5",null,"6.5",null,"6.5",null,null,null,null,null,"6.5","6.5",null,null,"6.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,3,null,3,null,3,null,3,null,null,null,null,3,null,3,null,3,null,null,null,null,null,3,3,null,null,3]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,4,null,4,null,4,null,4,null,null,null,null,4,null,4,null,4,null,null,null,null,null,4,4,null,null,4]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"CLON","index":54,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"CLON - Cloncurry (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"CHUM - Chumvale BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Nth Queensland"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/11kV 2/2.3MVA ONAN/ONAF;1x66/11kV 3MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -1.0%, 2020 S -0.4% W -0.4%2021 S -0.5% W -0.5%2022 S -0.7% W -0.7%2023 S -1.1% W -1.1"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"3.5 MVA on 06/11/2018 at 17:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,6.6999998092651367,null,6.6999998092651367,null,6.6999998092651367,null,6.6999998092651367,null,null,null,null,6.6999998092651367,null,6.9000000953674316,null,6.9000000953674316,null,null,null,null,null,6.9000000953674316,6.9000000953674316,null,null,6.9000000953674316]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,4.3000001907348633,null,4.3000001907348633,null,4.1999998092651367,null,4.1999998092651367,null,null,null,null,4.0999999046325684,null,2.0999999046325684,null,2.0999999046325684,null,null,null,null,null,2,2,null,null,2]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.97899999999999998,null,0.97899999999999998,null,0.97899999999999998,null,0.97899999999999998,null,null,null,null,0.97899999999999998,null,0.98499999999999999,null,0.98499999999999999,null,null,null,null,null,0.98499999999999999,0.98499999999999999,null,null,0.98499999999999999]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,3.4000000953674316,null,3.4000000953674316,null,3.4000000953674316,null,3.4000000953674316,null,null,null,null,3.4000000953674316,null,3.4000000953674316,null,3.4000000953674316,null,null,null,null,null,3.4000000953674316,3.4000000953674316,null,null,3.4000000953674316]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,4,null,3.9000000953674316,null,3.9000000953674316,null,3.7999999523162842,null,null,null,null,3.7999999523162842,null,1.8999999761581421,null,1.8999999761581421,null,null,null,null,null,1.8999999761581421,1.8999999761581421,null,null,1.8999999761581421]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.2,null,0.2,null,0.2,null,0.2,null,null,null,null,0.2,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"1068.5",null,"1068.5",null,"1068.5",null,"1068.5",null,null,null,null,"1068.5",null,"1068.5",null,"1068.5",null,null,null,null,null,"1068.5","1068.5",null,null,"1068.5"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,0.6,null,0.5,null,0.5,null,0.4,null,null,null,null,0.4]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,1.7000000476837158,null,1.7000000476837158,null,1.7000000476837158,null,1.7000000476837158,null,null,null,null,1.7000000476837158,null,1.7000000476837158,null,1.7000000476837158,null,null,null,null,null,1.7000000476837158,1.7000000476837158,null,null,1.7000000476837158]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"CLSO","index":55,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"CLSO - Clare South (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T193 - Clare South BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Nth Queensland"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/11kV 6.3MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.6%, 2020 S -0.0% W -0.0%2021 S -0.3% W -0.3%2022 S -0.4% W -0.4%2023 S -0.8% W -0.8"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"2.8 MVA on 14/11/2018 at 18:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,7.5,null,7.5,null,7.5,null,7.5,null,null,null,null,7.5,null,8.3000001907348633,null,8.3000001907348633,null,null,null,null,null,8.3000001907348633,8.3000001907348633,null,null,8.3000001907348633]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,3.0999999046325684,null,3.0999999046325684,null,3.0999999046325684,null,3,null,null,null,null,3,null,1.7000000476837158,null,1.7000000476837158,null,null,null,null,null,1.7000000476837158,1.7000000476837158,null,null,1.7000000476837158]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.877,null,0.877,null,0.877,null,0.877,null,null,null,null,0.877,null,0.86599999999999999,null,0.86599999999999999,null,null,null,null,null,0.86599999999999999,0.86599999999999999,null,null,0.86599999999999999]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,3,null,3,null,3,null,3,null,null,null,null,3,null,1.6000000238418579,null,1.6000000238418579,null,null,null,null,null,1.6000000238418579,1.6000000238418579,null,null,1.6000000238418579]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.2,null,0.2,null,0.2,null,0.2,null,null,null,null,0.2,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"11",null,"11",null,"11",null,"11",null,null,null,null,"11",null,"11",null,"11",null,null,null,null,null,"11","11",null,null,"11"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,3,null,3,null,3,null,3,null,null,null,null,3,null,1.6,null,1.6,null,null,null,null,null,1.6,1.6,null,null,1.6]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,2.2000000476837158,null,2.2000000476837158,null,2.2000000476837158,null,2.2000000476837158,null,null,null,null,2.2000000476837158,null,2.2000000476837158,null,2.2000000476837158,null,null,null,null,null,2.2000000476837158,2.2000000476837158,null,null,2.2000000476837158]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,1,null,1,null,1,null,1,null,null,null,null,1,null,1,null,1,null,null,null,null,null,1,1,null,null,1]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"COME","index":56,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"COME - Comet (66/22kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T032 - Blackwater BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Capricornia"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/22kV 5MVA ON;1x66/22kV 2MVA ON(Standby)"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -1.3%, 2020 S -0.8% W -0.8%2021 S -0.9% W -0.9%2022 S -0.8% W -0.8%2023 S -0.9% W -0.9"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"2.9 MVA on 15/12/2018 at 20:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,5.5,null,5.5,null,5.5,null,5.5,null,null,null,null,5.5,null,6.4000000953674316,null,6.4000000953674316,null,null,null,null,null,6.4000000953674316,6.4000000953674316,null,null,6.4000000953674316]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,3,null,2.9000000953674316,null,2.9000000953674316,null,2.9000000953674316,null,null,null,null,2.9000000953674316,null,2.5999999046325684,null,2.5999999046325684,null,null,null,null,null,2.5999999046325684,2.5,null,null,2.5]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.89500000000000002,null,0.89500000000000002,null,0.89500000000000002,null,0.89500000000000002,null,null,null,null,0.89500000000000002,null,0.79400000000000004,null,0.79400000000000004,null,null,null,null,null,0.79400000000000004,0.79400000000000004,null,null,0.79400000000000004]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,2.9000000953674316,null,2.9000000953674316,null,2.7999999523162842,null,2.7999999523162842,null,null,null,null,2.7999999523162842,null,2.5999999046325684,null,2.5999999046325684,null,null,null,null,null,2.5999999046325684,2.5,null,null,2.5]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.1,null,0.1,null,0.1,null,0.1,null,null,null,null,0.1,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"6.5",null,"6.5",null,"6.5",null,"6.5",null,null,null,null,"6.5",null,"6.5",null,"6.5",null,null,null,null,null,"6.5","6.5",null,null,"6.5"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,2.9,null,2.9,null,2.8,null,2.8,null,null,null,null,2.8,null,2.6,null,2.6,null,null,null,null,null,2.6,2.5,null,null,2.5]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,2.4000000953674316,null,2.4000000953674316,null,2.4000000953674316,null,2.4000000953674316,null,null,null,null,2.4000000953674316,null,2.4000000953674316,null,2.4000000953674316,null,null,null,null,null,2.4000000953674316,2.4000000953674316,null,null,2.4000000953674316]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0.5,null,0.5,null,0.5,null,0.5,null,null,null,null,0.5,null,0.5,null,0.5,null,null,null,null,null,0.5,0.5,null,null,0.5]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"COOK","index":57,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"COOK - Cooktown (66/22kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T159 - Lakeland BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Far North"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/22kV 8/10MVA ONAN/ONAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.2%, 2020 S 0.7% W 0.7%, 2021 S 0.5% W 0.5%, 2022 S 0.2% W 0.2%, 2023 S -0.1% W -0.1"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"4.8 MVA on 26/11/2018 at 19:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,21.5,null,21.5,null,21.5,null,21.5,null,null,null,null,21.5,null,24.600000381469727,null,24.600000381469727,null,null,null,null,null,24.600000381469727,24.600000381469727,null,null,24.600000381469727]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,5,null,5,null,5,null,5,null,null,null,null,5,null,3.2999999523162842,null,3.2999999523162842,null,null,null,null,null,3.2999999523162842,3.2999999523162842,null,null,3.2999999523162842]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.96799999999999997,null,0.96799999999999997,null,0.96799999999999997,null,0.96799999999999997,null,null,null,null,0.96799999999999997,null,0.98199999999999998,null,0.98199999999999998,null,null,null,null,null,0.98199999999999998,0.98199999999999998,null,null,0.98199999999999998]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,12.600000381469727,null,12.600000381469727,null,12.600000381469727,null,12.600000381469727,null,null,null,null,12.600000381469727,null,13.600000381469727,null,13.600000381469727,null,null,null,null,null,13.600000381469727,13.600000381469727,null,null,13.600000381469727]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,4.5999999046325684,null,4.5999999046325684,null,4.5999999046325684,null,4.5999999046325684,null,null,null,null,4.5999999046325684,null,3.0999999046325684,null,3.2000000476837158,null,null,null,null,null,3.2000000476837158,3.2000000476837158,null,null,3.2000000476837158]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.2,null,0.2,null,0.2,null,0.2,null,null,null,null,0.2,null,0.2,null,0.2,null,null,null,null,null,0.2,0.2,null,null,0.2]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"10.5",null,"10.5",null,"10.5",null,"10.5",null,null,null,null,"10.5",null,"10.5",null,"10.5",null,null,null,null,null,"10.5","10.5",null,null,"10.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"COOM","index":58,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"COOM - Coominglah (66/22kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T026 - Biloela BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Capricornia"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/22kV 2MVA ONAN;1x66/22kV 2MVA ONAN(Standby)"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.3%, 2020 S -0.2% W -0.2%2021 S -0.2% W -0.2%2022 S -0.2% W -0.2%2023 S -0.2% W -0.2"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"1.5 MVA on 21/02/2019 at 19:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,2.5999999046325684,null,2.5999999046325684,null,2.5999999046325684,null,2.5999999046325684,null,null,null,null,2.5999999046325684,null,3,null,3,null,null,null,null,null,3,3,null,null,3]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,1.6000000238418579,null,1.5,null,1.5,null,1.5,null,null,null,null,1.5,null,1.6000000238418579,null,1.6000000238418579,null,null,null,null,null,1.6000000238418579,1.6000000238418579,null,null,1.6000000238418579]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.94299999999999995,null,0.94299999999999995,null,0.94299999999999995,null,0.94299999999999995,null,null,null,null,0.94299999999999995,null,0.90600000000000003,null,0.90600000000000003,null,null,null,null,null,0.90600000000000003,0.90600000000000003,null,null,0.90600000000000003]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,1.3999999761581421,null,1.3999999761581421,null,1.3999999761581421,null,1.3999999761581421,null,null,null,null,1.3999999761581421,null,1.5,null,1.5,null,null,null,null,null,1.5,1.5,null,null,1.5]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.1,null,0.1,null,0.1,null,0.1,null,null,null,null,0.1,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"4",null,"4",null,"4",null,"4",null,null,null,null,"4",null,"4",null,"4",null,null,null,null,null,"4","4",null,null,"4"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,1.4,null,1.4,null,1.4,null,1.4,null,null,null,null,1.4,null,1.5,null,1.5,null,null,null,null,null,1.5,1.5,null,null,1.5]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,3,null,3,null,3,null,3,null,null,null,null,3,null,3,null,3,null,null,null,null,null,3,3,null,null,3]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"CRAI","index":59,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"CRAI - Craiglie (132/22kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"QTUH - Turkinje 132kV TCP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Far North"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x132/22kV 15/20MVA ONAN/ONAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.4%, 2020 S 0.6% W 0.6%, 2021 S 0.5% W 0.5%, 2022 S 0.4% W 0.4%, 2023 S 0.1% W 0.1%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"16.6 MVA on 29/11/2018 at 11:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,47.099998474121094,null,47.099998474121094,null,47.099998474121094,null,47.099998474121094,null,null,null,null,47.099998474121094,null,53.400001525878906,null,53.400001525878906,null,null,null,null,null,53.400001525878906,53.400001525878906,null,null,53.400001525878906]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,18.299999237060547,null,18.299999237060547,null,18.200000762939453,null,18.200000762939453,null,null,null,null,18.399999618530273,null,12.899999618530273,null,12.899999618530273,null,null,null,null,null,12.899999618530273,13,null,null,13.100000381469727]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.98499999999999999,null,0.98499999999999999,null,0.98499999999999999,null,0.98499999999999999,null,null,null,null,0.98499999999999999,null,0.98899999999999999,null,0.98899999999999999,null,null,null,null,null,0.98899999999999999,0.98899999999999999,null,null,0.98899999999999999]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,27.600000381469727,null,27.600000381469727,null,27.600000381469727,null,27.600000381469727,null,null,null,null,27.600000381469727,null,29.799999237060547,null,29.799999237060547,null,null,null,null,null,29.799999237060547,29.799999237060547,null,null,29.799999237060547]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,17.200000762939453,null,17.200000762939453,null,17.100000381469727,null,17.200000762939453,null,null,null,null,17.299999237060547,null,11.800000190734863,null,11.899999618530273,null,null,null,null,null,11.899999618530273,11.899999618530273,null,null,12]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.9,null,0.9,null,0.9,null,0.9,null,null,null,null,0.9,null,0.6,null,0.6,null,null,null,null,null,0.6,0.6,null,null,0.6]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"19.5",null,"19.5",null,"19.5",null,"19.5",null,null,null,null,"19.5",null,"19.5",null,"19.5",null,null,null,null,null,"19.5","19.5",null,null,"19.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,2,null,2,null,2,null,2,null,null,null,null,2,null,2,null,2,null,null,null,null,null,2,2,null,null,2]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,2,null,2,null,2,null,2,null,null,null,null,2,null,2,null,2,null,null,null,null,null,2,2,null,null,2]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"CRAN","index":60,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"CRAN - Cranbrook (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"TMES - Townsville Mesh"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Nth Queensland"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/11kV 15/20/25MVA ONAN/ONAF/OFDAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.6%, 2020 S -0.6% W -0.6%2021 S -0.8% W -0.8%2022 S -1.0% W -1.0%2023 S -1.3% W -1.3"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"17.6 MVA on 20/02/2019 at 17:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,55.599998474121094,null,55.599998474121094,null,55.599998474121094,null,55.599998474121094,null,null,null,null,55.599998474121094,null,57.900001525878906,null,57.900001525878906,null,null,null,null,null,57.900001525878906,57.900001525878906,null,null,57.900001525878906]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,19.5,null,19.200000762939453,null,18.899999618530273,null,18.600000381469727,null,null,null,null,18.5,null,10.100000381469727,null,10,null,null,null,null,null,9.8999996185302734,9.8000001907348633,null,null,9.6999998092651367]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.97099999999999997,null,0.97099999999999997,null,0.97099999999999997,null,0.97099999999999997,null,null,null,null,0.97099999999999997,null,0.98299999999999998,null,0.98299999999999998,null,null,null,null,null,0.98299999999999998,0.98299999999999998,null,null,0.98299999999999998]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,30.5,null,30.5,null,30.5,null,30.5,null,null,null,null,30.5,null,31.899999618530273,null,31.899999618530273,null,null,null,null,null,31.899999618530273,31.899999618530273,null,null,31.899999618530273]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,17.100000381469727,null,16.899999618530273,null,16.5,null,16.299999237060547,null,null,null,null,16.299999237060547,null,9.8000001907348633,null,9.6999998092651367,null,null,null,null,null,9.6000003814697266,9.5,null,null,9.3999996185302734]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.9,null,0.8,null,0.8,null,0.8,null,null,null,null,0.8,null,0.5,null,0.5,null,null,null,null,null,0.5,0.5,null,null,0.5]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"7",null,"7",null,"7",null,"7",null,null,null,null,"7",null,"7",null,"7",null,null,null,null,null,"7","7",null,null,"7"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"CRED","index":61,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"CRED - Crediton (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T141 - Pioneer Valley BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Mackay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/11kV 1MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.7%, 2020 S 1.2% W 1.2%, 2021 S 1.2% W 1.2%, 2022 S 0.4% W 0.4%, 2023 S 0.1% W 0.1%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"0.5 MVA on 28/11/2018 at 16:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,1.1000000238418579,null,1.1000000238418579,null,1.1000000238418579,null,1.1000000238418579,null,null,null,null,1.1000000238418579,null,1.1000000238418579,null,1.1000000238418579,null,null,null,null,null,1.1000000238418579,1.1000000238418579,null,null,1.1000000238418579]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,0.5,null,0.5,null,0.5,null,0.5,null,null,null,null,0.5,null,0.30000001192092896,null,0.30000001192092896,null,null,null,null,null,0.30000001192092896,0.30000001192092896,null,null,0.30000001192092896]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.94799999999999995,null,0.94799999999999995,null,0.94799999999999995,null,0.94799999999999995,null,null,null,null,0.94799999999999995,null,0.97,null,0.97,null,null,null,null,null,0.97,0.97,null,null,0.97]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,0.5,null,0.5,null,0.5,null,0.5,null,null,null,null,0.5,null,0.30000001192092896,null,0.30000001192092896,null,null,null,null,null,0.30000001192092896,0.30000001192092896,null,null,0.30000001192092896]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"5",null,"5",null,"5",null,"5",null,null,null,null,"5",null,"5",null,"5",null,null,null,null,null,"5","5",null,null,"5"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,0.5,null,0.5,null,0.5,null,0.5,null,null,null,null,0.5,null,0.3,null,0.3,null,null,null,null,null,0.3,0.3,null,null,0.3]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0.60000002384185791,null,0.60000002384185791,null,0.60000002384185791,null,0.60000002384185791,null,null,null,null,0.60000002384185791,null,0.60000002384185791,null,0.60000002384185791,null,null,null,null,null,0.60000002384185791,0.60000002384185791,null,null,0.60000002384185791]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"CRNE","index":62,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"CRNE - Crows Nest (33/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T029 - Postmans Ridge BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is South West"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x33/11kV 6.3MVA ONAN;1x33/11kV 1.5MVA ON(Standby)"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.1%, 2020 S 0.3% W 0.3%, 2021 S 0.3% W 0.3%, 2022 S 0.1% W 0.1%, 2023 S -0.3% W -0.3"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"4.3 MVA on 19/06/2018 at 18:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,8.3000001907348633,null,8.3000001907348633,null,8.3000001907348633,null,8.3000001907348633,null,null,null,null,8.3000001907348633,null,9.3999996185302734,null,9.3999996185302734,null,null,null,null,null,9.3999996185302734,9.3999996185302734,null,null,9.3999996185302734]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,4.5,null,4.5,null,4.4000000953674316,null,4.4000000953674316,null,null,null,null,4.4000000953674316,null,4.5999999046325684,null,4.5999999046325684,null,null,null,null,null,4.5999999046325684,4.5999999046325684,null,null,4.5999999046325684]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.98499999999999999,null,0.98499999999999999,null,0.98499999999999999,null,0.98499999999999999,null,null,null,null,0.98499999999999999,null,0.996,null,0.996,null,null,null,null,null,0.996,0.996,null,null,0.996]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,4,null,4,null,4,null,4,null,null,null,null,4,null,4.4000000953674316,null,4.4000000953674316,null,null,null,null,null,4.4000000953674316,4.4000000953674316,null,null,4.4000000953674316]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.2,null,0.2,null,0.2,null,0.2,null,null,null,null,0.2,null,0.2,null,0.2,null,null,null,null,null,0.2,0.2,null,null,0.2]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"6.5",null,"6.5",null,"6.5",null,"6.5",null,null,null,null,"6.5",null,"6.5",null,"6.5",null,null,null,null,null,"6.5","6.5",null,null,"6.5"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,4,null,4,null,4,null,4,null,null,null,null,4,null,4.4000000000000004,null,4.4000000000000004,null,null,null,null,null,4.4000000000000004,4.4000000000000004,null,null,4.4000000000000004]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,1.5,null,1.5,null,1.5,null,1.5,null,null,null,null,1.5,null,1.5,null,1.5,null,null,null,null,null,1.5,1.5,null,null,1.5]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,10,null,10,null,10,null,10,null,null,null,null,10,null,10,null,10,null,null,null,null,null,10,10,null,null,10]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"CROY","index":63,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"CROY - Croydon (66/22kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"GEOR - Georgetown BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Far North"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/22kV 2MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -1.2%, 2020 S -0.8% W -0.8%2021 S -1.1% W -1.1%2022 S -0.5% W -0.5%2023 S -0.8% W -0.8"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"0.6 MVA on 03/12/2018 at 19:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,5.0999999046325684,null,5.0999999046325684,null,5.0999999046325684,null,5.0999999046325684,null,null,null,null,5.0999999046325684,null,5.4000000953674316,null,5.4000000953674316,null,null,null,null,null,5.4000000953674316,5.4000000953674316,null,null,5.4000000953674316]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,0.60000002384185791,null,0.60000002384185791,null,0.60000002384185791,null,0.60000002384185791,null,null,null,null,0.60000002384185791,null,0.40000000596046448,null,0.40000000596046448,null,null,null,null,null,0.40000000596046448,0.40000000596046448,null,null,0.40000000596046448]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.99299999999999999,null,0.99299999999999999,null,0.99299999999999999,null,0.99299999999999999,null,null,null,null,0.99299999999999999,null,0.98,null,0.98,null,null,null,null,null,0.98,0.98,null,null,0.98]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,3,null,3,null,3,null,3,null,null,null,null,3,null,3,null,3,null,null,null,null,null,3,3,null,null,3]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,0.60000002384185791,null,0.60000002384185791,null,0.60000002384185791,null,0.60000002384185791,null,null,null,null,0.60000002384185791,null,0.40000000596046448,null,0.40000000596046448,null,null,null,null,null,0.40000000596046448,0.40000000596046448,null,null,0.40000000596046448]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"10",null,"10",null,"10",null,"10",null,null,null,null,"10",null,"10",null,"10",null,null,null,null,null,"10","10",null,null,"10"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"CUNN","index":64,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"CUNN - Cunnamulla (66/22kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T083 - Roma 66kV BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is South West"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/11kV 5 MVA;1x66/22kV 5 MVA;1x22/11kV 3 MVA(Standby)"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.0%, 2020 S 0.0% W 0.0%, 2021 S 0.0% W 0.0%, 2022 S 0.0% W 0.0%, 2023 S 0.0% W 0.0%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"4.2 MVA on 22/01/2019 at 18:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,11.300000190734863,null,11.300000190734863,null,11.300000190734863,null,11.300000190734863,null,null,null,null,11.300000190734863,null,13.899999618530273,null,13.899999618530273,null,null,null,null,null,13.899999618530273,13.899999618530273,null,null,13.899999618530273]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,4.8000001907348633,null,4.6999998092651367,null,4.6999998092651367,null,4.6999998092651367,null,null,null,null,4.6999998092651367,null,3.9000000953674316,null,3.7999999523162842,null,null,null,null,null,3.7999999523162842,3.7999999523162842,null,null,3.7999999523162842]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,1,null,1,null,1,null,1,null,null,null,null,1,null,0.999,null,0.999,null,null,null,null,null,0.999,0.999,null,null,0.999]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,6.5,null,6.5,null,6.5,null,6.5,null,null,null,null,6.5,null,7.1999998092651367,null,7.1999998092651367,null,null,null,null,null,7.1999998092651367,7.1999998092651367,null,null,7.1999998092651367]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,4.3000001907348633,null,4.3000001907348633,null,4.1999998092651367,null,4.1999998092651367,null,null,null,null,4.3000001907348633,null,3.5999999046325684,null,3.5999999046325684,null,null,null,null,null,3.5999999046325684,3.5999999046325684,null,null,3.5999999046325684]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.2,null,0.2,null,0.2,null,0.2,null,null,null,null,0.2,null,0.2,null,0.2,null,null,null,null,null,0.2,0.2,null,null,0.2]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"16.5",null,"16.5",null,"16.5",null,"16.5",null,null,null,null,"16.5",null,"16.5",null,"16.5",null,null,null,null,null,"16.5","16.5",null,null,"16.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"DACE","index":65,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"DACE - Dalby Central (33/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T002 - Dalby East BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is South West"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x33/11kV 16/20MVA ONAN/ONAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.8%, 2020 S -0.5% W -0.5%2021 S -0.6% W -0.6%2022 S -0.4% W -0.4%2023 S -0.8% W -0.8"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"15.6 MVA on 13/02/2019 at 16:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,47.599998474121094,null,47.599998474121094,null,47.599998474121094,null,47.599998474121094,null,null,null,null,47.599998474121094,null,50.900001525878906,null,50.900001525878906,null,null,null,null,null,50.900001525878906,50.900001525878906,null,null,50.900001525878906]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,19.200000762939453,null,19,null,18.700000762939453,null,18.600000381469727,null,null,null,null,18.600000381469727,null,14.100000381469727,null,14,null,null,null,null,null,13.899999618530273,13.800000190734863,null,null,13.800000190734863]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.95,null,0.95,null,0.95,null,0.95,null,null,null,null,0.95,null,0.96699999999999997,null,0.96699999999999997,null,null,null,null,null,0.96699999999999997,0.96699999999999997,null,null,0.96699999999999997]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,23.799999237060547,null,23.799999237060547,null,23.799999237060547,null,23.799999237060547,null,null,null,null,23.799999237060547,null,28.100000381469727,null,28.100000381469727,null,null,null,null,null,28.100000381469727,28.100000381469727,null,null,28.100000381469727]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,16.799999237060547,null,16.700000762939453,null,16.399999618530273,null,16.299999237060547,null,null,null,null,16.299999237060547,null,13.100000381469727,null,13,null,null,null,null,null,12.899999618530273,12.800000190734863,null,null,12.699999809265137]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.8,null,0.8,null,0.8,null,0.8,null,null,null,null,0.8,null,0.7,null,0.7,null,null,null,null,null,0.6,0.6,null,null,0.6]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"7",null,"7",null,"7",null,"7",null,null,null,null,"7",null,"7",null,"7",null,null,null,null,null,"7","7",null,null,"7"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"DAGL","index":66,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"DAGL - Dan Gleeson (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"TMES - Townsville Mesh"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Nth Queensland"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/11kV 15/20/25MVA ONAN/ODAN/ODAF;1x66/11kV 15/20/25MVA ONAN/ONAF/ODAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.4%, 2020 S 0.5% W 0.5%, 2021 S 0.5% W 0.5%, 2022 S 0.7% W 0.7%, 2023 S 0.5% W 0.5%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"30.9 MVA on 20/02/2019 at 18:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,42.599998474121094,null,42.599998474121094,null,42.599998474121094,null,42.599998474121094,null,null,null,null,42.599998474121094,null,39.799999237060547,null,39.799999237060547,null,null,null,null,null,39.799999237060547,39.799999237060547,null,null,39.799999237060547]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,36.400001525878906,null,36.5,null,36.299999237060547,null,36.599998474121094,null,null,null,null,37,null,16.899999618530273,null,16.899999618530273,null,null,null,null,null,17,17.100000381469727,null,null,17.200000762939453]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.97799999999999998,null,0.97799999999999998,null,0.97799999999999998,null,0.97799999999999998,null,null,null,null,0.97799999999999998,null,0.98399999999999999,null,0.98399999999999999,null,null,null,null,null,0.98399999999999999,0.98399999999999999,null,null,0.98399999999999999]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,28.100000381469727,null,28.100000381469727,null,28.100000381469727,null,28.100000381469727,null,null,null,null,28.100000381469727,null,26.299999237060547,null,26.299999237060547,null,null,null,null,null,26.299999237060547,26.299999237060547,null,null,26.299999237060547]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,30,null,30,null,29.899999618530273,null,30.100000381469727,null,null,null,null,30.5,null,16.100000381469727,null,16.100000381469727,null,null,null,null,null,16.200000762939453,16.299999237060547,null,null,16.399999618530273]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,1.5,null,1.5,null,1.5,null,1.5,null,null,null,null,1.5,null,0.8,null,0.8,null,null,null,null,null,0.8,0.8,null,null,0.8]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"14",null,"14",null,"14",null,"14",null,null,null,null,"14",null,"14",null,"14",null,null,null,null,null,"14","14",null,null,"14"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,1.9,null,1.9,null,1.8,null,2,null,null,null,null,2.4]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,2.4000000953674316,null,2.4000000953674316,null,2.4000000953674316,null,2.4000000953674316,null,null,null,null,2.4000000953674316,null,2.4000000953674316,null,2.4000000953674316,null,null,null,null,null,2.4000000953674316,2.4000000953674316,null,null,2.4000000953674316]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"DEGI","index":67,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"DEGI - Degilbo (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T131 - Isis BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Wide Bay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/11kV 2MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 2.8 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.4%, 2020 S 0.2% W 0.2%, 2021 S 0.0% W 0.0%, 2022 S -0.3% W -0.3%2023 S -0.6% W -0.6"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"2.4 MVA on 03/12/2018 at 18:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,5.0999999046325684,null,5.0999999046325684,null,5.0999999046325684,null,5.0999999046325684,null,null,null,null,5.0999999046325684,null,5.9000000953674316,null,5.9000000953674316,null,null,null,null,null,5.9000000953674316,5.9000000953674316,null,null,5.9000000953674316]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,2.5,null,2.4000000953674316,null,2.4000000953674316,null,2.4000000953674316,null,null,null,null,2.4000000953674316,null,2.2999999523162842,null,2.2999999523162842,null,null,null,null,null,2.2999999523162842,2.2999999523162842,null,null,2.2999999523162842]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.95899999999999996,null,0.95899999999999996,null,0.95899999999999996,null,0.95899999999999996,null,null,null,null,0.95899999999999996,null,0.97399999999999998,null,0.97399999999999998,null,null,null,null,null,0.97399999999999998,0.97399999999999998,null,null,0.97399999999999998]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,2.9000000953674316,null,2.9000000953674316,null,2.9000000953674316,null,2.9000000953674316,null,null,null,null,2.9000000953674316,null,3,null,3,null,null,null,null,null,3,3,null,null,3]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,2.2000000476837158,null,2.2000000476837158,null,2.2000000476837158,null,2.2000000476837158,null,null,null,null,2.2000000476837158,null,2.2000000476837158,null,2.2000000476837158,null,null,null,null,null,2.0999999046325684,2.0999999046325684,null,null,2.0999999046325684]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.1,null,0.1,null,0.1,null,0.1,null,null,null,null,0.1,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"12.5",null,"12.5",null,"12.5",null,"12.5",null,null,null,null,"12.5",null,"12.5",null,"12.5",null,null,null,null,null,"12.5","12.5",null,null,"12.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0.60000002384185791,null,0.60000002384185791,null,0.60000002384185791,null,0.60000002384185791,null,null,null,null,0.60000002384185791,null,0.60000002384185791,null,0.60000002384185791,null,null,null,null,null,0.60000002384185791,0.60000002384185791,null,null,0.60000002384185791]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"DIMB","index":68,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"DIMB - Dimbulah (66/22kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T055 - Turkinje 66kV BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Far North"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/22kV 10MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -2.2%, 2020 S 0.3% W 0.3%, 2021 S 0.1% W 0.1%, 2022 S -0.0% W -0.0%2023 S -0.4% W -0.4"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"5.4 MVA on 02/12/2018 at 13:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,24.200000762939453,null,24.200000762939453,null,24.200000762939453,null,24.200000762939453,null,null,null,null,24.200000762939453,null,25.899999618530273,null,25.899999618530273,null,null,null,null,null,25.899999618530273,25.899999618530273,null,null,25.899999618530273]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,6.9000000953674316,null,6.8000001907348633,null,6.8000001907348633,null,6.8000001907348633,null,null,null,null,6.8000001907348633,null,3.7000000476837158,null,3.7000000476837158,null,null,null,null,null,3.7000000476837158,3.7000000476837158,null,null,3.7000000476837158]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.91100000000000003,null,0.91100000000000003,null,0.91100000000000003,null,0.91100000000000003,null,null,null,null,0.91100000000000003,null,0.93600000000000005,null,0.93600000000000005,null,null,null,null,null,0.93600000000000005,0.93600000000000005,null,null,0.93600000000000005]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,13.199999809265137,null,13.199999809265137,null,13.199999809265137,null,13.199999809265137,null,null,null,null,13.199999809265137,null,14.399999618530273,null,14.399999618530273,null,null,null,null,null,14.399999618530273,14.399999618530273,null,null,14.399999618530273]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,6,null,6,null,5.9000000953674316,null,5.9000000953674316,null,null,null,null,5.9000000953674316,null,3.5,null,3.5,null,null,null,null,null,3.5,3.5,null,null,3.5]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.3,null,0.3,null,0.3,null,0.3,null,null,null,null,0.3,null,0.2,null,0.2,null,null,null,null,null,0.2,0.2,null,null,0.2]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"7.5",null,"7.5",null,"7.5",null,"7.5",null,null,null,null,"7.5",null,"7.5",null,"7.5",null,null,null,null,null,"7.5","7.5",null,null,"7.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"DURO","index":69,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"DURO - Duchess Road (132/66kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"QMCL - Mica Creek 132kV TCP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Nth Queensland"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x132/11kV 40/60MVA ONAN/ONAF;1x66/11kV 5/6.25MVA ONAN/ONAF(Standby)"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -1.4%, 2020 S -0.9% W -0.9%2021 S -1.0% W -1.0%2022 S -0.4% W -0.4%2023 S -0.7% W -0.7"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"34.3 MVA on 24/01/2019 at 18:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,129.30000305175781,null,129.30000305175781,null,129.30000305175781,null,129.30000305175781,null,null,null,null,129.30000305175781,null,151,null,151,null,null,null,null,null,151,151,null,null,151]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,40.099998474121094,null,39.5,null,39,null,38.799999237060547,null,null,null,null,38.700000762939453,null,21.200000762939453,null,21,null,null,null,null,null,20.700000762939453,20.600000381469727,null,null,20.5]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.98099999999999998,null,0.98099999999999998,null,0.98099999999999998,null,0.98099999999999998,null,null,null,null,0.98099999999999998,null,0.98799999999999999,null,0.98799999999999999,null,null,null,null,null,0.98799999999999999,0.98799999999999999,null,null,0.98799999999999999]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,73.699996948242188,null,73.699996948242188,null,73.699996948242188,null,73.699996948242188,null,null,null,null,73.699996948242188,null,83.5,null,83.5,null,null,null,null,null,83.5,83.5,null,null,83.5]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,36.799999237060547,null,36.299999237060547,null,35.799999237060547,null,35.599998474121094,null,null,null,null,35.599998474121094,null,19.600000381469727,null,19.399999618530273,null,null,null,null,null,19.200000762939453,19.100000381469727,null,null,19]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,1.8,null,1.8,null,1.8,null,1.8,null,null,null,null,1.8,null,1,null,1,null,null,null,null,null,1,1,null,null,1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"83.5",null,"83.5",null,"83.5",null,"83.5",null,null,null,null,"83.5",null,"83.5",null,"83.5",null,null,null,null,null,"83.5","83.5",null,null,"83.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"DYSA","index":70,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"DYSA - Dysart (66/22kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T035 - Dysart BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Capricornia"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x132/22kV 10 MVA"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -3.7%, 2020 S -1.7% W -1.7%2021 S -2.0% W -2.0%2022 S -0.8% W -0.8%2023 S -1.0% W -1.0"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"7.4 MVA on 20/02/2019 at 16:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,44,null,44,null,44,null,44,null,null,null,null,44,null,20,null,44,null,null,null,null,null,44,44,null,null,44]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,8.3999996185302734,null,8.1000003814697266,null,8,null,7.9000000953674316,null,null,null,null,7.9000000953674316,null,4.8000001907348633,null,4.6999998092651367,null,null,null,null,null,4.5999999046325684,4.5,null,null,4.5]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.997,null,0.997,null,0.997,null,0.998,null,null,null,null,0.998,null,1,null,1,null,null,null,null,null,1,1,null,null,1]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,23,null,23,null,23,null,23,null,null,null,null,23,null,10,null,26,null,null,null,null,null,26,26,null,null,26]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,7.5999999046325684,null,7.4000000953674316,null,7.3000001907348633,null,7.1999998092651367,null,null,null,null,7.1999998092651367,null,4.5,null,4.4000000953674316,null,null,null,null,null,4.3000001907348633,4.3000001907348633,null,null,4.1999998092651367]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.4,null,0.4,null,0.4,null,0.4,null,null,null,null,0.4,null,0.2,null,0.2,null,null,null,null,null,0.2,0.2,null,null,0.2]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"5.5",null,"5.5",null,"5.5",null,"5.5",null,null,null,null,"5.5",null,"5.5",null,"5.5",null,null,null,null,null,"5.5","5.5",null,null,"5.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"EAAY","index":71,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"EAAY - East Ayr (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T193 - Clare South BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Nth Queensland"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/11kV 15/18/25MVA ONAN/ODAN/ODAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.2%, 2020 S 0.1% W 0.1%, 2021 S -0.0% W -0.0%2022 S 0.2% W 0.2%, 2023 S -0.1% W -0.1"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"15.8 MVA on 28/11/2018 at 14:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,64.900001525878906,null,64.900001525878906,null,64.900001525878906,null,64.900001525878906,null,null,null,null,64.900001525878906,null,69.900001525878906,null,69.900001525878906,null,null,null,null,null,69.900001525878906,69.900001525878906,null,null,69.900001525878906]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,16.200000762939453,null,16.100000381469727,null,16,null,16,null,null,null,null,16.100000381469727,null,9.1000003814697266,null,9.1000003814697266,null,null,null,null,null,9.1000003814697266,9.1000003814697266,null,null,9.1000003814697266]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.999,null,1,null,1,null,1,null,null,null,null,1,null,0.995,null,0.995,null,null,null,null,null,0.995,0.995,null,null,0.995]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,37.099998474121094,null,37.099998474121094,null,37.099998474121094,null,37.099998474121094,null,null,null,null,37.099998474121094,null,37.400001525878906,null,37.400001525878906,null,null,null,null,null,37.400001525878906,37.400001525878906,null,null,37.400001525878906]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,14.5,null,14.399999618530273,null,14.300000190734863,null,14.300000190734863,null,null,null,null,14.399999618530273,null,8.5,null,8.5,null,null,null,null,null,8.5,8.5,null,null,8.5]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.7,null,0.7,null,0.7,null,0.7,null,null,null,null,0.7,null,0.4,null,0.4,null,null,null,null,null,0.4,0.4,null,null,0.4]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"13.5",null,"13.5",null,"13.5",null,"13.5",null,null,null,null,"13.5",null,"13.5",null,"13.5",null,null,null,null,null,"13.5","13.5",null,null,"13.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"EABU","index":72,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"EABU - East Bundaberg (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T020 - Bundaberg BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Wide Bay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/11kV 12/16MVA ONAN/ONAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 1.8 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 1.0%, 2020 S 1.2% W 1.2%, 2021 S 1.2% W 1.2%, 2022 S 0.9% W 0.9%, 2023 S 0.6% W 0.6%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"18.6 MVA on 11/02/2019 at 18:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,34.700000762939453,null,34.700000762939453,null,34.700000762939453,null,34.700000762939453,null,null,null,null,34.700000762939453,null,40.799999237060547,null,40.799999237060547,null,null,null,null,null,40.799999237060547,40.799999237060547,null,null,40.799999237060547]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0.10000000149011612,null,0.10000000149011612,null,0.10000000149011612,null,0.10000000149011612,null,null,null,null,0.10000000149011612,null,0.40000000596046448,null,0.40000000596046448,null,null,null,null,null,0.40000000596046448,0.40000000596046448,null,null,0.40000000596046448]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,21.5,null,22.700000762939453,null,23.700000762939453,null,23.799999237060547,null,null,null,null,24.100000381469727,null,19.600000381469727,null,19.799999237060547,null,null,null,null,null,20.899999618530273,21.899999618530273,null,null,22.100000381469727]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,1,null,1,null,1,null,1,null,null,null,null,1,null,0.999,null,0.999,null,null,null,null,null,0.999,1,null,null,1]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,20.399999618530273,null,20.399999618530273,null,20.399999618530273,null,20.399999618530273,null,null,null,null,20.399999618530273,null,23.299999237060547,null,23.299999237060547,null,null,null,null,null,23.299999237060547,23.299999237060547,null,null,23.299999237060547]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,19.799999237060547,null,21,null,22,null,22.200000762939453,null,null,null,null,22.399999618530273,null,18.5,null,18.700000762939453,null,null,null,null,null,19.799999237060547,20.799999237060547,null,null,21]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,1,null,1.1000000000000001,null,1.1000000000000001,null,1.1000000000000001,null,null,null,null,1.1000000000000001,null,0.9,null,0.9,null,null,null,null,null,1,1,null,null,1.1000000000000001]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"18",null,"18",null,"18",null,"18",null,null,null,null,"18",null,"18",null,"18",null,null,null,null,null,"18","18",null,null,"18"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,null,null,0.6,null,1.6,null,1.8,null,null,null,null,2]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,2.0999999046325684,null,2.0999999046325684,null,2.0999999046325684,null,2.0999999046325684,null,null,null,null,2.0999999046325684,null,2.0999999046325684,null,2.0999999046325684,null,null,null,null,null,2.0999999046325684,2.0999999046325684,null,null,2.0999999046325684]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"EATO","index":73,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"EATO - East Toowoomba (33/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T043 - South Toowoomba BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is South West"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x33/11kV 15/18/25MVA ONAN/OFDAN/OFDAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -1.1%, 2020 S -1.0% W -1.0%2021 S -1.1% W -1.1%2022 S -1.1% W -1.1%2023 S -1.4% W -1.4"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"32.9 MVA on 18/06/2018 at 18:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,56.299999237060547,null,56.299999237060547,null,56.299999237060547,null,56.299999237060547,null,null,null,null,56.299999237060547,null,66.099998474121094,null,66.099998474121094,null,null,null,null,null,66.099998474121094,66.099998474121094,null,null,66.099998474121094]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,31.299999237060547,null,30.799999237060547,null,30.200000762939453,null,29.799999237060547,null,null,null,null,29.600000381469727,null,35,null,34.5,null,null,null,null,null,34.099998474121094,33.700000762939453,null,null,33.299999237060547]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.97599999999999998,null,0.97599999999999998,null,0.97599999999999998,null,0.97599999999999998,null,null,null,null,0.97599999999999998,null,0.98699999999999999,null,0.98699999999999999,null,null,null,null,null,0.98699999999999999,0.98699999999999999,null,null,0.98699999999999999]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,28.100000381469727,null,28.100000381469727,null,28.100000381469727,null,28.100000381469727,null,null,null,null,28.100000381469727,null,34.299999237060547,null,34.299999237060547,null,null,null,null,null,34.299999237060547,34.299999237060547,null,null,34.299999237060547]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,27.600000381469727,null,27.200000762939453,null,26.600000381469727,null,26.200000762939453,null,null,null,null,26.100000381469727,null,31.700000762939453,null,31.299999237060547,null,null,null,null,null,30.899999618530273,30.5,null,null,30.200000762939453]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,1.4,null,1.4,null,1.3,null,1.3,null,null,null,null,1.3,null,1.6,null,1.6,null,null,null,null,null,1.5,1.5,null,null,1.5]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"7",null,"7",null,"7",null,"7",null,null,null,null,"7",null,"7",null,"7",null,null,null,null,null,"7","7",null,null,"7"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,5.5,null,5.5,null,5.5,null,5.5,null,null,null,null,5.5,null,5.5,null,5.5,null,null,null,null,null,5.5,5.5,null,null,5.5]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"EDMO","index":74,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"EDMO - Edmonton (132/22kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"QEMT - Edmonton TCP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Far North"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2xEDMOSS TRANSFORMER"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 16.3 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.5%, 2020 S 0.7% W 0.7%, 2021 S 0.6% W 0.6%, 2022 S 1.0% W 1.0%, 2023 S 0.8% W 0.8%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"49.5 MVA on 21/02/2019 at 19:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,75,null,75,null,75,null,75,null,null,null,null,75,null,75,null,75,null,null,null,null,null,75,75,null,null,75]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0.20000000298023224,null,0.20000000298023224,null,null,null,null,null,0.20000000298023224,0.20000000298023224,null,null,0.20000000298023224]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,52.299999237060547,null,52.5,null,52.400001525878906,null,52.900001525878906,null,null,null,null,53.599998474121094,null,30.5,null,30.700000762939453,null,null,null,null,null,30.700000762939453,31,null,null,31.399999618530273]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,1,null,1,null,1,null,1,null,null,null,null,1,null,0.998,null,0.999,null,null,null,null,null,0.999,0.999,null,null,0.999]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,50,null,50,null,50,null,50,null,null,null,null,50,null,50,null,50,null,null,null,null,null,50,50,null,null,50]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,48,null,48.099998474121094,null,48.099998474121094,null,48.599998474121094,null,null,null,null,49.200000762939453,null,28.799999237060547,null,28.899999618530273,null,null,null,null,null,29,29.299999237060547,null,null,29.600000381469727]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,2.4,null,2.4,null,2.4,null,2.4,null,null,null,null,2.5,null,1.4,null,1.4,null,null,null,null,null,1.5,1.5,null,null,1.5]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"7",null,"7",null,"7",null,"7",null,null,null,null,"7",null,"7",null,"7",null,null,null,null,null,"7","7",null,null,"7"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,6,null,6,null,6,null,6,null,null,null,null,6,null,6,null,6,null,null,null,null,null,6,6,null,null,6]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,4,null,4,null,4,null,4,null,null,null,null,4,null,4,null,4,null,null,null,null,null,4,4,null,null,4]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"EIDS","index":75,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"EIDS - Eidsvold (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T131 - Isis BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Wide Bay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x62/11kV 2MVA ON;1x66/11kV 2MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -1.6%, 2020 S 0.0% W 0.0%, 2021 S -0.1% W -0.1%2022 S -0.4% W -0.4%2023 S -0.6% W -0.6"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"1.8 MVA on 13/02/2019 at 19:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,4.5,null,4.5,null,4.5,null,4.5,null,null,null,null,4.5,null,5.3000001907348633,null,5.3000001907348633,null,null,null,null,null,5.3000001907348633,5.3000001907348633,null,null,5.3000001907348633]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,2,null,2,null,1.8999999761581421,null,1.8999999761581421,null,null,null,null,1.8999999761581421,null,1.3999999761581421,null,1.3999999761581421,null,null,null,null,null,1.3999999761581421,1.3999999761581421,null,null,1.3999999761581421]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.98,null,0.98,null,0.98,null,0.98,null,null,null,null,0.98,null,0.99199999999999999,null,0.99199999999999999,null,null,null,null,null,0.99199999999999999,0.99199999999999999,null,null,0.99199999999999999]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,2.7000000476837158,null,2.7000000476837158,null,2.7000000476837158,null,2.7000000476837158,null,null,null,null,2.7000000476837158,null,3,null,3,null,null,null,null,null,3,3,null,null,3]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,1.8999999761581421,null,1.8999999761581421,null,1.7999999523162842,null,1.7999999523162842,null,null,null,null,1.7999999523162842,null,1.2999999523162842,null,1.2999999523162842,null,null,null,null,null,1.2999999523162842,1.2999999523162842,null,null,1.2999999523162842]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.1,null,0.1,null,0.1,null,0.1,null,null,null,null,0.1,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"8.5",null,"8.5",null,"8.5",null,"8.5",null,null,null,null,"8.5",null,"8.5",null,"8.5",null,null,null,null,null,"8.5","8.5",null,null,"8.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"ELRO","index":76,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"ELRO - Ellwoods Road (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"H018 - Tarong BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Wide Bay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/11kV 4.1MVA ONAN;1x66/11kV 4.1MVA ONAN(Standby)"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -1.2%, 2020 S -1.1% W -1.1%2021 S -0.7% W -0.7%2022 S -0.7% W -0.7%2023 S -1.0% W -1.0"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"3 MVA on 15/06/2018 at 07:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,5,null,5,null,5,null,5,null,null,null,null,5,null,6.0999999046325684,null,6.0999999046325684,null,null,null,null,null,6.0999999046325684,6.0999999046325684,null,null,6.0999999046325684]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,3,null,2.9000000953674316,null,2.9000000953674316,null,2.9000000953674316,null,null,null,null,2.7999999523162842,null,2.9000000953674316,null,2.7999999523162842,null,null,null,null,null,2.7999999523162842,2.7999999523162842,null,null,2.7999999523162842]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.90200000000000002,null,0.90200000000000002,null,0.90200000000000002,null,0.90200000000000002,null,null,null,null,0.90200000000000002,null,0.89100000000000001,null,0.89100000000000001,null,null,null,null,null,0.89100000000000001,0.89100000000000001,null,null,0.89100000000000001]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,2.9000000953674316,null,2.9000000953674316,null,2.7999999523162842,null,2.7999999523162842,null,null,null,null,2.7999999523162842,null,2.9000000953674316,null,2.7999999523162842,null,null,null,null,null,2.7999999523162842,2.7999999523162842,null,null,2.7999999523162842]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.1,null,0.1,null,0.1,null,0.1,null,null,null,null,0.1,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"13.5",null,"13.5",null,"13.5",null,"13.5",null,null,null,null,"13.5",null,"13.5",null,"13.5",null,null,null,null,null,"13.5","13.5",null,null,"13.5"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,2.9,null,2.9,null,2.8,null,2.8,null,null,null,null,2.8,null,2.9,null,2.8,null,null,null,null,null,2.8,2.8,null,null,2.8]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,4.0999999046325684,null,4.0999999046325684,null,4.0999999046325684,null,4.0999999046325684,null,null,null,null,4.0999999046325684,null,4.0999999046325684,null,4.0999999046325684,null,null,null,null,null,4.0999999046325684,4.0999999046325684,null,null,4.0999999046325684]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"EMER","index":77,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"EMER - Emerald (66/22kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"H015 - Lilyvale BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Capricornia"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/22kV 15/20MVA ONAN/ONAF;1x66/22kV 16/20MVA ONAN/ONAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.8%, 2020 S -0.6% W -0.6%2021 S -0.5% W -0.5%2022 S -0.5% W -0.5%2023 S -0.7% W -0.7"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"35.8 MVA on 20/02/2019 at 19:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,69.599998474121094,null,69.599998474121094,null,69.599998474121094,null,69.599998474121094,null,null,null,null,69.599998474121094,null,81.099998474121094,null,81.099998474121094,null,null,null,null,null,81.099998474121094,81.099998474121094,null,null,81.099998474121094]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,41.400001525878906,null,41,null,40.400001525878906,null,40.200000762939453,null,null,null,null,40.299999237060547,null,25.799999237060547,null,25.600000381469727,null,null,null,null,null,25.299999237060547,25.200000762939453,null,null,25.100000381469727]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,1,null,1,null,1,null,1,null,null,null,null,1,null,1,null,1,null,null,null,null,null,1,1,null,null,1]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,52.900001525878906,null,52.900001525878906,null,52.900001525878906,null,52.900001525878906,null,null,null,null,52.900001525878906,null,58.400001525878906,null,58.400001525878906,null,null,null,null,null,58.400001525878906,58.400001525878906,null,null,58.400001525878906]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,36.200000762939453,null,35.900001525878906,null,35.400001525878906,null,35.200000762939453,null,null,null,null,35.200000762939453,null,24.299999237060547,null,24.100000381469727,null,null,null,null,null,23.899999618530273,23.700000762939453,null,null,23.700000762939453]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,1.8,null,1.8,null,1.8,null,1.8,null,null,null,null,1.8,null,1.2,null,1.2,null,null,null,null,null,1.2,1.2,null,null,1.2]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"8",null,"8",null,"8",null,"8",null,null,null,null,"8",null,"8",null,"8",null,null,null,null,null,"8","8",null,null,"8"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"ETON","index":78,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"ETON - Eton (33/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T065 - Alligator Creek BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Mackay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x33/11kV 7.5/5MVA ONAF/ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.0%, 2020 S 0.1% W 0.1%, 2021 S 0.1% W 0.1%, 2022 S 0.0% W 0.0%, 2023 S -0.0% W -0.0"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"7.4 MVA on 01/12/2018 at 20:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,14.100000381469727,null,14.100000381469727,null,14.100000381469727,null,14.100000381469727,null,null,null,null,14.100000381469727,null,15,null,15,null,null,null,null,null,15,15,null,null,15]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,11.600000381469727,null,11.5,null,11.399999618530273,null,11.399999618530273,null,null,null,null,11.5,null,4.5999999046325684,null,4.5999999046325684,null,null,null,null,null,4.5999999046325684,4.5,null,null,4.5999999046325684]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.98699999999999999,null,0.98699999999999999,null,0.98799999999999999,null,0.98799999999999999,null,null,null,null,0.98699999999999999,null,0.90300000000000002,null,0.90300000000000002,null,null,null,null,null,0.90300000000000002,0.90300000000000002,null,null,0.90300000000000002]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,7.5,null,7.5,null,7.5,null,7.5,null,null,null,null,7.5,null,7.5,null,7.5,null,null,null,null,null,7.5,7.5,null,null,7.5]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,8,null,8,null,7.9000000953674316,null,7.9000000953674316,null,null,null,null,8,null,4.1999998092651367,null,4.1999998092651367,null,null,null,null,null,4.1999998092651367,4.1999998092651367,null,null,4.1999998092651367]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.4,null,0.4,null,0.4,null,0.4,null,null,null,null,0.4,null,0.2,null,0.2,null,null,null,null,null,0.2,0.2,null,null,0.2]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"9.5",null,"9.5",null,"9.5",null,"9.5",null,null,null,null,"9.5",null,"9.5",null,"9.5",null,null,null,null,null,"9.5","9.5",null,null,"9.5"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,0.5,null,0.5,null,0.4,null,0.4,null,null,null,null,0.5]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,1.5,null,1.5,null,1.5,null,1.5,null,null,null,null,1.5,null,1.5,null,1.5,null,null,null,null,null,1.5,1.5,null,null,1.5]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0.30000001192092896,null,0.30000001192092896,null,0.30000001192092896,null,0.30000001192092896,null,null,null,null,0.30000001192092896,null,0.30000001192092896,null,0.30000001192092896,null,null,null,null,null,0.30000001192092896,0.30000001192092896,null,null,0.30000001192092896]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"EUDA","index":79,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"EUDA - Eungella Dam (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T141 - Pioneer Valley BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Mackay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/11kV 1MVA ONAN;1x66/11kV 5MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.0%, 2020 S 0.0% W 0.0%, 2021 S 0.0% W 0.0%, 2022 S 0.0% W 0.0%, 2023 S 0.0% W 0.0%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"1 MVA on 30/08/2018 at 05:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,6.5999999046325684,null,6.5999999046325684,null,6.5999999046325684,null,6.5999999046325684,null,null,null,null,6.5999999046325684,null,6.5999999046325684,null,6.5999999046325684,null,null,null,null,null,6.5999999046325684,6.5999999046325684,null,null,6.5999999046325684]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,1.1000000238418579,null,1.1000000238418579,null,1,null,1,null,null,null,null,1.1000000238418579,null,1.1000000238418579,null,1.1000000238418579,null,null,null,null,null,1.1000000238418579,1.1000000238418579,null,null,1.1000000238418579]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.878,null,0.878,null,0.878,null,0.878,null,null,null,null,0.878,null,0.878,null,0.878,null,null,null,null,null,0.878,0.878,null,null,0.878]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,1.1000000238418579,null,1.1000000238418579,null,1.1000000238418579,null,1.1000000238418579,null,null,null,null,1.1000000238418579,null,1.2000000476837158,null,1.2000000476837158,null,null,null,null,null,1.2000000476837158,1.2000000476837158,null,null,1.2000000476837158]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,1.1000000238418579,null,1.1000000238418579,null,1,null,1,null,null,null,null,1.1000000238418579,null,1.1000000238418579,null,1.1000000238418579,null,null,null,null,null,1,1,null,null,1.1000000238418579]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.1,null,0.1,null,0.1,null,0.1,null,null,null,null,0.1,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"0",null,"0",null,"0",null,"0",null,null,null,null,"0",null,"0",null,"0",null,null,null,null,null,"0","0",null,null,"0"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"EVEL","index":80,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"EVEL - Evelyn (66/22kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T055 - Turkinje 66kV BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Far North"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/22kV 6.3 MVA"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.1%, 2020 S 0.2% W 0.2%, 2021 S 0.1% W 0.1%, 2022 S -0.0% W -0.0%2023 S -0.2% W -0.2"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"1.9 MVA on 02/12/2018 at 18:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,6.3000001907348633,null,6.3000001907348633,null,6.3000001907348633,null,6.3000001907348633,null,null,null,null,6.3000001907348633,null,6.3000001907348633,null,6.3000001907348633,null,null,null,null,null,6.3000001907348633,6.3000001907348633,null,null,6.3000001907348633]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,1.8999999761581421,null,1.8999999761581421,null,1.8999999761581421,null,1.8999999761581421,null,null,null,null,1.8999999761581421,null,1.6000000238418579,null,1.6000000238418579,null,null,null,null,null,1.6000000238418579,1.6000000238418579,null,null,1.6000000238418579]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.95799999999999996,null,0.95799999999999996,null,0.95799999999999996,null,0.95799999999999996,null,null,null,null,0.95799999999999996,null,0.97299999999999998,null,0.97299999999999998,null,null,null,null,null,0.97299999999999998,0.97299999999999998,null,null,0.97299999999999998]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,1.7999999523162842,null,1.7999999523162842,null,1.7999999523162842,null,1.7999999523162842,null,null,null,null,1.7999999523162842,null,1.5,null,1.5,null,null,null,null,null,1.5,1.5,null,null,1.5]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.1,null,0.1,null,0.1,null,0.1,null,null,null,null,0.1,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"58",null,"58",null,"58",null,"58",null,null,null,null,"58",null,"58",null,"58",null,null,null,null,null,"58","58",null,null,"58"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,1.8,null,1.8,null,1.8,null,1.8,null,null,null,null,1.8,null,1.5,null,1.5,null,null,null,null,null,1.5,1.5,null,null,1.5]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,2.5,null,2.5,null,2.5,null,2.5,null,null,null,null,2.5,null,2.5,null,2.5,null,null,null,null,null,2.5,2.5,null,null,2.5]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,1.2999999523162842,null,1.2999999523162842,null,1.2999999523162842,null,1.2999999523162842,null,null,null,null,1.2999999523162842,null,1.2999999523162842,null,1.2999999523162842,null,null,null,null,null,1.2999999523162842,1.2999999523162842,null,null,1.2999999523162842]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"FARL","index":81,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"FARL - Farleigh (33/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T038 - Mackay BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Mackay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x33/11kV 5/7.5MVA ONAF/ONAN;1x33/11kV 5/7.5MVA ONAN/ONAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 14.4 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.5%, 2020 S 0.7% W 0.7%, 2021 S 0.7% W 0.7%, 2022 S 0.6% W 0.6%, 2023 S 0.4% W 0.4%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"4.4 MVA on 28/11/2018 at 15:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,16.5,null,16.5,null,16.5,null,16.5,null,null,null,null,16.5,null,18,null,18,null,null,null,null,null,18,18,null,null,18]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,4.5,null,4.5,null,4.5,null,4.5999999046325684,null,null,null,null,4.5999999046325684,null,3.2999999523162842,null,3.2999999523162842,null,null,null,null,null,3.2999999523162842,3.2999999523162842,null,null,3.4000000953674316]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.95299999999999996,null,0.95299999999999996,null,0.95299999999999996,null,0.95299999999999996,null,null,null,null,0.95299999999999996,null,0.97899999999999998,null,0.97899999999999998,null,null,null,null,null,0.97899999999999998,0.97899999999999998,null,null,0.97899999999999998]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,9,null,9,null,9,null,9,null,null,null,null,9,null,9,null,9,null,null,null,null,null,9,9,null,null,9]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,4.0999999046325684,null,4.0999999046325684,null,4.0999999046325684,null,4.1999998092651367,null,null,null,null,4.1999998092651367,null,3,null,3,null,null,null,null,null,3,3.0999999046325684,null,null,3.0999999046325684]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.2,null,0.2,null,0.2,null,0.2,null,null,null,null,0.2,null,0.2,null,0.2,null,null,null,null,null,0.2,0.2,null,null,0.2]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"8",null,"8",null,"8",null,"8",null,null,null,null,"8",null,"8",null,"8",null,null,null,null,null,"8","8",null,null,"8"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,2,null,2,null,2,null,2,null,null,null,null,2,null,2,null,2,null,null,null,null,null,2,2,null,null,2]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"FARN","index":82,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"FARN - Farnsfield (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T131 - Isis BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Wide Bay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/11kV 10/12.5MVA ONAN/ONAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.0%, 2020 S 0.1% W 0.1%, 2021 S 0.0% W 0.0%, 2022 S 0.0% W 0.0%, 2023 S -0.0% W -0.0"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"12.2 MVA on 24/01/2019 at 21:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,28.899999618530273,null,28.899999618530273,null,28.899999618530273,null,28.899999618530273,null,null,null,null,28.899999618530273,null,37.400001525878906,null,37.400001525878906,null,null,null,null,null,37.400001525878906,37.400001525878906,null,null,37.400001525878906]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,11.399999618530273,null,11.399999618530273,null,11.300000190734863,null,11.300000190734863,null,null,null,null,11.399999618530273,null,5.9000000953674316,null,5.9000000953674316,null,null,null,null,null,5.8000001907348633,5.8000001907348633,null,null,5.8000001907348633]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.96599999999999997,null,0.96699999999999997,null,0.96799999999999997,null,0.96699999999999997,null,null,null,null,0.96699999999999997,null,0.999,null,0.999,null,null,null,null,null,0.999,0.999,null,null,0.999]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,15.899999618530273,null,15.899999618530273,null,15.899999618530273,null,15.899999618530273,null,null,null,null,15.899999618530273,null,18.700000762939453,null,18.700000762939453,null,null,null,null,null,18.700000762939453,18.700000762939453,null,null,18.700000762939453]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,11.100000381469727,null,11.100000381469727,null,11,null,11,null,null,null,null,11.100000381469727,null,5.1999998092651367,null,5.1999998092651367,null,null,null,null,null,5.1999998092651367,5.1999998092651367,null,null,5.1999998092651367]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.6,null,0.6,null,0.6,null,0.6,null,null,null,null,0.6,null,0.3,null,0.3,null,null,null,null,null,0.3,0.3,null,null,0.3]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"5",null,"5",null,"5",null,"5",null,null,null,null,"5",null,"5",null,"5",null,null,null,null,null,"5","5",null,null,"5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"FREN","index":83,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"FREN - Frenchville (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"RMES - Rockhampton Mesh"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Capricornia"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/11kV 15/20MVA ONAN/ONAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.2%, 2020 S 0.4% W 0.4%, 2021 S 0.4% W 0.4%, 2022 S 0.4% W 0.4%, 2023 S 0.1% W 0.1%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"19.9 MVA on 28/11/2018 at 18:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,48,null,48,null,48,null,48,null,null,null,null,48,null,48,null,48,null,null,null,null,null,48,48,null,null,48]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,21.399999618530273,null,21.399999618530273,null,21.299999237060547,null,21.399999618530273,null,null,null,null,21.5,null,11.5,null,11.5,null,null,null,null,null,11.5,11.5,null,null,11.600000381469727]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.98,null,0.98,null,0.98,null,0.98,null,null,null,null,0.98,null,0.98699999999999999,null,0.98699999999999999,null,null,null,null,null,0.98699999999999999,0.98699999999999999,null,null,0.98699999999999999]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,24,null,24,null,24,null,24,null,null,null,null,24,null,24,null,24,null,null,null,null,null,24,24,null,null,24]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,18.5,null,18.5,null,18.399999618530273,null,18.399999618530273,null,null,null,null,18.5,null,11,null,11,null,null,null,null,null,11,11.100000381469727,null,null,11.100000381469727]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.9,null,0.9,null,0.9,null,0.9,null,null,null,null,0.9,null,0.6,null,0.6,null,null,null,null,null,0.6,0.6,null,null,0.6]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"2.5",null,"2.5",null,"2.5",null,"2.5",null,null,null,null,"2.5",null,"2.5",null,"2.5",null,null,null,null,null,"2.5","2.5",null,null,"2.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"GARB","index":84,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"GARB - Garbutt (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"TMES - Townsville Mesh"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Nth Queensland"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/11kV 21/26.25/35MVA ONAN/ODAN/ODAF;1x66/11kV 21/26.25/35MVA ONAN/ONAF/ODAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.3%, 2020 S 0.0% W 0.0%, 2021 S -0.2% W -0.2%2022 S -0.7% W -0.7%2023 S -1.0% W -1.0"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"30.3 MVA on 20/02/2019 at 15:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,53.799999237060547,null,53.799999237060547,null,53.799999237060547,null,53.799999237060547,null,null,null,null,53.799999237060547,null,54,null,54,null,null,null,null,null,54,54,null,null,54]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,33.5,null,33.299999237060547,null,32.700000762939453,null,32.5,null,null,null,null,32.400001525878906,null,19.399999618530273,null,19.399999618530273,null,null,null,null,null,19.200000762939453,19.100000381469727,null,null,19]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.92800000000000005,null,0.92800000000000005,null,0.92800000000000005,null,0.92800000000000005,null,null,null,null,0.92800000000000005,null,0.92100000000000004,null,0.92100000000000004,null,null,null,null,null,0.92100000000000004,0.92100000000000004,null,null,0.92100000000000004]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,29.799999237060547,null,29.799999237060547,null,29.799999237060547,null,29.799999237060547,null,null,null,null,29.799999237060547,null,30.799999237060547,null,30.799999237060547,null,null,null,null,null,30.799999237060547,30.799999237060547,null,null,30.799999237060547]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,30.899999618530273,null,30.700000762939453,null,30.200000762939453,null,30,null,null,null,null,29.899999618530273,null,18.700000762939453,null,18.700000762939453,null,null,null,null,null,18.600000381469727,18.399999618530273,null,null,18.299999237060547]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,1.5,null,1.5,null,1.5,null,1.5,null,null,null,null,1.5,null,0.9,null,0.9,null,null,null,null,null,0.9,0.9,null,null,0.9]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"17.5",null,"17.5",null,"17.5",null,"17.5",null,null,null,null,"17.5",null,"17.5",null,"17.5",null,null,null,null,null,"17.5","17.5",null,null,"17.5"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,1.1000000000000001,null,0.9,null,0.4,null,0.2,null,null,null,null,0.1]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,11.800000190734863,null,11.800000190734863,null,11.800000190734863,null,11.800000190734863,null,null,null,null,11.800000190734863,null,11.800000190734863,null,11.800000190734863,null,null,null,null,null,11.800000190734863,11.800000190734863,null,null,11.800000190734863]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,6,null,6,null,6,null,6,null,null,null,null,6,null,6,null,6,null,null,null,null,null,6,6,null,null,6]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"GAYN","index":85,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"GAYN - Gayndah (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T131 - Isis BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Wide Bay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/11kV 7.5/10MVA ONAN/ONAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.8%, 2020 S -0.3% W -0.3%2021 S -0.2% W -0.2%2022 S -0.5% W -0.5%2023 S -0.8% W -0.8"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"5.6 MVA on 20/02/2019 at 16:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,24.600000381469727,null,24.600000381469727,null,24.600000381469727,null,24.600000381469727,null,null,null,null,24.600000381469727,null,27.100000381469727,null,27.100000381469727,null,null,null,null,null,27.100000381469727,27.100000381469727,null,null,27.100000381469727]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,6.5999999046325684,null,6.5,null,6.4000000953674316,null,6.4000000953674316,null,null,null,null,6.4000000953674316,null,5.3000001907348633,null,5.3000001907348633,null,null,null,null,null,5.1999998092651367,5.1999998092651367,null,null,5.1999998092651367]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.93899999999999995,null,0.93899999999999995,null,0.93899999999999995,null,0.93899999999999995,null,null,null,null,0.93899999999999995,null,0.89800000000000002,null,0.89800000000000002,null,null,null,null,null,0.89800000000000002,0.89800000000000002,null,null,0.89800000000000002]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,14.300000190734863,null,14.300000190734863,null,14.300000190734863,null,14.300000190734863,null,null,null,null,14.300000190734863,null,15,null,15,null,null,null,null,null,15,15,null,null,15]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,6.0999999046325684,null,6,null,6,null,5.9000000953674316,null,null,null,null,5.9000000953674316,null,4.9000000953674316,null,4.9000000953674316,null,null,null,null,null,4.9000000953674316,4.8000001907348633,null,null,4.8000001907348633]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.3,null,0.3,null,0.3,null,0.3,null,null,null,null,0.3,null,0.2,null,0.2,null,null,null,null,null,0.2,0.2,null,null,0.2]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"3",null,"3",null,"3",null,"3",null,null,null,null,"3",null,"3",null,"3",null,null,null,null,null,"3","3",null,null,"3"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"GEOR","index":86,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"GEOR - Georgetown (66/22kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"GEOR - Georgetown BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Far North"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/22kV 2MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.8%, 2020 S -0.6% W -0.6%2021 S -0.8% W -0.8%2022 S -0.4% W -0.4%2023 S -0.6% W -0.6"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"1.7 MVA on 03/12/2018 at 19:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,5.5,null,5.5,null,5.5,null,5.5,null,null,null,null,5.5,null,6,null,6,null,null,null,null,null,6,6,null,null,6]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,1.6000000238418579,null,1.6000000238418579,null,1.6000000238418579,null,1.6000000238418579,null,null,null,null,1.6000000238418579,null,1.2999999523162842,null,1.2999999523162842,null,null,null,null,null,1.2999999523162842,1.2999999523162842,null,null,1.2000000476837158]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.99,null,0.99,null,0.99,null,0.99,null,null,null,null,0.99,null,0.98199999999999998,null,0.98199999999999998,null,null,null,null,null,0.98199999999999998,0.98199999999999998,null,null,0.98199999999999998]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,3,null,3,null,3,null,3,null,null,null,null,3,null,3,null,3,null,null,null,null,null,3,3,null,null,3]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,1.5,null,1.5,null,1.5,null,1.5,null,null,null,null,1.5,null,1.2000000476837158,null,1.2000000476837158,null,null,null,null,null,1.2000000476837158,1.2000000476837158,null,null,1.2000000476837158]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.1,null,0.1,null,0.1,null,0.1,null,null,null,null,0.1,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"7.5",null,"7.5",null,"7.5",null,"7.5",null,null,null,null,"7.5",null,"7.5",null,"7.5",null,null,null,null,null,"7.5","7.5",null,null,"7.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"GEOR1","index":87,"n_rows":48,"n_cols":35,"rows_kept":48,"cut":false,"hidden":false,"merged":[[0,2,0,40],[2,1,2,5],[2,8,4,20],[2,23,3,24],[2,26,4,37],[6,1,8,5],[6,8,6,36],[8,8,9,36],[11,8,11,36],[13,3,14,11],[13,14,13,26],[16,17,17,31],[17,3,18,11],[17,14,18,15],[21,4,22,8],[21,9,21,21],[21,22,21,34],[22,9,22,10],[22,11,22,12],[22,13,22,14],[22,15,22,19],[22,20,22,21],[22,22,22,23],[22,24,22,29],[22,31,22,33],[23,4,23,8],[23,9,23,10],[23,11,23,12],[23,13,23,14],[23,15,23,19],[23,20,23,21],[23,22,23,23],[23,24,23,29],[23,31,23,33],[24,4,24,8],[24,9,24,10],[24,11,24,12],[24,13,24,14],[24,15,24,19],[24,20,24,21],[24,22,24,23],[24,24,24,29],[24,31,24,33],[25,4,25,8],[25,9,25,10],[25,11,25,12],[25,13,25,14],[25,15,25,19],[25,20,25,21],[25,22,25,23],[25,24,25,29],[25,31,25,33],[26,4,26,8],[26,9,26,10],[26,11,26,12],[26,13,26,14],[26,15,26,19],[26,20,26,21],[26,22,26,23],[26,24,26,29],[26,31,26,33],[27,4,27,8],[27,9,27,10],[27,11,27,12],[27,13,27,14],[27,15,27,19],[27,20,27,21],[27,22,27,23],[27,24,27,29],[27,31,27,33],[28,4,28,8],[28,9,28,10],[28,11,28,12],[28,13,28,14],[28,15,28,19],[28,20,28,21],[28,22,28,23],[28,24,28,29],[28,31,28,33],[29,4,29,8],[29,9,29,10],[29,11,29,12],[29,13,29,14],[29,15,29,19],[29,20,29,21],[29,22,29,23],[29,24,29,29],[29,31,29,33],[30,4,30,8],[30,9,30,10],[30,11,30,12],[30,13,30,14],[30,15,30,19],[30,20,30,21],[30,22,30,23],[30,24,30,29],[30,31,30,33],[31,4,31,8],[31,9,31,10],[31,11,31,12],[31,13,31,14],[31,15,31,19],[31,20,31,21],[31,22,31,23],[31,24,31,29],[31,31,31,33],[32,4,32,8],[32,9,32,10],[32,11,32,12],[32,13,32,14],[32,15,32,19],[32,20,32,21],[32,22,32,23],[32,24,32,29],[32,31,32,33],[33,4,33,8],[33,9,33,10],[33,11,33,12],[33,13,33,14],[33,15,33,19],[33,20,33,21],[33,22,33,23],[33,24,33,29],[33,31,33,33],[34,4,34,8],[34,9,34,10],[34,11,34,12],[34,13,34,14],[34,15,34,19],[34,20,34,21],[34,22,34,23],[34,24,34,29],[34,31,34,33],[35,4,35,8],[35,9,35,10],[35,11,35,12],[35,13,35,14],[35,15,35,19],[35,20,35,21],[35,22,35,23],[35,24,35,29],[35,31,35,33],[36,4,36,8],[36,9,36,10],[36,11,36,12],[36,13,36,14],[36,15,36,19],[36,20,36,21],[36,22,36,23],[36,24,36,29],[36,31,36,33],[37,4,37,8],[37,9,37,10],[37,11,37,12],[37,13,37,14],[37,15,37,19],[37,20,37,21],[37,22,37,23],[37,24,37,29],[37,31,37,33],[39,31,39,33],[38,4,38,8],[38,9,38,10],[38,11,38,12],[38,13,38,14],[38,15,38,19],[38,20,38,21],[38,22,38,23],[38,24,38,29],[38,31,38,33],[40,4,40,8],[40,9,40,10],[40,11,40,12],[40,13,40,14],[40,15,40,19],[39,22,39,23],[39,24,39,29],[39,4,39,8],[39,9,39,10],[39,11,39,12],[39,13,39,14],[39,15,39,19],[39,20,39,21],[40,22,40,23],[40,24,40,29],[40,31,40,33],[42,20,42,21],[42,22,42,23],[40,20,40,21],[42,9,42,10],[42,11,42,12],[42,13,42,14],[42,15,42,19],[41,9,41,10],[41,11,41,12],[41,13,41,14],[41,15,41,19],[43,31,43,33],[41,20,41,21],[43,22,43,23],[43,24,43,29],[41,22,41,23],[41,24,41,29],[47,2,47,38],[42,24,42,29],[42,31,42,33],[43,4,43,8],[43,9,43,10],[43,11,43,12],[43,13,43,14],[43,15,43,19],[43,20,43,21],[42,4,42,8],[41,31,41,33],[41,4,41,8]]}
[null,null,"Bulk Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,"GEOR - Georgetown BSP (132/66kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"QROS - Ross (Kidston and Milchester) TCP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,"Region is Far North"]
[]
[null,null,null,null,null,null,null,null,"Transformer size is 2x132/66/6.6kV 8MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 5.3 MVA"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,"7.7 MVA on 04/12/2018 at 18:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,16.700000762939453,null,16.700000762939453,null,16.700000762939453,null,16.700000762939453,null,null,null,null,16.700000762939453,null,18,null,18,null,null,null,null,null,18,18,null,null,18]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,8.5,null,8.3000001907348633,null,8.1000003814697266,null,8,null,null,null,null,8,null,6.0999999046325684,null,6,null,null,null,null,null,5.9000000953674316,5.8000001907348633,null,null,5.8000001907348633]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,0.89600000000000002,null,0.89600000000000002,null,0.89600000000000002,null,0.89600000000000002,null,null,null,null,0.89600000000000002,null,0.88800000000000001,null,0.88800000000000001,null,null,null,null,null,0.88800000000000001,0.88800000000000001,null,null,0.88800000000000001]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,9.6000003814697266,null,9.6000003814697266,null,9.6000003814697266,null,9.6000003814697266,null,null,null,null,9.6000003814697266,null,10,null,10,null,null,null,null,null,10,10,null,null,10]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,7.8000001907348633,null,7.6999998092651367,null,7.5,null,7.4000000953674316,null,null,null,null,7.4000000953674316,null,5.6999998092651367,null,5.6999998092651367,null,null,null,null,null,5.5999999046325684,5.5,null,null,5.5]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,0.4,null,0.4,null,0.4,null,0.4,null,null,null,null,0.4,null,0.3,null,0.3,null,null,null,null,null,0.3,0.3,null,null,0.3]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,"36",null,"36",null,"36",null,"36",null,null,null,null,"36",null,"36",null,"36",null,null,null,null,null,"36","36",null,null,"36"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"GIRU","index":88,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"GIRU - Giru (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T193 - Clare South BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Nth Queensland"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/11kV 4MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -1.4%, 2020 S -0.2% W -0.2%2021 S -0.4% W -0.4%2022 S -0.3% W -0.3%2023 S -0.8% W -0.8"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"2 MVA on 03/12/2018 at 18:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,9.5,null,9.5,null,9.5,null,9.5,null,null,null,null,9.5,null,10.5,null,10.5,null,null,null,null,null,10.5,10.5,null,null,10.5]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,2.2000000476837158,null,2.2000000476837158,null,2.0999999046325684,null,2.0999999046325684,null,null,null,null,2.0999999046325684,null,1.6000000238418579,null,1.6000000238418579,null,null,null,null,null,1.6000000238418579,1.6000000238418579,null,null,1.6000000238418579]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.89,null,0.89,null,0.89,null,0.89,null,null,null,null,0.89,null,0.89,null,0.89,null,null,null,null,null,0.89,0.89,null,null,0.89]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,5,null,5,null,5,null,5,null,null,null,null,5,null,5.4000000953674316,null,5.4000000953674316,null,null,null,null,null,5.4000000953674316,5.4000000953674316,null,null,5.4000000953674316]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,2.0999999046325684,null,2.0999999046325684,null,2.0999999046325684,null,2.0999999046325684,null,null,null,null,2.0999999046325684,null,1.5,null,1.5,null,null,null,null,null,1.5,1.5,null,null,1.5]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.1,null,0.1,null,0.1,null,0.1,null,null,null,null,0.1,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"10",null,"10",null,"10",null,"10",null,null,null,null,"10",null,"10",null,"10",null,null,null,null,null,"10","10",null,null,"10"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"GIVE","index":89,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"GIVE - Givelda (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T020 - Bundaberg BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Wide Bay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/11kV 10MVA ONAN;1x66/11kV 7.5/10MVA ONAN/ONAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.0%, 2020 S 0.1% W 0.1%, 2021 S 0.0% W 0.0%, 2022 S 0.0% W 0.0%, 2023 S -0.1% W -0.1"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"6.7 MVA on 30/01/2019 at 19:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,24.399999618530273,null,24.399999618530273,null,24.399999618530273,null,24.399999618530273,null,null,null,null,24.399999618530273,null,29.600000381469727,null,29.600000381469727,null,null,null,null,null,29.600000381469727,29.600000381469727,null,null,29.600000381469727]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,7.1999998092651367,null,7.1999998092651367,null,7.0999999046325684,null,7.0999999046325684,null,null,null,null,7.0999999046325684,null,5.8000001907348633,null,5.8000001907348633,null,null,null,null,null,5.8000001907348633,5.8000001907348633,null,null,5.8000001907348633]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.86499999999999999,null,0.86499999999999999,null,0.86499999999999999,null,0.86499999999999999,null,null,null,null,0.86499999999999999,null,0.86,null,0.86,null,null,null,null,null,0.86,0.86,null,null,0.86]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,14.300000190734863,null,14.300000190734863,null,14.300000190734863,null,14.300000190734863,null,null,null,null,14.300000190734863,null,15,null,15,null,null,null,null,null,15,15,null,null,15]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,7,null,7,null,6.9000000953674316,null,6.9000000953674316,null,null,null,null,6.9000000953674316,null,5.5999999046325684,null,5.5999999046325684,null,null,null,null,null,5.5999999046325684,5.5999999046325684,null,null,5.5999999046325684]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.4,null,0.4,null,0.3,null,0.3,null,null,null,null,0.3,null,0.3,null,0.3,null,null,null,null,null,0.3,0.3,null,null,0.3]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"40.5",null,"40.5",null,"40.5",null,"40.5",null,null,null,null,"40.5",null,"40.5",null,"40.5",null,null,null,null,null,"40.5","40.5",null,null,"40.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"GLEE","index":90,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"GLEE - Glenelg (66/33kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T095 - Millchester BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Nth Queensland"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/0.0191kV 0.63 MVA"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.7%, 2020 S -0.1% W -0.1%2021 S -0.2% W -0.2%2022 S -0.4% W -0.4%2023 S -0.6% W -0.6"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"0.5 MVA on 21/12/2018 at 18:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,0.60000002384185791,null,0.60000002384185791,null,0.60000002384185791,null,0.60000002384185791,null,null,null,null,0.60000002384185791,null,0.60000002384185791,null,0.60000002384185791,null,null,null,null,null,0.60000002384185791,0.60000002384185791,null,null,0.60000002384185791]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,0.60000002384185791,null,0.60000002384185791,null,0.60000002384185791,null,0.60000002384185791,null,null,null,null,0.60000002384185791,null,0.40000000596046448,null,0.40000000596046448,null,null,null,null,null,0.40000000596046448,0.40000000596046448,null,null,0.40000000596046448]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.97699999999999998,null,0.97699999999999998,null,0.97699999999999998,null,0.97699999999999998,null,null,null,null,0.97699999999999998,null,0.91900000000000004,null,0.91900000000000004,null,null,null,null,null,0.91900000000000004,0.91900000000000004,null,null,0.91900000000000004]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,0.60000002384185791,null,0.60000002384185791,null,0.60000002384185791,null,0.60000002384185791,null,null,null,null,0.60000002384185791,null,0.40000000596046448,null,0.40000000596046448,null,null,null,null,null,0.40000000596046448,0.40000000596046448,null,null,0.40000000596046448]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"14",null,"14",null,"14",null,"14",null,null,null,null,"14",null,"14",null,"14",null,null,null,null,null,"14","14",null,null,"14"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,0.6,null,0.6,null,0.6,null,0.6,null,null,null,null,0.6,null,0.4,null,0.4,null,null,null,null,null,0.4,0.4,null,null,0.4]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0.60000002384185791,null,0.60000002384185791,null,0.60000002384185791,null,0.60000002384185791,null,null,null,null,0.60000002384185791,null,0.60000002384185791,null,0.60000002384185791,null,null,null,null,null,0.60000002384185791,0.60000002384185791,null,null,0.60000002384185791]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"GLEL","index":91,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"GLEL - Glenella 11kV (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T141 - Pioneer Valley BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Mackay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/11kV 19/26/32MVA ONAN/ODAN/ODAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.1%, 2020 S 0.3% W 0.3%, 2021 S 0.3% W 0.3%, 2022 S 0.1% W 0.1%, 2023 S -0.2% W -0.2"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"10.8 MVA on 28/11/2018 at 15:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,75.199996948242188,null,75.199996948242188,null,75.199996948242188,null,75.199996948242188,null,null,null,null,75.199996948242188,null,83.800003051757813,null,83.800003051757813,null,null,null,null,null,83.800003051757813,83.800003051757813,null,null,83.800003051757813]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,12.600000381469727,null,12.600000381469727,null,12.5,null,12.5,null,null,null,null,12.600000381469727,null,6.8000001907348633,null,6.8000001907348633,null,null,null,null,null,6.8000001907348633,6.8000001907348633,null,null,6.8000001907348633]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.96199999999999997,null,0.96199999999999997,null,0.96199999999999997,null,0.96199999999999997,null,null,null,null,0.96199999999999997,null,0.97099999999999997,null,0.97099999999999997,null,null,null,null,null,0.97099999999999997,0.97099999999999997,null,null,0.97099999999999997]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,41.900001525878906,null,41.900001525878906,null,41.900001525878906,null,41.900001525878906,null,null,null,null,41.900001525878906,null,44.700000762939453,null,44.700000762939453,null,null,null,null,null,44.700000762939453,44.700000762939453,null,null,44.700000762939453]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,11.199999809265137,null,11.199999809265137,null,11.100000381469727,null,11.100000381469727,null,null,null,null,11.100000381469727,null,6.5999999046325684,null,6.5999999046325684,null,null,null,null,null,6.5999999046325684,6.5999999046325684,null,null,6.5999999046325684]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.6,null,0.6,null,0.6,null,0.6,null,null,null,null,0.6,null,0.3,null,0.3,null,null,null,null,null,0.3,0.3,null,null,0.3]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"4.5",null,"4.5",null,"4.5",null,"4.5",null,null,null,null,"4.5",null,"4.5",null,"4.5",null,null,null,null,null,"4.5","4.5",null,null,"4.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"GLEN","index":92,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"GLEN - Glenden (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T069 - Newlands BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Mackay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/11kV 7.5MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -2.9%, 2020 S -1.7% W -1.7%2021 S -1.8% W -1.8%2022 S -0.6% W -0.6%2023 S -0.7% W -0.7"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"1.7 MVA on 28/11/2018 at 19:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,15,null,15,null,15,null,15,null,null,null,null,15,null,16.700000762939453,null,16.700000762939453,null,null,null,null,null,16.700000762939453,16.700000762939453,null,null,16.700000762939453]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,1.7999999523162842,null,1.7999999523162842,null,1.7999999523162842,null,1.7999999523162842,null,null,null,null,1.7999999523162842,null,1.2000000476837158,null,1.2000000476837158,null,null,null,null,null,1.1000000238418579,1.1000000238418579,null,null,1.1000000238418579]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.99,null,0.99,null,0.99,null,0.99,null,null,null,null,0.99,null,0.997,null,0.997,null,null,null,null,null,0.997,0.997,null,null,0.997]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,9.6999998092651367,null,9.6999998092651367,null,9.6999998092651367,null,9.6999998092651367,null,null,null,null,9.6999998092651367,null,10.199999809265137,null,10.199999809265137,null,null,null,null,null,10.199999809265137,10.199999809265137,null,null,10.199999809265137]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,1.7000000476837158,null,1.7000000476837158,null,1.7000000476837158,null,1.6000000238418579,null,null,null,null,1.6000000238418579,null,1.1000000238418579,null,1.1000000238418579,null,null,null,null,null,1.1000000238418579,1.1000000238418579,null,null,1.1000000238418579]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.1,null,0.1,null,0.1,null,0.1,null,null,null,null,0.1,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"3.5",null,"3.5",null,"3.5",null,"3.5",null,null,null,null,"3.5",null,"3.5",null,"3.5",null,null,null,null,null,"3.5","3.5",null,null,"3.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,7.5,null,7.5,null,7.5,null,7.5,null,null,null,null,7.5,null,7.5,null,7.5,null,null,null,null,null,7.5,7.5,null,null,7.5]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"GLFS","index":93,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"GLFS - Friend Street (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T019 - Gladstone South BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Capricornia"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/11kV 16/20MVA ONAN/ONAF;1x66/11kV 24/32MVA ONAN/ONAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.9%, 2020 S -1.1% W -1.1%2021 S -0.7% W -0.7%2022 S -0.9% W -0.9%2023 S -0.9% W -0.9"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"18.6 MVA on 28/11/2018 at 14:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,47.400001525878906,null,47.400001525878906,null,47.400001525878906,null,47.400001525878906,null,null,null,null,47.400001525878906,null,53.299999237060547,null,53.299999237060547,null,null,null,null,null,53.299999237060547,53.299999237060547,null,null,53.299999237060547]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,17,null,16.799999237060547,null,16.5,null,16.299999237060547,null,null,null,null,16.399999618530273,null,12.300000190734863,null,12.199999809265137,null,null,null,null,null,12.100000381469727,11.899999618530273,null,null,11.899999618530273]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.997,null,0.998,null,0.998,null,0.998,null,null,null,null,0.998,null,0.93799999999999994,null,0.93799999999999994,null,null,null,null,null,0.93799999999999994,0.93799999999999994,null,null,0.93799999999999994]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,27.200000762939453,null,27.200000762939453,null,27.200000762939453,null,27.200000762939453,null,null,null,null,27.200000762939453,null,29.799999237060547,null,29.799999237060547,null,null,null,null,null,29.799999237060547,29.799999237060547,null,null,29.799999237060547]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,15.699999809265137,null,15.5,null,15.199999809265137,null,15.100000381469727,null,null,null,null,15.100000381469727,null,12,null,11.899999618530273,null,null,null,null,null,11.800000190734863,11.600000381469727,null,null,11.600000381469727]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.8,null,0.8,null,0.8,null,0.8,null,null,null,null,0.8,null,0.6,null,0.6,null,null,null,null,null,0.6,0.6,null,null,0.6]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"7.5",null,"7.5",null,"7.5",null,"7.5",null,null,null,null,"7.5",null,"7.5",null,"7.5",null,null,null,null,null,"7.5","7.5",null,null,"7.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,2.2000000476837158,null,2.2000000476837158,null,2.2000000476837158,null,2.2000000476837158,null,null,null,null,2.2000000476837158,null,2.2000000476837158,null,2.2000000476837158,null,null,null,null,null,2.2000000476837158,2.2000000476837158,null,null,2.2000000476837158]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,1,null,1,null,1,null,1,null,null,null,null,1,null,1,null,1,null,null,null,null,null,1,1,null,null,1]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"GLSO","index":94,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"GLSO - Gladstone South (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T019 - Gladstone South BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Capricornia"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/11kV 15/20 MVA ONAN/ONAF;1x66/11kV 15/20MVA ONAN/ONAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.0%, 2020 S 0.2% W 0.2%, 2021 S 0.2% W 0.2%, 2022 S 0.8% W 0.8%, 2023 S 0.6% W 0.6%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"23.8 MVA on 28/11/2018 at 18:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,54.700000762939453,null,54.700000762939453,null,54.700000762939453,null,54.700000762939453,null,null,null,null,54.700000762939453,null,59.799999237060547,null,59.799999237060547,null,null,null,null,null,59.799999237060547,59.799999237060547,null,null,59.799999237060547]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,25.100000381469727,null,25.100000381469727,null,25,null,25.200000762939453,null,null,null,null,25.5,null,14.800000190734863,null,14.800000190734863,null,null,null,null,null,14.800000190734863,14.899999618530273,null,null,15]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.98599999999999999,null,0.98599999999999999,null,0.98599999999999999,null,0.98599999999999999,null,null,null,null,0.98599999999999999,null,0.99299999999999999,null,0.99299999999999999,null,null,null,null,null,0.99299999999999999,0.99299999999999999,null,null,0.99299999999999999]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,29.600000381469727,null,29.600000381469727,null,29.600000381469727,null,29.600000381469727,null,null,null,null,29.600000381469727,null,29.899999618530273,null,29.899999618530273,null,null,null,null,null,29.899999618530273,29.899999618530273,null,null,29.899999618530273]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,23.200000762939453,null,23.100000381469727,null,23.100000381469727,null,23.299999237060547,null,null,null,null,23.5,null,14.199999809265137,null,14.199999809265137,null,null,null,null,null,14.199999809265137,14.300000190734863,null,null,14.399999618530273]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,1.2,null,1.2,null,1.2,null,1.2,null,null,null,null,1.2,null,0.7,null,0.7,null,null,null,null,null,0.7,0.7,null,null,0.7]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"4.5",null,"4.5",null,"4.5",null,"4.5",null,null,null,null,"4.5",null,"4.5",null,"4.5",null,null,null,null,null,"4.5","4.5",null,null,"4.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,7.8000001907348633,null,7.8000001907348633,null,7.8000001907348633,null,7.8000001907348633,null,null,null,null,7.8000001907348633,null,7.8000001907348633,null,7.8000001907348633,null,null,null,null,null,7.8000001907348633,7.8000001907348633,null,null,7.8000001907348633]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0.80000001192092896,null,0.80000001192092896,null,0.80000001192092896,null,0.80000001192092896,null,null,null,null,0.80000001192092896,null,0.80000001192092896,null,0.80000001192092896,null,null,null,null,null,0.80000001192092896,0.80000001192092896,null,null,0.80000001192092896]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"GOOB","index":95,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"GOOB - Gooburrum (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T020 - Bundaberg BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Wide Bay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/11kV 5MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.3%, 2020 S 0.3% W 0.3%, 2021 S 0.3% W 0.3%, 2022 S 0.2% W 0.2%, 2023 S 0.1% W 0.1%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"5.5 MVA on 19/02/2019 at 19:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,14.300000190734863,null,14.300000190734863,null,14.300000190734863,null,14.300000190734863,null,null,null,null,14.300000190734863,null,15,null,15,null,null,null,null,null,15,15,null,null,15]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,5.9000000953674316,null,5.9000000953674316,null,5.9000000953674316,null,5.9000000953674316,null,null,null,null,5.9000000953674316,null,3,null,3,null,null,null,null,null,3,3,null,null,3]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.9,null,0.9,null,0.9,null,0.9,null,null,null,null,0.9,null,0.91800000000000004,null,0.91800000000000004,null,null,null,null,null,0.91800000000000004,0.91800000000000004,null,null,0.91800000000000004]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,7.5,null,7.5,null,7.5,null,7.5,null,null,null,null,7.5,null,7.5,null,7.5,null,null,null,null,null,7.5,7.5,null,null,7.5]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,5.5,null,5.5,null,5.4000000953674316,null,5.5,null,null,null,null,5.5,null,2.7999999523162842,null,2.7999999523162842,null,null,null,null,null,2.7999999523162842,2.7999999523162842,null,null,2.7999999523162842]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.3,null,0.3,null,0.3,null,0.3,null,null,null,null,0.3,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"8",null,"8",null,"8",null,"8",null,null,null,null,"8",null,"8",null,"8",null,null,null,null,null,"8","8",null,null,"8"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"GOOT","index":96,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"GOOT - Gootchie (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T059 - Maryborough BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Wide Bay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x62/11kV 2MVA ON;1x66/11kV 6.3MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.4%, 2020 S 0.3% W 0.3%, 2021 S 0.7% W 0.7%, 2022 S 0.6% W 0.6%, 2023 S 0.2% W 0.2%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"3.6 MVA on 13/02/2019 at 17:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,5,null,5,null,5,null,5,null,null,null,null,5,null,5.8000001907348633,null,5.8000001907348633,null,null,null,null,null,5.8000001907348633,5.8000001907348633,null,null,5.8000001907348633]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,3.9000000953674316,null,3.9000000953674316,null,3.9000000953674316,null,3.9000000953674316,null,null,null,null,4,null,2.9000000953674316,null,2.9000000953674316,null,null,null,null,null,2.9000000953674316,2.9000000953674316,null,null,3]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.95499999999999996,null,0.95499999999999996,null,0.95499999999999996,null,0.95499999999999996,null,null,null,null,0.95499999999999996,null,0.97099999999999997,null,0.97099999999999997,null,null,null,null,null,0.97099999999999997,0.97099999999999997,null,null,0.97099999999999997]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,2.7999999523162842,null,2.7999999523162842,null,2.7999999523162842,null,2.7999999523162842,null,null,null,null,2.7999999523162842,null,3,null,3,null,null,null,null,null,3,3,null,null,3]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,3.5,null,3.5999999046325684,null,3.5,null,3.5999999046325684,null,null,null,null,3.5999999046325684,null,2.7000000476837158,null,2.7000000476837158,null,null,null,null,null,2.7000000476837158,2.7999999523162842,null,null,2.7999999523162842]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.2,null,0.2,null,0.2,null,0.2,null,null,null,null,0.2,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"6",null,"6",null,"6",null,"6",null,null,null,null,"6",null,"6",null,"6",null,null,null,null,null,"6","6",null,null,"6"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,0.7,null,0.8,null,0.7,null,0.8,null,null,null,null,0.8]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,2,null,2,null,2,null,2,null,null,null,null,2,null,2,null,2,null,null,null,null,null,2,2,null,null,2]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"Gracem","index":97,"n_rows":47,"n_cols":29,"rows_kept":47,"cut":false,"hidden":false,"merged":[[0,2,0,35],[2,1,2,5],[2,8,4,18],[2,19,3,21],[2,24,4,30],[6,1,8,5],[6,8,6,31],[8,8,9,31],[11,8,11,31],[13,0,13,4],[13,8,13,31],[15,1,15,34],[17,12,17,17],[17,23,17,25],[20,3,21,9],[20,10,20,19],[20,20,20,28],[21,10,21,12],[21,15,21,16],[21,17,21,19],[21,21,21,24],[21,25,21,26],[22,3,22,9],[22,10,22,12],[22,15,22,16],[22,17,22,19],[22,21,22,24],[22,25,22,26],[23,3,23,9],[23,10,23,12],[23,15,23,16],[23,17,23,19],[23,21,23,24],[23,25,23,26],[24,3,24,9],[24,10,24,12],[24,15,24,16],[24,17,24,19],[24,21,24,24],[24,25,24,26],[25,3,25,9],[25,10,25,12],[25,15,25,16],[25,17,25,19],[25,21,25,24],[25,25,25,26],[26,3,26,9],[26,10,26,12],[26,15,26,16],[26,17,26,19],[26,21,26,24],[26,25,26,26],[27,3,27,9],[27,10,27,12],[27,15,27,16],[27,17,27,19],[27,21,27,24],[27,25,27,26],[28,3,28,9],[28,10,28,12],[28,15,28,16],[28,17,28,19],[28,21,28,24],[28,25,28,26],[29,3,29,9],[29,10,29,12],[29,15,29,16],[29,17,29,19],[29,21,29,24],[29,25,29,26],[30,3,30,9],[30,10,30,12],[30,15,30,16],[30,17,30,19],[30,21,30,24],[30,25,30,26],[31,3,31,9],[31,10,31,12],[31,15,31,16],[31,17,31,19],[31,21,31,24],[31,25,31,26],[32,3,32,9],[32,10,32,12],[32,15,32,16],[32,17,32,19],[32,21,32,24],[32,25,32,26],[33,3,33,9],[33,10,33,12],[33,15,33,16],[33,17,33,19],[33,21,33,24],[33,25,33,26],[34,3,34,9],[34,10,34,12],[34,15,34,16],[34,17,34,19],[34,21,34,24],[34,25,34,26],[35,3,35,9],[35,10,35,12],[35,15,35,16],[35,17,35,19],[35,21,35,24],[35,25,35,26],[36,3,36,9],[36,10,36,12],[36,15,36,16],[36,17,36,19],[36,21,36,24],[36,25,36,26],[37,3,37,9],[37,10,37,12],[37,15,37,16],[37,17,37,19],[37,21,37,24],[37,25,37,26],[38,3,38,9],[38,10,38,12],[38,15,38,16],[38,17,38,19],[38,21,38,24],[38,25,38,26],[39,3,39,9],[39,10,39,12],[39,15,39,16],[39,17,39,19],[39,21,39,24],[39,25,39,26],[46,2,46,32],[42,3,42,9],[42,10,42,12],[42,15,42,16],[42,17,42,19],[42,21,42,24],[42,25,42,26],[40,3,40,9],[40,10,40,12],[40,15,40,16],[40,17,40,19],[40,21,40,24],[40,25,40,26],[41,3,41,9],[41,10,41,12],[41,15,41,16],[41,17,41,19],[41,21,41,24],[41,25,41,26]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,"Gracem - Gracemere (66/11kV)",null,null,null,null,null,null,null,null,null,null,"Supply",null,null,null,null,"RMES - Rockhampton Mesh"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,"Region is Capricornia"]
[]
[null,null,null,null,null,null,null,null,"Transformer size is 1x10MVA 66kV Transformer"]
[]
[]
[null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,"2021 W 1.0%, 2022 S 1.3% W 1.3%, 2023 S 1.0% W 1.0%"]
[]
[null,"No current information, due to be commissioned Winter 2021 "]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,null,"2020/21","2021/22","2022/23",null,"2023/24",null,null,"2019","2020",null,null,null,"2021",null,"2022","2023"]
[null,null,null,"NCC Rating (MVA)",null,null,null,null,null,null,null,null,null,null,11,11,null,11,null,null,null,null,null,null,null,11,null,11,11]
[null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,null,null,null,null,null,0,0,null,0,null,null,null,null,null,null,null,0,null,0,0]
[null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,null,null,null,null,null,8.5,8.6000003814697266,null,8.8000001907348633,null,null,null,null,null,null,null,2.5999999046325684,null,2.5999999046325684,2.7000000476837158]
[null,null,null,"LARn (MVA)"]
[null,null,null,"LARn (MW)"]
[null,null,null,"Power Factor at Peak Load",null,null,null,null,null,null,null,null,null,null,0.97299999999999998,0.97299999999999998,null,0.97299999999999998,null,null,null,null,null,null,null,0.97699999999999998,null,0.97699999999999998,0.97699999999999998]
[null,null,null,"ECC Rating (MVA)",null,null,null,null,null,null,null,null,null,null,0,0,null,0,null,null,null,null,null,null,null,0,null,0,0]
[null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,null,null,null,null,null,8.5,8.6000003814697266,null,8.8000001907348633,null,null,null,null,null,null,null,2.5999999046325684,null,2.5999999046325684,2.7000000476837158]
[null,null,null,"50 PoE Load >    (MVA)",null,null,null,null,null,null,null,null,null,null,0.4,0.4,null,0.4,null,null,null,null,null,null,null,0.1,null,0.1,0.1]
[null,null,null,"Hours PA >    Peak Load",null,null,null,null,null,null,null,null,null,null,"N/A","N/A",null,"N/A",null,null,null,null,null,null,null,"N/A",null,"N/A","N/A"]
[null,null,null,"Raw LAR (MVA)",null,null,null,null,null,null,null,null,null,null,8.5,8.6,null,8.8000000000000007,null,null,null,null,null,null,null,2.6,null,2.6,2.7]
[null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,null,null,null,null,null,0,0,null,0,null,null,null,null,null,null,null,0,null,0,0]
[null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,null,null,null,null,null,0,0,null,0,null,null,null,null,null,null,null,0,null,0,0]
[null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,null,null,null,null,null,10,10,null,10,null,null,null,null,null,null,null,10,null,10,10]
[null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,null,null,null,null,null,0,0,null,0,null,null,null,null,null,null,null,0,null,0,0]
[null,null,null,"Shed(30min)",null,null,null,null,null,null,null,null,null,null,0,0,null,0,null,null,null,null,null,null,null,0,null,0,0]
[null,null,null,"Shed(4Hour)",null,null,null,null,null,null,null,null,null,null,0,0,null,0,null,null,null,null,null,null,null,0,null,0,0]
[null,null,null,"LARc (MVA)"]
[null,null,null,"LARc (MW)"]
[null,null,null,"Substation Category"]
[null,null,null,"Meets Security Standard",null,null,null,null,null,null,null,null,null,null,"Yes","Yes",null,"Yes",null,null,null,null,null,null,null,"Yes",null,"Yes","Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"GRCR","index":98,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"GRCR - Granite Creek (66/22kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T166 - Granite Creek BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Capricornia"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1xGRCRSS 22/22KV REGULATOR 1 REG 1"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.1%, 2020 S 0.2% W 0.2%, 2021 S 0.3% W 0.3%, 2022 S 0.1% W 0.1%, 2023 S 0.0% W 0.0%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"0.3 MVA on 21/02/2019 at 18:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,3.7999999523162842,null,3.7999999523162842,null,3.7999999523162842,null,3.7999999523162842,null,null,null,null,3.7999999523162842,null,3.7999999523162842,null,3.7999999523162842,null,null,null,null,null,3.7999999523162842,3.7999999523162842,null,null,3.7999999523162842]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,0.30000001192092896,null,0.30000001192092896,null,0.30000001192092896,null,0.30000001192092896,null,null,null,null,0.30000001192092896,null,0.30000001192092896,null,0.30000001192092896,null,null,null,null,null,0.30000001192092896,0.30000001192092896,null,null,0.30000001192092896]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.94299999999999995,null,0.94299999999999995,null,0.94299999999999995,null,0.94299999999999995,null,null,null,null,0.94299999999999995,null,0.91900000000000004,null,0.91900000000000004,null,null,null,null,null,0.91900000000000004,0.91900000000000004,null,null,0.91900000000000004]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,0.30000001192092896,null,0.30000001192092896,null,0.30000001192092896,null,0.30000001192092896,null,null,null,null,0.30000001192092896,null,0.30000001192092896,null,0.30000001192092896,null,null,null,null,null,0.30000001192092896,0.30000001192092896,null,null,0.30000001192092896]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"6",null,"6",null,"6",null,"6",null,null,null,null,"6",null,"6",null,"6",null,null,null,null,null,"6","6",null,null,"6"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,0.3,null,0.3,null,0.3,null,0.3,null,null,null,null,0.3,null,0.3,null,0.3,null,null,null,null,null,0.3,0.3,null,null,0.3]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0.30000001192092896,null,0.30000001192092896,null,0.30000001192092896,null,0.30000001192092896,null,null,null,null,0.30000001192092896,null,0.30000001192092896,null,0.30000001192092896,null,null,null,null,null,0.30000001192092896,0.30000001192092896,null,null,0.30000001192092896]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"GREN","index":99,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"GREN - Greenvale (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T047 - Ingham BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Nth Queensland"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/11kV 0.5MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.0%, 2020 S 0.3% W 0.3%, 2021 S 0.2% W 0.2%, 2022 S 0.0% W 0.0%, 2023 S -0.1% W -0.1"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"0.5 MVA on 25/11/2018 at 18:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,0.69999998807907104,null,0.69999998807907104,null,0.69999998807907104,null,0.69999998807907104,null,null,null,null,0.69999998807907104,null,0.69999998807907104,null,0.69999998807907104,null,null,null,null,null,0.69999998807907104,0.69999998807907104,null,null,0.69999998807907104]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,0.60000002384185791,null,0.60000002384185791,null,0.60000002384185791,null,0.60000002384185791,null,null,null,null,0.60000002384185791,null,0.5,null,0.5,null,null,null,null,null,0.5,0.5,null,null,0.5]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.98699999999999999,null,0.98699999999999999,null,0.98699999999999999,null,0.98699999999999999,null,null,null,null,0.98699999999999999,null,0.99,null,0.99,null,null,null,null,null,0.99,0.99,null,null,0.99]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,0.60000002384185791,null,0.60000002384185791,null,0.60000002384185791,null,0.60000002384185791,null,null,null,null,0.60000002384185791,null,0.40000000596046448,null,0.40000000596046448,null,null,null,null,null,0.40000000596046448,0.40000000596046448,null,null,0.40000000596046448]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"2",null,"2",null,"2",null,"2",null,null,null,null,"2",null,"2",null,"2",null,null,null,null,null,"2","2",null,null,"2"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,0.6,null,0.6,null,0.6,null,0.6,null,null,null,null,0.6,null,0.4,null,0.4,null,null,null,null,null,0.4,0.4,null,null,0.4]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,1,null,1,null,1,null,1,null,null,null,null,1,null,1,null,1,null,null,null,null,null,1,1,null,null,1]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"GUML","index":100,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"GUML - Gumlu (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T193 - Clare South BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Nth Queensland"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/11kV 0.5MVA ONAN;1x66/11kV 1MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -2.4%, 2020 S -1.7% W -1.7%2021 S -1.6% W -1.6%2022 S -1.0% W -1.0%2023 S -1.1% W -1.1"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"1.2 MVA on 07/07/2018 at 11:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,1.7,null,1.7,null,1.7,null,1.7,null,null,null,null,1.7,null,1.7,null,1.7,null,null,null,null,null,1.7,1.7,null,null,1.7]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,1.5,null,1.5,null,1.5,null,1.5,null,null,null,null,1.5,null,1.2000000476837158,null,1.2000000476837158,null,null,null,null,null,1.2000000476837158,1.2000000476837158,null,null,1.2000000476837158]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.87,null,0.87,null,0.87,null,0.87,null,null,null,null,0.87,null,0.88500000000000001,null,0.88500000000000001,null,null,null,null,null,0.88500000000000001,0.88500000000000001,null,null,0.88500000000000001]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0.69999998807907104,null,0.69999998807907104,null,0.69999998807907104,null,0.69999998807907104,null,null,null,null,0.69999998807907104,null,0.80000001192092896,null,0.80000001192092896,null,null,null,null,null,0.80000001192092896,0.80000001192092896,null,null,0.80000001192092896]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,1.2000000476837158,null,1.2000000476837158,null,1.2000000476837158,null,1.2000000476837158,null,null,null,null,1.2000000476837158,null,1.1000000238418579,null,1.1000000238418579,null,null,null,null,null,1.1000000238418579,1.1000000238418579,null,null,1.1000000238418579]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.1,null,0.1,null,0.1,null,0.1,null,null,null,null,0.1,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"11.5",null,"11.5",null,"11.5",null,"11.5",null,null,null,null,"11.5",null,"11.5",null,"11.5",null,null,null,null,null,"11.5","11.5",null,null,"11.5"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,0.5,null,0.5,null,0.5,null,0.5,null,null,null,null,0.5,null,0.3,null,0.3,null,null,null,null,null,0.3,0.3,null,null,0.3]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,1,null,1,null,1,null,1,null,null,null,null,1,null,1,null,1,null,null,null,null,null,1,1,null,null,1]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"GUTH","index":101,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"GUTH - Guthalungra (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T193 - Clare South BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Nth Queensland"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/11kV 0.5MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.0%, 2020 S 0.0% W 0.0%, 2021 S 0.0% W 0.0%, 2022 S 0.0% W 0.0%, 2023 S 0.0% W 0.0%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"0.5 MVA on 01/01/2019 at 17:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,0.60000002384185791,null,0.60000002384185791,null,0.60000002384185791,null,0.60000002384185791,null,null,null,null,0.60000002384185791,null,0.60000002384185791,null,0.60000002384185791,null,null,null,null,null,0.60000002384185791,0.60000002384185791,null,null,0.60000002384185791]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,0.60000002384185791,null,0.60000002384185791,null,0.60000002384185791,null,0.60000002384185791,null,null,null,null,0.60000002384185791,null,0.30000001192092896,null,0.30000001192092896,null,null,null,null,null,0.30000001192092896,0.30000001192092896,null,null,0.30000001192092896]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.85,null,0.85,null,0.85,null,0.85,null,null,null,null,0.85,null,0.85,null,0.85,null,null,null,null,null,0.85,0.85,null,null,0.85]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,0.5,null,0.5,null,0.5,null,0.5,null,null,null,null,0.5,null,0.30000001192092896,null,0.30000001192092896,null,null,null,null,null,0.30000001192092896,0.30000001192092896,null,null,0.30000001192092896]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"0",null,"0",null,"0",null,"0",null,null,null,null,"0",null,"0",null,"0",null,null,null,null,null,"0","0",null,null,"0"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,0.5,null,0.5,null,0.5,null,0.5,null,null,null,null,0.5,null,0.3,null,0.3,null,null,null,null,null,0.3,0.3,null,null,0.3]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,1,null,1,null,1,null,1,null,null,null,null,1,null,1,null,1,null,null,null,null,null,1,1,null,null,1]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"HAPU","index":102,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"HAPU - Haughton (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T193 - Clare South BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Nth Queensland"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/11kV 2.5MVA ONAN;1x66/11kV 4MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.3%, 2020 S 0.2% W 0.2%, 2021 S 0.1% W 0.1%, 2022 S 0.3% W 0.3%, 2023 S 0.2% W 0.2%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"4.8 MVA on 18/01/2019 at 14:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,6.1999998092651367,null,6.1999998092651367,null,6.1999998092651367,null,6.1999998092651367,null,null,null,null,6.1999998092651367,null,6.6999998092651367,null,6.6999998092651367,null,null,null,null,null,6.6999998092651367,6.6999998092651367,null,null,6.6999998092651367]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,5.0999999046325684,null,5.0999999046325684,null,5,null,5.0999999046325684,null,null,null,null,5.0999999046325684,null,4.5,null,4.5,null,null,null,null,null,4.5,4.5,null,null,4.5]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.83499999999999996,null,0.83499999999999996,null,0.83499999999999996,null,0.83499999999999996,null,null,null,null,0.83499999999999996,null,0.84299999999999997,null,0.84299999999999997,null,null,null,null,null,0.84299999999999997,0.84299999999999997,null,null,0.84299999999999997]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,3.7000000476837158,null,3.7000000476837158,null,3.7000000476837158,null,3.7000000476837158,null,null,null,null,3.7000000476837158,null,3.7000000476837158,null,3.7000000476837158,null,null,null,null,null,3.7000000476837158,3.7000000476837158,null,null,3.7000000476837158]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,5,null,5,null,4.9000000953674316,null,4.9000000953674316,null,null,null,null,5,null,4.5,null,4.5,null,null,null,null,null,4.5,4.5,null,null,4.5]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.3,null,0.3,null,0.2,null,0.2,null,null,null,null,0.3,null,0.2,null,0.2,null,null,null,null,null,0.2,0.2,null,null,0.2]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"169.5",null,"169.5",null,"169.5",null,"169.5",null,null,null,null,"169.5",null,"169.5",null,"169.5",null,null,null,null,null,"169.5","169.5",null,null,"169.5"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,1.3,null,1.3,null,1.2,null,1.2,null,null,null,null,1.3,null,0.8,null,0.8,null,null,null,null,null,0.8,0.8,null,null,0.8]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0.80000001192092896,null,0.80000001192092896,null,0.80000001192092896,null,0.80000001192092896,null,null,null,null,0.80000001192092896,null,0.80000001192092896,null,0.80000001192092896,null,null,null,null,null,0.80000001192092896,0.80000001192092896,null,null,0.80000001192092896]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0.69999998807907104,null,0.69999998807907104,null,0.69999998807907104,null,0.69999998807907104,null,null,null,null,0.69999998807907104,null,0.69999998807907104,null,0.69999998807907104,null,null,null,null,null,0.69999998807907104,0.69999998807907104,null,null,0.69999998807907104]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"HELE","index":103,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"HELE - Helenvale (66/22kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T159 - Lakeland BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Far North"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/22kV 4MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.0%, 2020 S 0.0% W 0.0%, 2021 S 0.0% W 0.0%, 2022 S 0.0% W 0.0%, 2023 S -0.0% W -0.0"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"0.7 MVA on 26/11/2018 at 18:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,5.6999998092651367,null,5.6999998092651367,null,5.6999998092651367,null,5.6999998092651367,null,null,null,null,5.6999998092651367,null,6.3000001907348633,null,6.3000001907348633,null,null,null,null,null,6.3000001907348633,6.3000001907348633,null,null,6.3000001907348633]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,0.69999998807907104,null,0.69999998807907104,null,0.69999998807907104,null,0.69999998807907104,null,null,null,null,0.69999998807907104,null,0.5,null,0.5,null,null,null,null,null,0.5,0.5,null,null,0.5]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.98699999999999999,null,0.98699999999999999,null,0.98699999999999999,null,0.98699999999999999,null,null,null,null,0.98699999999999999,null,0.97499999999999998,null,0.97499999999999998,null,null,null,null,null,0.97499999999999998,0.97499999999999998,null,null,0.97499999999999998]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,0.69999998807907104,null,0.69999998807907104,null,0.69999998807907104,null,0.69999998807907104,null,null,null,null,0.69999998807907104,null,0.5,null,0.5,null,null,null,null,null,0.5,0.5,null,null,0.5]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"24.5",null,"24.5",null,"24.5",null,"24.5",null,null,null,null,"24.5",null,"24.5",null,"24.5",null,null,null,null,null,"24.5","24.5",null,null,"24.5"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,0.7,null,0.7,null,0.7,null,0.7,null,null,null,null,0.7,null,0.5,null,0.5,null,null,null,null,null,0.5,0.5,null,null,0.5]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,1.2000000476837158,null,1.2000000476837158,null,1.2000000476837158,null,1.2000000476837158,null,null,null,null,1.2000000476837158,null,1.2000000476837158,null,1.2000000476837158,null,null,null,null,null,1.2000000476837158,1.2000000476837158,null,null,1.2000000476837158]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"HEPA","index":104,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"HEPA - Hermit Park (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"TMES - Townsville Mesh"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Nth Queensland"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/11kV 15/20/25MVA ONAN/ONAF/ODAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.1%, 2020 S 0.1% W 0.1%, 2021 S -0.0% W -0.0%2022 S -0.4% W -0.4%2023 S -0.7% W -0.7"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"22.6 MVA on 26/11/2018 at 16:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,56.599998474121094,null,56.599998474121094,null,56.599998474121094,null,56.599998474121094,null,null,null,null,56.599998474121094,null,58.599998474121094,null,58.599998474121094,null,null,null,null,null,58.599998474121094,58.599998474121094,null,null,58.599998474121094]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,23.5,null,23.5,null,23.100000381469727,null,23,null,null,null,null,23,null,13.399999618530273,null,13.399999618530273,null,null,null,null,null,13.300000190734863,13.300000190734863,null,null,13.199999809265137]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.96,null,0.96,null,0.96,null,0.96,null,null,null,null,0.96,null,0.96299999999999997,null,0.96299999999999997,null,null,null,null,null,0.96299999999999997,0.96299999999999997,null,null,0.96299999999999997]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,31.5,null,31.5,null,31.5,null,31.5,null,null,null,null,31.5,null,32.599998474121094,null,32.599998474121094,null,null,null,null,null,32.599998474121094,32.599998474121094,null,null,32.599998474121094]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,21.5,null,21.399999618530273,null,21.100000381469727,null,21,null,null,null,null,21,null,13,null,13,null,null,null,null,null,12.899999618530273,12.899999618530273,null,null,12.800000190734863]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,1.1000000000000001,null,1.1000000000000001,null,1.1000000000000001,null,1.1000000000000001,null,null,null,null,1.1000000000000001,null,0.7,null,0.7,null,null,null,null,null,0.6,0.6,null,null,0.6]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"5.5",null,"5.5",null,"5.5",null,"5.5",null,null,null,null,"5.5",null,"5.5",null,"5.5",null,null,null,null,null,"5.5","5.5",null,null,"5.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,3.5,null,3.5,null,3.5,null,3.5,null,null,null,null,3.5,null,3.5,null,3.5,null,null,null,null,null,3.5,3.5,null,null,3.5]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,1.2000000476837158,null,1.2000000476837158,null,1.2000000476837158,null,1.2000000476837158,null,null,null,null,1.2000000476837158,null,1.2000000476837158,null,1.2000000476837158,null,null,null,null,null,1.2000000476837158,1.2000000476837158,null,null,1.2000000476837158]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"HIGH","index":105,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"HIGH - Highfields (33/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T029 - Postmans Ridge BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is South West"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x33/11kV 5MVA ON"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.6%, 2020 S 0.9% W 0.9%, 2021 S 0.8% W 0.8%, 2022 S 1.1% W 1.1%, 2023 S 0.7% W 0.7%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"2.3 MVA on 19/06/2018 at 19:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,5.5,null,5.5,null,5.5,null,5.5,null,null,null,null,5.5,null,5.5,null,5.5,null,null,null,null,null,5.5,5.5,null,null,5.5]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,2.2999999523162842,null,2.2999999523162842,null,2.2999999523162842,null,2.4000000953674316,null,null,null,null,2.4000000953674316,null,2.5,null,2.5,null,null,null,null,null,2.5,2.5999999046325684,null,null,2.5999999046325684]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.97699999999999998,null,0.97699999999999998,null,0.97699999999999998,null,0.97699999999999998,null,null,null,null,0.97699999999999998,null,0.98699999999999999,null,0.98699999999999999,null,null,null,null,null,0.98699999999999999,0.98699999999999999,null,null,0.98699999999999999]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,2,null,2,null,2,null,2.0999999046325684,null,null,null,null,2.0999999046325684,null,2.2999999523162842,null,2.2999999523162842,null,null,null,null,null,2.4000000953674316,2.4000000953674316,null,null,2.4000000953674316]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.1,null,0.1,null,0.1,null,0.1,null,null,null,null,0.1,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"46",null,"46",null,"46",null,"46",null,null,null,null,"46",null,"46",null,"46",null,null,null,null,null,"46","46",null,null,"46"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,2,null,2,null,2,null,2.1,null,null,null,null,2.1,null,2.2999999999999998,null,2.2999999999999998,null,null,null,null,null,2.4,2.4,null,null,2.4]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,5.5,null,5.5,null,5.5,null,5.5,null,null,null,null,5.5,null,5.5,null,5.5,null,null,null,null,null,5.5,5.5,null,null,5.5]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"HILL","index":106,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"HILL - Hillsborough (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T193 - Clare South BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Nth Queensland"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/11kV 0.05MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.0%, 2020 S 0.0% W 0.0%, 2021 S 0.0% W 0.0%, 2022 S 0.0% W 0.0%, 2023 S 0.0% W 0.0%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"0.1 MVA on 01/01/2019 at 17:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,0.10000000149011612,null,0.10000000149011612,null,0.10000000149011612,null,0.10000000149011612,null,null,null,null,0.10000000149011612,null,0.10000000149011612,null,0.10000000149011612,null,null,null,null,null,0.10000000149011612,0.10000000149011612,null,null,0.10000000149011612]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,0.10000000149011612,null,0.10000000149011612,null,0.10000000149011612,null,0.10000000149011612,null,null,null,null,0.10000000149011612,null,0.10000000149011612,null,0.10000000149011612,null,null,null,null,null,0.10000000149011612,0.10000000149011612,null,null,0.10000000149011612]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.85,null,0.85,null,0.85,null,0.85,null,null,null,null,0.85,null,0.65900000000000003,null,0.65900000000000003,null,null,null,null,null,0.65900000000000003,0.65900000000000003,null,null,0.65900000000000003]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,0.10000000149011612,null,0.10000000149011612,null,0.10000000149011612,null,0.10000000149011612,null,null,null,null,0.10000000149011612,null,0.10000000149011612,null,0.10000000149011612,null,null,null,null,null,0.10000000149011612,0.10000000149011612,null,null,0.10000000149011612]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"0",null,"0",null,"0",null,"0",null,null,null,null,"0",null,"0",null,"0",null,null,null,null,null,"0","0",null,null,"0"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,0.1,null,0.1,null,0.1,null,0.1,null,null,null,null,0.1,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0.10000000149011612,null,0.10000000149011612,null,0.10000000149011612,null,0.10000000149011612,null,null,null,null,0.10000000149011612,null,0.10000000149011612,null,0.10000000149011612,null,null,null,null,null,0.10000000149011612,0.10000000149011612,null,null,0.10000000149011612]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"HOHI","index":107,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"HOHI - Home Hill (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T193 - Clare South BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Nth Queensland"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/11kV 15/20/25MVA ONAN/ODAN/ODAF;1x66/11kV 15/20/25MVA ONAN/ONAF/ODAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 15.1 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.5%, 2020 S -0.2% W -0.2%2021 S -0.3% W -0.3%2022 S -0.4% W -0.4%2023 S -0.6% W -0.6"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"14.1 MVA on 22/01/2019 at 19:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,59.299999237060547,null,59.299999237060547,null,59.299999237060547,null,59.299999237060547,null,null,null,null,59.299999237060547,null,65.099998474121094,null,65.099998474121094,null,null,null,null,null,65.099998474121094,65.099998474121094,null,null,65.099998474121094]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0.20000000298023224,null,0.20000000298023224,null,0.20000000298023224,null,0.20000000298023224,null,null,null,null,0.20000000298023224,null,0.10000000149011612,null,0.10000000149011612,null,null,null,null,null,0.10000000149011612,0.10000000149011612,null,null,0.10000000149011612]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,14.899999618530273,null,14.800000190734863,null,14.600000381469727,null,14.600000381469727,null,null,null,null,14.600000381469727,null,7.9000000953674316,null,7.9000000953674316,null,null,null,null,null,7.8000001907348633,7.8000001907348633,null,null,7.8000001907348633]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.89100000000000001,null,0.89100000000000001,null,0.89100000000000001,null,0.89100000000000001,null,null,null,null,0.89100000000000001,null,0.90200000000000002,null,0.90200000000000002,null,null,null,null,null,0.90200000000000002,0.90200000000000002,null,null,0.90200000000000002]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,34.599998474121094,null,34.599998474121094,null,34.599998474121094,null,34.599998474121094,null,null,null,null,34.599998474121094,null,36.799999237060547,null,36.799999237060547,null,null,null,null,null,36.799999237060547,36.799999237060547,null,null,36.799999237060547]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,14.600000381469727,null,14.5,null,14.300000190734863,null,14.199999809265137,null,null,null,null,14.199999809265137,null,7.1999998092651367,null,7.0999999046325684,null,null,null,null,null,7.0999999046325684,7,null,null,7]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.7,null,0.7,null,0.7,null,0.7,null,null,null,null,0.7,null,0.4,null,0.4,null,null,null,null,null,0.4,0.4,null,null,0.4]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"11",null,"11",null,"11",null,"11",null,null,null,null,"11",null,"11",null,"11",null,null,null,null,null,"11","11",null,null,"11"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"HOWA","index":108,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"HOWA - Howard (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T131 - Isis BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Wide Bay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x62/11kV 7.5MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 1.2%, 2020 S 1.4% W 1.4%, 2021 S 1.4% W 1.4%, 2022 S 1.3% W 1.3%, 2023 S 1.1% W 1.1%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"8.1 MVA on 10/02/2019 at 18:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,16.100000381469727,null,16.100000381469727,null,16.100000381469727,null,16.100000381469727,null,null,null,null,16.100000381469727,null,16.100000381469727,null,16.100000381469727,null,null,null,null,null,16.100000381469727,16.100000381469727,null,null,16.100000381469727]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,9.1000003814697266,null,9.1999998092651367,null,9.1999998092651367,null,9.3000001907348633,null,null,null,null,9.5,null,8.1999998092651367,null,8.3000001907348633,null,null,null,null,null,8.3999996185302734,8.5,null,null,8.6000003814697266]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.97799999999999998,null,0.97799999999999998,null,0.97799999999999998,null,0.97799999999999998,null,null,null,null,0.97799999999999998,null,0.99,null,0.99,null,null,null,null,null,0.99,0.99,null,null,0.99]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,8.3000001907348633,null,8.3000001907348633,null,8.3000001907348633,null,8.3000001907348633,null,null,null,null,8.3000001907348633,null,8.6000003814697266,null,8.6000003814697266,null,null,null,null,null,8.6000003814697266,8.6000003814697266,null,null,8.6000003814697266]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,8.5,null,8.5,null,8.6000003814697266,null,8.6999998092651367,null,null,null,null,8.8000001907348633,null,7.5999999046325684,null,7.6999998092651367,null,null,null,null,null,7.6999998092651367,7.8000001907348633,null,null,8]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.4,null,0.4,null,0.4,null,0.4,null,null,null,null,0.4,null,0.4,null,0.4,null,null,null,null,null,0.4,0.4,null,null,0.4]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"2",null,"2",null,"2",null,"2",null,null,null,null,"2",null,"2",null,"2",null,null,null,null,null,"2","2",null,null,"2"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,0.2,null,0.2,null,0.3,null,0.4,null,null,null,null,0.5]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0.5,null,0.5,null,0.5,null,0.5,null,null,null,null,0.5,null,0.5,null,0.5,null,null,null,null,null,0.5,0.5,null,null,0.5]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"HUGH","index":109,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"HUGH - Hughenden (66/33kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T095 - Millchester BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Nth Queensland"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/33/6.6kV 8/5.5MVA ONAF/ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 20.97 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -1.9%, 2020 S -1.7% W -1.7%2021 S -1.7% W -1.7%2022 S -1.1% W -1.1%2023 S -1.2% W -1.2"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"3.5 MVA on 07/11/2018 at 19:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,20,null,20,null,20,null,20,null,null,null,null,20,null,22.899999618530273,null,22.899999618530273,null,null,null,null,null,22.899999618530273,22.899999618530273,null,null,22.899999618530273]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,4,null,3.9000000953674316,null,3.7999999523162842,null,3.7999999523162842,null,null,null,null,3.7999999523162842,null,2.5,null,2.4000000953674316,null,null,null,null,null,2.4000000953674316,2.2999999523162842,null,null,2.2999999523162842]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.995,null,0.995,null,0.995,null,0.995,null,null,null,null,0.995,null,0.98699999999999999,null,0.98699999999999999,null,null,null,null,null,0.98699999999999999,0.98699999999999999,null,null,0.98699999999999999]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,11.399999618530273,null,11.399999618530273,null,11.399999618530273,null,11.399999618530273,null,null,null,null,11.399999618530273,null,11.399999618530273,null,11.399999618530273,null,null,null,null,null,11.399999618530273,11.399999618530273,null,null,11.399999618530273]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,3.7000000476837158,null,3.5999999046325684,null,3.5,null,3.5,null,null,null,null,3.5,null,2.2999999523162842,null,2.2999999523162842,null,null,null,null,null,2.2000000476837158,2.2000000476837158,null,null,2.2000000476837158]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.2,null,0.2,null,0.2,null,0.2,null,null,null,null,0.2,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"12",null,"12",null,"12",null,"12",null,null,null,null,"12",null,"12",null,"12",null,null,null,null,null,"12","12",null,null,"12"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"ILBI","index":110,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"ILBI - Ilbilbie (33/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T065 - Alligator Creek BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Mackay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x33/11kV 1MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -2.0%, 2020 S -1.7% W -1.7%2021 S -1.7% W -1.7%2022 S -0.5% W -0.5%2023 S -0.5% W -0.5"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"0.7 MVA on 29/11/2018 at 19:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,1.2000000476837158,null,1.2000000476837158,null,1.2000000476837158,null,1.2000000476837158,null,null,null,null,1.2000000476837158,null,1.3999999761581421,null,1.3999999761581421,null,null,null,null,null,1.3999999761581421,1.3999999761581421,null,null,1.3999999761581421]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,0.69999998807907104,null,0.69999998807907104,null,0.69999998807907104,null,0.69999998807907104,null,null,null,null,0.69999998807907104,null,0.60000002384185791,null,0.60000002384185791,null,null,null,null,null,0.60000002384185791,0.60000002384185791,null,null,0.60000002384185791]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.94599999999999995,null,0.94599999999999995,null,0.94599999999999995,null,0.94599999999999995,null,null,null,null,0.94599999999999995,null,0.96499999999999997,null,0.96499999999999997,null,null,null,null,null,0.96499999999999997,0.96499999999999997,null,null,0.96499999999999997]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,0.69999998807907104,null,0.69999998807907104,null,0.69999998807907104,null,0.69999998807907104,null,null,null,null,0.69999998807907104,null,0.5,null,0.5,null,null,null,null,null,0.5,0.5,null,null,0.5]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"196",null,"196",null,"196",null,"196",null,null,null,null,"196",null,"196",null,"196",null,null,null,null,null,"196","196",null,null,"196"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,0.7,null,0.7,null,0.7,null,0.7,null,null,null,null,0.7,null,0.5,null,0.5,null,null,null,null,null,0.5,0.5,null,null,0.5]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0.89999997615814209,null,0.89999997615814209,null,0.89999997615814209,null,0.89999997615814209,null,null,null,null,0.89999997615814209,null,0.89999997615814209,null,0.89999997615814209,null,null,null,null,null,0.89999997615814209,0.89999997615814209,null,null,0.89999997615814209]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"INGH","index":111,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"INGH - Ingham (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T047 - Ingham BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Nth Queensland"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/11kV 7.5/10MVA ONAN/ONAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -1.9%, 2020 S -2.3% W -2.3%2021 S -1.6% W -1.6%2022 S -1.7% W -1.7%2023 S -1.6% W -1.6"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"11.7 MVA on 14/02/2019 at 16:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,26.700000762939453,null,26.700000762939453,null,26.700000762939453,null,26.700000762939453,null,null,null,null,26.700000762939453,null,28.100000381469727,null,28.100000381469727,null,null,null,null,null,28.100000381469727,28.100000381469727,null,null,28.100000381469727]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,12.300000190734863,null,12,null,11.699999809265137,null,11.5,null,null,null,null,11.5,null,4.5999999046325684,null,4.5,null,null,null,null,null,4.4000000953674316,4.4000000953674316,null,null,4.3000001907348633]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.998,null,0.998,null,0.998,null,0.999,null,null,null,null,0.999,null,0.95899999999999996,null,0.95899999999999996,null,null,null,null,null,0.95899999999999996,0.95899999999999996,null,null,0.95899999999999996]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,14.100000381469727,null,14.100000381469727,null,14.100000381469727,null,14.100000381469727,null,null,null,null,14.100000381469727,null,15,null,15,null,null,null,null,null,15,15,null,null,15]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,10.399999618530273,null,10.100000381469727,null,9.8999996185302734,null,9.6999998092651367,null,null,null,null,9.6999998092651367,null,4.5,null,4.4000000953674316,null,null,null,null,null,4.3000001907348633,4.1999998092651367,null,null,4.1999998092651367]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.5,null,0.5,null,0.5,null,0.5,null,null,null,null,0.5,null,0.2,null,0.2,null,null,null,null,null,0.2,0.2,null,null,0.2]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"5.5",null,"5.5",null,"5.5",null,"5.5",null,null,null,null,"5.5",null,"5.5",null,"5.5",null,null,null,null,null,"5.5","5.5",null,null,"5.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"JAND","index":112,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"JAND - Jandowae (33/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T013 - Chinchilla BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is South West"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x33/11 3.15MVA ON;1x33/11kV 0.75MVA ON(Standby)"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.3%, 2020 S 0.0% W 0.0%, 2021 S -0.0% W -0.0%2022 S 0.3% W 0.3%, 2023 S 0.0% W 0.0%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"1.4 MVA on 13/02/2019 at 18:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,3.2000000476837158,null,3.2000000476837158,null,3.2000000476837158,null,3.2000000476837158,null,null,null,null,3.2000000476837158,null,3.2000000476837158,null,3.2000000476837158,null,null,null,null,null,3.2000000476837158,3.2000000476837158,null,null,3.2000000476837158]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,1.6000000238418579,null,1.6000000238418579,null,1.6000000238418579,null,1.6000000238418579,null,null,null,null,1.6000000238418579,null,1.2999999523162842,null,1.2999999523162842,null,null,null,null,null,1.2999999523162842,1.2999999523162842,null,null,1.2999999523162842]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.98199999999999998,null,0.98199999999999998,null,0.98199999999999998,null,0.98199999999999998,null,null,null,null,0.98199999999999998,null,0.99099999999999999,null,0.99099999999999999,null,null,null,null,null,0.99099999999999999,0.99099999999999999,null,null,0.99099999999999999]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,1.3999999761581421,null,1.3999999761581421,null,1.3999999761581421,null,1.3999999761581421,null,null,null,null,1.3999999761581421,null,1.2000000476837158,null,1.2000000476837158,null,null,null,null,null,1.2000000476837158,1.2000000476837158,null,null,1.2000000476837158]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.1,null,0.1,null,0.1,null,0.1,null,null,null,null,0.1,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"6.5",null,"6.5",null,"6.5",null,"6.5",null,null,null,null,"6.5",null,"6.5",null,"6.5",null,null,null,null,null,"6.5","6.5",null,null,"6.5"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,1.4,null,1.4,null,1.4,null,1.4,null,null,null,null,1.4,null,1.2,null,1.2,null,null,null,null,null,1.2,1.2,null,null,1.2]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0.80000001192092896,null,0.80000001192092896,null,0.80000001192092896,null,0.80000001192092896,null,null,null,null,0.80000001192092896,null,0.80000001192092896,null,0.80000001192092896,null,null,null,null,null,0.80000001192092896,0.80000001192092896,null,null,0.80000001192092896]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,1,null,1,null,1,null,1,null,null,null,null,1,null,1,null,1,null,null,null,null,null,1,1,null,null,1]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"JARV","index":113,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"JARV - Jarvisfield (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T193 - Clare South BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Nth Queensland"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/11kV 5MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.3%, 2020 S -0.0% W -0.0%2021 S -0.1% W -0.1%2022 S -0.2% W -0.2%2023 S -0.3% W -0.3"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"5.8 MVA on 03/12/2018 at 18:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,12.100000381469727,null,12.100000381469727,null,12.100000381469727,null,12.100000381469727,null,null,null,null,12.100000381469727,null,12.399999618530273,null,12.399999618530273,null,null,null,null,null,12.399999618530273,12.399999618530273,null,null,12.399999618530273]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,6.3000001907348633,null,6.3000001907348633,null,6.1999998092651367,null,6.1999998092651367,null,null,null,null,6.1999998092651367,null,3.2999999523162842,null,3.2999999523162842,null,null,null,null,null,3.2999999523162842,3.2000000476837158,null,null,3.2000000476837158]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.83299999999999996,null,0.83299999999999996,null,0.83299999999999996,null,0.83299999999999996,null,null,null,null,0.83299999999999996,null,0.84399999999999997,null,0.84399999999999997,null,null,null,null,null,0.84399999999999997,0.84399999999999997,null,null,0.84399999999999997]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,7,null,7,null,7,null,7,null,null,null,null,7,null,7.0999999046325684,null,7.0999999046325684,null,null,null,null,null,7.0999999046325684,7.0999999046325684,null,null,7.0999999046325684]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,6.1999998092651367,null,6.0999999046325684,null,6.0999999046325684,null,6.0999999046325684,null,null,null,null,6.0999999046325684,null,2.9000000953674316,null,2.9000000953674316,null,null,null,null,null,2.9000000953674316,2.9000000953674316,null,null,2.9000000953674316]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.3,null,0.3,null,0.3,null,0.3,null,null,null,null,0.3,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"10.5",null,"10.5",null,"10.5",null,"10.5",null,null,null,null,"10.5",null,"10.5",null,"10.5",null,null,null,null,null,"10.5","10.5",null,null,"10.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"JUCR","index":114,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"JUCR - Julia Creek (66/33kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T095 - Millchester BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Nth Queensland"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/33kV 7.5/6.3MVA ONAF/ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.8%, 2020 S -0.5% W -0.5%2021 S -0.7% W -0.7%2022 S -0.3% W -0.3%2023 S -0.6% W -0.6"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"2.7 MVA on 19/01/2019 at 19:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,7.4000000953674316,null,7.4000000953674316,null,7.4000000953674316,null,7.4000000953674316,null,null,null,null,7.4000000953674316,null,8.8000001907348633,null,8.8000001907348633,null,null,null,null,null,8.8000001907348633,8.8000001907348633,null,null,8.8000001907348633]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,3.2000000476837158,null,3.0999999046325684,null,3.0999999046325684,null,3.0999999046325684,null,null,null,null,3.0999999046325684,null,1.5,null,1.5,null,null,null,null,null,1.5,1.5,null,null,1.5]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.98099999999999998,null,0.98099999999999998,null,0.98099999999999998,null,0.98099999999999998,null,null,null,null,0.98099999999999998,null,0.98399999999999999,null,0.98399999999999999,null,null,null,null,null,0.98399999999999999,0.98399999999999999,null,null,0.98399999999999999]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,3,null,2.9000000953674316,null,2.9000000953674316,null,2.9000000953674316,null,null,null,null,2.9000000953674316,null,1.3999999761581421,null,1.3999999761581421,null,null,null,null,null,1.3999999761581421,1.3999999761581421,null,null,1.3999999761581421]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.2,null,0.1,null,0.1,null,0.1,null,null,null,null,0.1,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"8",null,"8",null,"8",null,"8",null,null,null,null,"8",null,"8",null,"8",null,null,null,null,null,"8","8",null,null,"8"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,3,null,2.9,null,2.9,null,2.9,null,null,null,null,2.9,null,1.4,null,1.4,null,null,null,null,null,1.4,1.4,null,null,1.4]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,2.7000000476837158,null,2.7000000476837158,null,2.7000000476837158,null,2.7000000476837158,null,null,null,null,2.7000000476837158,null,2.7000000476837158,null,2.7000000476837158,null,null,null,null,null,2.7000000476837158,2.7000000476837158,null,null,2.7000000476837158]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0.40000000596046448,null,0.40000000596046448,null,0.40000000596046448,null,0.40000000596046448,null,null,null,null,0.40000000596046448,null,0.40000000596046448,null,0.40000000596046448,null,null,null,null,null,0.40000000596046448,0.40000000596046448,null,null,0.40000000596046448]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"JUPO","index":115,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"JUPO - Jubilee Pocket (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T039 - Proserpine BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Mackay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/11kV 19/26/32MVA ONAN/ODAN/ODAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 1.1%, 2020 S 1.4% W 1.4%, 2021 S 1.4% W 1.4%, 2022 S 1.2% W 1.2%, 2023 S 1.0% W 1.0%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"4.2 MVA on 13/02/2019 at 17:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,39.599998474121094,null,39.599998474121094,null,39.599998474121094,null,39.599998474121094,null,null,null,null,39.599998474121094,null,43.400001525878906,null,43.400001525878906,null,null,null,null,null,43.400001525878906,43.400001525878906,null,null,43.400001525878906]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,4.9000000953674316,null,5,null,5,null,5,null,null,null,null,5.0999999046325684,null,3.7000000476837158,null,3.7000000476837158,null,null,null,null,null,3.7999999523162842,3.7999999523162842,null,null,3.7999999523162842]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.98199999999999998,null,0.98199999999999998,null,0.98199999999999998,null,0.98199999999999998,null,null,null,null,0.98199999999999998,null,0.98099999999999998,null,0.98099999999999998,null,null,null,null,null,0.98099999999999998,0.98099999999999998,null,null,0.98099999999999998]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,4.5999999046325684,null,4.5999999046325684,null,4.6999998092651367,null,4.6999998092651367,null,null,null,null,4.8000001907348633,null,3.4000000953674316,null,3.5,null,null,null,null,null,3.5,3.5,null,null,3.5999999046325684]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.2,null,0.2,null,0.2,null,0.2,null,null,null,null,0.2,null,0.2,null,0.2,null,null,null,null,null,0.2,0.2,null,null,0.2]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"1396",null,"1396",null,"1396",null,"1396",null,null,null,null,"1396",null,"1396",null,"1396",null,null,null,null,null,"1396","1396",null,null,"1396"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,4.5999999999999996,null,4.5999999999999996,null,4.7,null,4.7,null,null,null,null,4.8,null,3.4,null,3.5,null,null,null,null,null,3.5,3.5,null,null,3.6]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,4.3000001907348633,null,4.3000001907348633,null,4.3000001907348633,null,4.3000001907348633,null,null,null,null,4.3000001907348633,null,4.3000001907348633,null,4.3000001907348633,null,null,null,null,null,4.3000001907348633,4.3000001907348633,null,null,4.3000001907348633]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,1.5,null,1.5,null,1.5,null,1.5,null,null,null,null,1.5,null,1.5,null,1.5,null,null,null,null,null,1.5,1.5,null,null,1.5]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"KAIM","index":116,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"KAIM - Kaimkillenbun (33/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T002 - Dalby East BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is South West"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x33/11kV 1MVA ONAN;1x33/11kV 1MVA ONAN(Standby)"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.3%, 2020 S 0.0% W 0.0%, 2021 S -0.0% W -0.0%2022 S 0.3% W 0.3%, 2023 S 0.1% W 0.1%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"0.9 MVA on 20/02/2019 at 18:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,1,null,1,null,1,null,1,null,null,null,null,1,null,1,null,1,null,null,null,null,null,1,1,null,null,1]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,1,null,1,null,1,null,1,null,null,null,null,1,null,0.89999997615814209,null,0.89999997615814209,null,null,null,null,null,0.89999997615814209,0.89999997615814209,null,null,0.89999997615814209]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.96299999999999997,null,0.96299999999999997,null,0.96299999999999997,null,0.96299999999999997,null,null,null,null,0.96299999999999997,null,0.98599999999999999,null,0.98599999999999999,null,null,null,null,null,0.98599999999999999,0.98599999999999999,null,null,0.98599999999999999]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,0.89999997615814209,null,0.89999997615814209,null,0.89999997615814209,null,0.89999997615814209,null,null,null,null,0.89999997615814209,null,0.89999997615814209,null,0.89999997615814209,null,null,null,null,null,0.89999997615814209,0.89999997615814209,null,null,0.89999997615814209]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"21",null,"21",null,"21",null,"21",null,null,null,null,"21",null,"21",null,"21",null,null,null,null,null,"21","21",null,null,"21"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,0.9,null,0.9,null,0.9,null,0.9,null,null,null,null,0.9,null,0.9,null,0.9,null,null,null,null,null,0.9,0.9,null,null,0.9]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,1.1000000238418579,null,1.1000000238418579,null,1.1000000238418579,null,1.1000000238418579,null,null,null,null,1.1000000238418579,null,1.1000000238418579,null,1.1000000238418579,null,null,null,null,null,1.1000000238418579,1.1000000238418579,null,null,1.1000000238418579]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"KALA","index":117,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"KALA - Kalamia (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T193 - Clare South BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Nth Queensland"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/11kV 7.5/10MVA ONAN/ONAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 11.3 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.2%, 2020 S -0.0% W -0.0%2021 S -0.2% W -0.2%2022 S -0.2% W -0.2%2023 S -0.3% W -0.3"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"4.9 MVA on 28/11/2018 at 15:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,13,null,13,null,13,null,13,null,null,null,null,13,null,14.199999809265137,null,14.199999809265137,null,null,null,null,null,14.199999809265137,14.199999809265137,null,null,14.199999809265137]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0.60000002384185791,null,0.60000002384185791,null,0.60000002384185791,null,0.60000002384185791,null,null,null,null,0.60000002384185791,null,0.60000002384185791,null,0.60000002384185791,null,null,null,null,null,0.60000002384185791,0.60000002384185791,null,null,0.60000002384185791]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,5.0999999046325684,null,5.0999999046325684,null,5,null,5,null,null,null,null,5,null,4.6999998092651367,null,4.6999998092651367,null,null,null,null,null,4.6999998092651367,4.6999998092651367,null,null,4.6999998092651367]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.91900000000000004,null,0.91900000000000004,null,0.91900000000000004,null,0.91900000000000004,null,null,null,null,0.91900000000000004,null,0.98599999999999999,null,0.98599999999999999,null,null,null,null,null,0.98599999999999999,0.98599999999999999,null,null,0.98599999999999999]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,5,null,5,null,4.9000000953674316,null,4.9000000953674316,null,null,null,null,4.9000000953674316,null,4.5,null,4.5,null,null,null,null,null,4.5,4.5,null,null,4.5]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.3,null,0.3,null,0.2,null,0.2,null,null,null,null,0.2,null,0.2,null,0.2,null,null,null,null,null,0.2,0.2,null,null,0.2]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"3.5",null,"3.5",null,"3.5",null,"3.5",null,null,null,null,"3.5",null,"3.5",null,"3.5",null,null,null,null,null,"3.5","3.5",null,null,"3.5"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,5,null,5,null,4.9000000000000004,null,4.9000000000000004,null,null,null,null,4.9000000000000004,null,4.5,null,4.5,null,null,null,null,null,4.5,4.5,null,null,4.5]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,1.2999999523162842,null,1.2999999523162842,null,1.2999999523162842,null,1.2999999523162842,null,null,null,null,1.2999999523162842,null,1.2999999523162842,null,1.2999999523162842,null,null,null,null,null,1.2999999523162842,1.2999999523162842,null,null,1.2999999523162842]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,1.7999999523162842,null,1.7999999523162842,null,1.7999999523162842,null,1.7999999523162842,null,null,null,null,1.7999999523162842,null,1.7999999523162842,null,1.7999999523162842,null,null,null,null,null,1.7999999523162842,1.7999999523162842,null,null,1.7999999523162842]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,3,null,3,null,3,null,3,null,null,null,null,3,null,3,null,3,null,null,null,null,null,3,3,null,null,3]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"KECE","index":118,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"KECE - Kelsey Creek East (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T039 - Proserpine BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Mackay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/11kV 12.5/16MVA ONAN/ONAF;1x66/11kV 16/20MVA ONAN/ONAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.3%, 2020 S 0.1% W 0.1%, 2021 S 0.1% W 0.1%, 2022 S 0.5% W 0.5%, 2023 S 0.4% W 0.4%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"16 MVA on 27/11/2018 at 19:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,36.799999237060547,null,36.799999237060547,null,36.799999237060547,null,36.799999237060547,null,null,null,null,36.799999237060547,null,38.400001525878906,null,38.400001525878906,null,null,null,null,null,38.400001525878906,38.400001525878906,null,null,38.400001525878906]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,19.600000381469727,null,19.600000381469727,null,19.5,null,19.600000381469727,null,null,null,null,19.799999237060547,null,9.3999996185302734,null,9.3999996185302734,null,null,null,null,null,9.3000001907348633,9.3999996185302734,null,null,9.3999996185302734]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.94399999999999995,null,0.94399999999999995,null,0.94399999999999995,null,0.94399999999999995,null,null,null,null,0.94399999999999995,null,0.95399999999999996,null,0.95399999999999996,null,null,null,null,null,0.95399999999999996,0.95399999999999996,null,null,0.95399999999999996]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,18.399999618530273,null,18.399999618530273,null,18.399999618530273,null,18.399999618530273,null,null,null,null,18.399999618530273,null,20,null,20,null,null,null,null,null,20,20,null,null,20]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,15.100000381469727,null,15.100000381469727,null,15,null,15.100000381469727,null,null,null,null,15.199999809265137,null,8.8000001907348633,null,8.8000001907348633,null,null,null,null,null,8.8000001907348633,8.8000001907348633,null,null,8.8999996185302734]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.8,null,0.8,null,0.8,null,0.8,null,null,null,null,0.8,null,0.4,null,0.4,null,null,null,null,null,0.4,0.4,null,null,0.4]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"6.5",null,"6.5",null,"6.5",null,"6.5",null,null,null,null,"6.5",null,"6.5",null,"6.5",null,null,null,null,null,"6.5","6.5",null,null,"6.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,1,null,1,null,1,null,1,null,null,null,null,1,null,1,null,1,null,null,null,null,null,1,1,null,null,1]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,2,null,2,null,2,null,2,null,null,null,null,2,null,2,null,2,null,null,null,null,null,2,2,null,null,2]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"KESP","index":119,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"KESP - Kearneys Spring (110/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"QMRG - Middle Ridge (Ergon) TCP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is South West"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x110/11kV 30/40MVA ONAN/ONAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.4%, 2020 S 0.4% W 0.4%, 2021 S 0.4% W 0.4%, 2022 S 0.2% W 0.2%, 2023 S -0.3% W -0.3"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"22.3 MVA on 18/06/2018 at 17:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,79.099998474121094,null,79.099998474121094,null,79.099998474121094,null,79.099998474121094,null,null,null,null,79.099998474121094,null,89.800003051757813,null,89.800003051757813,null,null,null,null,null,89.800003051757813,89.800003051757813,null,null,89.800003051757813]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,23,null,23,null,22.799999237060547,null,22.799999237060547,null,null,null,null,22.899999618530273,null,25.700000762939453,null,25.799999237060547,null,null,null,null,null,25.799999237060547,25.799999237060547,null,null,25.799999237060547]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.98799999999999999,null,0.98799999999999999,null,0.98799999999999999,null,0.98799999999999999,null,null,null,null,0.98799999999999999,null,0.996,null,0.996,null,null,null,null,null,0.996,0.996,null,null,0.996]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,44.799999237060547,null,44.799999237060547,null,44.799999237060547,null,44.799999237060547,null,null,null,null,44.799999237060547,null,49.299999237060547,null,49.299999237060547,null,null,null,null,null,49.299999237060547,49.299999237060547,null,null,49.299999237060547]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,19.700000762939453,null,19.700000762939453,null,19.600000381469727,null,19.5,null,null,null,null,19.600000381469727,null,23.200000762939453,null,23.299999237060547,null,null,null,null,null,23.299999237060547,23.299999237060547,null,null,23.299999237060547]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,1,null,1,null,1,null,1,null,null,null,null,1,null,1.2,null,1.2,null,null,null,null,null,1.2,1.2,null,null,1.2]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"7",null,"7",null,"7",null,"7",null,null,null,null,"7",null,"7",null,"7",null,null,null,null,null,"7","7",null,null,"7"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"KIDS","index":120,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"KIDS - Kidston (132/6.6kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"QROS - Ross (Kidston and Milchester) TCP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Far North"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x132/6.6kV 20MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.0%, 2020 S 0.1% W 0.1%, 2021 S -0.3% W -0.3%2022 S -0.2% W -0.2%2023 S -0.4% W -0.4"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"0.3 MVA on 08/02/2019 at 15:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,42.5,null,42.5,null,42.5,null,42.5,null,null,null,null,42.5,null,44.900001525878906,null,44.900001525878906,null,null,null,null,null,44.900001525878906,44.900001525878906,null,null,44.900001525878906]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,0.30000001192092896,null,0.30000001192092896,null,0.30000001192092896,null,0.30000001192092896,null,null,null,null,0.30000001192092896,null,0.10000000149011612,null,0.10000000149011612,null,null,null,null,null,0.10000000149011612,0.10000000149011612,null,null,0.10000000149011612]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.86299999999999999,null,0.86299999999999999,null,0.86299999999999999,null,0.86299999999999999,null,null,null,null,0.86299999999999999,null,0.82599999999999996,null,0.82599999999999996,null,null,null,null,null,0.82599999999999996,0.82599999999999996,null,null,0.82599999999999996]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,25.399999618530273,null,25.399999618530273,null,25.399999618530273,null,25.399999618530273,null,null,null,null,25.399999618530273,null,25.799999237060547,null,25.799999237060547,null,null,null,null,null,25.799999237060547,25.799999237060547,null,null,25.799999237060547]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,0.30000001192092896,null,0.30000001192092896,null,0.30000001192092896,null,0.30000001192092896,null,null,null,null,0.30000001192092896,null,0.10000000149011612,null,0.10000000149011612,null,null,null,null,null,0.10000000149011612,0.10000000149011612,null,null,0.10000000149011612]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"27.5",null,"27.5",null,"27.5",null,"27.5",null,null,null,null,"27.5",null,"27.5",null,"27.5",null,null,null,null,null,"27.5","27.5",null,null,"27.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"KILL","index":121,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"KILL - Killarney (33/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T058 - Warwick BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is South West"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x33/11kV 3MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -4.7%, 2020 S -3.7% W -3.7%2021 S 0.1% W 0.1%, 2022 S 0.1% W 0.1%, 2023 S -0.1% W -0.1"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"2.1 MVA on 13/08/2018 at 07:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,7.5,null,7.5,null,7.5,null,7.5,null,null,null,null,7.5,null,8.8999996185302734,null,8.8999996185302734,null,null,null,null,null,8.8999996185302734,8.8999996185302734,null,null,8.8999996185302734]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,1.8999999761581421,null,1.7999999523162842,null,1.7999999523162842,null,1.7999999523162842,null,null,null,null,1.7999999523162842,null,2.0999999046325684,null,2,null,null,null,null,null,2,2,null,null,2]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.94499999999999995,null,0.94499999999999995,null,0.94499999999999995,null,0.94499999999999995,null,null,null,null,0.94499999999999995,null,0.96099999999999997,null,0.96099999999999997,null,null,null,null,null,0.96099999999999997,0.96099999999999997,null,null,0.96099999999999997]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,4.3000001907348633,null,4.3000001907348633,null,4.3000001907348633,null,4.3000001907348633,null,null,null,null,4.3000001907348633,null,4.5,null,4.5,null,null,null,null,null,4.5,4.5,null,null,4.5]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,1.7000000476837158,null,1.7000000476837158,null,1.7000000476837158,null,1.7000000476837158,null,null,null,null,1.7000000476837158,null,2,null,1.8999999761581421,null,null,null,null,null,1.8999999761581421,1.8999999761581421,null,null,1.8999999761581421]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.1,null,0.1,null,0.1,null,0.1,null,null,null,null,0.1,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"4.5",null,"4.5",null,"4.5",null,"4.5",null,null,null,null,"4.5",null,"4.5",null,"4.5",null,null,null,null,null,"4.5","4.5",null,null,"4.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"KING","index":122,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"KING - Kingaroy (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"H018 - Tarong BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Wide Bay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/11kV 20/25/27MVA ONAN/ONAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -1.5%, 2020 S -1.7% W -1.7%2021 S -1.1% W -1.1%2022 S -0.4% W -0.4%2023 S -0.9% W -0.9"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"22 MVA on 13/03/2019 at 16:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,57.400001525878906,null,57.400001525878906,null,57.400001525878906,null,57.400001525878906,null,null,null,null,57.400001525878906,null,64.699996948242188,null,64.699996948242188,null,null,null,null,null,64.699996948242188,64.699996948242188,null,null,64.699996948242188]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,28.799999237060547,null,29.100000381469727,null,28.700000762939453,null,28.5,null,null,null,null,28.5,null,23.700000762939453,null,23.899999618530273,null,null,null,null,null,24.200000762939453,24.100000381469727,null,null,24]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.94699999999999995,null,0.94699999999999995,null,0.94699999999999995,null,0.94699999999999995,null,null,null,null,0.94699999999999995,null,0.96899999999999997,null,0.96899999999999997,null,null,null,null,null,0.96899999999999997,0.96899999999999997,null,null,0.96899999999999997]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,32.5,null,32.5,null,32.5,null,32.5,null,null,null,null,32.5,null,36.200000762939453,null,36.200000762939453,null,null,null,null,null,36.200000762939453,36.200000762939453,null,null,36.200000762939453]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,26.600000381469727,null,26.899999618530273,null,26.600000381469727,null,26.399999618530273,null,null,null,null,26.399999618530273,null,22,null,22.200000762939453,null,null,null,null,null,22.600000381469727,22.5,null,null,22.399999618530273]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,1.3,null,1.3,null,1.3,null,1.3,null,null,null,null,1.3,null,1.1000000000000001,null,1.1000000000000001,null,null,null,null,null,1.1000000000000001,1.1000000000000001,null,null,1.1000000000000001]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"10",null,"10",null,"10",null,"10",null,null,null,null,"10",null,"10",null,"10",null,null,null,null,null,"10","10",null,null,"10"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"KIRK","index":123,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"KIRK - Kirknie (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T193 - Clare South BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Nth Queensland"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/11kV 10MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.5%, 2020 S -0.0% W -0.0%2021 S -0.4% W -0.4%2022 S -0.5% W -0.5%2023 S -0.7% W -0.7"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"8 MVA on 23/01/2019 at 18:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,9.6999998092651367,null,9.6999998092651367,null,9.6999998092651367,null,9.6999998092651367,null,null,null,null,9.6999998092651367,null,10.899999618530273,null,10.899999618530273,null,null,null,null,null,10.899999618530273,10.899999618530273,null,null,10.899999618530273]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,8.5,null,8.3999996185302734,null,8.3000001907348633,null,8.3000001907348633,null,null,null,null,8.1999998092651367,null,5.5999999046325684,null,5.5999999046325684,null,null,null,null,null,5.5999999046325684,5.5,null,null,5.5]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.85599999999999998,null,0.85599999999999998,null,0.85599999999999998,null,0.85599999999999998,null,null,null,null,0.85599999999999998,null,0.86599999999999999,null,0.86599999999999999,null,null,null,null,null,0.86599999999999999,0.86599999999999999,null,null,0.86599999999999999]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,8.3000001907348633,null,8.1999998092651367,null,8.1000003814697266,null,8.1000003814697266,null,null,null,null,8,null,5.5999999046325684,null,5.5999999046325684,null,null,null,null,null,5.5999999046325684,5.5,null,null,5.5]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.4,null,0.4,null,0.4,null,0.4,null,null,null,null,0.4,null,0.3,null,0.3,null,null,null,null,null,0.3,0.3,null,null,0.3]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"80.5",null,"80.5",null,"80.5",null,"80.5",null,null,null,null,"80.5",null,"80.5",null,"80.5",null,null,null,null,null,"80.5","80.5",null,null,"80.5"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,8.3000000000000007,null,8.1999999999999993,null,8.1,null,8.1,null,null,null,null,8,null,5.6,null,5.6,null,null,null,null,null,5.6,5.5,null,null,5.5]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,2,null,2,null,2,null,2,null,null,null,null,2,null,2,null,2,null,null,null,null,null,2,2,null,null,2]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,1.2999999523162842,null,1.2999999523162842,null,1.2999999523162842,null,1.2999999523162842,null,null,null,null,1.2999999523162842,null,1.2999999523162842,null,1.2999999523162842,null,null,null,null,null,1.2999999523162842,1.2999999523162842,null,null,1.2999999523162842]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,7,null,7,null,7,null,7,null,null,null,null,7,null,7,null,7,null,null,null,null,null,7,7,null,null,7]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"KITO","index":124,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"KITO - Kilkivan Town (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T012 - Kilkivan BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Wide Bay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x62/11kV 1MVA ON"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -1.0%, 2020 S -0.0% W -0.0%2021 S -0.0% W -0.0%2022 S 0.3% W 0.3%, 2023 S -0.2% W -0.2"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"1 MVA on 27/01/2019 at 19:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,2,null,2,null,2,null,2,null,null,null,null,2,null,2,null,2,null,null,null,null,null,2,2,null,null,2]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,1.2000000476837158,null,1.2000000476837158,null,1.2000000476837158,null,1.2000000476837158,null,null,null,null,1.2000000476837158,null,1,null,1,null,null,null,null,null,1,1,null,null,1]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.95,null,0.95,null,0.94799999999999995,null,0.94799999999999995,null,null,null,null,0.94799999999999995,null,0.95,null,0.95,null,null,null,null,null,0.95,0.95,null,null,0.95]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,1,null,1,null,1,null,1,null,null,null,null,1,null,1,null,1,null,null,null,null,null,1,1,null,null,1]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,1.1000000238418579,null,1.1000000238418579,null,1.1000000238418579,null,1.1000000238418579,null,null,null,null,1.1000000238418579,null,0.89999997615814209,null,0.89999997615814209,null,null,null,null,null,0.89999997615814209,0.89999997615814209,null,null,0.89999997615814209]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.1,null,0.1,null,0.1,null,0.1,null,null,null,null,0.1,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"3",null,"3",null,"3",null,"3",null,null,null,null,"3",null,"3",null,"3",null,null,null,null,null,"3","3",null,null,"3"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,0.1,null,0.1,null,0.1,null,0.1,null,null,null,null,0.1]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0.60000002384185791,null,0.60000002384185791,null,0.60000002384185791,null,0.60000002384185791,null,null,null,null,0.60000002384185791,null,0.60000002384185791,null,0.60000002384185791,null,null,null,null,null,0.60000002384185791,0.60000002384185791,null,null,0.60000002384185791]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"KOCR","index":125,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"KOCR - Kogan Creek (33/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T013 - Chinchilla BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is South West"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1xKOCR TFR1-66/33KV TRANSF 1"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 4.9%, 2020 S 7.2% W 7.2%, 2021 S 6.5% W 6.5%, 2022 S 7.7% W 7.7%, 2023 S 5.8% W 5.8%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"0 MVA on 03/12/2018 at 00:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,5,null,5,null,5,null,5,null,null,null,null,5,null,5,null,5,null,null,null,null,null,5,5,null,null,5]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.95299999999999996,null,0.95299999999999996,null,0.95299999999999996,null,0.95299999999999996,null,null,null,null,0.95299999999999996,null,0.90900000000000003,null,0.90900000000000003,null,null,null,null,null,0.90900000000000003,0.90900000000000003,null,null,0.90900000000000003]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"74.5",null,"74.5",null,"74.5",null,"74.5",null,null,null,null,"74.5",null,"74.5",null,"74.5",null,null,null,null,null,"74.5","74.5",null,null,"74.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0.30000001192092896,null,0.30000001192092896,null,0.30000001192092896,null,0.30000001192092896,null,null,null,null,0.30000001192092896,null,0.30000001192092896,null,0.30000001192092896,null,null,null,null,null,0.30000001192092896,0.30000001192092896,null,null,0.30000001192092896]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0.5,null,0.5,null,0.5,null,0.5,null,null,null,null,0.5,null,0.5,null,0.5,null,null,null,null,null,0.5,0.5,null,null,0.5]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"KOUM","index":126,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"KOUM - Koumala (33/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T065 - Alligator Creek BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Mackay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x33/11kV 5MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.2%, 2020 S 0.3% W 0.3%, 2021 S 0.4% W 0.4%, 2022 S 0.5% W 0.5%, 2023 S 0.4% W 0.4%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"1.9 MVA on 18/11/2018 at 20:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,7,null,7,null,7,null,7,null,null,null,null,7,null,7.5,null,7.5,null,null,null,null,null,7.5,7.5,null,null,7.5]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,2,null,2,null,2,null,2,null,null,null,null,2,null,1.7999999523162842,null,1.7999999523162842,null,null,null,null,null,1.7999999523162842,1.7999999523162842,null,null,1.8999999761581421]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.88400000000000001,null,0.88400000000000001,null,0.88400000000000001,null,0.88400000000000001,null,null,null,null,0.88400000000000001,null,0.89,null,0.89,null,null,null,null,null,0.89,0.89,null,null,0.89]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,1.8999999761581421,null,1.8999999761581421,null,1.8999999761581421,null,1.8999999761581421,null,null,null,null,2,null,1.5,null,1.5,null,null,null,null,null,1.5,1.5,null,null,1.5]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.1,null,0.1,null,0.1,null,0.1,null,null,null,null,0.1,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"16.5",null,"16.5",null,"16.5",null,"16.5",null,null,null,null,"16.5",null,"16.5",null,"16.5",null,null,null,null,null,"16.5","16.5",null,null,"16.5"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,1.9,null,1.9,null,1.9,null,1.9,null,null,null,null,2,null,1.5,null,1.5,null,null,null,null,null,1.5,1.5,null,null,1.5]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,1.8999999761581421,null,1.8999999761581421,null,1.8999999761581421,null,1.8999999761581421,null,null,null,null,1.8999999761581421,null,1.8999999761581421,null,1.8999999761581421,null,null,null,null,null,1.8999999761581421,1.8999999761581421,null,null,1.8999999761581421]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0.10000000149011612,null,0.10000000149011612,null,0.10000000149011612,null,0.10000000149011612,null,null,null,null,0.10000000149011612,null,0.10000000149011612,null,0.10000000149011612,null,null,null,null,null,0.10000000149011612,0.10000000149011612,null,null,0.10000000149011612]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"LACR","index":127,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"LACR - Lakes Creek (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"RMES - Rockhampton Mesh"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Capricornia"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/11kV 16/20MVA ONAN/ONAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.7%, 2020 S -0.6% W -0.6%2021 S -0.6% W -0.6%2022 S -0.6% W -0.6%2023 S -0.7% W -0.7"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"14.6 MVA on 03/12/2018 at 16:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,45.900001525878906,null,45.900001525878906,null,45.900001525878906,null,45.900001525878906,null,null,null,null,45.900001525878906,null,50.900001525878906,null,50.900001525878906,null,null,null,null,null,50.900001525878906,50.900001525878906,null,null,50.900001525878906]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,15.399999618530273,null,15.199999809265137,null,15,null,14.899999618530273,null,null,null,null,15,null,12.699999809265137,null,12.600000381469727,null,null,null,null,null,12.5,12.399999618530273,null,null,12.300000190734863]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.998,null,0.999,null,0.999,null,0.999,null,null,null,null,0.999,null,0.94599999999999995,null,0.94599999999999995,null,null,null,null,null,0.94599999999999995,0.94599999999999995,null,null,0.94599999999999995]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,27,null,27,null,27,null,27,null,null,null,null,27,null,29.299999237060547,null,29.299999237060547,null,null,null,null,null,29.299999237060547,29.299999237060547,null,null,29.299999237060547]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,15,null,14.899999618530273,null,14.600000381469727,null,14.5,null,null,null,null,14.600000381469727,null,12.199999809265137,null,12.100000381469727,null,null,null,null,null,12,11.899999618530273,null,null,11.899999618530273]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.8,null,0.7,null,0.7,null,0.7,null,null,null,null,0.7,null,0.6,null,0.6,null,null,null,null,null,0.6,0.6,null,null,0.6]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"12.5",null,"12.5",null,"12.5",null,"12.5",null,null,null,null,"12.5",null,"12.5",null,"12.5",null,null,null,null,null,"12.5","12.5",null,null,"12.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"LAKE","index":128,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"LAKE - Lakeland (66/22kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T159 - Lakeland BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Far North"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x20MVA"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.1%, 2020 S 0.3% W 0.3%, 2021 S 0.2% W 0.2%, 2022 S 0.0% W 0.0%, 2023 S -0.2% W -0.2"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"4 MVA on 05/11/2018 at 16:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,16,null,16,null,16,null,16,null,null,null,null,16,null,16,null,16,null,null,null,null,null,16,16,null,null,16]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,2.2999999523162842,null,2.2999999523162842,null,2.2999999523162842,null,2.2999999523162842,null,null,null,null,2.2999999523162842,null,1.7000000476837158,null,1.6000000238418579,null,null,null,null,null,1.7000000476837158,1.7000000476837158,null,null,1.6000000238418579]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.8,null,0.8,null,0.8,null,0.8,null,null,null,null,0.8,null,0.97,null,0.96599999999999997,null,null,null,null,null,0.97,0.97,null,null,0.96599999999999997]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,8,null,8,null,8,null,8,null,null,null,null,8,null,8,null,8,null,null,null,null,null,8,8,null,null,8]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,2.2000000476837158,null,2.2000000476837158,null,2.2000000476837158,null,2.2000000476837158,null,null,null,null,2.2000000476837158,null,1.5,null,1.5,null,null,null,null,null,1.5,1.5,null,null,1.5]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.1,null,0.1,null,0.1,null,0.1,null,null,null,null,0.1,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"15",null,"15",null,"15",null,"15",null,null,null,null,"15",null,"15",null,"15",null,null,null,null,null,"15","15",null,null,"15"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"LANN","index":129,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"LANN - Lannercost (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T047 - Ingham BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Nth Queensland"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/11kV 6.3MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.5%, 2020 S -0.3% W -0.3%2021 S -0.3% W -0.3%2022 S -0.6% W -0.6%2023 S -0.8% W -0.8"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"2.2 MVA on 26/11/2018 at 18:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,8.1999998092651367,null,8.1999998092651367,null,8.1999998092651367,null,8.1999998092651367,null,null,null,null,8.1999998092651367,null,8.6999998092651367,null,8.6999998092651367,null,null,null,null,null,8.6999998092651367,8.6999998092651367,null,null,8.6999998092651367]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,2.2999999523162842,null,2.2999999523162842,null,2.2999999523162842,null,2.2999999523162842,null,null,null,null,2.2999999523162842,null,1.5,null,1.3999999761581421,null,null,null,null,null,1.3999999761581421,1.3999999761581421,null,null,1.3999999761581421]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.98099999999999998,null,0.98099999999999998,null,0.98099999999999998,null,0.98099999999999998,null,null,null,null,0.98099999999999998,null,0.98199999999999998,null,0.98199999999999998,null,null,null,null,null,0.98199999999999998,0.98199999999999998,null,null,0.98199999999999998]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,2.0999999046325684,null,2.0999999046325684,null,2.0999999046325684,null,2.0999999046325684,null,null,null,null,2.0999999046325684,null,1.2999999523162842,null,1.2999999523162842,null,null,null,null,null,1.2999999523162842,1.2999999523162842,null,null,1.2999999523162842]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.1,null,0.1,null,0.1,null,0.1,null,null,null,null,0.1,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"11.5",null,"11.5",null,"11.5",null,"11.5",null,null,null,null,"11.5",null,"11.5",null,"11.5",null,null,null,null,null,"11.5","11.5",null,null,"11.5"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,2.1,null,2.1,null,2.1,null,2.1,null,null,null,null,2.1,null,1.3,null,1.3,null,null,null,null,null,1.3,1.3,null,null,1.3]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,2,null,2,null,2,null,2,null,null,null,null,2,null,2,null,2,null,null,null,null,null,2,2,null,null,2]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0.40000000596046448,null,0.40000000596046448,null,0.40000000596046448,null,0.40000000596046448,null,null,null,null,0.40000000596046448,null,0.40000000596046448,null,0.40000000596046448,null,null,null,null,null,0.40000000596046448,0.40000000596046448,null,null,0.40000000596046448]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"LAQU","index":130,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"LAQU - Laguna Quays (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T039 - Proserpine BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Mackay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/11kV 7.5MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.2%, 2020 S 0.4% W 0.4%, 2021 S 0.4% W 0.4%, 2022 S 0.5% W 0.5%, 2023 S 0.4% W 0.4%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"2 MVA on 27/11/2018 at 19:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,17.600000381469727,null,17.600000381469727,null,17.600000381469727,null,17.600000381469727,null,null,null,null,17.600000381469727,null,19,null,19,null,null,null,null,null,19,19,null,null,19]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,2.2000000476837158,null,2.2000000476837158,null,2.0999999046325684,null,2.2000000476837158,null,null,null,null,2.2000000476837158,null,1.7999999523162842,null,1.7999999523162842,null,null,null,null,null,1.7999999523162842,1.7999999523162842,null,null,1.7999999523162842]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.98099999999999998,null,0.98099999999999998,null,0.98099999999999998,null,0.98099999999999998,null,null,null,null,0.98099999999999998,null,0.98399999999999999,null,0.98399999999999999,null,null,null,null,null,0.98399999999999999,0.98399999999999999,null,null,0.98399999999999999]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,9.6999998092651367,null,9.6999998092651367,null,9.6999998092651367,null,9.6999998092651367,null,null,null,null,9.6999998092651367,null,10.300000190734863,null,10.300000190734863,null,null,null,null,null,10.300000190734863,10.300000190734863,null,null,10.300000190734863]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,2.0999999046325684,null,2.0999999046325684,null,2.0999999046325684,null,2.0999999046325684,null,null,null,null,2.0999999046325684,null,1.6000000238418579,null,1.6000000238418579,null,null,null,null,null,1.6000000238418579,1.6000000238418579,null,null,1.6000000238418579]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.1,null,0.1,null,0.1,null,0.1,null,null,null,null,0.1,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"12",null,"12",null,"12",null,"12",null,null,null,null,"12",null,"12",null,"12",null,null,null,null,null,"12","12",null,null,"12"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"LARO","index":131,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"LARO - Landing Road (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T130 - Boat Creek BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Capricornia"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/11kV 10 MVA"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.0%, 2020 S 0.0% W 0.0%, 2021 S 0.0% W 0.0%, 2022 S 0.0% W 0.0%, 2023 S 0.0% W 0.0%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"3.2 MVA on 28/11/2018 at 13:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,10,null,10,null,10,null,10,null,null,null,null,10,null,10,null,10,null,null,null,null,null,10,10,null,null,10]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,3.2,null,3.2,null,3.2,null,3.2,null,null,null,null,3.2,null,3.2,null,3.2,null,null,null,null,null,3.2,3.2,null,null,3.2]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.78900000000000003,null,0.78900000000000003,null,0.78900000000000003,null,0.78900000000000003,null,null,null,null,0.78900000000000003,null,0.81899999999999995,null,0.81899999999999995,null,null,null,null,null,0.81899999999999995,0.81899999999999995,null,null,0.81899999999999995]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,3.2,null,3.2,null,3.2,null,3.2,null,null,null,null,3.2,null,3.2,null,3.2,null,null,null,null,null,3.2,3.2,null,null,3.2]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.1,null,0.1,null,0.1,null,0.1,null,null,null,null,0.1,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"12",null,"12",null,"12",null,"12",null,null,null,null,"12",null,"12",null,"12",null,null,null,null,null,"12","12",null,null,"12"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,3.2,null,3.2,null,3.2,null,3.2,null,null,null,null,3.2,null,3.2,null,3.2,null,null,null,null,null,3.2,3.2,null,null,3.2]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,2.4000000953674316,null,2.4000000953674316,null,2.4000000953674316,null,2.4000000953674316,null,null,null,null,2.4000000953674316,null,2.4000000953674316,null,2.4000000953674316,null,null,null,null,null,2.4000000953674316,2.4000000953674316,null,null,2.4000000953674316]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,3.0999999046325684,null,3.0999999046325684,null,3.0999999046325684,null,3.0999999046325684,null,null,null,null,3.0999999046325684,null,3.0999999046325684,null,3.0999999046325684,null,null,null,null,null,3.0999999046325684,3.0999999046325684,null,null,3.0999999046325684]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"LITT","index":132,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"LITT - Littlemore (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T019 - Gladstone South BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Capricornia"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/11kV 2MVA ON;1x66/11kV 2MVA ON(Standby)"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.9%, 2020 S 0.2% W 0.2%, 2021 S -0.3% W -0.3%2022 S 0.1% W 0.1%, 2023 S -0.4% W -0.4"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"0.6 MVA on 01/12/2018 at 19:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,2.2000000476837158,null,2.2000000476837158,null,2.2000000476837158,null,2.2000000476837158,null,null,null,null,2.2000000476837158,null,2.2000000476837158,null,2.2000000476837158,null,null,null,null,null,2.2000000476837158,2.2000000476837158,null,null,2.2000000476837158]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,0.60000002384185791,null,0.60000002384185791,null,0.5,null,0.5,null,null,null,null,0.5,null,0.60000002384185791,null,0.60000002384185791,null,null,null,null,null,0.60000002384185791,0.60000002384185791,null,null,0.60000002384185791]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.92600000000000005,null,0.92600000000000005,null,0.92700000000000005,null,0.92700000000000005,null,null,null,null,0.92700000000000005,null,0.93,null,0.93,null,null,null,null,null,0.93,0.93,null,null,0.93]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,0.60000002384185791,null,0.60000002384185791,null,0.5,null,0.5,null,null,null,null,0.5,null,0.5,null,0.5,null,null,null,null,null,0.5,0.5,null,null,0.5]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"5.5",null,"5.5",null,"5.5",null,"5.5",null,null,null,null,"5.5",null,"5.5",null,"5.5",null,null,null,null,null,"5.5","5.5",null,null,"5.5"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,0.6,null,0.6,null,0.5,null,0.5,null,null,null,null,0.5,null,0.5,null,0.5,null,null,null,null,null,0.5,0.5,null,null,0.5]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,2,null,2,null,2,null,2,null,null,null,null,2,null,2,null,2,null,null,null,null,null,2,2,null,null,2]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"LOCR","index":133,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"LOCR - Louisa Creek (33/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T176 - Louisa Creek BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Mackay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x33/11kV 6.3MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.4%, 2020 S 0.7% W 0.7%, 2021 S 0.7% W 0.7%, 2022 S 0.9% W 0.9%, 2023 S 0.7% W 0.7%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"2.4 MVA on 26/11/2018 at 18:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,7.4000000953674316,null,7.4000000953674316,null,7.4000000953674316,null,7.4000000953674316,null,null,null,null,7.4000000953674316,null,7.8000001907348633,null,7.8000001907348633,null,null,null,null,null,7.8000001907348633,7.8000001907348633,null,null,7.8000001907348633]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,2.5999999046325684,null,2.5999999046325684,null,2.5999999046325684,null,2.5999999046325684,null,null,null,null,2.7000000476837158,null,1.8999999761581421,null,1.8999999761581421,null,null,null,null,null,1.8999999761581421,1.8999999761581421,null,null,1.8999999761581421]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.999,null,0.999,null,0.999,null,0.999,null,null,null,null,0.999,null,0.999,null,0.999,null,null,null,null,null,0.999,0.999,null,null,0.999]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,2.4000000953674316,null,2.5,null,2.5,null,2.5,null,null,null,null,2.5,null,1.7999999523162842,null,1.7999999523162842,null,null,null,null,null,1.7999999523162842,1.7999999523162842,null,null,1.8999999761581421]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.1,null,0.1,null,0.1,null,0.1,null,null,null,null,0.1,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"5.5",null,"5.5",null,"5.5",null,"5.5",null,null,null,null,"5.5",null,"5.5",null,"5.5",null,null,null,null,null,"5.5","5.5",null,null,"5.5"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,2.4,null,2.5,null,2.5,null,2.5,null,null,null,null,2.5,null,1.8,null,1.8,null,null,null,null,null,1.8,1.8,null,null,1.9]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,1.2000000476837158,null,1.2000000476837158,null,1.2000000476837158,null,1.2000000476837158,null,null,null,null,1.2000000476837158,null,1.2000000476837158,null,1.2000000476837158,null,null,null,null,null,1.2000000476837158,1.2000000476837158,null,null,1.2000000476837158]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,1.6000000238418579,null,1.6000000238418579,null,1.6000000238418579,null,1.6000000238418579,null,null,null,null,1.6000000238418579,null,1.6000000238418579,null,1.6000000238418579,null,null,null,null,null,1.6000000238418579,1.6000000238418579,null,null,1.6000000238418579]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"LONG","index":134,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"LONG - Longreach (66/22kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T072 - Barcaldine BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Capricornia"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/22kV 8/10MVA ONAN/ONAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -2.3%, 2020 S -1.9% W -1.9%2021 S -1.1% W -1.1%2022 S -0.7% W -0.7%2023 S -1.1% W -1.1"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"8.7 MVA on 11/03/2019 at 16:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,24.399999618530273,null,24.399999618530273,null,24.399999618530273,null,24.399999618530273,null,null,null,null,24.399999618530273,null,28.600000381469727,null,28.600000381469727,null,null,null,null,null,28.600000381469727,28.600000381469727,null,null,28.600000381469727]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,10.199999809265137,null,10.100000381469727,null,9.8999996185302734,null,9.8000001907348633,null,null,null,null,9.8000001907348633,null,7.4000000953674316,null,7.3000001907348633,null,null,null,null,null,7.1999998092651367,7.0999999046325684,null,null,7.0999999046325684]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.98599999999999999,null,0.98599999999999999,null,0.98599999999999999,null,0.98599999999999999,null,null,null,null,0.98599999999999999,null,0.997,null,0.997,null,null,null,null,null,0.997,0.997,null,null,0.997]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,13.899999618530273,null,13.899999618530273,null,13.899999618530273,null,13.899999618530273,null,null,null,null,13.899999618530273,null,15,null,15,null,null,null,null,null,15,15,null,null,15]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,9.3999996185302734,null,9.3000001907348633,null,9.1000003814697266,null,9,null,null,null,null,9,null,6.8000001907348633,null,6.6999998092651367,null,null,null,null,null,6.5999999046325684,6.5,null,null,6.5]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.5,null,0.5,null,0.5,null,0.5,null,null,null,null,0.5,null,0.3,null,0.3,null,null,null,null,null,0.3,0.3,null,null,0.3]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"6.5",null,"6.5",null,"6.5",null,"6.5",null,null,null,null,"6.5",null,"6.5",null,"6.5",null,null,null,null,null,"6.5","6.5",null,null,"6.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"LUCI","index":135,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"LUCI - Lucinda (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T047 - Ingham BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Nth Queensland"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/11kV 5/4MVA ONAF/ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.5%, 2020 S -0.4% W -0.4%2021 S -0.4% W -0.4%2022 S -0.6% W -0.6%2023 S -0.7% W -0.7"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"3 MVA on 25/08/2018 at 19:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,5.9000000953674316,null,5.9000000953674316,null,5.9000000953674316,null,5.9000000953674316,null,null,null,null,5.9000000953674316,null,6,null,6,null,null,null,null,null,6,6,null,null,6]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,3.0999999046325684,null,3.0999999046325684,null,3,null,3,null,null,null,null,3,null,2.9000000953674316,null,2.9000000953674316,null,null,null,null,null,2.9000000953674316,2.9000000953674316,null,null,2.7999999523162842]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.88600000000000001,null,0.88600000000000001,null,0.88600000000000001,null,0.88600000000000001,null,null,null,null,0.88600000000000001,null,0.88,null,0.88,null,null,null,null,null,0.88,0.88,null,null,0.88]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,3,null,3,null,3,null,2.9000000953674316,null,null,null,null,2.9000000953674316,null,2.9000000953674316,null,2.9000000953674316,null,null,null,null,null,2.9000000953674316,2.7999999523162842,null,null,2.7999999523162842]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.2,null,0.2,null,0.2,null,0.1,null,null,null,null,0.1,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"7",null,"7",null,"7",null,"7",null,null,null,null,"7",null,"7",null,"7",null,null,null,null,null,"7","7",null,null,"7"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,3,null,3,null,3,null,2.9,null,null,null,null,2.9,null,2.9,null,2.9,null,null,null,null,null,2.9,2.8,null,null,2.8]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,1.1000000238418579,null,1.1000000238418579,null,1.1000000238418579,null,1.1000000238418579,null,null,null,null,1.1000000238418579,null,1.1000000238418579,null,1.1000000238418579,null,null,null,null,null,1.1000000238418579,1.1000000238418579,null,null,1.1000000238418579]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0.40000000596046448,null,0.40000000596046448,null,0.40000000596046448,null,0.40000000596046448,null,null,null,null,0.40000000596046448,null,0.40000000596046448,null,0.40000000596046448,null,null,null,null,null,0.40000000596046448,0.40000000596046448,null,null,0.40000000596046448]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,2,null,2,null,2,null,2,null,null,null,null,2,null,2,null,2,null,null,null,null,null,2,2,null,null,2]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"LYLA","index":136,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"LYLA - Lyndley Lane (33/22kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T002 - Dalby East BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is South West"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x33/22kV 0.3MVA ON;1x33/22kV 0.75MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.3%, 2020 S 0.0% W 0.0%, 2021 S -0.0% W -0.0%2022 S 0.2% W 0.2%, 2023 S 0.0% W 0.0%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"0.6 MVA on 13/02/2019 at 19:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,1.1000000238418579,null,1.1000000238418579,null,1.1000000238418579,null,1.1000000238418579,null,null,null,null,1.1000000238418579,null,1.1000000238418579,null,1.1000000238418579,null,null,null,null,null,1.1000000238418579,1.1000000238418579,null,null,1.1000000238418579]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,0.69999998807907104,null,0.69999998807907104,null,0.69999998807907104,null,0.69999998807907104,null,null,null,null,0.69999998807907104,null,0.60000002384185791,null,0.60000002384185791,null,null,null,null,null,0.60000002384185791,0.60000002384185791,null,null,0.60000002384185791]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.95,null,0.95,null,0.95,null,0.95,null,null,null,null,0.95,null,0.94499999999999995,null,0.94499999999999995,null,null,null,null,null,0.94499999999999995,0.94499999999999995,null,null,0.94499999999999995]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0.30000001192092896,null,0.30000001192092896,null,0.30000001192092896,null,0.30000001192092896,null,null,null,null,0.30000001192092896,null,0.30000001192092896,null,0.30000001192092896,null,null,null,null,null,0.30000001192092896,0.30000001192092896,null,null,0.30000001192092896]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,0.69999998807907104,null,0.69999998807907104,null,0.69999998807907104,null,0.69999998807907104,null,null,null,null,0.69999998807907104,null,0.5,null,0.5,null,null,null,null,null,0.5,0.5,null,null,0.5]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"7.5",null,"7.5",null,"7.5",null,"7.5",null,null,null,null,"7.5",null,"7.5",null,"7.5",null,null,null,null,null,"7.5","7.5",null,null,"7.5"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,0.4,null,0.4,null,0.4,null,0.4,null,null,null,null,0.4,null,0.2,null,0.2,null,null,null,null,null,0.2,0.2,null,null,0.2]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0.30000001192092896,null,0.30000001192092896,null,0.30000001192092896,null,0.30000001192092896,null,null,null,null,0.30000001192092896,null,0.30000001192092896,null,0.30000001192092896,null,null,null,null,null,0.30000001192092896,0.30000001192092896,null,null,0.30000001192092896]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,1,null,1,null,1,null,1,null,null,null,null,1,null,1,null,1,null,null,null,null,null,1,1,null,null,1]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"MACI","index":137,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"MACI - Maryborough City (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T059 - Maryborough BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Wide Bay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/11kV 14/19MVA ONAN/ONAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 3.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -1.6%, 2020 S -1.6% W -1.6%2021 S -1.1% W -1.1%2022 S -1.1% W -1.1%2023 S -1.5% W -1.5"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"13.8 MVA on 13/02/2019 at 16:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,39.599998474121094,null,39.599998474121094,null,39.599998474121094,null,39.599998474121094,null,null,null,null,39.599998474121094,null,42.700000762939453,null,42.700000762939453,null,null,null,null,null,42.700000762939453,42.700000762939453,null,null,42.700000762939453]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,15.399999618530273,null,15.100000381469727,null,14.800000190734863,null,14.600000381469727,null,null,null,null,14.399999618530273,null,10.300000190734863,null,10.100000381469727,null,null,null,null,null,9.8999996185302734,9.8000001907348633,null,null,9.6999998092651367]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.98599999999999999,null,0.98699999999999999,null,0.98799999999999999,null,0.98899999999999999,null,null,null,null,0.98899999999999999,null,0.998,null,0.998,null,null,null,null,null,0.997,0.997,null,null,0.996]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,22.700000762939453,null,22.700000762939453,null,22.700000762939453,null,22.700000762939453,null,null,null,null,22.700000762939453,null,24.399999618530273,null,24.399999618530273,null,null,null,null,null,24.399999618530273,24.399999618530273,null,null,24.399999618530273]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,13.800000190734863,null,13.600000381469727,null,13.300000190734863,null,13.100000381469727,null,null,null,null,13,null,9.5,null,9.3000001907348633,null,null,null,null,null,9.1999998092651367,9.1000003814697266,null,null,9]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.7,null,0.7,null,0.7,null,0.7,null,null,null,null,0.7,null,0.5,null,0.5,null,null,null,null,null,0.5,0.5,null,null,0.5]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"16.5",null,"16.5",null,"16.5",null,"16.5",null,null,null,null,"16.5",null,"16.5",null,"16.5",null,null,null,null,null,"16.5","16.5",null,null,"16.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,2,null,2,null,2,null,2,null,null,null,null,2,null,2,null,2,null,null,null,null,null,2,2,null,null,2]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"MACN","index":138,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"MACN - Macknade (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T047 - Ingham BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Nth Queensland"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x6.3MVA 66kV Transformer;1x66/11kV 8/10MVA ONAN/ONAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 8.8 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.5%, 2020 S -0.3% W -0.3%2021 S -0.4% W -0.4%2022 S -0.7% W -0.7%2023 S -0.8% W -0.8"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"5.6 MVA on 20/02/2019 at 19:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,13.899999618530273,null,13.899999618530273,null,13.899999618530273,null,13.899999618530273,null,null,null,null,13.899999618530273,null,13.899999618530273,null,13.899999618530273,null,null,null,null,null,13.899999618530273,13.899999618530273,null,null,13.899999618530273]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0.10000000149011612,null,0.10000000149011612,null,0.10000000149011612,null,0.10000000149011612,null,null,null,null,0.10000000149011612,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,5.9000000953674316,null,5.9000000953674316,null,5.8000001907348633,null,5.8000001907348633,null,null,null,null,5.6999998092651367,null,3.2000000476837158,null,3.2000000476837158,null,null,null,null,null,3.2000000476837158,3.2000000476837158,null,null,3.2000000476837158]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.95799999999999996,null,0.95799999999999996,null,0.95799999999999996,null,0.95799999999999996,null,null,null,null,0.95799999999999996,null,0.97899999999999998,null,0.97899999999999998,null,null,null,null,null,0.97899999999999998,0.97899999999999998,null,null,0.97899999999999998]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,7.1999998092651367,null,7.1999998092651367,null,7.1999998092651367,null,7.1999998092651367,null,null,null,null,7.1999998092651367,null,8.1999998092651367,null,8.1999998092651367,null,null,null,null,null,8.1999998092651367,8.1999998092651367,null,null,8.1999998092651367]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,5.8000001907348633,null,5.6999998092651367,null,5.6999998092651367,null,5.5999999046325684,null,null,null,null,5.5999999046325684,null,3,null,3,null,null,null,null,null,3,3,null,null,3]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.3,null,0.3,null,0.3,null,0.3,null,null,null,null,0.3,null,0.2,null,0.2,null,null,null,null,null,0.2,0.2,null,null,0.2]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"509.5",null,"509.5",null,"509.5",null,"509.5",null,null,null,null,"509.5",null,"509.5",null,"509.5",null,null,null,null,null,"509.5","509.5",null,null,"509.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,2.7999999523162842,null,2.7999999523162842,null,2.7999999523162842,null,2.7999999523162842,null,null,null,null,2.7999999523162842,null,2.7999999523162842,null,2.7999999523162842,null,null,null,null,null,2.7999999523162842,2.7999999523162842,null,null,2.7999999523162842]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0.60000002384185791,null,0.60000002384185791,null,0.60000002384185791,null,0.60000002384185791,null,null,null,null,0.60000002384185791,null,0.60000002384185791,null,0.60000002384185791,null,null,null,null,null,0.60000002384185791,0.60000002384185791,null,null,0.60000002384185791]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"MAFU","index":139,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"MAFU - Max Fulton (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"TMES - Townsville Mesh"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Nth Queensland"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/11kV 21/26.25/35MVA ONAN/ODAN/ODAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.6%, 2020 S -0.1% W -0.1%2021 S -0.2% W -0.2%2022 S -0.5% W -0.5%2023 S -0.7% W -0.7"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"13.7 MVA on 28/11/2018 at 14:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,76.300003051757813,null,76.300003051757813,null,76.300003051757813,null,76.300003051757813,null,null,null,null,76.300003051757813,null,77.699996948242188,null,77.699996948242188,null,null,null,null,null,77.699996948242188,77.699996948242188,null,null,77.699996948242188]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,13.600000381469727,null,13.5,null,13.300000190734863,null,13.199999809265137,null,null,null,null,13.199999809265137,null,9.5,null,9.3999996185302734,null,null,null,null,null,9.3999996185302734,9.3000001907348633,null,null,9.3000001907348633]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.996,null,0.996,null,0.996,null,0.996,null,null,null,null,0.996,null,0.94599999999999995,null,0.94599999999999995,null,null,null,null,null,0.94599999999999995,0.94599999999999995,null,null,0.94599999999999995]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,38.5,null,38.5,null,38.5,null,38.5,null,null,null,null,38.5,null,39.200000762939453,null,39.200000762939453,null,null,null,null,null,39.200000762939453,39.200000762939453,null,null,39.200000762939453]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,12.399999618530273,null,12.300000190734863,null,12.100000381469727,null,12,null,null,null,null,12,null,9.1000003814697266,null,9.1000003814697266,null,null,null,null,null,9,9,null,null,9]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.6,null,0.6,null,0.6,null,0.6,null,null,null,null,0.6,null,0.5,null,0.5,null,null,null,null,null,0.5,0.5,null,null,0.5]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"21",null,"21",null,"21",null,"21",null,null,null,null,"21",null,"21",null,"21",null,null,null,null,null,"21","21",null,null,"21"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"MALC","index":140,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,13],[15,16,15,27],[18,19,19,32],[19,3,20,13],[19,16,20,17],[23,4,24,10],[23,11,23,22],[23,23,23,35],[24,11,24,12],[24,13,24,14],[24,15,24,16],[24,17,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,10],[25,11,25,12],[25,13,25,14],[25,15,25,16],[25,17,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,10],[26,11,26,12],[26,13,26,14],[26,15,26,16],[26,17,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,10],[27,11,27,12],[27,13,27,14],[27,15,27,16],[27,17,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,10],[28,11,28,12],[28,13,28,14],[28,15,28,16],[28,17,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,10],[29,11,29,12],[29,13,29,14],[29,15,29,16],[29,17,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,10],[30,11,30,12],[30,13,30,14],[30,15,30,16],[30,17,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,10],[31,11,31,12],[31,13,31,14],[31,15,31,16],[31,17,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,10],[32,11,32,12],[32,13,32,14],[32,15,32,16],[32,17,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,10],[33,11,33,12],[33,13,33,14],[33,15,33,16],[33,17,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,10],[34,11,34,12],[34,13,34,14],[34,15,34,16],[34,17,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,10],[35,11,35,12],[35,13,35,14],[35,15,35,16],[35,17,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,10],[36,11,36,12],[36,13,36,14],[36,15,36,16],[36,17,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,10],[37,11,37,12],[37,13,37,14],[37,15,37,16],[37,17,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,10],[38,11,38,12],[38,13,38,14],[38,15,38,16],[38,17,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,10],[39,11,39,12],[39,13,39,14],[39,15,39,16],[39,17,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,10],[40,11,40,12],[40,13,40,14],[40,15,40,16],[40,17,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,10],[42,11,42,12],[42,13,42,14],[42,15,42,16],[42,17,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,10],[41,11,41,12],[41,13,41,14],[41,15,41,16],[41,17,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,11,44,12],[44,13,44,14],[44,15,44,16],[44,17,44,20],[43,11,43,12],[43,13,43,14],[43,15,43,16],[43,17,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,10],[45,11,45,12],[45,13,45,14],[45,15,45,16],[45,17,45,20],[45,21,45,22],[44,4,44,10],[43,32,43,34],[43,4,43,10]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"MALC - Malchi (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"RMES - Rockhampton Mesh"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Capricornia"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/11kV 7.5/10MVA ONAN/ONAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.7%, 2020 S 1.0% W 1.0%, 2021 S 1.0% W 1.0%, 2022 S 1.3% W 1.3%, 2023 S 1.0% W 1.0%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,null,"17.4 MVA on 13/02/2019 at 18:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,null,23.799999237060547,null,23.799999237060547,null,23.799999237060547,null,23.799999237060547,null,null,null,23.799999237060547,null,28.700000762939453,null,28.700000762939453,null,null,null,null,null,28.700000762939453,28.700000762939453,null,null,28.700000762939453]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,null,19.799999237060547,null,19.899999618530273,null,11.5,null,11.600000381469727,null,null,null,11.899999618530273,null,9.8000001907348633,null,9.8000001907348633,null,null,null,null,null,4.9000000953674316,4.9000000953674316,null,null,5]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,null,0.97599999999999998,null,0.97599999999999998,null,0.97899999999999998,null,0.97899999999999998,null,null,null,0.97799999999999998,null,0.98299999999999998,null,0.98299999999999998,null,null,null,null,null,0.98799999999999999,0.98799999999999999,null,null,0.98699999999999999]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,null,13.300000190734863,null,13.300000190734863,null,13.300000190734863,null,13.300000190734863,null,null,null,13.300000190734863,null,15,null,15,null,null,null,null,null,15,15,null,null,15]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,null,17.299999237060547,null,17.399999618530273,null,9,null,9.1000003814697266,null,null,null,9.1999998092651367,null,9.3000001907348633,null,9.3999996185302734,null,null,null,null,null,4.5,4.5,null,null,4.5999999046325684]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,null,0.9,null,0.9,null,0.5,null,0.5,null,null,null,0.5,null,0.5,null,0.5,null,null,null,null,null,0.2,0.2,null,null,0.2]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,null,"6.5",null,"6.5",null,"6.5",null,"6.5",null,null,null,"6.5",null,"6.5",null,"6.5",null,null,null,null,null,"6.5","6.5",null,null,"6.5"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,null,4,null,4.0999999999999996]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,null,1.5,null,1.5,null,1.5,null,1.5,null,null,null,1.5,null,1.5,null,1.5,null,null,null,null,null,1.5,1.5,null,null,1.5]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,null,2.5,null,2.5,null,2.5,null,2.5,null,null,null,2.5,null,2.5,null,2.5,null,null,null,null,null,2.5,2.5,null,null,2.5]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)",null,null,null,null,null,null,null,null,0.10000000149011612]
[null,null,null,null,"LARc (MW)",null,null,null,null,null,null,null,null,0.1]
[null,null,null,null,"Substation Category",null,null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,null,"Yes",null,"No",null,"Yes",null,"Yes",null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"MARE","index":141,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"MARE - Mareeba (66/22kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T055 - Turkinje 66kV BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Far North"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/22kV 20/25MVA ONAN/ONAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.3%, 2020 S 1.0% W 1.0%, 2021 S 0.8% W 0.8%, 2022 S 0.7% W 0.7%, 2023 S 0.4% W 0.4%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"22.1 MVA on 26/11/2018 at 17:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,54.799999237060547,null,54.799999237060547,null,54.799999237060547,null,54.799999237060547,null,null,null,null,54.799999237060547,null,57.5,null,57.5,null,null,null,null,null,57.5,57.5,null,null,57.5]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,22.700000762939453,null,22.799999237060547,null,22.700000762939453,null,22.899999618530273,null,null,null,null,23.100000381469727,null,17.799999237060547,null,18,null,null,null,null,null,18,18.100000381469727,null,null,18.299999237060547]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,1,null,1,null,1,null,1,null,null,null,null,1,null,0.998,null,0.998,null,null,null,null,null,0.998,0.998,null,null,0.999]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,31.299999237060547,null,31.299999237060547,null,31.299999237060547,null,31.299999237060547,null,null,null,null,31.299999237060547,null,32.5,null,32.5,null,null,null,null,null,32.5,32.5,null,null,32.5]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,21.200000762939453,null,21.200000762939453,null,21.200000762939453,null,21.299999237060547,null,null,null,null,21.5,null,17.200000762939453,null,17.399999618530273,null,null,null,null,null,17.399999618530273,17.5,null,null,17.700000762939453]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,1.1000000000000001,null,1.1000000000000001,null,1.1000000000000001,null,1.1000000000000001,null,null,null,null,1.1000000000000001,null,0.9,null,0.9,null,null,null,null,null,0.9,0.9,null,null,0.9]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"10",null,"10",null,"10",null,"10",null,null,null,null,"10",null,"10",null,"10",null,null,null,null,null,"10","10",null,null,"10"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"MASO","index":142,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"MASO - Marian South (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T141 - Pioneer Valley BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Mackay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x10MVA 66/11kV Transformer"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.4%, 2020 S 0.7% W 0.7%, 2021 S 0.7% W 0.7%, 2022 S 0.2% W 0.2%, 2023 S -0.0% W -0.0"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"6.2 MVA on 28/11/2018 at 18:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,15,null,15,null,15,null,15,null,null,null,null,15,null,15,null,15,null,null,null,null,null,15,15,null,null,15]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,6.5999999046325684,null,6.6999998092651367,null,6.5999999046325684,null,6.5999999046325684,null,null,null,null,6.6999998092651367,null,6.3000001907348633,null,6.3000001907348633,null,null,null,null,null,6.3000001907348633,6.3000001907348633,null,null,6.4000000953674316]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.99099999999999999,null,0.99099999999999999,null,0.99099999999999999,null,0.99099999999999999,null,null,null,null,0.99099999999999999,null,0.995,null,0.995,null,null,null,null,null,0.995,0.995,null,null,0.995]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,5.8000001907348633,null,5.9000000953674316,null,5.8000001907348633,null,5.8000001907348633,null,null,null,null,5.9000000953674316,null,5.4000000953674316,null,5.5,null,null,null,null,null,5.5,5.5,null,null,5.5]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.3,null,0.3,null,0.3,null,0.3,null,null,null,null,0.3,null,0.3,null,0.3,null,null,null,null,null,0.3,0.3,null,null,0.3]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"11",null,"11",null,"11",null,"11",null,null,null,null,"11",null,"11",null,"11",null,null,null,null,null,"11","11",null,null,"11"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,5.8,null,5.9,null,5.8,null,5.8,null,null,null,null,5.9,null,5.4,null,5.5,null,null,null,null,null,5.5,5.5,null,null,5.5]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,3.4000000953674316,null,3.4000000953674316,null,3.4000000953674316,null,3.4000000953674316,null,null,null,null,3.4000000953674316,null,3.4000000953674316,null,3.4000000953674316,null,null,null,null,null,3.4000000953674316,3.4000000953674316,null,null,3.4000000953674316]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,10,null,10,null,10,null,10,null,null,null,null,10,null,10,null,10,null,null,null,null,null,10,10,null,null,10]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,2.7999999523162842,null,2.7999999523162842,null,2.7999999523162842,null,2.7999999523162842,null,null,null,null,2.7999999523162842,null,2.7999999523162842,null,2.7999999523162842,null,null,null,null,null,2.7999999523162842,2.7999999523162842,null,null,2.7999999523162842]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"MCCR","index":143,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"MCCR - McKinley Creek (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T141 - Pioneer Valley BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Mackay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/11kV 5/6.3MVA ONAN/ONAF;1xMCCR TX NO 1-66/11KV TRANSF 1"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.2%, 2020 S 0.5% W 0.5%, 2021 S 0.5% W 0.5%, 2022 S 0.6% W 0.6%, 2023 S 0.5% W 0.5%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"3.7 MVA on 12/02/2019 at 18:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,15.100000381469727,null,15.100000381469727,null,15.100000381469727,null,15.100000381469727,null,null,null,null,15.100000381469727,null,15.100000381469727,null,15.100000381469727,null,null,null,null,null,15.100000381469727,15.100000381469727,null,null,15.100000381469727]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,3.7999999523162842,null,3.7999999523162842,null,3.7999999523162842,null,3.9000000953674316,null,null,null,null,3.9000000953674316,null,2.7999999523162842,null,2.7999999523162842,null,null,null,null,null,2.7999999523162842,2.7999999523162842,null,null,2.7999999523162842]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.97399999999999998,null,0.97399999999999998,null,0.97399999999999998,null,0.97399999999999998,null,null,null,null,0.97399999999999998,null,0.97499999999999998,null,0.97499999999999998,null,null,null,null,null,0.97499999999999998,0.97499999999999998,null,null,0.97499999999999998]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,7.9000000953674316,null,7.9000000953674316,null,7.9000000953674316,null,7.9000000953674316,null,null,null,null,7.9000000953674316,null,8.1999998092651367,null,8.1999998092651367,null,null,null,null,null,8.1999998092651367,8.1999998092651367,null,null,8.1999998092651367]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,3.5,null,3.5,null,3.5,null,3.5999999046325684,null,null,null,null,3.5999999046325684,null,2.7000000476837158,null,2.7000000476837158,null,null,null,null,null,2.7000000476837158,2.7000000476837158,null,null,2.7000000476837158]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.2,null,0.2,null,0.2,null,0.2,null,null,null,null,0.2,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"9.5",null,"9.5",null,"9.5",null,"9.5",null,null,null,null,"9.5",null,"9.5",null,"9.5",null,null,null,null,null,"9.5","9.5",null,null,"9.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"MEAD","index":144,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"MEAD - Meadowvale (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T020 - Bundaberg BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Wide Bay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/11kV 12/14MVA ONAN/ONAF;1x62/11kV 7.5MVA ONAN(Standby)"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.2%, 2020 S 0.4% W 0.4%, 2021 S 0.3% W 0.3%, 2022 S 0.1% W 0.1%, 2023 S -0.1% W -0.1"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"9.3 MVA on 14/02/2019 at 19:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,14,null,14,null,14,null,14,null,null,null,null,14,null,15.199999809265137,null,15.199999809265137,null,null,null,null,null,15.199999809265137,15.199999809265137,null,null,15.199999809265137]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,10.699999809265137,null,10.699999809265137,null,10.600000381469727,null,10.600000381469727,null,null,null,null,10.699999809265137,null,8.5,null,8.6000003814697266,null,null,null,null,null,8.6000003814697266,8.6000003814697266,null,null,8.6000003814697266]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.996,null,0.996,null,0.996,null,0.996,null,null,null,null,0.996,null,1,null,1,null,null,null,null,null,1,1,null,null,1]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,9.8999996185302734,null,9.8999996185302734,null,9.8000001907348633,null,9.8000001907348633,null,null,null,null,9.8999996185302734,null,8.3999996185302734,null,8.5,null,null,null,null,null,8.5,8.5,null,null,8.5]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.5,null,0.5,null,0.5,null,0.5,null,null,null,null,0.5,null,0.4,null,0.4,null,null,null,null,null,0.4,0.4,null,null,0.4]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"13.5",null,"13.5",null,"13.5",null,"13.5",null,null,null,null,"13.5",null,"13.5",null,"13.5",null,null,null,null,null,"13.5","13.5",null,null,"13.5"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,9.9,null,9.9,null,9.8000000000000007,null,9.8000000000000007,null,null,null,null,9.9,null,8.4,null,8.5,null,null,null,null,null,8.5,8.5,null,null,8.5]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,11.199999809265137,null,11.199999809265137,null,11.199999809265137,null,11.199999809265137,null,null,null,null,11.199999809265137,null,11.199999809265137,null,11.199999809265137,null,null,null,null,null,11.199999809265137,11.199999809265137,null,null,11.199999809265137]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,2,null,2,null,2,null,2,null,null,null,null,2,null,2,null,2,null,null,null,null,null,2,2,null,null,2]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"MEAN","index":145,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"MEAN - Meandarra (33/22kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T194 - Columboola BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is South West"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x33/22kV 1MVA ONAN;1x33/22kV 1MVA ONAN(Standby)"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.4%, 2020 S -0.2% W -0.2%2021 S -0.2% W -0.2%2022 S -0.1% W -0.1%2023 S -0.3% W -0.3"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"0.8 MVA on 09/07/2018 at 19:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,1,null,1,null,1,null,1,null,null,null,null,1,null,1.1000000238418579,null,1.1000000238418579,null,null,null,null,null,1.1000000238418579,1.1000000238418579,null,null,1.1000000238418579]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,0.89999997615814209,null,0.89999997615814209,null,0.89999997615814209,null,0.89999997615814209,null,null,null,null,0.89999997615814209,null,0.80000001192092896,null,0.80000001192092896,null,null,null,null,null,0.80000001192092896,0.80000001192092896,null,null,0.80000001192092896]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,1,null,1,null,1,null,1,null,null,null,null,1,null,1,null,1,null,null,null,null,null,1,1,null,null,1]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,0.80000001192092896,null,0.80000001192092896,null,0.80000001192092896,null,0.80000001192092896,null,null,null,null,0.80000001192092896,null,0.69999998807907104,null,0.69999998807907104,null,null,null,null,null,0.69999998807907104,0.69999998807907104,null,null,0.69999998807907104]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"10",null,"10",null,"10",null,"10",null,null,null,null,"10",null,"10",null,"10",null,null,null,null,null,"10","10",null,null,"10"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,0.8,null,0.8,null,0.8,null,0.8,null,null,null,null,0.8,null,0.7,null,0.7,null,null,null,null,null,0.7,0.7,null,null,0.7]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,1,null,1,null,1,null,1,null,null,null,null,1,null,1,null,1,null,null,null,null,null,1,1,null,null,1]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"MERI","index":146,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"MERI - Merinda (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T181 - Bowen North BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Nth Queensland"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/11kV 6.3MVA ONAN;1x66/11kV 8/10MVA ONAN/ONAF(Standby)"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.8%, 2020 S -0.5% W -0.5%2021 S -0.5% W -0.5%2022 S -0.3% W -0.3%2023 S -0.3% W -0.3"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"5.3 MVA on 07/08/2018 at 13:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,8.1000003814697266,null,8.1000003814697266,null,8.1000003814697266,null,8.1000003814697266,null,null,null,null,8.1000003814697266,null,8.3000001907348633,null,8.3000001907348633,null,null,null,null,null,8.3000001907348633,8.3000001907348633,null,null,8.3000001907348633]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,4.8000001907348633,null,4.6999998092651367,null,4.6999998092651367,null,4.6999998092651367,null,null,null,null,4.6999998092651367,null,5.1999998092651367,null,5.0999999046325684,null,null,null,null,null,5.0999999046325684,5.0999999046325684,null,null,5.0999999046325684]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.85499999999999998,null,0.85499999999999998,null,0.85499999999999998,null,0.85499999999999998,null,null,null,null,0.85499999999999998,null,0.997,null,0.997,null,null,null,null,null,0.998,0.998,null,null,0.998]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,4.6999998092651367,null,4.5999999046325684,null,4.5999999046325684,null,4.5999999046325684,null,null,null,null,4.5999999046325684,null,4.8000001907348633,null,4.8000001907348633,null,null,null,null,null,4.8000001907348633,4.6999998092651367,null,null,4.6999998092651367]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.2,null,0.2,null,0.2,null,0.2,null,null,null,null,0.2,null,0.2,null,0.2,null,null,null,null,null,0.2,0.2,null,null,0.2]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"19",null,"19",null,"19",null,"19",null,null,null,null,"19",null,"19",null,"19",null,null,null,null,null,"19","19",null,null,"19"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,4.7,null,4.5999999999999996,null,4.5999999999999996,null,4.5999999999999996,null,null,null,null,4.5999999999999996,null,4.8,null,4.8,null,null,null,null,null,4.8,4.7,null,null,4.7]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,11,null,11,null,11,null,11,null,null,null,null,11,null,11,null,11,null,null,null,null,null,11,11,null,null,11]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"MERN","index":147,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"MERN - Meringandan (33/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T116 - Torrington BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is South West"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/11kV 6.3MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.6%, 2020 S 0.9% W 0.9%, 2021 S 0.8% W 0.8%, 2022 S 1.0% W 1.0%, 2023 S 0.6% W 0.6%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"10.5 MVA on 13/02/2019 at 18:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,16.899999618530273,null,16.899999618530273,null,16.899999618530273,null,16.899999618530273,null,null,null,null,16.899999618530273,null,18.5,null,18.5,null,null,null,null,null,18.5,18.5,null,null,18.5]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,10.899999618530273,null,11,null,11,null,11.100000381469727,null,null,null,null,11.199999809265137,null,11.199999809265137,null,11.300000190734863,null,null,null,null,null,11.399999618530273,11.5,null,null,11.600000381469727]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.98599999999999999,null,0.98599999999999999,null,0.98599999999999999,null,0.98599999999999999,null,null,null,null,0.98599999999999999,null,0.996,null,0.996,null,null,null,null,null,0.996,0.996,null,null,0.996]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,9.1999998092651367,null,9.1999998092651367,null,9.1999998092651367,null,9.1999998092651367,null,null,null,null,9.1999998092651367,null,9.3999996185302734,null,9.3999996185302734,null,null,null,null,null,9.3999996185302734,9.3999996185302734,null,null,9.3999996185302734]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,9.8000001907348633,null,9.8000001907348633,null,9.8000001907348633,null,9.8999996185302734,null,null,null,null,10,null,10.300000190734863,null,10.399999618530273,null,null,null,null,null,10.399999618530273,10.5,null,null,10.600000381469727]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.5,null,0.5,null,0.5,null,0.5,null,null,null,null,0.5,null,0.5,null,0.5,null,null,null,null,null,0.5,0.5,null,null,0.5]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"2.5",null,"2.5",null,"2.5",null,"2.5",null,null,null,null,"2.5",null,"2.5",null,"2.5",null,null,null,null,null,"2.5","2.5",null,null,"2.5"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,0.6,null,0.6,null,0.6,null,0.7,null,null,null,null,0.8,null,0.9,null,1,null,null,null,null,null,1,1.1000000000000001,null,null,1.2]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,1.5,null,1.5,null,1.5,null,1.5,null,null,null,null,1.5,null,1.5,null,1.5,null,null,null,null,null,1.5,1.5,null,null,1.5]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,1,null,1,null,1,null,1,null,null,null,null,1,null,1,null,1,null,null,null,null,null,1,1,null,null,1]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"MICO","index":148,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"MICO - Miles-Condamine (33/22kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T194 - Columboola BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is South West"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x33/22kV 0.75MVA ON;1x33/22kV 0.75MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.1%, 2020 S 0.1% W 0.1%, 2021 S 0.1% W 0.1%, 2022 S -0.2% W -0.2%2023 S -0.3% W -0.3"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"0.7 MVA on 23/01/2019 at 20:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,1.6,null,1.6,null,1.6,null,1.6,null,null,null,null,1.6,null,1.6,null,1.6,null,null,null,null,null,1.6,1.6,null,null,1.6]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,0.89999997615814209,null,0.89999997615814209,null,0.89999997615814209,null,0.89999997615814209,null,null,null,null,0.89999997615814209,null,0.69999998807907104,null,0.69999998807907104,null,null,null,null,null,0.69999998807907104,0.69999998807907104,null,null,0.69999998807907104]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.97699999999999998,null,0.97699999999999998,null,0.97699999999999998,null,0.97699999999999998,null,null,null,null,0.97699999999999998,null,0.97099999999999997,null,0.97099999999999997,null,null,null,null,null,0.97099999999999997,0.97099999999999997,null,null,0.97099999999999997]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0.8,null,0.8,null,0.8,null,0.8,null,null,null,null,0.8,null,0.8,null,0.8,null,null,null,null,null,0.8,0.8,null,null,0.8]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,0.80000001192092896,null,0.80000001192092896,null,0.80000001192092896,null,0.80000001192092896,null,null,null,null,0.80000001192092896,null,0.60000002384185791,null,0.60000002384185791,null,null,null,null,null,0.60000002384185791,0.60000002384185791,null,null,0.60000002384185791]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"4",null,"4",null,"4",null,"4",null,null,null,null,"4",null,"4",null,"4",null,null,null,null,null,"4","4",null,null,"4"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0.80000001192092896,null,0.80000001192092896,null,0.80000001192092896,null,0.80000001192092896,null,null,null,null,0.80000001192092896,null,0.80000001192092896,null,0.80000001192092896,null,null,null,null,null,0.80000001192092896,0.80000001192092896,null,null,0.80000001192092896]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0.20000000298023224,null,0.20000000298023224,null,0.20000000298023224,null,0.20000000298023224,null,null,null,null,0.20000000298023224,null,0.20000000298023224,null,0.20000000298023224,null,null,null,null,null,0.20000000298023224,0.20000000298023224,null,null,0.20000000298023224]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"MIDD","index":149,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"MIDD - Middlemount (66/22kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"H015 - Lilyvale BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Capricornia"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/22kV 5MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -1.8%, 2020 S -1.1% W -1.1%2021 S -1.1% W -1.1%2022 S -0.4% W -0.4%2023 S -0.5% W -0.5"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"5.3 MVA on 20/02/2019 at 19:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,15.300000190734863,null,15.300000190734863,null,15.300000190734863,null,15.300000190734863,null,null,null,null,15.300000190734863,null,18.600000381469727,null,18.600000381469727,null,null,null,null,null,18.600000381469727,18.600000381469727,null,null,18.600000381469727]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,5.8000001907348633,null,5.6999998092651367,null,5.5999999046325684,null,5.5999999046325684,null,null,null,null,5.5999999046325684,null,3.2999999523162842,null,3.2999999523162842,null,null,null,null,null,3.2000000476837158,3.2000000476837158,null,null,3.2000000476837158]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.98799999999999999,null,0.98799999999999999,null,0.98799999999999999,null,0.98799999999999999,null,null,null,null,0.98799999999999999,null,0.98799999999999999,null,0.98799999999999999,null,null,null,null,null,0.98799999999999999,0.98799999999999999,null,null,0.98799999999999999]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,8.6999998092651367,null,8.6999998092651367,null,8.6999998092651367,null,8.6999998092651367,null,null,null,null,8.6999998092651367,null,9.3000001907348633,null,9.3000001907348633,null,null,null,null,null,9.3000001907348633,9.3000001907348633,null,null,9.3000001907348633]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,5.3000001907348633,null,5.1999998092651367,null,5.0999999046325684,null,5.0999999046325684,null,null,null,null,5.0999999046325684,null,3.0999999046325684,null,3.0999999046325684,null,null,null,null,null,3.0999999046325684,3,null,null,3]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.3,null,0.3,null,0.3,null,0.3,null,null,null,null,0.3,null,0.2,null,0.2,null,null,null,null,null,0.2,0.2,null,null,0.2]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"4.5",null,"4.5",null,"4.5",null,"4.5",null,null,null,null,"4.5",null,"4.5",null,"4.5",null,null,null,null,null,"4.5","4.5",null,null,"4.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"MILC","index":150,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"MILC - Millchester (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T095 - Millchester BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Nth Queensland"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/11kV 10MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.9%, 2020 S -0.6% W -0.6%2021 S -0.8% W -0.8%2022 S -0.2% W -0.2%2023 S -0.3% W -0.3"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"5.4 MVA on 03/12/2018 at 15:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,10.600000381469727,null,10.600000381469727,null,10.600000381469727,null,10.600000381469727,null,null,null,null,10.600000381469727,null,12.199999809265137,null,12.199999809265137,null,null,null,null,null,12.199999809265137,12.199999809265137,null,null,12.199999809265137]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,5.9000000953674316,null,5.8000001907348633,null,5.6999998092651367,null,5.6999998092651367,null,null,null,null,5.6999998092651367,null,4.0999999046325684,null,4.0999999046325684,null,null,null,null,null,4,4,null,null,4]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.96899999999999997,null,0.96899999999999997,null,0.96899999999999997,null,0.96899999999999997,null,null,null,null,0.96899999999999997,null,0.98199999999999998,null,0.98199999999999998,null,null,null,null,null,0.98199999999999998,0.98199999999999998,null,null,0.98199999999999998]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,5.3000001907348633,null,5.1999998092651367,null,5.1999998092651367,null,5.1999998092651367,null,null,null,null,5.1999998092651367,null,3.7999999523162842,null,3.7999999523162842,null,null,null,null,null,3.7999999523162842,3.7000000476837158,null,null,3.7000000476837158]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.3,null,0.3,null,0.3,null,0.3,null,null,null,null,0.3,null,0.2,null,0.2,null,null,null,null,null,0.2,0.2,null,null,0.2]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"67",null,"67",null,"67",null,"67",null,null,null,null,"67",null,"67",null,"67",null,null,null,null,null,"67","67",null,null,"67"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,5.3,null,5.2,null,5.2,null,5.2,null,null,null,null,5.2,null,3.8,null,3.8,null,null,null,null,null,3.8,3.7,null,null,3.7]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,6.5,null,6.5,null,6.5,null,6.5,null,null,null,null,6.5,null,6.5,null,6.5,null,null,null,null,null,6.5,6.5,null,null,6.5]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"MILE","index":151,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"MILE - Miles (33/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T194 - Columboola BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is South West"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x33/11kV 6.3MVA ONAN;1x33/11KV 1.5MVA ONAN(Standby)"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -1.0%, 2020 S 0.3% W 0.3%, 2021 S 0.0% W 0.0%, 2022 S -0.7% W -0.7%2023 S -1.7% W -1.7"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"3.3 MVA on 20/02/2019 at 16:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,8.1000003814697266,null,8.1000003814697266,null,8.1000003814697266,null,8.1000003814697266,null,null,null,null,8.1000003814697266,null,9.3999996185302734,null,9.3999996185302734,null,null,null,null,null,9.3999996185302734,9.3999996185302734,null,null,9.3999996185302734]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,4.0999999046325684,null,4.0999999046325684,null,4,null,3.9000000953674316,null,null,null,null,3.9000000953674316,null,3,null,3,null,null,null,null,null,3,3,null,null,2.9000000953674316]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.97499999999999998,null,0.97499999999999998,null,0.97499999999999998,null,0.97499999999999998,null,null,null,null,0.97499999999999998,null,0.97299999999999998,null,0.97299999999999998,null,null,null,null,null,0.97299999999999998,0.97299999999999998,null,null,0.97299999999999998]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,3.5999999046325684,null,3.5999999046325684,null,3.5,null,3.5,null,null,null,null,3.5,null,2.7999999523162842,null,2.7999999523162842,null,null,null,null,null,2.7999999523162842,2.7000000476837158,null,null,2.7000000476837158]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.2,null,0.2,null,0.2,null,0.2,null,null,null,null,0.2,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"8.5",null,"8.5",null,"8.5",null,"8.5",null,null,null,null,"8.5",null,"8.5",null,"8.5",null,null,null,null,null,"8.5","8.5",null,null,"8.5"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,3.6,null,3.6,null,3.5,null,3.5,null,null,null,null,3.5,null,2.8,null,2.8,null,null,null,null,null,2.8,2.7,null,null,2.7]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,1.5,null,1.5,null,1.5,null,1.5,null,null,null,null,1.5,null,1.5,null,1.5,null,null,null,null,null,1.5,1.5,null,null,1.5]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,10,null,10,null,10,null,10,null,null,null,null,10,null,10,null,10,null,null,null,null,null,10,10,null,null,10]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"MILL","index":152,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"MILL - Millaroo (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T193 - Clare South BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Nth Queensland"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/11kV 5MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.4%, 2020 S -0.1% W -0.1%2021 S -0.3% W -0.3%2022 S -0.4% W -0.4%2023 S -0.5% W -0.5"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"2.6 MVA on 22/11/2018 at 16:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,5.5999999046325684,null,5.5999999046325684,null,5.5999999046325684,null,5.5999999046325684,null,null,null,null,5.5999999046325684,null,6.5,null,6.5,null,null,null,null,null,6.5,6.5,null,null,6.5]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,2.7000000476837158,null,2.7000000476837158,null,2.7000000476837158,null,2.7000000476837158,null,null,null,null,2.7000000476837158,null,1.6000000238418579,null,1.6000000238418579,null,null,null,null,null,1.6000000238418579,1.6000000238418579,null,null,1.5]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.876,null,0.876,null,0.876,null,0.876,null,null,null,null,0.876,null,0.88300000000000001,null,0.88300000000000001,null,null,null,null,null,0.88300000000000001,0.88300000000000001,null,null,0.88300000000000001]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,2.7000000476837158,null,2.5999999046325684,null,2.5999999046325684,null,2.5999999046325684,null,null,null,null,2.5999999046325684,null,1.6000000238418579,null,1.6000000238418579,null,null,null,null,null,1.6000000238418579,1.6000000238418579,null,null,1.6000000238418579]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.1,null,0.1,null,0.1,null,0.1,null,null,null,null,0.1,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"36",null,"36",null,"36",null,"36",null,null,null,null,"36",null,"36",null,"36",null,null,null,null,null,"36","36",null,null,"36"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,2.7,null,2.6,null,2.6,null,2.6,null,null,null,null,2.6,null,1.6,null,1.6,null,null,null,null,null,1.6,1.6,null,null,1.6]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,10,null,10,null,10,null,10,null,null,null,null,10,null,10,null,10,null,null,null,null,null,10,10,null,null,10]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"MILM","index":153,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"MILM - Millmerran (33/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T010 - Yarranlea BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is South West"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x33/11kV 6.3MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -2.3%, 2020 S -0.4% W -0.4%2021 S -0.4% W -0.4%2022 S -0.1% W -0.1%2023 S -0.4% W -0.4"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"4 MVA on 17/02/2018 at 19:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,7.5999999046325684,null,7.5999999046325684,null,7.5999999046325684,null,7.5999999046325684,null,null,null,null,7.5999999046325684,null,8.5,null,8.5,null,null,null,null,null,8.5,8.5,null,null,8.5]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,4.0999999046325684,null,4.0999999046325684,null,4.0999999046325684,null,4.0999999046325684,null,null,null,null,4.0999999046325684,null,4.0999999046325684,null,4.0999999046325684,null,null,null,null,null,4,4,null,null,4]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.996,null,0.996,null,0.996,null,0.996,null,null,null,null,0.996,null,0.91400000000000003,null,0.91400000000000003,null,null,null,null,null,0.91500000000000004,0.91500000000000004,null,null,0.91500000000000004]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,4,null,4,null,4,null,4,null,null,null,null,4,null,4.0999999046325684,null,4.0999999046325684,null,null,null,null,null,4,4,null,null,4]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.2,null,0.2,null,0.2,null,0.2,null,null,null,null,0.2,null,0.2,null,0.2,null,null,null,null,null,0.2,0.2,null,null,0.2]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"1505",null,"1505",null,"1505",null,"1505",null,null,null,null,"1505",null,"1505",null,"1505",null,null,null,null,null,"1505","1505",null,null,"1505"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,4,null,4,null,4,null,4,null,null,null,null,4,null,4.0999999999999996,null,4.0999999999999996,null,null,null,null,null,4,4,null,null,4]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,10,null,10,null,10,null,10,null,null,null,null,10,null,10,null,10,null,null,null,null,null,10,10,null,null,10]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"MING","index":154,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"MING - Mingela (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"TMES - Townsville Mesh"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Nth Queensland"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1xMING TX NO 1-66/11KV TRANSF 1"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.0%, 2020 S 0.2% W 0.2%, 2021 S 0.2% W 0.2%, 2022 S 0.0% W 0.0%, 2023 S -0.1% W -0.1"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"0.3 MVA on 01/06/2019 at 17:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,0.30000001192092896,null,0.30000001192092896,null,0.30000001192092896,null,0.30000001192092896,null,null,null,null,0.30000001192092896,null,0.30000001192092896,null,0.30000001192092896,null,null,null,null,null,0.30000001192092896,0.30000001192092896,null,null,0.30000001192092896]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,0.30000001192092896,null,0.30000001192092896,null,0.30000001192092896,null,0.30000001192092896,null,null,null,null,0.30000001192092896,null,0.30000001192092896,null,0.30000001192092896,null,null,null,null,null,0.30000001192092896,0.30000001192092896,null,null,0.30000001192092896]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.85,null,0.85,null,0.85,null,0.85,null,null,null,null,0.85,null,0.85,null,0.85,null,null,null,null,null,0.85,0.85,null,null,0.85]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,0.30000001192092896,null,0.30000001192092896,null,0.30000001192092896,null,0.30000001192092896,null,null,null,null,0.30000001192092896,null,0.20000000298023224,null,0.20000000298023224,null,null,null,null,null,0.20000000298023224,0.20000000298023224,null,null,0.20000000298023224]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"2709",null,"2709",null,"2709",null,"2709",null,null,null,null,"2709",null,"2709",null,"2709",null,null,null,null,null,"2709","2709",null,null,"2709"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,0.3,null,0.3,null,0.3,null,0.3,null,null,null,null,0.3,null,0.2,null,0.2,null,null,null,null,null,0.2,0.2,null,null,0.2]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,1,null,1,null,1,null,1,null,null,null,null,1,null,1,null,1,null,null,null,null,null,1,1,null,null,1]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"MIRA","index":155,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"MIRA - Mirani (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T141 - Pioneer Valley BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Mackay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/11kV 5MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.3%, 2020 S 0.6% W 0.6%, 2021 S 0.6% W 0.6%, 2022 S 0.2% W 0.2%, 2023 S 0.1% W 0.1%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"4.3 MVA on 01/12/2018 at 20:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,6.0999999046325684,null,6.0999999046325684,null,6.0999999046325684,null,6.0999999046325684,null,null,null,null,6.0999999046325684,null,7,null,7,null,null,null,null,null,7,7,null,null,7]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,4.5999999046325684,null,4.5999999046325684,null,4.5999999046325684,null,4.5999999046325684,null,null,null,null,4.5999999046325684,null,2.5999999046325684,null,2.5999999046325684,null,null,null,null,null,2.5999999046325684,2.5999999046325684,null,null,2.5999999046325684]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.94799999999999995,null,0.94799999999999995,null,0.94799999999999995,null,0.94799999999999995,null,null,null,null,0.94799999999999995,null,0.92500000000000004,null,0.92500000000000004,null,null,null,null,null,0.92500000000000004,0.92500000000000004,null,null,0.92500000000000004]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,4.5,null,4.5,null,4.5,null,4.5,null,null,null,null,4.5,null,2.2999999523162842,null,2.2999999523162842,null,null,null,null,null,2.4000000953674316,2.4000000953674316,null,null,2.4000000953674316]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.2,null,0.2,null,0.2,null,0.2,null,null,null,null,0.2,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"21",null,"21",null,"21",null,"21",null,null,null,null,"21",null,"21",null,"21",null,null,null,null,null,"21","21",null,null,"21"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,4.5,null,4.5,null,4.5,null,4.5,null,null,null,null,4.5,null,2.2999999999999998,null,2.2999999999999998,null,null,null,null,null,2.4,2.4,null,null,2.4]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,3.2000000476837158,null,3.2000000476837158,null,3.2000000476837158,null,3.2000000476837158,null,null,null,null,3.2000000476837158,null,3.2000000476837158,null,3.2000000476837158,null,null,null,null,null,3.2000000476837158,3.2000000476837158,null,null,3.2000000476837158]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,1.6000000238418579,null,1.6000000238418579,null,1.6000000238418579,null,1.6000000238418579,null,null,null,null,1.6000000238418579,null,1.6000000238418579,null,1.6000000238418579,null,null,null,null,null,1.6000000238418579,1.6000000238418579,null,null,1.6000000238418579]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"MITC","index":156,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"MITC - Mitchell (33/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T083 - Roma 33kV BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is South West"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 3x33/11kV 0.75MVA ON"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -2.3%, 2020 S -1.7% W -1.7%2021 S -1.6% W -1.6%2022 S -1.5% W -1.5%2023 S -1.9% W -1.9"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"2 MVA on 24/01/2019 at 15:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,2.2999999523162842,null,2.2999999523162842,null,2.2999999523162842,null,2.2999999523162842,null,null,null,null,2.2999999523162842,null,2.2999999523162842,null,2.2999999523162842,null,null,null,null,null,2.2999999523162842,2.2999999523162842,null,null,2.2999999523162842]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,2.4000000953674316,null,2.4000000953674316,null,2.2999999523162842,null,2.2999999523162842,null,null,null,null,2.2999999523162842,null,2,null,1.8999999761581421,null,null,null,null,null,1.8999999761581421,1.8999999761581421,null,null,1.7999999523162842]
[null,null,null,null,"LARn (MVA)",null,null,null,null,null,0.10000000149011612,null,0.10000000149011612]
[null,null,null,null,"LARn (MW)",null,null,null,null,null,0.1,null,0.1]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.91300000000000003,null,0.91300000000000003,null,0.91300000000000003,null,0.91300000000000003,null,null,null,null,0.91300000000000003,null,0.95899999999999996,null,0.95899999999999996,null,null,null,null,null,0.95899999999999996,0.95899999999999996,null,null,0.95899999999999996]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,1.5,null,1.5,null,1.5,null,1.5,null,null,null,null,1.5,null,1.5,null,1.5,null,null,null,null,null,1.5,1.5,null,null,1.5]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,2.2000000476837158,null,2.2000000476837158,null,2.0999999046325684,null,2.0999999046325684,null,null,null,null,2.0999999046325684,null,1.7999999523162842,null,1.7999999523162842,null,null,null,null,null,1.7999999523162842,1.7000000476837158,null,null,1.7000000476837158]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.1,null,0.1,null,0.1,null,0.1,null,null,null,null,0.1,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"10",null,"10",null,"10",null,"10",null,null,null,null,"10",null,"10",null,"10",null,null,null,null,null,"10","10",null,null,"10"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,0.7,null,0.7,null,0.6,null,0.6,null,null,null,null,0.6,null,0.3,null,0.3,null,null,null,null,null,0.3,0.2,null,null,0.2]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,1,null,1,null,1,null,1,null,null,null,null,1,null,1,null,1,null,null,null,null,null,1,1,null,null,1]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"No",null,"No",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"MIVA","index":157,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"MIVA - Miriam Vale (66/22kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T019 - Gladstone South BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Capricornia"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/22kV 6.3MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.0%, 2020 S 0.2% W 0.2%, 2021 S 0.2% W 0.2%, 2022 S 0.1% W 0.1%, 2023 S -0.1% W -0.1"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"1.9 MVA on 13/02/2019 at 19:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,9.1000003814697266,null,9.1000003814697266,null,9.1000003814697266,null,9.1000003814697266,null,null,null,null,9.1000003814697266,null,9.3999996185302734,null,9.3999996185302734,null,null,null,null,null,9.3999996185302734,9.3999996185302734,null,null,9.3999996185302734]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,2.0999999046325684,null,2.0999999046325684,null,2.0999999046325684,null,2.0999999046325684,null,null,null,null,2.0999999046325684,null,1.6000000238418579,null,1.6000000238418579,null,null,null,null,null,1.6000000238418579,1.6000000238418579,null,null,1.6000000238418579]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.996,null,0.996,null,0.996,null,0.996,null,null,null,null,0.996,null,0.999,null,0.999,null,null,null,null,null,0.999,0.999,null,null,0.999]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,1.8999999761581421,null,1.8999999761581421,null,1.8999999761581421,null,1.8999999761581421,null,null,null,null,1.8999999761581421,null,1.6000000238418579,null,1.6000000238418579,null,null,null,null,null,1.6000000238418579,1.6000000238418579,null,null,1.6000000238418579]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.1,null,0.1,null,0.1,null,0.1,null,null,null,null,0.1,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"89",null,"89",null,"89",null,"89",null,null,null,null,"89",null,"89",null,"89",null,null,null,null,null,"89","89",null,null,"89"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,1.9,null,1.9,null,1.9,null,1.9,null,null,null,null,1.9,null,1.6,null,1.6,null,null,null,null,null,1.6,1.6,null,null,1.6]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,1.6000000238418579,null,1.6000000238418579,null,1.6000000238418579,null,1.6000000238418579,null,null,null,null,1.6000000238418579,null,1.6000000238418579,null,1.6000000238418579,null,null,null,null,null,1.6000000238418579,1.6000000238418579,null,null,1.6000000238418579]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,3.0999999046325684,null,3.0999999046325684,null,3.0999999046325684,null,3.0999999046325684,null,null,null,null,3.0999999046325684,null,3.0999999046325684,null,3.0999999046325684,null,null,null,null,null,3.0999999046325684,3.0999999046325684,null,null,3.0999999046325684]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"MLEP","index":158,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"MLEP - Mount Leyshon Pump (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T095 - Millchester BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Nth Queensland"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/11kV 0MVA "]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.0%, 2020 S 0.0% W 0.0%, 2021 S 0.0% W 0.0%, 2022 S 0.0% W 0.0%, 2023 S 0.0% W 0.0%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"0.1 MVA on 01/01/2019 at 17:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,0.60000002384185791,null,0.60000002384185791,null,0.60000002384185791,null,0.60000002384185791,null,null,null,null,0.60000002384185791,null,0.60000002384185791,null,0.60000002384185791,null,null,null,null,null,0.60000002384185791,0.60000002384185791,null,null,0.60000002384185791]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,0.10000000149011612,null,0.10000000149011612,null,0.10000000149011612,null,0.10000000149011612,null,null,null,null,0.10000000149011612,null,0.10000000149011612,null,0.10000000149011612,null,null,null,null,null,0.10000000149011612,0.10000000149011612,null,null,0.10000000149011612]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.82,null,0.82,null,0.82,null,0.82,null,null,null,null,0.82,null,0.85,null,0.85,null,null,null,null,null,0.85,0.85,null,null,0.85]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,0.10000000149011612,null,0.10000000149011612,null,0.10000000149011612,null,0.10000000149011612,null,null,null,null,0.10000000149011612,null,0.10000000149011612,null,0.10000000149011612,null,null,null,null,null,0.10000000149011612,0.10000000149011612,null,null,0.10000000149011612]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"228.5",null,"228.5",null,"228.5",null,"228.5",null,null,null,null,"228.5",null,"228.5",null,"228.5",null,null,null,null,null,"228.5","228.5",null,null,"228.5"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,0.1,null,0.1,null,0.1,null,0.1,null,null,null,null,0.1,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,1,null,1,null,1,null,1,null,null,null,null,1,null,1,null,1,null,null,null,null,null,1,1,null,null,1]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"MOBA","index":159,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"MOBA - Mt Bassett (33/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T038 - Mackay BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Mackay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x33/11kV 10MVA ONAN;2x33/11kV 12.5MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.5%, 2020 S 1.0% W 1.0%, 2021 S 1.0% W 1.0%, 2022 S 0.6% W 0.6%, 2023 S 0.4% W 0.4%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"11.4 MVA on 28/11/2018 at 14:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,39,null,39,null,39,null,39,null,null,null,null,39,null,42,null,42,null,null,null,null,null,42,42,null,null,42]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,12.899999618530273,null,12.899999618530273,null,12.899999618530273,null,13,null,null,null,null,13.100000381469727,null,8.5,null,8.6000003814697266,null,null,null,null,null,8.6000003814697266,8.6999998092651367,null,null,8.8000001907348633]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.95799999999999996,null,0.95799999999999996,null,0.95799999999999996,null,0.95799999999999996,null,null,null,null,0.95799999999999996,null,0.95799999999999996,null,0.95799999999999996,null,null,null,null,null,0.95799999999999996,0.95799999999999996,null,null,0.95799999999999996]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,27.899999618530273,null,27.899999618530273,null,27.899999618530273,null,27.899999618530273,null,null,null,null,27.899999618530273,null,27.899999618530273,null,27.899999618530273,null,null,null,null,null,27.899999618530273,27.899999618530273,null,null,27.899999618530273]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,11.899999618530273,null,12,null,11.899999618530273,null,12,null,null,null,null,12.100000381469727,null,8.3000001907348633,null,8.3999996185302734,null,null,null,null,null,8.3999996185302734,8.5,null,null,8.5]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.6,null,0.6,null,0.6,null,0.6,null,null,null,null,0.6,null,0.4,null,0.4,null,null,null,null,null,0.4,0.4,null,null,0.4]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"13",null,"13",null,"13",null,"13",null,null,null,null,"13",null,"13",null,"13",null,null,null,null,null,"13","13",null,null,"13"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"MODA","index":160,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"MODA - Monduran Dam (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T020 - Bundaberg BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Wide Bay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1xMODA TX NO 2-66/11/3.3KV TRANSF 2(Standby);1xMODA TX NO 1-66/11/3.3KV TRANSF 1"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.0%, 2020 S 0.3% W 0.3%, 2021 S 0.1% W 0.1%, 2022 S 0.1% W 0.1%, 2023 S -0.2% W -0.2"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"0.3 MVA on 03/12/2018 at 18:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,1.5,null,1.5,null,1.5,null,1.5,null,null,null,null,1.5,null,1.5,null,1.5,null,null,null,null,null,1.5,1.5,null,null,1.5]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,0.30000001192092896,null,0.30000001192092896,null,0.30000001192092896,null,0.30000001192092896,null,null,null,null,0.30000001192092896,null,0.20000000298023224,null,0.20000000298023224,null,null,null,null,null,0.20000000298023224,0.20000000298023224,null,null,0.20000000298023224]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.998,null,0.998,null,0.998,null,0.998,null,null,null,null,0.998,null,0.997,null,0.997,null,null,null,null,null,0.997,0.997,null,null,0.997]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,0.30000001192092896,null,0.30000001192092896,null,0.30000001192092896,null,0.30000001192092896,null,null,null,null,0.30000001192092896,null,0.20000000298023224,null,0.20000000298023224,null,null,null,null,null,0.20000000298023224,0.20000000298023224,null,null,0.20000000298023224]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"4",null,"4",null,"4",null,"4",null,null,null,null,"4",null,"4",null,"4",null,null,null,null,null,"4","4",null,null,"4"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,0.3,null,0.3,null,0.3,null,0.3,null,null,null,null,0.3,null,0.2,null,0.2,null,null,null,null,null,0.2,0.2,null,null,0.2]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,1.5,null,1.5,null,1.5,null,1.5,null,null,null,null,1.5,null,1.5,null,1.5,null,null,null,null,null,1.5,1.5,null,null,1.5]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"MOFO","index":161,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"MOFO - Mount Fox (66/33kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T047 - Ingham BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Nth Queensland"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/11kV 0.63MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.6%, 2020 S -0.4% W -0.4%2021 S -0.4% W -0.4%2022 S -0.9% W -0.9%2023 S -1.0% W -1.0"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"0.1 MVA on 10/01/2019 at 23:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,0.69999998807907104,null,0.69999998807907104,null,0.69999998807907104,null,0.69999998807907104,null,null,null,null,0.69999998807907104,null,0.69999998807907104,null,0.69999998807907104,null,null,null,null,null,0.69999998807907104,0.69999998807907104,null,null,0.69999998807907104]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,0.10000000149011612,null,0.10000000149011612,null,0.10000000149011612,null,0.10000000149011612,null,null,null,null,0.10000000149011612,null,0.10000000149011612,null,0.10000000149011612,null,null,null,null,null,0.10000000149011612,0.10000000149011612,null,null,0.10000000149011612]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.86599999999999999,null,0.86599999999999999,null,0.86599999999999999,null,0.86599999999999999,null,null,null,null,0.86599999999999999,null,0.79600000000000004,null,0.79600000000000004,null,null,null,null,null,0.79600000000000004,0.79600000000000004,null,null,0.79600000000000004]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,0.10000000149011612,null,0.10000000149011612,null,0.10000000149011612,null,0.10000000149011612,null,null,null,null,0.10000000149011612,null,0.10000000149011612,null,0.10000000149011612,null,null,null,null,null,0.10000000149011612,0.10000000149011612,null,null,0.10000000149011612]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"1",null,"1",null,"1",null,"1",null,null,null,null,"1",null,"1",null,"1",null,null,null,null,null,"1","1",null,null,"1"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,0.1,null,0.1,null,0.1,null,0.1,null,null,null,null,0.1,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0.60000002384185791,null,0.60000002384185791,null,0.60000002384185791,null,0.60000002384185791,null,null,null,null,0.60000002384185791,null,0.60000002384185791,null,0.60000002384185791,null,null,null,null,null,0.60000002384185791,0.60000002384185791,null,null,0.60000002384185791]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"MOGA","index":162,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"MOGA - Mt Garnet (66/22kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T055 - Turkinje 66kV BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Far North"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/22kV 4MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -3.6%, 2020 S -2.8% W -2.8%2021 S -3.3% W -3.3%2022 S -3.5% W -3.5%2023 S -4.4% W -4.4"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"1.8 MVA on 08/08/2017 at 07:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,8,null,8,null,8,null,8,null,null,null,null,8,null,9.3000001907348633,null,9.3000001907348633,null,null,null,null,null,9.3000001907348633,9.3000001907348633,null,null,9.3000001907348633]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,1.6000000238418579,null,1.5,null,1.5,null,1.3999999761581421,null,null,null,null,1.2999999523162842,null,1.7999999523162842,null,1.7000000476837158,null,null,null,null,null,1.7000000476837158,1.6000000238418579,null,null,1.5]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.97899999999999998,null,0.98099999999999998,null,0.98099999999999998,null,0.97899999999999998,null,null,null,null,0.98099999999999998,null,0.98099999999999998,null,0.98099999999999998,null,null,null,null,null,0.98099999999999998,0.98099999999999998,null,null,0.98099999999999998]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,4.1999998092651367,null,4.1999998092651367,null,4.1999998092651367,null,4.1999998092651367,null,null,null,null,4.1999998092651367,null,4.6999998092651367,null,4.6999998092651367,null,null,null,null,null,4.6999998092651367,4.6999998092651367,null,null,4.6999998092651367]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,1.6000000238418579,null,1.5,null,1.3999999761581421,null,1.3999999761581421,null,null,null,null,1.2999999523162842,null,1.7999999523162842,null,1.7000000476837158,null,null,null,null,null,1.7000000476837158,1.6000000238418579,null,null,1.5]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.1,null,0.1,null,0.1,null,0.1,null,null,null,null,0.1,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"14.5",null,"14.5",null,"14.5",null,"14.5",null,null,null,null,"14.5",null,"14.5",null,"14.5",null,null,null,null,null,"14.5","14.5",null,null,"14.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"MOMO","index":163,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"MOMO - Mt Molloy (66/22kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T055 - Turkinje 66kV BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Far North"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/22kV 10/12.5MVA ONAN/ONAF;1x66/22kV 1.5MVA ONAN(Standby)"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.0%, 2020 S 0.6% W 0.6%, 2021 S 0.5% W 0.5%, 2022 S 0.2% W 0.2%, 2023 S -0.1% W -0.1"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"1.1 MVA on 26/11/2018 at 18:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,16.399999618530273,null,16.399999618530273,null,16.399999618530273,null,16.399999618530273,null,null,null,null,16.399999618530273,null,18,null,18,null,null,null,null,null,18,18,null,null,18]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,1.1000000238418579,null,1.1000000238418579,null,1.1000000238418579,null,1.1000000238418579,null,null,null,null,1.1000000238418579,null,1,null,1,null,null,null,null,null,1,1,null,null,1]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.99199999999999999,null,0.99199999999999999,null,0.99199999999999999,null,0.99199999999999999,null,null,null,null,0.99199999999999999,null,0.998,null,0.998,null,null,null,null,null,0.998,0.998,null,null,0.998]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,1.1000000238418579,null,1.1000000238418579,null,1,null,1,null,null,null,null,1.1000000238418579,null,1,null,1,null,null,null,null,null,1,1,null,null,1]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.1,null,0.1,null,0.1,null,0.1,null,null,null,null,0.1,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"16",null,"16",null,"16",null,"16",null,null,null,null,"16",null,"16",null,"16",null,null,null,null,null,"16","16",null,null,"16"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,1.1000000000000001,null,1.1000000000000001,null,1,null,1,null,null,null,null,1.1000000000000001,null,1,null,1,null,null,null,null,null,1,1,null,null,1]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,1.5,null,1.5,null,1.5,null,1.5,null,null,null,null,1.5,null,1.5,null,1.5,null,null,null,null,null,1.5,1.5,null,null,1.5]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"MOMR","index":164,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"MOMR - Mt Morgan (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"RMES - Rockhampton Mesh"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Capricornia"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/11kV 5/6.25MVA ONAN/ONAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.0%, 2020 S 0.2% W 0.2%, 2021 S 0.2% W 0.2%, 2022 S -0.2% W -0.2%2023 S -0.3% W -0.3"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"3.2 MVA on 13/02/2019 at 19:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,15.800000190734863,null,15.800000190734863,null,15.800000190734863,null,15.800000190734863,null,null,null,null,15.800000190734863,null,18,null,18,null,null,null,null,null,18,18,null,null,18]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,3.5,null,3.5,null,3.5,null,3.5,null,null,null,null,3.5,null,3,null,3,null,null,null,null,null,3,3,null,null,3]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.96299999999999997,null,0.96299999999999997,null,0.96299999999999997,null,0.96299999999999997,null,null,null,null,0.96299999999999997,null,0.98599999999999999,null,0.98599999999999999,null,null,null,null,null,0.98599999999999999,0.98599999999999999,null,null,0.98599999999999999]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,8.6999998092651367,null,8.6999998092651367,null,8.6999998092651367,null,8.6999998092651367,null,null,null,null,8.6999998092651367,null,9.3000001907348633,null,9.3000001907348633,null,null,null,null,null,9.3000001907348633,9.3000001907348633,null,null,9.3000001907348633]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,3.2000000476837158,null,3.2000000476837158,null,3.2000000476837158,null,3.2000000476837158,null,null,null,null,3.2000000476837158,null,2.7999999523162842,null,2.7999999523162842,null,null,null,null,null,2.7999999523162842,2.7999999523162842,null,null,2.7999999523162842]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.2,null,0.2,null,0.2,null,0.2,null,null,null,null,0.2,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"12",null,"12",null,"12",null,"12",null,null,null,null,"12",null,"12",null,"12",null,null,null,null,null,"12","12",null,null,"12"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"MOMW","index":165,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"MOMW - Mt Mowbullan (33/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T002 - Dalby East BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is South West"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x33/11kV 1MVA ON"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.5%, 2020 S -0.1% W -0.1%2021 S -0.2% W -0.2%2022 S 0.2% W 0.2%, 2023 S 0.1% W 0.1%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"0.7 MVA on 13/07/2018 at 19:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,1,null,1,null,1,null,1,null,null,null,null,1,null,1,null,1,null,null,null,null,null,1,1,null,null,1]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,0.5,null,0.5,null,0.5,null,0.5,null,null,null,null,0.5,null,0.80000001192092896,null,0.80000001192092896,null,null,null,null,null,0.69999998807907104,0.69999998807907104,null,null,0.80000001192092896]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.99199999999999999,null,0.99199999999999999,null,0.99199999999999999,null,0.99199999999999999,null,null,null,null,0.99199999999999999,null,0.99299999999999999,null,0.99299999999999999,null,null,null,null,null,0.99299999999999999,0.99299999999999999,null,null,0.99299999999999999]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,0.5,null,0.5,null,0.5,null,0.5,null,null,null,null,0.5,null,0.69999998807907104,null,0.69999998807907104,null,null,null,null,null,0.69999998807907104,0.69999998807907104,null,null,0.69999998807907104]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"3.5",null,"3.5",null,"3.5",null,"3.5",null,null,null,null,"3.5",null,"3.5",null,"3.5",null,null,null,null,null,"3.5","3.5",null,null,"3.5"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,0.5,null,0.5,null,0.5,null,0.5,null,null,null,null,0.5,null,0.7,null,0.7,null,null,null,null,null,0.7,0.7,null,null,0.7]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,1,null,1,null,1,null,1,null,null,null,null,1,null,1,null,1,null,null,null,null,null,1,1,null,null,1]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"MONT","index":166,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"MONT - Monto (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T026 - Biloela BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Capricornia"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/11kV 6.25MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.4%, 2020 S 0.0% W 0.0%, 2021 S -0.1% W -0.1%2022 S -0.5% W -0.5%2023 S -0.6% W -0.6"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"5.2 MVA on 10/02/2019 at 19:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,14,null,14,null,14,null,14,null,null,null,null,14,null,16.700000762939453,null,16.700000762939453,null,null,null,null,null,16.700000762939453,16.700000762939453,null,null,16.700000762939453]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,5.9000000953674316,null,5.9000000953674316,null,5.8000001907348633,null,5.8000001907348633,null,null,null,null,5.8000001907348633,null,4,null,4,null,null,null,null,null,4,3.9000000953674316,null,null,3.9000000953674316]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.99299999999999999,null,0.99299999999999999,null,0.99399999999999999,null,0.99399999999999999,null,null,null,null,0.99399999999999999,null,0.99299999999999999,null,0.99299999999999999,null,null,null,null,null,0.99299999999999999,0.99399999999999999,null,null,0.99399999999999999]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,8,null,8,null,8,null,8,null,null,null,null,8,null,9.3000001907348633,null,9.3000001907348633,null,null,null,null,null,9.3000001907348633,9.3000001907348633,null,null,9.3000001907348633]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,5.3000001907348633,null,5.1999998092651367,null,5.1999998092651367,null,5.0999999046325684,null,null,null,null,5.0999999046325684,null,3.7999999523162842,null,3.7999999523162842,null,null,null,null,null,3.7999999523162842,3.7000000476837158,null,null,3.7000000476837158]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.3,null,0.3,null,0.3,null,0.3,null,null,null,null,0.3,null,0.2,null,0.2,null,null,null,null,null,0.2,0.2,null,null,0.2]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"4.5",null,"4.5",null,"4.5",null,"4.5",null,null,null,null,"4.5",null,"4.5",null,"4.5",null,null,null,null,null,"4.5","4.5",null,null,"4.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"MOOR","index":167,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"MOOR - Moorvale (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T198 - Broadlea BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Mackay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/11kV 7.5/10MVA ON/OB"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -2.3%, 2020 S -0.8% W -0.8%2021 S -1.0% W -1.0%2022 S -0.5% W -0.5%2023 S -0.5% W -0.5"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"6.3 MVA on 03/12/2018 at 19:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,10.5,null,10.5,null,10.5,null,10.5,null,null,null,null,10.5,null,11,null,11,null,null,null,null,null,11,11,null,null,11]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,6.5999999046325684,null,6.5,null,6.4000000953674316,null,6.4000000953674316,null,null,null,null,6.4000000953674316,null,5,null,5,null,null,null,null,null,4.9000000953674316,4.9000000953674316,null,null,4.9000000953674316]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.97699999999999998,null,0.97699999999999998,null,0.97699999999999998,null,0.97699999999999998,null,null,null,null,0.97699999999999998,null,0.96699999999999997,null,0.96699999999999997,null,null,null,null,null,0.96699999999999997,0.96699999999999997,null,null,0.96699999999999997]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,6.4000000953674316,null,6.4000000953674316,null,6.3000001907348633,null,6.1999998092651367,null,null,null,null,6.3000001907348633,null,5,null,4.9000000953674316,null,null,null,null,null,4.9000000953674316,4.9000000953674316,null,null,4.8000001907348633]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.3,null,0.3,null,0.3,null,0.3,null,null,null,null,0.3,null,0.3,null,0.2,null,null,null,null,null,0.2,0.2,null,null,0.2]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"15",null,"15",null,"15",null,"15",null,null,null,null,"15",null,"15",null,"15",null,null,null,null,null,"15","15",null,null,"15"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,6.4,null,6.4,null,6.3,null,6.2,null,null,null,null,6.3,null,5,null,4.9000000000000004,null,null,null,null,null,4.9000000000000004,4.9000000000000004,null,null,4.8]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,11.5,null,11.5,null,11.5,null,11.5,null,null,null,null,11.5,null,11.5,null,11.5,null,null,null,null,null,11.5,11.5,null,null,11.5]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,3.0999999046325684,null,3.0999999046325684,null,3.0999999046325684,null,3.0999999046325684,null,null,null,null,3.0999999046325684,null,3.0999999046325684,null,3.0999999046325684,null,null,null,null,null,3.0999999046325684,3.0999999046325684,null,null,3.0999999046325684]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"MOPA","index":168,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"MOPA - Mona Park (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T193 - Clare South BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Nth Queensland"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/11kV 4MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.3%, 2020 S -0.0% W -0.0%2021 S -0.2% W -0.2%2022 S -0.3% W -0.3%2023 S -0.5% W -0.5"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"5.8 MVA on 02/01/2019 at 18:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,7.5999999046325684,null,7.5999999046325684,null,7.5999999046325684,null,7.5999999046325684,null,null,null,null,7.5999999046325684,null,8,null,8,null,null,null,null,null,8,8,null,null,8]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,6.1999998092651367,null,6.1999998092651367,null,6.0999999046325684,null,6.0999999046325684,null,null,null,null,6.0999999046325684,null,3.7000000476837158,null,3.5999999046325684,null,null,null,null,null,3.5999999046325684,3.5999999046325684,null,null,3.5999999046325684]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.84,null,0.84,null,0.84,null,0.84,null,null,null,null,0.84,null,0.84099999999999997,null,0.83399999999999996,null,null,null,null,null,0.83399999999999996,0.83399999999999996,null,null,0.83399999999999996]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,4,null,4,null,4,null,4,null,null,null,null,4,null,4,null,4,null,null,null,null,null,4,4,null,null,4]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,6.0999999046325684,null,6,null,6,null,5.9000000953674316,null,null,null,null,5.9000000953674316,null,3.7000000476837158,null,3.5999999046325684,null,null,null,null,null,3.5999999046325684,3.5999999046325684,null,null,3.5999999046325684]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.3,null,0.3,null,0.3,null,0.3,null,null,null,null,0.3,null,0.2,null,0.2,null,null,null,null,null,0.2,0.2,null,null,0.2]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"34",null,"34",null,"34",null,"34",null,null,null,null,"34",null,"34",null,"34",null,null,null,null,null,"34","34",null,null,"34"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,2.1,null,2,null,2,null,1.9,null,null,null,null,1.9]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,2.2999999523162842,null,2.2999999523162842,null,2.2999999523162842,null,2.2999999523162842,null,null,null,null,2.2999999523162842,null,2.2999999523162842,null,2.2999999523162842,null,null,null,null,null,2.2999999523162842,2.2999999523162842,null,null,2.2999999523162842]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0.80000001192092896,null,0.80000001192092896,null,0.80000001192092896,null,0.80000001192092896,null,null,null,null,0.80000001192092896,null,0.80000001192092896,null,0.80000001192092896,null,null,null,null,null,0.80000001192092896,0.80000001192092896,null,null,0.80000001192092896]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"MORA","index":169,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"MORA - Moranbah Town (132/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"QMRL - Moranbah 11kV TCP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Mackay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x20 MVA;1x20MVA"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 19.3 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -8.1%, 2020 S 0.4% W 0.4%, 2021 S -0.9% W -0.9%2022 S 0.8% W 0.8%, 2023 S 0.2% W 0.2%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"16.2 MVA on 07/11/2018 at 19:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,40,null,40,null,40,null,40,null,null,null,null,40,null,40,null,40,null,null,null,null,null,40,40,null,null,40]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,3.9000000953674316,null,3.9000000953674316,null,3.9000000953674316,null,3.9000000953674316,null,null,null,null,3.9000000953674316,null,4.9000000953674316,null,4.9000000953674316,null,null,null,null,null,4.9000000953674316,4.9000000953674316,null,null,4.9000000953674316]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,15.100000381469727,null,14.899999618530273,null,14.899999618530273,null,15,null,null,null,null,15.5,null,6.6999998092651367,null,6.6999998092651367,null,null,null,null,null,6.5999999046325684,6.6999998092651367,null,null,6.6999998092651367]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,1,null,1,null,1,null,1,null,null,null,null,1,null,0.997,null,0.997,null,null,null,null,null,0.997,0.997,null,null,0.997]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,20,null,20,null,20,null,20,null,null,null,null,20,null,20,null,20,null,null,null,null,null,20,20,null,null,20]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,13.699999809265137,null,13.5,null,13.5,null,13.5,null,null,null,null,14,null,6.3000001907348633,null,6.3000001907348633,null,null,null,null,null,6.1999998092651367,6.3000001907348633,null,null,6.3000001907348633]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.7,null,0.7,null,0.7,null,0.7,null,null,null,null,0.7,null,0.3,null,0.3,null,null,null,null,null,0.3,0.3,null,null,0.3]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"12",null,"12",null,"12",null,"12",null,null,null,null,"12",null,"12",null,"12",null,null,null,null,null,"12","12",null,null,"12"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,6,null,6,null,6,null,6,null,null,null,null,6,null,6,null,6,null,null,null,null,null,6,6,null,null,6]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,4,null,4,null,4,null,4,null,null,null,null,4,null,4,null,4,null,null,null,null,null,4,4,null,null,4]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"MORO","index":170,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"MORO - Mount Rooper (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T039 - Proserpine BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Mackay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/11kV 5MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.1%, 2020 S 0.6% W 0.6%, 2021 S 0.6% W 0.6%, 2022 S 0.5% W 0.5%, 2023 S 0.1% W 0.1%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"0.7 MVA on 21/03/2019 at 08:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,5.8000001907348633,null,5.8000001907348633,null,5.8000001907348633,null,5.8000001907348633,null,null,null,null,5.8000001907348633,null,6.4000000953674316,null,6.4000000953674316,null,null,null,null,null,6.4000000953674316,6.4000000953674316,null,null,6.4000000953674316]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,0.80000001192092896,null,0.80000001192092896,null,0.80000001192092896,null,0.80000001192092896,null,null,null,null,0.80000001192092896,null,0.30000001192092896,null,0.30000001192092896,null,null,null,null,null,0.30000001192092896,0.30000001192092896,null,null,0.30000001192092896]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.94899999999999995,null,0.94899999999999995,null,0.94899999999999995,null,0.94899999999999995,null,null,null,null,0.94899999999999995,null,0.94899999999999995,null,0.94899999999999995,null,null,null,null,null,0.94899999999999995,0.94899999999999995,null,null,0.94899999999999995]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,0.80000001192092896,null,0.80000001192092896,null,0.80000001192092896,null,0.80000001192092896,null,null,null,null,0.80000001192092896,null,0.30000001192092896,null,0.30000001192092896,null,null,null,null,null,0.30000001192092896,0.30000001192092896,null,null,0.30000001192092896]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"67",null,"67",null,"67",null,"67",null,null,null,null,"67",null,"67",null,"67",null,null,null,null,null,"67","67",null,null,"67"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,0.8,null,0.8,null,0.8,null,0.8,null,null,null,null,0.8,null,0.3,null,0.3,null,null,null,null,null,0.3,0.3,null,null,0.3]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0.5,null,0.5,null,0.5,null,0.5,null,null,null,null,0.5,null,0.5,null,0.5,null,null,null,null,null,0.5,0.5,null,null,0.5]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,1.1000000238418579,null,1.1000000238418579,null,1.1000000238418579,null,1.1000000238418579,null,null,null,null,1.1000000238418579,null,1.1000000238418579,null,1.1000000238418579,null,null,null,null,null,1.1000000238418579,1.1000000238418579,null,null,1.1000000238418579]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"MOSI","index":171,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"MOSI - Mt Sibley (33/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T043 - South Toowoomba BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is South West"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x33/11kV 3MVA ON;1x33/11KV 5MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.3%, 2020 S 0.5% W 0.5%, 2021 S 0.5% W 0.5%, 2022 S 0.2% W 0.2%, 2023 S 0.0% W 0.0%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"5.3 MVA on 19/02/2019 at 18:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,6.3000001907348633,null,6.3000001907348633,null,6.3000001907348633,null,6.3000001907348633,null,null,null,null,6.3000001907348633,null,6.3000001907348633,null,6.3000001907348633,null,null,null,null,null,6.3000001907348633,6.3000001907348633,null,null,6.3000001907348633]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,5.5999999046325684,null,5.5999999046325684,null,5.5,null,5.5,null,null,null,null,5.5999999046325684,null,4.4000000953674316,null,4.5,null,null,null,null,null,4.5,4.5,null,null,4.5]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.90700000000000003,null,0.90700000000000003,null,0.90700000000000003,null,0.90700000000000003,null,null,null,null,0.90700000000000003,null,0.92400000000000004,null,0.92400000000000004,null,null,null,null,null,0.92400000000000004,0.92400000000000004,null,null,0.92400000000000004]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,3.2999999523162842,null,3.2999999523162842,null,3.2999999523162842,null,3.2999999523162842,null,null,null,null,3.2999999523162842,null,3.5,null,3.5,null,null,null,null,null,3.5,3.5,null,null,3.5]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,4.9000000953674316,null,4.9000000953674316,null,4.8000001907348633,null,4.9000000953674316,null,null,null,null,4.9000000953674316,null,4.0999999046325684,null,4.1999998092651367,null,null,null,null,null,4.1999998092651367,4.1999998092651367,null,null,4.1999998092651367]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.2,null,0.2,null,0.2,null,0.2,null,null,null,null,0.2,null,0.2,null,0.2,null,null,null,null,null,0.2,0.2,null,null,0.2]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"27.5",null,"27.5",null,"27.5",null,"27.5",null,null,null,null,"27.5",null,"27.5",null,"27.5",null,null,null,null,null,"27.5","27.5",null,null,"27.5"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,1.6,null,1.6,null,1.5,null,1.6,null,null,null,null,1.6,null,0.6,null,0.7,null,null,null,null,null,0.7,0.7,null,null,0.7]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0.30000001192092896,null,0.80000001192092896,null,0.80000001192092896,null,0.80000001192092896,null,null,null,null,0.80000001192092896,null,0.30000001192092896,null,0.80000001192092896,null,null,null,null,null,0.80000001192092896,0.80000001192092896,null,null,0.80000001192092896]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,1,null,1,null,1,null,1,null,null,null,null,1,null,1,null,1,null,null,null,null,null,1,1,null,null,1]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)",null,null,null,null,null,0.30000001192092896]
[null,null,null,null,"LARc (MW)",null,null,null,null,null,0.3]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"No",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"MOSK","index":172,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"MOSK - Moranbah Skid J (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T034 - Moranbah BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Mackay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1xSKID Transformer"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.0%, 2020 S 0.0% W 0.0%, 2021 S 0.0% W 0.0%, 2022 S 0.0% W 0.0%, 2023 S 0.0% W 0.0%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"7.6 MVA on 28/11/2018 at 19:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,10,null,10,null,10,null,10,null,null,null,null,10,null,10,null,10,null,null,null,null,null,10,10,null,null,10]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,9.6000003814697266,null,9.6000003814697266,null,9.5,null,9.5,null,null,null,null,9.5,null,4.5999999046325684,null,4.5999999046325684,null,null,null,null,null,4.5999999046325684,4.5999999046325684,null,null,4.5999999046325684]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.97699999999999998,null,0.97699999999999998,null,0.97699999999999998,null,0.97699999999999998,null,null,null,null,0.97699999999999998,null,0.95699999999999996,null,0.95699999999999996,null,null,null,null,null,0.95699999999999996,0.95699999999999996,null,null,0.95699999999999996]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,8.1000003814697266,null,8,null,8,null,8,null,null,null,null,8,null,4.1999998092651367,null,4.1999998092651367,null,null,null,null,null,4.1999998092651367,4.1999998092651367,null,null,4.1999998092651367]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.4,null,0.4,null,0.4,null,0.4,null,null,null,null,0.4,null,0.2,null,0.2,null,null,null,null,null,0.2,0.2,null,null,0.2]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"7",null,"7",null,"7",null,"7",null,null,null,null,"7",null,"7",null,"7",null,null,null,null,null,"7","7",null,null,"7"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,8.1,null,8,null,8,null,8,null,null,null,null,8,null,4.2,null,4.2,null,null,null,null,null,4.2,4.2,null,null,4.2]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,6,null,6,null,6,null,6,null,null,null,null,6,null,6,null,6,null,null,null,null,null,6,6,null,null,6]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,4,null,4,null,4,null,4,null,null,null,null,4,null,4,null,4,null,null,null,null,null,4,4,null,null,4]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"MOSS","index":173,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"MOSS - Mossman (66/22kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T055 - Turkinje 66kV BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Far North"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/22kV 10MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 11.3 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.1%, 2020 S 0.3% W 0.3%, 2021 S 0.3% W 0.3%, 2022 S 0.1% W 0.1%, 2023 S -0.1% W -0.1"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"8 MVA on 26/11/2018 at 16:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,18.5,null,18.5,null,18.5,null,18.5,null,null,null,null,18.5,null,20.600000381469727,null,20.600000381469727,null,null,null,null,null,20.600000381469727,20.600000381469727,null,null,20.600000381469727]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,8.6000003814697266,null,8.6000003814697266,null,8.5,null,8.5,null,null,null,null,8.6000003814697266,null,7.1999998092651367,null,7.1999998092651367,null,null,null,null,null,7.1999998092651367,7.1999998092651367,null,null,7.1999998092651367]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.98499999999999999,null,0.98499999999999999,null,0.98499999999999999,null,0.98499999999999999,null,null,null,null,0.98499999999999999,null,0.98199999999999998,null,0.98199999999999998,null,null,null,null,null,0.98199999999999998,0.98199999999999998,null,null,0.98199999999999998]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,9.3000001907348633,null,9.3000001907348633,null,9.3000001907348633,null,9.3000001907348633,null,null,null,null,9.3000001907348633,null,10.300000190734863,null,10.300000190734863,null,null,null,null,null,10.300000190734863,10.300000190734863,null,null,10.300000190734863]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,7.9000000953674316,null,7.9000000953674316,null,7.8000001907348633,null,7.8000001907348633,null,null,null,null,7.9000000953674316,null,6.6999998092651367,null,6.6999998092651367,null,null,null,null,null,6.6999998092651367,6.6999998092651367,null,null,6.8000001907348633]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.4,null,0.4,null,0.4,null,0.4,null,null,null,null,0.4,null,0.3,null,0.3,null,null,null,null,null,0.3,0.3,null,null,0.3]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"21",null,"21",null,"21",null,"21",null,null,null,null,"21",null,"21",null,"21",null,null,null,null,null,"21","21",null,null,"21"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"MOUR","index":174,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,13],[15,16,15,27],[18,19,19,32],[19,3,20,13],[19,16,20,17],[23,4,24,10],[23,11,23,22],[23,23,23,35],[24,11,24,12],[24,13,24,14],[24,15,24,16],[24,17,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,10],[25,11,25,12],[25,13,25,14],[25,15,25,16],[25,17,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,10],[26,11,26,12],[26,13,26,14],[26,15,26,16],[26,17,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,10],[27,11,27,12],[27,13,27,14],[27,15,27,16],[27,17,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,10],[28,11,28,12],[28,13,28,14],[28,15,28,16],[28,17,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,10],[29,11,29,12],[29,13,29,14],[29,15,29,16],[29,17,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,10],[30,11,30,12],[30,13,30,14],[30,15,30,16],[30,17,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,10],[31,11,31,12],[31,13,31,14],[31,15,31,16],[31,17,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,10],[32,11,32,12],[32,13,32,14],[32,15,32,16],[32,17,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,10],[33,11,33,12],[33,13,33,14],[33,15,33,16],[33,17,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,10],[34,11,34,12],[34,13,34,14],[34,15,34,16],[34,17,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,10],[35,11,35,12],[35,13,35,14],[35,15,35,16],[35,17,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,10],[36,11,36,12],[36,13,36,14],[36,15,36,16],[36,17,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,10],[37,11,37,12],[37,13,37,14],[37,15,37,16],[37,17,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,10],[38,11,38,12],[38,13,38,14],[38,15,38,16],[38,17,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,10],[39,11,39,12],[39,13,39,14],[39,15,39,16],[39,17,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,10],[40,11,40,12],[40,13,40,14],[40,15,40,16],[40,17,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,10],[42,11,42,12],[42,13,42,14],[42,15,42,16],[42,17,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,10],[41,11,41,12],[41,13,41,14],[41,15,41,16],[41,17,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,11,44,12],[44,13,44,14],[44,15,44,16],[44,17,44,20],[43,11,43,12],[43,13,43,14],[43,15,43,16],[43,17,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,10],[45,11,45,12],[45,13,45,14],[45,15,45,16],[45,17,45,20],[45,21,45,22],[44,4,44,10],[43,32,43,34],[43,4,43,10]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"MOUR - Moura (66/22kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T027 - Moura BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Capricornia"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x7.5/10 MVA ONAN/ONAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -1.0%, 2020 S -0.5% W -0.5%2021 S -0.6% W -0.6%2022 S -0.5% W -0.5%2023 S -0.7% W -0.7"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,null,"8 MVA on 11/03/2019 at 19:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,null,20,null,20,null,20,null,20,null,null,null,20,null,20,null,20,null,null,null,null,null,20,20,null,null,20]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,null,8.5,null,8.3999996185302734,null,8.3000001907348633,null,8.3000001907348633,null,null,null,8.3000001907348633,null,7,null,7,null,null,null,null,null,6.9000000953674316,6.8000001907348633,null,null,6.8000001907348633]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,null,0.97599999999999998,null,0.97599999999999998,null,0.97599999999999998,null,0.97599999999999998,null,null,null,0.97599999999999998,null,0.98699999999999999,null,0.98699999999999999,null,null,null,null,null,0.98699999999999999,0.98699999999999999,null,null,0.98699999999999999]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,null,10,null,10,null,10,null,10,null,null,null,10,null,10,null,10,null,null,null,null,null,10,10,null,null,10]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,null,8.3000001907348633,null,8.1999998092651367,null,8.1000003814697266,null,8.1000003814697266,null,null,null,8.1000003814697266,null,6.3000001907348633,null,6.3000001907348633,null,null,null,null,null,6.1999998092651367,6.1999998092651367,null,null,6.1999998092651367]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,null,0.4,null,0.4,null,0.4,null,0.4,null,null,null,0.4,null,0.3,null,0.3,null,null,null,null,null,0.3,0.3,null,null,0.3]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,null,"6.5",null,"6.5",null,"6.5",null,"6.5",null,null,null,"6.5",null,"6.5",null,"6.5",null,null,null,null,null,"6.5","6.5",null,null,"6.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"MUND","index":175,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"MUND - Mundubbera Town (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T131 - Isis BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Wide Bay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/11kV 16/20MVA ONAN/ONAF;1xMUTO 66/11kV TRANSF 2 TX02T01"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.7%, 2020 S -0.1% W -0.1%2021 S -0.3% W -0.3%2022 S -0.5% W -0.5%2023 S -0.8% W -0.8"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"7 MVA on 12/03/2019 at 13:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,49.400001525878906,null,49.400001525878906,null,49.400001525878906,null,49.400001525878906,null,null,null,null,49.400001525878906,null,54.599998474121094,null,54.599998474121094,null,null,null,null,null,54.599998474121094,54.599998474121094,null,null,54.599998474121094]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,6.9000000953674316,null,6.8000001907348633,null,6.6999998092651367,null,6.5999999046325684,null,null,null,null,6.5999999046325684,null,5.0999999046325684,null,5.0999999046325684,null,null,null,null,null,5.0999999046325684,5.0999999046325684,null,null,5.5999999046325684]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.997,null,0.998,null,0.998,null,0.997,null,null,null,null,0.997,null,1,null,1,null,null,null,null,null,1,1,null,null,0.89600000000000002]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,28.399999618530273,null,28.399999618530273,null,28.399999618530273,null,28.399999618530273,null,null,null,null,28.399999618530273,null,29.899999618530273,null,29.899999618530273,null,null,null,null,null,29.899999618530273,29.899999618530273,null,null,29.899999618530273]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,6.3000001907348633,null,6.3000001907348633,null,6.1999998092651367,null,6.0999999046325684,null,null,null,null,6.0999999046325684,null,5.4000000953674316,null,5.4000000953674316,null,null,null,null,null,5.3000001907348633,5.3000001907348633,null,null,5.3000001907348633]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.3,null,0.3,null,0.3,null,0.3,null,null,null,null,0.3,null,0.3,null,0.3,null,null,null,null,null,0.3,0.3,null,null,0.3]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"6",null,"6",null,"6",null,"6",null,null,null,null,"6",null,"6",null,"6",null,null,null,null,null,"6","6",null,null,"6"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"MURG","index":176,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"MURG - Murgon (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T012 - Kilkivan BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Wide Bay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/11kV 8.5/12.5MVA ONAN/ONAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -1.5%, 2020 S 0.1% W 0.1%, 2021 S 0.0% W 0.0%, 2022 S -0.1% W -0.1%2023 S -0.3% W -0.3"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"12.8 MVA on 13/02/2019 at 18:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,29.600000381469727,null,29.600000381469727,null,29.600000381469727,null,29.600000381469727,null,null,null,null,29.600000381469727,null,35.400001525878906,null,35.400001525878906,null,null,null,null,null,35.400001525878906,35.400001525878906,null,null,35.400001525878906]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,15.600000381469727,null,15.600000381469727,null,15.399999618530273,null,15.399999618530273,null,null,null,null,15.399999618530273,null,12.199999809265137,null,12.199999809265137,null,null,null,null,null,12.100000381469727,12.100000381469727,null,null,12.100000381469727]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.92900000000000005,null,0.92900000000000005,null,0.92900000000000005,null,0.92900000000000005,null,null,null,null,0.92900000000000005,null,0.96199999999999997,null,0.96199999999999997,null,null,null,null,null,0.96199999999999997,0.96199999999999997,null,null,0.96199999999999997]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,17,null,17,null,17,null,17,null,null,null,null,17,null,18.700000762939453,null,18.700000762939453,null,null,null,null,null,18.700000762939453,18.700000762939453,null,null,18.700000762939453]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,14,null,13.899999618530273,null,13.800000190734863,null,13.800000190734863,null,null,null,null,13.800000190734863,null,11.5,null,11.5,null,null,null,null,null,11.5,11.5,null,null,11.5]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.7,null,0.7,null,0.7,null,0.7,null,null,null,null,0.7,null,0.6,null,0.6,null,null,null,null,null,0.6,0.6,null,null,0.6]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"10",null,"10",null,"10",null,"10",null,null,null,null,"10",null,"10",null,"10",null,null,null,null,null,"10","10",null,null,"10"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"MUTA","index":177,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"MUTA - Mutarnee (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T047 - Ingham BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Nth Queensland"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/11kV 1MVA ON"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -1.8%, 2020 S -0.5% W -0.5%2021 S 0.8% W 0.8%, 2022 S 0.0% W 0.0%, 2023 S -0.1% W -0.1"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"0.4 MVA on 01/12/2018 at 18:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,1.1000000238418579,null,1.1000000238418579,null,1.1000000238418579,null,1.1000000238418579,null,null,null,null,1.1000000238418579,null,1.1000000238418579,null,1.1000000238418579,null,null,null,null,null,1.1000000238418579,1.1000000238418579,null,null,1.1000000238418579]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,0.40000000596046448,null,0.40000000596046448,null,0.40000000596046448,null,0.40000000596046448,null,null,null,null,0.40000000596046448,null,0.30000001192092896,null,0.30000001192092896,null,null,null,null,null,0.30000001192092896,0.30000001192092896,null,null,0.30000001192092896]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.96,null,0.96,null,0.96,null,0.96,null,null,null,null,0.96,null,0.97,null,0.97,null,null,null,null,null,0.97,0.97,null,null,0.97]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,0.40000000596046448,null,0.40000000596046448,null,0.40000000596046448,null,0.40000000596046448,null,null,null,null,0.40000000596046448,null,0.30000001192092896,null,0.30000001192092896,null,null,null,null,null,0.30000001192092896,0.30000001192092896,null,null,0.30000001192092896]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"29",null,"29",null,"29",null,"29",null,null,null,null,"29",null,"29",null,"29",null,null,null,null,null,"29","29",null,null,"29"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,0.4,null,0.4,null,0.4,null,0.4,null,null,null,null,0.4,null,0.3,null,0.3,null,null,null,null,null,0.3,0.3,null,null,0.3]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,1,null,1,null,1,null,1,null,null,null,null,1,null,1,null,1,null,null,null,null,null,1,1,null,null,1]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"NANA","index":178,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"NANA - Nanango (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"H018 - Tarong BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Wide Bay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/11kV 5/6.25MVA ONAN/ONAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -1.7%, 2020 S -0.5% W -0.5%2021 S -0.6% W -0.6%2022 S 0.3% W 0.3%, 2023 S -0.3% W -0.3"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"7.1 MVA on 13/02/2019 at 18:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,13.699999809265137,null,13.699999809265137,null,13.699999809265137,null,13.699999809265137,null,null,null,null,13.699999809265137,null,15.600000381469727,null,15.600000381469727,null,null,null,null,null,15.600000381469727,15.600000381469727,null,null,15.600000381469727]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,7.9000000953674316,null,7.8000001907348633,null,7.8000001907348633,null,7.8000001907348633,null,null,null,null,7.8000001907348633,null,6.6999998092651367,null,6.6999998092651367,null,null,null,null,null,6.5999999046325684,6.5999999046325684,null,null,6.5999999046325684]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.96599999999999997,null,0.96599999999999997,null,0.96599999999999997,null,0.96599999999999997,null,null,null,null,0.96599999999999997,null,0.97799999999999998,null,0.97799999999999998,null,null,null,null,null,0.97799999999999998,0.97799999999999998,null,null,0.97799999999999998]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,6.8000001907348633,null,6.8000001907348633,null,6.8000001907348633,null,6.8000001907348633,null,null,null,null,6.8000001907348633,null,7.8000001907348633,null,7.8000001907348633,null,null,null,null,null,7.8000001907348633,7.8000001907348633,null,null,7.8000001907348633]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,7.0999999046325684,null,7.0999999046325684,null,7,null,7,null,null,null,null,7.0999999046325684,null,6.3000001907348633,null,6.3000001907348633,null,null,null,null,null,6.1999998092651367,6.1999998092651367,null,null,6.1999998092651367]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.4,null,0.4,null,0.4,null,0.4,null,null,null,null,0.4,null,0.3,null,0.3,null,null,null,null,null,0.3,0.3,null,null,0.3]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"13.5",null,"13.5",null,"13.5",null,"13.5",null,null,null,null,"13.5",null,"13.5",null,"13.5",null,null,null,null,null,"13.5","13.5",null,null,"13.5"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,0.3,null,0.3,null,0.2,null,0.2,null,null,null,null,0.3]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0.80000001192092896,null,0.80000001192092896,null,0.80000001192092896,null,0.80000001192092896,null,null,null,null,0.80000001192092896,null,0.80000001192092896,null,0.80000001192092896,null,null,null,null,null,0.80000001192092896,0.80000001192092896,null,null,0.80000001192092896]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"NAND","index":179,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"NAND - Nandi (33/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T002 - Dalby East BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is South West"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x33/11 3.15MVA ON;1x33/11kV 1MVA ON"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -1.3%, 2020 S 0.0% W 0.0%, 2021 S -0.1% W -0.1%2022 S -0.0% W -0.0%2023 S -0.3% W -0.3"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"1.4 MVA on 31/01/2019 at 18:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,2,null,2,null,2,null,2,null,null,null,null,2,null,2,null,2,null,null,null,null,null,2,2,null,null,2]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,1.5,null,1.5,null,1.5,null,1.5,null,null,null,null,1.5,null,1,null,1,null,null,null,null,null,1,1,null,null,1]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.89,null,0.89,null,0.89,null,0.89,null,null,null,null,0.89,null,0.90800000000000003,null,0.90800000000000003,null,null,null,null,null,0.90800000000000003,0.90800000000000003,null,null,0.90800000000000003]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,1.1000000238418579,null,1.1000000238418579,null,1.1000000238418579,null,1.1000000238418579,null,null,null,null,1.1000000238418579,null,1.1000000238418579,null,1.1000000238418579,null,null,null,null,null,1.1000000238418579,1.1000000238418579,null,null,1.1000000238418579]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,1.5,null,1.5,null,1.5,null,1.5,null,null,null,null,1.5,null,1,null,1,null,null,null,null,null,1,1,null,null,1]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.1,null,0.1,null,0.1,null,0.1,null,null,null,null,0.1,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"4",null,"4",null,"4",null,"4",null,null,null,null,"4",null,"4",null,"4",null,null,null,null,null,"4","4",null,null,"4"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,0.4,null,0.4,null,0.4,null,0.4,null,null,null,null,0.4]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,1,null,1,null,1,null,1,null,null,null,null,1,null,1,null,1,null,null,null,null,null,1,1,null,null,1]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"NEBO","index":180,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"NEBO - Nebo (132/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"QNEB - Nebo TCP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Mackay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1xNEBOSS 3T 132/11KV TRANSF 3 3T;1xNEBOSS TRANSF 4"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -1.9%, 2020 S -1.0% W -1.0%2021 S -1.1% W -1.1%2022 S -0.4% W -0.4%2023 S -0.5% W -0.5"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"3.5 MVA on 28/11/2018 at 19:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,10,null,10,null,10,null,10,null,null,null,null,10,null,10,null,10,null,null,null,null,null,10,10,null,null,10]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,3.5,null,3.5,null,3.4000000953674316,null,3.4000000953674316,null,null,null,null,3.4000000953674316,null,2.5999999046325684,null,2.5,null,null,null,null,null,2.5,2.5,null,null,2.5]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.98,null,0.98,null,0.98,null,0.98,null,null,null,null,0.98,null,0.99099999999999999,null,0.99099999999999999,null,null,null,null,null,0.99099999999999999,0.99099999999999999,null,null,0.99099999999999999]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,5,null,5,null,5,null,5,null,null,null,null,5,null,5,null,5,null,null,null,null,null,5,5,null,null,5]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,3.2000000476837158,null,3.2000000476837158,null,3.0999999046325684,null,3.0999999046325684,null,null,null,null,3.0999999046325684,null,2.4000000953674316,null,2.4000000953674316,null,null,null,null,null,2.2999999523162842,2.2999999523162842,null,null,2.2999999523162842]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.2,null,0.2,null,0.2,null,0.2,null,null,null,null,0.2,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"4.5",null,"4.5",null,"4.5",null,"4.5",null,null,null,null,"4.5",null,"4.5",null,"4.5",null,null,null,null,null,"4.5","4.5",null,null,"4.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"NESM","index":181,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"NESM - Neil Smith (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"TMES - Townsville Mesh"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Nth Queensland"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/11kV 15/20/25MVA ON/OB/OFB"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.2%, 2020 S 0.2% W 0.2%, 2021 S 0.1% W 0.1%, 2022 S -0.0% W -0.0%2023 S -0.2% W -0.2"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"16.6 MVA on 20/02/2019 at 16:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,65.5,null,65.5,null,65.5,null,65.5,null,null,null,null,65.5,null,68,null,68,null,null,null,null,null,68,68,null,null,68]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,17.200000762939453,null,17.100000381469727,null,16.899999618530273,null,16.899999618530273,null,null,null,null,17,null,9.6000003814697266,null,9.6000003814697266,null,null,null,null,null,9.6000003814697266,9.6000003814697266,null,null,9.6000003814697266]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.97899999999999998,null,0.97899999999999998,null,0.97899999999999998,null,0.97899999999999998,null,null,null,null,0.97899999999999998,null,0.99299999999999999,null,0.99299999999999999,null,null,null,null,null,0.99299999999999999,0.99299999999999999,null,null,0.99299999999999999]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,36.799999237060547,null,36.799999237060547,null,36.799999237060547,null,36.799999237060547,null,null,null,null,36.799999237060547,null,37.400001525878906,null,37.400001525878906,null,null,null,null,null,37.400001525878906,37.400001525878906,null,null,37.400001525878906]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,15.899999618530273,null,15.800000190734863,null,15.699999809265137,null,15.600000381469727,null,null,null,null,15.699999809265137,null,9.3000001907348633,null,9.3000001907348633,null,null,null,null,null,9.3000001907348633,9.3000001907348633,null,null,9.3000001907348633]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.8,null,0.8,null,0.8,null,0.8,null,null,null,null,0.8,null,0.5,null,0.5,null,null,null,null,null,0.5,0.5,null,null,0.5]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"21",null,"21",null,"21",null,"21",null,null,null,null,"21",null,"21",null,"21",null,null,null,null,null,"21","21",null,null,"21"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"NOCL","index":182,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"NOCL - North Cloncurry (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"CHUM - Chumvale BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Nth Queensland"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/11kV 5/6.5MVA ONAN/ONAF;1x66/11kV 6.5/5MVA ONAF/ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.9%, 2020 S -0.3% W -0.3%2021 S -0.5% W -0.5%2022 S -0.6% W -0.6%2023 S -1.0% W -1.0"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"3.6 MVA on 02/12/2018 at 18:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,10,null,10,null,10,null,10,null,null,null,null,10,null,13.100000381469727,null,13.100000381469727,null,null,null,null,null,13.100000381469727,13.100000381469727,null,null,13.100000381469727]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,4.3000001907348633,null,4.3000001907348633,null,4.1999998092651367,null,4.1999998092651367,null,null,null,null,4.1999998092651367,null,2.0999999046325684,null,2.0999999046325684,null,null,null,null,null,2.0999999046325684,2,null,null,2]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.99099999999999999,null,0.99099999999999999,null,0.99099999999999999,null,0.99099999999999999,null,null,null,null,0.99099999999999999,null,0.99099999999999999,null,0.99099999999999999,null,null,null,null,null,0.99099999999999999,0.99099999999999999,null,null,0.99099999999999999]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,6.1999998092651367,null,6.1999998092651367,null,6.1999998092651367,null,6.1999998092651367,null,null,null,null,6.1999998092651367,null,7.1999998092651367,null,7.1999998092651367,null,null,null,null,null,7.1999998092651367,7.1999998092651367,null,null,7.1999998092651367]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,4,null,3.9000000953674316,null,3.9000000953674316,null,3.7999999523162842,null,null,null,null,3.7999999523162842,null,2,null,2,null,null,null,null,null,1.8999999761581421,1.8999999761581421,null,null,1.8999999761581421]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.2,null,0.2,null,0.2,null,0.2,null,null,null,null,0.2,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"19",null,"19",null,"19",null,"19",null,null,null,null,"19",null,"19",null,"19",null,null,null,null,null,"19","19",null,null,"19"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0.30000001192092896,null,0.30000001192092896,null,0.30000001192092896,null,0.30000001192092896,null,null,null,null,0.30000001192092896,null,0.30000001192092896,null,0.30000001192092896,null,null,null,null,null,0.30000001192092896,0.30000001192092896,null,null,0.30000001192092896]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"NOMA","index":183,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"NOMA - North Mackay (33/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"GZSA - Glenella ZS Accumulator"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Mackay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x33/11kV 15/20MVA ONAN/ONAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.3%, 2020 S 0.5% W 0.5%, 2021 S 0.5% W 0.5%, 2022 S 0.6% W 0.6%, 2023 S 0.4% W 0.4%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"23.1 MVA on 28/11/2018 at 19:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,47.700000762939453,null,47.700000762939453,null,47.700000762939453,null,47.700000762939453,null,null,null,null,47.700000762939453,null,53.099998474121094,null,53.099998474121094,null,null,null,null,null,53.099998474121094,53.099998474121094,null,null,53.099998474121094]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,25.5,null,25.5,null,25.399999618530273,null,25.5,null,null,null,null,25.799999237060547,null,16.700000762939453,null,16.700000762939453,null,null,null,null,null,16.799999237060547,16.799999237060547,null,null,17]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.999,null,0.999,null,0.999,null,0.999,null,null,null,null,0.999,null,0.99399999999999999,null,0.99399999999999999,null,null,null,null,null,0.99399999999999999,0.99399999999999999,null,null,0.99399999999999999]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,26.899999618530273,null,26.899999618530273,null,26.899999618530273,null,26.899999618530273,null,null,null,null,26.899999618530273,null,29.100000381469727,null,29.100000381469727,null,null,null,null,null,29.100000381469727,29.100000381469727,null,null,29.100000381469727]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,23.600000381469727,null,23.600000381469727,null,23.5,null,23.600000381469727,null,null,null,null,23.899999618530273,null,15.899999618530273,null,16,null,null,null,null,null,16,16.100000381469727,null,null,16.200000762939453]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,1.2,null,1.2,null,1.2,null,1.2,null,null,null,null,1.2,null,0.8,null,0.8,null,null,null,null,null,0.8,0.8,null,null,0.8]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"5.5",null,"5.5",null,"5.5",null,"5.5",null,null,null,null,"5.5",null,"5.5",null,"5.5",null,null,null,null,null,"5.5","5.5",null,null,"5.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"NORM","index":184,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"NORM - Normanton (66/22kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"GEOR - Georgetown BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Far North"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1xNORM TX NO 1-66/22KV TRANSF 1;1xNORM TX NO 2-66/22KV TRANSF 2"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 5.3 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -1.7%, 2020 S -0.6% W -0.6%2021 S -1.4% W -1.4%2022 S -1.5% W -1.5%2023 S -1.9% W -1.9"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"4.6 MVA on 04/12/2018 at 16:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,8.1999998092651367,null,8.1999998092651367,null,8.1999998092651367,null,8.1999998092651367,null,null,null,null,8.1999998092651367,null,9.5,null,9.5,null,null,null,null,null,9.5,9.5,null,null,9.5]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,5.0999999046325684,null,5,null,4.9000000953674316,null,4.8000001907348633,null,null,null,null,4.6999998092651367,null,3.7000000476837158,null,3.5999999046325684,null,null,null,null,null,3.5,3.5,null,null,3.5]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.99,null,0.99,null,0.99,null,0.99,null,null,null,null,0.99,null,0.98799999999999999,null,0.95599999999999996,null,null,null,null,null,0.95599999999999996,0.95599999999999996,null,null,0.98799999999999999]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,3.2999999523162842,null,3.2999999523162842,null,3.2999999523162842,null,3.2999999523162842,null,null,null,null,3.2999999523162842,null,3.7000000476837158,null,3.7000000476837158,null,null,null,null,null,3.7000000476837158,3.7000000476837158,null,null,3.7000000476837158]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,4.6999998092651367,null,4.5999999046325684,null,4.5,null,4.4000000953674316,null,null,null,null,4.4000000953674316,null,3.5,null,3.4000000953674316,null,null,null,null,null,3.4000000953674316,3.2999999523162842,null,null,3.2999999523162842]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.2,null,0.2,null,0.2,null,0.2,null,null,null,null,0.2,null,0.2,null,0.2,null,null,null,null,null,0.2,0.2,null,null,0.2]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"66",null,"66",null,"66",null,"66",null,null,null,null,"66",null,"66",null,"66",null,null,null,null,null,"66","66",null,null,"66"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,1.4,null,1.3,null,1.2,null,1.1000000000000001,null,null,null,null,1.1000000000000001]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,1.2999999523162842,null,1.2999999523162842,null,1.2999999523162842,null,1.2999999523162842,null,null,null,null,1.2999999523162842,null,1.2999999523162842,null,1.2999999523162842,null,null,null,null,null,1.2999999523162842,1.2999999523162842,null,null,1.2999999523162842]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,1.2999999523162842,null,1.2999999523162842,null,1.2999999523162842,null,1.2999999523162842,null,null,null,null,1.2999999523162842,null,1.2999999523162842,null,1.2999999523162842,null,null,null,null,null,1.2999999523162842,1.2999999523162842,null,null,1.2999999523162842]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"NORW","index":185,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"NORW - Norwin (33/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T010 - Yarranlea BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is South West"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x33/11kV 3MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.3%, 2020 S -0.0% W -0.0%2021 S -0.1% W -0.1%2022 S -0.0% W -0.0%2023 S -0.1% W -0.1"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"2.2 MVA on 30/11/2018 at 19:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,6,null,6,null,6,null,6,null,null,null,null,6,null,7.9000000953674316,null,7.9000000953674316,null,null,null,null,null,7.9000000953674316,7.9000000953674316,null,null,7.9000000953674316]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,2.4000000953674316,null,2.4000000953674316,null,2.4000000953674316,null,2.4000000953674316,null,null,null,null,2.4000000953674316,null,1.6000000238418579,null,1.6000000238418579,null,null,null,null,null,1.6000000238418579,1.6000000238418579,null,null,1.6000000238418579]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.86,null,0.86,null,0.86,null,0.86,null,null,null,null,0.86,null,0.85299999999999998,null,0.85299999999999998,null,null,null,null,null,0.85299999999999998,0.85299999999999998,null,null,0.85299999999999998]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,4,null,4,null,4,null,4,null,null,null,null,4,null,4.5,null,4.5,null,null,null,null,null,4.5,4.5,null,null,4.5]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,2.2999999523162842,null,2.2999999523162842,null,2.2999999523162842,null,2.2999999523162842,null,null,null,null,2.2999999523162842,null,1.5,null,1.5,null,null,null,null,null,1.5,1.5,null,null,1.5]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.1,null,0.1,null,0.1,null,0.1,null,null,null,null,0.1,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"17.5",null,"17.5",null,"17.5",null,"17.5",null,null,null,null,"17.5",null,"17.5",null,"17.5",null,null,null,null,null,"17.5","17.5",null,null,"17.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"NOST","index":186,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"NOST - North Street (33/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T116 - Torrington BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is South West"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 3x33/11kV 10MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.9%, 2020 S -0.7% W -0.7%2021 S -0.7% W -0.7%2022 S -0.7% W -0.7%2023 S -1.2% W -1.2"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"21.9 MVA on 13/02/2019 at 17:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,30,null,30,null,30,null,30,null,null,null,null,30,null,34.5,null,34.5,null,null,null,null,null,34.5,34.5,null,null,34.5]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,20.399999618530273,null,20.200000762939453,null,19.799999237060547,null,19.600000381469727,null,null,null,null,19.5,null,21.700000762939453,null,21.600000381469727,null,null,null,null,null,21.299999237060547,21.200000762939453,null,null,21]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.92,null,0.92,null,0.92,null,0.92,null,null,null,null,0.92,null,0.98199999999999998,null,0.98199999999999998,null,null,null,null,null,0.98199999999999998,0.98199999999999998,null,null,0.98199999999999998]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,23.600000381469727,null,23.600000381469727,null,23.600000381469727,null,23.600000381469727,null,null,null,null,23.600000381469727,null,26.5,null,26.5,null,null,null,null,null,26.5,26.5,null,null,26.5]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,18.299999237060547,null,18.100000381469727,null,17.799999237060547,null,17.600000381469727,null,null,null,null,17.600000381469727,null,20.100000381469727,null,20,null,null,null,null,null,19.799999237060547,19.600000381469727,null,null,19.399999618530273]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.9,null,0.9,null,0.9,null,0.9,null,null,null,null,0.9,null,1,null,1,null,null,null,null,null,1,1,null,null,1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"3.5",null,"3.5",null,"3.5",null,"3.5",null,null,null,null,"3.5",null,"3.5",null,"3.5",null,null,null,null,null,"3.5","3.5",null,null,"3.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"OAKE","index":187,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"OAKE - Oakey (33/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T189 - Oakey BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is South West"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x33/11kV 20/25MVA ONAN/ONAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -1.7%, 2020 S -1.4% W -1.4%2021 S -1.2% W -1.2%2022 S -1.0% W -1.0%2023 S -1.5% W -1.5"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"15.9 MVA on 13/02/2019 at 15:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,49.700000762939453,null,49.700000762939453,null,49.700000762939453,null,49.700000762939453,null,null,null,null,49.700000762939453,null,56.299999237060547,null,56.299999237060547,null,null,null,null,null,56.299999237060547,56.299999237060547,null,null,56.299999237060547]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,17.899999618530273,null,17.600000381469727,null,17.299999237060547,null,17,null,null,null,null,16.899999618530273,null,15.399999618530273,null,15.199999809265137,null,null,null,null,null,14.899999618530273,14.800000190734863,null,null,14.600000381469727]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.97099999999999997,null,0.97099999999999997,null,0.97099999999999997,null,0.97099999999999997,null,null,null,null,0.97099999999999997,null,0.96699999999999997,null,0.96699999999999997,null,null,null,null,null,0.96699999999999997,0.96699999999999997,null,null,0.96699999999999997]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,28.399999618530273,null,28.399999618530273,null,28.399999618530273,null,28.399999618530273,null,null,null,null,28.399999618530273,null,32.299999237060547,null,32.299999237060547,null,null,null,null,null,32.299999237060547,32.299999237060547,null,null,32.299999237060547]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,16.799999237060547,null,16.5,null,16.200000762939453,null,16,null,null,null,null,15.899999618530273,null,14.899999618530273,null,14.699999809265137,null,null,null,null,null,14.399999618530273,14.300000190734863,null,null,14.100000381469727]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.8,null,0.8,null,0.8,null,0.8,null,null,null,null,0.8,null,0.7,null,0.7,null,null,null,null,null,0.7,0.7,null,null,0.7]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"9",null,"9",null,"9",null,"9",null,null,null,null,"9",null,"9",null,"9",null,null,null,null,null,"9","9",null,null,"9"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"OONN","index":188,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"OONN - Oonoonba (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"TMES - Townsville Mesh"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Nth Queensland"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/11kV 19/26/32MVA ONAN/ODAN/ODAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 1.7%, 2020 S 1.8% W 1.8%, 2021 S 1.7% W 1.7%, 2022 S 1.7% W 1.7%, 2023 S 1.5% W 1.5%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"15.8 MVA on 26/11/2018 at 19:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,74.199996948242188,null,74.199996948242188,null,74.199996948242188,null,74.199996948242188,null,null,null,null,74.199996948242188,null,77.599998474121094,null,77.599998474121094,null,null,null,null,null,77.599998474121094,77.599998474121094,null,null,77.599998474121094]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,15.5,null,15.699999809265137,null,15.899999618530273,null,16.100000381469727,null,null,null,null,16.5,null,9.5,null,9.6000003814697266,null,null,null,null,null,9.8000001907348633,9.8999996185302734,null,null,10.100000381469727]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.98199999999999998,null,0.98199999999999998,null,0.98199999999999998,null,0.98199999999999998,null,null,null,null,0.98199999999999998,null,0.98,null,0.98,null,null,null,null,null,0.98,0.98,null,null,0.98]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,41.200000762939453,null,41.200000762939453,null,41.200000762939453,null,41.200000762939453,null,null,null,null,41.200000762939453,null,42.799999237060547,null,42.799999237060547,null,null,null,null,null,42.799999237060547,42.799999237060547,null,null,42.799999237060547]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,14,null,14.199999809265137,null,14.300000190734863,null,14.5,null,null,null,null,14.800000190734863,null,8.8999996185302734,null,9.1000003814697266,null,null,null,null,null,9.1999998092651367,9.3999996185302734,null,null,9.5]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.7,null,0.7,null,0.7,null,0.7,null,null,null,null,0.7,null,0.4,null,0.5,null,null,null,null,null,0.5,0.5,null,null,0.5]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"11.5",null,"11.5",null,"11.5",null,"11.5",null,null,null,null,"11.5",null,"11.5",null,"11.5",null,null,null,null,null,"11.5","11.5",null,null,"11.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"OWAN","index":189,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[44,4,44,9],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[44,21,44,22],[44,23,44,24],[44,25,44,30],[49,2,49,39],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[45,23,45,24],[45,25,45,30],[45,32,45,34],[42,23,42,24],[42,25,42,30],[42,32,42,34],[43,4,43,9],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[43,21,43,22],[43,23,43,24],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[42,21,42,22],[43,25,43,30],[43,32,43,34],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[41,23,41,24],[41,25,41,30],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[39,25,39,30],[39,32,39,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[35,25,35,30],[35,32,35,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[31,25,31,30],[31,32,31,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[27,25,27,30],[27,32,27,34],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"OWAN - Owanyilla (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T059 - Maryborough BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Wide Bay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/11kV 10MVA ONAN;1xOWAN TX NO 1 TRANSF 1 RG91765711 10 MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.4%, 2020 S 0.5% W 0.5%, 2021 S 0.5% W 0.5%, 2022 S 0.4% W 0.4%, 2023 S 0.4% W 0.4%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"6 MVA on 14/03/2019 at 20:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,22,null,22,null,22,null,22,null,null,null,null,22,null,22,null,22,null,null,null,null,null,22,22,null,null,22]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,8.8999996185302734,null,8.8999996185302734,null,8.8999996185302734,null,8.8999996185302734,null,null,null,null,9,null,3.7000000476837158,null,3.7000000476837158,null,null,null,null,null,3.7000000476837158,3.7000000476837158,null,null,3.7999999523162842]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.91400000000000003,null,0.91400000000000003,null,0.91400000000000003,null,0.91400000000000003,null,null,null,null,0.91400000000000003,null,0.92400000000000004,null,0.92400000000000004,null,null,null,null,null,0.92400000000000004,0.92400000000000004,null,null,0.92400000000000004]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,12,null,12,null,12,null,12,null,null,null,null,12,null,13,null,13,null,null,null,null,null,13,13,null,null,13]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,7.0999999046325684,null,7.0999999046325684,null,7.0999999046325684,null,7.0999999046325684,null,null,null,null,7.1999998092651367,null,3.5,null,3.5,null,null,null,null,null,3.5,3.5,null,null,3.5999999046325684]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.4,null,0.4,null,0.4,null,0.4,null,null,null,null,0.4,null,0.2,null,0.2,null,null,null,null,null,0.2,0.2,null,null,0.2]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"4.5",null,"4.5",null,"4.5",null,"4.5",null,null,null,null,"4.5",null,"4.5",null,"4.5",null,null,null,null,null,"4.5","4.5",null,null,"4.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"PAMP","index":190,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"PAMP - Pampas (33/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T010 - Yarranlea BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is South West"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x33/11kV 5MVA ON"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -1.3%, 2020 S -1.3% W -1.3%2021 S -1.2% W -1.2%2022 S -1.3% W -1.3%2023 S -1.4% W -1.4"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"7.2 MVA on 16/01/2019 at 18:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,10,null,10,null,10,null,10,null,null,null,null,10,null,10,null,10,null,null,null,null,null,10,10,null,null,10]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,6.9000000953674316,null,6.8000001907348633,null,6.5999999046325684,null,6.5,null,null,null,null,6.5,null,3.2000000476837158,null,3.0999999046325684,null,null,null,null,null,3.0999999046325684,3,null,null,3]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.79100000000000004,null,0.79100000000000004,null,0.79100000000000004,null,0.79100000000000004,null,null,null,null,0.79100000000000004,null,0.79900000000000004,null,0.79900000000000004,null,null,null,null,null,0.79900000000000004,0.79900000000000004,null,null,0.79900000000000004]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,5.5,null,5.5,null,5.5,null,5.5,null,null,null,null,5.5,null,5.5,null,5.5,null,null,null,null,null,5.5,5.5,null,null,5.5]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,6,null,5.9000000953674316,null,5.6999998092651367,null,5.6999998092651367,null,null,null,null,5.6999998092651367,null,3,null,3,null,null,null,null,null,2.9000000953674316,2.9000000953674316,null,null,2.9000000953674316]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.3,null,0.3,null,0.3,null,0.3,null,null,null,null,0.3,null,0.2,null,0.2,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"9.5",null,"9.5",null,"9.5",null,"9.5",null,null,null,null,"9.5",null,"9.5",null,"9.5",null,null,null,null,null,"9.5","9.5",null,null,"9.5"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,0.5,null,0.4,null,0.2,null,0.2,null,null,null,null,0.2]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,10,null,10,null,10,null,10,null,null,null,null,10,null,10,null,10,null,null,null,null,null,10,10,null,null,10]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"PAND","index":191,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"PAND - Pandoin (66/22kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"RMES - Rockhampton Mesh"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Capricornia"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/22kV 8/10MVA ONAN/ONAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.4%, 2020 S -0.1% W -0.1%2021 S -0.1% W -0.1%2022 S 0.1% W 0.1%, 2023 S -0.1% W -0.1"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"10.3 MVA on 02/12/2018 at 15:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,23.200000762939453,null,23.200000762939453,null,23.200000762939453,null,23.200000762939453,null,null,null,null,23.200000762939453,null,26.600000381469727,null,26.600000381469727,null,null,null,null,null,26.600000381469727,26.600000381469727,null,null,26.600000381469727]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,11.100000381469727,null,11,null,10.899999618530273,null,10.899999618530273,null,null,null,null,11,null,9.1999998092651367,null,9.1999998092651367,null,null,null,null,null,9.1999998092651367,9.1999998092651367,null,null,9.1999998092651367]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.96599999999999997,null,0.96599999999999997,null,0.96599999999999997,null,0.96599999999999997,null,null,null,null,0.96599999999999997,null,0.97299999999999998,null,0.97299999999999998,null,null,null,null,null,0.97299999999999998,0.97299999999999998,null,null,0.97299999999999998]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,13.600000381469727,null,13.600000381469727,null,13.600000381469727,null,13.600000381469727,null,null,null,null,13.600000381469727,null,14.5,null,14.5,null,null,null,null,null,14.5,14.5,null,null,14.5]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,10.100000381469727,null,10,null,9.8999996185302734,null,9.8999996185302734,null,null,null,null,10,null,8.5,null,8.5,null,null,null,null,null,8.3999996185302734,8.3999996185302734,null,null,8.3999996185302734]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.5,null,0.5,null,0.5,null,0.5,null,null,null,null,0.5,null,0.4,null,0.4,null,null,null,null,null,0.4,0.4,null,null,0.4]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"7",null,"7",null,"7",null,"7",null,null,null,null,"7",null,"7",null,"7",null,null,null,null,null,"7","7",null,null,"7"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"PARK","index":192,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"PARK - Parkhurst (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"RMES - Rockhampton Mesh"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Capricornia"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/11kV 15/20MVA ONAN/ONAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.1%, 2020 S 0.4% W 0.4%, 2021 S 0.1% W 0.1%, 2022 S 0.0% W 0.0%, 2023 S -0.4% W -0.4"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"16 MVA on 03/12/2018 at 16:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,48.299999237060547,null,48.299999237060547,null,48.299999237060547,null,48.299999237060547,null,null,null,null,48.299999237060547,null,55.400001525878906,null,55.400001525878906,null,null,null,null,null,55.400001525878906,55.400001525878906,null,null,55.400001525878906]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,17.600000381469727,null,17.5,null,17.299999237060547,null,17.299999237060547,null,null,null,null,17.5,null,10.600000381469727,null,10.600000381469727,null,null,null,null,null,10.600000381469727,10.600000381469727,null,null,10.600000381469727]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.99399999999999999,null,0.99399999999999999,null,0.99399999999999999,null,0.99399999999999999,null,null,null,null,0.99399999999999999,null,0.91100000000000003,null,0.91100000000000003,null,null,null,null,null,0.91100000000000003,0.91100000000000003,null,null,0.91100000000000003]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,28,null,28,null,28,null,28,null,null,null,null,28,null,29.899999618530273,null,29.899999618530273,null,null,null,null,null,29.899999618530273,29.899999618530273,null,null,29.899999618530273]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,15.600000381469727,null,15.600000381469727,null,15.399999618530273,null,15.399999618530273,null,null,null,null,15.5,null,10.199999809265137,null,10.199999809265137,null,null,null,null,null,10.199999809265137,10.199999809265137,null,null,10.199999809265137]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.8,null,0.8,null,0.8,null,0.8,null,null,null,null,0.8,null,0.5,null,0.5,null,null,null,null,null,0.5,0.5,null,null,0.5]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"14.5",null,"14.5",null,"14.5",null,"14.5",null,null,null,null,"14.5",null,"14.5",null,"14.5",null,null,null,null,null,"14.5","14.5",null,null,"14.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"PEAR","index":193,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"PEAR - Peter Arlett (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"TMES - Townsville Mesh"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Nth Queensland"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/11kV 21/26.25/35MVA ONAN/ODAN/ODAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.7%, 2020 S 0.9% W 0.9%, 2021 S 0.7% W 0.7%, 2022 S 1.0% W 1.0%, 2023 S 0.8% W 0.8%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"25.4 MVA on 20/02/2019 at 19:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,78.900001525878906,null,78.900001525878906,null,78.900001525878906,null,78.900001525878906,null,null,null,null,78.900001525878906,null,87.400001525878906,null,87.400001525878906,null,null,null,null,null,87.400001525878906,87.400001525878906,null,null,87.400001525878906]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,26.5,null,26.600000381469727,null,26.600000381469727,null,26.899999618530273,null,null,null,null,27.299999237060547,null,15.800000190734863,null,15.899999618530273,null,null,null,null,null,16,16.100000381469727,null,null,16.299999237060547]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.97399999999999998,null,0.97399999999999998,null,0.97399999999999998,null,0.97399999999999998,null,null,null,null,0.97399999999999998,null,0.96599999999999997,null,0.96599999999999997,null,null,null,null,null,0.96599999999999997,0.96599999999999997,null,null,0.96599999999999997]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,44.400001525878906,null,44.400001525878906,null,44.400001525878906,null,44.400001525878906,null,null,null,null,44.400001525878906,null,47.099998474121094,null,47.099998474121094,null,null,null,null,null,47.099998474121094,47.099998474121094,null,null,47.099998474121094]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,24.700000762939453,null,24.799999237060547,null,24.799999237060547,null,25,null,null,null,null,25.399999618530273,null,15.300000190734863,null,15.399999618530273,null,null,null,null,null,15.399999618530273,15.600000381469727,null,null,15.800000190734863]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,1.2,null,1.2,null,1.2,null,1.3,null,null,null,null,1.3,null,0.8,null,0.8,null,null,null,null,null,0.8,0.8,null,null,0.8]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"6.5",null,"6.5",null,"6.5",null,"6.5",null,null,null,null,"6.5",null,"6.5",null,"6.5",null,null,null,null,null,"6.5","6.5",null,null,"6.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"PERA","index":194,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"PERA - Peranga (33/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T189 - Oakey BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is South West"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x33/11kV 0.75MVA ON;1x33/11kV 3MVA ON"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.8%, 2020 S 0.1% W 0.1%, 2021 S -0.0% W -0.0%2022 S -0.1% W -0.1%2023 S -0.6% W -0.6"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"1.7 MVA on 11/02/2019 at 18:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,4.6999998092651367,null,4.6999998092651367,null,4.6999998092651367,null,4.6999998092651367,null,null,null,null,4.6999998092651367,null,5.0999999046325684,null,5.0999999046325684,null,null,null,null,null,5.0999999046325684,5.0999999046325684,null,null,5.0999999046325684]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,1.7999999523162842,null,1.7000000476837158,null,1.7000000476837158,null,1.7000000476837158,null,null,null,null,1.7000000476837158,null,1.6000000238418579,null,1.6000000238418579,null,null,null,null,null,1.6000000238418579,1.6000000238418579,null,null,1.6000000238418579]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.89400000000000002,null,0.89400000000000002,null,0.89400000000000002,null,0.89400000000000002,null,null,null,null,0.89400000000000002,null,0.90200000000000002,null,0.90200000000000002,null,null,null,null,null,0.90200000000000002,0.90200000000000002,null,null,0.90200000000000002]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0.80000001192092896,null,0.80000001192092896,null,0.80000001192092896,null,0.80000001192092896,null,null,null,null,0.80000001192092896,null,0.80000001192092896,null,0.80000001192092896,null,null,null,null,null,0.80000001192092896,0.80000001192092896,null,null,0.80000001192092896]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,1.6000000238418579,null,1.6000000238418579,null,1.6000000238418579,null,1.6000000238418579,null,null,null,null,1.6000000238418579,null,1.6000000238418579,null,1.6000000238418579,null,null,null,null,null,1.6000000238418579,1.6000000238418579,null,null,1.6000000238418579]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.1,null,0.1,null,0.1,null,0.1,null,null,null,null,0.1,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"4.5",null,"4.5",null,"4.5",null,"4.5",null,null,null,null,"4.5",null,"4.5",null,"4.5",null,null,null,null,null,"4.5","4.5",null,null,"4.5"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,0.8,null,0.8,null,0.8,null,0.8,null,null,null,null,0.8,null,0.8,null,0.8,null,null,null,null,null,0.8,0.8,null,null,0.8]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,1,null,1,null,1,null,1,null,null,null,null,1,null,1,null,1,null,null,null,null,null,1,1,null,null,1]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"PIAL","index":195,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"PIAL - Pialba (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T059 - Maryborough BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Wide Bay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/11kV 12.5/16MVA ONAN/ONAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.4 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.1%, 2020 S 0.3% W 0.3%, 2021 S 0.4% W 0.4%, 2022 S 0.3% W 0.3%, 2023 S -0.1% W -0.1"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"15.3 MVA on 13/02/2019 at 16:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,33.200000762939453,null,33.200000762939453,null,33.200000762939453,null,33.200000762939453,null,null,null,null,33.200000762939453,null,37.200000762939453,null,37.200000762939453,null,null,null,null,null,37.200000762939453,37.200000762939453,null,null,37.200000762939453]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,17,null,16.899999618530273,null,16.799999237060547,null,16.799999237060547,null,null,null,null,16.899999618530273,null,11.699999809265137,null,11.699999809265137,null,null,null,null,null,11.699999809265137,11.699999809265137,null,null,11.800000190734863]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.996,null,0.996,null,0.996,null,0.996,null,null,null,null,0.996,null,0.98699999999999999,null,0.98699999999999999,null,null,null,null,null,0.98699999999999999,0.98699999999999999,null,null,0.98699999999999999]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,19.100000381469727,null,19.100000381469727,null,19.100000381469727,null,19.100000381469727,null,null,null,null,19.100000381469727,null,21,null,21,null,null,null,null,null,21,21,null,null,21]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,15.699999809265137,null,15.699999809265137,null,15.600000381469727,null,15.600000381469727,null,null,null,null,15.699999809265137,null,11.100000381469727,null,11.100000381469727,null,null,null,null,null,11.100000381469727,11.199999809265137,null,null,11.199999809265137]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.8,null,0.8,null,0.8,null,0.8,null,null,null,null,0.8,null,0.6,null,0.6,null,null,null,null,null,0.6,0.6,null,null,0.6]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"8",null,"8",null,"8",null,"8",null,null,null,null,"8",null,"8",null,"8",null,null,null,null,null,"8","8",null,null,"8"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,4,null,4,null,4,null,4,null,null,null,null,4,null,4,null,4,null,null,null,null,null,4,4,null,null,4]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"PINN","index":196,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"PINN - Pinnacle (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T141 - Pioneer Valley BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Mackay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/11kV 5MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.6%, 2020 S 0.9% W 0.9%, 2021 S 0.9% W 0.9%, 2022 S 0.3% W 0.3%, 2023 S 0.2% W 0.2%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"4.2 MVA on 02/12/2018 at 19:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,11,null,11,null,11,null,11,null,null,null,null,11,null,12,null,12,null,null,null,null,null,12,12,null,null,12]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,5.1999998092651367,null,5.1999998092651367,null,5.0999999046325684,null,5.1999998092651367,null,null,null,null,5.1999998092651367,null,2.7000000476837158,null,2.7000000476837158,null,null,null,null,null,2.7000000476837158,2.7999999523162842,null,null,2.7999999523162842]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.91400000000000003,null,0.91400000000000003,null,0.91500000000000004,null,0.91400000000000003,null,null,null,null,0.91300000000000003,null,0.96899999999999997,null,0.96799999999999997,null,null,null,null,null,0.96799999999999997,0.96699999999999997,null,null,0.96599999999999997]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,6.3000001907348633,null,6.3000001907348633,null,6.3000001907348633,null,6.3000001907348633,null,null,null,null,6.3000001907348633,null,6.5,null,6.5,null,null,null,null,null,6.5,6.5,null,null,6.5]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,4,null,4,null,4,null,4,null,null,null,null,4.0999999046325684,null,2.5,null,2.5,null,null,null,null,null,2.5,2.5,null,null,2.5999999046325684]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.2,null,0.2,null,0.2,null,0.2,null,null,null,null,0.2,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"8",null,"8",null,"8",null,"8",null,null,null,null,"8",null,"8",null,"8",null,null,null,null,null,"8","8",null,null,"8"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"PIRR","index":197,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"PIRR - Pirrinuan (33/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T002 - Dalby East BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is South West"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x33/11kV 3.15MVA ONAN;1x33/11kV 1MVA ON(Standby)"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.6%, 2020 S 0.0% W 0.0%, 2021 S -0.1% W -0.1%2022 S 0.1% W 0.1%, 2023 S -0.4% W -0.4"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"2.2 MVA on 08/02/2019 at 07:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,3.5,null,3.5,null,3.5,null,3.5,null,null,null,null,3.5,null,3.5,null,3.5,null,null,null,null,null,3.5,3.5,null,null,3.5]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,1.1000000238418579,null,1.1000000238418579,null,1.1000000238418579,null,1.1000000238418579,null,null,null,null,1.1000000238418579,null,1.2999999523162842,null,1.2999999523162842,null,null,null,null,null,1.2999999523162842,1.2999999523162842,null,null,1.2999999523162842]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.623,null,0.623,null,0.623,null,0.623,null,null,null,null,0.623,null,0.624,null,0.624,null,null,null,null,null,0.624,0.624,null,null,0.624]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,1,null,1,null,1,null,1,null,null,null,null,1,null,1.2999999523162842,null,1.2999999523162842,null,null,null,null,null,1.2000000476837158,1.2000000476837158,null,null,1.2000000476837158]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.1,null,0.1,null,0.1,null,0.1,null,null,null,null,0.1,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"5.5",null,"5.5",null,"5.5",null,"5.5",null,null,null,null,"5.5",null,"5.5",null,"5.5",null,null,null,null,null,"5.5","5.5",null,null,"5.5"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,1,null,1,null,1,null,1,null,null,null,null,1,null,1.3,null,1.3,null,null,null,null,null,1.2,1.2,null,null,1.2]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0.30000001192092896,null,0.30000001192092896,null,0.30000001192092896,null,0.30000001192092896,null,null,null,null,0.30000001192092896,null,0.30000001192092896,null,0.30000001192092896,null,null,null,null,null,0.30000001192092896,0.30000001192092896,null,null,0.30000001192092896]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,1.5,null,1.5,null,1.5,null,1.5,null,null,null,null,1.5,null,1.5,null,1.5,null,null,null,null,null,1.5,1.5,null,null,1.5]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"PLAN","index":198,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"PLAN - Planella (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T141 - Pioneer Valley BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Mackay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x33/11kV 13MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.9%, 2020 S 1.2% W 1.2%, 2021 S 1.2% W 1.2%, 2022 S 1.7% W 1.7%, 2023 S 1.3% W 1.3%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"16.2 MVA on 20/02/2019 at 18:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,30,null,30,null,30,null,30,null,null,null,null,30,null,30.600000381469727,null,30.600000381469727,null,null,null,null,null,30.600000381469727,30.600000381469727,null,null,30.600000381469727]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,18.799999237060547,null,18.899999618530273,null,19,null,19.299999237060547,null,null,null,null,19.700000762939453,null,11.100000381469727,null,11.199999809265137,null,null,null,null,null,11.300000190734863,11.5,null,null,11.699999809265137]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.99299999999999999,null,0.99299999999999999,null,0.99299999999999999,null,0.99299999999999999,null,null,null,null,0.99299999999999999,null,0.996,null,0.996,null,null,null,null,null,0.996,0.996,null,null,0.996]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,15.300000190734863,null,15.300000190734863,null,15.300000190734863,null,15.300000190734863,null,null,null,null,15.300000190734863,null,15.300000190734863,null,15.300000190734863,null,null,null,null,null,15.300000190734863,15.300000190734863,null,null,15.300000190734863]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,17.100000381469727,null,17.200000762939453,null,17.299999237060547,null,17.600000381469727,null,null,null,null,17.899999618530273,null,10.699999809265137,null,10.800000190734863,null,null,null,null,null,10.899999618530273,11.100000381469727,null,null,11.199999809265137]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.9,null,0.9,null,0.9,null,0.9,null,null,null,null,0.9,null,0.5,null,0.5,null,null,null,null,null,0.5,0.6,null,null,0.6]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"17",null,"17",null,"17",null,"17",null,null,null,null,"17",null,"17",null,"17",null,null,null,null,null,"17","17",null,null,"17"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,1.8,null,1.9,null,2,null,2.2999999999999998,null,null,null,null,2.6]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,2.2999999523162842,null,2.2999999523162842,null,2.2999999523162842,null,2.2999999523162842,null,null,null,null,2.2999999523162842,null,2.2999999523162842,null,2.2999999523162842,null,null,null,null,null,2.2999999523162842,2.2999999523162842,null,null,2.2999999523162842]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,1.5,null,1.5,null,1.5,null,1.5,null,null,null,null,1.5,null,1.5,null,1.5,null,null,null,null,null,1.5,1.5,null,null,1.5]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"PLEY","index":199,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"PLEY - Pleystowe (33/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T038 - Mackay BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Mackay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 3x33/11kV 5MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.0%, 2020 S 0.3% W 0.3%, 2021 S 0.3% W 0.3%, 2022 S 0.1% W 0.1%, 2023 S -0.1% W -0.1"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"8.8 MVA on 28/11/2018 at 19:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,13.5,null,13.5,null,13.5,null,13.5,null,null,null,null,13.5,null,13.5,null,13.5,null,null,null,null,null,13.5,13.5,null,null,13.5]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,10.399999618530273,null,10.300000190734863,null,10.300000190734863,null,10.300000190734863,null,null,null,null,10.300000190734863,null,6,null,6,null,null,null,null,null,6,6,null,null,6.0999999046325684]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.96799999999999997,null,0.96799999999999997,null,0.96799999999999997,null,0.96799999999999997,null,null,null,null,0.96799999999999997,null,0.97299999999999998,null,0.97299999999999998,null,null,null,null,null,0.97299999999999998,0.97299999999999998,null,null,0.97299999999999998]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,9,null,9,null,9,null,9,null,null,null,null,9,null,9,null,9,null,null,null,null,null,9,9,null,null,9]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,8.5,null,8.5,null,8.3999996185302734,null,8.5,null,null,null,null,8.5,null,5.5,null,5.5,null,null,null,null,null,5.5,5.5,null,null,5.5]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.4,null,0.4,null,0.4,null,0.4,null,null,null,null,0.4,null,0.3,null,0.3,null,null,null,null,null,0.3,0.3,null,null,0.3]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"5",null,"5",null,"5",null,"5",null,null,null,null,"5",null,"5",null,"5",null,null,null,null,null,"5","5",null,null,"5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,2,null,2,null,2,null,2,null,null,null,null,2,null,2,null,2,null,null,null,null,null,2,2,null,null,2]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"POVE","index":200,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"POVE - Point Vernon (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T059 - Maryborough BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Wide Bay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1xPoint Vernon Tx No 1;1xPoint Vernon Tx No 2"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.3%, 2020 S 0.3% W 0.3%, 2021 S 0.4% W 0.4%, 2022 S 0.2% W 0.2%, 2023 S -0.3% W -0.3"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"20.2 MVA on 13/02/2019 at 16:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,84.599998474121094,null,84.599998474121094,null,84.599998474121094,null,84.599998474121094,null,null,null,null,84.599998474121094,null,95.699996948242188,null,95.699996948242188,null,null,null,null,null,95.699996948242188,95.699996948242188,null,null,95.699996948242188]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,22.399999618530273,null,22.399999618530273,null,22.200000762939453,null,22.200000762939453,null,null,null,null,22.299999237060547,null,17.799999237060547,null,17.799999237060547,null,null,null,null,null,17.799999237060547,17.799999237060547,null,null,17.899999618530273]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,1,null,1,null,1,null,1,null,null,null,null,1,null,0.999,null,0.999,null,null,null,null,null,0.999,0.999,null,null,0.999]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,47.599998474121094,null,47.599998474121094,null,47.599998474121094,null,47.599998474121094,null,null,null,null,47.599998474121094,null,47.799999237060547,null,47.799999237060547,null,null,null,null,null,47.799999237060547,47.799999237060547,null,null,47.799999237060547]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,20.5,null,20.5,null,20.399999618530273,null,20.399999618530273,null,null,null,null,20.5,null,16.700000762939453,null,16.700000762939453,null,null,null,null,null,16.700000762939453,16.700000762939453,null,null,16.700000762939453]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,1,null,1,null,1,null,1,null,null,null,null,1,null,0.8,null,0.8,null,null,null,null,null,0.8,0.8,null,null,0.8]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"9",null,"9",null,"9",null,"9",null,null,null,null,"9",null,"9",null,"9",null,null,null,null,null,"9","9",null,null,"9"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"POZI","index":201,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"POZI - Pozieres (33/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T060 - Stanthorpe BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is South West"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x33/11kV 3MVA ON"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -2.7%, 2020 S -2.3% W -2.3%2021 S -2.1% W -2.1%2022 S -1.5% W -1.5%2023 S -1.8% W -1.8"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"3.5 MVA on 19/02/2019 at 15:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,7.0999999046325684,null,7.0999999046325684,null,7.0999999046325684,null,7.0999999046325684,null,null,null,null,7.0999999046325684,null,7.5,null,7.5,null,null,null,null,null,7.5,7.5,null,null,7.5]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,3.9000000953674316,null,3.7999999523162842,null,3.7000000476837158,null,3.7000000476837158,null,null,null,null,3.5999999046325684,null,2.2999999523162842,null,2.2999999523162842,null,null,null,null,null,2.2000000476837158,2.2000000476837158,null,null,2.0999999046325684]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.84499999999999997,null,0.84499999999999997,null,0.84499999999999997,null,0.84499999999999997,null,null,null,null,0.84499999999999997,null,0.88600000000000001,null,0.88600000000000001,null,null,null,null,null,0.88600000000000001,0.88600000000000001,null,null,0.88600000000000001]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,3.9000000953674316,null,3.9000000953674316,null,3.9000000953674316,null,3.9000000953674316,null,null,null,null,3.9000000953674316,null,4,null,4,null,null,null,null,null,4,4,null,null,4]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,3.5999999046325684,null,3.5,null,3.5,null,3.4000000953674316,null,null,null,null,3.2999999523162842,null,2.2000000476837158,null,2.0999999046325684,null,null,null,null,null,2.0999999046325684,2,null,null,2]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.2,null,0.2,null,0.2,null,0.2,null,null,null,null,0.2,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"7",null,"7",null,"7",null,"7",null,null,null,null,"7",null,"7",null,"7",null,null,null,null,null,"7","7",null,null,"7"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0.5,null,0.5,null,0.5,null,0.5,null,null,null,null,0.5,null,0.5,null,0.5,null,null,null,null,null,0.5,0.5,null,null,0.5]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"PROT","index":202,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"PROT - Proston (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T012 - Kilkivan BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Wide Bay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/11kV 2.3MVA ONAN;1x66/11kV 2MVA ON"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.0%, 2020 S 0.2% W 0.2%, 2021 S 0.2% W 0.2%, 2022 S -0.0% W -0.0%2023 S -0.2% W -0.2"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"1.5 MVA on 21/08/2018 at 18:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,5.4000000953674316,null,5.4000000953674316,null,5.4000000953674316,null,5.4000000953674316,null,null,null,null,5.4000000953674316,null,6,null,6,null,null,null,null,null,6,6,null,null,6]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,1.7000000476837158,null,1.7000000476837158,null,1.6000000238418579,null,1.6000000238418579,null,null,null,null,1.7000000476837158,null,1.5,null,1.5,null,null,null,null,null,1.5,1.5,null,null,1.5]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.96299999999999997,null,0.96299999999999997,null,0.96299999999999997,null,0.96299999999999997,null,null,null,null,0.96299999999999997,null,0.98199999999999998,null,0.98199999999999998,null,null,null,null,null,0.98199999999999998,0.98199999999999998,null,null,0.98199999999999998]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,3,null,3,null,3,null,3,null,null,null,null,3,null,3,null,3,null,null,null,null,null,3,3,null,null,3]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,1.5,null,1.5,null,1.5,null,1.5,null,null,null,null,1.5,null,1.3999999761581421,null,1.3999999761581421,null,null,null,null,null,1.3999999761581421,1.3999999761581421,null,null,1.3999999761581421]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.1,null,0.1,null,0.1,null,0.1,null,null,null,null,0.1,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"6",null,"6",null,"6",null,"6",null,null,null,null,"6",null,"6",null,"6",null,null,null,null,null,"6","6",null,null,"6"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"PURR","index":203,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"PURR - Purrawunda (33/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T116 - Torrington BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is South West"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x33/11kV 6.25MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.4%, 2020 S -0.0% W -0.0%2021 S -0.2% W -0.2%2022 S -0.1% W -0.1%2023 S -0.3% W -0.3"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"6.7 MVA on 06/11/2018 at 19:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,14,null,14,null,14,null,14,null,null,null,null,14,null,15.5,null,15.5,null,null,null,null,null,15.5,15.5,null,null,15.5]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,7,null,7,null,6.9000000953674316,null,6.9000000953674316,null,null,null,null,6.9000000953674316,null,5.6999998092651367,null,5.6999998092651367,null,null,null,null,null,5.6999998092651367,5.6999998092651367,null,null,5.6999998092651367]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.999,null,0.999,null,0.999,null,0.999,null,null,null,null,0.999,null,0.996,null,0.996,null,null,null,null,null,0.996,0.996,null,null,0.996]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,8.1999998092651367,null,8.1999998092651367,null,8.1999998092651367,null,8.1999998092651367,null,null,null,null,8.1999998092651367,null,8.8000001907348633,null,8.8000001907348633,null,null,null,null,null,8.8000001907348633,8.8000001907348633,null,null,8.8000001907348633]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,6.6999998092651367,null,6.6999998092651367,null,6.5999999046325684,null,6.5999999046325684,null,null,null,null,6.5999999046325684,null,5.6999998092651367,null,5.6999998092651367,null,null,null,null,null,5.6999998092651367,5.5999999046325684,null,null,5.6999998092651367]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.3,null,0.3,null,0.3,null,0.3,null,null,null,null,0.3,null,0.3,null,0.3,null,null,null,null,null,0.3,0.3,null,null,0.3]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"18",null,"18",null,"18",null,"18",null,null,null,null,"18",null,"18",null,"18",null,null,null,null,null,"18","18",null,null,"18"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"QUIL","index":204,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"QUIL - Quilpie (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T083 - Roma 66kV BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is South West"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/11kV 3MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -1.6%, 2020 S -1.2% W -1.2%2021 S -1.3% W -1.3%2022 S -0.8% W -0.8%2023 S -1.1% W -1.1"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"2.3 MVA on 24/01/2019 at 19:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,6,null,6,null,6,null,6,null,null,null,null,6,null,7.4000000953674316,null,7.4000000953674316,null,null,null,null,null,7.4000000953674316,7.4000000953674316,null,null,7.4000000953674316]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,2.5999999046325684,null,2.5999999046325684,null,2.5,null,2.5,null,null,null,null,2.5,null,1.7999999523162842,null,1.7000000476837158,null,null,null,null,null,1.7000000476837158,1.7000000476837158,null,null,1.7000000476837158]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.98099999999999998,null,0.98099999999999998,null,0.98099999999999998,null,0.98099999999999998,null,null,null,null,0.98099999999999998,null,0.94899999999999995,null,0.94899999999999995,null,null,null,null,null,0.94899999999999995,0.94899999999999995,null,null,0.94899999999999995]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,3.7000000476837158,null,3.7000000476837158,null,3.7000000476837158,null,3.7000000476837158,null,null,null,null,3.7000000476837158,null,4.3000001907348633,null,4.3000001907348633,null,null,null,null,null,4.3000001907348633,4.3000001907348633,null,null,4.3000001907348633]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,2.4000000953674316,null,2.2999999523162842,null,2.2999999523162842,null,2.2999999523162842,null,null,null,null,2.2000000476837158,null,1.6000000238418579,null,1.6000000238418579,null,null,null,null,null,1.6000000238418579,1.6000000238418579,null,null,1.6000000238418579]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.1,null,0.1,null,0.1,null,0.1,null,null,null,null,0.1,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"17.5",null,"17.5",null,"17.5",null,"17.5",null,null,null,null,"17.5",null,"17.5",null,"17.5",null,null,null,null,null,"17.5","17.5",null,null,"17.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"RAGL","index":205,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"RAGL - Raglan (66/22kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"RMES - Rockhampton Mesh"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Capricornia"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/22kV 5MVA ON"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.0%, 2020 S 0.2% W 0.2%, 2021 S 0.2% W 0.2%, 2022 S 0.3% W 0.3%, 2023 S 0.1% W 0.1%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"3.9 MVA on 13/02/2019 at 19:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,12.5,null,12.5,null,12.5,null,12.5,null,null,null,null,12.5,null,14,null,14,null,null,null,null,null,14,14,null,null,14]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,4.1999998092651367,null,4.1999998092651367,null,4.1999998092651367,null,4.1999998092651367,null,null,null,null,4.1999998092651367,null,3.2999999523162842,null,3.2999999523162842,null,null,null,null,null,3.2999999523162842,3.2999999523162842,null,null,3.2999999523162842]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.96899999999999997,null,0.96899999999999997,null,0.96899999999999997,null,0.96899999999999997,null,null,null,null,0.96899999999999997,null,0.96099999999999997,null,0.96099999999999997,null,null,null,null,null,0.96099999999999997,0.96099999999999997,null,null,0.96099999999999997]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,7.5,null,7.5,null,7.5,null,7.5,null,null,null,null,7.5,null,7.5,null,7.5,null,null,null,null,null,7.5,7.5,null,null,7.5]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,3.9000000953674316,null,3.9000000953674316,null,3.9000000953674316,null,3.9000000953674316,null,null,null,null,3.9000000953674316,null,3.2000000476837158,null,3.2000000476837158,null,null,null,null,null,3.0999999046325684,3.2000000476837158,null,null,3.2000000476837158]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.2,null,0.2,null,0.2,null,0.2,null,null,null,null,0.2,null,0.2,null,0.2,null,null,null,null,null,0.2,0.2,null,null,0.2]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"14",null,"14",null,"14",null,"14",null,null,null,null,"14",null,"14",null,"14",null,null,null,null,null,"14","14",null,null,"14"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"RASM","index":206,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"RASM - Rasmussen (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"TMES - Townsville Mesh"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Nth Queensland"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/11kV 19/26/32MVA ONAN/ODAN/ODAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.0%, 2020 S 0.1% W 0.1%, 2021 S 0.1% W 0.1%, 2022 S 0.5% W 0.5%, 2023 S 0.4% W 0.4%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"20.8 MVA on 26/11/2018 at 18:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,80.400001525878906,null,80.400001525878906,null,80.400001525878906,null,80.400001525878906,null,null,null,null,80.400001525878906,null,84.400001525878906,null,84.400001525878906,null,null,null,null,null,84.400001525878906,84.400001525878906,null,null,84.400001525878906]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,22.5,null,22.399999618530273,null,22.299999237060547,null,22.5,null,null,null,null,22.700000762939453,null,12.300000190734863,null,12.300000190734863,null,null,null,null,null,12.300000190734863,12.399999618530273,null,null,12.399999618530273]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.997,null,0.997,null,0.997,null,0.997,null,null,null,null,0.997,null,0.98399999999999999,null,0.98399999999999999,null,null,null,null,null,0.98399999999999999,0.98399999999999999,null,null,0.98399999999999999]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,42.900001525878906,null,42.900001525878906,null,42.900001525878906,null,42.900001525878906,null,null,null,null,42.900001525878906,null,45,null,45,null,null,null,null,null,45,45,null,null,45]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,19.299999237060547,null,19.299999237060547,null,19.200000762939453,null,19.299999237060547,null,null,null,null,19.5,null,11.899999618530273,null,11.899999618530273,null,null,null,null,null,11.899999618530273,11.899999618530273,null,null,12]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,1,null,1,null,1,null,1,null,null,null,null,1,null,0.6,null,0.6,null,null,null,null,null,0.6,0.6,null,null,0.6]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"13.5",null,"13.5",null,"13.5",null,"13.5",null,null,null,null,"13.5",null,"13.5",null,"13.5",null,null,null,null,null,"13.5","13.5",null,null,"13.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"RAVE","index":207,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"RAVE - Ravenshoe (66/22kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T055 - Turkinje 66kV BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Far North"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/22kV 12/15MVA ONAN/ONAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 12.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -1.9%, 2020 S -3.1% W -3.1%2021 S -2.4% W -2.4%2022 S -2.1% W -2.1%2023 S -2.5% W -2.5"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"2.7 MVA on 20/06/2018 at 07:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,19.600000381469727,null,19.600000381469727,null,19.600000381469727,null,19.600000381469727,null,null,null,null,19.600000381469727,null,22.299999237060547,null,22.299999237060547,null,null,null,null,null,22.299999237060547,22.299999237060547,null,null,22.299999237060547]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,4.9000000953674316,null,4.9000000953674316,null,4.9000000953674316,null,4.9000000953674316,null,null,null,null,4.9000000953674316,null,4.9000000953674316,null,4.9000000953674316,null,null,null,null,null,4.9000000953674316,4.9000000953674316,null,null,4.9000000953674316]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,2.4000000953674316,null,2.2999999523162842,null,2.2999999523162842,null,2.2000000476837158,null,null,null,null,2.2000000476837158,null,2.7000000476837158,null,2.5999999046325684,null,null,null,null,null,2.5,2.5,null,null,2.4000000953674316]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.90400000000000003,null,0.90400000000000003,null,0.90400000000000003,null,0.90400000000000003,null,null,null,null,0.90400000000000003,null,0.90400000000000003,null,0.90400000000000003,null,null,null,null,null,0.90400000000000003,0.90400000000000003,null,null,0.90400000000000003]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,2.2999999523162842,null,2.2000000476837158,null,2.2000000476837158,null,2.0999999046325684,null,null,null,null,2.0999999046325684,null,2.5999999046325684,null,2.5,null,null,null,null,null,2.4000000953674316,2.4000000953674316,null,null,2.2999999523162842]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.1,null,0.1,null,0.1,null,0.1,null,null,null,null,0.1,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"20.5",null,"20.5",null,"20.5",null,"20.5",null,null,null,null,"20.5",null,"20.5",null,"20.5",null,null,null,null,null,"20.5","20.5",null,null,"20.5"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,2.2999999999999998,null,2.2000000000000002,null,2.2000000000000002,null,2.1,null,null,null,null,2.1,null,2.6,null,2.5,null,null,null,null,null,2.4,2.4,null,null,2.2999999999999998]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,3.9000000953674316,null,3.9000000953674316,null,3.9000000953674316,null,3.9000000953674316,null,null,null,null,3.9000000953674316,null,3.9000000953674316,null,3.9000000953674316,null,null,null,null,null,3.9000000953674316,3.9000000953674316,null,null,3.9000000953674316]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"RAVN","index":208,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"RAVN - Ravenswood (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T193 - Clare South BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Nth Queensland"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/11kV 2.5MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.0%, 2020 S 0.3% W 0.3%, 2021 S 0.1% W 0.1%, 2022 S -0.1% W -0.1%2023 S -0.3% W -0.3"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"1.1 MVA on 22/12/2018 at 16:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,2.5,null,2.5,null,2.5,null,2.5,null,null,null,null,2.5,null,2.5,null,2.5,null,null,null,null,null,2.5,2.5,null,null,2.5]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,1.2000000476837158,null,1.2000000476837158,null,1.2000000476837158,null,1.2000000476837158,null,null,null,null,1.2000000476837158,null,1.1000000238418579,null,1.1000000238418579,null,null,null,null,null,1.1000000238418579,1.1000000238418579,null,null,1.1000000238418579]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.94199999999999995,null,0.94199999999999995,null,0.94199999999999995,null,0.94199999999999995,null,null,null,null,0.94199999999999995,null,0.94399999999999995,null,0.94399999999999995,null,null,null,null,null,0.94399999999999995,0.94399999999999995,null,null,0.94399999999999995]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,1.2000000476837158,null,1.2000000476837158,null,1.2000000476837158,null,1.1000000238418579,null,null,null,null,1.2000000476837158,null,1,null,1,null,null,null,null,null,1,1,null,null,1]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.1,null,0.1,null,0.1,null,0.1,null,null,null,null,0.1,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"9.5",null,"9.5",null,"9.5",null,"9.5",null,null,null,null,"9.5",null,"9.5",null,"9.5",null,null,null,null,null,"9.5","9.5",null,null,"9.5"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,1.2,null,1.2,null,1.2,null,1.1000000000000001,null,null,null,null,1.2,null,1,null,1,null,null,null,null,null,1,1,null,null,1]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,2,null,2,null,2,null,2,null,null,null,null,2,null,2,null,2,null,null,null,null,null,2,2,null,null,2]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"RICH","index":209,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"RICH - Richmond (66/33kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T095 - Millchester BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Nth Queensland"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/33kV 6.3MVA ONAN;1x66/33kV 7.5/6.3MVA ONAF/ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.9%, 2020 S -0.8% W -0.8%2021 S -0.9% W -0.9%2022 S -0.5% W -0.5%2023 S -0.7% W -0.7"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"2.2 MVA on 03/12/2018 at 19:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,14.600000381469727,null,14.600000381469727,null,14.600000381469727,null,14.600000381469727,null,null,null,null,14.600000381469727,null,16.299999237060547,null,16.299999237060547,null,null,null,null,null,16.299999237060547,16.299999237060547,null,null,16.299999237060547]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,2.5,null,2.5,null,2.5,null,2.5,null,null,null,null,2.5,null,1.5,null,1.5,null,null,null,null,null,1.5,1.5,null,null,1.5]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.99299999999999999,null,0.99299999999999999,null,0.99299999999999999,null,0.99299999999999999,null,null,null,null,0.99299999999999999,null,0.96199999999999997,null,0.96199999999999997,null,null,null,null,null,0.96199999999999997,0.96199999999999997,null,null,0.96199999999999997]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,8.5,null,8.5,null,8.5,null,8.5,null,null,null,null,8.5,null,9.3999996185302734,null,9.3999996185302734,null,null,null,null,null,9.3999996185302734,9.3999996185302734,null,null,9.3999996185302734]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,2.4000000953674316,null,2.2999999523162842,null,2.2999999523162842,null,2.2999999523162842,null,null,null,null,2.2999999523162842,null,1.3999999761581421,null,1.3999999761581421,null,null,null,null,null,1.3999999761581421,1.3999999761581421,null,null,1.3999999761581421]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.1,null,0.1,null,0.1,null,0.1,null,null,null,null,0.1,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"724.5",null,"724.5",null,"724.5",null,"724.5",null,null,null,null,"724.5",null,"724.5",null,"724.5",null,null,null,null,null,"724.5","724.5",null,null,"724.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"ROEA","index":210,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"ROEA - Roma East (33/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T083 - Roma 33kV BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is South West"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x33/11kV 6.3MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -1.2%, 2020 S -0.7% W -0.7%2021 S -0.8% W -0.8%2022 S -0.6% W -0.6%2023 S -1.0% W -1.0"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"9.3 MVA on 20/02/2019 at 16:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,14,null,14,null,14,null,14,null,null,null,null,14,null,17.5,null,17.5,null,null,null,null,null,17.5,17.5,null,null,17.5]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,11.5,null,11.399999618530273,null,11.199999809265137,null,11.100000381469727,null,null,null,null,11,null,7.8000001907348633,null,7.6999998092651367,null,null,null,null,null,7.5999999046325684,7.5999999046325684,null,null,7.5]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.95299999999999996,null,0.95299999999999996,null,0.95299999999999996,null,0.95299999999999996,null,null,null,null,0.95299999999999996,null,0.97,null,0.97,null,null,null,null,null,0.97,0.97,null,null,0.97]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,8,null,8,null,8,null,8,null,null,null,null,8,null,9.3999996185302734,null,9.3999996185302734,null,null,null,null,null,9.3999996185302734,9.3999996185302734,null,null,9.3999996185302734]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,10.399999618530273,null,10.300000190734863,null,10.100000381469727,null,10,null,null,null,null,10,null,7.1999998092651367,null,7.1999998092651367,null,null,null,null,null,7.0999999046325684,7,null,null,7]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.5,null,0.5,null,0.5,null,0.5,null,null,null,null,0.5,null,0.4,null,0.4,null,null,null,null,null,0.4,0.4,null,null,0.4]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"50.5",null,"50.5",null,"50.5",null,"50.5",null,null,null,null,"50.5",null,"50.5",null,"50.5",null,null,null,null,null,"50.5","50.5",null,null,"50.5"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,2.4,null,2.2999999999999998,null,2.1,null,2,null,null,null,null,2]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,2,null,2,null,2,null,2,null,null,null,null,2,null,2,null,2,null,null,null,null,null,2,2,null,null,2]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,11.5,null,11.5,null,11.5,null,11.5,null,null,null,null,11.5,null,11.5,null,11.5,null,null,null,null,null,11.5,11.5,null,null,11.5]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"ROGL","index":211,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"ROGL - Rockhampton Glenmore (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"RMES - Rockhampton Mesh"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Capricornia"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x25MVA 66kV Transformer;1x66/11kV 20/25MVA ONAN/ONAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.7%, 2020 S -0.3% W -0.3%2021 S -0.3% W -0.3%2022 S -0.5% W -0.5%2023 S -0.9% W -0.9"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"22.2 MVA on 03/12/2018 at 15:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,54.299999237060547,null,54.299999237060547,null,54.299999237060547,null,54.299999237060547,null,null,null,null,54.299999237060547,null,55,null,55,null,null,null,null,null,55,55,null,null,55]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,23.700000762939453,null,23.600000381469727,null,23.200000762939453,null,23,null,null,null,null,23,null,12.899999618530273,null,12.800000190734863,null,null,null,null,null,12.800000190734863,12.699999809265137,null,null,12.600000381469727]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.999,null,0.999,null,0.999,null,0.999,null,null,null,null,0.999,null,0.92700000000000005,null,0.92700000000000005,null,null,null,null,null,0.92700000000000005,0.92700000000000005,null,null,0.92700000000000005]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,28.799999237060547,null,28.799999237060547,null,28.799999237060547,null,28.799999237060547,null,null,null,null,28.799999237060547,null,32.5,null,32.5,null,null,null,null,null,32.5,32.5,null,null,32.5]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,21.399999618530273,null,21.299999237060547,null,21,null,20.799999237060547,null,null,null,null,20.799999237060547,null,12.5,null,12.5,null,null,null,null,null,12.399999618530273,12.300000190734863,null,null,12.199999809265137]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,1.1000000000000001,null,1.1000000000000001,null,1.1000000000000001,null,1,null,null,null,null,1,null,0.6,null,0.6,null,null,null,null,null,0.6,0.6,null,null,0.6]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"18.5",null,"18.5",null,"18.5",null,"18.5",null,null,null,null,"18.5",null,"18.5",null,"18.5",null,null,null,null,null,"18.5","18.5",null,null,"18.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"ROLE","index":212,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"ROLE - Rolleston (66/22kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T163 - Rolleston BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Capricornia"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x12.5 MVA"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.6%, 2020 S -0.5% W -0.5%2021 S -0.5% W -0.5%2022 S -0.3% W -0.3%2023 S -0.4% W -0.4"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"7.4 MVA on 13/02/2019 at 17:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,25,null,25,null,25,null,25,null,null,null,null,25,null,25,null,25,null,null,null,null,null,25,25,null,null,25]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,8.3999996185302734,null,8.3000001907348633,null,8.1999998092651367,null,8.1999998092651367,null,null,null,null,8.1999998092651367,null,6,null,6,null,null,null,null,null,5.9000000953674316,5.9000000953674316,null,null,5.9000000953674316]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.995,null,0.995,null,0.995,null,0.995,null,null,null,null,0.995,null,0.998,null,0.998,null,null,null,null,null,0.998,0.998,null,null,0.998]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,12.5,null,12.5,null,12.5,null,12.5,null,null,null,null,12.5,null,12.5,null,12.5,null,null,null,null,null,12.5,12.5,null,null,12.5]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,7.6999998092651367,null,7.5999999046325684,null,7.5,null,7.5,null,null,null,null,7.5,null,5.6999998092651367,null,5.5999999046325684,null,null,null,null,null,5.5999999046325684,5.5999999046325684,null,null,5.5999999046325684]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.4,null,0.4,null,0.4,null,0.4,null,null,null,null,0.4,null,0.3,null,0.3,null,null,null,null,null,0.3,0.3,null,null,0.3]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"4.5",null,"4.5",null,"4.5",null,"4.5",null,null,null,null,"4.5",null,"4.5",null,"4.5",null,null,null,null,null,"4.5","4.5",null,null,"4.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"ROLL","index":213,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"ROLL - Rollingstone (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"TMES - Townsville Mesh"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Nth Queensland"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/11kV 2.5/2.9MVA ONAN/ONAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 1.2%, 2020 S 1.3% W 1.3%, 2021 S 1.3% W 1.3%, 2022 S 0.4% W 0.4%, 2023 S 0.2% W 0.2%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"1.4 MVA on 26/11/2018 at 18:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,3.7999999523162842,null,3.7999999523162842,null,3.7999999523162842,null,3.7999999523162842,null,null,null,null,3.7999999523162842,null,3.7999999523162842,null,3.7999999523162842,null,null,null,null,null,3.7999999523162842,3.7999999523162842,null,null,3.7999999523162842]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,1.6000000238418579,null,1.6000000238418579,null,1.6000000238418579,null,1.6000000238418579,null,null,null,null,1.6000000238418579,null,1.1000000238418579,null,1.1000000238418579,null,null,null,null,null,1.2000000476837158,1.2000000476837158,null,null,1.2000000476837158]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.97599999999999998,null,0.97599999999999998,null,0.97599999999999998,null,0.97599999999999998,null,null,null,null,0.97599999999999998,null,0.98699999999999999,null,0.98699999999999999,null,null,null,null,null,0.98699999999999999,0.98699999999999999,null,null,0.98699999999999999]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,1.3999999761581421,null,1.3999999761581421,null,1.3999999761581421,null,1.3999999761581421,null,null,null,null,1.3999999761581421,null,1,null,1.1000000238418579,null,null,null,null,null,1.1000000238418579,1.1000000238418579,null,null,1.1000000238418579]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.1,null,0.1,null,0.1,null,0.1,null,null,null,null,0.1,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"2.5",null,"2.5",null,"2.5",null,"2.5",null,null,null,null,"2.5",null,"2.5",null,"2.5",null,null,null,null,null,"2.5","2.5",null,null,"2.5"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,1.4,null,1.4,null,1.4,null,1.4,null,null,null,null,1.4,null,1,null,1.1000000000000001,null,null,null,null,null,1.1000000000000001,1.1000000000000001,null,null,1.1000000000000001]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,2,null,2,null,2,null,2,null,null,null,null,2,null,2,null,2,null,null,null,null,null,2,2,null,null,2]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"ROPL","index":214,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"ROPL - Ross Plains (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"TMES - Townsville Mesh"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Nth Queensland"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/11kV 12/15MVA ONAN/ONAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.3%, 2020 S -0.1% W -0.1%2021 S -0.2% W -0.2%2022 S -0.2% W -0.2%2023 S -0.7% W -0.7"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"16.4 MVA on 20/02/2019 at 17:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,33,null,33,null,33,null,33,null,null,null,null,33,null,37.799999237060547,null,37.799999237060547,null,null,null,null,null,37.799999237060547,37.799999237060547,null,null,37.799999237060547]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,17.899999618530273,null,17.799999237060547,null,17.600000381469727,null,17.5,null,null,null,null,17.5,null,8.6000003814697266,null,8.5,null,null,null,null,null,8.5,8.5,null,null,8.3999996185302734]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.998,null,0.998,null,0.998,null,0.998,null,null,null,null,0.998,null,0.98799999999999999,null,0.98799999999999999,null,null,null,null,null,0.98799999999999999,0.98799999999999999,null,null,0.98799999999999999]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,19.200000762939453,null,19.200000762939453,null,19.200000762939453,null,19.200000762939453,null,null,null,null,19.200000762939453,null,20.799999237060547,null,20.799999237060547,null,null,null,null,null,20.799999237060547,20.799999237060547,null,null,20.799999237060547]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,15.199999809265137,null,15.100000381469727,null,14.899999618530273,null,14.899999618530273,null,null,null,null,14.899999618530273,null,8.1999998092651367,null,8.1999998092651367,null,null,null,null,null,8.1999998092651367,8.1999998092651367,null,null,8.1000003814697266]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.8,null,0.8,null,0.7,null,0.7,null,null,null,null,0.7,null,0.4,null,0.4,null,null,null,null,null,0.4,0.4,null,null,0.4]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"7",null,"7",null,"7",null,"7",null,null,null,null,"7",null,"7",null,"7",null,null,null,null,null,"7","7",null,null,"7"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"ROSE","index":215,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"ROSE - Rosella (33/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T065 - Alligator Creek BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Mackay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x33/11kV 4.5MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.3%, 2020 S 0.4% W 0.4%, 2021 S 0.4% W 0.4%, 2022 S 0.6% W 0.6%, 2023 S 0.4% W 0.4%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"5.1 MVA on 26/03/2019 at 16:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,11.5,null,11.5,null,11.5,null,11.5,null,null,null,null,11.5,null,12.300000190734863,null,12.300000190734863,null,null,null,null,null,12.300000190734863,12.300000190734863,null,null,12.300000190734863]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,6.4000000953674316,null,6.4000000953674316,null,6.3000001907348633,null,6.4000000953674316,null,null,null,null,6.4000000953674316,null,3.7000000476837158,null,3.7000000476837158,null,null,null,null,null,3.7000000476837158,3.7999999523162842,null,null,3.7999999523162842]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.94499999999999995,null,0.94499999999999995,null,0.94499999999999995,null,0.94499999999999995,null,null,null,null,0.94499999999999995,null,0.93,null,0.93,null,null,null,null,null,0.93,0.93,null,null,0.93]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,6.5999999046325684,null,6.5999999046325684,null,6.5999999046325684,null,6.5999999046325684,null,null,null,null,6.5999999046325684,null,6.6999998092651367,null,6.6999998092651367,null,null,null,null,null,6.6999998092651367,6.6999998092651367,null,null,6.6999998092651367]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,5.9000000953674316,null,5.9000000953674316,null,5.9000000953674316,null,5.9000000953674316,null,null,null,null,6,null,3.5,null,3.5999999046325684,null,null,null,null,null,3.5999999046325684,3.5999999046325684,null,null,3.5999999046325684]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.3,null,0.3,null,0.3,null,0.3,null,null,null,null,0.3,null,0.2,null,0.2,null,null,null,null,null,0.2,0.2,null,null,0.2]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"57",null,"57",null,"57",null,"57",null,null,null,null,"57",null,"57",null,"57",null,null,null,null,null,"57","57",null,null,"57"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,1.6000000238418579,null,1.6000000238418579,null,1.6000000238418579,null,1.6000000238418579,null,null,null,null,1.6000000238418579,null,1.6000000238418579,null,1.6000000238418579,null,null,null,null,null,1.6000000238418579,1.6000000238418579,null,null,1.6000000238418579]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,1.2000000476837158,null,1.2000000476837158,null,1.2000000476837158,null,1.2000000476837158,null,null,null,null,1.2000000476837158,null,1.2000000476837158,null,1.2000000476837158,null,null,null,null,null,1.2000000476837158,1.2000000476837158,null,null,1.2000000476837158]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"ROSO","index":216,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"ROSO - Rockhampton South (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"RMES - Rockhampton Mesh"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Capricornia"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/11kV 15/20MVA ONAN/OFDAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -1.3%, 2020 S -0.7% W -0.7%2021 S -0.7% W -0.7%2022 S -0.6% W -0.6%2023 S -0.8% W -0.8"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"14.5 MVA on 03/12/2018 at 15:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,32.700000762939453,null,32.700000762939453,null,32.700000762939453,null,32.700000762939453,null,null,null,null,32.700000762939453,null,32.700000762939453,null,32.700000762939453,null,null,null,null,null,32.700000762939453,32.700000762939453,null,null,32.700000762939453]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,14.300000190734863,null,14.100000381469727,null,13.899999618530273,null,13.800000190734863,null,null,null,null,13.800000190734863,null,8.1000003814697266,null,8,null,null,null,null,null,7.9000000953674316,7.8000001907348633,null,null,7.8000001907348633]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.997,null,0.998,null,0.998,null,0.998,null,null,null,null,0.998,null,1,null,1,null,null,null,null,null,1,1,null,null,1]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,16.5,null,16.5,null,16.5,null,16.5,null,null,null,null,16.5,null,18,null,18,null,null,null,null,null,18,18,null,null,18]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,13.300000190734863,null,13.199999809265137,null,12.899999618530273,null,12.899999618530273,null,null,null,null,12.800000190734863,null,7.5999999046325684,null,7.5999999046325684,null,null,null,null,null,7.5,7.4000000953674316,null,null,7.4000000953674316]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.7,null,0.7,null,0.6,null,0.6,null,null,null,null,0.6,null,0.4,null,0.4,null,null,null,null,null,0.4,0.4,null,null,0.4]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"11.5",null,"11.5",null,"11.5",null,"11.5",null,null,null,null,"11.5",null,"11.5",null,"11.5",null,null,null,null,null,"11.5","11.5",null,null,"11.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"ROST","index":217,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"ROST - Rocky Street (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T059 - Maryborough BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Wide Bay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/11kV 15/20/25MVA ONAN/ONAF/ODAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.1%, 2020 S 0.2% W 0.2%, 2021 S 0.2% W 0.2%, 2022 S 0.2% W 0.2%, 2023 S -0.1% W -0.1"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"19.8 MVA on 13/02/2019 at 16:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,57.5,null,57.5,null,57.5,null,57.5,null,null,null,null,57.5,null,64.300003051757813,null,64.300003051757813,null,null,null,null,null,64.300003051757813,64.300003051757813,null,null,64.300003051757813]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,26,null,25.899999618530273,null,27.899999618530273,null,30.100000381469727,null,null,null,null,30.299999237060547,null,17.600000381469727,null,19.5,null,null,null,null,null,19.5,21.299999237060547,null,null,23.100000381469727]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.98199999999999998,null,0.98199999999999998,null,0.97899999999999998,null,0.97699999999999998,null,null,null,null,0.97599999999999998,null,1,null,0.999,null,null,null,null,null,0.999,0.998,null,null,0.997]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,32.099998474121094,null,32.099998474121094,null,32.099998474121094,null,32.099998474121094,null,null,null,null,32.099998474121094,null,36.099998474121094,null,36.099998474121094,null,null,null,null,null,36.099998474121094,36.099998474121094,null,null,36.099998474121094]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,23.899999618530273,null,23.799999237060547,null,25.899999618530273,null,28.100000381469727,null,null,null,null,28.299999237060547,null,16.700000762939453,null,18.600000381469727,null,null,null,null,null,18.600000381469727,20.399999618530273,null,null,22.200000762939453]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,1.2,null,1.2,null,1.3,null,1.4,null,null,null,null,1.4,null,0.8,null,0.9,null,null,null,null,null,0.9,1,null,null,1.1000000000000001]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"7.5",null,"7.5",null,"7.5",null,"7.5",null,null,null,null,"7.5",null,"7.5",null,"7.5",null,null,null,null,null,"7.5","7.5",null,null,"7.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"ROWE","index":218,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"ROWE - Roma West (33/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T083 - Roma 33kV BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is South West"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x33/11kV 2.5MVA ONAN;1xROWESS T1 33KV TRANSF 1 TRANSF T1"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -1.2%, 2020 S -0.8% W -0.8%2021 S -0.5% W -0.5%2022 S 0.1% W 0.1%, 2023 S -0.4% W -0.4"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"4.8 MVA on 24/01/2019 at 15:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,6.3000001907348633,null,6.3000001907348633,null,6.3000001907348633,null,6.3000001907348633,null,null,null,null,6.3000001907348633,null,6.3000001907348633,null,6.3000001907348633,null,null,null,null,null,6.3000001907348633,6.3000001907348633,null,null,6.3000001907348633]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,5.9000000953674316,null,5.8000001907348633,null,5.8000001907348633,null,5.8000001907348633,null,null,null,null,5.8000001907348633,null,4.5,null,4.4000000953674316,null,null,null,null,null,4.3000001907348633,4.3000001907348633,null,null,4.3000001907348633]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.95899999999999996,null,0.95599999999999996,null,0.95899999999999996,null,0.95899999999999996,null,null,null,null,0.95599999999999996,null,0.98699999999999999,null,0.98599999999999999,null,null,null,null,null,0.98599999999999999,0.98599999999999999,null,null,0.98599999999999999]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,3.2000000476837158,null,3.2000000476837158,null,3.2000000476837158,null,3.2000000476837158,null,null,null,null,3.2000000476837158,null,3.2000000476837158,null,3.2000000476837158,null,null,null,null,null,3.2000000476837158,3.2000000476837158,null,null,3.2000000476837158]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,5.1999998092651367,null,5.0999999046325684,null,5.0999999046325684,null,5.0999999046325684,null,null,null,null,5.0999999046325684,null,4.0999999046325684,null,4,null,null,null,null,null,4,4,null,null,4]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.3,null,0.3,null,0.3,null,0.3,null,null,null,null,0.3,null,0.2,null,0.2,null,null,null,null,null,0.2,0.2,null,null,0.2]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"7.5",null,"7.5",null,"7.5",null,"7.5",null,null,null,null,"7.5",null,"7.5",null,"7.5",null,null,null,null,null,"7.5","7.5",null,null,"7.5"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,2,null,1.9,null,1.9,null,1.9,null,null,null,null,1.9,null,0.9,null,0.8,null,null,null,null,null,0.8,0.8,null,null,0.8]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,4,null,4,null,4,null,4,null,null,null,null,4,null,4,null,4,null,null,null,null,null,4,4,null,null,4]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"ROWO","index":219,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"ROWO - Roo Works (33/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"SGZA - St George ZS Accumulator"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is South West"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x33/11kV 2MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.3%, 2020 S -0.2% W -0.2%2021 S -0.3% W -0.3%2022 S -0.2% W -0.2%2023 S -0.4% W -0.4"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"1.2 MVA on 21/12/2018 at 17:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,2.4000000953674316,null,2.4000000953674316,null,2.4000000953674316,null,2.4000000953674316,null,null,null,null,2.4000000953674316,null,2.4000000953674316,null,2.4000000953674316,null,null,null,null,null,2.4000000953674316,2.4000000953674316,null,null,2.4000000953674316]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,1.5,null,1.3999999761581421,null,1.3999999761581421,null,1.3999999761581421,null,null,null,null,1.3999999761581421,null,0.5,null,0.5,null,null,null,null,null,0.5,0.5,null,null,0.5]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.90200000000000002,null,0.90200000000000002,null,0.90200000000000002,null,0.90200000000000002,null,null,null,null,0.90200000000000002,null,0.97099999999999997,null,0.97099999999999997,null,null,null,null,null,0.97099999999999997,0.97099999999999997,null,null,0.97099999999999997]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,1.2000000476837158,null,1.2000000476837158,null,1.2000000476837158,null,1.2000000476837158,null,null,null,null,1.2000000476837158,null,0.5,null,0.5,null,null,null,null,null,0.5,0.5,null,null,0.5]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.1,null,0.1,null,0.1,null,0.1,null,null,null,null,0.1,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"4",null,"4",null,"4",null,"4",null,null,null,null,"4",null,"4",null,"4",null,null,null,null,null,"4","4",null,null,"4"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,1.2,null,1.2,null,1.2,null,1.2,null,null,null,null,1.2,null,0.5,null,0.5,null,null,null,null,null,0.5,0.5,null,null,0.5]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,1.2000000476837158,null,1.2000000476837158,null,1.2000000476837158,null,1.2000000476837158,null,null,null,null,1.2000000476837158,null,1.2000000476837158,null,1.2000000476837158,null,null,null,null,null,1.2000000476837158,1.2000000476837158,null,null,1.2000000476837158]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"SAGE","index":220,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"SAGE - St. George (66/33kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T083 - Roma 66kV BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is South West"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/33/11kV 20MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.3%, 2020 S -0.1% W -0.1%2021 S -0.2% W -0.2%2022 S -0.2% W -0.2%2023 S -0.3% W -0.3"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"12.1 MVA on 21/12/2018 at 18:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,48.700000762939453,null,48.700000762939453,null,48.700000762939453,null,48.700000762939453,null,null,null,null,48.700000762939453,null,55.900001525878906,null,55.900001525878906,null,null,null,null,null,55.900001525878906,55.900001525878906,null,null,55.900001525878906]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,14.100000381469727,null,14,null,13.800000190734863,null,13.800000190734863,null,null,null,null,13.800000190734863,null,11.5,null,11.5,null,null,null,null,null,11.399999618530273,11.399999618530273,null,null,11.399999618530273]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.93300000000000005,null,0.93300000000000005,null,0.93300000000000005,null,0.93300000000000005,null,null,null,null,0.93300000000000005,null,0.93899999999999995,null,0.93899999999999995,null,null,null,null,null,0.93899999999999995,0.93899999999999995,null,null,0.93899999999999995]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,27.600000381469727,null,27.600000381469727,null,27.600000381469727,null,27.600000381469727,null,null,null,null,27.600000381469727,null,29.899999618530273,null,29.899999618530273,null,null,null,null,null,29.899999618530273,29.899999618530273,null,null,29.899999618530273]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,12.399999618530273,null,12.300000190734863,null,12.199999809265137,null,12.100000381469727,null,null,null,null,12.199999809265137,null,10.300000190734863,null,10.300000190734863,null,null,null,null,null,10.199999809265137,10.199999809265137,null,null,10.199999809265137]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.6,null,0.6,null,0.6,null,0.6,null,null,null,null,0.6,null,0.5,null,0.5,null,null,null,null,null,0.5,0.5,null,null,0.5]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"18",null,"18",null,"18",null,"18",null,null,null,null,"18",null,"18",null,"18",null,null,null,null,null,"18","18",null,null,"18"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"SAGT","index":221,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"SAGT - St. George Town (33/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"SGZA - St George ZS Accumulator"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is South West"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x33/11kV 3MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -1.4%, 2020 S -0.8% W -0.8%2021 S -1.0% W -1.0%2022 S -0.6% W -0.6%2023 S -1.0% W -1.0"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"5.1 MVA on 04/01/2019 at 17:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,6.5999999046325684,null,6.5999999046325684,null,6.5999999046325684,null,6.5999999046325684,null,null,null,null,6.5999999046325684,null,6.5999999046325684,null,6.5999999046325684,null,null,null,null,null,6.5999999046325684,6.5999999046325684,null,null,6.5999999046325684]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,5.8000001907348633,null,5.8000001907348633,null,5.5999999046325684,null,5.5999999046325684,null,null,null,null,5.5999999046325684,null,4.0999999046325684,null,4.0999999046325684,null,null,null,null,null,4,4,null,null,3.9000000953674316]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.96099999999999997,null,0.96099999999999997,null,0.96,null,0.96099999999999997,null,null,null,null,0.96099999999999997,null,0.96599999999999997,null,0.96599999999999997,null,null,null,null,null,0.96599999999999997,0.96599999999999997,null,null,0.96599999999999997]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,3.5,null,3.5,null,3.5,null,3.5,null,null,null,null,3.5,null,3.5999999046325684,null,3.5999999046325684,null,null,null,null,null,3.5999999046325684,3.5999999046325684,null,null,3.5999999046325684]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,5.1999998092651367,null,5.0999999046325684,null,5,null,5,null,null,null,null,5,null,3.7999999523162842,null,3.7999999523162842,null,null,null,null,null,3.7000000476837158,3.7000000476837158,null,null,3.7000000476837158]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.3,null,0.3,null,0.3,null,0.3,null,null,null,null,0.3,null,0.2,null,0.2,null,null,null,null,null,0.2,0.2,null,null,0.2]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"16",null,"16",null,"16",null,"16",null,null,null,null,"16",null,"16",null,"16",null,null,null,null,null,"16","16",null,null,"16"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,1.7,null,1.6,null,1.5,null,1.5,null,null,null,null,1.5,null,0.2,null,0.2,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0.80000001192092896,null,0.80000001192092896,null,0.80000001192092896,null,0.80000001192092896,null,null,null,null,0.80000001192092896,null,0.80000001192092896,null,0.80000001192092896,null,null,null,null,null,0.80000001192092896,0.80000001192092896,null,null,0.80000001192092896]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,10,null,10,null,10,null,10,null,null,null,null,10,null,10,null,10,null,null,null,null,null,10,10,null,null,10]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"SARI","index":222,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"SARI - Sarina (33/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T065 - Alligator Creek BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Mackay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x33/11kV 10/12.5MVA ONAN/ONAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 17.5 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.1%, 2020 S 0.4% W 0.4%, 2021 S 0.4% W 0.4%, 2022 S 0.7% W 0.7%, 2023 S 0.4% W 0.4%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"15.1 MVA on 28/11/2018 at 19:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,24,null,24,null,24,null,24,null,null,null,null,24,null,26.799999237060547,null,26.799999237060547,null,null,null,null,null,26.799999237060547,26.799999237060547,null,null,26.799999237060547]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,16.100000381469727,null,16.100000381469727,null,16,null,16.100000381469727,null,null,null,null,16.299999237060547,null,12.600000381469727,null,12.600000381469727,null,null,null,null,null,12.600000381469727,12.699999809265137,null,null,12.800000190734863]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.96399999999999997,null,0.96399999999999997,null,0.96399999999999997,null,0.96399999999999997,null,null,null,null,0.96399999999999997,null,0.97199999999999998,null,0.97199999999999998,null,null,null,null,null,0.97199999999999998,0.97199999999999998,null,null,0.97199999999999998]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,13.699999809265137,null,13.699999809265137,null,13.699999809265137,null,13.699999809265137,null,null,null,null,13.699999809265137,null,14.899999618530273,null,14.899999618530273,null,null,null,null,null,14.899999618530273,14.899999618530273,null,null,14.899999618530273]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,15.100000381469727,null,15.100000381469727,null,15,null,15.100000381469727,null,null,null,null,15.300000190734863,null,11.199999809265137,null,11.199999809265137,null,null,null,null,null,11.199999809265137,11.300000190734863,null,null,11.399999618530273]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.8,null,0.8,null,0.8,null,0.8,null,null,null,null,0.8,null,0.6,null,0.6,null,null,null,null,null,0.6,0.6,null,null,0.6]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"10",null,"10",null,"10",null,"10",null,null,null,null,"10",null,"10",null,"10",null,null,null,null,null,"10","10",null,null,"10"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,1.4,null,1.4,null,1.3,null,1.4,null,null,null,null,1.6]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,1.1000000238418579,null,1.1000000238418579,null,1.1000000238418579,null,1.1000000238418579,null,null,null,null,1.1000000238418579,null,1.1000000238418579,null,1.1000000238418579,null,null,null,null,null,1.1000000238418579,1.1000000238418579,null,null,1.1000000238418579]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0.5,null,0.5,null,0.5,null,0.5,null,null,null,null,0.5,null,0.5,null,0.5,null,null,null,null,null,0.5,0.5,null,null,0.5]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"SAUN","index":223,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"SAUN - Saunders (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"TMES - Townsville Mesh"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Nth Queensland"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/11kV 4MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.3%, 2020 S -0.1% W -0.1%2021 S -0.1% W -0.1%2022 S -0.6% W -0.6%2023 S -0.6% W -0.6"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"1.3 MVA on 28/11/2018 at 14:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,5.0999999046325684,null,5.0999999046325684,null,5.0999999046325684,null,5.0999999046325684,null,null,null,null,5.0999999046325684,null,5.4000000953674316,null,5.4000000953674316,null,null,null,null,null,5.4000000953674316,5.4000000953674316,null,null,5.4000000953674316]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,1.2000000476837158,null,1.2000000476837158,null,1.2000000476837158,null,1.1000000238418579,null,null,null,null,1.1000000238418579,null,1.1000000238418579,null,1.1000000238418579,null,null,null,null,null,1.1000000238418579,1.1000000238418579,null,null,1.1000000238418579]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.98499999999999999,null,0.98499999999999999,null,0.98499999999999999,null,0.95399999999999996,null,null,null,null,0.95399999999999996,null,0.86,null,0.86,null,null,null,null,null,0.86,0.86,null,null,0.86]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,1.1000000238418579,null,1.1000000238418579,null,1.1000000238418579,null,1,null,null,null,null,1,null,1,null,1,null,null,null,null,null,1,1,null,null,1]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.1,null,0.1,null,0.1,null,0.1,null,null,null,null,0.1,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"62",null,"62",null,"62",null,"62",null,null,null,null,"62",null,"62",null,"62",null,null,null,null,null,"62","62",null,null,"62"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,1.1000000000000001,null,1.1000000000000001,null,1.1000000000000001,null,1,null,null,null,null,1,null,1,null,1,null,null,null,null,null,1,1,null,null,1]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,2.7000000476837158,null,2.7000000476837158,null,2.7000000476837158,null,2.7000000476837158,null,null,null,null,2.7000000476837158,null,2.7000000476837158,null,2.7000000476837158,null,null,null,null,null,2.7000000476837158,2.7000000476837158,null,null,2.7000000476837158]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"SHUT","index":224,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"SHUT - Shutehaven (66/22kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T039 - Proserpine BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Mackay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/22kV 15/20/25MVA ONAN/ONAF/ODAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.6%, 2020 S 0.4% W 0.4%, 2021 S 0.3% W 0.3%, 2022 S 0.3% W 0.3%, 2023 S 0.1% W 0.1%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"8.1 MVA on 26/11/2018 at 14:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,30.399999618530273,null,30.399999618530273,null,30.399999618530273,null,30.399999618530273,null,null,null,null,30.399999618530273,null,33.200000762939453,null,33.200000762939453,null,null,null,null,null,33.200000762939453,33.200000762939453,null,null,33.200000762939453]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,9.1000003814697266,null,9.1000003814697266,null,9.1000003814697266,null,9.1000003814697266,null,null,null,null,9.1999998092651367,null,4.5999999046325684,null,4.5999999046325684,null,null,null,null,null,4.5999999046325684,4.5999999046325684,null,null,4.6999998092651367]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.97899999999999998,null,0.97899999999999998,null,0.97899999999999998,null,0.97899999999999998,null,null,null,null,0.97899999999999998,null,0.98399999999999999,null,0.98399999999999999,null,null,null,null,null,0.98399999999999999,0.98399999999999999,null,null,0.98399999999999999]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,8.6000003814697266,null,8.6000003814697266,null,8.5,null,8.6000003814697266,null,null,null,null,8.6000003814697266,null,4.5999999046325684,null,4.5999999046325684,null,null,null,null,null,4.5999999046325684,4.5999999046325684,null,null,4.6999998092651367]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.4,null,0.4,null,0.4,null,0.4,null,null,null,null,0.4,null,0.2,null,0.2,null,null,null,null,null,0.2,0.2,null,null,0.2]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"25.5",null,"25.5",null,"25.5",null,"25.5",null,null,null,null,"25.5",null,"25.5",null,"25.5",null,null,null,null,null,"25.5","25.5",null,null,"25.5"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,8.6,null,8.6,null,8.5,null,8.6,null,null,null,null,8.6,null,4.5999999999999996,null,4.5999999999999996,null,null,null,null,null,4.5999999999999996,4.5999999999999996,null,null,4.7]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0.30000001192092896,null,0.30000001192092896,null,0.30000001192092896,null,0.30000001192092896,null,null,null,null,0.30000001192092896,null,0.30000001192092896,null,0.30000001192092896,null,null,null,null,null,0.30000001192092896,0.30000001192092896,null,null,0.30000001192092896]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,13.300000190734863,null,13.300000190734863,null,13.300000190734863,null,13.300000190734863,null,null,null,null,13.300000190734863,null,13.300000190734863,null,13.300000190734863,null,null,null,null,null,13.300000190734863,13.300000190734863,null,null,13.300000190734863]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"SKIE","index":225,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"SKIE - Chinchilla Skid (33/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T013 - Chinchilla BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is South West"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x33/11kV 5MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.5%, 2020 S 0.7% W 0.7%, 2021 S 0.7% W 0.7%, 2022 S 0.7% W 0.7%, 2023 S 0.4% W 0.4%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"5.6 MVA on 20/02/2019 at 18:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,7.5,null,7.5,null,7.5,null,7.5,null,null,null,null,7.5,null,7.5,null,7.5,null,null,null,null,null,7.5,7.5,null,null,7.5]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,7,null,7.0999999046325684,null,7,null,7.0999999046325684,null,null,null,null,7.1999998092651367,null,5.3000001907348633,null,5.3000001907348633,null,null,null,null,null,5.3000001907348633,5.3000001907348633,null,null,5.4000000953674316]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.96299999999999997,null,0.96299999999999997,null,0.96299999999999997,null,0.96299999999999997,null,null,null,null,0.96299999999999997,null,0.97699999999999998,null,0.97699999999999998,null,null,null,null,null,0.97699999999999998,0.97699999999999998,null,null,0.97699999999999998]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,6.0999999046325684,null,6.0999999046325684,null,6.0999999046325684,null,6.1999998092651367,null,null,null,null,6.1999998092651367,null,4.8000001907348633,null,4.8000001907348633,null,null,null,null,null,4.8000001907348633,4.9000000953674316,null,null,4.9000000953674316]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.3,null,0.3,null,0.3,null,0.3,null,null,null,null,0.3,null,0.2,null,0.2,null,null,null,null,null,0.2,0.2,null,null,0.2]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"3.5",null,"3.5",null,"3.5",null,"3.5",null,null,null,null,"3.5",null,"3.5",null,"3.5",null,null,null,null,null,"3.5","3.5",null,null,"3.5"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,6.1,null,6.1,null,6.1,null,6.2,null,null,null,null,6.2,null,4.8,null,4.8,null,null,null,null,null,4.8,4.9000000000000004,null,null,4.9000000000000004]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,2.2000000476837158,null,2.2000000476837158,null,2.2000000476837158,null,2.2000000476837158,null,null,null,null,2.2000000476837158,null,2.2000000476837158,null,2.2000000476837158,null,null,null,null,null,2.2000000476837158,2.2000000476837158,null,null,2.2000000476837158]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,10,null,10,null,10,null,10,null,null,null,null,10,null,10,null,10,null,null,null,null,null,10,10,null,null,10]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"SOBL","index":226,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"SOBL - South Blackwater (66/22kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T032 - Blackwater BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Capricornia"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/22kV 0.3MVA ON"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.1%, 2020 S -0.1% W -0.1%2021 S -0.1% W -0.1%2022 S -0.0% W -0.0%2023 S -0.0% W -0.0"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"0.4 MVA on 13/02/2019 at 19:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,0.36,null,0.36,null,0.36,null,0.36,null,null,null,null,0.36,null,0.36,null,0.36,null,null,null,null,null,0.36,0.36,null,null,0.36]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,0.38,null,0.38,null,0.38,null,0.38,null,null,null,null,0.38,null,0.30000001192092896,null,0.30000001192092896,null,null,null,null,null,0.30000001192092896,0.30000001192092896,null,null,0.30000001192092896]
[null,null,null,null,"LARn (MVA)",null,null,null,null,null,0.14000000000000001,null,0.14000000000000001,null,0.14000000000000001,null,0.14000000000000001,null,null,null,null,0.14000000000000001]
[null,null,null,null,"LARn (MW)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.84799999999999998,null,0.84799999999999998,null,0.84799999999999998,null,0.84799999999999998,null,null,null,null,0.84799999999999998,null,0.79900000000000004,null,0.79900000000000004,null,null,null,null,null,0.79900000000000004,0.79900000000000004,null,null,0.79900000000000004]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,0.40000000596046448,null,0.40000000596046448,null,0.40000000596046448,null,0.40000000596046448,null,null,null,null,0.40000000596046448,null,0.30000001192092896,null,0.30000001192092896,null,null,null,null,null,0.30000001192092896,0.30000001192092896,null,null,0.30000001192092896]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,130,null,130,null,130,null,130,null,null,null,null,130,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,0.4,null,0.4,null,0.4,null,0.4,null,null,null,null,0.4,null,0.3,null,0.3,null,null,null,null,null,0.3,0.3,null,null,0.3]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,1,null,1,null,1,null,1,null,null,null,null,1,null,1,null,1,null,null,null,null,null,1,1,null,null,1]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0.40000000596046448,null,0.40000000596046448,null,0.40000000596046448,null,0.40000000596046448,null,null,null,null,0.40000000596046448,null,0.40000000596046448,null,0.40000000596046448,null,null,null,null,null,0.40000000596046448,0.40000000596046448,null,null,0.40000000596046448]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[null,null,null,null,"Note:  System spare is kept on hand and some additional overloading is accepted in this case"]
[]
[null,null,"Return to Index"]

{"sheet":"SOBU","index":227,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"SOBU - South Bundaberg (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T020 - Bundaberg BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Wide Bay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/11kV 14/19MVA ONAN/ONAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.5%, 2020 S 0.7% W 0.7%, 2021 S 0.7% W 0.7%, 2022 S 0.6% W 0.6%, 2023 S 0.4% W 0.4%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"12.8 MVA on 19/02/2019 at 18:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,42.400001525878906,null,42.400001525878906,null,42.400001525878906,null,42.400001525878906,null,null,null,null,42.400001525878906,null,46.599998474121094,null,46.599998474121094,null,null,null,null,null,46.599998474121094,46.599998474121094,null,null,46.599998474121094]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,14.600000381469727,null,14.600000381469727,null,14.600000381469727,null,14.600000381469727,null,null,null,null,14.800000190734863,null,10.199999809265137,null,10.300000190734863,null,null,null,null,null,10.300000190734863,10.399999618530273,null,null,10.399999618530273]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,1,null,1,null,1,null,1,null,null,null,null,1,null,0.995,null,0.995,null,null,null,null,null,0.995,0.995,null,null,0.996]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,24.200000762939453,null,24.200000762939453,null,24.200000762939453,null,24.200000762939453,null,null,null,null,24.200000762939453,null,25.399999618530273,null,25.399999618530273,null,null,null,null,null,25.399999618530273,25.399999618530273,null,null,25.399999618530273]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,13.600000381469727,null,13.699999809265137,null,13.600000381469727,null,13.699999809265137,null,null,null,null,13.800000190734863,null,9.6999998092651367,null,9.8000001907348633,null,null,null,null,null,9.8000001907348633,9.8999996185302734,null,null,9.8999996185302734]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.7,null,0.7,null,0.7,null,0.7,null,null,null,null,0.7,null,0.5,null,0.5,null,null,null,null,null,0.5,0.5,null,null,0.5]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"16",null,"16",null,"16",null,"16",null,null,null,null,"16",null,"16",null,"16",null,null,null,null,null,"16","16",null,null,"16"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,1,null,1,null,1,null,1,null,null,null,null,1,null,1,null,1,null,null,null,null,null,1,1,null,null,1]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"SOKO","index":228,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"SOKO - South Kolan (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T020 - Bundaberg BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Wide Bay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/11kV 7.5/10MVA ON/ONB"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 1.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -1.0%, 2020 S -1.8% W -1.8%2021 S -0.9% W -0.9%2022 S -1.2% W -1.2%2023 S -1.4% W -1.4"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"5 MVA on 19/02/2019 at 19:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,27.5,null,27.5,null,27.5,null,27.5,null,null,null,null,27.5,null,29.899999618530273,null,29.899999618530273,null,null,null,null,null,29.899999618530273,29.899999618530273,null,null,29.899999618530273]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,7.0999999046325684,null,7,null,6.9000000953674316,null,6.8000001907348633,null,null,null,null,6.6999998092651367,null,4.5,null,4.4000000953674316,null,null,null,null,null,4.4000000953674316,4.3000001907348633,null,null,4.3000001907348633]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.93799999999999994,null,0.93799999999999994,null,0.93799999999999994,null,0.93799999999999994,null,null,null,null,0.93799999999999994,null,0.94099999999999995,null,0.94099999999999995,null,null,null,null,null,0.94099999999999995,0.94099999999999995,null,null,0.94099999999999995]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,15,null,15,null,15,null,15,null,null,null,null,15,null,15,null,15,null,null,null,null,null,15,15,null,null,15]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,6.1999998092651367,null,6.0999999046325684,null,5.9000000953674316,null,5.9000000953674316,null,null,null,null,5.8000001907348633,null,4.0999999046325684,null,4,null,null,null,null,null,4,3.9000000953674316,null,null,3.9000000953674316]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.3,null,0.3,null,0.3,null,0.3,null,null,null,null,0.3,null,0.2,null,0.2,null,null,null,null,null,0.2,0.2,null,null,0.2]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"14",null,"14",null,"14",null,"14",null,null,null,null,"14",null,"14",null,"14",null,null,null,null,null,"14","14",null,null,"14"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"SOMA","index":229,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"SOMA - South Mackay (33/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T038 - Mackay BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Mackay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x33/11kV 12.5/15/20MVA ONAN/ONAF/ODAF;1x33/11kV 12.5/15/21MVA ONAN/ONAF/ODAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 2.4 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -1.0%, 2020 S -0.3% W -0.3%2021 S -0.2% W -0.2%2022 S -0.2% W -0.2%2023 S -0.4% W -0.4"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"19.2 MVA on 28/11/2018 at 13:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,40,null,40,null,40,null,40,null,null,null,null,40,null,40,null,40,null,null,null,null,null,40,40,null,null,40]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,19.700000762939453,null,19.600000381469727,null,19.399999618530273,null,19.399999618530273,null,null,null,null,19.399999618530273,null,17.299999237060547,null,17.200000762939453,null,null,null,null,null,17.100000381469727,17.100000381469727,null,null,17.100000381469727]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.999,null,0.999,null,0.998,null,0.998,null,null,null,null,0.999,null,0.99399999999999999,null,0.99399999999999999,null,null,null,null,null,0.99299999999999999,0.99299999999999999,null,null,0.99299999999999999]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,21,null,21,null,21,null,21,null,null,null,null,21,null,22,null,22,null,null,null,null,null,22,22,null,null,22]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,18.700000762939453,null,18.600000381469727,null,18.399999618530273,null,18.399999618530273,null,null,null,null,18.399999618530273,null,16.299999237060547,null,16.200000762939453,null,null,null,null,null,16.100000381469727,16.100000381469727,null,null,16.100000381469727]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.9,null,0.9,null,0.9,null,0.9,null,null,null,null,0.9,null,0.8,null,0.8,null,null,null,null,null,0.8,0.8,null,null,0.8]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"46.5",null,"46.5",null,"46.5",null,"46.5",null,null,null,null,"46.5",null,"46.5",null,"46.5",null,null,null,null,null,"46.5","46.5",null,null,"46.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,1.7999999523162842,null,1.7999999523162842,null,1.7999999523162842,null,1.7999999523162842,null,null,null,null,1.7999999523162842,null,1.7999999523162842,null,1.7999999523162842,null,null,null,null,null,1.7999999523162842,1.7999999523162842,null,null,1.7999999523162842]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,2,null,2,null,2,null,2,null,null,null,null,2,null,2,null,2,null,null,null,null,null,2,2,null,null,2]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"SOTO","index":230,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"SOTO - South Toowoomba (33/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T043 - South Toowoomba BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is South West"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 3x33/11kV 11.5MVA ONAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.2%, 2020 S -0.3% W -0.3%2021 S -0.1% W -0.1%2022 S -0.3% W -0.3%2023 S -0.8% W -0.8"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"25 MVA on 18/06/2018 at 18:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,37.400001525878906,null,37.400001525878906,null,37.400001525878906,null,37.400001525878906,null,null,null,null,37.400001525878906,null,42.400001525878906,null,42.400001525878906,null,null,null,null,null,42.400001525878906,42.400001525878906,null,null,42.400001525878906]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,23.799999237060547,null,23.700000762939453,null,23.399999618530273,null,23.200000762939453,null,null,null,null,23.399999618530273,null,26.899999618530273,null,26.799999237060547,null,null,null,null,null,26.600000381469727,26.5,null,null,26.399999618530273]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.95299999999999996,null,0.95299999999999996,null,0.95299999999999996,null,0.95299999999999996,null,null,null,null,0.95299999999999996,null,0.97099999999999997,null,0.97099999999999997,null,null,null,null,null,0.97099999999999997,0.97099999999999997,null,null,0.97099999999999997]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,28.299999237060547,null,28.299999237060547,null,28.299999237060547,null,28.299999237060547,null,null,null,null,28.299999237060547,null,31.200000762939453,null,31.200000762939453,null,null,null,null,null,31.200000762939453,31.200000762939453,null,null,31.200000762939453]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,21.299999237060547,null,21.200000762939453,null,20.899999618530273,null,20.799999237060547,null,null,null,null,21,null,24.700000762939453,null,24.600000381469727,null,null,null,null,null,24.5,24.399999618530273,null,null,24.200000762939453]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,1.1000000000000001,null,1.1000000000000001,null,1,null,1,null,null,null,null,1.1000000000000001,null,1.2,null,1.2,null,null,null,null,null,1.2,1.2,null,null,1.2]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"4",null,"4",null,"4",null,"4",null,null,null,null,"4",null,"4",null,"4",null,null,null,null,null,"4","4",null,null,"4"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"STAM","index":231,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"STAM - Stamford (66/33kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T095 - Millchester BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Nth Queensland"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/33/19kV 0.63MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -1.4%, 2020 S -0.8% W -0.8%2021 S -0.9% W -0.9%2022 S -0.7% W -0.7%2023 S -0.8% W -0.8"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"0.3 MVA on 04/12/2018 at 20:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,0.60000002384185791,null,0.60000002384185791,null,0.60000002384185791,null,0.60000002384185791,null,null,null,null,0.60000002384185791,null,0.60000002384185791,null,0.60000002384185791,null,null,null,null,null,0.60000002384185791,0.60000002384185791,null,null,0.60000002384185791]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,0.40000000596046448,null,0.40000000596046448,null,0.40000000596046448,null,0.40000000596046448,null,null,null,null,0.40000000596046448,null,0.20000000298023224,null,0.20000000298023224,null,null,null,null,null,0.20000000298023224,0.20000000298023224,null,null,0.20000000298023224]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.83099999999999996,null,0.83499999999999996,null,0.83499999999999996,null,0.83499999999999996,null,null,null,null,0.83499999999999996,null,0.77800000000000002,null,0.77800000000000002,null,null,null,null,null,0.77800000000000002,0.77800000000000002,null,null,0.77800000000000002]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,0.40000000596046448,null,0.30000001192092896,null,0.30000001192092896,null,0.30000001192092896,null,null,null,null,0.30000001192092896,null,0.20000000298023224,null,0.20000000298023224,null,null,null,null,null,0.20000000298023224,0.20000000298023224,null,null,0.20000000298023224]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"2.5",null,"2.5",null,"2.5",null,"2.5",null,null,null,null,"2.5",null,"2.5",null,"2.5",null,null,null,null,null,"2.5","2.5",null,null,"2.5"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,0.4,null,0.3,null,0.3,null,0.3,null,null,null,null,0.3,null,0.2,null,0.2,null,null,null,null,null,0.2,0.2,null,null,0.2]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0.60000002384185791,null,0.60000002384185791,null,0.60000002384185791,null,0.60000002384185791,null,null,null,null,0.60000002384185791,null,0.60000002384185791,null,0.60000002384185791,null,null,null,null,null,0.60000002384185791,0.60000002384185791,null,null,0.60000002384185791]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"STTO","index":232,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"STTO - Stanthorpe Town (33/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T060 - Stanthorpe BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is South West"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x33/11kV 10/12.5MVA ONAN/ONAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -1.2%, 2020 S -0.1% W -0.1%2021 S -0.1% W -0.1%2022 S -0.1% W -0.1%2023 S -0.5% W -0.5"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"12.3 MVA on 18/06/2018 at 17:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,27.100000381469727,null,27.100000381469727,null,27.100000381469727,null,27.100000381469727,null,null,null,null,27.100000381469727,null,29.200000762939453,null,29.200000762939453,null,null,null,null,null,29.200000762939453,29.200000762939453,null,null,29.200000762939453]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,12.699999809265137,null,12.600000381469727,null,12.5,null,12.5,null,null,null,null,12.5,null,13.600000381469727,null,13.600000381469727,null,null,null,null,null,13.5,13.5,null,null,13.5]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.90600000000000003,null,0.90600000000000003,null,0.90600000000000003,null,0.90600000000000003,null,null,null,null,0.90600000000000003,null,0.94399999999999995,null,0.94399999999999995,null,null,null,null,null,0.94399999999999995,0.94399999999999995,null,null,0.94399999999999995]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,14.899999618530273,null,14.899999618530273,null,14.899999618530273,null,14.899999618530273,null,null,null,null,14.899999618530273,null,15.899999618530273,null,15.899999618530273,null,null,null,null,null,15.899999618530273,15.899999618530273,null,null,15.899999618530273]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,11.699999809265137,null,11.699999809265137,null,11.600000381469727,null,11.5,null,null,null,null,11.5,null,12.800000190734863,null,12.800000190734863,null,null,null,null,null,12.699999809265137,12.699999809265137,null,null,12.699999809265137]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.6,null,0.6,null,0.6,null,0.6,null,null,null,null,0.6,null,0.6,null,0.6,null,null,null,null,null,0.6,0.6,null,null,0.6]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"10",null,"10",null,"10",null,"10",null,null,null,null,"10",null,"10",null,"10",null,null,null,null,null,"10","10",null,null,"10"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,10,null,10,null,10,null,10,null,null,null,null,10,null,10,null,10,null,null,null,null,null,10,10,null,null,10]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"STUA","index":233,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"STUA - Stuart (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"TMES - Townsville Mesh"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Nth Queensland"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/11kV 21/26/35MVA ONAN/ODAN/ODAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.5%, 2020 S 0.7% W 0.7%, 2021 S 0.6% W 0.6%, 2022 S 1.8% W 1.8%, 2023 S 1.5% W 1.5%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"26.1 MVA on 19/12/2018 at 19:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,76.699996948242188,null,76.699996948242188,null,76.699996948242188,null,76.699996948242188,null,null,null,null,76.699996948242188,null,81.599998474121094,null,81.599998474121094,null,null,null,null,null,81.599998474121094,81.599998474121094,null,null,81.599998474121094]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,28.799999237060547,null,28.799999237060547,null,29.100000381469727,null,14.199999809265137,null,null,null,null,14.699999809265137,null,27.700000762939453,null,27.899999618530273,null,null,null,null,null,27.899999618530273,28.399999618530273,null,null,14.399999618530273]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.94,null,0.94,null,0.94,null,0.94,null,null,null,null,0.94,null,0.92500000000000004,null,0.92500000000000004,null,null,null,null,null,0.92500000000000004,0.92500000000000004,null,null,0.92500000000000004]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,45.5,null,45.5,null,45.5,null,45.5,null,null,null,null,45.5,null,47.200000762939453,null,47.200000762939453,null,null,null,null,null,47.200000762939453,47.200000762939453,null,null,47.200000762939453]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,28.100000381469727,null,28.100000381469727,null,28.299999237060547,null,13.5,null,null,null,null,14,null,26.200000762939453,null,26.399999618530273,null,null,null,null,null,26.399999618530273,26.899999618530273,null,null,12.800000190734863]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,1.4,null,1.4,null,1.4,null,0.7,null,null,null,null,0.7,null,1.3,null,1.3,null,null,null,null,null,1.3,1.3,null,null,0.6]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"102",null,"102",null,"102",null,"102",null,null,null,null,"102",null,"102",null,"102",null,null,null,null,null,"102","102",null,null,"102"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"T002","index":234,"n_rows":48,"n_cols":35,"rows_kept":48,"cut":false,"hidden":false,"merged":[[0,2,0,40],[2,1,2,5],[2,8,4,20],[2,23,3,24],[2,26,4,37],[6,1,8,5],[6,8,6,36],[8,8,9,36],[11,8,11,36],[13,3,14,11],[13,14,13,26],[16,17,17,31],[17,3,18,11],[17,14,18,15],[21,4,22,8],[21,9,21,21],[21,22,21,34],[22,9,22,10],[22,11,22,12],[22,13,22,14],[22,15,22,19],[22,20,22,21],[22,22,22,23],[22,24,22,29],[22,31,22,33],[23,4,23,8],[23,9,23,10],[23,11,23,12],[23,13,23,14],[23,15,23,19],[23,20,23,21],[23,22,23,23],[23,24,23,29],[23,31,23,33],[24,4,24,8],[24,9,24,10],[24,11,24,12],[24,13,24,14],[24,15,24,19],[24,20,24,21],[24,22,24,23],[24,24,24,29],[24,31,24,33],[25,4,25,8],[25,9,25,10],[25,11,25,12],[25,13,25,14],[25,15,25,19],[25,20,25,21],[25,22,25,23],[25,24,25,29],[25,31,25,33],[26,4,26,8],[26,9,26,10],[26,11,26,12],[26,13,26,14],[26,15,26,19],[26,20,26,21],[26,22,26,23],[26,24,26,29],[26,31,26,33],[27,4,27,8],[27,9,27,10],[27,11,27,12],[27,13,27,14],[27,15,27,19],[27,20,27,21],[27,22,27,23],[27,24,27,29],[27,31,27,33],[28,4,28,8],[28,9,28,10],[28,11,28,12],[28,13,28,14],[28,15,28,19],[28,20,28,21],[28,22,28,23],[28,24,28,29],[28,31,28,33],[29,4,29,8],[29,9,29,10],[29,11,29,12],[29,13,29,14],[29,15,29,19],[29,20,29,21],[29,22,29,23],[29,24,29,29],[29,31,29,33],[30,4,30,8],[30,9,30,10],[30,11,30,12],[30,13,30,14],[30,15,30,19],[30,20,30,21],[30,22,30,23],[30,24,30,29],[30,31,30,33],[31,4,31,8],[31,9,31,10],[31,11,31,12],[31,13,31,14],[31,15,31,19],[31,20,31,21],[31,22,31,23],[31,24,31,29],[31,31,31,33],[32,4,32,8],[32,9,32,10],[32,11,32,12],[32,13,32,14],[32,15,32,19],[32,20,32,21],[32,22,32,23],[32,24,32,29],[32,31,32,33],[33,4,33,8],[33,9,33,10],[33,11,33,12],[33,13,33,14],[33,15,33,19],[33,20,33,21],[33,22,33,23],[33,24,33,29],[33,31,33,33],[34,4,34,8],[34,9,34,10],[34,11,34,12],[34,13,34,14],[34,15,34,19],[34,20,34,21],[34,22,34,23],[34,24,34,29],[34,31,34,33],[35,4,35,8],[35,9,35,10],[35,11,35,12],[35,13,35,14],[35,15,35,19],[35,20,35,21],[35,22,35,23],[35,24,35,29],[35,31,35,33],[36,4,36,8],[36,9,36,10],[36,11,36,12],[36,13,36,14],[36,15,36,19],[36,20,36,21],[36,22,36,23],[36,24,36,29],[36,31,36,33],[37,4,37,8],[37,9,37,10],[37,11,37,12],[37,13,37,14],[37,15,37,19],[37,20,37,21],[37,22,37,23],[37,24,37,29],[37,31,37,33],[39,31,39,33],[38,4,38,8],[38,9,38,10],[38,11,38,12],[38,13,38,14],[38,15,38,19],[38,20,38,21],[38,22,38,23],[38,24,38,29],[38,31,38,33],[40,4,40,8],[40,9,40,10],[40,11,40,12],[40,13,40,14],[40,15,40,19],[39,22,39,23],[39,24,39,29],[39,4,39,8],[39,9,39,10],[39,11,39,12],[39,13,39,14],[39,15,39,19],[39,20,39,21],[40,22,40,23],[40,24,40,29],[40,31,40,33],[42,20,42,21],[42,22,42,23],[40,20,40,21],[42,9,42,10],[42,11,42,12],[42,13,42,14],[42,15,42,19],[41,9,41,10],[41,11,41,12],[41,13,41,14],[41,15,41,19],[43,31,43,33],[41,20,41,21],[43,22,43,23],[43,24,43,29],[41,22,41,23],[41,24,41,29],[47,2,47,38],[42,24,42,29],[42,31,42,33],[43,4,43,8],[43,9,43,10],[43,11,43,12],[43,13,43,14],[43,15,43,19],[43,20,43,21],[42,4,42,8],[41,31,41,33],[41,4,41,8]]}
[null,null,"Bulk Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,"T002 - Dalby East BSP (110/33kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"QTKM - Tangkam TCP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,"Region is South West"]
[]
[null,null,null,null,null,null,null,null,"Transformer size is 2x110/33kV 50/63MVA ONAN/ONAF"]
[]
[]
[null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,"32.8 MVA on 19/06/2018 at 07:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,130.30000305175781,null,130.30000305175781,null,130.30000305175781,null,130.30000305175781,null,null,null,null,130.30000305175781,null,149.69999694824219,null,149.69999694824219,null,null,null,null,null,149.69999694824219,149.69999694824219,null,null,149.69999694824219]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,35.200000762939453,null,39.900001525878906,null,39.299999237060547,null,39.099998474121094,null,null,null,null,39.099998474121094,null,33.5,null,37.799999237060547,null,null,null,null,null,37.5,37.299999237060547,null,null,37.299999237060547]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,0.99299999999999999,null,0.98799999999999999,null,0.98799999999999999,null,0.98899999999999999,null,null,null,null,0.98899999999999999,null,1,null,1,null,null,null,null,null,1,1,null,null,1]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,74.400001525878906,null,74.400001525878906,null,74.400001525878906,null,74.400001525878906,null,null,null,null,74.400001525878906,null,85.5,null,85.5,null,null,null,null,null,85.5,85.5,null,null,85.5]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,31.600000381469727,null,36.299999237060547,null,35.799999237060547,null,35.599998474121094,null,null,null,null,35.700000762939453,null,31.899999618530273,null,36.099998474121094,null,null,null,null,null,35.799999237060547,35.700000762939453,null,null,35.599998474121094]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,1.6,null,1.8,null,1.8,null,1.8,null,null,null,null,1.8,null,1.6,null,1.8,null,null,null,null,null,1.8,1.8,null,null,1.8]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,"10",null,"10",null,"10",null,"10",null,null,null,null,"10",null,"10",null,"10",null,null,null,null,null,"10","10",null,null,"10"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"T010","index":235,"n_rows":48,"n_cols":35,"rows_kept":48,"cut":false,"hidden":false,"merged":[[0,2,0,40],[2,1,2,5],[2,8,4,20],[2,23,3,24],[2,26,4,37],[6,1,8,5],[6,8,6,36],[8,8,9,36],[11,8,11,36],[13,3,14,11],[13,14,13,26],[16,17,17,31],[17,3,18,11],[17,14,18,15],[21,4,22,8],[21,9,21,21],[21,22,21,34],[22,9,22,10],[22,11,22,12],[22,13,22,14],[22,15,22,19],[22,20,22,21],[22,22,22,23],[22,24,22,29],[22,31,22,33],[23,4,23,8],[23,9,23,10],[23,11,23,12],[23,13,23,14],[23,15,23,19],[23,20,23,21],[23,22,23,23],[23,24,23,29],[23,31,23,33],[24,4,24,8],[24,9,24,10],[24,11,24,12],[24,13,24,14],[24,15,24,19],[24,20,24,21],[24,22,24,23],[24,24,24,29],[24,31,24,33],[25,4,25,8],[25,9,25,10],[25,11,25,12],[25,13,25,14],[25,15,25,19],[25,20,25,21],[25,22,25,23],[25,24,25,29],[25,31,25,33],[26,4,26,8],[26,9,26,10],[26,11,26,12],[26,13,26,14],[26,15,26,19],[26,20,26,21],[26,22,26,23],[26,24,26,29],[26,31,26,33],[27,4,27,8],[27,9,27,10],[27,11,27,12],[27,13,27,14],[27,15,27,19],[27,20,27,21],[27,22,27,23],[27,24,27,29],[27,31,27,33],[28,4,28,8],[28,9,28,10],[28,11,28,12],[28,13,28,14],[28,15,28,19],[28,20,28,21],[28,22,28,23],[28,24,28,29],[28,31,28,33],[29,4,29,8],[29,9,29,10],[29,11,29,12],[29,13,29,14],[29,15,29,19],[29,20,29,21],[29,22,29,23],[29,24,29,29],[29,31,29,33],[30,4,30,8],[30,9,30,10],[30,11,30,12],[30,13,30,14],[30,15,30,19],[30,20,30,21],[30,22,30,23],[30,24,30,29],[30,31,30,33],[31,4,31,8],[31,9,31,10],[31,11,31,12],[31,13,31,14],[31,15,31,19],[31,20,31,21],[31,22,31,23],[31,24,31,29],[31,31,31,33],[32,4,32,8],[32,9,32,10],[32,11,32,12],[32,13,32,14],[32,15,32,19],[32,20,32,21],[32,22,32,23],[32,24,32,29],[32,31,32,33],[33,4,33,8],[33,9,33,10],[33,11,33,12],[33,13,33,14],[33,15,33,19],[33,20,33,21],[33,22,33,23],[33,24,33,29],[33,31,33,33],[34,4,34,8],[34,9,34,10],[34,11,34,12],[34,13,34,14],[34,15,34,19],[34,20,34,21],[34,22,34,23],[34,24,34,29],[34,31,34,33],[35,4,35,8],[35,9,35,10],[35,11,35,12],[35,13,35,14],[35,15,35,19],[35,20,35,21],[35,22,35,23],[35,24,35,29],[35,31,35,33],[36,4,36,8],[36,9,36,10],[36,11,36,12],[36,13,36,14],[36,15,36,19],[36,20,36,21],[36,22,36,23],[36,24,36,29],[36,31,36,33],[37,4,37,8],[37,9,37,10],[37,11,37,12],[37,13,37,14],[37,15,37,19],[37,20,37,21],[37,22,37,23],[37,24,37,29],[37,31,37,33],[39,31,39,33],[38,4,38,8],[38,9,38,10],[38,11,38,12],[38,13,38,14],[38,15,38,19],[38,20,38,21],[38,22,38,23],[38,24,38,29],[38,31,38,33],[40,4,40,8],[40,9,40,10],[40,11,40,12],[40,13,40,14],[40,15,40,19],[39,22,39,23],[39,24,39,29],[39,4,39,8],[39,9,39,10],[39,11,39,12],[39,13,39,14],[39,15,39,19],[39,20,39,21],[40,22,40,23],[40,24,40,29],[40,31,40,33],[42,20,42,21],[42,22,42,23],[40,20,40,21],[42,9,42,10],[42,11,42,12],[42,13,42,14],[42,15,42,19],[41,9,41,10],[41,11,41,12],[41,13,41,14],[41,15,41,19],[43,31,43,33],[41,20,41,21],[43,22,43,23],[43,24,43,29],[41,22,41,23],[41,24,41,29],[47,2,47,38],[42,24,42,29],[42,31,42,33],[43,4,43,8],[43,9,43,10],[43,11,43,12],[43,13,43,14],[43,15,43,19],[43,20,43,21],[42,4,42,8],[41,31,41,33],[41,4,41,8]]}
[null,null,"Bulk Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,"T010 - Yarranlea BSP (110/33kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"QMRG - Middle Ridge (Ergon) TCP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,"Region is South West"]
[]
[null,null,null,null,null,null,null,null,"Transformer size is 2x106/33/11kV 15MVA ON"]
[]
[]
[null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,"22.7 MVA on 19/02/2019 at 18:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,30,null,30,null,30,null,30,null,null,null,null,30,null,30,null,30,null,null,null,null,null,30,30,null,null,30]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,26.299999237060547,null,26.100000381469727,null,27.100000381469727,null,27,null,null,null,null,27,null,25.899999618530273,null,25.700000762939453,null,null,null,null,null,27,26.899999618530273,null,null,26.799999237060547]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,0.92400000000000004,null,0.92400000000000004,null,0.92400000000000004,null,0.92400000000000004,null,null,null,null,0.92400000000000004,null,0.96499999999999997,null,0.96499999999999997,null,null,null,null,null,0.96499999999999997,0.96499999999999997,null,null,0.96499999999999997]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,15,null,15,null,15,null,15,null,null,null,null,15,null,15,null,15,null,null,null,null,null,15,15,null,null,15]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,23.700000762939453,null,23.5,null,24.5,null,24.399999618530273,null,null,null,null,24.399999618530273,null,24.700000762939453,null,24.5,null,null,null,null,null,25.799999237060547,25.700000762939453,null,null,25.600000381469727]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,1.2,null,1.2,null,1.2,null,1.2,null,null,null,null,1.2,null,1.2,null,1.2,null,null,null,null,null,1.3,1.3,null,null,1.3]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,"39.5",null,"39.5",null,"39.5",null,"39.5",null,null,null,null,"39.5",null,"39.5",null,"39.5",null,null,null,null,null,"39.5","39.5",null,null,"39.5"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,8.6999999999999993,null,8.5,null,9.5,null,9.4,null,null,null,null,9.4,null,9.6999999999999993,null,9.5,null,null,null,null,null,10.8,10.7,null,null,10.6]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,7,null,7,null,7,null,7,null,null,null,null,7,null,7,null,7,null,null,null,null,null,7,7,null,null,7]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,1.7000000476837158,null,1.7000000476837158,null,1.7000000476837158,null,1.7000000476837158,null,null,null,null,1.7000000476837158,null,1.7000000476837158,null,1.7000000476837158,null,null,null,null,null,1.7000000476837158,1.7000000476837158,null,null,1.7000000476837158]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,2.5,null,2.5,null,2.5,null,2.5,null,null,null,null,2.5,null,2.5,null,2.5,null,null,null,null,null,2.5,2.5,null,null,2.5]
[null,null,null,null,"Shed(30min)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"T012","index":236,"n_rows":48,"n_cols":35,"rows_kept":48,"cut":false,"hidden":false,"merged":[[0,2,0,40],[2,1,2,5],[2,8,4,20],[2,23,3,24],[2,26,4,37],[6,1,8,5],[6,8,6,36],[8,8,9,36],[11,8,11,36],[13,3,14,11],[13,14,13,26],[16,17,17,31],[17,3,18,11],[17,14,18,15],[21,4,22,8],[21,9,21,21],[21,22,21,34],[22,9,22,10],[22,11,22,12],[22,13,22,14],[22,15,22,19],[22,20,22,21],[22,22,22,23],[22,24,22,29],[22,31,22,33],[23,4,23,8],[23,9,23,10],[23,11,23,12],[23,13,23,14],[23,15,23,19],[23,20,23,21],[23,22,23,23],[23,24,23,29],[23,31,23,33],[24,4,24,8],[24,9,24,10],[24,11,24,12],[24,13,24,14],[24,15,24,19],[24,20,24,21],[24,22,24,23],[24,24,24,29],[24,31,24,33],[25,4,25,8],[25,9,25,10],[25,11,25,12],[25,13,25,14],[25,15,25,19],[25,20,25,21],[25,22,25,23],[25,24,25,29],[25,31,25,33],[26,4,26,8],[26,9,26,10],[26,11,26,12],[26,13,26,14],[26,15,26,19],[26,20,26,21],[26,22,26,23],[26,24,26,29],[26,31,26,33],[27,4,27,8],[27,9,27,10],[27,11,27,12],[27,13,27,14],[27,15,27,19],[27,20,27,21],[27,22,27,23],[27,24,27,29],[27,31,27,33],[28,4,28,8],[28,9,28,10],[28,11,28,12],[28,13,28,14],[28,15,28,19],[28,20,28,21],[28,22,28,23],[28,24,28,29],[28,31,28,33],[29,4,29,8],[29,9,29,10],[29,11,29,12],[29,13,29,14],[29,15,29,19],[29,20,29,21],[29,22,29,23],[29,24,29,29],[29,31,29,33],[30,4,30,8],[30,9,30,10],[30,11,30,12],[30,13,30,14],[30,15,30,19],[30,20,30,21],[30,22,30,23],[30,24,30,29],[30,31,30,33],[31,4,31,8],[31,9,31,10],[31,11,31,12],[31,13,31,14],[31,15,31,19],[31,20,31,21],[31,22,31,23],[31,24,31,29],[31,31,31,33],[32,4,32,8],[32,9,32,10],[32,11,32,12],[32,13,32,14],[32,15,32,19],[32,20,32,21],[32,22,32,23],[32,24,32,29],[32,31,32,33],[33,4,33,8],[33,9,33,10],[33,11,33,12],[33,13,33,14],[33,15,33,19],[33,20,33,21],[33,22,33,23],[33,24,33,29],[33,31,33,33],[34,4,34,8],[34,9,34,10],[34,11,34,12],[34,13,34,14],[34,15,34,19],[34,20,34,21],[34,22,34,23],[34,24,34,29],[34,31,34,33],[35,4,35,8],[35,9,35,10],[35,11,35,12],[35,13,35,14],[35,15,35,19],[35,20,35,21],[35,22,35,23],[35,24,35,29],[35,31,35,33],[36,4,36,8],[36,9,36,10],[36,11,36,12],[36,13,36,14],[36,15,36,19],[36,20,36,21],[36,22,36,23],[36,24,36,29],[36,31,36,33],[37,4,37,8],[37,9,37,10],[37,11,37,12],[37,13,37,14],[37,15,37,19],[37,20,37,21],[37,22,37,23],[37,24,37,29],[37,31,37,33],[39,31,39,33],[38,4,38,8],[38,9,38,10],[38,11,38,12],[38,13,38,14],[38,15,38,19],[38,20,38,21],[38,22,38,23],[38,24,38,29],[38,31,38,33],[40,4,40,8],[40,9,40,10],[40,11,40,12],[40,13,40,14],[40,15,40,19],[39,22,39,23],[39,24,39,29],[39,4,39,8],[39,9,39,10],[39,11,39,12],[39,13,39,14],[39,15,39,19],[39,20,39,21],[40,22,40,23],[40,24,40,29],[40,31,40,33],[42,20,42,21],[42,22,42,23],[40,20,40,21],[42,9,42,10],[42,11,42,12],[42,13,42,14],[42,15,42,19],[41,9,41,10],[41,11,41,12],[41,13,41,14],[41,15,41,19],[43,31,43,33],[41,20,41,21],[43,22,43,23],[43,24,43,29],[41,22,41,23],[41,24,41,29],[47,2,47,38],[42,24,42,29],[42,31,42,33],[43,4,43,8],[43,9,43,10],[43,11,43,12],[43,13,43,14],[43,15,43,19],[43,20,43,21],[42,4,42,8],[41,31,41,33],[41,4,41,8]]}
[null,null,"Bulk Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,"T012 - Kilkivan BSP (132/66kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"QWLN - Woolooga TCP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,"Region is Wide Bay"]
[]
[null,null,null,null,null,null,null,null,"Transformer size is 1x132/66/11kV 34MVA ONAF;1x132/66kV 15/18MVA ON/ONB(Standby)"]
[]
[]
[null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,"19.8 MVA on 13/02/2019 at 18:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,34,null,34,null,34,null,34,null,null,null,null,34,null,34,null,34,null,null,null,null,null,34,34,null,null,34]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,24.100000381469727,null,24,null,23.799999237060547,null,23.700000762939453,null,null,null,null,23.799999237060547,null,15.100000381469727,null,15.100000381469727,null,null,null,null,null,15.100000381469727,15.100000381469727,null,null,15.100000381469727]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,0.94399999999999995,null,0.94399999999999995,null,0.94399999999999995,null,0.94399999999999995,null,null,null,null,0.94399999999999995,null,0.98299999999999998,null,0.98299999999999998,null,null,null,null,null,0.98299999999999998,0.98299999999999998,null,null,0.98299999999999998]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,21.399999618530273,null,21.299999237060547,null,21.100000381469727,null,21.100000381469727,null,null,null,null,21.200000762939453,null,14.300000190734863,null,14.300000190734863,null,null,null,null,null,14.300000190734863,14.300000190734863,null,null,14.300000190734863]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,1.1000000000000001,null,1.1000000000000001,null,1.1000000000000001,null,1.1000000000000001,null,null,null,null,1.1000000000000001,null,0.7,null,0.7,null,null,null,null,null,0.7,0.7,null,null,0.7]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,"6.5",null,"6.5",null,"6.5",null,"6.5",null,null,null,null,"6.5",null,"6.5",null,"6.5",null,null,null,null,null,"6.5","6.5",null,null,"6.5"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,21.4,null,21.3,null,21.1,null,21.1,null,null,null,null,21.2,null,14.3,null,14.3,null,null,null,null,null,14.3,14.3,null,null,14.3]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,25.700000762939453,null,25.700000762939453,null,25.700000762939453,null,25.700000762939453,null,null,null,null,25.700000762939453,null,28.399999618530273,null,28.399999618530273,null,null,null,null,null,28.399999618530273,28.399999618530273,null,null,28.399999618530273]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"T013","index":237,"n_rows":48,"n_cols":35,"rows_kept":48,"cut":false,"hidden":false,"merged":[[0,2,0,40],[2,1,2,5],[2,8,4,20],[2,23,3,24],[2,26,4,37],[6,1,8,5],[6,8,6,36],[8,8,9,36],[11,8,11,36],[13,3,14,11],[13,14,13,26],[16,17,17,31],[17,3,18,11],[17,14,18,15],[21,4,22,8],[21,9,21,21],[21,22,21,34],[22,9,22,10],[22,11,22,12],[22,13,22,14],[22,15,22,19],[22,20,22,21],[22,22,22,23],[22,24,22,29],[22,31,22,33],[23,4,23,8],[23,9,23,10],[23,11,23,12],[23,13,23,14],[23,15,23,19],[23,20,23,21],[23,22,23,23],[23,24,23,29],[23,31,23,33],[24,4,24,8],[24,9,24,10],[24,11,24,12],[24,13,24,14],[24,15,24,19],[24,20,24,21],[24,22,24,23],[24,24,24,29],[24,31,24,33],[25,4,25,8],[25,9,25,10],[25,11,25,12],[25,13,25,14],[25,15,25,19],[25,20,25,21],[25,22,25,23],[25,24,25,29],[25,31,25,33],[26,4,26,8],[26,9,26,10],[26,11,26,12],[26,13,26,14],[26,15,26,19],[26,20,26,21],[26,22,26,23],[26,24,26,29],[26,31,26,33],[27,4,27,8],[27,9,27,10],[27,11,27,12],[27,13,27,14],[27,15,27,19],[27,20,27,21],[27,22,27,23],[27,24,27,29],[27,31,27,33],[28,4,28,8],[28,9,28,10],[28,11,28,12],[28,13,28,14],[28,15,28,19],[28,20,28,21],[28,22,28,23],[28,24,28,29],[28,31,28,33],[29,4,29,8],[29,9,29,10],[29,11,29,12],[29,13,29,14],[29,15,29,19],[29,20,29,21],[29,22,29,23],[29,24,29,29],[29,31,29,33],[30,4,30,8],[30,9,30,10],[30,11,30,12],[30,13,30,14],[30,15,30,19],[30,20,30,21],[30,22,30,23],[30,24,30,29],[30,31,30,33],[31,4,31,8],[31,9,31,10],[31,11,31,12],[31,13,31,14],[31,15,31,19],[31,20,31,21],[31,22,31,23],[31,24,31,29],[31,31,31,33],[32,4,32,8],[32,9,32,10],[32,11,32,12],[32,13,32,14],[32,15,32,19],[32,20,32,21],[32,22,32,23],[32,24,32,29],[32,31,32,33],[33,4,33,8],[33,9,33,10],[33,11,33,12],[33,13,33,14],[33,15,33,19],[33,20,33,21],[33,22,33,23],[33,24,33,29],[33,31,33,33],[34,4,34,8],[34,9,34,10],[34,11,34,12],[34,13,34,14],[34,15,34,19],[34,20,34,21],[34,22,34,23],[34,24,34,29],[34,31,34,33],[35,4,35,8],[35,9,35,10],[35,11,35,12],[35,13,35,14],[35,15,35,19],[35,20,35,21],[35,22,35,23],[35,24,35,29],[35,31,35,33],[36,4,36,8],[36,9,36,10],[36,11,36,12],[36,13,36,14],[36,15,36,19],[36,20,36,21],[36,22,36,23],[36,24,36,29],[36,31,36,33],[37,4,37,8],[37,9,37,10],[37,11,37,12],[37,13,37,14],[37,15,37,19],[37,20,37,21],[37,22,37,23],[37,24,37,29],[37,31,37,33],[39,31,39,33],[38,4,38,8],[38,9,38,10],[38,11,38,12],[38,13,38,14],[38,15,38,19],[38,20,38,21],[38,22,38,23],[38,24,38,29],[38,31,38,33],[40,4,40,8],[40,9,40,10],[40,11,40,12],[40,13,40,14],[40,15,40,19],[39,22,39,23],[39,24,39,29],[39,4,39,8],[39,9,39,10],[39,11,39,12],[39,13,39,14],[39,15,39,19],[39,20,39,21],[40,22,40,23],[40,24,40,29],[40,31,40,33],[42,20,42,21],[42,22,42,23],[40,20,40,21],[42,9,42,10],[42,11,42,12],[42,13,42,14],[42,15,42,19],[41,9,41,10],[41,11,41,12],[41,13,41,14],[41,15,41,19],[43,31,43,33],[41,20,41,21],[43,22,43,23],[43,24,43,29],[41,22,41,23],[41,24,41,29],[47,2,47,38],[42,24,42,29],[42,31,42,33],[43,4,43,8],[43,9,43,10],[43,11,43,12],[43,13,43,14],[43,15,43,19],[43,20,43,21],[42,4,42,8],[41,31,41,33],[41,4,41,8]]}
[null,null,"Bulk Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,"T013 - Chinchilla BSP (132/33kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"QCHA - Chinchilla TCP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,"Region is South West"]
[]
[null,null,null,null,null,null,null,null,"Transformer size is 1x132/110kV 30MVA ONAN;1x132/33/11kV 50/63MVA ONAN/ONAF;1x20MVA 110kV Transformer;2x106/33/11kV 20MVA ON(Standby)"]
[]
[]
[null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 15.3 MVA"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,"22.4 MVA on 13/02/2019 at 18:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,66,null,66,null,66,null,66,null,null,null,null,66,null,66,null,66,null,null,null,null,null,66,66,null,null,66]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,25.600000381469727,null,25.5,null,25.299999237060547,null,25.399999618530273,null,null,null,null,25.5,null,19.100000381469727,null,19.100000381469727,null,null,null,null,null,19.100000381469727,19.100000381469727,null,null,19.200000762939453]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,1,null,1,null,1,null,1,null,null,null,null,1,null,1,null,1,null,null,null,null,null,1,1,null,null,1]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,46,null,46,null,46,null,46,null,null,null,null,46,null,52,null,52,null,null,null,null,null,52,52,null,null,52]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,23.200000762939453,null,23.100000381469727,null,23,null,23,null,null,null,null,23.100000381469727,null,17.899999618530273,null,17.899999618530273,null,null,null,null,null,17.899999618530273,17.899999618530273,null,null,18]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,1.2,null,1.2,null,1.2,null,1.2,null,null,null,null,1.2,null,0.9,null,0.9,null,null,null,null,null,0.9,0.9,null,null,0.9]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,"27",null,"27",null,"27",null,"27",null,null,null,null,"27",null,"27",null,"27",null,null,null,null,null,"27","27",null,null,"27"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"T019","index":238,"n_rows":48,"n_cols":35,"rows_kept":48,"cut":false,"hidden":false,"merged":[[0,2,0,40],[2,1,2,5],[2,8,4,20],[2,23,3,24],[2,26,4,37],[6,1,8,5],[6,8,6,36],[8,8,9,36],[11,8,11,36],[13,3,14,11],[13,14,13,26],[16,17,17,31],[17,3,18,11],[17,14,18,15],[21,4,22,8],[21,9,21,21],[21,22,21,34],[22,9,22,10],[22,11,22,12],[22,13,22,14],[22,15,22,19],[22,20,22,21],[22,22,22,23],[22,24,22,29],[22,31,22,33],[23,4,23,8],[23,9,23,10],[23,11,23,12],[23,13,23,14],[23,15,23,19],[23,20,23,21],[23,22,23,23],[23,24,23,29],[23,31,23,33],[24,4,24,8],[24,9,24,10],[24,11,24,12],[24,13,24,14],[24,15,24,19],[24,20,24,21],[24,22,24,23],[24,24,24,29],[24,31,24,33],[25,4,25,8],[25,9,25,10],[25,11,25,12],[25,13,25,14],[25,15,25,19],[25,20,25,21],[25,22,25,23],[25,24,25,29],[25,31,25,33],[26,4,26,8],[26,9,26,10],[26,11,26,12],[26,13,26,14],[26,15,26,19],[26,20,26,21],[26,22,26,23],[26,24,26,29],[26,31,26,33],[27,4,27,8],[27,9,27,10],[27,11,27,12],[27,13,27,14],[27,15,27,19],[27,20,27,21],[27,22,27,23],[27,24,27,29],[27,31,27,33],[28,4,28,8],[28,9,28,10],[28,11,28,12],[28,13,28,14],[28,15,28,19],[28,20,28,21],[28,22,28,23],[28,24,28,29],[28,31,28,33],[29,4,29,8],[29,9,29,10],[29,11,29,12],[29,13,29,14],[29,15,29,19],[29,20,29,21],[29,22,29,23],[29,24,29,29],[29,31,29,33],[30,4,30,8],[30,9,30,10],[30,11,30,12],[30,13,30,14],[30,15,30,19],[30,20,30,21],[30,22,30,23],[30,24,30,29],[30,31,30,33],[31,4,31,8],[31,9,31,10],[31,11,31,12],[31,13,31,14],[31,15,31,19],[31,20,31,21],[31,22,31,23],[31,24,31,29],[31,31,31,33],[32,4,32,8],[32,9,32,10],[32,11,32,12],[32,13,32,14],[32,15,32,19],[32,20,32,21],[32,22,32,23],[32,24,32,29],[32,31,32,33],[33,4,33,8],[33,9,33,10],[33,11,33,12],[33,13,33,14],[33,15,33,19],[33,20,33,21],[33,22,33,23],[33,24,33,29],[33,31,33,33],[34,4,34,8],[34,9,34,10],[34,11,34,12],[34,13,34,14],[34,15,34,19],[34,20,34,21],[34,22,34,23],[34,24,34,29],[34,31,34,33],[35,4,35,8],[35,9,35,10],[35,11,35,12],[35,13,35,14],[35,15,35,19],[35,20,35,21],[35,22,35,23],[35,24,35,29],[35,31,35,33],[36,4,36,8],[36,9,36,10],[36,11,36,12],[36,13,36,14],[36,15,36,19],[36,20,36,21],[36,22,36,23],[36,24,36,29],[36,31,36,33],[37,4,37,8],[37,9,37,10],[37,11,37,12],[37,13,37,14],[37,15,37,19],[37,20,37,21],[37,22,37,23],[37,24,37,29],[37,31,37,33],[39,31,39,33],[38,4,38,8],[38,9,38,10],[38,11,38,12],[38,13,38,14],[38,15,38,19],[38,20,38,21],[38,22,38,23],[38,24,38,29],[38,31,38,33],[40,4,40,8],[40,9,40,10],[40,11,40,12],[40,13,40,14],[40,15,40,19],[39,22,39,23],[39,24,39,29],[39,4,39,8],[39,9,39,10],[39,11,39,12],[39,13,39,14],[39,15,39,19],[39,20,39,21],[40,22,40,23],[40,24,40,29],[40,31,40,33],[42,20,42,21],[42,22,42,23],[40,20,40,21],[42,9,42,10],[42,11,42,12],[42,13,42,14],[42,15,42,19],[41,9,41,10],[41,11,41,12],[41,13,41,14],[41,15,41,19],[43,31,43,33],[41,20,41,21],[43,22,43,23],[43,24,43,29],[41,22,41,23],[41,24,41,29],[47,2,47,38],[42,24,42,29],[42,31,42,33],[43,4,43,8],[43,9,43,10],[43,11,43,12],[43,13,43,14],[43,15,43,19],[43,20,43,21],[42,4,42,8],[41,31,41,33],[41,4,41,8]]}
[null,null,"Bulk Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,"T019 - Gladstone South BSP (132/66kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"QGST - Gladstone South TCP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,"Region is Capricornia"]
[]
[null,null,null,null,null,null,null,null,"Transformer size is 1xGLSO 3 TRANSFORMER-132/66/11KV TRANSF 3;1xGLSO 6 TRANSFORMER-132/66/11 TRANSF 6"]
[]
[]
[null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 1.1 MVA"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,"44.6 MVA on 20/12/2018 at 21:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,120,null,120,null,120,null,120,null,null,null,null,120,null,120,null,120,null,null,null,null,null,120,120,null,null,120]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,1.5,null,1.5,null,1.5,null,1.5,null,null,null,null,1.5,null,1.3999999761581421,null,1.3999999761581421,null,null,null,null,null,1.3999999761581421,1.3999999761581421,null,null,1.3999999761581421]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,45.799999237060547,null,45.599998474121094,null,45.299999237060547,null,45.400001525878906,null,null,null,null,45.799999237060547,null,46.200000762939453,null,46,null,null,null,null,null,45.799999237060547,45.900001525878906,null,null,46.200000762939453]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,0.99199999999999999,null,0.99199999999999999,null,0.99199999999999999,null,0.99199999999999999,null,null,null,null,0.99199999999999999,null,0.91,null,0.91,null,null,null,null,null,0.91,0.91,null,null,0.91]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,80,null,80,null,80,null,80,null,null,null,null,80,null,80,null,80,null,null,null,null,null,80,80,null,null,80]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,42.799999237060547,null,42.599998474121094,null,42.299999237060547,null,42.400001525878906,null,null,null,null,42.799999237060547,null,44.700000762939453,null,44.599998474121094,null,null,null,null,null,44.400001525878906,44.5,null,null,44.700000762939453]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,2.1,null,2.1,null,2.1,null,2.1,null,null,null,null,2.1,null,2.2000000000000002,null,2.2000000000000002,null,null,null,null,null,2.2000000000000002,2.2000000000000002,null,null,2.2000000000000002]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,"22.5",null,"22.5",null,"22.5",null,"22.5",null,null,null,null,"22.5",null,"22.5",null,"22.5",null,null,null,null,null,"22.5","22.5",null,null,"22.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,6,null,6,null,6,null,6,null,null,null,null,6,null,6,null,6,null,null,null,null,null,6,6,null,null,6]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,4,null,4,null,4,null,4,null,null,null,null,4,null,4,null,4,null,null,null,null,null,4,4,null,null,4]
[null,null,null,null,"Shed(30min)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"T020","index":239,"n_rows":48,"n_cols":35,"rows_kept":48,"cut":false,"hidden":false,"merged":[[0,2,0,40],[2,1,2,5],[2,8,4,20],[2,23,3,24],[2,26,4,37],[6,1,8,5],[6,8,6,36],[8,8,9,36],[11,8,11,36],[13,3,14,11],[13,14,13,26],[16,17,17,31],[17,3,18,11],[17,14,18,15],[21,4,22,8],[21,9,21,21],[21,22,21,34],[22,9,22,10],[22,11,22,12],[22,13,22,14],[22,15,22,19],[22,20,22,21],[22,22,22,23],[22,24,22,29],[22,31,22,33],[23,4,23,8],[23,9,23,10],[23,11,23,12],[23,13,23,14],[23,15,23,19],[23,20,23,21],[23,22,23,23],[23,24,23,29],[23,31,23,33],[24,4,24,8],[24,9,24,10],[24,11,24,12],[24,13,24,14],[24,15,24,19],[24,20,24,21],[24,22,24,23],[24,24,24,29],[24,31,24,33],[25,4,25,8],[25,9,25,10],[25,11,25,12],[25,13,25,14],[25,15,25,19],[25,20,25,21],[25,22,25,23],[25,24,25,29],[25,31,25,33],[26,4,26,8],[26,9,26,10],[26,11,26,12],[26,13,26,14],[26,15,26,19],[26,20,26,21],[26,22,26,23],[26,24,26,29],[26,31,26,33],[27,4,27,8],[27,9,27,10],[27,11,27,12],[27,13,27,14],[27,15,27,19],[27,20,27,21],[27,22,27,23],[27,24,27,29],[27,31,27,33],[28,4,28,8],[28,9,28,10],[28,11,28,12],[28,13,28,14],[28,15,28,19],[28,20,28,21],[28,22,28,23],[28,24,28,29],[28,31,28,33],[29,4,29,8],[29,9,29,10],[29,11,29,12],[29,13,29,14],[29,15,29,19],[29,20,29,21],[29,22,29,23],[29,24,29,29],[29,31,29,33],[30,4,30,8],[30,9,30,10],[30,11,30,12],[30,13,30,14],[30,15,30,19],[30,20,30,21],[30,22,30,23],[30,24,30,29],[30,31,30,33],[31,4,31,8],[31,9,31,10],[31,11,31,12],[31,13,31,14],[31,15,31,19],[31,20,31,21],[31,22,31,23],[31,24,31,29],[31,31,31,33],[32,4,32,8],[32,9,32,10],[32,11,32,12],[32,13,32,14],[32,15,32,19],[32,20,32,21],[32,22,32,23],[32,24,32,29],[32,31,32,33],[33,4,33,8],[33,9,33,10],[33,11,33,12],[33,13,33,14],[33,15,33,19],[33,20,33,21],[33,22,33,23],[33,24,33,29],[33,31,33,33],[34,4,34,8],[34,9,34,10],[34,11,34,12],[34,13,34,14],[34,15,34,19],[34,20,34,21],[34,22,34,23],[34,24,34,29],[34,31,34,33],[35,4,35,8],[35,9,35,10],[35,11,35,12],[35,13,35,14],[35,15,35,19],[35,20,35,21],[35,22,35,23],[35,24,35,29],[35,31,35,33],[36,4,36,8],[36,9,36,10],[36,11,36,12],[36,13,36,14],[36,15,36,19],[36,20,36,21],[36,22,36,23],[36,24,36,29],[36,31,36,33],[37,4,37,8],[37,9,37,10],[37,11,37,12],[37,13,37,14],[37,15,37,19],[37,20,37,21],[37,22,37,23],[37,24,37,29],[37,31,37,33],[39,31,39,33],[38,4,38,8],[38,9,38,10],[38,11,38,12],[38,13,38,14],[38,15,38,19],[38,20,38,21],[38,22,38,23],[38,24,38,29],[38,31,38,33],[40,4,40,8],[40,9,40,10],[40,11,40,12],[40,13,40,14],[40,15,40,19],[39,22,39,23],[39,24,39,29],[39,4,39,8],[39,9,39,10],[39,11,39,12],[39,13,39,14],[39,15,39,19],[39,20,39,21],[40,22,40,23],[40,24,40,29],[40,31,40,33],[42,20,42,21],[42,22,42,23],[40,20,40,21],[42,9,42,10],[42,11,42,12],[42,13,42,14],[42,15,42,19],[41,9,41,10],[41,11,41,12],[41,13,41,14],[41,15,41,19],[43,31,43,33],[41,20,41,21],[43,22,43,23],[43,24,43,29],[41,22,41,23],[41,24,41,29],[47,2,47,38],[42,24,42,29],[42,31,42,33],[43,4,43,8],[43,9,43,10],[43,11,43,12],[43,13,43,14],[43,15,43,19],[43,20,43,21],[42,4,42,8],[41,31,41,33],[41,4,41,8]]}
[null,null,"Bulk Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,"T020 - Bundaberg BSP (132/66kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"QGNG - Gin Gin TCP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,"Region is Wide Bay"]
[]
[null,null,null,null,null,null,null,null,"Transformer size is 1x132/66kV 36/70MVA ONAN/ONAF;2x132/66kV 40/50/60MVA ON/OFN/OFB"]
[]
[]
[null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 2.8 MVA"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,"119.3 MVA on 14/02/2019 at 17:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,226.39999389648438,null,226.39999389648438,null,226.39999389648438,null,226.39999389648438,null,null,null,null,226.39999389648438,null,250.80000305175781,null,250.80000305175781,null,null,null,null,null,250.80000305175781,250.80000305175781,null,null,250.80000305175781]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0.10000000149011612,null,0.10000000149011612,null,null,null,null,null,0.10000000149011612,0.10000000149011612,null,null,0.10000000149011612]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,130.89999389648438,null,131.5,null,131.19999694824219,null,131.19999694824219,null,null,null,null,131.89999389648438,null,102.09999847412109,null,102,null,null,null,null,null,102.80000305175781,103.80000305175781,null,null,104.09999847412109]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,0.98499999999999999,null,0.98499999999999999,null,0.98499999999999999,null,0.98499999999999999,null,null,null,null,0.98499999999999999,null,0.996,null,0.996,null,null,null,null,null,0.996,0.996,null,null,0.996]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,170.19999694824219,null,170.19999694824219,null,170.19999694824219,null,170.19999694824219,null,null,null,null,170.19999694824219,null,179.39999389648438,null,179.39999389648438,null,null,null,null,null,179.39999389648438,179.39999389648438,null,null,179.39999389648438]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,121.69999694824219,null,122.19999694824219,null,122,null,122,null,null,null,null,122.69999694824219,null,96.400001525878906,null,96.300003051757813,null,null,null,null,null,97.199996948242188,98.099998474121094,null,null,98.400001525878906]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,6.1,null,6.1,null,6.1,null,6.1,null,null,null,null,6.1,null,4.8,null,4.8,null,null,null,null,null,4.9000000000000004,4.9000000000000004,null,null,4.9000000000000004]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,"21",null,"21",null,"21",null,"21",null,null,null,null,"21",null,"21",null,"21",null,null,null,null,null,"21","21",null,null,"21"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"T043","index":240,"n_rows":48,"n_cols":35,"rows_kept":48,"cut":false,"hidden":false,"merged":[[0,2,0,40],[2,1,2,5],[2,8,4,20],[2,23,3,24],[2,26,4,37],[6,1,8,5],[6,8,6,36],[8,8,9,36],[11,8,11,36],[13,3,14,11],[13,14,13,26],[16,17,17,31],[17,3,18,11],[17,14,18,15],[21,4,22,8],[21,9,21,21],[21,22,21,34],[22,9,22,10],[22,11,22,12],[22,13,22,14],[22,15,22,19],[22,20,22,21],[22,22,22,23],[22,24,22,29],[22,31,22,33],[23,4,23,8],[23,9,23,10],[23,11,23,12],[23,13,23,14],[23,15,23,19],[23,20,23,21],[23,22,23,23],[23,24,23,29],[23,31,23,33],[24,4,24,8],[24,9,24,10],[24,11,24,12],[24,13,24,14],[24,15,24,19],[24,20,24,21],[24,22,24,23],[24,24,24,29],[24,31,24,33],[25,4,25,8],[25,9,25,10],[25,11,25,12],[25,13,25,14],[25,15,25,19],[25,20,25,21],[25,22,25,23],[25,24,25,29],[25,31,25,33],[26,4,26,8],[26,9,26,10],[26,11,26,12],[26,13,26,14],[26,15,26,19],[26,20,26,21],[26,22,26,23],[26,24,26,29],[26,31,26,33],[27,4,27,8],[27,9,27,10],[27,11,27,12],[27,13,27,14],[27,15,27,19],[27,20,27,21],[27,22,27,23],[27,24,27,29],[27,31,27,33],[28,4,28,8],[28,9,28,10],[28,11,28,12],[28,13,28,14],[28,15,28,19],[28,20,28,21],[28,22,28,23],[28,24,28,29],[28,31,28,33],[29,4,29,8],[29,9,29,10],[29,11,29,12],[29,13,29,14],[29,15,29,19],[29,20,29,21],[29,22,29,23],[29,24,29,29],[29,31,29,33],[30,4,30,8],[30,9,30,10],[30,11,30,12],[30,13,30,14],[30,15,30,19],[30,20,30,21],[30,22,30,23],[30,24,30,29],[30,31,30,33],[31,4,31,8],[31,9,31,10],[31,11,31,12],[31,13,31,14],[31,15,31,19],[31,20,31,21],[31,22,31,23],[31,24,31,29],[31,31,31,33],[32,4,32,8],[32,9,32,10],[32,11,32,12],[32,13,32,14],[32,15,32,19],[32,20,32,21],[32,22,32,23],[32,24,32,29],[32,31,32,33],[33,4,33,8],[33,9,33,10],[33,11,33,12],[33,13,33,14],[33,15,33,19],[33,20,33,21],[33,22,33,23],[33,24,33,29],[33,31,33,33],[34,4,34,8],[34,9,34,10],[34,11,34,12],[34,13,34,14],[34,15,34,19],[34,20,34,21],[34,22,34,23],[34,24,34,29],[34,31,34,33],[35,4,35,8],[35,9,35,10],[35,11,35,12],[35,13,35,14],[35,15,35,19],[35,20,35,21],[35,22,35,23],[35,24,35,29],[35,31,35,33],[36,4,36,8],[36,9,36,10],[36,11,36,12],[36,13,36,14],[36,15,36,19],[36,20,36,21],[36,22,36,23],[36,24,36,29],[36,31,36,33],[37,4,37,8],[37,9,37,10],[37,11,37,12],[37,13,37,14],[37,15,37,19],[37,20,37,21],[37,22,37,23],[37,24,37,29],[37,31,37,33],[39,31,39,33],[38,4,38,8],[38,9,38,10],[38,11,38,12],[38,13,38,14],[38,15,38,19],[38,20,38,21],[38,22,38,23],[38,24,38,29],[38,31,38,33],[40,4,40,8],[40,9,40,10],[40,11,40,12],[40,13,40,14],[40,15,40,19],[39,22,39,23],[39,24,39,29],[39,4,39,8],[39,9,39,10],[39,11,39,12],[39,13,39,14],[39,15,39,19],[39,20,39,21],[40,22,40,23],[40,24,40,29],[40,31,40,33],[42,20,42,21],[42,22,42,23],[40,20,40,21],[42,9,42,10],[42,11,42,12],[42,13,42,14],[42,15,42,19],[41,9,41,10],[41,11,41,12],[41,13,41,14],[41,15,41,19],[43,31,43,33],[41,20,41,21],[43,22,43,23],[43,24,43,29],[41,22,41,23],[41,24,41,29],[47,2,47,38],[42,24,42,29],[42,31,42,33],[43,4,43,8],[43,9,43,10],[43,11,43,12],[43,13,43,14],[43,15,43,19],[43,20,43,21],[42,4,42,8],[41,31,41,33],[41,4,41,8]]}
[null,null,"Bulk Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,"T043 - South Toowoomba BSP (110/33kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"QMRG - Middle Ridge (Ergon) TCP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,"Region is South West"]
[]
[null,null,null,null,null,null,null,null,"Transformer size is 1x106/33kV 35/60MVA ON/OFB;1x106/33kV 37/48/60MVA ON/OB/OFB"]
[]
[]
[null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,"79.7 MVA on 20/06/2018 at 18:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,144.89999389648438,null,144.89999389648438,null,144.89999389648438,null,144.89999389648438,null,null,null,null,144.89999389648438,null,163.60000610351563,null,163.60000610351563,null,null,null,null,null,163.60000610351563,163.60000610351563,null,null,163.60000610351563]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,64,null,63.400001525878906,null,62.299999237060547,null,61.799999237060547,null,null,null,null,61.900001525878906,null,84.599998474121094,null,83.900001525878906,null,null,null,null,null,83.199996948242188,82.599998474121094,null,null,82.099998474121094]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,0.97599999999999998,null,0.97599999999999998,null,0.97599999999999998,null,0.97599999999999998,null,null,null,null,0.97599999999999998,null,0.97699999999999998,null,0.97699999999999998,null,null,null,null,null,0.97699999999999998,0.97699999999999998,null,null,0.97699999999999998]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,81.400001525878906,null,81.400001525878906,null,81.400001525878906,null,81.400001525878906,null,null,null,null,81.400001525878906,null,89.300003051757813,null,89.300003051757813,null,null,null,null,null,89.300003051757813,89.300003051757813,null,null,89.300003051757813]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,56.700000762939453,null,56.200000762939453,null,55.200000762939453,null,54.700000762939453,null,null,null,null,54.900001525878906,null,77.300003051757813,null,76.599998474121094,null,null,null,null,null,76,75.5,null,null,75]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,2.8,null,2.8,null,2.8,null,2.7,null,null,null,null,2.7,null,3.9,null,3.8,null,null,null,null,null,3.8,3.8,null,null,3.8]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,"24",null,"24",null,"24",null,"24",null,null,null,null,"24",null,"24",null,"24",null,null,null,null,null,"24","24",null,null,"24"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"T058","index":241,"n_rows":48,"n_cols":35,"rows_kept":48,"cut":false,"hidden":false,"merged":[[0,2,0,40],[2,1,2,5],[2,8,4,20],[2,23,3,24],[2,26,4,37],[6,1,8,5],[6,8,6,36],[8,8,9,36],[11,8,11,36],[13,3,14,11],[13,14,13,26],[16,17,17,31],[17,3,18,11],[17,14,18,15],[21,4,22,8],[21,9,21,21],[21,22,21,34],[22,9,22,10],[22,11,22,12],[22,13,22,14],[22,15,22,19],[22,20,22,21],[22,22,22,23],[22,24,22,29],[22,31,22,33],[23,4,23,8],[23,9,23,10],[23,11,23,12],[23,13,23,14],[23,15,23,19],[23,20,23,21],[23,22,23,23],[23,24,23,29],[23,31,23,33],[24,4,24,8],[24,9,24,10],[24,11,24,12],[24,13,24,14],[24,15,24,19],[24,20,24,21],[24,22,24,23],[24,24,24,29],[24,31,24,33],[25,4,25,8],[25,9,25,10],[25,11,25,12],[25,13,25,14],[25,15,25,19],[25,20,25,21],[25,22,25,23],[25,24,25,29],[25,31,25,33],[26,4,26,8],[26,9,26,10],[26,11,26,12],[26,13,26,14],[26,15,26,19],[26,20,26,21],[26,22,26,23],[26,24,26,29],[26,31,26,33],[27,4,27,8],[27,9,27,10],[27,11,27,12],[27,13,27,14],[27,15,27,19],[27,20,27,21],[27,22,27,23],[27,24,27,29],[27,31,27,33],[28,4,28,8],[28,9,28,10],[28,11,28,12],[28,13,28,14],[28,15,28,19],[28,20,28,21],[28,22,28,23],[28,24,28,29],[28,31,28,33],[29,4,29,8],[29,9,29,10],[29,11,29,12],[29,13,29,14],[29,15,29,19],[29,20,29,21],[29,22,29,23],[29,24,29,29],[29,31,29,33],[30,4,30,8],[30,9,30,10],[30,11,30,12],[30,13,30,14],[30,15,30,19],[30,20,30,21],[30,22,30,23],[30,24,30,29],[30,31,30,33],[31,4,31,8],[31,9,31,10],[31,11,31,12],[31,13,31,14],[31,15,31,19],[31,20,31,21],[31,22,31,23],[31,24,31,29],[31,31,31,33],[32,4,32,8],[32,9,32,10],[32,11,32,12],[32,13,32,14],[32,15,32,19],[32,20,32,21],[32,22,32,23],[32,24,32,29],[32,31,32,33],[33,4,33,8],[33,9,33,10],[33,11,33,12],[33,13,33,14],[33,15,33,19],[33,20,33,21],[33,22,33,23],[33,24,33,29],[33,31,33,33],[34,4,34,8],[34,9,34,10],[34,11,34,12],[34,13,34,14],[34,15,34,19],[34,20,34,21],[34,22,34,23],[34,24,34,29],[34,31,34,33],[35,4,35,8],[35,9,35,10],[35,11,35,12],[35,13,35,14],[35,15,35,19],[35,20,35,21],[35,22,35,23],[35,24,35,29],[35,31,35,33],[36,4,36,8],[36,9,36,10],[36,11,36,12],[36,13,36,14],[36,15,36,19],[36,20,36,21],[36,22,36,23],[36,24,36,29],[36,31,36,33],[37,4,37,8],[37,9,37,10],[37,11,37,12],[37,13,37,14],[37,15,37,19],[37,20,37,21],[37,22,37,23],[37,24,37,29],[37,31,37,33],[39,31,39,33],[38,4,38,8],[38,9,38,10],[38,11,38,12],[38,13,38,14],[38,15,38,19],[38,20,38,21],[38,22,38,23],[38,24,38,29],[38,31,38,33],[40,4,40,8],[40,9,40,10],[40,11,40,12],[40,13,40,14],[40,15,40,19],[39,22,39,23],[39,24,39,29],[39,4,39,8],[39,9,39,10],[39,11,39,12],[39,13,39,14],[39,15,39,19],[39,20,39,21],[40,22,40,23],[40,24,40,29],[40,31,40,33],[42,20,42,21],[42,22,42,23],[40,20,40,21],[42,9,42,10],[42,11,42,12],[42,13,42,14],[42,15,42,19],[41,9,41,10],[41,11,41,12],[41,13,41,14],[41,15,41,19],[43,31,43,33],[41,20,41,21],[43,22,43,23],[43,24,43,29],[41,22,41,23],[41,24,41,29],[47,2,47,38],[42,24,42,29],[42,31,42,33],[43,4,43,8],[43,9,43,10],[43,11,43,12],[43,13,43,14],[43,15,43,19],[43,20,43,21],[42,4,42,8],[41,31,41,33],[41,4,41,8]]}
[null,null,"Bulk Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,"T058 - Warwick BSP (110/33kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"QMRG - Middle Ridge (Ergon) TCP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,"Region is South West"]
[]
[null,null,null,null,null,null,null,null,"Transformer size is 1x110/33/11kV 40/50MVA ONAN/ONAF;1x110/33kV 40/50MVA ONAN/ONAF"]
[]
[]
[null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,"34.9 MVA on 13/02/2019 at 17:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,118.5,null,118.5,null,118.5,null,118.5,null,null,null,null,118.5,null,135.60000610351563,null,135.60000610351563,null,null,null,null,null,135.60000610351563,135.60000610351563,null,null,135.60000610351563]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,41.900001525878906,null,41.5,null,41,null,40.799999237060547,null,null,null,null,40.900001525878906,null,37.700000762939453,null,37.299999237060547,null,null,null,null,null,37,36.900001525878906,null,null,36.799999237060547]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,0.997,null,0.997,null,0.997,null,0.997,null,null,null,null,0.997,null,0.996,null,0.996,null,null,null,null,null,0.996,0.996,null,null,0.996]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,68,null,68,null,68,null,68,null,null,null,null,68,null,74.800003051757813,null,74.800003051757813,null,null,null,null,null,74.800003051757813,74.800003051757813,null,null,74.800003051757813]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,36.099998474121094,null,35.700000762939453,null,35.299999237060547,null,35.200000762939453,null,null,null,null,35.299999237060547,null,35,null,34.599998474121094,null,null,null,null,null,34.299999237060547,34.299999237060547,null,null,34.200000762939453]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,1.8,null,1.8,null,1.8,null,1.8,null,null,null,null,1.8,null,1.8,null,1.7,null,null,null,null,null,1.7,1.7,null,null,1.7]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,"17",null,"17",null,"17",null,"17",null,null,null,null,"17",null,"17",null,"17",null,null,null,null,null,"17","17",null,null,"17"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"T059","index":242,"n_rows":48,"n_cols":35,"rows_kept":48,"cut":false,"hidden":false,"merged":[[0,2,0,40],[2,1,2,5],[2,8,4,20],[2,23,3,24],[2,26,4,37],[6,1,8,5],[6,8,6,36],[8,8,9,36],[11,8,11,36],[13,3,14,11],[13,14,13,26],[16,17,17,31],[17,3,18,11],[17,14,18,15],[21,4,22,8],[21,9,21,21],[21,22,21,34],[22,9,22,10],[22,11,22,12],[22,13,22,14],[22,15,22,19],[22,20,22,21],[22,22,22,23],[22,24,22,29],[22,31,22,33],[23,4,23,8],[23,9,23,10],[23,11,23,12],[23,13,23,14],[23,15,23,19],[23,20,23,21],[23,22,23,23],[23,24,23,29],[23,31,23,33],[24,4,24,8],[24,9,24,10],[24,11,24,12],[24,13,24,14],[24,15,24,19],[24,20,24,21],[24,22,24,23],[24,24,24,29],[24,31,24,33],[25,4,25,8],[25,9,25,10],[25,11,25,12],[25,13,25,14],[25,15,25,19],[25,20,25,21],[25,22,25,23],[25,24,25,29],[25,31,25,33],[26,4,26,8],[26,9,26,10],[26,11,26,12],[26,13,26,14],[26,15,26,19],[26,20,26,21],[26,22,26,23],[26,24,26,29],[26,31,26,33],[27,4,27,8],[27,9,27,10],[27,11,27,12],[27,13,27,14],[27,15,27,19],[27,20,27,21],[27,22,27,23],[27,24,27,29],[27,31,27,33],[28,4,28,8],[28,9,28,10],[28,11,28,12],[28,13,28,14],[28,15,28,19],[28,20,28,21],[28,22,28,23],[28,24,28,29],[28,31,28,33],[29,4,29,8],[29,9,29,10],[29,11,29,12],[29,13,29,14],[29,15,29,19],[29,20,29,21],[29,22,29,23],[29,24,29,29],[29,31,29,33],[30,4,30,8],[30,9,30,10],[30,11,30,12],[30,13,30,14],[30,15,30,19],[30,20,30,21],[30,22,30,23],[30,24,30,29],[30,31,30,33],[31,4,31,8],[31,9,31,10],[31,11,31,12],[31,13,31,14],[31,15,31,19],[31,20,31,21],[31,22,31,23],[31,24,31,29],[31,31,31,33],[32,4,32,8],[32,9,32,10],[32,11,32,12],[32,13,32,14],[32,15,32,19],[32,20,32,21],[32,22,32,23],[32,24,32,29],[32,31,32,33],[33,4,33,8],[33,9,33,10],[33,11,33,12],[33,13,33,14],[33,15,33,19],[33,20,33,21],[33,22,33,23],[33,24,33,29],[33,31,33,33],[34,4,34,8],[34,9,34,10],[34,11,34,12],[34,13,34,14],[34,15,34,19],[34,20,34,21],[34,22,34,23],[34,24,34,29],[34,31,34,33],[35,4,35,8],[35,9,35,10],[35,11,35,12],[35,13,35,14],[35,15,35,19],[35,20,35,21],[35,22,35,23],[35,24,35,29],[35,31,35,33],[36,4,36,8],[36,9,36,10],[36,11,36,12],[36,13,36,14],[36,15,36,19],[36,20,36,21],[36,22,36,23],[36,24,36,29],[36,31,36,33],[37,4,37,8],[37,9,37,10],[37,11,37,12],[37,13,37,14],[37,15,37,19],[37,20,37,21],[37,22,37,23],[37,24,37,29],[37,31,37,33],[39,31,39,33],[38,4,38,8],[38,9,38,10],[38,11,38,12],[38,13,38,14],[38,15,38,19],[38,20,38,21],[38,22,38,23],[38,24,38,29],[38,31,38,33],[40,4,40,8],[40,9,40,10],[40,11,40,12],[40,13,40,14],[40,15,40,19],[39,22,39,23],[39,24,39,29],[39,4,39,8],[39,9,39,10],[39,11,39,12],[39,13,39,14],[39,15,39,19],[39,20,39,21],[40,22,40,23],[40,24,40,29],[40,31,40,33],[42,20,42,21],[42,22,42,23],[40,20,40,21],[42,9,42,10],[42,11,42,12],[42,13,42,14],[42,15,42,19],[41,9,41,10],[41,11,41,12],[41,13,41,14],[41,15,41,19],[43,31,43,33],[41,20,41,21],[43,22,43,23],[43,24,43,29],[41,22,41,23],[41,24,41,29],[47,2,47,38],[42,24,42,29],[42,31,42,33],[43,4,43,8],[43,9,43,10],[43,11,43,12],[43,13,43,14],[43,15,43,19],[43,20,43,21],[42,4,42,8],[41,31,41,33],[41,4,41,8]]}
[null,null,"Bulk Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,"T059 - Maryborough BSP (132/66kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"QTBC - Teebar Creek TCP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,"Region is Wide Bay"]
[]
[null,null,null,null,null,null,null,null,"Transformer size is 2x132/66/11kV 80/100MVA ONAN/ODAN;1x132/66kV 64/80/90MVA ONAN/ODAN/ODAF"]
[]
[]
[null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 78.4 MVA"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,"116.7 MVA on 13/02/2019 at 16:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,356.10000610351563,null,356.10000610351563,null,356.10000610351563,null,356.10000610351563,null,null,null,null,356.10000610351563,null,403.70001220703125,null,403.70001220703125,null,null,null,null,null,403.70001220703125,403.70001220703125,null,null,403.70001220703125]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,0.10000000149011612,null,0.10000000149011612,null,0.10000000149011612,null,0.10000000149011612,null,null,null,null,0.10000000149011612,null,0.10000000149011612,null,0.10000000149011612,null,null,null,null,null,0.10000000149011612,0.10000000149011612,null,null,0.10000000149011612]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,135.30000305175781,null,135.89999389648438,null,137.19999694824219,null,139.5,null,null,null,null,140.69999694824219,null,96.900001525878906,null,99.599998474121094,null,null,null,null,null,100.40000152587891,102.5,null,null,104.69999694824219]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,0.99,null,0.99,null,0.99,null,0.99,null,null,null,null,0.99,null,1,null,0.999,null,null,null,null,null,0.999,0.999,null,null,0.999]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,266.79998779296875,null,266.79998779296875,null,266.79998779296875,null,266.79998779296875,null,null,null,null,266.79998779296875,null,269.10000610351563,null,269.10000610351563,null,null,null,null,null,269.10000610351563,269.10000610351563,null,null,269.10000610351563]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,124.5,null,125.09999847412109,null,126.40000152587891,null,128.80000305175781,null,null,null,null,129.80000305175781,null,91.400001525878906,null,94.099998474121094,null,null,null,null,null,94.900001525878906,96.900001525878906,null,null,99.199996948242188]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,6.2,null,6.3,null,6.3,null,6.4,null,null,null,null,6.5,null,4.5999999999999996,null,4.7,null,null,null,null,null,4.7,4.8,null,null,5]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,"7.5",null,"7.5",null,"7.5",null,"7.5",null,null,null,null,"7.5",null,"7.5",null,"7.5",null,null,null,null,null,"7.5","7.5",null,null,"7.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"T060","index":243,"n_rows":48,"n_cols":35,"rows_kept":48,"cut":false,"hidden":false,"merged":[[0,2,0,40],[2,1,2,5],[2,8,4,20],[2,23,3,24],[2,26,4,37],[6,1,8,5],[6,8,6,36],[8,8,9,36],[11,8,11,36],[13,3,14,11],[13,14,13,26],[16,17,17,31],[17,3,18,11],[17,14,18,15],[21,4,22,8],[21,9,21,21],[21,22,21,34],[22,9,22,10],[22,11,22,12],[22,13,22,14],[22,15,22,19],[22,20,22,21],[22,22,22,23],[22,24,22,29],[22,31,22,33],[23,4,23,8],[23,9,23,10],[23,11,23,12],[23,13,23,14],[23,15,23,19],[23,20,23,21],[23,22,23,23],[23,24,23,29],[23,31,23,33],[24,4,24,8],[24,9,24,10],[24,11,24,12],[24,13,24,14],[24,15,24,19],[24,20,24,21],[24,22,24,23],[24,24,24,29],[24,31,24,33],[25,4,25,8],[25,9,25,10],[25,11,25,12],[25,13,25,14],[25,15,25,19],[25,20,25,21],[25,22,25,23],[25,24,25,29],[25,31,25,33],[26,4,26,8],[26,9,26,10],[26,11,26,12],[26,13,26,14],[26,15,26,19],[26,20,26,21],[26,22,26,23],[26,24,26,29],[26,31,26,33],[27,4,27,8],[27,9,27,10],[27,11,27,12],[27,13,27,14],[27,15,27,19],[27,20,27,21],[27,22,27,23],[27,24,27,29],[27,31,27,33],[28,4,28,8],[28,9,28,10],[28,11,28,12],[28,13,28,14],[28,15,28,19],[28,20,28,21],[28,22,28,23],[28,24,28,29],[28,31,28,33],[29,4,29,8],[29,9,29,10],[29,11,29,12],[29,13,29,14],[29,15,29,19],[29,20,29,21],[29,22,29,23],[29,24,29,29],[29,31,29,33],[30,4,30,8],[30,9,30,10],[30,11,30,12],[30,13,30,14],[30,15,30,19],[30,20,30,21],[30,22,30,23],[30,24,30,29],[30,31,30,33],[31,4,31,8],[31,9,31,10],[31,11,31,12],[31,13,31,14],[31,15,31,19],[31,20,31,21],[31,22,31,23],[31,24,31,29],[31,31,31,33],[32,4,32,8],[32,9,32,10],[32,11,32,12],[32,13,32,14],[32,15,32,19],[32,20,32,21],[32,22,32,23],[32,24,32,29],[32,31,32,33],[33,4,33,8],[33,9,33,10],[33,11,33,12],[33,13,33,14],[33,15,33,19],[33,20,33,21],[33,22,33,23],[33,24,33,29],[33,31,33,33],[34,4,34,8],[34,9,34,10],[34,11,34,12],[34,13,34,14],[34,15,34,19],[34,20,34,21],[34,22,34,23],[34,24,34,29],[34,31,34,33],[35,4,35,8],[35,9,35,10],[35,11,35,12],[35,13,35,14],[35,15,35,19],[35,20,35,21],[35,22,35,23],[35,24,35,29],[35,31,35,33],[36,4,36,8],[36,9,36,10],[36,11,36,12],[36,13,36,14],[36,15,36,19],[36,20,36,21],[36,22,36,23],[36,24,36,29],[36,31,36,33],[37,4,37,8],[37,9,37,10],[37,11,37,12],[37,13,37,14],[37,15,37,19],[37,20,37,21],[37,22,37,23],[37,24,37,29],[37,31,37,33],[39,31,39,33],[38,4,38,8],[38,9,38,10],[38,11,38,12],[38,13,38,14],[38,15,38,19],[38,20,38,21],[38,22,38,23],[38,24,38,29],[38,31,38,33],[40,4,40,8],[40,9,40,10],[40,11,40,12],[40,13,40,14],[40,15,40,19],[39,22,39,23],[39,24,39,29],[39,4,39,8],[39,9,39,10],[39,11,39,12],[39,13,39,14],[39,15,39,19],[39,20,39,21],[40,22,40,23],[40,24,40,29],[40,31,40,33],[42,20,42,21],[42,22,42,23],[40,20,40,21],[42,9,42,10],[42,11,42,12],[42,13,42,14],[42,15,42,19],[41,9,41,10],[41,11,41,12],[41,13,41,14],[41,15,41,19],[43,31,43,33],[41,20,41,21],[43,22,43,23],[43,24,43,29],[41,22,41,23],[41,24,41,29],[47,2,47,38],[42,24,42,29],[42,31,42,33],[43,4,43,8],[43,9,43,10],[43,11,43,12],[43,13,43,14],[43,15,43,19],[43,20,43,21],[42,4,42,8],[41,31,41,33],[41,4,41,8]]}
[null,null,"Bulk Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,"T060 - Stanthorpe BSP (110/33kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"QMRG - Middle Ridge (Ergon) TCP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,"Region is South West"]
[]
[null,null,null,null,null,null,null,null,"Transformer size is 2x103/33kV 20/30MVA ON/OB"]
[]
[]
[null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,"14.6 MVA on 18/06/2018 at 18:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,71.300003051757813,null,71.300003051757813,null,71.300003051757813,null,71.300003051757813,null,null,null,null,71.300003051757813,null,80.400001525878906,null,80.400001525878906,null,null,null,null,null,80.400001525878906,80.400001525878906,null,null,80.400001525878906]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,14.899999618530273,null,14.800000190734863,null,14.600000381469727,null,14.5,null,null,null,null,14.5,null,15.399999618530273,null,15.300000190734863,null,null,null,null,null,15.199999809265137,15.100000381469727,null,null,15.100000381469727]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,0.99,null,0.99,null,0.99,null,0.99,null,null,null,null,0.99,null,0.99199999999999999,null,0.99199999999999999,null,null,null,null,null,0.99199999999999999,0.99199999999999999,null,null,0.99199999999999999]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,40.5,null,40.5,null,40.5,null,40.5,null,null,null,null,40.5,null,43.799999237060547,null,43.799999237060547,null,null,null,null,null,43.799999237060547,43.799999237060547,null,null,43.799999237060547]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,13.800000190734863,null,13.699999809265137,null,13.5,null,13.399999618530273,null,null,null,null,13.399999618530273,null,14.5,null,14.399999618530273,null,null,null,null,null,14.300000190734863,14.300000190734863,null,null,14.199999809265137]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,0.7,null,0.7,null,0.7,null,0.7,null,null,null,null,0.7,null,0.7,null,0.7,null,null,null,null,null,0.7,0.7,null,null,0.7]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,"15",null,"15",null,"15",null,"15",null,null,null,null,"15",null,"15",null,"15",null,null,null,null,null,"15","15",null,null,"15"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"T065","index":244,"n_rows":48,"n_cols":35,"rows_kept":48,"cut":false,"hidden":false,"merged":[[0,2,0,40],[2,1,2,5],[2,8,4,20],[2,23,3,24],[2,26,4,37],[6,1,8,5],[6,8,6,36],[8,8,9,36],[11,8,11,36],[13,3,14,11],[13,14,13,26],[16,17,17,31],[17,3,18,11],[17,14,18,15],[21,4,22,8],[21,9,21,21],[21,22,21,34],[22,9,22,10],[22,11,22,12],[22,13,22,14],[22,15,22,19],[22,20,22,21],[22,22,22,23],[22,24,22,29],[22,31,22,33],[23,4,23,8],[23,9,23,10],[23,11,23,12],[23,13,23,14],[23,15,23,19],[23,20,23,21],[23,22,23,23],[23,24,23,29],[23,31,23,33],[24,4,24,8],[24,9,24,10],[24,11,24,12],[24,13,24,14],[24,15,24,19],[24,20,24,21],[24,22,24,23],[24,24,24,29],[24,31,24,33],[25,4,25,8],[25,9,25,10],[25,11,25,12],[25,13,25,14],[25,15,25,19],[25,20,25,21],[25,22,25,23],[25,24,25,29],[25,31,25,33],[26,4,26,8],[26,9,26,10],[26,11,26,12],[26,13,26,14],[26,15,26,19],[26,20,26,21],[26,22,26,23],[26,24,26,29],[26,31,26,33],[27,4,27,8],[27,9,27,10],[27,11,27,12],[27,13,27,14],[27,15,27,19],[27,20,27,21],[27,22,27,23],[27,24,27,29],[27,31,27,33],[28,4,28,8],[28,9,28,10],[28,11,28,12],[28,13,28,14],[28,15,28,19],[28,20,28,21],[28,22,28,23],[28,24,28,29],[28,31,28,33],[29,4,29,8],[29,9,29,10],[29,11,29,12],[29,13,29,14],[29,15,29,19],[29,20,29,21],[29,22,29,23],[29,24,29,29],[29,31,29,33],[30,4,30,8],[30,9,30,10],[30,11,30,12],[30,13,30,14],[30,15,30,19],[30,20,30,21],[30,22,30,23],[30,24,30,29],[30,31,30,33],[31,4,31,8],[31,9,31,10],[31,11,31,12],[31,13,31,14],[31,15,31,19],[31,20,31,21],[31,22,31,23],[31,24,31,29],[31,31,31,33],[32,4,32,8],[32,9,32,10],[32,11,32,12],[32,13,32,14],[32,15,32,19],[32,20,32,21],[32,22,32,23],[32,24,32,29],[32,31,32,33],[33,4,33,8],[33,9,33,10],[33,11,33,12],[33,13,33,14],[33,15,33,19],[33,20,33,21],[33,22,33,23],[33,24,33,29],[33,31,33,33],[34,4,34,8],[34,9,34,10],[34,11,34,12],[34,13,34,14],[34,15,34,19],[34,20,34,21],[34,22,34,23],[34,24,34,29],[34,31,34,33],[35,4,35,8],[35,9,35,10],[35,11,35,12],[35,13,35,14],[35,15,35,19],[35,20,35,21],[35,22,35,23],[35,24,35,29],[35,31,35,33],[36,4,36,8],[36,9,36,10],[36,11,36,12],[36,13,36,14],[36,15,36,19],[36,20,36,21],[36,22,36,23],[36,24,36,29],[36,31,36,33],[37,4,37,8],[37,9,37,10],[37,11,37,12],[37,13,37,14],[37,15,37,19],[37,20,37,21],[37,22,37,23],[37,24,37,29],[37,31,37,33],[39,31,39,33],[38,4,38,8],[38,9,38,10],[38,11,38,12],[38,13,38,14],[38,15,38,19],[38,20,38,21],[38,22,38,23],[38,24,38,29],[38,31,38,33],[40,4,40,8],[40,9,40,10],[40,11,40,12],[40,13,40,14],[40,15,40,19],[39,22,39,23],[39,24,39,29],[39,4,39,8],[39,9,39,10],[39,11,39,12],[39,13,39,14],[39,15,39,19],[39,20,39,21],[40,22,40,23],[40,24,40,29],[40,31,40,33],[42,20,42,21],[42,22,42,23],[40,20,40,21],[42,9,42,10],[42,11,42,12],[42,13,42,14],[42,15,42,19],[41,9,41,10],[41,11,41,12],[41,13,41,14],[41,15,41,19],[43,31,43,33],[41,20,41,21],[43,22,43,23],[43,24,43,29],[41,22,41,23],[41,24,41,29],[47,2,47,38],[42,24,42,29],[42,31,42,33],[43,4,43,8],[43,9,43,10],[43,11,43,12],[43,13,43,14],[43,15,43,19],[43,20,43,21],[42,4,42,8],[41,31,41,33],[41,4,41,8]]}
[null,null,"Bulk Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,"T065 - Alligator Creek BSP (132/33kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"QALC - Alligator Creek 33kV TCP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,"Region is Mackay"]
[]
[null,null,null,null,null,null,null,null,"Transformer size is 1xALCR TFMR-2-2 TRANSFORMER 132/33/11KV-100 MVA;1xALCR TFMR-3 TRANSFORMER 132/33/11KV-100 MVA"]
[]
[]
[null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 17.5 MVA"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,"32.9 MVA on 28/11/2018 at 19:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,200,null,200,null,200,null,200,null,null,null,null,200,null,200,null,200,null,null,null,null,null,200,200,null,null,200]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,38.599998474121094,null,38.5,null,38.299999237060547,null,38.400001525878906,null,null,null,null,38.799999237060547,null,21.200000762939453,null,21.200000762939453,null,null,null,null,null,21.200000762939453,21.200000762939453,null,null,21.399999618530273]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,0.99099999999999999,null,0.99099999999999999,null,0.99099999999999999,null,0.99099999999999999,null,null,null,null,0.99099999999999999,null,0.99299999999999999,null,0.99299999999999999,null,null,null,null,null,0.99299999999999999,0.99299999999999999,null,null,0.99299999999999999]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,100,null,100,null,100,null,100,null,null,null,null,100,null,100,null,100,null,null,null,null,null,100,100,null,null,100]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,33.099998474121094,null,33,null,32.799999237060547,null,32.900001525878906,null,null,null,null,33.200000762939453,null,19,null,19,null,null,null,null,null,19,19.100000381469727,null,null,19.200000762939453]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,1.7,null,1.7,null,1.6,null,1.6,null,null,null,null,1.7,null,1,null,1,null,null,null,null,null,1,1,null,null,1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,"8",null,"8",null,"8",null,"8",null,null,null,null,"8",null,"8",null,"8",null,null,null,null,null,"8","8",null,null,"8"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,1,null,1,null,1,null,1,null,null,null,null,1,null,1,null,1,null,null,null,null,null,1,1,null,null,1]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,2,null,2,null,2,null,2,null,null,null,null,2,null,2,null,2,null,null,null,null,null,2,2,null,null,2]
[null,null,null,null,"Shed(30min)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"T071","index":245,"n_rows":48,"n_cols":35,"rows_kept":48,"cut":false,"hidden":false,"merged":[[0,2,0,40],[2,1,2,5],[2,8,4,20],[2,23,3,24],[2,26,4,37],[6,1,8,5],[6,8,6,36],[8,8,9,36],[11,8,11,36],[13,3,14,11],[13,14,13,26],[16,17,17,31],[17,3,18,11],[17,14,18,15],[21,4,22,8],[21,9,21,21],[21,22,21,34],[22,9,22,10],[22,11,22,12],[22,13,22,14],[22,15,22,19],[22,20,22,21],[22,22,22,23],[22,24,22,29],[22,31,22,33],[23,4,23,8],[23,9,23,10],[23,11,23,12],[23,13,23,14],[23,15,23,19],[23,20,23,21],[23,22,23,23],[23,24,23,29],[23,31,23,33],[24,4,24,8],[24,9,24,10],[24,11,24,12],[24,13,24,14],[24,15,24,19],[24,20,24,21],[24,22,24,23],[24,24,24,29],[24,31,24,33],[25,4,25,8],[25,9,25,10],[25,11,25,12],[25,13,25,14],[25,15,25,19],[25,20,25,21],[25,22,25,23],[25,24,25,29],[25,31,25,33],[26,4,26,8],[26,9,26,10],[26,11,26,12],[26,13,26,14],[26,15,26,19],[26,20,26,21],[26,22,26,23],[26,24,26,29],[26,31,26,33],[27,4,27,8],[27,9,27,10],[27,11,27,12],[27,13,27,14],[27,15,27,19],[27,20,27,21],[27,22,27,23],[27,24,27,29],[27,31,27,33],[28,4,28,8],[28,9,28,10],[28,11,28,12],[28,13,28,14],[28,15,28,19],[28,20,28,21],[28,22,28,23],[28,24,28,29],[28,31,28,33],[29,4,29,8],[29,9,29,10],[29,11,29,12],[29,13,29,14],[29,15,29,19],[29,20,29,21],[29,22,29,23],[29,24,29,29],[29,31,29,33],[30,4,30,8],[30,9,30,10],[30,11,30,12],[30,13,30,14],[30,15,30,19],[30,20,30,21],[30,22,30,23],[30,24,30,29],[30,31,30,33],[31,4,31,8],[31,9,31,10],[31,11,31,12],[31,13,31,14],[31,15,31,19],[31,20,31,21],[31,22,31,23],[31,24,31,29],[31,31,31,33],[32,4,32,8],[32,9,32,10],[32,11,32,12],[32,13,32,14],[32,15,32,19],[32,20,32,21],[32,22,32,23],[32,24,32,29],[32,31,32,33],[33,4,33,8],[33,9,33,10],[33,11,33,12],[33,13,33,14],[33,15,33,19],[33,20,33,21],[33,22,33,23],[33,24,33,29],[33,31,33,33],[34,4,34,8],[34,9,34,10],[34,11,34,12],[34,13,34,14],[34,15,34,19],[34,20,34,21],[34,22,34,23],[34,24,34,29],[34,31,34,33],[35,4,35,8],[35,9,35,10],[35,11,35,12],[35,13,35,14],[35,15,35,19],[35,20,35,21],[35,22,35,23],[35,24,35,29],[35,31,35,33],[36,4,36,8],[36,9,36,10],[36,11,36,12],[36,13,36,14],[36,15,36,19],[36,20,36,21],[36,22,36,23],[36,24,36,29],[36,31,36,33],[37,4,37,8],[37,9,37,10],[37,11,37,12],[37,13,37,14],[37,15,37,19],[37,20,37,21],[37,22,37,23],[37,24,37,29],[37,31,37,33],[39,31,39,33],[38,4,38,8],[38,9,38,10],[38,11,38,12],[38,13,38,14],[38,15,38,19],[38,20,38,21],[38,22,38,23],[38,24,38,29],[38,31,38,33],[40,4,40,8],[40,9,40,10],[40,11,40,12],[40,13,40,14],[40,15,40,19],[39,22,39,23],[39,24,39,29],[39,4,39,8],[39,9,39,10],[39,11,39,12],[39,13,39,14],[39,15,39,19],[39,20,39,21],[40,22,40,23],[40,24,40,29],[40,31,40,33],[42,20,42,21],[42,22,42,23],[40,20,40,21],[42,9,42,10],[42,11,42,12],[42,13,42,14],[42,15,42,19],[41,9,41,10],[41,11,41,12],[41,13,41,14],[41,15,41,19],[43,31,43,33],[41,20,41,21],[43,22,43,23],[43,24,43,29],[41,22,41,23],[41,24,41,29],[47,2,47,38],[42,24,42,29],[42,31,42,33],[43,4,43,8],[43,9,43,10],[43,11,43,12],[43,13,43,14],[43,15,43,19],[43,20,43,21],[42,4,42,8],[41,31,41,33],[41,4,41,8]]}
[null,null,"Bulk Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,"T071 - Clermont BSP (132/66kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"QLCM - Lilyvale (Barcaldine & Clermont) TCP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,"Region is Capricornia"]
[]
[null,null,null,null,null,null,null,null,"Transformer size is 2x132/69/11kV 30MVA OFDAN"]
[]
[]
[null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,"19 MVA on 21/02/2019 at 19:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,80.900001525878906,null,80.900001525878906,null,80.900001525878906,null,80.900001525878906,null,null,null,null,80.900001525878906,null,86.900001525878906,null,86.900001525878906,null,null,null,null,null,86.900001525878906,86.900001525878906,null,null,86.900001525878906]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,21.299999237060547,null,21.100000381469727,null,20.899999618530273,null,21,null,null,null,null,21.200000762939453,null,17.100000381469727,null,17,null,null,null,null,null,16.799999237060547,16.899999618530273,null,null,17]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,0.97099999999999997,null,0.97099999999999997,null,0.97099999999999997,null,0.97099999999999997,null,null,null,null,0.97099999999999997,null,0.98199999999999998,null,0.98199999999999998,null,null,null,null,null,0.98199999999999998,0.98199999999999998,null,null,0.98199999999999998]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,44.900001525878906,null,44.900001525878906,null,44.900001525878906,null,44.900001525878906,null,null,null,null,44.900001525878906,null,44.900001525878906,null,44.900001525878906,null,null,null,null,null,44.900001525878906,44.900001525878906,null,null,44.900001525878906]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,19.899999618530273,null,19.700000762939453,null,19.5,null,19.600000381469727,null,null,null,null,19.799999237060547,null,16.399999618530273,null,16.299999237060547,null,null,null,null,null,16.200000762939453,16.200000762939453,null,null,16.299999237060547]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,1,null,1,null,1,null,1,null,null,null,null,1,null,0.8,null,0.8,null,null,null,null,null,0.8,0.8,null,null,0.8]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,"4",null,"4",null,"4",null,"4",null,null,null,null,"4",null,"4",null,"4",null,null,null,null,null,"4","4",null,null,"4"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"T072","index":246,"n_rows":48,"n_cols":35,"rows_kept":48,"cut":false,"hidden":false,"merged":[[0,2,0,40],[2,1,2,5],[2,8,4,20],[2,23,3,24],[2,26,4,37],[6,1,8,5],[6,8,6,36],[8,8,9,36],[11,8,11,36],[13,3,14,11],[13,14,13,26],[16,17,17,31],[17,3,18,11],[17,14,18,15],[21,4,22,8],[21,9,21,21],[21,22,21,34],[22,9,22,10],[22,11,22,12],[22,13,22,14],[22,15,22,19],[22,20,22,21],[22,22,22,23],[22,24,22,29],[22,31,22,33],[23,4,23,8],[23,9,23,10],[23,11,23,12],[23,13,23,14],[23,15,23,19],[23,20,23,21],[23,22,23,23],[23,24,23,29],[23,31,23,33],[24,4,24,8],[24,9,24,10],[24,11,24,12],[24,13,24,14],[24,15,24,19],[24,20,24,21],[24,22,24,23],[24,24,24,29],[24,31,24,33],[25,4,25,8],[25,9,25,10],[25,11,25,12],[25,13,25,14],[25,15,25,19],[25,20,25,21],[25,22,25,23],[25,24,25,29],[25,31,25,33],[26,4,26,8],[26,9,26,10],[26,11,26,12],[26,13,26,14],[26,15,26,19],[26,20,26,21],[26,22,26,23],[26,24,26,29],[26,31,26,33],[27,4,27,8],[27,9,27,10],[27,11,27,12],[27,13,27,14],[27,15,27,19],[27,20,27,21],[27,22,27,23],[27,24,27,29],[27,31,27,33],[28,4,28,8],[28,9,28,10],[28,11,28,12],[28,13,28,14],[28,15,28,19],[28,20,28,21],[28,22,28,23],[28,24,28,29],[28,31,28,33],[29,4,29,8],[29,9,29,10],[29,11,29,12],[29,13,29,14],[29,15,29,19],[29,20,29,21],[29,22,29,23],[29,24,29,29],[29,31,29,33],[30,4,30,8],[30,9,30,10],[30,11,30,12],[30,13,30,14],[30,15,30,19],[30,20,30,21],[30,22,30,23],[30,24,30,29],[30,31,30,33],[31,4,31,8],[31,9,31,10],[31,11,31,12],[31,13,31,14],[31,15,31,19],[31,20,31,21],[31,22,31,23],[31,24,31,29],[31,31,31,33],[32,4,32,8],[32,9,32,10],[32,11,32,12],[32,13,32,14],[32,15,32,19],[32,20,32,21],[32,22,32,23],[32,24,32,29],[32,31,32,33],[33,4,33,8],[33,9,33,10],[33,11,33,12],[33,13,33,14],[33,15,33,19],[33,20,33,21],[33,22,33,23],[33,24,33,29],[33,31,33,33],[34,4,34,8],[34,9,34,10],[34,11,34,12],[34,13,34,14],[34,15,34,19],[34,20,34,21],[34,22,34,23],[34,24,34,29],[34,31,34,33],[35,4,35,8],[35,9,35,10],[35,11,35,12],[35,13,35,14],[35,15,35,19],[35,20,35,21],[35,22,35,23],[35,24,35,29],[35,31,35,33],[36,4,36,8],[36,9,36,10],[36,11,36,12],[36,13,36,14],[36,15,36,19],[36,20,36,21],[36,22,36,23],[36,24,36,29],[36,31,36,33],[37,4,37,8],[37,9,37,10],[37,11,37,12],[37,13,37,14],[37,15,37,19],[37,20,37,21],[37,22,37,23],[37,24,37,29],[37,31,37,33],[39,31,39,33],[38,4,38,8],[38,9,38,10],[38,11,38,12],[38,13,38,14],[38,15,38,19],[38,20,38,21],[38,22,38,23],[38,24,38,29],[38,31,38,33],[40,4,40,8],[40,9,40,10],[40,11,40,12],[40,13,40,14],[40,15,40,19],[39,22,39,23],[39,24,39,29],[39,4,39,8],[39,9,39,10],[39,11,39,12],[39,13,39,14],[39,15,39,19],[39,20,39,21],[40,22,40,23],[40,24,40,29],[40,31,40,33],[42,20,42,21],[42,22,42,23],[40,20,40,21],[42,9,42,10],[42,11,42,12],[42,13,42,14],[42,15,42,19],[41,9,41,10],[41,11,41,12],[41,13,41,14],[41,15,41,19],[43,31,43,33],[41,20,41,21],[43,22,43,23],[43,24,43,29],[41,22,41,23],[41,24,41,29],[47,2,47,38],[42,24,42,29],[42,31,42,33],[43,4,43,8],[43,9,43,10],[43,11,43,12],[43,13,43,14],[43,15,43,19],[43,20,43,21],[42,4,42,8],[41,31,41,33],[41,4,41,8]]}
[null,null,"Bulk Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,"T072 - Barcaldine BSP (132/66kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"QLCM - Lilyvale (Barcaldine & Clermont) TCP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,"Region is Capricornia"]
[]
[null,null,null,null,null,null,null,null,"Transformer size is 1xBARC TX NO 1-132/66KV TRANSF 1;1xBARC TX NO 2-132/66KV TRANSF 2"]
[]
[]
[null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 43.4 MVA"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,"19.7 MVA on 11/03/2019 at 19:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,26.600000381469727,null,26.600000381469727,null,26.600000381469727,null,26.600000381469727,null,null,null,null,26.600000381469727,null,26.600000381469727,null,26.600000381469727,null,null,null,null,null,26.600000381469727,26.600000381469727,null,null,26.600000381469727]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,2.5999999046325684,null,2.5999999046325684,null,null,null,null,null,2.5999999046325684,2.5999999046325684,null,null,2.5999999046325684]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,22.200000762939453,null,21.899999618530273,null,21.5,null,21.399999618530273,null,null,null,null,21.299999237060547,null,16.899999618530273,null,16.600000381469727,null,null,null,null,null,16.399999618530273,16.299999237060547,null,null,16.200000762939453]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,0.999,null,0.999,null,0.999,null,0.999,null,null,null,null,0.999,null,0.97099999999999997,null,0.97099999999999997,null,null,null,null,null,0.97099999999999997,0.97099999999999997,null,null,0.97099999999999997]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,13.300000190734863,null,13.300000190734863,null,13.300000190734863,null,13.300000190734863,null,null,null,null,13.300000190734863,null,14.600000381469727,null,14.600000381469727,null,null,null,null,null,14.600000381469727,14.600000381469727,null,null,14.600000381469727]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,20.700000762939453,null,20.399999618530273,null,20.100000381469727,null,19.899999618530273,null,null,null,null,19.899999618530273,null,15.300000190734863,null,15.100000381469727,null,null,null,null,null,14.899999618530273,14.800000190734863,null,null,14.699999809265137]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,1,null,1,null,1,null,1,null,null,null,null,1,null,0.8,null,0.8,null,null,null,null,null,0.7,0.7,null,null,0.7]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,"8",null,"8",null,"8",null,"8",null,null,null,null,"8",null,"8",null,"8",null,null,null,null,null,"8","8",null,null,"8"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,7.4,null,7.1,null,6.8,null,6.6,null,null,null,null,6.6,null,0.7,null,0.5,null,null,null,null,null,0.3,0.2,null,null,0.1]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,6.6999998092651367,null,6.6999998092651367,null,6.6999998092651367,null,6.6999998092651367,null,null,null,null,6.6999998092651367,null,6.6999998092651367,null,6.6999998092651367,null,null,null,null,null,6.6999998092651367,6.6999998092651367,null,null,6.6999998092651367]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,0.69999998807907104,null,0.69999998807907104,null,0.69999998807907104,null,0.69999998807907104,null,null,null,null,0.69999998807907104,null,0.69999998807907104,null,0.69999998807907104,null,null,null,null,null,0.69999998807907104,0.69999998807907104,null,null,0.69999998807907104]
[null,null,null,null,"Shed(30min)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"T074","index":247,"n_rows":48,"n_cols":35,"rows_kept":48,"cut":false,"hidden":false,"merged":[[0,2,0,40],[2,1,2,5],[2,8,4,20],[2,23,3,24],[2,26,4,37],[6,1,8,5],[6,8,6,36],[8,8,9,36],[11,8,11,36],[13,3,14,11],[13,14,13,26],[16,17,17,31],[17,3,18,11],[17,14,18,15],[21,4,22,8],[21,9,21,21],[21,22,21,34],[22,9,22,10],[22,11,22,12],[22,13,22,14],[22,15,22,19],[22,20,22,21],[22,22,22,23],[22,24,22,29],[22,31,22,33],[23,4,23,8],[23,9,23,10],[23,11,23,12],[23,13,23,14],[23,15,23,19],[23,20,23,21],[23,22,23,23],[23,24,23,29],[23,31,23,33],[24,4,24,8],[24,9,24,10],[24,11,24,12],[24,13,24,14],[24,15,24,19],[24,20,24,21],[24,22,24,23],[24,24,24,29],[24,31,24,33],[25,4,25,8],[25,9,25,10],[25,11,25,12],[25,13,25,14],[25,15,25,19],[25,20,25,21],[25,22,25,23],[25,24,25,29],[25,31,25,33],[26,4,26,8],[26,9,26,10],[26,11,26,12],[26,13,26,14],[26,15,26,19],[26,20,26,21],[26,22,26,23],[26,24,26,29],[26,31,26,33],[27,4,27,8],[27,9,27,10],[27,11,27,12],[27,13,27,14],[27,15,27,19],[27,20,27,21],[27,22,27,23],[27,24,27,29],[27,31,27,33],[28,4,28,8],[28,9,28,10],[28,11,28,12],[28,13,28,14],[28,15,28,19],[28,20,28,21],[28,22,28,23],[28,24,28,29],[28,31,28,33],[29,4,29,8],[29,9,29,10],[29,11,29,12],[29,13,29,14],[29,15,29,19],[29,20,29,21],[29,22,29,23],[29,24,29,29],[29,31,29,33],[30,4,30,8],[30,9,30,10],[30,11,30,12],[30,13,30,14],[30,15,30,19],[30,20,30,21],[30,22,30,23],[30,24,30,29],[30,31,30,33],[31,4,31,8],[31,9,31,10],[31,11,31,12],[31,13,31,14],[31,15,31,19],[31,20,31,21],[31,22,31,23],[31,24,31,29],[31,31,31,33],[32,4,32,8],[32,9,32,10],[32,11,32,12],[32,13,32,14],[32,15,32,19],[32,20,32,21],[32,22,32,23],[32,24,32,29],[32,31,32,33],[33,4,33,8],[33,9,33,10],[33,11,33,12],[33,13,33,14],[33,15,33,19],[33,20,33,21],[33,22,33,23],[33,24,33,29],[33,31,33,33],[34,4,34,8],[34,9,34,10],[34,11,34,12],[34,13,34,14],[34,15,34,19],[34,20,34,21],[34,22,34,23],[34,24,34,29],[34,31,34,33],[35,4,35,8],[35,9,35,10],[35,11,35,12],[35,13,35,14],[35,15,35,19],[35,20,35,21],[35,22,35,23],[35,24,35,29],[35,31,35,33],[36,4,36,8],[36,9,36,10],[36,11,36,12],[36,13,36,14],[36,15,36,19],[36,20,36,21],[36,22,36,23],[36,24,36,29],[36,31,36,33],[37,4,37,8],[37,9,37,10],[37,11,37,12],[37,13,37,14],[37,15,37,19],[37,20,37,21],[37,22,37,23],[37,24,37,29],[37,31,37,33],[39,31,39,33],[38,4,38,8],[38,9,38,10],[38,11,38,12],[38,13,38,14],[38,15,38,19],[38,20,38,21],[38,22,38,23],[38,24,38,29],[38,31,38,33],[40,22,40,23],[40,24,40,29],[39,4,39,8],[39,9,39,10],[39,11,39,12],[39,13,39,14],[39,15,39,19],[39,20,39,21],[39,22,39,23],[39,24,39,29],[40,31,40,33],[41,4,41,8],[41,9,41,10],[41,11,41,12],[41,13,41,14],[41,15,41,19],[41,20,41,21],[43,31,43,33],[41,24,41,29],[41,31,41,33],[42,4,42,8],[42,9,42,10],[42,11,42,12],[42,13,42,14],[42,15,42,19],[42,20,42,21],[42,22,42,23],[41,22,41,23],[40,4,40,8],[40,9,40,10],[40,11,40,12],[40,13,40,14],[40,15,40,19],[40,20,40,21],[47,2,47,38],[42,31,42,33],[43,4,43,8],[43,9,43,10],[43,11,43,12],[43,13,43,14],[43,15,43,19],[43,20,43,21],[43,22,43,23],[43,24,43,29],[42,24,42,29]]}
[null,null,"Bulk Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,"T074 - Gladstone North BSP (132/66kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"H067 - Calliope River TCP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,"Region is Capricornia"]
[]
[null,null,null,null,null,null,null,null,"Transformer size is 2x132/66/11kV 60/80MVA ONAN/ODAN"]
[]
[]
[null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,"51 MVA on 28/11/2018 at 18:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,184,null,184,null,184,null,184,null,null,null,null,184,null,208.80000305175781,null,208.80000305175781,null,null,null,null,null,208.80000305175781,208.80000305175781,null,null,208.80000305175781]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,54.299999237060547,null,54.099998474121094,null,53.5,null,53.5,null,null,null,null,53.799999237060547,null,34.200000762939453,null,34,null,null,null,null,null,33.900001525878906,33.900001525878906,null,null,34]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,0.997,null,0.997,null,0.997,null,0.997,null,null,null,null,0.997,null,0.98299999999999998,null,0.98299999999999998,null,null,null,null,null,0.98299999999999998,0.98299999999999998,null,null,0.98299999999999998]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,105.30000305175781,null,105.30000305175781,null,105.30000305175781,null,105.30000305175781,null,null,null,null,105.30000305175781,null,115.90000152587891,null,115.90000152587891,null,null,null,null,null,115.90000152587891,115.90000152587891,null,null,115.90000152587891]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,51.799999237060547,null,51.599998474121094,null,51.099998474121094,null,51,null,null,null,null,51.299999237060547,null,33.799999237060547,null,33.599998474121094,null,null,null,null,null,33.5,33.5,null,null,33.599998474121094]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,2.6,null,2.6,null,2.6,null,2.6,null,null,null,null,2.6,null,1.7,null,1.7,null,null,null,null,null,1.7,1.7,null,null,1.7]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,"9.5",null,"9.5",null,"9.5",null,"9.5",null,null,null,null,"9.5",null,"9.5",null,"9.5",null,null,null,null,null,"9.5","9.5",null,null,"9.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"T083","index":248,"n_rows":48,"n_cols":35,"rows_kept":48,"cut":false,"hidden":false,"merged":[[0,2,0,40],[2,1,2,5],[2,8,4,20],[2,23,3,24],[2,26,4,37],[6,1,8,5],[6,8,6,36],[8,8,9,36],[11,8,11,36],[13,3,14,11],[13,14,13,26],[16,17,17,31],[17,3,18,11],[17,14,18,15],[21,4,22,8],[21,9,21,21],[21,22,21,34],[22,9,22,10],[22,11,22,12],[22,13,22,14],[22,15,22,19],[22,20,22,21],[22,22,22,23],[22,24,22,29],[22,31,22,33],[23,4,23,8],[23,9,23,10],[23,11,23,12],[23,13,23,14],[23,15,23,19],[23,20,23,21],[23,22,23,23],[23,24,23,29],[23,31,23,33],[24,4,24,8],[24,9,24,10],[24,11,24,12],[24,13,24,14],[24,15,24,19],[24,20,24,21],[24,22,24,23],[24,24,24,29],[24,31,24,33],[25,4,25,8],[25,9,25,10],[25,11,25,12],[25,13,25,14],[25,15,25,19],[25,20,25,21],[25,22,25,23],[25,24,25,29],[25,31,25,33],[26,4,26,8],[26,9,26,10],[26,11,26,12],[26,13,26,14],[26,15,26,19],[26,20,26,21],[26,22,26,23],[26,24,26,29],[26,31,26,33],[27,4,27,8],[27,9,27,10],[27,11,27,12],[27,13,27,14],[27,15,27,19],[27,20,27,21],[27,22,27,23],[27,24,27,29],[27,31,27,33],[28,4,28,8],[28,9,28,10],[28,11,28,12],[28,13,28,14],[28,15,28,19],[28,20,28,21],[28,22,28,23],[28,24,28,29],[28,31,28,33],[29,4,29,8],[29,9,29,10],[29,11,29,12],[29,13,29,14],[29,15,29,19],[29,20,29,21],[29,22,29,23],[29,24,29,29],[29,31,29,33],[30,4,30,8],[30,9,30,10],[30,11,30,12],[30,13,30,14],[30,15,30,19],[30,20,30,21],[30,22,30,23],[30,24,30,29],[30,31,30,33],[31,4,31,8],[31,9,31,10],[31,11,31,12],[31,13,31,14],[31,15,31,19],[31,20,31,21],[31,22,31,23],[31,24,31,29],[31,31,31,33],[32,4,32,8],[32,9,32,10],[32,11,32,12],[32,13,32,14],[32,15,32,19],[32,20,32,21],[32,22,32,23],[32,24,32,29],[32,31,32,33],[33,4,33,8],[33,9,33,10],[33,11,33,12],[33,13,33,14],[33,15,33,19],[33,20,33,21],[33,22,33,23],[33,24,33,29],[33,31,33,33],[34,4,34,8],[34,9,34,10],[34,11,34,12],[34,13,34,14],[34,15,34,19],[34,20,34,21],[34,22,34,23],[34,24,34,29],[34,31,34,33],[35,4,35,8],[35,9,35,10],[35,11,35,12],[35,13,35,14],[35,15,35,19],[35,20,35,21],[35,22,35,23],[35,24,35,29],[35,31,35,33],[36,4,36,8],[36,9,36,10],[36,11,36,12],[36,13,36,14],[36,15,36,19],[36,20,36,21],[36,22,36,23],[36,24,36,29],[36,31,36,33],[37,4,37,8],[37,9,37,10],[37,11,37,12],[37,13,37,14],[37,15,37,19],[37,20,37,21],[37,22,37,23],[37,24,37,29],[37,31,37,33],[39,31,39,33],[38,4,38,8],[38,9,38,10],[38,11,38,12],[38,13,38,14],[38,15,38,19],[38,20,38,21],[38,22,38,23],[38,24,38,29],[38,31,38,33],[40,4,40,8],[40,9,40,10],[40,11,40,12],[40,13,40,14],[40,15,40,19],[39,22,39,23],[39,24,39,29],[39,4,39,8],[39,9,39,10],[39,11,39,12],[39,13,39,14],[39,15,39,19],[39,20,39,21],[40,22,40,23],[40,24,40,29],[40,31,40,33],[42,20,42,21],[42,22,42,23],[40,20,40,21],[42,9,42,10],[42,11,42,12],[42,13,42,14],[42,15,42,19],[41,9,41,10],[41,11,41,12],[41,13,41,14],[41,15,41,19],[43,31,43,33],[41,20,41,21],[43,22,43,23],[43,24,43,29],[41,22,41,23],[41,24,41,29],[47,2,47,38],[42,24,42,29],[42,31,42,33],[43,4,43,8],[43,9,43,10],[43,11,43,12],[43,13,43,14],[43,15,43,19],[43,20,43,21],[42,4,42,8],[41,31,41,33],[41,4,41,8]]}
[null,null,"Bulk Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,"T083 - Roma 33kV BSP (132/33kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T194 - Columboola TCP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,"Region is South West"]
[]
[null,null,null,null,null,null,null,null,"Transformer size is 1xROMA 132/33/11KV TRANSF 6"]
[]
[]
[null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,"25.5 MVA on 19/02/2019 at 18:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,97.800003051757813,null,97.800003051757813,null,97.800003051757813,null,97.800003051757813,null,null,null,null,97.800003051757813,null,115.19999694824219,null,115.19999694824219,null,null,null,null,null,115.19999694824219,115.19999694824219,null,null,115.19999694824219]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,31.399999618530273,null,31.100000381469727,null,30.700000762939453,null,30.5,null,null,null,null,30.600000381469727,null,22.600000381469727,null,22.399999618530273,null,null,null,null,null,22.299999237060547,22.200000762939453,null,null,22.200000762939453]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,0.97799999999999998,null,0.97799999999999998,null,0.97799999999999998,null,0.97799999999999998,null,null,null,null,0.97799999999999998,null,0.998,null,0.998,null,null,null,null,null,0.998,0.998,null,null,0.998]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,27.899999618530273,null,27.700000762939453,null,27.299999237060547,null,27.200000762939453,null,null,null,null,27.200000762939453,null,21,null,20.799999237060547,null,null,null,null,null,20.700000762939453,20.600000381469727,null,null,20.600000381469727]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,1.4,null,1.4,null,1.4,null,1.4,null,null,null,null,1.4,null,1.1000000000000001,null,1,null,null,null,null,null,1,1,null,null,1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,"72",null,"72",null,"72",null,"72",null,null,null,null,"72",null,"72",null,"72",null,null,null,null,null,"72","72",null,null,"72"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,27.9,null,27.7,null,27.3,null,27.2,null,null,null,null,27.2,null,21,null,20.8,null,null,null,null,null,20.7,20.6,null,null,20.6]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,50,null,50,null,50,null,50,null,null,null,null,50,null,50,null,50,null,null,null,null,null,50,50,null,null,50]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"T0831","index":249,"n_rows":48,"n_cols":35,"rows_kept":48,"cut":false,"hidden":false,"merged":[[0,2,0,40],[2,1,2,5],[2,8,4,20],[2,23,3,24],[2,26,4,37],[6,1,8,5],[6,8,6,36],[8,8,9,36],[11,8,11,36],[13,3,14,11],[13,14,13,26],[16,17,17,31],[17,3,18,11],[17,14,18,15],[21,4,22,8],[21,9,21,21],[21,22,21,34],[22,9,22,10],[22,11,22,12],[22,13,22,14],[22,15,22,19],[22,20,22,21],[22,22,22,23],[22,24,22,29],[22,31,22,33],[23,4,23,8],[23,9,23,10],[23,11,23,12],[23,13,23,14],[23,15,23,19],[23,20,23,21],[23,22,23,23],[23,24,23,29],[23,31,23,33],[24,4,24,8],[24,9,24,10],[24,11,24,12],[24,13,24,14],[24,15,24,19],[24,20,24,21],[24,22,24,23],[24,24,24,29],[24,31,24,33],[25,4,25,8],[25,9,25,10],[25,11,25,12],[25,13,25,14],[25,15,25,19],[25,20,25,21],[25,22,25,23],[25,24,25,29],[25,31,25,33],[26,4,26,8],[26,9,26,10],[26,11,26,12],[26,13,26,14],[26,15,26,19],[26,20,26,21],[26,22,26,23],[26,24,26,29],[26,31,26,33],[27,4,27,8],[27,9,27,10],[27,11,27,12],[27,13,27,14],[27,15,27,19],[27,20,27,21],[27,22,27,23],[27,24,27,29],[27,31,27,33],[28,4,28,8],[28,9,28,10],[28,11,28,12],[28,13,28,14],[28,15,28,19],[28,20,28,21],[28,22,28,23],[28,24,28,29],[28,31,28,33],[29,4,29,8],[29,9,29,10],[29,11,29,12],[29,13,29,14],[29,15,29,19],[29,20,29,21],[29,22,29,23],[29,24,29,29],[29,31,29,33],[30,4,30,8],[30,9,30,10],[30,11,30,12],[30,13,30,14],[30,15,30,19],[30,20,30,21],[30,22,30,23],[30,24,30,29],[30,31,30,33],[31,4,31,8],[31,9,31,10],[31,11,31,12],[31,13,31,14],[31,15,31,19],[31,20,31,21],[31,22,31,23],[31,24,31,29],[31,31,31,33],[32,4,32,8],[32,9,32,10],[32,11,32,12],[32,13,32,14],[32,15,32,19],[32,20,32,21],[32,22,32,23],[32,24,32,29],[32,31,32,33],[33,4,33,8],[33,9,33,10],[33,11,33,12],[33,13,33,14],[33,15,33,19],[33,20,33,21],[33,22,33,23],[33,24,33,29],[33,31,33,33],[34,4,34,8],[34,9,34,10],[34,11,34,12],[34,13,34,14],[34,15,34,19],[34,20,34,21],[34,22,34,23],[34,24,34,29],[34,31,34,33],[35,4,35,8],[35,9,35,10],[35,11,35,12],[35,13,35,14],[35,15,35,19],[35,20,35,21],[35,22,35,23],[35,24,35,29],[35,31,35,33],[36,4,36,8],[36,9,36,10],[36,11,36,12],[36,13,36,14],[36,15,36,19],[36,20,36,21],[36,22,36,23],[36,24,36,29],[36,31,36,33],[37,4,37,8],[37,9,37,10],[37,11,37,12],[37,13,37,14],[37,15,37,19],[37,20,37,21],[37,22,37,23],[37,24,37,29],[37,31,37,33],[39,31,39,33],[38,4,38,8],[38,9,38,10],[38,11,38,12],[38,13,38,14],[38,15,38,19],[38,20,38,21],[38,22,38,23],[38,24,38,29],[38,31,38,33],[40,4,40,8],[40,9,40,10],[40,11,40,12],[40,13,40,14],[40,15,40,19],[39,22,39,23],[39,24,39,29],[39,4,39,8],[39,9,39,10],[39,11,39,12],[39,13,39,14],[39,15,39,19],[39,20,39,21],[40,22,40,23],[40,24,40,29],[40,31,40,33],[42,20,42,21],[42,22,42,23],[40,20,40,21],[42,9,42,10],[42,11,42,12],[42,13,42,14],[42,15,42,19],[41,9,41,10],[41,11,41,12],[41,13,41,14],[41,15,41,19],[43,31,43,33],[41,20,41,21],[43,22,43,23],[43,24,43,29],[41,22,41,23],[41,24,41,29],[47,2,47,38],[42,24,42,29],[42,31,42,33],[43,4,43,8],[43,9,43,10],[43,11,43,12],[43,13,43,14],[43,15,43,19],[43,20,43,21],[42,4,42,8],[41,31,41,33],[41,4,41,8]]}
[null,null,"Bulk Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,"T083 - Roma 66kV BSP (132/66kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T194 - Columboola TCP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,"Region is South West"]
[]
[null,null,null,null,null,null,null,null,"Transformer size is 1x132/66/11kV 60/80MVA ONAN/ODAF"]
[]
[]
[null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,"32.6 MVA on 24/01/2019 at 18:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,101.40000152587891,null,101.40000152587891,null,101.40000152587891,null,101.40000152587891,null,null,null,null,101.40000152587891,null,119.59999847412109,null,119.59999847412109,null,null,null,null,null,119.59999847412109,119.59999847412109,null,null,119.59999847412109]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,38,null,37.799999237060547,null,37.299999237060547,null,37.299999237060547,null,null,null,null,37.400001525878906,null,28.600000381469727,null,28.5,null,null,null,null,null,28.399999618530273,28.299999237060547,null,null,28.399999618530273]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,0.97599999999999998,null,0.97599999999999998,null,0.97599999999999998,null,0.97599999999999998,null,null,null,null,0.97599999999999998,null,0.96199999999999997,null,0.96199999999999997,null,null,null,null,null,0.96199999999999997,0.96199999999999997,null,null,0.96199999999999997]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,34.099998474121094,null,33.900001525878906,null,33.5,null,33.5,null,null,null,null,33.599998474121094,null,26.299999237060547,null,26.200000762939453,null,null,null,null,null,26.100000381469727,26,null,null,26.100000381469727]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,1.7,null,1.7,null,1.7,null,1.7,null,null,null,null,1.7,null,1.3,null,1.3,null,null,null,null,null,1.3,1.3,null,null,1.3]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,"82",null,"82",null,"82",null,"82",null,null,null,null,"82",null,"82",null,"82",null,null,null,null,null,"82","82",null,null,"82"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,34.1,null,33.9,null,33.5,null,33.5,null,null,null,null,33.6,null,26.3,null,26.2,null,null,null,null,null,26.1,26,null,null,26.1]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,50,null,50,null,50,null,50,null,null,null,null,50,null,50,null,50,null,null,null,null,null,50,50,null,null,50]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"T095","index":250,"n_rows":48,"n_cols":35,"rows_kept":48,"cut":false,"hidden":false,"merged":[[0,2,0,40],[2,1,2,5],[2,8,4,20],[2,23,3,24],[2,26,4,37],[6,1,8,5],[6,8,6,36],[8,8,9,36],[11,8,11,36],[13,3,14,11],[13,14,13,26],[16,17,17,31],[17,3,18,11],[17,14,18,15],[21,4,22,8],[21,9,21,21],[21,22,21,34],[22,9,22,10],[22,11,22,12],[22,13,22,14],[22,15,22,19],[22,20,22,21],[22,22,22,23],[22,24,22,29],[22,31,22,33],[23,4,23,8],[23,9,23,10],[23,11,23,12],[23,13,23,14],[23,15,23,19],[23,20,23,21],[23,22,23,23],[23,24,23,29],[23,31,23,33],[24,4,24,8],[24,9,24,10],[24,11,24,12],[24,13,24,14],[24,15,24,19],[24,20,24,21],[24,22,24,23],[24,24,24,29],[24,31,24,33],[25,4,25,8],[25,9,25,10],[25,11,25,12],[25,13,25,14],[25,15,25,19],[25,20,25,21],[25,22,25,23],[25,24,25,29],[25,31,25,33],[26,4,26,8],[26,9,26,10],[26,11,26,12],[26,13,26,14],[26,15,26,19],[26,20,26,21],[26,22,26,23],[26,24,26,29],[26,31,26,33],[27,4,27,8],[27,9,27,10],[27,11,27,12],[27,13,27,14],[27,15,27,19],[27,20,27,21],[27,22,27,23],[27,24,27,29],[27,31,27,33],[28,4,28,8],[28,9,28,10],[28,11,28,12],[28,13,28,14],[28,15,28,19],[28,20,28,21],[28,22,28,23],[28,24,28,29],[28,31,28,33],[29,4,29,8],[29,9,29,10],[29,11,29,12],[29,13,29,14],[29,15,29,19],[29,20,29,21],[29,22,29,23],[29,24,29,29],[29,31,29,33],[30,4,30,8],[30,9,30,10],[30,11,30,12],[30,13,30,14],[30,15,30,19],[30,20,30,21],[30,22,30,23],[30,24,30,29],[30,31,30,33],[31,4,31,8],[31,9,31,10],[31,11,31,12],[31,13,31,14],[31,15,31,19],[31,20,31,21],[31,22,31,23],[31,24,31,29],[31,31,31,33],[32,4,32,8],[32,9,32,10],[32,11,32,12],[32,13,32,14],[32,15,32,19],[32,20,32,21],[32,22,32,23],[32,24,32,29],[32,31,32,33],[33,4,33,8],[33,9,33,10],[33,11,33,12],[33,13,33,14],[33,15,33,19],[33,20,33,21],[33,22,33,23],[33,24,33,29],[33,31,33,33],[34,4,34,8],[34,9,34,10],[34,11,34,12],[34,13,34,14],[34,15,34,19],[34,20,34,21],[34,22,34,23],[34,24,34,29],[34,31,34,33],[35,4,35,8],[35,9,35,10],[35,11,35,12],[35,13,35,14],[35,15,35,19],[35,20,35,21],[35,22,35,23],[35,24,35,29],[35,31,35,33],[36,4,36,8],[36,9,36,10],[36,11,36,12],[36,13,36,14],[36,15,36,19],[36,20,36,21],[36,22,36,23],[36,24,36,29],[36,31,36,33],[37,4,37,8],[37,9,37,10],[37,11,37,12],[37,13,37,14],[37,15,37,19],[37,20,37,21],[37,22,37,23],[37,24,37,29],[37,31,37,33],[39,31,39,33],[38,4,38,8],[38,9,38,10],[38,11,38,12],[38,13,38,14],[38,15,38,19],[38,20,38,21],[38,22,38,23],[38,24,38,29],[38,31,38,33],[40,4,40,8],[40,9,40,10],[40,11,40,12],[40,13,40,14],[40,15,40,19],[39,22,39,23],[39,24,39,29],[39,4,39,8],[39,9,39,10],[39,11,39,12],[39,13,39,14],[39,15,39,19],[39,20,39,21],[40,22,40,23],[40,24,40,29],[40,31,40,33],[42,20,42,21],[42,22,42,23],[40,20,40,21],[42,9,42,10],[42,11,42,12],[42,13,42,14],[42,15,42,19],[41,9,41,10],[41,11,41,12],[41,13,41,14],[41,15,41,19],[43,31,43,33],[41,20,41,21],[43,22,43,23],[43,24,43,29],[41,22,41,23],[41,24,41,29],[47,2,47,38],[42,24,42,29],[42,31,42,33],[43,4,43,8],[43,9,43,10],[43,11,43,12],[43,13,43,14],[43,15,43,19],[43,20,43,21],[42,4,42,8],[41,31,41,33],[41,4,41,8]]}
[null,null,"Bulk Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,"T095 - Millchester BSP (132/66kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"QROS - Ross (Kidston and Milchester) TCP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,"Region is Nth Queensland"]
[]
[null,null,null,null,null,null,null,null,"Transformer size is 1x132/66/11kV 25/34/40MVA ONAN/ONAF/ODAF;1x132/66kV 20/27MVA ON/OB"]
[]
[]
[null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 10.0 MVA"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,"32.8 MVA on 22/01/2019 at 19:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,68,null,68,null,68,null,68,null,null,null,null,68,null,68,null,68,null,null,null,null,null,68,68,null,null,68]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,36.200000762939453,null,41.900001525878906,null,43,null,42.799999237060547,null,null,null,null,42.900001525878906,null,23.899999618530273,null,28.899999618530273,null,null,null,null,null,30.200000762939453,30.100000381469727,null,null,30]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,1,null,0.998,null,0.997,null,0.997,null,null,null,null,0.997,null,0.999,null,0.999,null,null,null,null,null,0.999,0.999,null,null,0.999]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,37.400001525878906,null,37.400001525878906,null,37.400001525878906,null,37.400001525878906,null,null,null,null,37.400001525878906,null,37.400001525878906,null,37.400001525878906,null,null,null,null,null,37.400001525878906,37.400001525878906,null,null,37.400001525878906]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,33.799999237060547,null,39.400001525878906,null,40.599998474121094,null,40.400001525878906,null,null,null,null,40.5,null,22.899999618530273,null,27.899999618530273,null,null,null,null,null,29.200000762939453,29.100000381469727,null,null,29.100000381469727]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,1.7,null,2,null,2,null,2,null,null,null,null,2,null,1.1000000000000001,null,1.4,null,null,null,null,null,1.5,1.5,null,null,1.5]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,"21",null,"21",null,"21",null,"21",null,null,null,null,"21",null,"21",null,"21",null,null,null,null,null,"21","21",null,null,"21"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,null,2,null,3.2,null,3,null,null,null,null,3.1]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,19.100000381469727,null,19.100000381469727,null,19.100000381469727,null,19.100000381469727,null,null,null,null,19.100000381469727,null,19.100000381469727,null,19.100000381469727,null,null,null,null,null,19.100000381469727,19.100000381469727,null,null,19.100000381469727]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,7.9000000953674316,null,7.9000000953674316,null,7.9000000953674316,null,7.9000000953674316,null,null,null,null,7.9000000953674316,null,7.9000000953674316,null,7.9000000953674316,null,null,null,null,null,7.9000000953674316,7.9000000953674316,null,null,7.9000000953674316]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"T116","index":251,"n_rows":48,"n_cols":35,"rows_kept":48,"cut":false,"hidden":false,"merged":[[0,2,0,40],[2,1,2,5],[2,8,4,20],[2,23,3,24],[2,26,4,37],[6,1,8,5],[6,8,6,36],[8,8,9,36],[11,8,11,36],[13,3,14,11],[13,14,13,26],[16,17,17,31],[17,3,18,11],[17,14,18,15],[21,4,22,8],[21,9,21,21],[21,22,21,34],[22,9,22,10],[22,11,22,12],[22,13,22,14],[22,15,22,19],[22,20,22,21],[22,22,22,23],[22,24,22,29],[22,31,22,33],[23,4,23,8],[23,9,23,10],[23,11,23,12],[23,13,23,14],[23,15,23,19],[23,20,23,21],[23,22,23,23],[23,24,23,29],[23,31,23,33],[24,4,24,8],[24,9,24,10],[24,11,24,12],[24,13,24,14],[24,15,24,19],[24,20,24,21],[24,22,24,23],[24,24,24,29],[24,31,24,33],[25,4,25,8],[25,9,25,10],[25,11,25,12],[25,13,25,14],[25,15,25,19],[25,20,25,21],[25,22,25,23],[25,24,25,29],[25,31,25,33],[26,4,26,8],[26,9,26,10],[26,11,26,12],[26,13,26,14],[26,15,26,19],[26,20,26,21],[26,22,26,23],[26,24,26,29],[26,31,26,33],[27,4,27,8],[27,9,27,10],[27,11,27,12],[27,13,27,14],[27,15,27,19],[27,20,27,21],[27,22,27,23],[27,24,27,29],[27,31,27,33],[28,4,28,8],[28,9,28,10],[28,11,28,12],[28,13,28,14],[28,15,28,19],[28,20,28,21],[28,22,28,23],[28,24,28,29],[28,31,28,33],[29,4,29,8],[29,9,29,10],[29,11,29,12],[29,13,29,14],[29,15,29,19],[29,20,29,21],[29,22,29,23],[29,24,29,29],[29,31,29,33],[30,4,30,8],[30,9,30,10],[30,11,30,12],[30,13,30,14],[30,15,30,19],[30,20,30,21],[30,22,30,23],[30,24,30,29],[30,31,30,33],[31,4,31,8],[31,9,31,10],[31,11,31,12],[31,13,31,14],[31,15,31,19],[31,20,31,21],[31,22,31,23],[31,24,31,29],[31,31,31,33],[32,4,32,8],[32,9,32,10],[32,11,32,12],[32,13,32,14],[32,15,32,19],[32,20,32,21],[32,22,32,23],[32,24,32,29],[32,31,32,33],[33,4,33,8],[33,9,33,10],[33,11,33,12],[33,13,33,14],[33,15,33,19],[33,20,33,21],[33,22,33,23],[33,24,33,29],[33,31,33,33],[34,4,34,8],[34,9,34,10],[34,11,34,12],[34,13,34,14],[34,15,34,19],[34,20,34,21],[34,22,34,23],[34,24,34,29],[34,31,34,33],[35,4,35,8],[35,9,35,10],[35,11,35,12],[35,13,35,14],[35,15,35,19],[35,20,35,21],[35,22,35,23],[35,24,35,29],[35,31,35,33],[36,4,36,8],[36,9,36,10],[36,11,36,12],[36,13,36,14],[36,15,36,19],[36,20,36,21],[36,22,36,23],[36,24,36,29],[36,31,36,33],[37,4,37,8],[37,9,37,10],[37,11,37,12],[37,13,37,14],[37,15,37,19],[37,20,37,21],[37,22,37,23],[37,24,37,29],[37,31,37,33],[39,31,39,33],[38,4,38,8],[38,9,38,10],[38,11,38,12],[38,13,38,14],[38,15,38,19],[38,20,38,21],[38,22,38,23],[38,24,38,29],[38,31,38,33],[40,4,40,8],[40,9,40,10],[40,11,40,12],[40,13,40,14],[40,15,40,19],[39,22,39,23],[39,24,39,29],[39,4,39,8],[39,9,39,10],[39,11,39,12],[39,13,39,14],[39,15,39,19],[39,20,39,21],[40,22,40,23],[40,24,40,29],[40,31,40,33],[42,20,42,21],[42,22,42,23],[40,20,40,21],[42,9,42,10],[42,11,42,12],[42,13,42,14],[42,15,42,19],[41,9,41,10],[41,11,41,12],[41,13,41,14],[41,15,41,19],[43,31,43,33],[41,20,41,21],[43,22,43,23],[43,24,43,29],[41,22,41,23],[41,24,41,29],[47,2,47,38],[42,24,42,29],[42,31,42,33],[43,4,43,8],[43,9,43,10],[43,11,43,12],[43,13,43,14],[43,15,43,19],[43,20,43,21],[42,4,42,8],[41,31,41,33],[41,4,41,8]]}
[null,null,"Bulk Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,"T116 - Torrington BSP (110/33kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"QMRG - Middle Ridge (Ergon) TCP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,"Region is South West"]
[]
[null,null,null,null,null,null,null,null,"Transformer size is 2x110/33/11kV 64/80/106MVA ONAN/ODAN/ODAF"]
[]
[]
[null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,"88.8 MVA on 13/02/2019 at 18:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,239,null,239,null,239,null,239,null,null,null,null,239,null,286.20001220703125,null,286.20001220703125,null,null,null,null,null,286.20001220703125,286.20001220703125,null,null,286.20001220703125]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,95.199996948242188,null,96.900001525878906,null,95.699996948242188,null,95.300003051757813,null,null,null,null,95.699996948242188,null,94.199996948242188,null,96,null,null,null,null,null,97.800003051757813,97.5,null,null,97.300003051757813]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,0.99399999999999999,null,0.99299999999999999,null,0.99399999999999999,null,0.99399999999999999,null,null,null,null,0.99399999999999999,null,0.999,null,0.999,null,null,null,null,null,0.999,0.999,null,null,0.999]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,132.30000305175781,null,132.30000305175781,null,132.30000305175781,null,132.30000305175781,null,null,null,null,132.30000305175781,null,157.10000610351563,null,157.10000610351563,null,null,null,null,null,157.10000610351563,157.10000610351563,null,null,157.10000610351563]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,85.599998474121094,null,87.400001525878906,null,86.400001525878906,null,86,null,null,null,null,86.300003051757813,null,87.599998474121094,null,89.5,null,null,null,null,null,91.300003051757813,91,null,null,90.800003051757813]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,4.3,null,4.4000000000000004,null,4.3,null,4.3,null,null,null,null,4.3,null,4.4000000000000004,null,4.5,null,null,null,null,null,4.5999999999999996,4.5999999999999996,null,null,4.5]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,"23",null,"23",null,"23",null,"23",null,null,null,null,"23",null,"23",null,"23",null,null,null,null,null,"23","23",null,null,"23"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"T130","index":252,"n_rows":48,"n_cols":35,"rows_kept":48,"cut":false,"hidden":false,"merged":[[0,2,0,40],[2,1,2,5],[2,8,4,20],[2,23,3,24],[2,26,4,37],[6,1,8,5],[6,8,6,36],[8,8,9,36],[11,8,11,36],[13,3,14,11],[13,14,13,26],[16,17,17,31],[17,3,18,11],[17,14,18,15],[21,4,22,8],[21,9,21,21],[21,22,21,34],[22,9,22,10],[22,11,22,12],[22,13,22,14],[22,15,22,19],[22,20,22,21],[22,22,22,23],[22,24,22,29],[22,31,22,33],[23,4,23,8],[23,9,23,10],[23,11,23,12],[23,13,23,14],[23,15,23,19],[23,20,23,21],[23,22,23,23],[23,24,23,29],[23,31,23,33],[24,4,24,8],[24,9,24,10],[24,11,24,12],[24,13,24,14],[24,15,24,19],[24,20,24,21],[24,22,24,23],[24,24,24,29],[24,31,24,33],[25,4,25,8],[25,9,25,10],[25,11,25,12],[25,13,25,14],[25,15,25,19],[25,20,25,21],[25,22,25,23],[25,24,25,29],[25,31,25,33],[26,4,26,8],[26,9,26,10],[26,11,26,12],[26,13,26,14],[26,15,26,19],[26,20,26,21],[26,22,26,23],[26,24,26,29],[26,31,26,33],[27,4,27,8],[27,9,27,10],[27,11,27,12],[27,13,27,14],[27,15,27,19],[27,20,27,21],[27,22,27,23],[27,24,27,29],[27,31,27,33],[28,4,28,8],[28,9,28,10],[28,11,28,12],[28,13,28,14],[28,15,28,19],[28,20,28,21],[28,22,28,23],[28,24,28,29],[28,31,28,33],[29,4,29,8],[29,9,29,10],[29,11,29,12],[29,13,29,14],[29,15,29,19],[29,20,29,21],[29,22,29,23],[29,24,29,29],[29,31,29,33],[30,4,30,8],[30,9,30,10],[30,11,30,12],[30,13,30,14],[30,15,30,19],[30,20,30,21],[30,22,30,23],[30,24,30,29],[30,31,30,33],[31,4,31,8],[31,9,31,10],[31,11,31,12],[31,13,31,14],[31,15,31,19],[31,20,31,21],[31,22,31,23],[31,24,31,29],[31,31,31,33],[32,4,32,8],[32,9,32,10],[32,11,32,12],[32,13,32,14],[32,15,32,19],[32,20,32,21],[32,22,32,23],[32,24,32,29],[32,31,32,33],[33,4,33,8],[33,9,33,10],[33,11,33,12],[33,13,33,14],[33,15,33,19],[33,20,33,21],[33,22,33,23],[33,24,33,29],[33,31,33,33],[34,4,34,8],[34,9,34,10],[34,11,34,12],[34,13,34,14],[34,15,34,19],[34,20,34,21],[34,22,34,23],[34,24,34,29],[34,31,34,33],[35,4,35,8],[35,9,35,10],[35,11,35,12],[35,13,35,14],[35,15,35,19],[35,20,35,21],[35,22,35,23],[35,24,35,29],[35,31,35,33],[36,4,36,8],[36,9,36,10],[36,11,36,12],[36,13,36,14],[36,15,36,19],[36,20,36,21],[36,22,36,23],[36,24,36,29],[36,31,36,33],[37,4,37,8],[37,9,37,10],[37,11,37,12],[37,13,37,14],[37,15,37,19],[37,20,37,21],[37,22,37,23],[37,24,37,29],[37,31,37,33],[39,31,39,33],[38,4,38,8],[38,9,38,10],[38,11,38,12],[38,13,38,14],[38,15,38,19],[38,20,38,21],[38,22,38,23],[38,24,38,29],[38,31,38,33],[40,4,40,8],[40,9,40,10],[40,11,40,12],[40,13,40,14],[40,15,40,19],[39,22,39,23],[39,24,39,29],[39,4,39,8],[39,9,39,10],[39,11,39,12],[39,13,39,14],[39,15,39,19],[39,20,39,21],[40,22,40,23],[40,24,40,29],[40,31,40,33],[42,20,42,21],[42,22,42,23],[40,20,40,21],[42,9,42,10],[42,11,42,12],[42,13,42,14],[42,15,42,19],[41,9,41,10],[41,11,41,12],[41,13,41,14],[41,15,41,19],[43,31,43,33],[41,20,41,21],[43,22,43,23],[43,24,43,29],[41,22,41,23],[41,24,41,29],[47,2,47,38],[42,24,42,29],[42,31,42,33],[43,4,43,8],[43,9,43,10],[43,11,43,12],[43,13,43,14],[43,15,43,19],[43,20,43,21],[42,4,42,8],[41,31,41,33],[41,4,41,8]]}
[null,null,"Bulk Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,"T130 - Boat Creek BSP (132/66kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"QYAE - Boat Creek TCP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,"Region is Capricornia"]
[]
[null,null,null,null,null,null,null,null,"Transformer size is 2x132/66/11kV 60/80MVA ONAN/ODAN"]
[]
[]
[null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,"45.7 MVA on 20/08/2018 at 23:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,151.19999694824219,null,151.19999694824219,null,151.19999694824219,null,151.19999694824219,null,null,null,null,151.19999694824219,null,162,null,162,null,null,null,null,null,162,162,null,null,162]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,47.5,null,47.299999237060547,null,46.799999237060547,null,46.900001525878906,null,null,null,null,47.099998474121094,null,44.5,null,44.400001525878906,null,null,null,null,null,44.299999237060547,44.200000762939453,null,null,44.400001525878906]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,0.93300000000000005,null,0.93300000000000005,null,0.93300000000000005,null,0.93300000000000005,null,null,null,null,0.93300000000000005,null,0.95599999999999996,null,0.95599999999999996,null,null,null,null,null,0.95599999999999996,0.95599999999999996,null,null,0.95599999999999996]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,90.900001525878906,null,90.900001525878906,null,90.900001525878906,null,90.900001525878906,null,null,null,null,90.900001525878906,null,95.699996948242188,null,95.699996948242188,null,null,null,null,null,95.699996948242188,95.699996948242188,null,null,95.699996948242188]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,46.400001525878906,null,46.099998474121094,null,45.700000762939453,null,45.700000762939453,null,null,null,null,46,null,44.299999237060547,null,44.200000762939453,null,null,null,null,null,44.099998474121094,44.099998474121094,null,null,44.200000762939453]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,2.2999999999999998,null,2.2999999999999998,null,2.2999999999999998,null,2.2999999999999998,null,null,null,null,2.2999999999999998,null,2.2000000000000002,null,2.2000000000000002,null,null,null,null,null,2.2000000000000002,2.2000000000000002,null,null,2.2000000000000002]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,"203",null,"203",null,"203",null,"203",null,null,null,null,"203",null,"203",null,"203",null,null,null,null,null,"203","203",null,null,"203"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"T131","index":253,"n_rows":48,"n_cols":35,"rows_kept":48,"cut":false,"hidden":false,"merged":[[0,2,0,40],[2,1,2,5],[2,8,4,20],[2,23,3,24],[2,26,4,37],[6,1,8,5],[6,8,6,36],[8,8,9,36],[11,8,11,36],[13,3,14,11],[13,14,13,26],[16,17,17,31],[17,3,18,11],[17,14,18,15],[21,4,22,8],[21,9,21,21],[21,22,21,34],[22,9,22,10],[22,11,22,12],[22,13,22,14],[22,15,22,19],[22,20,22,21],[22,22,22,23],[22,24,22,29],[22,31,22,33],[23,4,23,8],[23,9,23,10],[23,11,23,12],[23,13,23,14],[23,15,23,19],[23,20,23,21],[23,22,23,23],[23,24,23,29],[23,31,23,33],[24,4,24,8],[24,9,24,10],[24,11,24,12],[24,13,24,14],[24,15,24,19],[24,20,24,21],[24,22,24,23],[24,24,24,29],[24,31,24,33],[25,4,25,8],[25,9,25,10],[25,11,25,12],[25,13,25,14],[25,15,25,19],[25,20,25,21],[25,22,25,23],[25,24,25,29],[25,31,25,33],[26,4,26,8],[26,9,26,10],[26,11,26,12],[26,13,26,14],[26,15,26,19],[26,20,26,21],[26,22,26,23],[26,24,26,29],[26,31,26,33],[27,4,27,8],[27,9,27,10],[27,11,27,12],[27,13,27,14],[27,15,27,19],[27,20,27,21],[27,22,27,23],[27,24,27,29],[27,31,27,33],[28,4,28,8],[28,9,28,10],[28,11,28,12],[28,13,28,14],[28,15,28,19],[28,20,28,21],[28,22,28,23],[28,24,28,29],[28,31,28,33],[29,4,29,8],[29,9,29,10],[29,11,29,12],[29,13,29,14],[29,15,29,19],[29,20,29,21],[29,22,29,23],[29,24,29,29],[29,31,29,33],[30,4,30,8],[30,9,30,10],[30,11,30,12],[30,13,30,14],[30,15,30,19],[30,20,30,21],[30,22,30,23],[30,24,30,29],[30,31,30,33],[31,4,31,8],[31,9,31,10],[31,11,31,12],[31,13,31,14],[31,15,31,19],[31,20,31,21],[31,22,31,23],[31,24,31,29],[31,31,31,33],[32,4,32,8],[32,9,32,10],[32,11,32,12],[32,13,32,14],[32,15,32,19],[32,20,32,21],[32,22,32,23],[32,24,32,29],[32,31,32,33],[33,4,33,8],[33,9,33,10],[33,11,33,12],[33,13,33,14],[33,15,33,19],[33,20,33,21],[33,22,33,23],[33,24,33,29],[33,31,33,33],[34,4,34,8],[34,9,34,10],[34,11,34,12],[34,13,34,14],[34,15,34,19],[34,20,34,21],[34,22,34,23],[34,24,34,29],[34,31,34,33],[35,4,35,8],[35,9,35,10],[35,11,35,12],[35,13,35,14],[35,15,35,19],[35,20,35,21],[35,22,35,23],[35,24,35,29],[35,31,35,33],[36,4,36,8],[36,9,36,10],[36,11,36,12],[36,13,36,14],[36,15,36,19],[36,20,36,21],[36,22,36,23],[36,24,36,29],[36,31,36,33],[37,4,37,8],[37,9,37,10],[37,11,37,12],[37,13,37,14],[37,15,37,19],[37,20,37,21],[37,22,37,23],[37,24,37,29],[37,31,37,33],[39,31,39,33],[38,4,38,8],[38,9,38,10],[38,11,38,12],[38,13,38,14],[38,15,38,19],[38,20,38,21],[38,22,38,23],[38,24,38,29],[38,31,38,33],[40,4,40,8],[40,9,40,10],[40,11,40,12],[40,13,40,14],[40,15,40,19],[39,22,39,23],[39,24,39,29],[39,4,39,8],[39,9,39,10],[39,11,39,12],[39,13,39,14],[39,15,39,19],[39,20,39,21],[40,22,40,23],[40,24,40,29],[40,31,40,33],[42,20,42,21],[42,22,42,23],[40,20,40,21],[42,9,42,10],[42,11,42,12],[42,13,42,14],[42,15,42,19],[41,9,41,10],[41,11,41,12],[41,13,41,14],[41,15,41,19],[43,31,43,33],[41,20,41,21],[43,22,43,23],[43,24,43,29],[41,22,41,23],[41,24,41,29],[47,2,47,38],[42,24,42,29],[42,31,42,33],[43,4,43,8],[43,9,43,10],[43,11,43,12],[43,13,43,14],[43,15,43,19],[43,20,43,21],[42,4,42,8],[41,31,41,33],[41,4,41,8]]}
[null,null,"Bulk Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,"T131 - Isis BSP (132/66kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"QTBC - Teebar Creek TCP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,"Region is Wide Bay"]
[]
[null,null,null,null,null,null,null,null,"Transformer size is 1x132/66/11kV 80/100MVA ONAN/ODAN;1x132/66kV 32/40/52MVA ONAN/ODAN/ODAF"]
[]
[]
[null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 91.8 MVA"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,"47.1 MVA on 19/02/2019 at 18:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,134,null,134,null,134,null,134,null,null,null,null,134,null,145,null,145,null,null,null,null,null,145,145,null,null,145]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,6,null,6,null,null,null,null,null,6,6,null,null,6]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,53.599998474121094,null,53.5,null,53.099998474121094,null,53.200000762939453,null,null,null,null,53.5,null,41.700000762939453,null,41.700000762939453,null,null,null,null,null,41.700000762939453,41.799999237060547,null,null,42]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,0.98099999999999998,null,0.98099999999999998,null,0.98099999999999998,null,0.98099999999999998,null,null,null,null,0.98099999999999998,null,0.995,null,0.995,null,null,null,null,null,0.995,0.995,null,null,0.995]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,75.300003051757813,null,75.300003051757813,null,75.300003051757813,null,75.300003051757813,null,null,null,null,75.300003051757813,null,77.800003051757813,null,77.800003051757813,null,null,null,null,null,77.800003051757813,77.800003051757813,null,null,77.800003051757813]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,49.700000762939453,null,49.599998474121094,null,49.200000762939453,null,49.299999237060547,null,null,null,null,49.599998474121094,null,39.200000762939453,null,39.299999237060547,null,null,null,null,null,39.299999237060547,39.299999237060547,null,null,39.5]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,2.5,null,2.5,null,2.5,null,2.5,null,null,null,null,2.5,null,2,null,2,null,null,null,null,null,2,2,null,null,2]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,"11.5",null,"11.5",null,"11.5",null,"11.5",null,null,null,null,"11.5",null,"11.5",null,"11.5",null,null,null,null,null,"11.5","11.5",null,null,"11.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"T159","index":254,"n_rows":48,"n_cols":35,"rows_kept":48,"cut":false,"hidden":false,"merged":[[0,2,0,40],[2,1,2,5],[2,8,4,20],[2,23,3,24],[2,26,4,37],[6,1,8,5],[6,8,6,36],[8,8,9,36],[11,8,11,36],[13,3,14,11],[13,14,13,26],[16,17,17,31],[17,3,18,11],[17,14,18,15],[21,4,22,8],[21,9,21,21],[21,22,21,34],[22,9,22,10],[22,11,22,12],[22,13,22,14],[22,15,22,19],[22,20,22,21],[22,22,22,23],[22,24,22,29],[22,31,22,33],[23,4,23,8],[23,9,23,10],[23,11,23,12],[23,13,23,14],[23,15,23,19],[23,20,23,21],[23,22,23,23],[23,24,23,29],[23,31,23,33],[24,4,24,8],[24,9,24,10],[24,11,24,12],[24,13,24,14],[24,15,24,19],[24,20,24,21],[24,22,24,23],[24,24,24,29],[24,31,24,33],[25,4,25,8],[25,9,25,10],[25,11,25,12],[25,13,25,14],[25,15,25,19],[25,20,25,21],[25,22,25,23],[25,24,25,29],[25,31,25,33],[26,4,26,8],[26,9,26,10],[26,11,26,12],[26,13,26,14],[26,15,26,19],[26,20,26,21],[26,22,26,23],[26,24,26,29],[26,31,26,33],[27,4,27,8],[27,9,27,10],[27,11,27,12],[27,13,27,14],[27,15,27,19],[27,20,27,21],[27,22,27,23],[27,24,27,29],[27,31,27,33],[28,4,28,8],[28,9,28,10],[28,11,28,12],[28,13,28,14],[28,15,28,19],[28,20,28,21],[28,22,28,23],[28,24,28,29],[28,31,28,33],[29,4,29,8],[29,9,29,10],[29,11,29,12],[29,13,29,14],[29,15,29,19],[29,20,29,21],[29,22,29,23],[29,24,29,29],[29,31,29,33],[30,4,30,8],[30,9,30,10],[30,11,30,12],[30,13,30,14],[30,15,30,19],[30,20,30,21],[30,22,30,23],[30,24,30,29],[30,31,30,33],[31,4,31,8],[31,9,31,10],[31,11,31,12],[31,13,31,14],[31,15,31,19],[31,20,31,21],[31,22,31,23],[31,24,31,29],[31,31,31,33],[32,4,32,8],[32,9,32,10],[32,11,32,12],[32,13,32,14],[32,15,32,19],[32,20,32,21],[32,22,32,23],[32,24,32,29],[32,31,32,33],[33,4,33,8],[33,9,33,10],[33,11,33,12],[33,13,33,14],[33,15,33,19],[33,20,33,21],[33,22,33,23],[33,24,33,29],[33,31,33,33],[34,4,34,8],[34,9,34,10],[34,11,34,12],[34,13,34,14],[34,15,34,19],[34,20,34,21],[34,22,34,23],[34,24,34,29],[34,31,34,33],[35,4,35,8],[35,9,35,10],[35,11,35,12],[35,13,35,14],[35,15,35,19],[35,20,35,21],[35,22,35,23],[35,24,35,29],[35,31,35,33],[36,4,36,8],[36,9,36,10],[36,11,36,12],[36,13,36,14],[36,15,36,19],[36,20,36,21],[36,22,36,23],[36,24,36,29],[36,31,36,33],[37,4,37,8],[37,9,37,10],[37,11,37,12],[37,13,37,14],[37,15,37,19],[37,20,37,21],[37,22,37,23],[37,24,37,29],[37,31,37,33],[39,31,39,33],[38,4,38,8],[38,9,38,10],[38,11,38,12],[38,13,38,14],[38,15,38,19],[38,20,38,21],[38,22,38,23],[38,24,38,29],[38,31,38,33],[40,4,40,8],[40,9,40,10],[40,11,40,12],[40,13,40,14],[40,15,40,19],[39,22,39,23],[39,24,39,29],[39,4,39,8],[39,9,39,10],[39,11,39,12],[39,13,39,14],[39,15,39,19],[39,20,39,21],[40,22,40,23],[40,24,40,29],[40,31,40,33],[42,20,42,21],[42,22,42,23],[40,20,40,21],[42,9,42,10],[42,11,42,12],[42,13,42,14],[42,15,42,19],[41,9,41,10],[41,11,41,12],[41,13,41,14],[41,15,41,19],[43,31,43,33],[41,20,41,21],[43,22,43,23],[43,24,43,29],[41,22,41,23],[41,24,41,29],[47,2,47,38],[42,24,42,29],[42,31,42,33],[43,4,43,8],[43,9,43,10],[43,11,43,12],[43,13,43,14],[43,15,43,19],[43,20,43,21],[42,4,42,8],[41,31,41,33],[41,4,41,8]]}
[null,null,"Bulk Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,"T159 - Lakeland BSP (132/66kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"QTUH - Turkinje 132kV TCP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,"Region is Far North"]
[]
[null,null,null,null,null,null,null,null,"Transformer size is 2x132/66/22kV 15/20MVA ONAN/ONAF"]
[]
[]
[null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 10.5 MVA"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,"7.3 MVA on 26/11/2018 at 18:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,49.799999237060547,null,49.799999237060547,null,49.799999237060547,null,49.799999237060547,null,null,null,null,49.799999237060547,null,55.799999237060547,null,55.799999237060547,null,null,null,null,null,55.799999237060547,55.799999237060547,null,null,55.799999237060547]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,7.6999998092651367,null,7.6999998092651367,null,7.5999999046325684,null,7.5999999046325684,null,null,null,null,7.6999998092651367,null,5.8000001907348633,null,5.8000001907348633,null,null,null,null,null,5.8000001907348633,5.8000001907348633,null,null,5.8000001907348633]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,1,null,1,null,1,null,1,null,null,null,null,1,null,0.89900000000000002,null,0.89900000000000002,null,null,null,null,null,0.89900000000000002,0.89900000000000002,null,null,0.89900000000000002]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,29.399999618530273,null,29.399999618530273,null,29.399999618530273,null,29.399999618530273,null,null,null,null,29.399999618530273,null,29.899999618530273,null,29.899999618530273,null,null,null,null,null,29.899999618530273,29.899999618530273,null,null,29.899999618530273]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,7.1999998092651367,null,7.1999998092651367,null,7.0999999046325684,null,7.0999999046325684,null,null,null,null,7.1999998092651367,null,5.4000000953674316,null,5.5,null,null,null,null,null,5.5,5.5,null,null,5.5]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,0.4,null,0.4,null,0.4,null,0.4,null,null,null,null,0.4,null,0.3,null,0.3,null,null,null,null,null,0.3,0.3,null,null,0.3]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,"23.5",null,"23.5",null,"23.5",null,"23.5",null,null,null,null,"23.5",null,"23.5",null,"23.5",null,null,null,null,null,"23.5","23.5",null,null,"23.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"T163","index":255,"n_rows":48,"n_cols":35,"rows_kept":48,"cut":false,"hidden":false,"merged":[[0,2,0,40],[2,1,2,5],[2,8,4,20],[2,23,3,24],[2,26,4,37],[6,1,8,5],[6,8,6,36],[8,8,9,36],[11,8,11,36],[13,3,14,11],[13,14,13,26],[16,17,17,31],[17,3,18,11],[17,14,18,15],[21,4,22,8],[21,9,21,21],[21,22,21,34],[22,9,22,10],[22,11,22,12],[22,13,22,14],[22,15,22,19],[22,20,22,21],[22,22,22,23],[22,24,22,29],[22,31,22,33],[23,4,23,8],[23,9,23,10],[23,11,23,12],[23,13,23,14],[23,15,23,19],[23,20,23,21],[23,22,23,23],[23,24,23,29],[23,31,23,33],[24,4,24,8],[24,9,24,10],[24,11,24,12],[24,13,24,14],[24,15,24,19],[24,20,24,21],[24,22,24,23],[24,24,24,29],[24,31,24,33],[25,4,25,8],[25,9,25,10],[25,11,25,12],[25,13,25,14],[25,15,25,19],[25,20,25,21],[25,22,25,23],[25,24,25,29],[25,31,25,33],[26,4,26,8],[26,9,26,10],[26,11,26,12],[26,13,26,14],[26,15,26,19],[26,20,26,21],[26,22,26,23],[26,24,26,29],[26,31,26,33],[27,4,27,8],[27,9,27,10],[27,11,27,12],[27,13,27,14],[27,15,27,19],[27,20,27,21],[27,22,27,23],[27,24,27,29],[27,31,27,33],[28,4,28,8],[28,9,28,10],[28,11,28,12],[28,13,28,14],[28,15,28,19],[28,20,28,21],[28,22,28,23],[28,24,28,29],[28,31,28,33],[29,4,29,8],[29,9,29,10],[29,11,29,12],[29,13,29,14],[29,15,29,19],[29,20,29,21],[29,22,29,23],[29,24,29,29],[29,31,29,33],[30,4,30,8],[30,9,30,10],[30,11,30,12],[30,13,30,14],[30,15,30,19],[30,20,30,21],[30,22,30,23],[30,24,30,29],[30,31,30,33],[31,4,31,8],[31,9,31,10],[31,11,31,12],[31,13,31,14],[31,15,31,19],[31,20,31,21],[31,22,31,23],[31,24,31,29],[31,31,31,33],[32,4,32,8],[32,9,32,10],[32,11,32,12],[32,13,32,14],[32,15,32,19],[32,20,32,21],[32,22,32,23],[32,24,32,29],[32,31,32,33],[33,4,33,8],[33,9,33,10],[33,11,33,12],[33,13,33,14],[33,15,33,19],[33,20,33,21],[33,22,33,23],[33,24,33,29],[33,31,33,33],[34,4,34,8],[34,9,34,10],[34,11,34,12],[34,13,34,14],[34,15,34,19],[34,20,34,21],[34,22,34,23],[34,24,34,29],[34,31,34,33],[35,4,35,8],[35,9,35,10],[35,11,35,12],[35,13,35,14],[35,15,35,19],[35,20,35,21],[35,22,35,23],[35,24,35,29],[35,31,35,33],[36,4,36,8],[36,9,36,10],[36,11,36,12],[36,13,36,14],[36,15,36,19],[36,20,36,21],[36,22,36,23],[36,24,36,29],[36,31,36,33],[37,4,37,8],[37,9,37,10],[37,11,37,12],[37,13,37,14],[37,15,37,19],[37,20,37,21],[37,22,37,23],[37,24,37,29],[37,31,37,33],[39,31,39,33],[38,4,38,8],[38,9,38,10],[38,11,38,12],[38,13,38,14],[38,15,38,19],[38,20,38,21],[38,22,38,23],[38,24,38,29],[38,31,38,33],[40,4,40,8],[40,9,40,10],[40,11,40,12],[40,13,40,14],[40,15,40,19],[39,22,39,23],[39,24,39,29],[39,4,39,8],[39,9,39,10],[39,11,39,12],[39,13,39,14],[39,15,39,19],[39,20,39,21],[40,22,40,23],[40,24,40,29],[40,31,40,33],[42,20,42,21],[42,22,42,23],[40,20,40,21],[42,9,42,10],[42,11,42,12],[42,13,42,14],[42,15,42,19],[41,9,41,10],[41,11,41,12],[41,13,41,14],[41,15,41,19],[43,31,43,33],[41,20,41,21],[43,22,43,23],[43,24,43,29],[41,22,41,23],[41,24,41,29],[47,2,47,38],[42,24,42,29],[42,31,42,33],[43,4,43,8],[43,9,43,10],[43,11,43,12],[43,13,43,14],[43,15,43,19],[43,20,43,21],[42,4,42,8],[41,31,41,33],[41,4,41,8]]}
[null,null,"Bulk Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,"T163 - Rolleston BSP (132/66kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"QBWH - Blackwater 132kV TCP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,"Region is Capricornia"]
[]
[null,null,null,null,null,null,null,null,"Transformer size is 2x132/66/22kV 30/40/37.5MVA ONAN/ODAN/ODAF"]
[]
[]
[null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,"20.6 MVA on 22/03/2019 at 19:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,89.300003051757813,null,89.300003051757813,null,89.300003051757813,null,89.300003051757813,null,null,null,null,89.300003051757813,null,97.699996948242188,null,97.699996948242188,null,null,null,null,null,97.699996948242188,97.699996948242188,null,null,97.699996948242188]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,22.299999237060547,null,22.100000381469727,null,21.899999618530273,null,21.899999618530273,null,null,null,null,22,null,18.799999237060547,null,18.700000762939453,null,null,null,null,null,18.600000381469727,18.600000381469727,null,null,18.600000381469727]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,0.96699999999999997,null,0.96699999999999997,null,0.96699999999999997,null,0.96699999999999997,null,null,null,null,0.96699999999999997,null,0.95599999999999996,null,0.95599999999999996,null,null,null,null,null,0.95599999999999996,0.95599999999999996,null,null,0.95599999999999996]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,52.299999237060547,null,52.299999237060547,null,52.299999237060547,null,52.299999237060547,null,null,null,null,52.299999237060547,null,56.099998474121094,null,56.099998474121094,null,null,null,null,null,56.099998474121094,56.099998474121094,null,null,56.099998474121094]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,21.299999237060547,null,21.200000762939453,null,20.899999618530273,null,20.899999618530273,null,null,null,null,21,null,18.399999618530273,null,18.399999618530273,null,null,null,null,null,18.299999237060547,18.299999237060547,null,null,18.299999237060547]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,1.1000000000000001,null,1.1000000000000001,null,1,null,1,null,null,null,null,1.1000000000000001,null,0.9,null,0.9,null,null,null,null,null,0.9,0.9,null,null,0.9]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,"5.5",null,"5.5",null,"5.5",null,"5.5",null,null,null,null,"5.5",null,"5.5",null,"5.5",null,null,null,null,null,"5.5","5.5",null,null,"5.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"T166","index":256,"n_rows":48,"n_cols":35,"rows_kept":48,"cut":false,"hidden":false,"merged":[[0,2,0,40],[2,1,2,5],[2,8,4,20],[2,23,3,24],[2,26,4,37],[6,1,8,5],[6,8,6,36],[8,8,9,36],[11,8,11,36],[13,3,14,11],[13,14,13,26],[16,17,17,31],[17,3,18,11],[17,14,18,15],[21,4,22,8],[21,9,21,21],[21,22,21,34],[22,9,22,10],[22,11,22,12],[22,13,22,14],[22,15,22,19],[22,20,22,21],[22,22,22,23],[22,24,22,29],[22,31,22,33],[23,4,23,8],[23,9,23,10],[23,11,23,12],[23,13,23,14],[23,15,23,19],[23,20,23,21],[23,22,23,23],[23,24,23,29],[23,31,23,33],[24,4,24,8],[24,9,24,10],[24,11,24,12],[24,13,24,14],[24,15,24,19],[24,20,24,21],[24,22,24,23],[24,24,24,29],[24,31,24,33],[25,4,25,8],[25,9,25,10],[25,11,25,12],[25,13,25,14],[25,15,25,19],[25,20,25,21],[25,22,25,23],[25,24,25,29],[25,31,25,33],[26,4,26,8],[26,9,26,10],[26,11,26,12],[26,13,26,14],[26,15,26,19],[26,20,26,21],[26,22,26,23],[26,24,26,29],[26,31,26,33],[27,4,27,8],[27,9,27,10],[27,11,27,12],[27,13,27,14],[27,15,27,19],[27,20,27,21],[27,22,27,23],[27,24,27,29],[27,31,27,33],[28,4,28,8],[28,9,28,10],[28,11,28,12],[28,13,28,14],[28,15,28,19],[28,20,28,21],[28,22,28,23],[28,24,28,29],[28,31,28,33],[29,4,29,8],[29,9,29,10],[29,11,29,12],[29,13,29,14],[29,15,29,19],[29,20,29,21],[29,22,29,23],[29,24,29,29],[29,31,29,33],[30,4,30,8],[30,9,30,10],[30,11,30,12],[30,13,30,14],[30,15,30,19],[30,20,30,21],[30,22,30,23],[30,24,30,29],[30,31,30,33],[31,4,31,8],[31,9,31,10],[31,11,31,12],[31,13,31,14],[31,15,31,19],[31,20,31,21],[31,22,31,23],[31,24,31,29],[31,31,31,33],[32,4,32,8],[32,9,32,10],[32,11,32,12],[32,13,32,14],[32,15,32,19],[32,20,32,21],[32,22,32,23],[32,24,32,29],[32,31,32,33],[33,4,33,8],[33,9,33,10],[33,11,33,12],[33,13,33,14],[33,15,33,19],[33,20,33,21],[33,22,33,23],[33,24,33,29],[33,31,33,33],[34,4,34,8],[34,9,34,10],[34,11,34,12],[34,13,34,14],[34,15,34,19],[34,20,34,21],[34,22,34,23],[34,24,34,29],[34,31,34,33],[35,4,35,8],[35,9,35,10],[35,11,35,12],[35,13,35,14],[35,15,35,19],[35,20,35,21],[35,22,35,23],[35,24,35,29],[35,31,35,33],[36,4,36,8],[36,9,36,10],[36,11,36,12],[36,13,36,14],[36,15,36,19],[36,20,36,21],[36,22,36,23],[36,24,36,29],[36,31,36,33],[37,4,37,8],[37,9,37,10],[37,11,37,12],[37,13,37,14],[37,15,37,19],[37,20,37,21],[37,22,37,23],[37,24,37,29],[37,31,37,33],[39,31,39,33],[38,4,38,8],[38,9,38,10],[38,11,38,12],[38,13,38,14],[38,15,38,19],[38,20,38,21],[38,22,38,23],[38,24,38,29],[38,31,38,33],[40,4,40,8],[40,9,40,10],[40,11,40,12],[40,13,40,14],[40,15,40,19],[39,22,39,23],[39,24,39,29],[39,4,39,8],[39,9,39,10],[39,11,39,12],[39,13,39,14],[39,15,39,19],[39,20,39,21],[40,22,40,23],[40,24,40,29],[40,31,40,33],[42,20,42,21],[42,22,42,23],[40,20,40,21],[42,9,42,10],[42,11,42,12],[42,13,42,14],[42,15,42,19],[41,9,41,10],[41,11,41,12],[41,13,41,14],[41,15,41,19],[43,31,43,33],[41,20,41,21],[43,22,43,23],[43,24,43,29],[41,22,41,23],[41,24,41,29],[47,2,47,38],[42,24,42,29],[42,31,42,33],[43,4,43,8],[43,9,43,10],[43,11,43,12],[43,13,43,14],[43,15,43,19],[43,20,43,21],[42,4,42,8],[41,31,41,33],[41,4,41,8]]}
[null,null,"Bulk Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,"T166 - Granite Creek BSP (132/66kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"QGNG - Gin Gin TCP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,"Region is Capricornia"]
[]
[null,null,null,null,null,null,null,null,"Transformer size is 1xGRCR TRANSF 1-132/66/22KV TRANSF 1;1xGRCR TRANSF 2-132/66/11KV TRANSF 2(Standby)"]
[]
[]
[null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,"6.5 MVA on 29/12/2018 at 19:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,32,null,32,null,32,null,32,null,null,null,null,32,null,32,null,32,null,null,null,null,null,32,32,null,null,32]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,5.1999998092651367,null,5.1999998092651367,null,5.1999998092651367,null,5.1999998092651367,null,null,null,null,5.1999998092651367,null,4.6999998092651367,null,4.6999998092651367,null,null,null,null,null,4.6999998092651367,4.6999998092651367,null,null,4.6999998092651367]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,0.97799999999999998,null,0.97799999999999998,null,0.97799999999999998,null,0.97799999999999998,null,null,null,null,0.97799999999999998,null,0.96599999999999997,null,0.96599999999999997,null,null,null,null,null,0.96599999999999997,0.96599999999999997,null,null,0.96599999999999997]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,5,null,4.9000000953674316,null,4.9000000953674316,null,4.9000000953674316,null,null,null,null,4.9000000953674316,null,4.5,null,4.5,null,null,null,null,null,4.5,4.5,null,null,4.5]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,0.3,null,0.2,null,0.2,null,0.2,null,null,null,null,0.2,null,0.2,null,0.2,null,null,null,null,null,0.2,0.2,null,null,0.2]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,"7.5",null,"7.5",null,"7.5",null,"7.5",null,null,null,null,"7.5",null,"7.5",null,"7.5",null,null,null,null,null,"7.5","7.5",null,null,"7.5"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,5,null,4.9000000000000004,null,4.9000000000000004,null,4.9000000000000004,null,null,null,null,4.9000000000000004,null,4.5,null,4.5,null,null,null,null,null,4.5,4.5,null,null,4.5]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,15,null,15,null,15,null,15,null,null,null,null,15,null,15,null,15,null,null,null,null,null,15,15,null,null,15]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"T176","index":257,"n_rows":48,"n_cols":35,"rows_kept":48,"cut":false,"hidden":false,"merged":[[0,2,0,40],[2,1,2,5],[2,8,4,20],[2,23,3,24],[2,26,4,37],[6,1,8,5],[6,8,6,36],[8,8,9,36],[11,8,11,36],[13,3,14,11],[13,14,13,26],[16,17,17,31],[17,3,18,11],[17,14,18,15],[21,4,22,8],[21,9,21,21],[21,22,21,34],[22,9,22,10],[22,11,22,12],[22,13,22,14],[22,15,22,19],[22,20,22,21],[22,22,22,23],[22,24,22,29],[22,31,22,33],[23,4,23,8],[23,9,23,10],[23,11,23,12],[23,13,23,14],[23,15,23,19],[23,20,23,21],[23,22,23,23],[23,24,23,29],[23,31,23,33],[24,4,24,8],[24,9,24,10],[24,11,24,12],[24,13,24,14],[24,15,24,19],[24,20,24,21],[24,22,24,23],[24,24,24,29],[24,31,24,33],[25,4,25,8],[25,9,25,10],[25,11,25,12],[25,13,25,14],[25,15,25,19],[25,20,25,21],[25,22,25,23],[25,24,25,29],[25,31,25,33],[26,4,26,8],[26,9,26,10],[26,11,26,12],[26,13,26,14],[26,15,26,19],[26,20,26,21],[26,22,26,23],[26,24,26,29],[26,31,26,33],[27,4,27,8],[27,9,27,10],[27,11,27,12],[27,13,27,14],[27,15,27,19],[27,20,27,21],[27,22,27,23],[27,24,27,29],[27,31,27,33],[28,4,28,8],[28,9,28,10],[28,11,28,12],[28,13,28,14],[28,15,28,19],[28,20,28,21],[28,22,28,23],[28,24,28,29],[28,31,28,33],[29,4,29,8],[29,9,29,10],[29,11,29,12],[29,13,29,14],[29,15,29,19],[29,20,29,21],[29,22,29,23],[29,24,29,29],[29,31,29,33],[30,4,30,8],[30,9,30,10],[30,11,30,12],[30,13,30,14],[30,15,30,19],[30,20,30,21],[30,22,30,23],[30,24,30,29],[30,31,30,33],[31,4,31,8],[31,9,31,10],[31,11,31,12],[31,13,31,14],[31,15,31,19],[31,20,31,21],[31,22,31,23],[31,24,31,29],[31,31,31,33],[32,4,32,8],[32,9,32,10],[32,11,32,12],[32,13,32,14],[32,15,32,19],[32,20,32,21],[32,22,32,23],[32,24,32,29],[32,31,32,33],[33,4,33,8],[33,9,33,10],[33,11,33,12],[33,13,33,14],[33,15,33,19],[33,20,33,21],[33,22,33,23],[33,24,33,29],[33,31,33,33],[34,4,34,8],[34,9,34,10],[34,11,34,12],[34,13,34,14],[34,15,34,19],[34,20,34,21],[34,22,34,23],[34,24,34,29],[34,31,34,33],[35,4,35,8],[35,9,35,10],[35,11,35,12],[35,13,35,14],[35,15,35,19],[35,20,35,21],[35,22,35,23],[35,24,35,29],[35,31,35,33],[36,4,36,8],[36,9,36,10],[36,11,36,12],[36,13,36,14],[36,15,36,19],[36,20,36,21],[36,22,36,23],[36,24,36,29],[36,31,36,33],[37,4,37,8],[37,9,37,10],[37,11,37,12],[37,13,37,14],[37,15,37,19],[37,20,37,21],[37,22,37,23],[37,24,37,29],[37,31,37,33],[39,31,39,33],[38,4,38,8],[38,9,38,10],[38,11,38,12],[38,13,38,14],[38,15,38,19],[38,20,38,21],[38,22,38,23],[38,24,38,29],[38,31,38,33],[40,4,40,8],[40,9,40,10],[40,11,40,12],[40,13,40,14],[40,15,40,19],[39,22,39,23],[39,24,39,29],[39,4,39,8],[39,9,39,10],[39,11,39,12],[39,13,39,14],[39,15,39,19],[39,20,39,21],[40,22,40,23],[40,24,40,29],[40,31,40,33],[42,20,42,21],[42,22,42,23],[40,20,40,21],[42,9,42,10],[42,11,42,12],[42,13,42,14],[42,15,42,19],[41,9,41,10],[41,11,41,12],[41,13,41,14],[41,15,41,19],[43,31,43,33],[41,20,41,21],[43,22,43,23],[43,24,43,29],[41,22,41,23],[41,24,41,29],[47,2,47,38],[42,24,42,29],[42,31,42,33],[43,4,43,8],[43,9,43,10],[43,11,43,12],[43,13,43,14],[43,15,43,19],[43,20,43,21],[42,4,42,8],[41,31,41,33],[41,4,41,8]]}
[null,null,"Bulk Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,"T176 - Louisa Creek BSP (132/33kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"QALH - Alligator Creek 132kV TCP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,"Region is Mackay"]
[]
[null,null,null,null,null,null,null,null,"Transformer size is 2x132/33/11kV 60/80MVA ONAN/ODAN"]
[]
[]
[null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,"41.4 MVA on 06/03/2019 at 04:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,175.80000305175781,null,175.80000305175781,null,175.80000305175781,null,175.80000305175781,null,null,null,null,175.80000305175781,null,185.19999694824219,null,185.19999694824219,null,null,null,null,null,185.19999694824219,185.19999694824219,null,null,185.19999694824219]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,43.599998474121094,null,43.400001525878906,null,43,null,43,null,null,null,null,43.299999237060547,null,40.200000762939453,null,40,null,null,null,null,null,40,39.900001525878906,null,null,40.099998474121094]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,0.96199999999999997,null,0.96199999999999997,null,0.96199999999999997,null,0.96199999999999997,null,null,null,null,0.96199999999999997,null,0.95699999999999996,null,0.95699999999999996,null,null,null,null,null,0.95699999999999996,0.95699999999999996,null,null,0.95699999999999996]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,100.40000152587891,null,100.40000152587891,null,100.40000152587891,null,100.40000152587891,null,null,null,null,100.40000152587891,null,105.5,null,105.5,null,null,null,null,null,105.5,105.5,null,null,105.5]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,42.400001525878906,null,42.299999237060547,null,41.900001525878906,null,41.900001525878906,null,null,null,null,42.200000762939453,null,40,null,39.900001525878906,null,null,null,null,null,39.799999237060547,39.799999237060547,null,null,40]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,2.1,null,2.1,null,2.1,null,2.1,null,null,null,null,2.1,null,2,null,2,null,null,null,null,null,2,2,null,null,2]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,"12.5",null,"12.5",null,"12.5",null,"12.5",null,null,null,null,"12.5",null,"12.5",null,"12.5",null,null,null,null,null,"12.5","12.5",null,null,"12.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"T188","index":258,"n_rows":48,"n_cols":35,"rows_kept":48,"cut":false,"hidden":false,"merged":[[0,2,0,40],[2,1,2,5],[2,8,4,20],[2,23,3,24],[2,26,4,37],[6,1,8,5],[6,8,6,36],[8,8,9,36],[11,8,11,36],[13,3,14,11],[13,14,13,26],[16,17,17,31],[17,3,18,11],[17,14,18,15],[21,4,22,8],[21,9,21,21],[21,22,21,34],[22,9,22,10],[22,11,22,12],[22,13,22,14],[22,15,22,19],[22,20,22,21],[22,22,22,23],[22,24,22,29],[22,31,22,33],[23,4,23,8],[23,9,23,10],[23,11,23,12],[23,13,23,14],[23,15,23,19],[23,20,23,21],[23,22,23,23],[23,24,23,29],[23,31,23,33],[24,4,24,8],[24,9,24,10],[24,11,24,12],[24,13,24,14],[24,15,24,19],[24,20,24,21],[24,22,24,23],[24,24,24,29],[24,31,24,33],[25,4,25,8],[25,9,25,10],[25,11,25,12],[25,13,25,14],[25,15,25,19],[25,20,25,21],[25,22,25,23],[25,24,25,29],[25,31,25,33],[26,4,26,8],[26,9,26,10],[26,11,26,12],[26,13,26,14],[26,15,26,19],[26,20,26,21],[26,22,26,23],[26,24,26,29],[26,31,26,33],[27,4,27,8],[27,9,27,10],[27,11,27,12],[27,13,27,14],[27,15,27,19],[27,20,27,21],[27,22,27,23],[27,24,27,29],[27,31,27,33],[28,4,28,8],[28,9,28,10],[28,11,28,12],[28,13,28,14],[28,15,28,19],[28,20,28,21],[28,22,28,23],[28,24,28,29],[28,31,28,33],[29,4,29,8],[29,9,29,10],[29,11,29,12],[29,13,29,14],[29,15,29,19],[29,20,29,21],[29,22,29,23],[29,24,29,29],[29,31,29,33],[30,4,30,8],[30,9,30,10],[30,11,30,12],[30,13,30,14],[30,15,30,19],[30,20,30,21],[30,22,30,23],[30,24,30,29],[30,31,30,33],[31,4,31,8],[31,9,31,10],[31,11,31,12],[31,13,31,14],[31,15,31,19],[31,20,31,21],[31,22,31,23],[31,24,31,29],[31,31,31,33],[32,4,32,8],[32,9,32,10],[32,11,32,12],[32,13,32,14],[32,15,32,19],[32,20,32,21],[32,22,32,23],[32,24,32,29],[32,31,32,33],[33,4,33,8],[33,9,33,10],[33,11,33,12],[33,13,33,14],[33,15,33,19],[33,20,33,21],[33,22,33,23],[33,24,33,29],[33,31,33,33],[34,4,34,8],[34,9,34,10],[34,11,34,12],[34,13,34,14],[34,15,34,19],[34,20,34,21],[34,22,34,23],[34,24,34,29],[34,31,34,33],[35,4,35,8],[35,9,35,10],[35,11,35,12],[35,13,35,14],[35,15,35,19],[35,20,35,21],[35,22,35,23],[35,24,35,29],[35,31,35,33],[36,4,36,8],[36,9,36,10],[36,11,36,12],[36,13,36,14],[36,15,36,19],[36,20,36,21],[36,22,36,23],[36,24,36,29],[36,31,36,33],[37,4,37,8],[37,9,37,10],[37,11,37,12],[37,13,37,14],[37,15,37,19],[37,20,37,21],[37,22,37,23],[37,24,37,29],[37,31,37,33],[39,31,39,33],[38,4,38,8],[38,9,38,10],[38,11,38,12],[38,13,38,14],[38,15,38,19],[38,20,38,21],[38,22,38,23],[38,24,38,29],[38,31,38,33],[40,4,40,8],[40,9,40,10],[40,11,40,12],[40,13,40,14],[40,15,40,19],[39,22,39,23],[39,24,39,29],[39,4,39,8],[39,9,39,10],[39,11,39,12],[39,13,39,14],[39,15,39,19],[39,20,39,21],[40,22,40,23],[40,24,40,29],[40,31,40,33],[42,20,42,21],[42,22,42,23],[40,20,40,21],[42,9,42,10],[42,11,42,12],[42,13,42,14],[42,15,42,19],[41,9,41,10],[41,11,41,12],[41,13,41,14],[41,15,41,19],[43,31,43,33],[41,20,41,21],[43,22,43,23],[43,24,43,29],[41,22,41,23],[41,24,41,29],[47,2,47,38],[42,24,42,29],[42,31,42,33],[43,4,43,8],[43,9,43,10],[43,11,43,12],[43,13,43,14],[43,15,43,19],[43,20,43,21],[42,4,42,8],[41,31,41,33],[41,4,41,8]]}
[null,null,"Bulk Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,"T188 - Daandine BSP (110/33kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"QTKM - Tangkam TCP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,"Region is South West"]
[]
[null,null,null,null,null,null,null,null,"Transformer size is 1x110/33/11kV 24/32MVA ONAN/ODAN"]
[]
[]
[null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 30.0 MVA"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,"3 MVA on 17/12/2018 at 18:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,37.299999237060547,null,37.299999237060547,null,37.299999237060547,null,37.299999237060547,null,null,null,null,37.299999237060547,null,40.5,null,40.5,null,null,null,null,null,40.5,40.5,null,null,40.5]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,-209.80000305175781,null,-209.80000305175781,null,-209.80000305175781,null,-209.80000305175781,null,null,null,null,-209.80000305175781,null,-24.200000762939453,null,-24.200000762939453,null,null,null,null,null,-24.200000762939453,-24.200000762939453,null,null,-24.200000762939453]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,3.7000000476837158,null,3.5999999046325684,null,3.5999999046325684,null,3.5999999046325684,null,null,null,null,3.5999999046325684,null,1.5,null,1.5,null,null,null,null,null,1.5,1.5,null,null,1.5]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,0.59899999999999998,null,0.59899999999999998,null,0.59899999999999998,null,0.59899999999999998,null,null,null,null,0.59899999999999998,null,0.7,null,0.7,null,null,null,null,null,0.7,0.7,null,null,0.7]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,3.5999999046325684,null,3.5,null,3.5,null,3.5,null,null,null,null,3.5,null,1.5,null,1.5,null,null,null,null,null,1.5,1.5,null,null,1.5]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,0.2,null,0.2,null,0.2,null,0.2,null,null,null,null,0.2,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,"6.5",null,"6.5",null,"6.5",null,"6.5",null,null,null,null,"6.5",null,"6.5",null,"6.5",null,null,null,null,null,"6.5","6.5",null,null,"6.5"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,3.6,null,3.5,null,3.5,null,3.5,null,null,null,null,3.5,null,1.5,null,1.5,null,null,null,null,null,1.5,1.5,null,null,1.5]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,3.5999999046325684,null,3.5999999046325684,null,3.5999999046325684,null,3.5999999046325684,null,null,null,null,3.5999999046325684,null,3.5999999046325684,null,3.5999999046325684,null,null,null,null,null,3.5999999046325684,3.5999999046325684,null,null,3.5999999046325684]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"T189","index":259,"n_rows":48,"n_cols":35,"rows_kept":48,"cut":false,"hidden":false,"merged":[[0,2,0,40],[2,1,2,5],[2,8,4,20],[2,23,3,24],[2,26,4,37],[6,1,8,5],[6,8,6,36],[8,8,9,36],[11,8,11,36],[13,3,14,11],[13,14,13,26],[16,17,17,31],[17,3,18,11],[17,14,18,15],[21,4,22,8],[21,9,21,21],[21,22,21,34],[22,9,22,10],[22,11,22,12],[22,13,22,14],[22,15,22,19],[22,20,22,21],[22,22,22,23],[22,24,22,29],[22,31,22,33],[23,4,23,8],[23,9,23,10],[23,11,23,12],[23,13,23,14],[23,15,23,19],[23,20,23,21],[23,22,23,23],[23,24,23,29],[23,31,23,33],[24,4,24,8],[24,9,24,10],[24,11,24,12],[24,13,24,14],[24,15,24,19],[24,20,24,21],[24,22,24,23],[24,24,24,29],[24,31,24,33],[25,4,25,8],[25,9,25,10],[25,11,25,12],[25,13,25,14],[25,15,25,19],[25,20,25,21],[25,22,25,23],[25,24,25,29],[25,31,25,33],[26,4,26,8],[26,9,26,10],[26,11,26,12],[26,13,26,14],[26,15,26,19],[26,20,26,21],[26,22,26,23],[26,24,26,29],[26,31,26,33],[27,4,27,8],[27,9,27,10],[27,11,27,12],[27,13,27,14],[27,15,27,19],[27,20,27,21],[27,22,27,23],[27,24,27,29],[27,31,27,33],[28,4,28,8],[28,9,28,10],[28,11,28,12],[28,13,28,14],[28,15,28,19],[28,20,28,21],[28,22,28,23],[28,24,28,29],[28,31,28,33],[29,4,29,8],[29,9,29,10],[29,11,29,12],[29,13,29,14],[29,15,29,19],[29,20,29,21],[29,22,29,23],[29,24,29,29],[29,31,29,33],[30,4,30,8],[30,9,30,10],[30,11,30,12],[30,13,30,14],[30,15,30,19],[30,20,30,21],[30,22,30,23],[30,24,30,29],[30,31,30,33],[31,4,31,8],[31,9,31,10],[31,11,31,12],[31,13,31,14],[31,15,31,19],[31,20,31,21],[31,22,31,23],[31,24,31,29],[31,31,31,33],[32,4,32,8],[32,9,32,10],[32,11,32,12],[32,13,32,14],[32,15,32,19],[32,20,32,21],[32,22,32,23],[32,24,32,29],[32,31,32,33],[33,4,33,8],[33,9,33,10],[33,11,33,12],[33,13,33,14],[33,15,33,19],[33,20,33,21],[33,22,33,23],[33,24,33,29],[33,31,33,33],[34,4,34,8],[34,9,34,10],[34,11,34,12],[34,13,34,14],[34,15,34,19],[34,20,34,21],[34,22,34,23],[34,24,34,29],[34,31,34,33],[35,4,35,8],[35,9,35,10],[35,11,35,12],[35,13,35,14],[35,15,35,19],[35,20,35,21],[35,22,35,23],[35,24,35,29],[35,31,35,33],[36,4,36,8],[36,9,36,10],[36,11,36,12],[36,13,36,14],[36,15,36,19],[36,20,36,21],[36,22,36,23],[36,24,36,29],[36,31,36,33],[37,4,37,8],[37,9,37,10],[37,11,37,12],[37,13,37,14],[37,15,37,19],[37,20,37,21],[37,22,37,23],[37,24,37,29],[37,31,37,33],[39,31,39,33],[38,4,38,8],[38,9,38,10],[38,11,38,12],[38,13,38,14],[38,15,38,19],[38,20,38,21],[38,22,38,23],[38,24,38,29],[38,31,38,33],[40,4,40,8],[40,9,40,10],[40,11,40,12],[40,13,40,14],[40,15,40,19],[39,22,39,23],[39,24,39,29],[39,4,39,8],[39,9,39,10],[39,11,39,12],[39,13,39,14],[39,15,39,19],[39,20,39,21],[40,22,40,23],[40,24,40,29],[40,31,40,33],[42,20,42,21],[42,22,42,23],[40,20,40,21],[42,9,42,10],[42,11,42,12],[42,13,42,14],[42,15,42,19],[41,9,41,10],[41,11,41,12],[41,13,41,14],[41,15,41,19],[43,31,43,33],[41,20,41,21],[43,22,43,23],[43,24,43,29],[41,22,41,23],[41,24,41,29],[47,2,47,38],[42,24,42,29],[42,31,42,33],[43,4,43,8],[43,9,43,10],[43,11,43,12],[43,13,43,14],[43,15,43,19],[43,20,43,21],[42,4,42,8],[41,31,41,33],[41,4,41,8]]}
[null,null,"Bulk Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,"T189 - Oakey BSP (110/33kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"QOKT - Oakey TCP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,"Region is South West"]
[]
[null,null,null,null,null,null,null,null,"Transformer size is 2x110/33/11kV 48/63MVA ONAN/ODAN"]
[]
[]
[null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,"23.8 MVA on 06/11/2018 at 15:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,147.19999694824219,null,147.19999694824219,null,147.19999694824219,null,147.19999694824219,null,null,null,null,147.19999694824219,null,165.19999694824219,null,165.19999694824219,null,null,null,null,null,165.19999694824219,165.19999694824219,null,null,165.19999694824219]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,26.5,null,26.200000762939453,null,25.700000762939453,null,25.5,null,null,null,null,25.399999618530273,null,23.299999237060547,null,23,null,null,null,null,null,22.700000762939453,22.5,null,null,22.399999618530273]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,0.95899999999999996,null,0.95899999999999996,null,0.95899999999999996,null,0.95899999999999996,null,null,null,null,0.95899999999999996,null,0.96599999999999997,null,0.96599999999999997,null,null,null,null,null,0.96599999999999997,0.96599999999999997,null,null,0.96599999999999997]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,82,null,82,null,82,null,82,null,null,null,null,82,null,92.5,null,92.5,null,null,null,null,null,92.5,92.5,null,null,92.5]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,25.100000381469727,null,24.700000762939453,null,24.299999237060547,null,24.100000381469727,null,null,null,null,24,null,22.600000381469727,null,22.299999237060547,null,null,null,null,null,22.100000381469727,21.899999618530273,null,null,21.700000762939453]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,1.3,null,1.2,null,1.2,null,1.2,null,null,null,null,1.2,null,1.1000000000000001,null,1.1000000000000001,null,null,null,null,null,1.1000000000000001,1.1000000000000001,null,null,1.1000000000000001]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,"19.5",null,"19.5",null,"19.5",null,"19.5",null,null,null,null,"19.5",null,"19.5",null,"19.5",null,null,null,null,null,"19.5","19.5",null,null,"19.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"T194","index":260,"n_rows":48,"n_cols":35,"rows_kept":48,"cut":false,"hidden":false,"merged":[[0,2,0,40],[2,1,2,5],[2,8,4,20],[2,23,3,24],[2,26,4,37],[6,1,8,5],[6,8,6,36],[8,8,9,36],[11,8,11,36],[13,3,14,11],[13,14,13,26],[16,17,17,31],[17,3,18,11],[17,14,18,15],[21,4,22,8],[21,9,21,21],[21,22,21,34],[22,9,22,10],[22,11,22,12],[22,13,22,14],[22,15,22,19],[22,20,22,21],[22,22,22,23],[22,24,22,29],[22,31,22,33],[23,4,23,8],[23,9,23,10],[23,11,23,12],[23,13,23,14],[23,15,23,19],[23,20,23,21],[23,22,23,23],[23,24,23,29],[23,31,23,33],[24,4,24,8],[24,9,24,10],[24,11,24,12],[24,13,24,14],[24,15,24,19],[24,20,24,21],[24,22,24,23],[24,24,24,29],[24,31,24,33],[25,4,25,8],[25,9,25,10],[25,11,25,12],[25,13,25,14],[25,15,25,19],[25,20,25,21],[25,22,25,23],[25,24,25,29],[25,31,25,33],[26,4,26,8],[26,9,26,10],[26,11,26,12],[26,13,26,14],[26,15,26,19],[26,20,26,21],[26,22,26,23],[26,24,26,29],[26,31,26,33],[27,4,27,8],[27,9,27,10],[27,11,27,12],[27,13,27,14],[27,15,27,19],[27,20,27,21],[27,22,27,23],[27,24,27,29],[27,31,27,33],[28,4,28,8],[28,9,28,10],[28,11,28,12],[28,13,28,14],[28,15,28,19],[28,20,28,21],[28,22,28,23],[28,24,28,29],[28,31,28,33],[29,4,29,8],[29,9,29,10],[29,11,29,12],[29,13,29,14],[29,15,29,19],[29,20,29,21],[29,22,29,23],[29,24,29,29],[29,31,29,33],[30,4,30,8],[30,9,30,10],[30,11,30,12],[30,13,30,14],[30,15,30,19],[30,20,30,21],[30,22,30,23],[30,24,30,29],[30,31,30,33],[31,4,31,8],[31,9,31,10],[31,11,31,12],[31,13,31,14],[31,15,31,19],[31,20,31,21],[31,22,31,23],[31,24,31,29],[31,31,31,33],[32,4,32,8],[32,9,32,10],[32,11,32,12],[32,13,32,14],[32,15,32,19],[32,20,32,21],[32,22,32,23],[32,24,32,29],[32,31,32,33],[33,4,33,8],[33,9,33,10],[33,11,33,12],[33,13,33,14],[33,15,33,19],[33,20,33,21],[33,22,33,23],[33,24,33,29],[33,31,33,33],[34,4,34,8],[34,9,34,10],[34,11,34,12],[34,13,34,14],[34,15,34,19],[34,20,34,21],[34,22,34,23],[34,24,34,29],[34,31,34,33],[35,4,35,8],[35,9,35,10],[35,11,35,12],[35,13,35,14],[35,15,35,19],[35,20,35,21],[35,22,35,23],[35,24,35,29],[35,31,35,33],[36,4,36,8],[36,9,36,10],[36,11,36,12],[36,13,36,14],[36,15,36,19],[36,20,36,21],[36,22,36,23],[36,24,36,29],[36,31,36,33],[37,4,37,8],[37,9,37,10],[37,11,37,12],[37,13,37,14],[37,15,37,19],[37,20,37,21],[37,22,37,23],[37,24,37,29],[37,31,37,33],[39,31,39,33],[38,4,38,8],[38,9,38,10],[38,11,38,12],[38,13,38,14],[38,15,38,19],[38,20,38,21],[38,22,38,23],[38,24,38,29],[38,31,38,33],[40,4,40,8],[40,9,40,10],[40,11,40,12],[40,13,40,14],[40,15,40,19],[39,22,39,23],[39,24,39,29],[39,4,39,8],[39,9,39,10],[39,11,39,12],[39,13,39,14],[39,15,39,19],[39,20,39,21],[40,22,40,23],[40,24,40,29],[40,31,40,33],[42,20,42,21],[42,22,42,23],[40,20,40,21],[42,9,42,10],[42,11,42,12],[42,13,42,14],[42,15,42,19],[41,9,41,10],[41,11,41,12],[41,13,41,14],[41,15,41,19],[43,31,43,33],[41,20,41,21],[43,22,43,23],[43,24,43,29],[41,22,41,23],[41,24,41,29],[47,2,47,38],[42,24,42,29],[42,31,42,33],[43,4,43,8],[43,9,43,10],[43,11,43,12],[43,13,43,14],[43,15,43,19],[43,20,43,21],[42,4,42,8],[41,31,41,33],[41,4,41,8]]}
[null,null,"Bulk Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,"T194 - Columboola BSP (132/33kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T194 - Columboola TCP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,"Region is South West"]
[]
[null,null,null,null,null,null,null,null,"Transformer size is 1xCOLU 132/33KV TRANSF 1"]
[]
[]
[null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,"14.4 MVA on 12/02/2019 at 17:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,40.200000762939453,null,40.200000762939453,null,40.200000762939453,null,40.200000762939453,null,null,null,null,40.200000762939453,null,47.400001525878906,null,47.400001525878906,null,null,null,null,null,47.400001525878906,47.400001525878906,null,null,47.400001525878906]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,16.700000762939453,null,16.600000381469727,null,16.399999618530273,null,16.299999237060547,null,null,null,null,16.299999237060547,null,12.399999618530273,null,12.300000190734863,null,null,null,null,null,12.300000190734863,12.300000190734863,null,null,12.199999809265137]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,0.98,null,0.98,null,0.98,null,0.98,null,null,null,null,0.98,null,0.99299999999999999,null,0.99299999999999999,null,null,null,null,null,0.99299999999999999,0.99299999999999999,null,null,0.99299999999999999]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,15.199999809265137,null,15.100000381469727,null,14.899999618530273,null,14.800000190734863,null,null,null,null,14.800000190734863,null,11.600000381469727,null,11.5,null,null,null,null,null,11.5,11.399999618530273,null,null,11.399999618530273]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,0.8,null,0.8,null,0.7,null,0.7,null,null,null,null,0.7,null,0.6,null,0.6,null,null,null,null,null,0.6,0.6,null,null,0.6]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,"12",null,"12",null,"12",null,"12",null,null,null,null,"12",null,"12",null,"12",null,null,null,null,null,"12","12",null,null,"12"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,15.2,null,15.1,null,14.9,null,14.8,null,null,null,null,14.8,null,11.6,null,11.5,null,null,null,null,null,11.5,11.4,null,null,11.4]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,14,null,14,null,14,null,14,null,null,null,null,14,null,14,null,14,null,null,null,null,null,14,14,null,null,14]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,2,null,2,null,2,null,2,null,null,null,null,2,null,2,null,2,null,null,null,null,null,2,2,null,null,2]
[null,null,null,null,"Shed(30min)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"T198","index":261,"n_rows":48,"n_cols":35,"rows_kept":48,"cut":false,"hidden":false,"merged":[[0,2,0,40],[2,1,2,5],[2,8,4,20],[2,23,3,24],[2,26,4,37],[6,1,8,5],[6,8,6,36],[8,8,9,36],[11,8,11,36],[13,3,14,11],[13,14,13,26],[16,17,17,31],[17,3,18,11],[17,14,18,15],[21,4,22,8],[21,9,21,21],[21,22,21,34],[22,9,22,10],[22,11,22,12],[22,13,22,14],[22,15,22,19],[22,20,22,21],[22,22,22,23],[22,24,22,29],[22,31,22,33],[23,4,23,8],[23,9,23,10],[23,11,23,12],[23,13,23,14],[23,15,23,19],[23,20,23,21],[23,22,23,23],[23,24,23,29],[23,31,23,33],[24,4,24,8],[24,9,24,10],[24,11,24,12],[24,13,24,14],[24,15,24,19],[24,20,24,21],[24,22,24,23],[24,24,24,29],[24,31,24,33],[25,4,25,8],[25,9,25,10],[25,11,25,12],[25,13,25,14],[25,15,25,19],[25,20,25,21],[25,22,25,23],[25,24,25,29],[25,31,25,33],[26,4,26,8],[26,9,26,10],[26,11,26,12],[26,13,26,14],[26,15,26,19],[26,20,26,21],[26,22,26,23],[26,24,26,29],[26,31,26,33],[27,4,27,8],[27,9,27,10],[27,11,27,12],[27,13,27,14],[27,15,27,19],[27,20,27,21],[27,22,27,23],[27,24,27,29],[27,31,27,33],[28,4,28,8],[28,9,28,10],[28,11,28,12],[28,13,28,14],[28,15,28,19],[28,20,28,21],[28,22,28,23],[28,24,28,29],[28,31,28,33],[29,4,29,8],[29,9,29,10],[29,11,29,12],[29,13,29,14],[29,15,29,19],[29,20,29,21],[29,22,29,23],[29,24,29,29],[29,31,29,33],[30,4,30,8],[30,9,30,10],[30,11,30,12],[30,13,30,14],[30,15,30,19],[30,20,30,21],[30,22,30,23],[30,24,30,29],[30,31,30,33],[31,4,31,8],[31,9,31,10],[31,11,31,12],[31,13,31,14],[31,15,31,19],[31,20,31,21],[31,22,31,23],[31,24,31,29],[31,31,31,33],[32,4,32,8],[32,9,32,10],[32,11,32,12],[32,13,32,14],[32,15,32,19],[32,20,32,21],[32,22,32,23],[32,24,32,29],[32,31,32,33],[33,4,33,8],[33,9,33,10],[33,11,33,12],[33,13,33,14],[33,15,33,19],[33,20,33,21],[33,22,33,23],[33,24,33,29],[33,31,33,33],[34,4,34,8],[34,9,34,10],[34,11,34,12],[34,13,34,14],[34,15,34,19],[34,20,34,21],[34,22,34,23],[34,24,34,29],[34,31,34,33],[35,4,35,8],[35,9,35,10],[35,11,35,12],[35,13,35,14],[35,15,35,19],[35,20,35,21],[35,22,35,23],[35,24,35,29],[35,31,35,33],[36,4,36,8],[36,9,36,10],[36,11,36,12],[36,13,36,14],[36,15,36,19],[36,20,36,21],[36,22,36,23],[36,24,36,29],[36,31,36,33],[37,4,37,8],[37,9,37,10],[37,11,37,12],[37,13,37,14],[37,15,37,19],[37,20,37,21],[37,22,37,23],[37,24,37,29],[37,31,37,33],[39,31,39,33],[38,4,38,8],[38,9,38,10],[38,11,38,12],[38,13,38,14],[38,15,38,19],[38,20,38,21],[38,22,38,23],[38,24,38,29],[38,31,38,33],[40,4,40,8],[40,9,40,10],[40,11,40,12],[40,13,40,14],[40,15,40,19],[39,22,39,23],[39,24,39,29],[39,4,39,8],[39,9,39,10],[39,11,39,12],[39,13,39,14],[39,15,39,19],[39,20,39,21],[40,22,40,23],[40,24,40,29],[40,31,40,33],[42,20,42,21],[42,22,42,23],[40,20,40,21],[42,9,42,10],[42,11,42,12],[42,13,42,14],[42,15,42,19],[41,9,41,10],[41,11,41,12],[41,13,41,14],[41,15,41,19],[43,31,43,33],[41,20,41,21],[43,22,43,23],[43,24,43,29],[41,22,41,23],[41,24,41,29],[47,2,47,38],[42,24,42,29],[42,31,42,33],[43,4,43,8],[43,9,43,10],[43,11,43,12],[43,13,43,14],[43,15,43,19],[43,20,43,21],[42,4,42,8],[41,31,41,33],[41,4,41,8]]}
[null,null,"Bulk Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,"T198 - Broadlea BSP (132/66kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"QMRH - Moranbah 132kV TCP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,"Region is Mackay"]
[]
[null,null,null,null,null,null,null,null,"Transformer size is 2x132/66/11kV 80/100MVA ONAN/ODAN"]
[]
[]
[null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,"43.6 MVA on 27/03/2019 at 01:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,223.10000610351563,null,223.10000610351563,null,223.10000610351563,null,223.10000610351563,null,null,null,null,223.10000610351563,null,241.39999389648438,null,241.39999389648438,null,null,null,null,null,241.39999389648438,241.39999389648438,null,null,241.39999389648438]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,46.400001525878906,null,46.099998474121094,null,45.599998474121094,null,45.599998474121094,null,null,null,null,45.900001525878906,null,41.5,null,41.400001525878906,null,null,null,null,null,41.200000762939453,41.200000762939453,null,null,41.299999237060547]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,0.98,null,0.98,null,0.98,null,0.98,null,null,null,null,0.98,null,0.97899999999999998,null,0.97899999999999998,null,null,null,null,null,0.97899999999999998,0.97899999999999998,null,null,0.97899999999999998]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,132.39999389648438,null,132.39999389648438,null,132.39999389648438,null,132.39999389648438,null,null,null,null,132.39999389648438,null,140.10000610351563,null,140.10000610351563,null,null,null,null,null,140.10000610351563,140.10000610351563,null,null,140.10000610351563]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,45.200000762939453,null,45,null,44.5,null,44.5,null,null,null,null,44.799999237060547,null,41.400001525878906,null,41.299999237060547,null,null,null,null,null,41.099998474121094,41.099998474121094,null,null,41.200000762939453]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,2.2999999999999998,null,2.2999999999999998,null,2.2000000000000002,null,2.2000000000000002,null,null,null,null,2.2000000000000002,null,2.1,null,2.1,null,null,null,null,null,2.1,2.1,null,null,2.1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,"25",null,"25",null,"25",null,"25",null,null,null,null,"25",null,"25",null,"25",null,null,null,null,null,"25","25",null,null,"25"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"TANB","index":262,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"TANB - Tanby (66/22kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"RMES - Rockhampton Mesh"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Capricornia"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/22kV 15/20MVA ONAN/ONAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 1.2%, 2020 S 1.4% W 1.4%, 2021 S 1.4% W 1.4%, 2022 S 1.9% W 1.9%, 2023 S 1.5% W 1.5%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"12.4 MVA on 28/11/2018 at 18:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,50.400001525878906,null,50.400001525878906,null,50.400001525878906,null,50.400001525878906,null,null,null,null,50.400001525878906,null,56.599998474121094,null,56.599998474121094,null,null,null,null,null,56.599998474121094,56.599998474121094,null,null,56.599998474121094]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,12.100000381469727,null,12.199999809265137,null,12.300000190734863,null,13.5,null,null,null,null,13.800000190734863,null,9.3999996185302734,null,9.5,null,null,null,null,null,9.6000003814697266,10.600000381469727,null,null,10.800000190734863]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.99,null,0.99,null,0.99,null,0.99,null,null,null,null,0.99,null,0.997,null,0.997,null,null,null,null,null,0.997,0.997,null,null,0.997]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,27.399999618530273,null,27.399999618530273,null,27.399999618530273,null,27.399999618530273,null,null,null,null,27.399999618530273,null,29.899999618530273,null,29.899999618530273,null,null,null,null,null,29.899999618530273,29.899999618530273,null,null,29.899999618530273]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,11.199999809265137,null,11.300000190734863,null,11.399999618530273,null,12.600000381469727,null,null,null,null,12.899999618530273,null,8.8000001907348633,null,8.8999996185302734,null,null,null,null,null,9,10.100000381469727,null,null,10.199999809265137]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.6,null,0.6,null,0.6,null,0.6,null,null,null,null,0.6,null,0.4,null,0.4,null,null,null,null,null,0.5,0.5,null,null,0.5]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"3.5",null,"3.5",null,"3.5",null,"3.5",null,null,null,null,"3.5",null,"3.5",null,"3.5",null,null,null,null,null,"3.5","3.5",null,null,"3.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"TARA","index":263,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"TARA - Tara (33/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T194 - Columboola BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is South West"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x33/11kV 1.5MVA ON;1x33/11kV 1MVA ON"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -1.5%, 2020 S -1.4% W -1.4%2021 S -0.4% W -0.4%2022 S -0.2% W -0.2%2023 S -0.5% W -0.5"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"1.5 MVA on 24/01/2019 at 16:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,2,null,2,null,2,null,2,null,null,null,null,2,null,2,null,2,null,null,null,null,null,2,2,null,null,2]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,1.7000000476837158,null,1.7000000476837158,null,1.7000000476837158,null,1.7000000476837158,null,null,null,null,1.7000000476837158,null,1.3999999761581421,null,1.3999999761581421,null,null,null,null,null,1.2999999523162842,1.2999999523162842,null,null,1.2999999523162842]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.95499999999999996,null,0.95499999999999996,null,0.95499999999999996,null,0.95499999999999996,null,null,null,null,0.95499999999999996,null,0.97899999999999998,null,0.98099999999999998,null,null,null,null,null,0.97899999999999998,0.97899999999999998,null,null,0.97899999999999998]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,1,null,1,null,1,null,1,null,null,null,null,1,null,1,null,1,null,null,null,null,null,1,1,null,null,1]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,1.6000000238418579,null,1.5,null,1.5,null,1.5,null,null,null,null,1.5,null,1.2999999523162842,null,1.2999999523162842,null,null,null,null,null,1.2000000476837158,1.2000000476837158,null,null,1.2000000476837158]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.1,null,0.1,null,0.1,null,0.1,null,null,null,null,0.1,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"11.5",null,"11.5",null,"11.5",null,"11.5",null,null,null,null,"11.5",null,"11.5",null,"11.5",null,null,null,null,null,"11.5","11.5",null,null,"11.5"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,0.6,null,0.5,null,0.5,null,0.5,null,null,null,null,0.5,null,0.3,null,0.3,null,null,null,null,null,0.2,0.2,null,null,0.2]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0.60000002384185791,null,0.60000002384185791,null,0.60000002384185791,null,0.60000002384185791,null,null,null,null,0.60000002384185791,null,0.60000002384185791,null,0.60000002384185791,null,null,null,null,null,0.60000002384185791,0.60000002384185791,null,null,0.60000002384185791]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"TEST","index":264,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"TEST - Tennyson Street (33/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T038 - Mackay BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Mackay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x33/11kV 10/12.5MVA ONAN/ONAF;1x33/11kV 12.5MVA ON"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -2.0%, 2020 S -1.3% W -1.3%2021 S -1.1% W -1.1%2022 S -0.8% W -0.8%2023 S -1.1% W -1.1"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"17.8 MVA on 28/11/2018 at 15:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,25,null,25,null,25,null,25,null,null,null,null,25,null,25,null,25,null,null,null,null,null,25,25,null,null,25]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,19.600000381469727,null,19.299999237060547,null,18.899999618530273,null,18.700000762939453,null,null,null,null,18.600000381469727,null,10,null,9.8999996185302734,null,null,null,null,null,9.6999998092651367,9.6000003814697266,null,null,9.6000003814697266]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.90800000000000003,null,0.90800000000000003,null,0.90800000000000003,null,0.90800000000000003,null,null,null,null,0.90800000000000003,null,0.89500000000000002,null,0.89500000000000002,null,null,null,null,null,0.89500000000000002,0.89500000000000002,null,null,0.89500000000000002]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,12.5,null,12.5,null,12.5,null,12.5,null,null,null,null,12.5,null,12.5,null,12.5,null,null,null,null,null,12.5,12.5,null,null,12.5]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,17.700000762939453,null,17.399999618530273,null,17.100000381469727,null,16.899999618530273,null,null,null,null,16.799999237060547,null,9.6999998092651367,null,9.6000003814697266,null,null,null,null,null,9.5,9.3999996185302734,null,null,9.3000001907348633]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.9,null,0.9,null,0.9,null,0.8,null,null,null,null,0.8,null,0.5,null,0.5,null,null,null,null,null,0.5,0.5,null,null,0.5]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"11.5",null,"11.5",null,"11.5",null,"11.5",null,null,null,null,"11.5",null,"11.5",null,"11.5",null,null,null,null,null,"11.5","11.5",null,null,"11.5"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,5.2,null,4.9000000000000004,null,4.5999999999999996,null,4.4000000000000004,null,null,null,null,4.3]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,5.1999998092651367,null,5.1999998092651367,null,5.1999998092651367,null,5.1999998092651367,null,null,null,null,5.1999998092651367,null,5.1999998092651367,null,5.1999998092651367,null,null,null,null,null,5.1999998092651367,5.1999998092651367,null,null,5.1999998092651367]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"THAL","index":265,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"THAL - Thalanga (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T095 - Millchester BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Nth Queensland"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/11kV 7.5MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.2%, 2020 S 0.5% W 0.5%, 2021 S -0.0% W -0.0%2022 S -0.2% W -0.2%2023 S -0.7% W -0.7"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"4.3 MVA on 23/01/2019 at 21:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,6.4000000953674316,null,6.4000000953674316,null,6.4000000953674316,null,6.4000000953674316,null,null,null,null,6.4000000953674316,null,6.8000001907348633,null,6.8000001907348633,null,null,null,null,null,6.8000001907348633,6.8000001907348633,null,null,6.8000001907348633]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,4.1999998092651367,null,4.1999998092651367,null,4.0999999046325684,null,4.0999999046325684,null,null,null,null,4.0999999046325684,null,3.2999999523162842,null,3.2999999523162842,null,null,null,null,null,3.2999999523162842,3.2999999523162842,null,null,3.2999999523162842]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.91500000000000004,null,0.91500000000000004,null,0.91500000000000004,null,0.91500000000000004,null,null,null,null,0.91500000000000004,null,0.93200000000000005,null,0.93200000000000005,null,null,null,null,null,0.93200000000000005,0.93200000000000005,null,null,0.93200000000000005]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,4.0999999046325684,null,4.0999999046325684,null,4,null,4,null,null,null,null,4,null,3.2999999523162842,null,3.2999999523162842,null,null,null,null,null,3.2999999523162842,3.2999999523162842,null,null,3.2999999523162842]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.2,null,0.2,null,0.2,null,0.2,null,null,null,null,0.2,null,0.2,null,0.2,null,null,null,null,null,0.2,0.2,null,null,0.2]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"86",null,"86",null,"86",null,"86",null,null,null,null,"86",null,"86",null,"86",null,null,null,null,null,"86","86",null,null,"86"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,4.0999999999999996,null,4.0999999999999996,null,4,null,4,null,null,null,null,4,null,3.3,null,3.3,null,null,null,null,null,3.3,3.3,null,null,3.3]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,1,null,1,null,1,null,1,null,null,null,null,1,null,1,null,1,null,null,null,null,null,1,1,null,null,1]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,2,null,2,null,2,null,2,null,null,null,null,2,null,2,null,2,null,null,null,null,null,2,2,null,null,2]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)",null,null,null,null,null,1.1000000238418579,null,1.1000000238418579,null,1,null,1,null,null,null,null,1,null,0.30000001192092896,null,0.30000001192092896,null,null,null,null,null,0.30000001192092896,0.30000001192092896,null,null,0.30000001192092896]
[null,null,null,null,"LARc (MW)",null,null,null,null,null,1,null,1,null,0.9,null,0.9,null,null,null,null,0.9,null,0.3,null,0.3,null,null,null,null,null,0.3,0.3,null,null,0.3]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"No",null,"No",null,"No",null,"No",null,null,null,null,"No",null,"No",null,"No",null,null,null,null,null,"No","No",null,null,"No"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"THEO","index":266,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"THEO - Theodore (66/22kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T027 - Moura BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Capricornia"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/22kV 5MVA ON;1x66/22kV 5MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -2.3%, 2020 S -0.9% W -0.9%2021 S -1.3% W -1.3%2022 S -0.8% W -0.8%2023 S -1.0% W -1.0"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"11.6 MVA on 11/03/2019 at 16:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,16.600000381469727,null,16.600000381469727,null,16.600000381469727,null,16.600000381469727,null,null,null,null,16.600000381469727,null,18.200000762939453,null,18.200000762939453,null,null,null,null,null,18.200000762939453,18.200000762939453,null,null,18.200000762939453]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,12.699999809265137,null,12.5,null,12.300000190734863,null,12.199999809265137,null,null,null,null,12.199999809265137,null,10,null,9.8999996185302734,null,null,null,null,null,9.6999998092651367,9.6000003814697266,null,null,9.6000003814697266]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.98699999999999999,null,0.98699999999999999,null,0.98699999999999999,null,0.98699999999999999,null,null,null,null,0.98699999999999999,null,0.97799999999999998,null,0.97799999999999998,null,null,null,null,null,0.97799999999999998,0.97799999999999998,null,null,0.97799999999999998]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,11.399999618530273,null,11.399999618530273,null,11.399999618530273,null,11.399999618530273,null,null,null,null,11.399999618530273,null,12.5,null,12.5,null,null,null,null,null,12.5,12.5,null,null,12.5]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,12.100000381469727,null,11.899999618530273,null,11.699999809265137,null,11.600000381469727,null,null,null,null,11.600000381469727,null,9.6999998092651367,null,9.6000003814697266,null,null,null,null,null,9.3999996185302734,9.3000001907348633,null,null,9.3000001907348633]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.6,null,0.6,null,0.6,null,0.6,null,null,null,null,0.6,null,0.5,null,0.5,null,null,null,null,null,0.5,0.5,null,null,0.5]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"36",null,"36",null,"36",null,"36",null,null,null,null,"36",null,"36",null,"36",null,null,null,null,null,"36","36",null,null,"36"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,0.7,null,0.5,null,0.3,null,0.2,null,null,null,null,0.2]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,5.1999998092651367,null,5.1999998092651367,null,5.1999998092651367,null,5.1999998092651367,null,null,null,null,5.1999998092651367,null,5.1999998092651367,null,5.1999998092651367,null,null,null,null,null,5.1999998092651367,5.1999998092651367,null,null,5.1999998092651367]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,1.7999999523162842,null,1.7999999523162842,null,1.7999999523162842,null,1.7999999523162842,null,null,null,null,1.7999999523162842,null,1.7999999523162842,null,1.7999999523162842,null,null,null,null,null,1.7999999523162842,1.7999999523162842,null,null,1.7999999523162842]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"TIER","index":267,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"TIER - Tieri (66/22kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"H015 - Lilyvale BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Capricornia"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/22kV 5MVA ON"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -1.1%, 2020 S -0.8% W -0.8%2021 S -0.8% W -0.8%2022 S -0.5% W -0.5%2023 S -0.8% W -0.8"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"2 MVA on 20/02/2019 at 19:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,10,null,10,null,10,null,10,null,null,null,null,10,null,10,null,10,null,null,null,null,null,10,10,null,null,10]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,2.2000000476837158,null,2.2000000476837158,null,2.2000000476837158,null,2.0999999046325684,null,null,null,null,2.0999999046325684,null,1.6000000238418579,null,1.6000000238418579,null,null,null,null,null,1.5,1.5,null,null,1.5]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.99,null,0.99,null,0.99,null,0.99,null,null,null,null,0.99,null,0.98899999999999999,null,0.98899999999999999,null,null,null,null,null,0.98899999999999999,0.98899999999999999,null,null,0.98899999999999999]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,5,null,5,null,5,null,5,null,null,null,null,5,null,5,null,5,null,null,null,null,null,5,5,null,null,5]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,2,null,1.8999999761581421,null,1.8999999761581421,null,1.8999999761581421,null,null,null,null,1.8999999761581421,null,1.3999999761581421,null,1.3999999761581421,null,null,null,null,null,1.2999999523162842,1.2999999523162842,null,null,1.2999999523162842]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.1,null,0.1,null,0.1,null,0.1,null,null,null,null,0.1,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"6",null,"6",null,"6",null,"6",null,null,null,null,"6",null,"6",null,"6",null,null,null,null,null,"6","6",null,null,"6"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"TOPO","index":268,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"TOPO - Townsville Port (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"TMES - Townsville Mesh"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Nth Queensland"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/11kV 19.2/24/32MVA ONAN/ODAN/ODAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.2%, 2020 S 0.3% W 0.3%, 2021 S 0.2% W 0.2%, 2022 S -0.0% W -0.0%2023 S -0.2% W -0.2"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"11.3 MVA on 18/12/2018 at 19:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,83.199996948242188,null,83.199996948242188,null,83.199996948242188,null,83.199996948242188,null,null,null,null,83.199996948242188,null,83.199996948242188,null,83.199996948242188,null,null,null,null,null,83.199996948242188,83.199996948242188,null,null,83.199996948242188]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,12.899999618530273,null,12.800000190734863,null,12.699999809265137,null,12.699999809265137,null,null,null,null,12.800000190734863,null,7.4000000953674316,null,7.5,null,null,null,null,null,7.5,7.4000000953674316,null,null,7.5]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.96199999999999997,null,0.96199999999999997,null,0.96199999999999997,null,0.96199999999999997,null,null,null,null,0.96199999999999997,null,0.93899999999999995,null,0.93899999999999995,null,null,null,null,null,0.93899999999999995,0.93899999999999995,null,null,0.93899999999999995]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,41.599998474121094,null,41.599998474121094,null,41.599998474121094,null,41.599998474121094,null,null,null,null,41.599998474121094,null,41.599998474121094,null,41.599998474121094,null,null,null,null,null,41.599998474121094,41.599998474121094,null,null,41.599998474121094]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,11.699999809265137,null,11.699999809265137,null,11.600000381469727,null,11.600000381469727,null,null,null,null,11.699999809265137,null,7.1999998092651367,null,7.1999998092651367,null,null,null,null,null,7.1999998092651367,7.1999998092651367,null,null,7.1999998092651367]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.6,null,0.6,null,0.6,null,0.6,null,null,null,null,0.6,null,0.4,null,0.4,null,null,null,null,null,0.4,0.4,null,null,0.4]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"24.5",null,"24.5",null,"24.5",null,"24.5",null,null,null,null,"24.5",null,"24.5",null,"24.5",null,null,null,null,null,"24.5","24.5",null,null,"24.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"TORQ","index":269,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"TORQ - Torquay (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T059 - Maryborough BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Wide Bay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/11kV 21/26.25/35MVA ONAN/ODAN/ODAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.8%, 2020 S 1.0% W 1.0%, 2021 S 1.0% W 1.0%, 2022 S 1.5% W 1.5%, 2023 S 1.2% W 1.2%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"26.8 MVA on 14/02/2019 at 18:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,91.099998474121094,null,91.099998474121094,null,91.099998474121094,null,91.099998474121094,null,null,null,null,91.099998474121094,null,99,null,99,null,null,null,null,null,99,99,null,null,99]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,31.899999618530273,null,32,null,32.200000762939453,null,32.700000762939453,null,null,null,null,33.299999237060547,null,26.799999237060547,null,27.100000381469727,null,null,null,null,null,27.200000762939453,27.600000381469727,null,null,28.100000381469727]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.998,null,0.998,null,0.998,null,0.998,null,null,null,null,0.998,null,0.98799999999999999,null,0.98799999999999999,null,null,null,null,null,0.98799999999999999,0.98799999999999999,null,null,0.98799999999999999]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,48.799999237060547,null,48.799999237060547,null,48.799999237060547,null,48.799999237060547,null,null,null,null,48.799999237060547,null,52.299999237060547,null,52.299999237060547,null,null,null,null,null,52.299999237060547,52.299999237060547,null,null,52.299999237060547]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,29.5,null,29.700000762939453,null,29.799999237060547,null,30.200000762939453,null,null,null,null,30.799999237060547,null,25,null,25.299999237060547,null,null,null,null,null,25.399999618530273,25.799999237060547,null,null,26.200000762939453]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,1.5,null,1.5,null,1.5,null,1.5,null,null,null,null,1.5,null,1.3,null,1.3,null,null,null,null,null,1.3,1.3,null,null,1.3]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"4",null,"4",null,"4",null,"4",null,null,null,null,"4",null,"4",null,"4",null,null,null,null,null,"4","4",null,null,"4"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"TORR","index":270,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"TORR - Torrington (33/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T116 - Torrington BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is South West"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x33/11kV 15/18.5/25 ONAN/ODAN/ODAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.5%, 2020 S -0.0% W -0.0%2021 S -0.2% W -0.2%2022 S 0.5% W 0.5%, 2023 S -0.1% W -0.1"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"22.6 MVA on 18/06/2018 at 07:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,56.700000762939453,null,56.700000762939453,null,56.700000762939453,null,56.700000762939453,null,null,null,null,56.700000762939453,null,67.5,null,67.5,null,null,null,null,null,67.5,67.5,null,null,67.5]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,24,null,23.899999618530273,null,23.799999237060547,null,23.799999237060547,null,null,null,null,24,null,23.700000762939453,null,23.700000762939453,null,null,null,null,null,23.5,23.600000381469727,null,null,23.700000762939453]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.94499999999999995,null,0.94499999999999995,null,0.94499999999999995,null,0.94499999999999995,null,null,null,null,0.94499999999999995,null,0.95899999999999996,null,0.95899999999999996,null,null,null,null,null,0.95899999999999996,0.95899999999999996,null,null,0.95899999999999996]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,31.600000381469727,null,31.600000381469727,null,31.600000381469727,null,31.600000381469727,null,null,null,null,31.600000381469727,null,37.400001525878906,null,37.400001525878906,null,null,null,null,null,37.400001525878906,37.400001525878906,null,null,37.400001525878906]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,21.399999618530273,null,21.299999237060547,null,21.200000762939453,null,21.200000762939453,null,null,null,null,21.399999618530273,null,22,null,22,null,null,null,null,null,21.899999618530273,21.899999618530273,null,null,22]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,1.1000000000000001,null,1.1000000000000001,null,1.1000000000000001,null,1.1000000000000001,null,null,null,null,1.1000000000000001,null,1.1000000000000001,null,1.1000000000000001,null,null,null,null,null,1.1000000000000001,1.1000000000000001,null,null,1.1000000000000001]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"32",null,"32",null,"32",null,"32",null,null,null,null,"32",null,"32",null,"32",null,null,null,null,null,"32","32",null,null,"32"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"TUAN","index":271,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"TUAN - Tuan (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T059 - Maryborough BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Wide Bay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/11kV 7.5/10MVA ONAN/ONAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.1%, 2020 S 0.4% W 0.4%, 2021 S 0.4% W 0.4%, 2022 S 0.4% W 0.4%, 2023 S 0.2% W 0.2%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"7.9 MVA on 18/06/2018 at 18:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,10.800000190734863,null,10.800000190734863,null,10.800000190734863,null,10.800000190734863,null,null,null,null,10.800000190734863,null,11.399999618530273,null,11.399999618530273,null,null,null,null,null,11.399999618530273,11.399999618530273,null,null,11.399999618530273]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,8.8999996185302734,null,9.8999996185302734,null,9.8000001907348633,null,9.8000001907348633,null,null,null,null,9.8999996185302734,null,7.8000001907348633,null,8.6999998092651367,null,null,null,null,null,9.5,9.6000003814697266,null,null,9.6000003814697266]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.86199999999999999,null,0.86199999999999999,null,0.86199999999999999,null,0.86199999999999999,null,null,null,null,0.86199999999999999,null,0.86499999999999999,null,0.86499999999999999,null,null,null,null,null,0.86499999999999999,0.86499999999999999,null,null,0.86499999999999999]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,8.6999998092651367,null,9.6999998092651367,null,9.6000003814697266,null,9.6000003814697266,null,null,null,null,9.6999998092651367,null,7.8000001907348633,null,8.6999998092651367,null,null,null,null,null,9.5,9.5,null,null,9.6000003814697266]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.4,null,0.5,null,0.5,null,0.5,null,null,null,null,0.5,null,0.4,null,0.4,null,null,null,null,null,0.5,0.5,null,null,0.5]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"16",null,"16",null,"16",null,"16",null,null,null,null,"16",null,"16",null,"16",null,null,null,null,null,"16","16",null,null,"16"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,8.6999999999999993,null,9.6999999999999993,null,9.6,null,9.6,null,null,null,null,9.6999999999999993,null,7.8,null,8.6999999999999993,null,null,null,null,null,9.5,9.5,null,null,9.6]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,2.0999999046325684,null,2.0999999046325684,null,2.0999999046325684,null,2.0999999046325684,null,null,null,null,2.0999999046325684,null,2.0999999046325684,null,2.0999999046325684,null,null,null,null,null,2.0999999046325684,2.0999999046325684,null,null,2.0999999046325684]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,1.6000000238418579,null,1.6000000238418579,null,1.6000000238418579,null,1.6000000238418579,null,null,null,null,1.6000000238418579,null,1.6000000238418579,null,1.6000000238418579,null,null,null,null,null,1.6000000238418579,1.6000000238418579,null,null,1.6000000238418579]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,6,null,6,null,6,null,6,null,null,null,null,6,null,6,null,6,null,null,null,null,null,6,6,null,null,6]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"TWCE","index":272,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"TWCE - Toowoomba Central (110/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"QMRG - Middle Ridge (Ergon) TCP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is South West"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x40MVA 110/11kV Transformer"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -1.7%, 2020 S -0.5% W -0.5%2021 S -0.8% W -0.8%2022 S -0.6% W -0.6%2023 S -0.7% W -0.7"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"23 MVA on 13/12/2018 at 14:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,84,null,84,null,84,null,84,null,null,null,null,84,null,84,null,84,null,null,null,null,null,84,84,null,null,84]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,25,null,24.700000762939453,null,24.299999237060547,null,24.200000762939453,null,null,null,null,24.100000381469727,null,17.399999618530273,null,17.299999237060547,null,null,null,null,null,17.100000381469727,17,null,null,16.899999618530273]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.95,null,0.95,null,0.95,null,0.95,null,null,null,null,0.95,null,0.96,null,0.96,null,null,null,null,null,0.96,0.96,null,null,0.96]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,44,null,44,null,44,null,44,null,null,null,null,44,null,46,null,46,null,null,null,null,null,46,46,null,null,46]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,23,null,22.700000762939453,null,22.399999618530273,null,22.200000762939453,null,null,null,null,22.200000762939453,null,16.5,null,16.399999618530273,null,null,null,null,null,16.100000381469727,16,null,null,16]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,1.2,null,1.1000000000000001,null,1.1000000000000001,null,1.1000000000000001,null,null,null,null,1.1000000000000001,null,0.8,null,0.8,null,null,null,null,null,0.8,0.8,null,null,0.8]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"15",null,"15",null,"15",null,"15",null,null,null,null,"15",null,"15",null,"15",null,null,null,null,null,"15","15",null,null,"15"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"VERM","index":273,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"VERM - Vermont (66/22kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T035 - Dysart BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Capricornia"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/22kV 10MVA ONAN;1xVERMSS TRANSF 2"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -4.3%, 2020 S -1.0% W -1.0%2021 S -1.0% W -1.0%2022 S -0.5% W -0.5%2023 S -0.5% W -0.5"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"10.9 MVA on 15/11/2018 at 14:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,22.100000381469727,null,22.100000381469727,null,22.100000381469727,null,22.100000381469727,null,null,null,null,22.100000381469727,null,24.299999237060547,null,24.299999237060547,null,null,null,null,null,24.299999237060547,24.299999237060547,null,null,24.299999237060547]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,11.5,null,11.300000190734863,null,11.100000381469727,null,11.100000381469727,null,null,null,null,11.199999809265137,null,9.8000001907348633,null,9.6999998092651367,null,null,null,null,null,9.6000003814697266,9.5,null,null,9.5]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.93200000000000005,null,0.93200000000000005,null,0.93200000000000005,null,0.93200000000000005,null,null,null,null,0.93200000000000005,null,0.93600000000000005,null,0.93600000000000005,null,null,null,null,null,0.93600000000000005,0.93600000000000005,null,null,0.93600000000000005]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,13.699999809265137,null,13.699999809265137,null,13.699999809265137,null,13.699999809265137,null,null,null,null,13.699999809265137,null,14.699999809265137,null,14.699999809265137,null,null,null,null,null,14.699999809265137,14.699999809265137,null,null,14.699999809265137]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,11.199999809265137,null,11,null,10.899999618530273,null,10.800000190734863,null,null,null,null,10.899999618530273,null,9.8000001907348633,null,9.6999998092651367,null,null,null,null,null,9.5,9.5,null,null,9.5]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.6,null,0.6,null,0.5,null,0.5,null,null,null,null,0.5,null,0.5,null,0.5,null,null,null,null,null,0.5,0.5,null,null,0.5]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"174.5",null,"174.5",null,"174.5",null,"174.5",null,null,null,null,"174.5",null,"174.5",null,"174.5",null,null,null,null,null,"174.5","174.5",null,null,"174.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"VICT","index":274,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"VICT - Victoria (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T047 - Ingham BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Nth Queensland"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/11kV 6.3MVA ON"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.8%, 2020 S -0.5% W -0.5%2021 S -0.6% W -0.6%2022 S -1.1% W -1.1%2023 S -1.3% W -1.3"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"2.1 MVA on 20/02/2019 at 19:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,0,null,0,null,7.56,null,7.6,null,null,null,null,7.6,null,7.6,null,7.6,null,null,null,null,null,7.6,7.6,null,null,7.6]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,0,null,0,null,3.5999999046325684,null,3.5,null,null,null,null,3.5,null,0,null,0,null,null,null,null,null,3.0999999046325684,3,null,null,3]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0,null,0,null,0.96399999999999997,null,0.96399999999999997,null,null,null,null,0.96399999999999997,null,0.95799999999999996,null,0.95699999999999996,null,null,null,null,null,0.95799999999999996,0.95799999999999996,null,null,0.95699999999999996]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,0,null,0,null,3.2000000476837158,null,3.2000000476837158,null,null,null,null,3.0999999046325684,null,3.0999999046325684,null,3.0999999046325684,null,null,null,null,null,3,3,null,null,3]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0,null,0,null,0.2,null,0.2,null,null,null,null,0.2,null,0.2,null,0.2,null,null,null,null,null,0.2,0.2,null,null,0.2]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,0,null,0,null,"4.5",null,"4.5",null,null,null,null,"4.5",null,"4.5",null,"4.5",null,null,null,null,null,"4.5","4.5",null,null,"4.5"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,0,null,0,null,3.2,null,3.2,null,null,null,null,3.1,null,3.1,null,3.1,null,null,null,null,null,3,3,null,null,3]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,3.2999999523162842,null,3.2999999523162842,null,null,null,null,3.2999999523162842,null,3.2999999523162842,null,3.2999999523162842,null,null,null,null,null,3.2999999523162842,3.2999999523162842,null,null,3.2999999523162842]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"WAEA","index":275,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"WAEA - Warwick East (33/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T058 - Warwick BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is South West"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x33/11kV 25/32MVA ONAN/ODAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.8%, 2020 S -1.0% W -1.0%2021 S -0.8% W -0.8%2022 S -0.6% W -0.6%2023 S -0.9% W -0.9"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"16.8 MVA on 13/02/2019 at 16:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,69.599998474121094,null,69.599998474121094,null,69.599998474121094,null,69.599998474121094,null,null,null,null,69.599998474121094,null,79.199996948242188,null,79.199996948242188,null,null,null,null,null,79.199996948242188,79.199996948242188,null,null,79.199996948242188]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,20.899999618530273,null,20.600000381469727,null,20.299999237060547,null,20.100000381469727,null,null,null,null,20.100000381469727,null,18.5,null,18.299999237060547,null,null,null,null,null,18.100000381469727,18,null,null,17.899999618530273]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.94199999999999995,null,0.94199999999999995,null,0.94199999999999995,null,0.94199999999999995,null,null,null,null,0.94199999999999995,null,0.97699999999999998,null,0.97699999999999998,null,null,null,null,null,0.97699999999999998,0.97699999999999998,null,null,0.97699999999999998]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,38.799999237060547,null,38.799999237060547,null,38.799999237060547,null,38.799999237060547,null,null,null,null,38.799999237060547,null,42.200000762939453,null,42.200000762939453,null,null,null,null,null,42.200000762939453,42.200000762939453,null,null,42.200000762939453]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,18.100000381469727,null,17.899999618530273,null,17.600000381469727,null,17.5,null,null,null,null,17.399999618530273,null,17.399999618530273,null,17.200000762939453,null,null,null,null,null,17,16.899999618530273,null,null,16.799999237060547]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.9,null,0.9,null,0.9,null,0.9,null,null,null,null,0.9,null,0.9,null,0.9,null,null,null,null,null,0.9,0.8,null,null,0.8]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"178",null,"178",null,"178",null,"178",null,null,null,null,"178",null,"178",null,"178",null,null,null,null,null,"178","178",null,null,"178"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"WALL","index":276,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"WALL - Wallaville (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T020 - Bundaberg BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Wide Bay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/11kV 8/10MVA ONAN/ONAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.1%, 2020 S 0.3% W 0.3%, 2021 S 0.2% W 0.2%, 2022 S 0.1% W 0.1%, 2023 S -0.0% W -0.0"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"8.2 MVA on 20/02/2019 at 18:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,25.600000381469727,null,25.600000381469727,null,25.600000381469727,null,25.600000381469727,null,null,null,null,25.600000381469727,null,27,null,27,null,null,null,null,null,27,27,null,null,27]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,9.5,null,9.5,null,9.3999996185302734,null,9.3999996185302734,null,null,null,null,9.5,null,6,null,6,null,null,null,null,null,6,6,null,null,6]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.996,null,0.996,null,0.996,null,0.996,null,null,null,null,0.996,null,0.93200000000000005,null,0.93200000000000005,null,null,null,null,null,0.93200000000000005,0.93200000000000005,null,null,0.93200000000000005]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,14.699999809265137,null,14.699999809265137,null,14.699999809265137,null,14.699999809265137,null,null,null,null,14.699999809265137,null,15,null,15,null,null,null,null,null,15,15,null,null,15]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,9,null,8.8999996185302734,null,8.8999996185302734,null,8.8999996185302734,null,null,null,null,8.8999996185302734,null,5.5999999046325684,null,5.5999999046325684,null,null,null,null,null,5.5999999046325684,5.5999999046325684,null,null,5.5999999046325684]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.5,null,0.4,null,0.4,null,0.4,null,null,null,null,0.4,null,0.3,null,0.3,null,null,null,null,null,0.3,0.3,null,null,0.3]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"12.5",null,"12.5",null,"12.5",null,"12.5",null,null,null,null,"12.5",null,"12.5",null,"12.5",null,null,null,null,null,"12.5","12.5",null,null,"12.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"WAND","index":277,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"WAND - Wandoan (33/22kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T194 - Columboola BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is South West"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x33/22kV 5MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.5%, 2020 S 0.1% W 0.1%, 2021 S -0.0% W -0.0%2022 S -0.3% W -0.3%2023 S -0.5% W -0.5"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"2.8 MVA on 13/02/2019 at 19:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,12.199999809265137,null,12.199999809265137,null,12.199999809265137,null,12.199999809265137,null,null,null,null,12.199999809265137,null,14.5,null,14.5,null,null,null,null,null,14.5,14.5,null,null,14.5]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,3.0999999046325684,null,3,null,3.0999999046325684,null,3.0999999046325684,null,null,null,null,3.0999999046325684,null,2.7000000476837158,null,2.7000000476837158,null,null,null,null,null,2.7000000476837158,2.7000000476837158,null,null,2.7000000476837158]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.998,null,0.995,null,0.998,null,0.998,null,null,null,null,0.998,null,0.99199999999999999,null,0.99199999999999999,null,null,null,null,null,0.99199999999999999,0.99199999999999999,null,null,0.99199999999999999]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,7.0999999046325684,null,7.0999999046325684,null,7.0999999046325684,null,7.0999999046325684,null,null,null,null,7.0999999046325684,null,7.5,null,7.5,null,null,null,null,null,7.5,7.5,null,null,7.5]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,2.9000000953674316,null,2.7999999523162842,null,2.7999999523162842,null,2.7999999523162842,null,null,null,null,2.7999999523162842,null,2.5,null,2.5,null,null,null,null,null,2.5,2.5,null,null,2.5]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.1,null,0.1,null,0.1,null,0.1,null,null,null,null,0.1,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"14",null,"14",null,"14",null,"14",null,null,null,null,"14",null,"14",null,"14",null,null,null,null,null,"14","14",null,null,"14"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"WEBU","index":278,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"WEBU - West Bundaberg (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T020 - Bundaberg BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Wide Bay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/11kV 15/18/25MVA ONAN/ODAN/ODAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -1.0%, 2020 S -1.0% W -1.0%2021 S -0.9% W -0.9%2022 S -0.8% W -0.8%2023 S -0.8% W -0.8"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"29.7 MVA on 13/02/2019 at 15:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,61.299999237060547,null,61.299999237060547,null,61.299999237060547,null,61.299999237060547,null,null,null,null,61.299999237060547,null,65,null,65,null,null,null,null,null,65,65,null,null,65]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,30.399999618530273,null,30,null,29.399999618530273,null,29.200000762939453,null,null,null,null,29.200000762939453,null,23,null,22.700000762939453,null,null,null,null,null,22.5,22.299999237060547,null,null,22.200000762939453]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.998,null,0.999,null,0.999,null,0.999,null,null,null,null,0.999,null,0.999,null,0.998,null,null,null,null,null,0.998,0.998,null,null,0.998]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,34.299999237060547,null,34.299999237060547,null,34.299999237060547,null,34.299999237060547,null,null,null,null,34.299999237060547,null,36.5,null,36.5,null,null,null,null,null,36.5,36.5,null,null,36.5]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,27.799999237060547,null,27.399999618530273,null,26.899999618530273,null,26.700000762939453,null,null,null,null,26.700000762939453,null,21.899999618530273,null,21.700000762939453,null,null,null,null,null,21.399999618530273,21.200000762939453,null,null,21.100000381469727]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,1.4,null,1.4,null,1.3,null,1.3,null,null,null,null,1.3,null,1.1000000000000001,null,1.1000000000000001,null,null,null,null,null,1.1000000000000001,1.1000000000000001,null,null,1.1000000000000001]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"7",null,"7",null,"7",null,"7",null,null,null,null,"7",null,"7",null,"7",null,null,null,null,null,"7","7",null,null,"7"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"WEDA","index":279,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"WEDA - West Dalby (33/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T002 - Dalby East BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is South West"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x33/11KV 6.25MVA ONAN;1x33/11KV 6.3MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -3.3%, 2020 S -2.2% W -2.2%2021 S -2.5% W -2.5%2022 S -1.6% W -1.6%2023 S -2.2% W -2.2"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"5.1 MVA on 13/02/2019 at 13:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,14.600000381469727,null,14.600000381469727,null,14.600000381469727,null,14.600000381469727,null,null,null,null,14.600000381469727,null,17.5,null,17.5,null,null,null,null,null,17.5,17.5,null,null,17.5]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,6.1999998092651367,null,6,null,5.9000000953674316,null,5.8000001907348633,null,null,null,null,5.6999998092651367,null,4.8000001907348633,null,4.6999998092651367,null,null,null,null,null,4.5999999046325684,4.5,null,null,4.3000001907348633]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.90100000000000002,null,0.90100000000000002,null,0.90100000000000002,null,0.90100000000000002,null,null,null,null,0.90100000000000002,null,0.89800000000000002,null,0.89800000000000002,null,null,null,null,null,0.89800000000000002,0.89800000000000002,null,null,0.89500000000000002]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,8.1999998092651367,null,8.1999998092651367,null,8.1999998092651367,null,8.1999998092651367,null,null,null,null,8.1999998092651367,null,9.3000001907348633,null,9.3000001907348633,null,null,null,null,null,9.3000001907348633,9.3000001907348633,null,null,9.3000001907348633]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,5.4000000953674316,null,5.3000001907348633,null,5.0999999046325684,null,5,null,null,null,null,5,null,4.5,null,4.4000000953674316,null,null,null,null,null,4.3000001907348633,4.1999998092651367,null,null,4.0999999046325684]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.3,null,0.3,null,0.3,null,0.3,null,null,null,null,0.3,null,0.2,null,0.2,null,null,null,null,null,0.2,0.2,null,null,0.2]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"4.5",null,"4.5",null,"4.5",null,"4.5",null,null,null,null,"4.5",null,"4.5",null,"4.5",null,null,null,null,null,"4.5","4.5",null,null,"4.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"WEMA","index":280,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"WEMA - West Mackay (33/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T038 - Mackay BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Mackay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x33/11kV 15/20MVA ONAN/ONAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.8%, 2020 S -0.3% W -0.3%2021 S -0.2% W -0.2%2022 S -0.1% W -0.1%2023 S -0.5% W -0.5"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"18.8 MVA on 28/11/2018 at 15:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,38.700000762939453,null,38.700000762939453,null,38.700000762939453,null,38.700000762939453,null,null,null,null,38.700000762939453,null,40.900001525878906,null,40.900001525878906,null,null,null,null,null,40.900001525878906,40.900001525878906,null,null,40.900001525878906]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,21,null,20.899999618530273,null,20.600000381469727,null,20.600000381469727,null,null,null,null,20.600000381469727,null,11.199999809265137,null,11.199999809265137,null,null,null,null,null,11.100000381469727,11.100000381469727,null,null,11.100000381469727]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.96599999999999997,null,0.96599999999999997,null,0.96599999999999997,null,0.96599999999999997,null,null,null,null,0.96599999999999997,null,0.96699999999999997,null,0.96699999999999997,null,null,null,null,null,0.96699999999999997,0.96699999999999997,null,null,0.96699999999999997]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,22.299999237060547,null,22.299999237060547,null,22.299999237060547,null,22.299999237060547,null,null,null,null,22.299999237060547,null,23.399999618530273,null,23.399999618530273,null,null,null,null,null,23.399999618530273,23.399999618530273,null,null,23.399999618530273]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,18.600000381469727,null,18.5,null,18.299999237060547,null,18.299999237060547,null,null,null,null,18.299999237060547,null,10.899999618530273,null,10.899999618530273,null,null,null,null,null,10.800000190734863,10.800000190734863,null,null,10.800000190734863]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.9,null,0.9,null,0.9,null,0.9,null,null,null,null,0.9,null,0.5,null,0.5,null,null,null,null,null,0.5,0.5,null,null,0.5]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"9.5",null,"9.5",null,"9.5",null,"9.5",null,null,null,null,"9.5",null,"9.5",null,"9.5",null,null,null,null,null,"9.5","9.5",null,null,"9.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"WETO","index":281,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"WETO - West Toowoomba (33/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T116 - Torrington BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is South West"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 3x33/11kV 10MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.9%, 2020 S -0.9% W -0.9%2021 S -1.0% W -1.0%2022 S -1.2% W -1.2%2023 S -1.5% W -1.5"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"22.4 MVA on 09/07/2018 at 18:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,30,null,30,null,30,null,30,null,null,null,null,30,null,36.200000762939453,null,36.200000762939453,null,null,null,null,null,36.200000762939453,36.200000762939453,null,null,36.200000762939453]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,21.799999237060547,null,21.399999618530273,null,21,null,20.700000762939453,null,null,null,null,20.600000381469727,null,26.5,null,26.299999237060547,null,null,null,null,null,25.899999618530273,25.600000381469727,null,null,25.299999237060547]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.96099999999999997,null,0.96099999999999997,null,0.96099999999999997,null,0.96099999999999997,null,null,null,null,0.96099999999999997,null,0.98099999999999998,null,0.98099999999999998,null,null,null,null,null,0.98099999999999998,0.98099999999999998,null,null,0.98099999999999998]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,23.799999237060547,null,23.799999237060547,null,23.799999237060547,null,23.799999237060547,null,null,null,null,23.799999237060547,null,26.899999618530273,null,26.899999618530273,null,null,null,null,null,26.899999618530273,26.899999618530273,null,null,26.899999618530273]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,19.100000381469727,null,18.899999618530273,null,18.5,null,18.200000762939453,null,null,null,null,18.100000381469727,null,24.299999237060547,null,24,null,null,null,null,null,23.700000762939453,23.399999618530273,null,null,23.100000381469727]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,1,null,0.9,null,0.9,null,0.9,null,null,null,null,0.9,null,1.2,null,1.2,null,null,null,null,null,1.2,1.2,null,null,1.2]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"9",null,"9",null,"9",null,"9",null,null,null,null,"9",null,"9",null,"9",null,null,null,null,null,"9","9",null,null,"9"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,6,null,6,null,6,null,6,null,null,null,null,6,null,6,null,6,null,null,null,null,null,6,6,null,null,6]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"WEWA","index":282,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"WEWA - West Warwick (33/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T058 - Warwick BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is South West"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x33/11kV 10/12.5MVA ONAN/ONAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.9%, 2020 S -0.4% W -0.4%2021 S -0.2% W -0.2%2022 S 0.2% W 0.2%, 2023 S -0.2% W -0.2"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"12 MVA on 16/01/2019 at 16:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,27,null,27,null,27,null,27,null,null,null,null,27,null,30,null,30,null,null,null,null,null,30,30,null,null,30]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,15.100000381469727,null,15,null,14.899999618530273,null,14.899999618530273,null,null,null,null,14.899999618530273,null,11.100000381469727,null,11,null,null,null,null,null,10.899999618530273,10.899999618530273,null,null,11]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.99,null,0.99,null,0.99,null,0.99099999999999999,null,null,null,null,0.99,null,0.97199999999999998,null,0.97199999999999998,null,null,null,null,null,0.97199999999999998,0.97199999999999998,null,null,0.97199999999999998]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,15.199999809265137,null,15.199999809265137,null,15.199999809265137,null,15.199999809265137,null,null,null,null,15.199999809265137,null,16.899999618530273,null,16.899999618530273,null,null,null,null,null,16.899999618530273,16.899999618530273,null,null,16.899999618530273]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,12.699999809265137,null,12.600000381469727,null,12.5,null,12.5,null,null,null,null,12.600000381469727,null,10.100000381469727,null,10,null,null,null,null,null,9.8999996185302734,10,null,null,10]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.6,null,0.6,null,0.6,null,0.6,null,null,null,null,0.6,null,0.5,null,0.5,null,null,null,null,null,0.5,0.5,null,null,0.5]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"52.5",null,"52.5",null,"52.5",null,"52.5",null,null,null,null,"52.5",null,"52.5",null,"52.5",null,null,null,null,null,"52.5","52.5",null,null,"52.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"WINT","index":283,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"WINT - Winton (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T095 - Millchester BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Nth Queensland"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/11kV 4MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.2%, 2020 S 0.1% W 0.1%, 2021 S 0.1% W 0.1%, 2022 S -0.5% W -0.5%2023 S -0.8% W -0.8"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"2.7 MVA on 25/11/2018 at 17:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,9.3999996185302734,null,9.3999996185302734,null,9.3999996185302734,null,9.3999996185302734,null,null,null,null,9.3999996185302734,null,10.899999618530273,null,10.899999618530273,null,null,null,null,null,10.899999618530273,10.899999618530273,null,null,10.899999618530273]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,3.2999999523162842,null,3.2999999523162842,null,3.2000000476837158,null,3.2000000476837158,null,null,null,null,3.2000000476837158,null,2.2000000476837158,null,2.2000000476837158,null,null,null,null,null,2.2000000476837158,2.2000000476837158,null,null,2.2000000476837158]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.98799999999999999,null,0.98799999999999999,null,0.98799999999999999,null,0.98799999999999999,null,null,null,null,0.98799999999999999,null,0.99099999999999999,null,0.99099999999999999,null,null,null,null,null,0.99099999999999999,0.99099999999999999,null,null,0.99099999999999999]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,5.4000000953674316,null,5.4000000953674316,null,5.4000000953674316,null,5.4000000953674316,null,null,null,null,5.4000000953674316,null,6,null,6,null,null,null,null,null,6,6,null,null,6]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,3,null,3,null,3,null,3,null,null,null,null,3,null,2,null,2,null,null,null,null,null,2,1.8999999761581421,null,null,1.8999999761581421]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.2,null,0.2,null,0.2,null,0.2,null,null,null,null,0.2,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"14",null,"14",null,"14",null,"14",null,null,null,null,"14",null,"14",null,"14",null,null,null,null,null,"14","14",null,null,"14"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"WOOD","index":284,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"WOOD - Woodhouse Station (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T193 - Clare South BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Nth Queensland"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/11kV 0.25MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.0%, 2020 S 0.0% W 0.0%, 2021 S 0.0% W 0.0%, 2022 S 0.0% W 0.0%, 2023 S 0.0% W 0.0%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"0.1 MVA on 01/06/2019 at 17:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,0.30000001192092896,null,0.30000001192092896,null,0.30000001192092896,null,0.30000001192092896,null,null,null,null,0.30000001192092896,null,0.30000001192092896,null,0.30000001192092896,null,null,null,null,null,0.30000001192092896,0.30000001192092896,null,null,0.30000001192092896]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,0.10000000149011612,null,0.10000000149011612,null,0.10000000149011612,null,0.10000000149011612,null,null,null,null,0.10000000149011612,null,0.10000000149011612,null,0.10000000149011612,null,null,null,null,null,0.10000000149011612,0.10000000149011612,null,null,0.10000000149011612]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.85,null,0.85,null,0.85,null,0.85,null,null,null,null,0.85,null,0.85,null,0.85,null,null,null,null,null,0.85,0.85,null,null,0.85]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,0.10000000149011612,null,0.10000000149011612,null,0.10000000149011612,null,0.10000000149011612,null,null,null,null,0.10000000149011612,null,0.10000000149011612,null,0.10000000149011612,null,null,null,null,null,0.10000000149011612,0.10000000149011612,null,null,0.10000000149011612]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"0",null,"0",null,"0",null,"0",null,null,null,null,"0",null,"0",null,"0",null,null,null,null,null,"0","0",null,null,"0"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,0.1,null,0.1,null,0.1,null,0.1,null,null,null,null,0.1,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0.10000000149011612,null,0.10000000149011612,null,0.10000000149011612,null,0.10000000149011612,null,null,null,null,0.10000000149011612,null,0.10000000149011612,null,0.10000000149011612,null,null,null,null,null,0.10000000149011612,0.10000000149011612,null,null,0.10000000149011612]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"WOOG","index":285,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"WOOG - Woodgate (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T131 - Isis BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Wide Bay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x66/11kV 5MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 1.1%, 2020 S 1.2% W 1.2%, 2021 S 1.2% W 1.2%, 2022 S 1.0% W 1.0%, 2023 S 0.9% W 0.9%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"2.4 MVA on 29/12/2018 at 19:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,5.3000001907348633,null,5.3000001907348633,null,5.3000001907348633,null,5.3000001907348633,null,null,null,null,5.3000001907348633,null,5.3000001907348633,null,5.3000001907348633,null,null,null,null,null,5.3000001907348633,5.3000001907348633,null,null,5.3000001907348633]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,2.5999999046325684,null,2.5999999046325684,null,2.7000000476837158,null,2.7000000476837158,null,null,null,null,2.7000000476837158,null,2.4000000953674316,null,2.4000000953674316,null,null,null,null,null,2.4000000953674316,2.5,null,null,2.5]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.97499999999999998,null,0.97499999999999998,null,0.97499999999999998,null,0.97499999999999998,null,null,null,null,0.97499999999999998,null,0.97699999999999998,null,0.97699999999999998,null,null,null,null,null,0.97699999999999998,0.97699999999999998,null,null,0.97699999999999998]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,2.4000000953674316,null,2.4000000953674316,null,2.4000000953674316,null,2.4000000953674316,null,null,null,null,2.5,null,2.2000000476837158,null,2.2000000476837158,null,null,null,null,null,2.2000000476837158,2.2000000476837158,null,null,2.2999999523162842]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.1,null,0.1,null,0.1,null,0.1,null,null,null,null,0.1,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"8",null,"8",null,"8",null,"8",null,null,null,null,"8",null,"8",null,"8",null,null,null,null,null,"8","8",null,null,"8"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,2.4,null,2.4,null,2.4,null,2.4,null,null,null,null,2.5,null,2.2000000000000002,null,2.2000000000000002,null,null,null,null,null,2.2000000000000002,2.2000000000000002,null,null,2.2999999999999998]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,2.2000000476837158,null,2.2000000476837158,null,2.2000000476837158,null,2.2000000476837158,null,null,null,null,2.2000000476837158,null,2.2000000476837158,null,2.2000000476837158,null,null,null,null,null,2.2000000476837158,2.2000000476837158,null,null,2.2000000476837158]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0.60000002384185791,null,0.60000002384185791,null,0.60000002384185791,null,0.60000002384185791,null,null,null,null,0.60000002384185791,null,0.60000002384185791,null,0.60000002384185791,null,null,null,null,null,0.60000002384185791,0.60000002384185791,null,null,0.60000002384185791]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"WOOL","index":286,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"WOOL - Woolooga (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T012 - Kilkivan BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Wide Bay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/11kV 5/6.25MVA ONAN/ONAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.0%, 2020 S 0.3% W 0.3%, 2021 S 0.5% W 0.5%, 2022 S 0.3% W 0.3%, 2023 S -0.0% W -0.0"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"4.4 MVA on 13/02/2019 at 18:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,17.700000762939453,null,17.700000762939453,null,17.700000762939453,null,17.700000762939453,null,null,null,null,17.700000762939453,null,18.700000762939453,null,18.700000762939453,null,null,null,null,null,18.700000762939453,18.700000762939453,null,null,18.700000762939453]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,5.1999998092651367,null,5.1999998092651367,null,5.1999998092651367,null,5.1999998092651367,null,null,null,null,5.1999998092651367,null,3.5,null,3.5,null,null,null,null,null,3.5,3.5,null,null,3.5]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.95799999999999996,null,0.95799999999999996,null,0.95799999999999996,null,0.95799999999999996,null,null,null,null,0.95799999999999996,null,0.97599999999999998,null,0.97599999999999998,null,null,null,null,null,0.97599999999999998,0.97599999999999998,null,null,0.97599999999999998]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,9.3000001907348633,null,9.3000001907348633,null,9.3000001907348633,null,9.3000001907348633,null,null,null,null,9.3000001907348633,null,9.3000001907348633,null,9.3000001907348633,null,null,null,null,null,9.3000001907348633,9.3000001907348633,null,null,9.3000001907348633]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,4.5,null,4.5,null,4.5,null,4.5,null,null,null,null,4.5,null,3.2999999523162842,null,3.2999999523162842,null,null,null,null,null,3.2999999523162842,3.2999999523162842,null,null,3.2999999523162842]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.2,null,0.2,null,0.2,null,0.2,null,null,null,null,0.2,null,0.2,null,0.2,null,null,null,null,null,0.2,0.2,null,null,0.2]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"7",null,"7",null,"7",null,"7",null,null,null,null,"7",null,"7",null,"7",null,null,null,null,null,"7","7",null,null,"7"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"WOSO","index":287,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"WOSO - Woodstock South (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"TMES - Townsville Mesh"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Nth Queensland"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1xWOSO TX01 66/11kV TRANSF 1"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 2.2%, 2020 S 2.3% W 2.3%, 2021 S 2.2% W 2.2%, 2022 S 4.8% W 4.8%, 2023 S 4.3% W 4.3%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"1.3 MVA on 26/11/2018 at 19:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,8.6000003814697266,null,8.6000003814697266,null,8.6000003814697266,null,8.6000003814697266,null,null,null,null,8.6000003814697266,null,9.3999996185302734,null,9.3999996185302734,null,null,null,null,null,9.3999996185302734,9.3999996185302734,null,null,9.3999996185302734]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,1.2999999523162842,null,1.2999999523162842,null,1.3999999761581421,null,1.3999999761581421,null,null,null,null,1.5,null,0.89999997615814209,null,0.89999997615814209,null,null,null,null,null,1,1.1000000238418579,null,null,1.1000000238418579]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.97699999999999998,null,0.97699999999999998,null,0.97699999999999998,null,0.97699999999999998,null,null,null,null,0.97699999999999998,null,0.92900000000000005,null,0.92900000000000005,null,null,null,null,null,0.94699999999999995,0.94699999999999995,null,null,0.94699999999999995]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,1.2000000476837158,null,1.2000000476837158,null,1.2000000476837158,null,1.2999999523162842,null,null,null,null,1.3999999761581421,null,0.89999997615814209,null,0.89999997615814209,null,null,null,null,null,1,1,null,null,1.1000000238418579]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.1,null,0.1,null,0.1,null,0.1,null,null,null,null,0.1,null,0,null,0,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"8",null,"8",null,"8",null,"8",null,null,null,null,"8",null,"8",null,"8",null,null,null,null,null,"8","8",null,null,"8"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,1.2,null,1.2,null,1.2,null,1.3,null,null,null,null,1.4,null,0.9,null,0.9,null,null,null,null,null,1,1,null,null,1.1000000000000001]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,1.7999999523162842,null,1.7999999523162842,null,1.7999999523162842,null,1.7999999523162842,null,null,null,null,1.7999999523162842,null,1.7999999523162842,null,1.7999999523162842,null,null,null,null,null,1.7999999523162842,1.7999999523162842,null,null,1.7999999523162842]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"WOWA","index":288,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"WOWA - Wowan (66/22kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T026 - Biloela BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Capricornia"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/22kV 5/6.3MVA ONAN/ONAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.8%, 2020 S -0.5% W -0.5%2021 S -0.6% W -0.6%2022 S -0.5% W -0.5%2023 S -0.5% W -0.5"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"5.5 MVA on 19/02/2019 at 19:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,16.100000381469727,null,16.100000381469727,null,16.100000381469727,null,16.100000381469727,null,null,null,null,16.100000381469727,null,18,null,18,null,null,null,null,null,18,18,null,null,18]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,6.0999999046325684,null,6.0999999046325684,null,6,null,5.9000000953674316,null,null,null,null,5.9000000953674316,null,4.9000000953674316,null,4.8000001907348633,null,null,null,null,null,4.8000001907348633,4.8000001907348633,null,null,4.8000001907348633]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.98,null,0.98,null,0.98,null,0.98,null,null,null,null,0.98,null,0.99299999999999999,null,0.99299999999999999,null,null,null,null,null,0.99299999999999999,0.99299999999999999,null,null,0.99299999999999999]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,9,null,9,null,9,null,9,null,null,null,null,9,null,9.3999996185302734,null,9.3999996185302734,null,null,null,null,null,9.3999996185302734,9.3999996185302734,null,null,9.3999996185302734]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,5.5,null,5.5,null,5.4000000953674316,null,5.4000000953674316,null,null,null,null,5.4000000953674316,null,4.5999999046325684,null,4.5999999046325684,null,null,null,null,null,4.5,4.5,null,null,4.5]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.3,null,0.3,null,0.3,null,0.3,null,null,null,null,0.3,null,0.2,null,0.2,null,null,null,null,null,0.2,0.2,null,null,0.2]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"8",null,"8",null,"8",null,"8",null,null,null,null,"8",null,"8",null,"8",null,null,null,null,null,"8","8",null,null,"8"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"YARR","index":289,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"YARR - Yarraman (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"H018 - Tarong BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Wide Bay"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/11kV 5/6MVA ON/ONB"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -0.2%, 2020 S 0.2% W 0.2%, 2021 S 0.2% W 0.2%, 2022 S 0.4% W 0.4%, 2023 S 0.1% W 0.1%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"4.1 MVA on 27/06/2018 at 17:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,15.5,null,15.5,null,15.5,null,15.5,null,null,null,null,15.5,null,17.899999618530273,null,17.899999618530273,null,null,null,null,null,17.899999618530273,17.899999618530273,null,null,17.899999618530273]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,3.7999999523162842,null,3.7999999523162842,null,3.7999999523162842,null,3.7999999523162842,null,null,null,null,3.7999999523162842,null,4.5999999046325684,null,4.5999999046325684,null,null,null,null,null,4.5999999046325684,4.5999999046325684,null,null,4.6999998092651367]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.95499999999999996,null,0.95499999999999996,null,0.95499999999999996,null,0.95499999999999996,null,null,null,null,0.95499999999999996,null,0.96099999999999997,null,0.96099999999999997,null,null,null,null,null,0.96099999999999997,0.96099999999999997,null,null,0.96099999999999997]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,8.5,null,8.5,null,8.5,null,8.5,null,null,null,null,8.5,null,9,null,9,null,null,null,null,null,9,9,null,null,9]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,3.4000000953674316,null,3.4000000953674316,null,3.4000000953674316,null,3.4000000953674316,null,null,null,null,3.4000000953674316,null,4.4000000953674316,null,4.4000000953674316,null,null,null,null,null,4.4000000953674316,4.4000000953674316,null,null,4.4000000953674316]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.2,null,0.2,null,0.2,null,0.2,null,null,null,null,0.2,null,0.2,null,0.2,null,null,null,null,null,0.2,0.2,null,null,0.2]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"7.5",null,"7.5",null,"7.5",null,"7.5",null,null,null,null,"7.5",null,"7.5",null,"7.5",null,null,null,null,null,"7.5","7.5",null,null,"7.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"YASO","index":290,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"YASO - Yarranlea South (33/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"T010 - Yarranlea BSP"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is South West"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 1x33/11kV 1.5MVA ONAN;1x33/11kV 1MVA ONAN"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W -1.0%, 2020 S 0.0% W 0.0%, 2021 S -0.1% W -0.1%2022 S -0.3% W -0.3%2023 S -0.6% W -0.6"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"1.6 MVA on 13/02/2019 at 16:00"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,2.7999999523162842,null,2.7999999523162842,null,2.7999999523162842,null,2.7999999523162842,null,null,null,null,2.7999999523162842,null,2.7999999523162842,null,2.7999999523162842,null,null,null,null,null,2.7999999523162842,2.7999999523162842,null,null,2.7999999523162842]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,1.8999999761581421,null,1.8999999761581421,null,1.8999999761581421,null,1.8999999761581421,null,null,null,null,1.8999999761581421,null,1.5,null,1.5,null,null,null,null,null,1.5,1.5,null,null,1.5]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,0.85,null,0.85,null,0.85,null,0.85,null,null,null,null,0.85,null,0.85,null,0.85,null,null,null,null,null,0.85,0.85,null,null,0.85]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,1.2000000476837158,null,1.2000000476837158,null,1.2000000476837158,null,1.2000000476837158,null,null,null,null,1.2000000476837158,null,1.2999999523162842,null,1.2999999523162842,null,null,null,null,null,1.2999999523162842,1.2999999523162842,null,null,1.2999999523162842]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,1.7000000476837158,null,1.7000000476837158,null,1.7000000476837158,null,1.7000000476837158,null,null,null,null,1.7000000476837158,null,1.3999999761581421,null,1.3999999761581421,null,null,null,null,null,1.3999999761581421,1.3999999761581421,null,null,1.3999999761581421]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,0.1,null,0.1,null,0.1,null,0.1,null,null,null,null,0.1,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"6",null,"6",null,"6",null,"6",null,null,null,null,"6",null,"6",null,"6",null,null,null,null,null,"6","6",null,null,"6"]
[null,null,null,null,"Raw LAR (MVA)",null,null,null,null,null,0.5,null,0.5,null,0.5,null,0.5,null,null,null,null,0.5,null,0.1,null,0.1,null,null,null,null,null,0.1,0.1,null,null,0.1]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,1.2000000476837158,null,1.2000000476837158,null,1.2000000476837158,null,1.2000000476837158,null,null,null,null,1.2000000476837158,null,1.2000000476837158,null,1.2000000476837158,null,null,null,null,null,1.2000000476837158,1.2000000476837158,null,null,1.2000000476837158]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0.40000000596046448,null,0.40000000596046448,null,0.40000000596046448,null,0.40000000596046448,null,null,null,null,0.40000000596046448,null,0.40000000596046448,null,0.40000000596046448,null,null,null,null,null,0.40000000596046448,0.40000000596046448,null,null,0.40000000596046448]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,"Rural/ Remote",null,"Rural/ Remote",null,"Rural/ Remote",null,null,null,null,null,"Rural/ Remote","Rural/ Remote",null,null,"Rural/ Remote"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]

{"sheet":"YEPP","index":291,"n_rows":50,"n_cols":36,"rows_kept":50,"cut":false,"hidden":false,"merged":[[0,2,0,41],[2,1,2,6],[2,9,4,21],[2,24,3,25],[2,27,4,38],[6,1,8,6],[6,9,6,37],[8,9,9,37],[11,9,11,37],[13,0,13,5],[13,9,13,37],[15,3,16,12],[15,15,15,27],[18,18,19,32],[19,3,20,12],[19,15,20,16],[23,4,24,9],[23,10,23,22],[23,23,23,35],[24,10,24,11],[24,12,24,13],[24,14,24,15],[24,16,24,20],[24,21,24,22],[24,23,24,24],[24,25,24,30],[24,32,24,34],[25,4,25,9],[25,10,25,11],[25,12,25,13],[25,14,25,15],[25,16,25,20],[25,21,25,22],[25,23,25,24],[25,25,25,30],[25,32,25,34],[26,4,26,9],[26,10,26,11],[26,12,26,13],[26,14,26,15],[26,16,26,20],[26,21,26,22],[26,23,26,24],[26,25,26,30],[26,32,26,34],[27,4,27,9],[27,10,27,11],[27,12,27,13],[27,14,27,15],[27,16,27,20],[27,21,27,22],[27,23,27,24],[27,25,27,30],[27,32,27,34],[28,4,28,9],[28,10,28,11],[28,12,28,13],[28,14,28,15],[28,16,28,20],[28,21,28,22],[28,23,28,24],[28,25,28,30],[28,32,28,34],[29,4,29,9],[29,10,29,11],[29,12,29,13],[29,14,29,15],[29,16,29,20],[29,21,29,22],[29,23,29,24],[29,25,29,30],[29,32,29,34],[30,4,30,9],[30,10,30,11],[30,12,30,13],[30,14,30,15],[30,16,30,20],[30,21,30,22],[30,23,30,24],[30,25,30,30],[30,32,30,34],[31,4,31,9],[31,10,31,11],[31,12,31,13],[31,14,31,15],[31,16,31,20],[31,21,31,22],[31,23,31,24],[31,25,31,30],[31,32,31,34],[32,4,32,9],[32,10,32,11],[32,12,32,13],[32,14,32,15],[32,16,32,20],[32,21,32,22],[32,23,32,24],[32,25,32,30],[32,32,32,34],[33,4,33,9],[33,10,33,11],[33,12,33,13],[33,14,33,15],[33,16,33,20],[33,21,33,22],[33,23,33,24],[33,25,33,30],[33,32,33,34],[34,4,34,9],[34,10,34,11],[34,12,34,13],[34,14,34,15],[34,16,34,20],[34,21,34,22],[34,23,34,24],[34,25,34,30],[34,32,34,34],[35,4,35,9],[35,10,35,11],[35,12,35,13],[35,14,35,15],[35,16,35,20],[35,21,35,22],[35,23,35,24],[35,25,35,30],[35,32,35,34],[36,4,36,9],[36,10,36,11],[36,12,36,13],[36,14,36,15],[36,16,36,20],[36,21,36,22],[36,23,36,24],[36,25,36,30],[36,32,36,34],[37,4,37,9],[37,10,37,11],[37,12,37,13],[37,14,37,15],[37,16,37,20],[37,21,37,22],[37,23,37,24],[37,25,37,30],[37,32,37,34],[38,4,38,9],[38,10,38,11],[38,12,38,13],[38,14,38,15],[38,16,38,20],[38,21,38,22],[38,23,38,24],[38,25,38,30],[38,32,38,34],[39,4,39,9],[39,10,39,11],[39,12,39,13],[39,14,39,15],[39,16,39,20],[39,21,39,22],[39,23,39,24],[39,25,39,30],[39,32,39,34],[41,32,41,34],[40,4,40,9],[40,10,40,11],[40,12,40,13],[40,14,40,15],[40,16,40,20],[40,21,40,22],[40,23,40,24],[40,25,40,30],[40,32,40,34],[42,4,42,9],[42,10,42,11],[42,12,42,13],[42,14,42,15],[42,16,42,20],[41,23,41,24],[41,25,41,30],[41,4,41,9],[41,10,41,11],[41,12,41,13],[41,14,41,15],[41,16,41,20],[41,21,41,22],[42,23,42,24],[42,25,42,30],[42,32,42,34],[44,21,44,22],[44,23,44,24],[42,21,42,22],[44,10,44,11],[44,12,44,13],[44,14,44,15],[44,16,44,20],[43,10,43,11],[43,12,43,13],[43,14,43,15],[43,16,43,20],[45,32,45,34],[43,21,43,22],[45,23,45,24],[45,25,45,30],[43,23,43,24],[43,25,43,30],[49,2,49,39],[44,25,44,30],[44,32,44,34],[45,4,45,9],[45,10,45,11],[45,12,45,13],[45,14,45,15],[45,16,45,20],[45,21,45,22],[44,4,44,9],[43,32,43,34],[43,4,43,9]]}
[null,null,"Zone Summary Information and Peak Load Forecast"]
[]
[null,"Substation",null,null,null,null,null,null,null,"YEPP - Yeppoon (66/11kV)",null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Supply",null,null,"RMES - Rockhampton Mesh"]
[]
[]
[]
[null,"Description",null,null,null,null,null,null,null,"Region is Capricornia"]
[]
[null,null,null,null,null,null,null,null,null,"Transformer size is 2x66/11kV 16/25MVA ONAN/ONAF"]
[]
[]
[null,null,null,null,null,null,null,null,null,"Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA"]
[]
["Growth Rates",null,null,null,null,null,null,null,null,"2019 W 0.2%, 2020 S 0.3% W 0.3%, 2021 S 0.3% W 0.3%, 2022 S 0.7% W 0.7%, 2023 S 0.5% W 0.5%"]
[]
[null,null,null,"Latest Peak Compensated Load",null,null,null,null,null,null,null,null,null,null,null,"23.9 MVA on 28/11/2018 at 18:30"]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[null,null,null,"Hours PA Exceeding 95% Peak Load",null,null,null,null,null,null,null,null,null,null,null," "]
[]
[]
[]
[null,null,null,null,"PEAK LOAD FORECAST AND CAPACITY",null,null,null,null,null,"SUMMER",null,null,null,null,null,null,null,null,null,null,null,null,"WINTER"]
[null,null,null,null,null,null,null,null,null,null,"2019/20",null,"2020/21",null,"2021/22",null,"2022/23",null,null,null,null,"2023/24",null,"2019",null,"2020",null,null,null,null,null,"2021","2022",null,null,"2023"]
[null,null,null,null,"NCC Rating (MVA)",null,null,null,null,null,59,null,59,null,59,null,59,null,null,null,null,59,null,67.800003051757813,null,67.800003051757813,null,null,null,null,null,67.800003051757813,67.800003051757813,null,null,67.800003051757813]
[null,null,null,null,"Contracted non-network (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"10 PoE Load (MVA)",null,null,null,null,null,23,null,22.899999618530273,null,22.899999618530273,null,23,null,null,null,null,23.200000762939453,null,17,null,17,null,null,null,null,null,17,17.100000381469727,null,null,17.299999237060547]
[null,null,null,null,"LARn (MVA)"]
[null,null,null,null,"LARn (MW)"]
[null,null,null,null,"Power Factor at Peak Load",null,null,null,null,null,1,null,1,null,1,null,1,null,null,null,null,1,null,0.99199999999999999,null,0.99199999999999999,null,null,null,null,null,0.99199999999999999,0.99199999999999999,null,null,0.99199999999999999]
[null,null,null,null,"ECC Rating (MVA)",null,null,null,null,null,32.299999237060547,null,32.299999237060547,null,32.299999237060547,null,32.299999237060547,null,null,null,null,32.299999237060547,null,36.299999237060547,null,36.299999237060547,null,null,null,null,null,36.299999237060547,36.299999237060547,null,null,36.299999237060547]
[null,null,null,null,"50 PoE Load (MVA)",null,null,null,null,null,21.399999618530273,null,21.299999237060547,null,21.299999237060547,null,21.399999618530273,null,null,null,null,21.600000381469727,null,16.200000762939453,null,16.299999237060547,null,null,null,null,null,16.299999237060547,16.399999618530273,null,null,16.5]
[null,null,null,null,"50 PoE Load >  95%  (MVA)",null,null,null,null,null,1.1000000000000001,null,1.1000000000000001,null,1.1000000000000001,null,1.1000000000000001,null,null,null,null,1.1000000000000001,null,0.8,null,0.8,null,null,null,null,null,0.8,0.8,null,null,0.8]
[null,null,null,null,"Hours PA >  95%  Peak Load",null,null,null,null,null,"7.5",null,"7.5",null,"7.5",null,"7.5",null,null,null,null,"7.5",null,"7.5",null,"7.5",null,null,null,null,null,"7.5","7.5",null,null,"7.5"]
[null,null,null,null,"Raw LAR (MVA)"]
[null,null,null,null,"Auto Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Remote Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Manual Trans Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Mobile Plant Avail (MVA)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(30min)",null,null,null,null,null,0,null,0,null,0,null,0,null,null,null,null,0,null,0,null,0,null,null,null,null,null,0,0,null,null,0]
[null,null,null,null,"Shed(4Hour)",null,null,null,null,null,1.5,null,1.5,null,1.5,null,1.5,null,null,null,null,1.5,null,1.5,null,1.5,null,null,null,null,null,1.5,1.5,null,null,1.5]
[null,null,null,null,"LARc (MVA)"]
[null,null,null,null,"LARc (MW)"]
[null,null,null,null,"Substation Category",null,null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,"Regional Centre",null,"Regional Centre",null,"Regional Centre",null,null,null,null,null,"Regional Centre","Regional Centre",null,null,"Regional Centre"]
[null,null,null,null,"Meets Security Standard",null,null,null,null,null,"Yes",null,"Yes",null,"Yes",null,"Yes",null,null,null,null,"Yes",null,"Yes",null,"Yes",null,null,null,null,null,"Yes","Yes",null,null,"Yes"]
[]
[]
[]
[null,null,"Return to Index"]