## Disclaimer & Introduction
1. Disclaimer and Introduction
1.1 Disclaimer
These set of Subtransmission load flow studies results are prepared and made available solely for information purposes as part of the Distribution Annual Planning Report (DAPR). Whilst care was taken in the preparation of the information in this report, and it is provided with the best intentions and good faith, the Network Modelling Team accepts no responsibility or liability (including without limitation, liability to any person by reason of negligence or negligent mis-statement) for any loss or damage that may be incurred by any person acting in reliance on this information or assumptions drawn from it, except to the extent that liability under any applicable Queensland or Commonwealth of Australia statute cannot be excluded.
Ergon Energy makes no representation or warranty as to the accuracy, reliability, completeness or suitability for any particular purpose of the information in this document. All information should be independently investigated, reviewed, analysed, and verified, and must not be relied upon in connection with any investment proposal or decision. The information contained in this report is subject to annual review.
The Known Issues section below outlines some factors that could affect the accuracy of the results presented in this studies summary and should be considered when making network augmentation or financial decisions based on these values. The basis of the disclosed studies results are the network demand forecasts obtained from the SIFT system/database. The Network Modelling Team obtain these forecast values as populated by the Strategic Forecasting Team following quality assurance processes for accuracy.
1.2 Introduction and Methodology
This load flow studies summary is prepared to provide a reference for Strategic Planners during the preparation of the DAPR. Engineers should carry out their own due diligence on the information provided by this summary prior to applying it to engineering activities. The results of these studies contained herein are produced as per the methodology described below.
In preparing the load flow summary results:
· The subtransmission network model was developed and prepared using Power Factory 2021 SP4. The results were calculated in Power Factory 2023 SP4.
· For the Ergon Energy network the model is connected to the Powerlink TAPR model at the common coupling points.
· All approved projects (in the form of variations) and new connection load/generators are incorporated into the model.
· Obtain 10 and 50 PoE demand forecasts from SIFT and minimum demand forecast from Tableau.
· Using Python automation to pull demand forecasts into Power Factory model.
· Run Load Flow studies for each of the following scenarios and document result summaries:
Ergon Energy Network (EE)
a) Time of Day conditions with SIFT 10% PoE profile (10PoE_EE_NNC);
b) Static normal conditions with minimum demand profile (MinLoad_EE_NNC);
c) N-1 conditions with SIFT 50% PoE profile (50PoE_EE_N-1);
d) N-1 conditions with minimum demand profile (MinLoad_EE_N-1);
1.3 High level Process Summary
1. Derive Master Model, Pack External Objects and Export
2. Activate Model
3. Activate Load Characteristic Application Study Case (ie. 2023TransLF-ErgonSubtrans-WithVars for EE, EnergexST_AppPrjs[DAPR2023] for EX)
4. Run Forecast Load script for required conditions (e.g. 10PoE Day SUMWIN for 10PoE peak conditions)
5. Run Power Factory Information Producer (ie. a Report Nearly Anything Sequential Creator and Task Automation of Report Nearly anything Scripts or SubtransFeederForecastProducer for 10PoE_EE_NNC)
6. Repeat steps 3-5 for other Load Characteristic Configurations if required
8. Run a Python Interpreter that reads the output files and produces the formatted document
1.4 Definition of Terms Feeder Capacity and Forecast Tables
Term | Definition
10 PoE Load (A) | Peak load forecast with 10% probability of being exceeded (one in every 10 years will be exceeded). Based on normal expected growth rates and weather corrected starting loads.
50 PoE Load (A) | Peak load forecast with 50% probability of being exceeded (one in every two years will be exceeded). Based on normal expected growth rates & weather corrected starting loads. This is the worst case (highest) load forecast beween summer day and summer night.
NNC | Normal Network Configuration, Outages labelled "_NNC" indicate the limitations for the feeder were identical or worse under the Normal Network Configuration.
NCC Rating (A) | Normal Cyclic Capacity - the total capacity with all network components and equipment intact. This is the maximum permissible peak daily loading for a given load cycle that a feeder can supply each day of its life. For overhead feeders, the NCC is the conductor rating with an assumed 1m/s wind, orthogonal to the line. For underground cables, the NCC assumes that there are sufficient temperature and current operating margins from the thermal inertia of the cable and its surroundings.
Power Factor (System Normal) | Lowest power factor along the feeder at 10 PoE Peak Load. Where the Power Factor is either 0 or blank, the feeder is a normally open feeder that does not have load under System Normal conditions.
Security Standard | For security standard application, the general type of customer a sub-transmission, or transmission feeder is supplying.
Transfers | This is the total amount of load transfers that are available following the worst case network contingency. This includes automatic transfers that are controlled automatically through SCADA and are generally implemented within a minute, load transfers that can be implemented through screen switching by a network controller, manual transfers that are deployed via manually controlled switchgear locally by field staff, and mobile generation which can be deployed by field staff by moving generation to specific sites.
Note: It should be noted under the Safety Net in the Distribution Authority, it is generally assumed that 4MVA (70A) of generation is available for Urban feeders and 10MVA (170A) for Rural feeders to meet specific criteria. These values have been used as a default in the forecast tables where these are sufficient to reduce the 50PoE load below the ECC rating. Where the load is still above the ECC rating, specific load transfers have been calculated for the feeder to determine whether the Safety Net criteria is met.

## Important Info-MinLF_EE_N-1
2. Important Information
2.1 Study Information - MinLF_EE_N-1
A summary of most information used as inputs is given in the Study Info Worksheet referenced below. This includes what Project Version was used, Study times, Variations, what Generators are included etc.
2.2 Results
The results of this study are referenced in the documented versions disclosed below.
Result Version: | MinLF_EE_N-1_20231013_2223 MinLF_EE_N-1_20231016_1704
2.3 Known Issues and Limitations
· The List of Subtransmission Projects to be stored as Variations has been produced manually from Copperleaf and SIFT for the next 10 years.
· Automatic Outage Switching is not incorporated for both Ergon Energy and Energex N-1 Studies
· Ratings are the NCC (Normal Cyclic Capacity) Rating and do not consider increased capacity due to the outage (eg. Parallel cable runs where no load in another feeder increases trench capacity for the remaining feeders)
· N-1 Outages modelled take the entire feeder out of service.
· N-1 Outages that do not produce convergent results are ignored. The list of these can be seen in the Study Info worksheet.
· North West Power System (ie. The Network around Mount Isa) has been reported in a separate Spreadsheet this year.
· The Report is not suitable to determine "directionality" of the real or reactive power-flows due to the use of absolute value functions prior to the limits being calculated.
3. Additional Information
2.1 Information About Variables
The Values for a given timeslot shown are calculated as follows. All of the values will be for the line element in Power Factory with the Loading Constraint.
This means that the Power Factor and Voltage values are recorded at the line that is considered the most "limited" not the minimum voltage on the feeder or the minimum Power Factor on the feeder.
For each Contingency Event the values for each line are recorded with them eventually ending up in the following fields
% of Rated A: The % Utilisation called "loading" in Power Factory [c:loading]
Loading (A): Absolute Maximum Current for Both Ends in kA
Loading (MVA): Absolute Maximum Apparent Power for Both Ends in MVA
Loading (MW): Absolute Maximum Real Power for Both Ends in MW
Power Factor: Absolute Min Power Factor for Both Ends
Rating (A): Line Nominal Rating using [e:Inom_a]
Min Voltage at Constrained Conductor: Min Voltage seen on both sides of the feeder line
Once they are calculated for each feeder and Timeslot the Limiting entry is determined. This will be the values for a single line limited in the following order.
At each step all lines that share the "limiting" value will be recorded, provided their float representative is identical.
Minor differences in the float representation will result in the Min or Max value being utilised even if the value when considering real life significant figures are otherwise identical.
1. % of Rated A - Max
2. Rating (A) - Min
3. Loading (MVA) - Max
The following limit calculations are applied to ensure only 1 line's values are recorded even if all entries have the same electrical loading characteristics.
4. Contingency Outage: Alphabetical Max
Note that "_NNC" is used with is a "Normal Network Configuration" contingency where nothing is taken out of service. If it is displayed, then taking a feeder out of service did not make a recordable difference to the feeder loading.
If multiple feeder outage contingencies have the same effect on the feeder, then the higher alphabetical name will be recorded.
5. Limiting Line Name: Alphabetical Min: This is to ensure there is a unique value
6. Current Study Case Time: Alphabetical Min: This is a stopgap to ensure there is a unique value

## MinLF_EE_N-1
Grid Association | Associated Feeders | Variable | 2024 SD | 2025 SD | 2026 SD | 2027 SD | 2028 SD
CA-Dysart | 6064_Dysart - Saraji Mine 66 kV | % of Rated A | 4.932% | 4.932% | 4.932% | 4.932% | 4.932%
CA-Dysart | 6064_Dysart - Saraji Mine 66 kV | Limiting Line Name | 3-Phase Link 66kV_Term7_6064 SARAJI MINE | 3-Phase Link 66kV_Term7_6064 SARAJI MINE | 3-Phase Link 66kV_Term7_6064 SARAJI MINE | 3-Phase Link 66kV_Term7_6064 SARAJI MINE | 3-Phase Link 66kV_Term7_6064 SARAJI MINE
CA-Dysart | 6064_Dysart - Saraji Mine 66 kV | Loading (A) | 246.6115 | 246.6111 | 246.6109 | 246.6107 | 246.6107
CA-Dysart | 6064_Dysart - Saraji Mine 66 kV | Loading (MVA) | 29.5 | 29.5 | 29.5 | 29.5 | 29.5
CA-Dysart | 6064_Dysart - Saraji Mine 66 kV | Loading (MW) | 29.5 | 29.5 | 29.5 | 29.5 | 29.5
CA-Dysart | 6064_Dysart - Saraji Mine 66 kV | Power Factor | 1 | 1 | 1 | 1 | 1
CA-Dysart | 6064_Dysart - Saraji Mine 66 kV | Rating (A) | 5000 | 5000 | 5000 | 5000 | 5000
CA-Dysart | 6064_Dysart - Saraji Mine 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Dysart | 6064_Dysart - Saraji Mine 66 kV | Min Voltage at Constrained Conductor | 69.0634 | 69.0635 | 69.0636 | 69.0636 | 69.0636
CA-Dysart | 6064_Dysart - Saraji Mine 66 kV | Contingency Outage | 6106_Shale Oil Tee - Shale Oil 66kV | 6106_Shale Oil Tee - Shale Oil 66kV | 6106_Shale Oil Tee - Shale Oil 66kV | 6106_Shale Oil Tee - Shale Oil 66kV | 6106_Shale Oil Tee - Shale Oil 66kV
CA-Dysart | 6130_Dysart - Vermont 66 kV | % of Rated A | 14.3% | 14.3% | 14.3% | 14.3% | 14.3%
CA-Dysart | 6130_Dysart - Vermont 66 kV | Limiting Line Name | TR_LINE 82005_1 | TR_LINE 82005_1 | TR_LINE 82005_1 | TR_LINE 82005_1 | TR_LINE 82005_1
CA-Dysart | 6130_Dysart - Vermont 66 kV | Loading (A) | 31.1711 | 31.171 | 31.171 | 31.171 | 31.171
CA-Dysart | 6130_Dysart - Vermont 66 kV | Loading (MVA) | 3.7287 | 3.7287 | 3.7287 | 3.7287 | 3.7287
CA-Dysart | 6130_Dysart - Vermont 66 kV | Loading (MW) | 3.7272 | 3.7272 | 3.7272 | 3.7272 | 3.7272
CA-Dysart | 6130_Dysart - Vermont 66 kV | Power Factor | 0.99959 | 0.99959 | 0.99959 | 0.99959 | 0.99959
CA-Dysart | 6130_Dysart - Vermont 66 kV | Rating (A) | 218 | 218 | 218 | 218 | 218
CA-Dysart | 6130_Dysart - Vermont 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Dysart | 6130_Dysart - Vermont 66 kV | Min Voltage at Constrained Conductor | 68.9911 | 68.9912 | 68.9913 | 68.9913 | 68.9914
CA-Dysart | 6130_Dysart - Vermont 66 kV | Contingency Outage | 6106_Shale Oil Tee - Shale Oil 66kV | 6106_Shale Oil Tee - Shale Oil 66kV | 6106_Shale Oil Tee - Shale Oil 66kV | 6106_Shale Oil Tee - Shale Oil 66kV | 6106_Shale Oil Tee - Shale Oil 66kV
CA-Emerald | 6011_Blackwater - Comet 66 kV | % of Rated A | 33.04% | 32.83% | 32.85% | 32.78% | 32.89%
CA-Emerald | 6011_Blackwater - Comet 66 kV | Limiting Line Name | TR_LINE 22148_1 | TR_LINE 22148_1 | TR_LINE 22148_1 | TR_LINE 22148_1 | TR_LINE 22148_1
CA-Emerald | 6011_Blackwater - Comet 66 kV | Loading (A) | 91.5167 | 90.9466 | 90.9965 | 90.8029 | 91.0957
CA-Emerald | 6011_Blackwater - Comet 66 kV | Loading (MVA) | 10.9031 | 10.8361 | 10.8414 | 10.8191 | 10.8546
CA-Emerald | 6011_Blackwater - Comet 66 kV | Loading (MW) | 2.3863 | 1.2981 | 1.769 | 0.88791 | 0.0098579
CA-Emerald | 6011_Blackwater - Comet 66 kV | Power Factor | 0.21882 | 0.11974 | 0.16312 | 0.082013 | 0.0008491
CA-Emerald | 6011_Blackwater - Comet 66 kV | Rating (A) | 277 | 277 | 277 | 277 | 277
CA-Emerald | 6011_Blackwater - Comet 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Emerald | 6011_Blackwater - Comet 66 kV | Min Voltage at Constrained Conductor | 68.7844 | 68.7904 | 68.7862 | 68.7907 | 68.7947
CA-Emerald | 6011_Blackwater - Comet 66 kV | Contingency Outage | 6067 Lilyvale - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV
CA-Emerald | 6012_Blackwater - Bedford Weir 66 kV | % of Rated A | 16.43% | 15.91% | 15.48% | 15.17% | 14.98%
CA-Emerald | 6012_Blackwater - Bedford Weir 66 kV | Limiting Line Name | TR_LINE 22153_1 | TR_LINE 22153_1 | TR_LINE 22153_1 | TR_LINE 22153_1 | TR_LINE 22153_1
CA-Emerald | 6012_Blackwater - Bedford Weir 66 kV | Loading (A) | 45.6838 | 44.2414 | 43.0442 | 42.1717 | 41.6418
CA-Emerald | 6012_Blackwater - Bedford Weir 66 kV | Loading (MVA) | 5.4199 | 5.2489 | 5.1067 | 5.0032 | 4.9404
CA-Emerald | 6012_Blackwater - Bedford Weir 66 kV | Loading (MW) | 5.3348 | 5.1599 | 5.0143 | 4.9083 | 4.8438
CA-Emerald | 6012_Blackwater - Bedford Weir 66 kV | Power Factor | 0.98429 | 0.98304 | 0.9819 | 0.98101 | 0.98044
CA-Emerald | 6012_Blackwater - Bedford Weir 66 kV | Rating (A) | 278 | 278 | 278 | 278 | 278
CA-Emerald | 6012_Blackwater - Bedford Weir 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Emerald | 6012_Blackwater - Bedford Weir 66 kV | Min Voltage at Constrained Conductor | 68.4967 | 68.4976 | 68.4959 | 68.4966 | 68.4972
CA-Emerald | 6012_Blackwater - Bedford Weir 66 kV | Contingency Outage | 6011_Blackwater - Comet 66 kV | 6011_Blackwater - Comet 66 kV | 6011_Blackwater - Comet 66 kV | 6011_Blackwater - Comet 66 kV | 6011_Blackwater - Comet 66 kV
CA-Emerald | 6014_Blackwater - South Blackwater 66 kV | % of Rated A | 11.34% | 11.34% | 11.34% | 11.34% | 11.34%
CA-Emerald | 6014_Blackwater - South Blackwater 66 kV | Limiting Line Name | TR_LINE 22149_1 | TR_LINE 22149_1 | TR_LINE 22149_1 | TR_LINE 22149_1 | TR_LINE 22149_1
CA-Emerald | 6014_Blackwater - South Blackwater 66 kV | Loading (A) | 56.2516 | 56.2508 | 56.2522 | 56.2516 | 56.2512
CA-Emerald | 6014_Blackwater - South Blackwater 66 kV | Loading (MVA) | 6.6737 | 6.6737 | 6.6737 | 6.6737 | 6.6737
CA-Emerald | 6014_Blackwater - South Blackwater 66 kV | Loading (MW) | 6.6513 | 6.6513 | 6.6513 | 6.6513 | 6.6513
CA-Emerald | 6014_Blackwater - South Blackwater 66 kV | Power Factor | 0.99664 | 0.99664 | 0.99664 | 0.99664 | 0.99664
CA-Emerald | 6014_Blackwater - South Blackwater 66 kV | Rating (A) | 496 | 496 | 496 | 496 | 496
CA-Emerald | 6014_Blackwater - South Blackwater 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Emerald | 6014_Blackwater - South Blackwater 66 kV | Min Voltage at Constrained Conductor | 68.4962 | 68.4972 | 68.4954 | 68.4961 | 68.4967
CA-Emerald | 6014_Blackwater - South Blackwater 66 kV | Contingency Outage | 6011_Blackwater - Comet 66 kV | 6011_Blackwater - Comet 66 kV | 6011_Blackwater - Comet 66 kV | 6011_Blackwater - Comet 66 kV | 6011_Blackwater - Comet 66 kV
CA-Emerald | 6015_Blackwater - Curragh Mine 66 kV | % of Rated A | 66.43% | 66.43% | 66.43% | 66.43% | 66.43%
CA-Emerald | 6015_Blackwater - Curragh Mine 66 kV | Limiting Line Name | TR_LINE 18371_1 | TR_LINE 18371_1 | TR_LINE 18371_1 | TR_LINE 18371_1 | TR_LINE 18371_1
CA-Emerald | 6015_Blackwater - Curragh Mine 66 kV | Loading (A) | 369.3609 | 369.3558 | 369.3653 | 369.3615 | 369.3584
CA-Emerald | 6015_Blackwater - Curragh Mine 66 kV | Loading (MVA) | 43.82 | 43.82 | 43.82 | 43.82 | 43.82
CA-Emerald | 6015_Blackwater - Curragh Mine 66 kV | Loading (MW) | 43.8098 | 43.8098 | 43.8098 | 43.8098 | 43.8098
CA-Emerald | 6015_Blackwater - Curragh Mine 66 kV | Power Factor | 0.99977 | 0.99977 | 0.99977 | 0.99977 | 0.99977
CA-Emerald | 6015_Blackwater - Curragh Mine 66 kV | Rating (A) | 556 | 556 | 556 | 556 | 556
CA-Emerald | 6015_Blackwater - Curragh Mine 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Emerald | 6015_Blackwater - Curragh Mine 66 kV | Min Voltage at Constrained Conductor | 68.0062 | 68.0071 | 68.0054 | 68.0061 | 68.0066
CA-Emerald | 6015_Blackwater - Curragh Mine 66 kV | Contingency Outage | 6011_Blackwater - Comet 66 kV | 6011_Blackwater - Comet 66 kV | 6011_Blackwater - Comet 66 kV | 6011_Blackwater - Comet 66 kV | 6011_Blackwater - Comet 66 kV
CA-Emerald | 6055 Cook Colliery-Miniere Mining 66 kV | % of Rated A | 35.26% | 35.15% | 35.06% | 34.98% | 34.91%
CA-Emerald | 6055 Cook Colliery-Miniere Mining 66 kV | Limiting Line Name | TR_LINE 22527_1 | TR_LINE 22527_1 | TR_LINE 22527_1 | TR_LINE 22527_1 | TR_LINE 22527_1
CA-Emerald | 6055 Cook Colliery-Miniere Mining 66 kV | Loading (A) | 50.4282 | 50.2686 | 50.1352 | 50.0234 | 49.9214
CA-Emerald | 6055 Cook Colliery-Miniere Mining 66 kV | Loading (MVA) | 5.9011 | 5.8827 | 5.8671 | 5.8543 | 5.8425
CA-Emerald | 6055 Cook Colliery-Miniere Mining 66 kV | Loading (MW) | 5.897 | 5.8786 | 5.863 | 5.8501 | 5.8383
CA-Emerald | 6055 Cook Colliery-Miniere Mining 66 kV | Power Factor | 0.9993 | 0.99929 | 0.99929 | 0.99929 | 0.99928
CA-Emerald | 6055 Cook Colliery-Miniere Mining 66 kV | Rating (A) | 143 | 143 | 143 | 143 | 143
CA-Emerald | 6055 Cook Colliery-Miniere Mining 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Emerald | 6055 Cook Colliery-Miniere Mining 66 kV | Min Voltage at Constrained Conductor | 67.5602 | 67.5636 | 67.5639 | 67.5664 | 67.5686
CA-Emerald | 6055 Cook Colliery-Miniere Mining 66 kV | Contingency Outage | 6011_Blackwater - Comet 66 kV | 6011_Blackwater - Comet 66 kV | 6011_Blackwater - Comet 66 kV | 6011_Blackwater - Comet 66 kV | 6011_Blackwater - Comet 66 kV
CA-Emerald | 6056_Comet - Emerald 66 kV | % of Rated A | 31.59% | 31.45% | 31.52% | 31.47% | 31.53%
CA-Emerald | 6056_Comet - Emerald 66 kV | Limiting Line Name | TR_LINE 22146_1 | TR_LINE 22146_1 | TR_LINE 22146_1 | TR_LINE 22146_1 | TR_LINE 22146_1
CA-Emerald | 6056_Comet - Emerald 66 kV | Loading (A) | 87.4914 | 87.1195 | 87.3066 | 87.166 | 87.3502
CA-Emerald | 6056_Comet - Emerald 66 kV | Loading (MVA) | 10.683 | 10.6624 | 10.674 | 10.6765 | 10.7184
CA-Emerald | 6056_Comet - Emerald 66 kV | Loading (MW) | 1.9457 | 0.97424 | 1.5785 | 0.86941 | 0.22739
CA-Emerald | 6056_Comet - Emerald 66 kV | Power Factor | 0.18212 | 0.091353 | 0.14787 | 0.081413 | 0.021195
CA-Emerald | 6056_Comet - Emerald 66 kV | Rating (A) | 277 | 277 | 277 | 277 | 277
CA-Emerald | 6056_Comet - Emerald 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Emerald | 6056_Comet - Emerald 66 kV | Min Voltage at Constrained Conductor | 70.4963 | 70.6607 | 70.5859 | 70.7169 | 70.8446
CA-Emerald | 6056_Comet - Emerald 66 kV | Contingency Outage | 6067 Lilyvale - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV
CA-Emerald | 6058_Bedford Weir - Bingegang 66 kV | % of Rated A | 12.92% | 12.82% | 12.75% | 12.69% | 12.64%
CA-Emerald | 6058_Bedford Weir - Bingegang 66 kV | Limiting Line Name | TR_LINE 22154_1 | TR_LINE 22154_1 | TR_LINE 22154_1 | TR_LINE 22154_1 | TR_LINE 22154_1
CA-Emerald | 6058_Bedford Weir - Bingegang 66 kV | Loading (A) | 35.9049 | 35.6392 | 35.4369 | 35.28 | 35.1471
CA-Emerald | 6058_Bedford Weir - Bingegang 66 kV | Loading (MVA) | 4.2402 | 4.2097 | 4.1864 | 4.1685 | 4.1531
CA-Emerald | 6058_Bedford Weir - Bingegang 66 kV | Loading (MW) | 4.1738 | 4.1426 | 4.1188 | 4.1003 | 4.0846
CA-Emerald | 6058_Bedford Weir - Bingegang 66 kV | Power Factor | 0.98436 | 0.98406 | 0.98384 | 0.98366 | 0.98351
CA-Emerald | 6058_Bedford Weir - Bingegang 66 kV | Rating (A) | 278 | 278 | 278 | 278 | 278
CA-Emerald | 6058_Bedford Weir - Bingegang 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Emerald | 6058_Bedford Weir - Bingegang 66 kV | Min Voltage at Constrained Conductor | 68.1804 | 68.1955 | 68.2054 | 68.2146 | 68.2203
CA-Emerald | 6058_Bedford Weir - Bingegang 66 kV | Contingency Outage | 6011_Blackwater - Comet 66 kV | 6011_Blackwater - Comet 66 kV | 6011_Blackwater - Comet 66 kV | 6011_Blackwater - Comet 66 kV | 6011_Blackwater - Comet 66 kV
CA-Emerald | 6059_Leichardt - Cook Colliery 66 kV | % of Rated A | 35.32% | 35.21% | 35.12% | 35.04% | 34.97%
CA-Emerald | 6059_Leichardt - Cook Colliery 66 kV | Limiting Line Name | TR_LINE 22402_1 | TR_LINE 22402_1 | TR_LINE 22402_1 | TR_LINE 22402_1 | TR_LINE 22402_1
CA-Emerald | 6059_Leichardt - Cook Colliery 66 kV | Loading (A) | 50.5075 | 50.3483 | 50.2151 | 50.1036 | 50.0018
CA-Emerald | 6059_Leichardt - Cook Colliery 66 kV | Loading (MVA) | 5.9379 | 5.9194 | 5.9037 | 5.8908 | 5.8789
CA-Emerald | 6059_Leichardt - Cook Colliery 66 kV | Loading (MW) | 5.9267 | 5.9081 | 5.8924 | 5.8794 | 5.8675
CA-Emerald | 6059_Leichardt - Cook Colliery 66 kV | Power Factor | 0.99811 | 0.99809 | 0.99808 | 0.99807 | 0.99806
CA-Emerald | 6059_Leichardt - Cook Colliery 66 kV | Rating (A) | 143 | 143 | 143 | 143 | 143
CA-Emerald | 6059_Leichardt - Cook Colliery 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Emerald | 6059_Leichardt - Cook Colliery 66 kV | Min Voltage at Constrained Conductor | 67.5615 | 67.5649 | 67.5653 | 67.5677 | 67.5699
CA-Emerald | 6059_Leichardt - Cook Colliery 66 kV | Contingency Outage | 6011_Blackwater - Comet 66 kV | 6011_Blackwater - Comet 66 kV | 6011_Blackwater - Comet 66 kV | 6011_Blackwater - Comet 66 kV | 6011_Blackwater - Comet 66 kV
CA-Emerald | 6062_Thiess 66 kV | % of Rated A | 19.78% | 19.78% | 19.78% | 19.78% | 19.78%
CA-Emerald | 6062_Thiess 66 kV | Limiting Line Name | TR_LINE 22551_1 | TR_LINE 22551_1 | TR_LINE 22551_1 | TR_LINE 22551_1 | TR_LINE 22551_1
CA-Emerald | 6062_Thiess 66 kV | Loading (A) | 28.2897 | 28.2878 | 28.2872 | 28.2858 | 28.2846
CA-Emerald | 6062_Thiess 66 kV | Loading (MVA) | 3.3003 | 3.3003 | 3.3003 | 3.3003 | 3.3003
CA-Emerald | 6062_Thiess 66 kV | Loading (MW) | 3.3003 | 3.3003 | 3.3003 | 3.3003 | 3.3003
CA-Emerald | 6062_Thiess 66 kV | Power Factor | 1 | 1 | 1 | 1 | 1
CA-Emerald | 6062_Thiess 66 kV | Rating (A) | 143 | 143 | 143 | 143 | 143
CA-Emerald | 6062_Thiess 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Emerald | 6062_Thiess 66 kV | Min Voltage at Constrained Conductor | 67.3492 | 67.3538 | 67.3552 | 67.3585 | 67.3615
CA-Emerald | 6062_Thiess 66 kV | Contingency Outage | 6011_Blackwater - Comet 66 kV | 6011_Blackwater - Comet 66 kV | 6011_Blackwater - Comet 66 kV | 6011_Blackwater - Comet 66 kV | 6011_Blackwater - Comet 66 kV
CA-Emerald | 6065_Lilyvale - Tieri Tee 66 kV | % of Rated A | 29.91% | 29.81% | 29.73% | 29.67% | 29.66%
CA-Emerald | 6065_Lilyvale - Tieri Tee 66 kV | Limiting Line Name | TR_LINE 22248_1 | TR_LINE 22248_1 | TR_LINE 22248_1 | TR_LINE 22248_1 | TR_LINE 22248_1
CA-Emerald | 6065_Lilyvale - Tieri Tee 66 kV | Loading (A) | 72.6914 | 72.4351 | 72.2394 | 72.1077 | 72.0753
CA-Emerald | 6065_Lilyvale - Tieri Tee 66 kV | Loading (MVA) | 8.5922 | 8.5621 | 8.5392 | 8.5239 | 8.5202
CA-Emerald | 6065_Lilyvale - Tieri Tee 66 kV | Loading (MW) | 8.5698 | 8.5394 | 8.5164 | 8.5008 | 8.4971
CA-Emerald | 6065_Lilyvale - Tieri Tee 66 kV | Power Factor | 0.99739 | 0.99735 | 0.99732 | 0.9973 | 0.99729
CA-Emerald | 6065_Lilyvale - Tieri Tee 66 kV | Rating (A) | 243 | 243 | 243 | 243 | 243
CA-Emerald | 6065_Lilyvale - Tieri Tee 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Emerald | 6065_Lilyvale - Tieri Tee 66 kV | Min Voltage at Constrained Conductor | 68.2409 | 68.2421 | 68.2445 | 68.2461 | 68.2472
CA-Emerald | 6065_Lilyvale - Tieri Tee 66 kV | Contingency Outage | 6067 Lilyvale - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV
CA-Emerald | 6067 Lilyvale - Emerald 66 kV | % of Rated A | 40.83% | 40.57% | 40.59% | 40.57% | 40.64%
CA-Emerald | 6067 Lilyvale - Emerald 66 kV | Limiting Line Name | TR_LINE 17480_1 | TR_LINE 17480_1 | TR_LINE 17480_1 | TR_LINE 17480_1 | TR_LINE 17480_1
CA-Emerald | 6067 Lilyvale - Emerald 66 kV | Loading (A) | 139.2375 | 138.3433 | 138.419 | 138.3485 | 138.5778
CA-Emerald | 6067 Lilyvale - Emerald 66 kV | Loading (MVA) | 16.9175 | 16.7581 | 16.7574 | 16.7691 | 16.8215
CA-Emerald | 6067 Lilyvale - Emerald 66 kV | Loading (MW) | 2.3283 | 1.2395 | 1.7094 | 0.82986 | 0.43282
CA-Emerald | 6067 Lilyvale - Emerald 66 kV | Power Factor | 0.1147 | 0.051135 | 0.079148 | 0.026671 | 0.0029614
CA-Emerald | 6067 Lilyvale - Emerald 66 kV | Rating (A) | 341 | 341 | 341 | 341 | 341
CA-Emerald | 6067 Lilyvale - Emerald 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Emerald | 6067 Lilyvale - Emerald 66 kV | Min Voltage at Constrained Conductor | 69.1062 | 68.8208 | 68.8176 | 68.8268 | 68.8353
CA-Emerald | 6067 Lilyvale - Emerald 66 kV | Contingency Outage | 6011_Blackwater - Comet 66 kV | 6011_Blackwater - Comet 66 kV | 6011_Blackwater - Comet 66 kV | 6011_Blackwater - Comet 66 kV | 6011_Blackwater - Comet 66 kV
CA-Emerald | 6078_SOBL - Dragline South 66 kV | % of Rated A | 0.5598% | 0.5598% | 0.5599% | 0.5599% | 0.5598%
CA-Emerald | 6078_SOBL - Dragline South 66 kV | Limiting Line Name | TR_LINE SOBL - SOBL Dragline South | TR_LINE SOBL - SOBL Dragline South | TR_LINE SOBL - SOBL Dragline South | TR_LINE SOBL - SOBL Dragline South | TR_LINE SOBL - SOBL Dragline South
CA-Emerald | 6078_SOBL - Dragline South 66 kV | Loading (A) | 27.9925 | 27.9921 | 27.9928 | 27.9925 | 27.9923
CA-Emerald | 6078_SOBL - Dragline South 66 kV | Loading (MVA) | 3.3 | 3.3 | 3.3 | 3.3 | 3.3
CA-Emerald | 6078_SOBL - Dragline South 66 kV | Loading (MW) | 3.3 | 3.3 | 3.3 | 3.3 | 3.3
CA-Emerald | 6078_SOBL - Dragline South 66 kV | Power Factor | 1 | 1 | 1 | 1 | 1
CA-Emerald | 6078_SOBL - Dragline South 66 kV | Rating (A) | 5000 | 5000 | 5000 | 5000 | 5000
CA-Emerald | 6078_SOBL - Dragline South 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Emerald | 6078_SOBL - Dragline South 66 kV | Min Voltage at Constrained Conductor | 68.0632 | 68.0641 | 68.0624 | 68.0631 | 68.0636
CA-Emerald | 6078_SOBL - Dragline South 66 kV | Contingency Outage | 6011_Blackwater - Comet 66 kV | 6011_Blackwater - Comet 66 kV | 6011_Blackwater - Comet 66 kV | 6011_Blackwater - Comet 66 kV | 6011_Blackwater - Comet 66 kV
CA-Emerald | 6079_Barcaldine - Longreach 66 kV | % of Rated A | 17.99% | 17.37% | 16.94% | 16.63% | 16.43%
CA-Emerald | 6079_Barcaldine - Longreach 66 kV | Limiting Line Name | TR_CABLE 562_1 | TR_CABLE 562_1 | TR_CABLE 562_1 | TR_CABLE 562_1 | TR_CABLE 562_1
CA-Emerald | 6079_Barcaldine - Longreach 66 kV | Loading (A) | 17.9947 | 17.368 | 16.9387 | 16.6349 | 16.4266
CA-Emerald | 6079_Barcaldine - Longreach 66 kV | Loading (MVA) | 2.2509 | 2.1756 | 2.1241 | 2.0878 | 2.0632
CA-Emerald | 6079_Barcaldine - Longreach 66 kV | Loading (MW) | 1.1135 | 0.92681 | 0.7766 | 0.65058 | 0.54756
CA-Emerald | 6079_Barcaldine - Longreach 66 kV | Power Factor | 0.49467 | 0.42599 | 0.36561 | 0.31161 | 0.2654
CA-Emerald | 6079_Barcaldine - Longreach 66 kV | Rating (A) | 100 | 100 | 100 | 100 | 100
CA-Emerald | 6079_Barcaldine - Longreach 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Emerald | 6079_Barcaldine - Longreach 66 kV | Min Voltage at Constrained Conductor | 72.2189 | 72.3229 | 72.3987 | 72.4624 | 72.5149
CA-Emerald | 6079_Barcaldine - Longreach 66 kV | Contingency Outage | 6073_Clermont - Blair Athol 66 kV | 6073_Clermont - Blair Athol 66 kV | 6073_Clermont - Blair Athol 66 kV | 6073_Clermont - Blair Athol 66 kV | 6073_Clermont - Blair Athol 66 kV
CA-Emerald | 6080_Barcaldine - Blackall 66 kV | % of Rated A | 3.627% | 3.618% | 3.612% | 3.609% | 3.607%
CA-Emerald | 6080_Barcaldine - Blackall 66 kV | Limiting Line Name | TR_LINE 22558_1 | TR_LINE 22558_1 | TR_LINE 22558_1 | TR_LINE 22558_1 | TR_LINE 22558_1
CA-Emerald | 6080_Barcaldine - Blackall 66 kV | Loading (A) | 13.9997 | 13.9652 | 13.9436 | 13.9305 | 13.9238
CA-Emerald | 6080_Barcaldine - Blackall 66 kV | Loading (MVA) | 1.7475 | 1.7456 | 1.7446 | 1.7445 | 1.7448
CA-Emerald | 6080_Barcaldine - Blackall 66 kV | Loading (MW) | 0.32048 | 0.27783 | 0.24513 | 0.21917 | 0.20007
CA-Emerald | 6080_Barcaldine - Blackall 66 kV | Power Factor | 0.18339 | 0.15916 | 0.1405 | 0.12564 | 0.11467
CA-Emerald | 6080_Barcaldine - Blackall 66 kV | Rating (A) | 386 | 386 | 386 | 386 | 386
CA-Emerald | 6080_Barcaldine - Blackall 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Emerald | 6080_Barcaldine - Blackall 66 kV | Min Voltage at Constrained Conductor | 72.068 | 72.1669 | 72.2389 | 72.2996 | 72.3496
CA-Emerald | 6080_Barcaldine - Blackall 66 kV | Contingency Outage | 6073_Clermont - Blair Athol 66 kV | 6073_Clermont - Blair Athol 66 kV | 6073_Clermont - Blair Athol 66 kV | 6073_Clermont - Blair Athol 66 kV | 6073_Clermont - Blair Athol 66 kV
CA-Emerald | 6085_Tieri Tee - Tieri 66 kV | % of Rated A | 2.714% | 2.708% | 2.706% | 2.712% | 2.727%
CA-Emerald | 6085_Tieri Tee - Tieri 66 kV | Limiting Line Name | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1
CA-Emerald | 6085_Tieri Tee - Tieri 66 kV | Loading (A) | 6.5948 | 6.5805 | 6.5756 | 6.5895 | 6.6265
CA-Emerald | 6085_Tieri Tee - Tieri 66 kV | Loading (MVA) | 0.77673 | 0.77507 | 0.77453 | 0.77619 | 0.78056
CA-Emerald | 6085_Tieri Tee - Tieri 66 kV | Loading (MW) | 0.76864 | 0.76696 | 0.7664 | 0.76809 | 0.7725
CA-Emerald | 6085_Tieri Tee - Tieri 66 kV | Power Factor | 0.98958 | 0.98953 | 0.98951 | 0.98956 | 0.98969
CA-Emerald | 6085_Tieri Tee - Tieri 66 kV | Rating (A) | 243 | 243 | 243 | 243 | 243
CA-Emerald | 6085_Tieri Tee - Tieri 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Emerald | 6085_Tieri Tee - Tieri 66 kV | Min Voltage at Constrained Conductor | 67.9766 | 67.9789 | 67.9821 | 67.9842 | 67.9853
CA-Emerald | 6085_Tieri Tee - Tieri 66 kV | Contingency Outage | 6067 Lilyvale - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV
CA-Emerald | 6086_Tieri Tee - Middlemount 66 kV | % of Rated A | 27.18% | 27.08% | 27% | 26.94% | 26.91%
CA-Emerald | 6086_Tieri Tee - Middlemount 66 kV | Limiting Line Name | TR_LINE 16972_1 | TR_LINE 16972_1 | TR_LINE 16972_1 | TR_LINE 16972_1 | TR_LINE 16972_1
CA-Emerald | 6086_Tieri Tee - Middlemount 66 kV | Loading (A) | 66.0516 | 65.809 | 65.6176 | 65.4714 | 65.4015
CA-Emerald | 6086_Tieri Tee - Middlemount 66 kV | Loading (MVA) | 7.7783 | 7.75 | 7.7279 | 7.7109 | 7.7028
CA-Emerald | 6086_Tieri Tee - Middlemount 66 kV | Loading (MW) | 7.7656 | 7.7371 | 7.7148 | 7.6978 | 7.6896
CA-Emerald | 6086_Tieri Tee - Middlemount 66 kV | Power Factor | 0.99837 | 0.99834 | 0.99831 | 0.9983 | 0.99829
CA-Emerald | 6086_Tieri Tee - Middlemount 66 kV | Rating (A) | 243 | 243 | 243 | 243 | 243
CA-Emerald | 6086_Tieri Tee - Middlemount 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Emerald | 6086_Tieri Tee - Middlemount 66 kV | Min Voltage at Constrained Conductor | 67.2757 | 67.2811 | 67.2868 | 67.2908 | 67.293
CA-Emerald | 6086_Tieri Tee - Middlemount 66 kV | Contingency Outage | 6067 Lilyvale - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV
CA-Emerald | 7153_Lilyvale - Clermont 132 kV | % of Rated A | 17.74% | 17.62% | 17.54% | 17.46% | 17.41%
CA-Emerald | 7153_Lilyvale - Clermont 132 kV | Limiting Line Name | TR_LINE 52800_1 | TR_LINE 52800_1 | TR_LINE 52800_1 | TR_LINE 52800_1 | TR_LINE 52800_1
CA-Emerald | 7153_Lilyvale - Clermont 132 kV | Loading (A) | 125.5788 | 124.7747 | 124.1603 | 123.6265 | 123.244
CA-Emerald | 7153_Lilyvale - Clermont 132 kV | Loading (MVA) | 30.8052 | 30.608 | 30.457 | 30.309 | 30.2172
CA-Emerald | 7153_Lilyvale - Clermont 132 kV | Loading (MW) | 15.7077 | 15.169 | 14.7479 | 14.4053 | 14.1317
CA-Emerald | 7153_Lilyvale - Clermont 132 kV | Power Factor | 0.5099 | 0.49559 | 0.48422 | 0.47528 | 0.46767
CA-Emerald | 7153_Lilyvale - Clermont 132 kV | Rating (A) | 708 | 708 | 708 | 708 | 708
CA-Emerald | 7153_Lilyvale - Clermont 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Emerald | 7153_Lilyvale - Clermont 132 kV | Min Voltage at Constrained Conductor | 141.6272 | 141.6275 | 141.6263 | 141.5467 | 141.5558
CA-Emerald | 7153_Lilyvale - Clermont 132 kV | Contingency Outage | 6011_Blackwater - Comet 66 kV | 6056_Comet - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6068_Lilyvale - Ensham Mine 66 kV | 6068_Lilyvale - Ensham Mine 66 kV
CA-Emerald | 7154_Clermont - Barcaldine 132 kV | % of Rated A | 22.57% | 22.58% | 22.59% | 22.6% | 22.61%
CA-Emerald | 7154_Clermont - Barcaldine 132 kV | Limiting Line Name | TR_LINE 52329_1 | TR_LINE 52329_1 | TR_LINE 52329_1 | TR_LINE 52329_1 | TR_LINE 52329_1
CA-Emerald | 7154_Clermont - Barcaldine 132 kV | Loading (A) | 81.2657 | 81.3043 | 81.3379 | 81.3739 | 81.4087
CA-Emerald | 7154_Clermont - Barcaldine 132 kV | Loading (MVA) | 20.8038 | 20.8228 | 20.837 | 20.8515 | 20.8651
CA-Emerald | 7154_Clermont - Barcaldine 132 kV | Loading (MW) | 2.3055 | 1.9536 | 1.6764 | 1.4499 | 1.2693
CA-Emerald | 7154_Clermont - Barcaldine 132 kV | Power Factor | 0.11082 | 0.09382 | 0.080451 | 0.069494 | 0.060622
CA-Emerald | 7154_Clermont - Barcaldine 132 kV | Rating (A) | 360 | 360 | 360 | 360 | 360
CA-Emerald | 7154_Clermont - Barcaldine 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Emerald | 7154_Clermont - Barcaldine 132 kV | Min Voltage at Constrained Conductor | 147.8003 | 147.8647 | 147.9046 | 147.9417 | 147.9751
CA-Emerald | 7154_Clermont - Barcaldine 132 kV | Contingency Outage | 6073_Clermont - Blair Athol 66 kV | 6073_Clermont - Blair Athol 66 kV | 6073_Clermont - Blair Athol 66 kV | 6073_Clermont - Blair Athol 66 kV | 6073_Clermont - Blair Athol 66 kV
CA-Emerald | 7450_Memooloo - Rolleston 132 kV | % of Rated A | 10.12% | 10.08% | 10.88% | 10.85% | 10.83%
CA-Emerald | 7450_Memooloo - Rolleston 132 kV | Limiting Line Name | TR_LINE 200880_1 | TR_LINE 200880_1 | TR_LINE 200880_1 | TR_LINE 200880_1 | TR_LINE 200880_1
CA-Emerald | 7450_Memooloo - Rolleston 132 kV | Loading (A) | 71.3657 | 71.0885 | 76.6886 | 76.4964 | 76.3329
CA-Emerald | 7450_Memooloo - Rolleston 132 kV | Loading (MVA) | 17.3329 | 17.2662 | 18.6127 | 18.5665 | 18.5273
CA-Emerald | 7450_Memooloo - Rolleston 132 kV | Loading (MW) | 17.2245 | 17.1568 | 18.5216 | 18.4749 | 18.4351
CA-Emerald | 7450_Memooloo - Rolleston 132 kV | Power Factor | 0.99375 | 0.99367 | 0.99511 | 0.99506 | 0.99502
CA-Emerald | 7450_Memooloo - Rolleston 132 kV | Rating (A) | 705 | 705 | 705 | 705 | 705
CA-Emerald | 7450_Memooloo - Rolleston 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Emerald | 7450_Memooloo - Rolleston 132 kV | Min Voltage at Constrained Conductor | 139.8667 | 139.8739 | 139.7256 | 139.7308 | 139.7352
CA-Emerald | 7450_Memooloo - Rolleston 132 kV | Contingency Outage | 6106_Shale Oil Tee - Shale Oil 66kV | 6106_Shale Oil Tee - Shale Oil 66kV | 6106_Shale Oil Tee - Shale Oil 66kV | 6106_Shale Oil Tee - Shale Oil 66kV | 6106_Shale Oil Tee - Shale Oil 66kV
CA-Gladstone Rockhampton | 6001_Glenmore - Parkhurst 66 kV | % of Rated A | 12.34% | 11.26% | 10.8% | 12.3% | 13.94%
CA-Gladstone Rockhampton | 6001_Glenmore - Parkhurst 66 kV | Limiting Line Name | TR_LINE 22133_1 | TR_LINE 22133_1 | TR_LINE 22133_1 | TR_LINE 21203_1 | TR_LINE 21203_1
CA-Gladstone Rockhampton | 6001_Glenmore - Parkhurst 66 kV | Loading (A) | 49.5026 | 45.1357 | 43.2997 | 49.3389 | 55.9047
CA-Gladstone Rockhampton | 6001_Glenmore - Parkhurst 66 kV | Loading (MVA) | 5.9526 | 5.4289 | 5.2144 | 5.9611 | 6.7552
CA-Gladstone Rockhampton | 6001_Glenmore - Parkhurst 66 kV | Loading (MW) | 4.7875 | 4.5803 | 5.2141 | 5.958 | 6.7458
CA-Gladstone Rockhampton | 6001_Glenmore - Parkhurst 66 kV | Power Factor | 0.80427 | 0.84366 | 0.99992 | 0.99948 | 0.99861
CA-Gladstone Rockhampton | 6001_Glenmore - Parkhurst 66 kV | Rating (A) | 401 | 401 | 401 | 401 | 401
CA-Gladstone Rockhampton | 6001_Glenmore - Parkhurst 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6001_Glenmore - Parkhurst 66 kV | Min Voltage at Constrained Conductor | 69.4254 | 69.4438 | 69.5273 | 69.5645 | 69.5562
CA-Gladstone Rockhampton | 6001_Glenmore - Parkhurst 66 kV | Contingency Outage | 6087_Glenmore - QMAG Tee 66 kV | 6088_QMAG Tee - Parkhurst 66 kV | 6088_QMAG Tee - Parkhurst 66 kV | 6088_QMAG Tee - Parkhurst 66 kV | 6088_QMAG Tee - Parkhurst 66 kV
CA-Gladstone Rockhampton | 6003_Glenmore - Berserker 66 kV | % of Rated A | 26.66% | 26.04% | 27.13% | 30.9% | 36.13%
CA-Gladstone Rockhampton | 6003_Glenmore - Berserker 66 kV | Limiting Line Name | TR_LINE 22137_1 | TR_LINE 22137_1 | TR_LINE 22137_1 | TR_LINE 22137_1 | TR_LINE 22137_1
CA-Gladstone Rockhampton | 6003_Glenmore - Berserker 66 kV | Loading (A) | 106.9224 | 104.4169 | 108.776 | 123.9085 | 144.8721
CA-Gladstone Rockhampton | 6003_Glenmore - Berserker 66 kV | Loading (MVA) | 12.8589 | 12.5751 | 13.1068 | 14.9377 | 17.462
CA-Gladstone Rockhampton | 6003_Glenmore - Berserker 66 kV | Loading (MW) | 3.0617 | 0.65858 | 6.3153 | 9.7952 | 13.6178
CA-Gladstone Rockhampton | 6003_Glenmore - Berserker 66 kV | Power Factor | 0.23805 | 0.052315 | 0.48179 | 0.65571 | 0.77986
CA-Gladstone Rockhampton | 6003_Glenmore - Berserker 66 kV | Rating (A) | 401 | 401 | 401 | 401 | 401
CA-Gladstone Rockhampton | 6003_Glenmore - Berserker 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6003_Glenmore - Berserker 66 kV | Min Voltage at Constrained Conductor | 69.4341 | 69.5312 | 69.5651 | 69.5975 | 69.5831
CA-Gladstone Rockhampton | 6003_Glenmore - Berserker 66 kV | Contingency Outage | 6096_Egan's Hill - Lakes Creek 66 kV | 6096_Egan's Hill - Lakes Creek 66 kV | 6051_Parkhurst - Keppel 66 kV | 6051_Parkhurst - Keppel 66 kV | 6051_Parkhurst - Keppel 66 kV
CA-Gladstone Rockhampton | 6004_Glenmore - Rockhampton South 66 kV | % of Rated A | 9.338% | 6.167% | 10.64% | 11.4% | 11.09%
CA-Gladstone Rockhampton | 6004_Glenmore - Rockhampton South 66 kV | Limiting Line Name | TR_LINE 139201_1 | TR_LINE 139201_1 | TR_CABLE 301_1 | TR_CABLE 301_1 | TR_CABLE 301_1
CA-Gladstone Rockhampton | 6004_Glenmore - Rockhampton South 66 kV | Loading (A) | 34.2691 | 22.6311 | 39.5979 | 42.4164 | 41.2726
CA-Gladstone Rockhampton | 6004_Glenmore - Rockhampton South 66 kV | Loading (MVA) | 4.12 | 2.7239 | 4.7698 | 5.1117 | 4.9732
CA-Gladstone Rockhampton | 6004_Glenmore - Rockhampton South 66 kV | Loading (MW) | 3.0474 | 0.22476 | 0.86058 | 2.0269 | 1.644
CA-Gladstone Rockhampton | 6004_Glenmore - Rockhampton South 66 kV | Power Factor | 0.73966 | 0.082507 | 0.18042 | 0.39651 | 0.33056
CA-Gladstone Rockhampton | 6004_Glenmore - Rockhampton South 66 kV | Rating (A) | 367 | 367 | 372 | 372 | 372
CA-Gladstone Rockhampton | 6004_Glenmore - Rockhampton South 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6004_Glenmore - Rockhampton South 66 kV | Min Voltage at Constrained Conductor | 69.4122 | 69.4913 | 69.545 | 69.5782 | 69.569
CA-Gladstone Rockhampton | 6004_Glenmore - Rockhampton South 66 kV | Contingency Outage | 6097_Egan's Hill - Canning 66 kV | 6096_Egan's Hill - Lakes Creek 66 kV | 6005_Rockhampton Glenmore-Canning 66 kV | 6005_Rockhampton Glenmore-Canning 66 kV | 6005_Rockhampton Glenmore-Canning 66 kV
CA-Gladstone Rockhampton | 6005_Rockhampton Glenmore-Canning 66 kV | % of Rated A | 12.29% | 11.13% | 12.9% | 13.24% | 13.19%
CA-Gladstone Rockhampton | 6005_Rockhampton Glenmore-Canning 66 kV | Limiting Line Name | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1
CA-Gladstone Rockhampton | 6005_Rockhampton Glenmore-Canning 66 kV | Loading (A) | 49.0235 | 44.4125 | 51.4539 | 52.8451 | 52.6249
CA-Gladstone Rockhampton | 6005_Rockhampton Glenmore-Canning 66 kV | Loading (MVA) | 5.8949 | 5.3411 | 6.1971 | 6.3698 | 6.3404
CA-Gladstone Rockhampton | 6005_Rockhampton Glenmore-Canning 66 kV | Loading (MW) | 3.4171 | 0.068677 | 0.09349 | 1.4535 | 1.2765
CA-Gladstone Rockhampton | 6005_Rockhampton Glenmore-Canning 66 kV | Power Factor | 0.57967 | 0.012737 | 0.014942 | 0.22818 | 0.20116
CA-Gladstone Rockhampton | 6005_Rockhampton Glenmore-Canning 66 kV | Rating (A) | 399 | 399 | 399 | 399 | 399
CA-Gladstone Rockhampton | 6005_Rockhampton Glenmore-Canning 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6005_Rockhampton Glenmore-Canning 66 kV | Min Voltage at Constrained Conductor | 69.4239 | 69.4329 | 69.5359 | 69.5918 | 69.5614
CA-Gladstone Rockhampton | 6005_Rockhampton Glenmore-Canning 66 kV | Contingency Outage | 6097_Egan's Hill - Canning 66 kV | 6003_Glenmore - Berserker 66 kV | 6310_Lakes Creek - Berserker 66 kV | 6004_Glenmore - Rockhampton South 66 kV | 6310_Lakes Creek - Berserker 66 kV
CA-Gladstone Rockhampton | 6006_Glenmore - Frenchville 66 kV | % of Rated A | 11.12% | 15.09% | 17.63% | 21.47% | 26.34%
CA-Gladstone Rockhampton | 6006_Glenmore - Frenchville 66 kV | Limiting Line Name | TR_LINE 22134_1 | TR_LINE 22134_1 | TR_LINE 22209_1 | TR_LINE 22209_1 | TR_LINE 22209_1
CA-Gladstone Rockhampton | 6006_Glenmore - Frenchville 66 kV | Loading (A) | 44.5804 | 60.5058 | 70.6891 | 86.091 | 105.6046
CA-Gladstone Rockhampton | 6006_Glenmore - Frenchville 66 kV | Loading (MVA) | 5.3558 | 7.2776 | 8.5332 | 10.4116 | 12.7781
CA-Gladstone Rockhampton | 6006_Glenmore - Frenchville 66 kV | Loading (MW) | 4.7109 | 6.8778 | 8.5327 | 10.4066 | 12.7688
CA-Gladstone Rockhampton | 6006_Glenmore - Frenchville 66 kV | Power Factor | 0.87955 | 0.945 | 0.99995 | 0.99951 | 0.99927
CA-Gladstone Rockhampton | 6006_Glenmore - Frenchville 66 kV | Rating (A) | 401 | 401 | 401 | 401 | 401
CA-Gladstone Rockhampton | 6006_Glenmore - Frenchville 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6006_Glenmore - Frenchville 66 kV | Min Voltage at Constrained Conductor | 69.3619 | 69.4438 | 69.6926 | 69.8213 | 69.8565
CA-Gladstone Rockhampton | 6006_Glenmore - Frenchville 66 kV | Contingency Outage | 6088_QMAG Tee - Parkhurst 66 kV | 6088_QMAG Tee - Parkhurst 66 kV | 6088_QMAG Tee - Parkhurst 66 kV | 6050_Parkhurst - Frenchville 66 kV | 6050_Parkhurst - Frenchville 66 kV
CA-Gladstone Rockhampton | 6007_Biloela - Coominglah Tee 66 kV | % of Rated A | 14.57% | 14.48% | 14.42% | 14.39% | 14.37%
CA-Gladstone Rockhampton | 6007_Biloela - Coominglah Tee 66 kV | Limiting Line Name | TR_LINE 18121_1 | TR_LINE 18121_1 | TR_LINE 18121_1 | TR_LINE 18121_1 | TR_LINE 18121_1
CA-Gladstone Rockhampton | 6007_Biloela - Coominglah Tee 66 kV | Loading (A) | 19.2279 | 19.1086 | 19.0368 | 18.9939 | 18.9714
CA-Gladstone Rockhampton | 6007_Biloela - Coominglah Tee 66 kV | Loading (MVA) | 2.3191 | 2.3059 | 2.2972 | 2.2914 | 2.2878
CA-Gladstone Rockhampton | 6007_Biloela - Coominglah Tee 66 kV | Loading (MW) | 0.45625 | 0.34053 | 0.24679 | 0.16753 | 0.10075
CA-Gladstone Rockhampton | 6007_Biloela - Coominglah Tee 66 kV | Power Factor | 0.19674 | 0.14768 | 0.10743 | 0.073112 | 0.044041
CA-Gladstone Rockhampton | 6007_Biloela - Coominglah Tee 66 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
CA-Gladstone Rockhampton | 6007_Biloela - Coominglah Tee 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6007_Biloela - Coominglah Tee 66 kV | Min Voltage at Constrained Conductor | 69.6349 | 69.671 | 69.6702 | 69.6498 | 69.6229
CA-Gladstone Rockhampton | 6007_Biloela - Coominglah Tee 66 kV | Contingency Outage | 6196_Callide Mine 66 kV | 6196_Callide Mine 66 kV | 6196_Callide Mine 66 kV | 6196_Callide Mine 66 kV | 6196_Callide Mine 66 kV
CA-Gladstone Rockhampton | 6008_Biloela - Wowan 66 kV | % of Rated A | 6.962% | 6.701% | 6.54% | 6.441% | 6.383%
CA-Gladstone Rockhampton | 6008_Biloela - Wowan 66 kV | Limiting Line Name | TR_LINE 21790_1 | TR_LINE 21790_1 | TR_LINE 21790_1 | TR_LINE 21790_1 | TR_LINE 21790_1
CA-Gladstone Rockhampton | 6008_Biloela - Wowan 66 kV | Loading (A) | 9.1893 | 8.8453 | 8.6327 | 8.5016 | 8.4249
CA-Gladstone Rockhampton | 6008_Biloela - Wowan 66 kV | Loading (MVA) | 1.1083 | 1.0674 | 1.0417 | 1.0256 | 1.016
CA-Gladstone Rockhampton | 6008_Biloela - Wowan 66 kV | Loading (MW) | 0.47052 | 0.35541 | 0.26369 | 0.1884 | 0.12666
CA-Gladstone Rockhampton | 6008_Biloela - Wowan 66 kV | Power Factor | 0.42453 | 0.33296 | 0.25313 | 0.1837 | 0.12467
CA-Gladstone Rockhampton | 6008_Biloela - Wowan 66 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
CA-Gladstone Rockhampton | 6008_Biloela - Wowan 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6008_Biloela - Wowan 66 kV | Min Voltage at Constrained Conductor | 69.6351 | 69.6713 | 69.6706 | 69.6502 | 69.6234
CA-Gladstone Rockhampton | 6008_Biloela - Wowan 66 kV | Contingency Outage | 6196_Callide Mine 66 kV | 6196_Callide Mine 66 kV | 6196_Callide Mine 66 kV | 6196_Callide Mine 66 kV | 6196_Callide Mine 66 kV
CA-Gladstone Rockhampton | 6019_Gladstone South - Friend St 66 kV | % of Rated A | 33.52% | 32.39% | 32.04% | 31.62% | 46.16%
CA-Gladstone Rockhampton | 6019_Gladstone South - Friend St 66 kV | Limiting Line Name | TR_LINE 22252_1 | TR_LINE 22252_1 | TR_LINE 22252_1 | TR_LINE 22252_1 | TR_LINE 22252_1
CA-Gladstone Rockhampton | 6019_Gladstone South - Friend St 66 kV | Loading (A) | 82.1157 | 79.3654 | 78.5092 | 77.4773 | 113.0799
CA-Gladstone Rockhampton | 6019_Gladstone South - Friend St 66 kV | Loading (MVA) | 9.7119 | 9.4018 | 9.3007 | 9.1513 | 13.3671
CA-Gladstone Rockhampton | 6019_Gladstone South - Friend St 66 kV | Loading (MW) | 5.6647 | 5.0555 | 4.7419 | 4.3772 | 1.8553
CA-Gladstone Rockhampton | 6019_Gladstone South - Friend St 66 kV | Power Factor | 0.58326 | 0.53771 | 0.50983 | 0.47831 | 0.13871
CA-Gladstone Rockhampton | 6019_Gladstone South - Friend St 66 kV | Rating (A) | 245 | 245 | 245 | 245 | 245
CA-Gladstone Rockhampton | 6019_Gladstone South - Friend St 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6019_Gladstone South - Friend St 66 kV | Min Voltage at Constrained Conductor | 68.2836 | 68.3938 | 68.3966 | 68.1941 | 68.2479
CA-Gladstone Rockhampton | 6019_Gladstone South - Friend St 66 kV | Contingency Outage | 6109_Gladstone North - Clinton 66 kV | 6109_Gladstone North - Clinton 66 kV | 6109_Gladstone North - Clinton 66 kV | 6109_Gladstone North - Clinton 66 kV | 6031_Calliope - Littlemore 66 kV
CA-Gladstone Rockhampton | 6020_Gladstone South - BORE 66 kV | % of Rated A | 14.55% | 13.44% | 14.54% | 15.73% | 17.01%
CA-Gladstone Rockhampton | 6020_Gladstone South - BORE 66 kV | Limiting Line Name | TR_LINE 215689_1 | TR_LINE 215689_1 | TR_LINE 215689_1 | TR_LINE 215689_1 | TR_LINE 215689_1
CA-Gladstone Rockhampton | 6020_Gladstone South - BORE 66 kV | Loading (A) | 30.7026 | 28.3666 | 30.6864 | 33.1933 | 35.8969
CA-Gladstone Rockhampton | 6020_Gladstone South - BORE 66 kV | Loading (MVA) | 3.6363 | 3.3643 | 3.6403 | 3.9266 | 4.2573
CA-Gladstone Rockhampton | 6020_Gladstone South - BORE 66 kV | Loading (MW) | 1.8278 | 1.204 | 1.8383 | 2.3831 | 2.8833
CA-Gladstone Rockhampton | 6020_Gladstone South - BORE 66 kV | Power Factor | 0.5026 | 0.3578 | 0.50494 | 0.60684 | 0.67717
CA-Gladstone Rockhampton | 6020_Gladstone South - BORE 66 kV | Rating (A) | 211 | 211 | 211 | 211 | 211
CA-Gladstone Rockhampton | 6020_Gladstone South - BORE 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6020_Gladstone South - BORE 66 kV | Min Voltage at Constrained Conductor | 68.3784 | 68.4751 | 68.4897 | 68.2975 | 68.473
CA-Gladstone Rockhampton | 6020_Gladstone South - BORE 66 kV | Contingency Outage | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV
CA-Gladstone Rockhampton | 6022_Gladstone South - Calliope 66 kV | % of Rated A | 4.925% | 4.556% | 4.923% | 5.321% | 5.755%
CA-Gladstone Rockhampton | 6022_Gladstone South - Calliope 66 kV | Limiting Line Name | TR_LINE 72653_1 | TR_LINE 72653_1 | TR_LINE 72653_1 | TR_LINE 72653_1 | TR_LINE 72653_1
CA-Gladstone Rockhampton | 6022_Gladstone South - Calliope 66 kV | Loading (A) | 30.6822 | 28.3841 | 30.672 | 33.1525 | 35.8515
CA-Gladstone Rockhampton | 6022_Gladstone South - Calliope 66 kV | Loading (MVA) | 3.6373 | 3.3698 | 3.642 | 3.9253 | 4.2556
CA-Gladstone Rockhampton | 6022_Gladstone South - Calliope 66 kV | Loading (MW) | 1.8378 | 1.2158 | 1.8498 | 2.3945 | 2.8953
CA-Gladstone Rockhampton | 6022_Gladstone South - Calliope 66 kV | Power Factor | 0.50502 | 0.36055 | 0.50765 | 0.60973 | 0.68004
CA-Gladstone Rockhampton | 6022_Gladstone South - Calliope 66 kV | Rating (A) | 623 | 623 | 623 | 623 | 623
CA-Gladstone Rockhampton | 6022_Gladstone South - Calliope 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6022_Gladstone South - Calliope 66 kV | Min Voltage at Constrained Conductor | 68.4432 | 68.543 | 68.5545 | 68.3592 | 68.5325
CA-Gladstone Rockhampton | 6022_Gladstone South - Calliope 66 kV | Contingency Outage | 6020_Gladstone South - BORE 66 kV | 6020_Gladstone South - BORE 66 kV | 6020_Gladstone South - BORE 66 kV | 6020_Gladstone South - BORE 66 kV | 6020_Gladstone South - BORE 66 kV
CA-Gladstone Rockhampton | 6023_Friend St-Clinton Industrial 66 kV | % of Rated A | 12.99% | 12.6% | 12.31% | 12.05% | 13.66%
CA-Gladstone Rockhampton | 6023_Friend St-Clinton Industrial 66 kV | Limiting Line Name | TR_LINE 22245_1 | TR_LINE 22245_1 | TR_LINE 22245_1 | TR_LINE 22245_1 | TR_LINE 22275_1
CA-Gladstone Rockhampton | 6023_Friend St-Clinton Industrial 66 kV | Loading (A) | 57.2905 | 55.5808 | 54.2791 | 53.1558 | 59.9788
CA-Gladstone Rockhampton | 6023_Friend St-Clinton Industrial 66 kV | Loading (MVA) | 6.8234 | 6.631 | 6.4761 | 6.324 | 7.1232
CA-Gladstone Rockhampton | 6023_Friend St-Clinton Industrial 66 kV | Loading (MW) | 3.0806 | 2.5516 | 2.0898 | 1.6639 | 0.5642
CA-Gladstone Rockhampton | 6023_Friend St-Clinton Industrial 66 kV | Power Factor | 0.45147 | 0.38481 | 0.3227 | 0.26311 | 0.07919
CA-Gladstone Rockhampton | 6023_Friend St-Clinton Industrial 66 kV | Rating (A) | 441 | 441 | 441 | 441 | 439
CA-Gladstone Rockhampton | 6023_Friend St-Clinton Industrial 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6023_Friend St-Clinton Industrial 66 kV | Min Voltage at Constrained Conductor | 68.7635 | 68.8796 | 68.8847 | 68.6878 | 68.5669
CA-Gladstone Rockhampton | 6023_Friend St-Clinton Industrial 66 kV | Contingency Outage | 6019_Gladstone South - Friend St 66 kV | 6019_Gladstone South - Friend St 66 kV | 6019_Gladstone South - Friend St 66 kV | 6019_Gladstone South - Friend St 66 kV | 6031_Calliope - Littlemore 66 kV
CA-Gladstone Rockhampton | 6024_Awoonga - Calliope 66kV | % of Rated A | 14.43% | 14.5% | 14.82% | 15.24% | 15.84%
CA-Gladstone Rockhampton | 6024_Awoonga - Calliope 66kV | Limiting Line Name | TR_LINE 181307_1 | TR_LINE 181307_1 | TR_LINE 181307_1 | TR_LINE 181307_1 | TR_LINE 181307_1
CA-Gladstone Rockhampton | 6024_Awoonga - Calliope 66kV | Loading (A) | 24.3898 | 24.4968 | 25.0435 | 25.7634 | 26.7745
CA-Gladstone Rockhampton | 6024_Awoonga - Calliope 66kV | Loading (MVA) | 2.9048 | 2.9192 | 2.9866 | 3.0652 | 3.1951
CA-Gladstone Rockhampton | 6024_Awoonga - Calliope 66kV | Loading (MW) | 0.18341 | 0.287 | 0.67261 | 1.0061 | 1.3172
CA-Gladstone Rockhampton | 6024_Awoonga - Calliope 66kV | Power Factor | 0.06314 | 0.096171 | 0.22301 | 0.32594 | 0.40988
CA-Gladstone Rockhampton | 6024_Awoonga - Calliope 66kV | Rating (A) | 169 | 169 | 169 | 169 | 169
CA-Gladstone Rockhampton | 6024_Awoonga - Calliope 66kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6024_Awoonga - Calliope 66kV | Min Voltage at Constrained Conductor | 68.7615 | 68.8006 | 68.8525 | 68.6914 | 68.8968
CA-Gladstone Rockhampton | 6024_Awoonga - Calliope 66kV | Contingency Outage | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV
CA-Gladstone Rockhampton | 6029_Littlemore - Miriam Vale 66 kV | % of Rated A | 3.324% | 3.587% | 3.805% | 4% | 4.159%
CA-Gladstone Rockhampton | 6029_Littlemore - Miriam Vale 66 kV | Limiting Line Name | TR_LINE 16162_1 | TR_LINE 16162_1 | TR_LINE 16162_1 | TR_LINE 16162_1 | TR_LINE 16162_1
CA-Gladstone Rockhampton | 6029_Littlemore - Miriam Vale 66 kV | Loading (A) | 4.3882 | 4.7354 | 5.0232 | 5.2801 | 5.4905
CA-Gladstone Rockhampton | 6029_Littlemore - Miriam Vale 66 kV | Loading (MVA) | 0.52349 | 0.56593 | 0.60062 | 0.62972 | 0.65662
CA-Gladstone Rockhampton | 6029_Littlemore - Miriam Vale 66 kV | Loading (MW) | 0.43394 | 0.48399 | 0.52426 | 0.55841 | 0.58794
CA-Gladstone Rockhampton | 6029_Littlemore - Miriam Vale 66 kV | Power Factor | 0.82892 | 0.85521 | 0.87286 | 0.88676 | 0.89539
CA-Gladstone Rockhampton | 6029_Littlemore - Miriam Vale 66 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
CA-Gladstone Rockhampton | 6029_Littlemore - Miriam Vale 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6029_Littlemore - Miriam Vale 66 kV | Min Voltage at Constrained Conductor | 68.8752 | 68.9995 | 69.0334 | 68.8567 | 69.0464
CA-Gladstone Rockhampton | 6029_Littlemore - Miriam Vale 66 kV | Contingency Outage | 6030_Littlemore - Monto 66 kV | 6030_Littlemore - Monto 66 kV | 6030_Littlemore - Monto 66 kV | 6030_Littlemore - Monto 66 kV | 6030_Littlemore - Monto 66 kV
CA-Gladstone Rockhampton | 6030_Littlemore - Monto 66 kV | % of Rated A | 5.428% | 5.37% | 5.373% | 5.425% | 5.42%
CA-Gladstone Rockhampton | 6030_Littlemore - Monto 66 kV | Limiting Line Name | TR_LINE 19505_1 | TR_LINE 19505_1 | TR_LINE 19505_1 | TR_LINE 19505_1 | TR_LINE 19505_1
CA-Gladstone Rockhampton | 6030_Littlemore - Monto 66 kV | Loading (A) | 7.1644 | 7.0889 | 7.0926 | 7.1612 | 7.155
CA-Gladstone Rockhampton | 6030_Littlemore - Monto 66 kV | Loading (MVA) | 0.87748 | 0.85908 | 0.85997 | 0.8767 | 0.87518
CA-Gladstone Rockhampton | 6030_Littlemore - Monto 66 kV | Loading (MW) | 0.0016046 | 0.0015709 | 0.0015726 | 0.0016032 | 0.0016004
CA-Gladstone Rockhampton | 6030_Littlemore - Monto 66 kV | Power Factor | 0.001768 | 0.001768 | 0.001768 | 0.001768 | 0.001768
CA-Gladstone Rockhampton | 6030_Littlemore - Monto 66 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
CA-Gladstone Rockhampton | 6030_Littlemore - Monto 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6030_Littlemore - Monto 66 kV | Min Voltage at Constrained Conductor | 70.712 | 69.9667 | 70.0031 | 70.6806 | 70.6194
CA-Gladstone Rockhampton | 6030_Littlemore - Monto 66 kV | Contingency Outage | 6019_Gladstone South - Friend St 66 kV | 6019_Gladstone South - Friend St 66 kV | 6022_Gladstone South - Calliope 66 kV | 6019_Gladstone South - Friend St 66 kV | 6019_Gladstone South - Friend St 66 kV
CA-Gladstone Rockhampton | 6031_Calliope - Littlemore 66 kV | % of Rated A | 13.66% | 13.64% | 13.74% | 13.93% | 13.99%
CA-Gladstone Rockhampton | 6031_Calliope - Littlemore 66 kV | Limiting Line Name | TR_LINE 13872_1 | TR_LINE 13872_1 | TR_LINE 13872_1 | TR_LINE 13872_1 | TR_LINE 13872_1
CA-Gladstone Rockhampton | 6031_Calliope - Littlemore 66 kV | Loading (A) | 18.0367 | 18.004 | 18.1332 | 18.3852 | 18.4676
CA-Gladstone Rockhampton | 6031_Calliope - Littlemore 66 kV | Loading (MVA) | 2.1826 | 2.1548 | 2.1708 | 2.222 | 2.2296
CA-Gladstone Rockhampton | 6031_Calliope - Littlemore 66 kV | Loading (MW) | 0.49401 | 0.56394 | 0.61936 | 0.66481 | 0.70408
CA-Gladstone Rockhampton | 6031_Calliope - Littlemore 66 kV | Power Factor | 0.22615 | 0.26152 | 0.28511 | 0.299 | 0.3156
CA-Gladstone Rockhampton | 6031_Calliope - Littlemore 66 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
CA-Gladstone Rockhampton | 6031_Calliope - Littlemore 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6031_Calliope - Littlemore 66 kV | Min Voltage at Constrained Conductor | 69.8633 | 69.1002 | 69.118 | 69.776 | 69.7023
CA-Gladstone Rockhampton | 6031_Calliope - Littlemore 66 kV | Contingency Outage | 6019_Gladstone South - Friend St 66 kV | 6019_Gladstone South - Friend St 66 kV | 6022_Gladstone South - Calliope 66 kV | 6019_Gladstone South - Friend St 66 kV | 6019_Gladstone South - Friend St 66 kV
CA-Gladstone Rockhampton | 6032_Boyne Residential Tee-Awoonga 66 kV | % of Rated A | 11.51% | 12.01% | 11.67% | 11.51% | 11.56%
CA-Gladstone Rockhampton | 6032_Boyne Residential Tee-Awoonga 66 kV | Limiting Line Name | TR_LINE 69280_1 | TR_LINE 69280_1 | TR_LINE 69280_1 | TR_LINE 69280_1 | TR_LINE 69280_1
CA-Gladstone Rockhampton | 6032_Boyne Residential Tee-Awoonga 66 kV | Loading (A) | 24.2853 | 25.3454 | 24.6283 | 24.2775 | 24.3849
CA-Gladstone Rockhampton | 6032_Boyne Residential Tee-Awoonga 66 kV | Loading (MVA) | 2.8852 | 3.0144 | 2.9307 | 2.8816 | 2.9025
CA-Gladstone Rockhampton | 6032_Boyne Residential Tee-Awoonga 66 kV | Loading (MW) | 0.04028 | 0.8693 | 0.46922 | 0.12464 | 0.19537
CA-Gladstone Rockhampton | 6032_Boyne Residential Tee-Awoonga 66 kV | Power Factor | 0.013879 | 0.28838 | 0.16011 | 0.043253 | 0.067231
CA-Gladstone Rockhampton | 6032_Boyne Residential Tee-Awoonga 66 kV | Rating (A) | 211 | 211 | 211 | 211 | 211
CA-Gladstone Rockhampton | 6032_Boyne Residential Tee-Awoonga 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6032_Boyne Residential Tee-Awoonga 66 kV | Min Voltage at Constrained Conductor | 68.5914 | 68.667 | 68.7026 | 68.5281 | 68.7202
CA-Gladstone Rockhampton | 6032_Boyne Residential Tee-Awoonga 66 kV | Contingency Outage | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV
CA-Gladstone Rockhampton | 6034_Boyne Residential Tee - BORE 66 kV | % of Rated A | 9.226% | 10.66% | 11.86% | 12.91% | 13.82%
CA-Gladstone Rockhampton | 6034_Boyne Residential Tee - BORE 66 kV | Limiting Line Name | TR_LINE 18809_1 | TR_LINE 18809_1 | TR_LINE 18809_1 | TR_LINE 18809_1 | TR_LINE 18809_1
CA-Gladstone Rockhampton | 6034_Boyne Residential Tee - BORE 66 kV | Loading (A) | 15.223 | 17.5961 | 19.5709 | 21.3049 | 22.8004
CA-Gladstone Rockhampton | 6034_Boyne Residential Tee - BORE 66 kV | Loading (MVA) | 1.8004 | 2.0837 | 2.318 | 2.5186 | 2.6999
CA-Gladstone Rockhampton | 6034_Boyne Residential Tee - BORE 66 kV | Loading (MW) | 1.7938 | 2.0785 | 2.3137 | 2.5149 | 2.6966
CA-Gladstone Rockhampton | 6034_Boyne Residential Tee - BORE 66 kV | Power Factor | 0.99633 | 0.99744 | 0.99807 | 0.99847 | 0.99874
CA-Gladstone Rockhampton | 6034_Boyne Residential Tee - BORE 66 kV | Rating (A) | 165 | 165 | 165 | 165 | 165
CA-Gladstone Rockhampton | 6034_Boyne Residential Tee - BORE 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6034_Boyne Residential Tee - BORE 66 kV | Min Voltage at Constrained Conductor | 68.2808 | 68.3682 | 68.3823 | 68.2526 | 68.3649
CA-Gladstone Rockhampton | 6034_Boyne Residential Tee - BORE 66 kV | Contingency Outage | 6031_Calliope - Littlemore 66 kV | 6031_Calliope - Littlemore 66 kV | 6031_Calliope - Littlemore 66 kV | 6024_Awoonga - Calliope 66kV | 6031_Calliope - Littlemore 66 kV
CA-Gladstone Rockhampton | 6039_Clinton Industrial - Beecher 66 kV | % of Rated A | 6.469% | 6.46% | 6.46% | 6.475% | 6.473%
CA-Gladstone Rockhampton | 6039_Clinton Industrial - Beecher 66 kV | Limiting Line Name | TR_LINE 33766_1 | TR_LINE 33766_1 | TR_LINE 33766_1 | TR_LINE 33766_1 | TR_LINE 33766_1
CA-Gladstone Rockhampton | 6039_Clinton Industrial - Beecher 66 kV | Loading (A) | 15.8482 | 15.826 | 15.8259 | 15.8634 | 15.8586
CA-Gladstone Rockhampton | 6039_Clinton Industrial - Beecher 66 kV | Loading (MVA) | 1.8755 | 1.876 | 1.876 | 1.8752 | 1.8753
CA-Gladstone Rockhampton | 6039_Clinton Industrial - Beecher 66 kV | Loading (MW) | 1.818 | 1.8179 | 1.8179 | 1.818 | 1.818
CA-Gladstone Rockhampton | 6039_Clinton Industrial - Beecher 66 kV | Power Factor | 0.96932 | 0.96903 | 0.96903 | 0.96952 | 0.96946
CA-Gladstone Rockhampton | 6039_Clinton Industrial - Beecher 66 kV | Rating (A) | 245 | 245 | 245 | 245 | 245
CA-Gladstone Rockhampton | 6039_Clinton Industrial - Beecher 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6039_Clinton Industrial - Beecher 66 kV | Min Voltage at Constrained Conductor | 68.3247 | 68.4387 | 68.4393 | 68.2467 | 68.2714
CA-Gladstone Rockhampton | 6039_Clinton Industrial - Beecher 66 kV | Contingency Outage | 6031_Calliope - Littlemore 66 kV | 6031_Calliope - Littlemore 66 kV | 6031_Calliope - Littlemore 66 kV | 6071_Lilyvale - Oaky Creek Mine 66 kV | 6023_Friend St-Clinton Industrial 66 kV
CA-Gladstone Rockhampton | 6041_Yarwun - Boat Creek 66 kV | % of Rated A | 11.95% | 11.94% | 11.94% | 11.97% | 11.96%
CA-Gladstone Rockhampton | 6041_Yarwun - Boat Creek 66 kV | Limiting Line Name | TR_LINE 15181_1 | TR_LINE 15181_1 | TR_LINE 15181_1 | TR_LINE 15181_1 | TR_LINE 15181_1
CA-Gladstone Rockhampton | 6041_Yarwun - Boat Creek 66 kV | Loading (A) | 15.7791 | 15.7566 | 15.7564 | 15.7946 | 15.7897
CA-Gladstone Rockhampton | 6041_Yarwun - Boat Creek 66 kV | Loading (MVA) | 1.8668 | 1.8673 | 1.8673 | 1.8665 | 1.8666
CA-Gladstone Rockhampton | 6041_Yarwun - Boat Creek 66 kV | Loading (MW) | 1.8172 | 1.8172 | 1.8172 | 1.8173 | 1.8173
CA-Gladstone Rockhampton | 6041_Yarwun - Boat Creek 66 kV | Power Factor | 0.97344 | 0.97318 | 0.97318 | 0.97362 | 0.97356
CA-Gladstone Rockhampton | 6041_Yarwun - Boat Creek 66 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
CA-Gladstone Rockhampton | 6041_Yarwun - Boat Creek 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6041_Yarwun - Boat Creek 66 kV | Min Voltage at Constrained Conductor | 68.2628 | 68.377 | 68.3776 | 68.1846 | 68.2094
CA-Gladstone Rockhampton | 6041_Yarwun - Boat Creek 66 kV | Contingency Outage | 6031_Calliope - Littlemore 66 kV | 6031_Calliope - Littlemore 66 kV | 6031_Calliope - Littlemore 66 kV | 6071_Lilyvale - Oaky Creek Mine 66 kV | 6023_Friend St-Clinton Industrial 66 kV
CA-Gladstone Rockhampton | 6044_Raglan-East End Quarry/Yarwun 66 kV | % of Rated A | 1.514% | 1.516% | 1.52% | 1.521% | 1.521%
CA-Gladstone Rockhampton | 6044_Raglan-East End Quarry/Yarwun 66 kV | Limiting Line Name | TR_LINE 22122_1 | TR_LINE 22122_1 | TR_LINE 22122_1 | TR_LINE 22122_1 | TR_LINE 22122_1
CA-Gladstone Rockhampton | 6044_Raglan-East End Quarry/Yarwun 66 kV | Loading (A) | 1.9991 | 2.0009 | 2.0065 | 2.0073 | 2.0072
CA-Gladstone Rockhampton | 6044_Raglan-East End Quarry/Yarwun 66 kV | Loading (MVA) | 0.24085 | 0.24126 | 0.24262 | 0.24282 | 0.24278
CA-Gladstone Rockhampton | 6044_Raglan-East End Quarry/Yarwun 66 kV | Loading (MW) | 3.5851e-05 | 3.5914e-05 | 3.6115e-05 | 3.6145e-05 | 3.6139e-05
CA-Gladstone Rockhampton | 6044_Raglan-East End Quarry/Yarwun 66 kV | Power Factor | 0.00014836 | 0.00014836 | 0.00014836 | 0.00014836 | 0.00014836
CA-Gladstone Rockhampton | 6044_Raglan-East End Quarry/Yarwun 66 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
CA-Gladstone Rockhampton | 6044_Raglan-East End Quarry/Yarwun 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6044_Raglan-East End Quarry/Yarwun 66 kV | Min Voltage at Constrained Conductor | 69.5561 | 69.6165 | 69.8114 | 69.8404 | 69.8349
CA-Gladstone Rockhampton | 6044_Raglan-East End Quarry/Yarwun 66 kV | Contingency Outage | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6046_Mt Morgan - Wowan 66 kV | 6005_Rockhampton Glenmore-Canning 66 kV | 6005_Rockhampton Glenmore-Canning 66 kV
CA-Gladstone Rockhampton | 6045_Coominglah Tee - Monto 66 kV | % of Rated A | 10.8% | 10.69% | 10.63% | 10.58% | 10.55%
CA-Gladstone Rockhampton | 6045_Coominglah Tee - Monto 66 kV | Limiting Line Name | TR_LINE 75765_1 | TR_LINE 75765_1 | TR_LINE 75765_1 | TR_LINE 75765_1 | TR_LINE 75765_1
CA-Gladstone Rockhampton | 6045_Coominglah Tee - Monto 66 kV | Loading (A) | 14.2509 | 14.1127 | 14.0253 | 13.9677 | 13.9318
CA-Gladstone Rockhampton | 6045_Coominglah Tee - Monto 66 kV | Loading (MVA) | 1.7298 | 1.7149 | 1.705 | 1.6981 | 1.6936
CA-Gladstone Rockhampton | 6045_Coominglah Tee - Monto 66 kV | Loading (MW) | 0.42575 | 0.33331 | 0.25983 | 0.19861 | 0.14901
CA-Gladstone Rockhampton | 6045_Coominglah Tee - Monto 66 kV | Power Factor | 0.24612 | 0.19436 | 0.15239 | 0.11696 | 0.087982
CA-Gladstone Rockhampton | 6045_Coominglah Tee - Monto 66 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
CA-Gladstone Rockhampton | 6045_Coominglah Tee - Monto 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6045_Coominglah Tee - Monto 66 kV | Min Voltage at Constrained Conductor | 70.0815 | 70.156 | 70.1859 | 70.1912 | 70.1859
CA-Gladstone Rockhampton | 6045_Coominglah Tee - Monto 66 kV | Contingency Outage | 6196_Callide Mine 66 kV | 6196_Callide Mine 66 kV | 6196_Callide Mine 66 kV | 6196_Callide Mine 66 kV | 6196_Callide Mine 66 kV
CA-Gladstone Rockhampton | 6046_Mt Morgan - Wowan 66 kV | % of Rated A | 4.359% | 43.67% | 85.82% | 86.38% | 86.41%
CA-Gladstone Rockhampton | 6046_Mt Morgan - Wowan 66 kV | Limiting Line Name | TR_LINE 22233_1 | TR_LINE 22233_1 | TR_LINE 22233_1 | TR_LINE 22233_1 | TR_LINE 22233_1
CA-Gladstone Rockhampton | 6046_Mt Morgan - Wowan 66 kV | Loading (A) | 5.7533 | 57.6453 | 113.2788 | 114.0274 | 114.0551
CA-Gladstone Rockhampton | 6046_Mt Morgan - Wowan 66 kV | Loading (MVA) | 0.69565 | 6.8399 | 13.2651 | 13.2655 | 13.2655
CA-Gladstone Rockhampton | 6046_Mt Morgan - Wowan 66 kV | Loading (MW) | 0.30049 | 6.8143 | 13.2543 | 13.255 | 13.255
CA-Gladstone Rockhampton | 6046_Mt Morgan - Wowan 66 kV | Power Factor | 0.43196 | 0.99626 | 0.99918 | 0.99921 | 0.99921
CA-Gladstone Rockhampton | 6046_Mt Morgan - Wowan 66 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
CA-Gladstone Rockhampton | 6046_Mt Morgan - Wowan 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6046_Mt Morgan - Wowan 66 kV | Min Voltage at Constrained Conductor | 69.8087 | 68.5038 | 67.6058 | 67.1638 | 67.1476
CA-Gladstone Rockhampton | 6046_Mt Morgan - Wowan 66 kV | Contingency Outage | 6003_Glenmore - Berserker 66 kV | 6094_Malchi Tee - Malchi 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV
CA-Gladstone Rockhampton | 6047_Coominglah Sub Tee 66 kV | % of Rated A | 0.06305% | 0.0614% | 0.1693% | 0.2659% | 0.3582%
CA-Gladstone Rockhampton | 6047_Coominglah Sub Tee 66 kV | Limiting Line Name | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1
CA-Gladstone Rockhampton | 6047_Coominglah Sub Tee 66 kV | Loading (A) | 0.0971 | 0.094558 | 0.26068 | 0.40941 | 0.55156
CA-Gladstone Rockhampton | 6047_Coominglah Sub Tee 66 kV | Loading (MVA) | 0.011695 | 0.011396 | 0.03142 | 0.049336 | 0.066445
CA-Gladstone Rockhampton | 6047_Coominglah Sub Tee 66 kV | Loading (MW) | 0.01163 | 0.01133 | 0.031397 | 0.049322 | 0.066436
CA-Gladstone Rockhampton | 6047_Coominglah Sub Tee 66 kV | Power Factor | 0.99446 | 0.99415 | 0.99926 | 0.99972 | 0.99986
CA-Gladstone Rockhampton | 6047_Coominglah Sub Tee 66 kV | Rating (A) | 154 | 154 | 154 | 154 | 154
CA-Gladstone Rockhampton | 6047_Coominglah Sub Tee 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6047_Coominglah Sub Tee 66 kV | Min Voltage at Constrained Conductor | 69.5396 | 69.5825 | 69.5876 | 69.5726 | 69.551
CA-Gladstone Rockhampton | 6047_Coominglah Sub Tee 66 kV | Contingency Outage | 6045_Coominglah Tee - Monto 66 kV | 6045_Coominglah Tee - Monto 66 kV | 6045_Coominglah Tee - Monto 66 kV | 6045_Coominglah Tee - Monto 66 kV | 6045_Coominglah Tee - Monto 66 kV
CA-Gladstone Rockhampton | 6050_Parkhurst - Frenchville 66 kV | % of Rated A | 13.5% | 13.55% | 17% | 21.46% | 26.31%
CA-Gladstone Rockhampton | 6050_Parkhurst - Frenchville 66 kV | Limiting Line Name | TR_LINE 22210_1 | TR_LINE 22210_1 | TR_LINE 22210_1 | TR_LINE 22210_1 | TR_LINE 22210_1
CA-Gladstone Rockhampton | 6050_Parkhurst - Frenchville 66 kV | Loading (A) | 54.1182 | 54.3249 | 68.1516 | 86.0396 | 105.5076
CA-Gladstone Rockhampton | 6050_Parkhurst - Frenchville 66 kV | Loading (MVA) | 6.5132 | 6.5491 | 8.2352 | 10.4116 | 12.7781
CA-Gladstone Rockhampton | 6050_Parkhurst - Frenchville 66 kV | Loading (MW) | 5.8273 | 5.9241 | 8.2327 | 10.4066 | 12.7688
CA-Gladstone Rockhampton | 6050_Parkhurst - Frenchville 66 kV | Power Factor | 0.89468 | 0.90457 | 0.9997 | 0.99952 | 0.99927
CA-Gladstone Rockhampton | 6050_Parkhurst - Frenchville 66 kV | Rating (A) | 401 | 401 | 401 | 401 | 401
CA-Gladstone Rockhampton | 6050_Parkhurst - Frenchville 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6050_Parkhurst - Frenchville 66 kV | Min Voltage at Constrained Conductor | 69.485 | 69.6013 | 69.7634 | 69.8627 | 69.9204
CA-Gladstone Rockhampton | 6050_Parkhurst - Frenchville 66 kV | Contingency Outage | 6087_Glenmore - QMAG Tee 66 kV | 6087_Glenmore - QMAG Tee 66 kV | 6006_Glenmore - Frenchville 66 kV | 6006_Glenmore - Frenchville 66 kV | 6006_Glenmore - Frenchville 66 kV
CA-Gladstone Rockhampton | 6051_Parkhurst - Keppel 66 kV | % of Rated A | 20.78% | 33.67% | 46.62% | 59.37% | 73.11%
CA-Gladstone Rockhampton | 6051_Parkhurst - Keppel 66 kV | Limiting Line Name | TR_LINE 19655_1 | TR_LINE 19655_1 | TR_LINE 19655_1 | TR_LINE 19655_1 | TR_LINE 19655_1
CA-Gladstone Rockhampton | 6051_Parkhurst - Keppel 66 kV | Loading (A) | 44.0492 | 71.3833 | 98.832 | 125.8699 | 154.9962
CA-Gladstone Rockhampton | 6051_Parkhurst - Keppel 66 kV | Loading (MVA) | 5.3834 | 8.7913 | 12.2468 | 15.696 | 19.4374
CA-Gladstone Rockhampton | 6051_Parkhurst - Keppel 66 kV | Loading (MW) | 4.3756 | 8.2331 | 11.8736 | 15.4283 | 19.2467
CA-Gladstone Rockhampton | 6051_Parkhurst - Keppel 66 kV | Power Factor | 0.81201 | 0.93551 | 0.96927 | 0.98294 | 0.99019
CA-Gladstone Rockhampton | 6051_Parkhurst - Keppel 66 kV | Rating (A) | 212 | 212 | 212 | 212 | 212
CA-Gladstone Rockhampton | 6051_Parkhurst - Keppel 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6051_Parkhurst - Keppel 66 kV | Min Voltage at Constrained Conductor | 70.5599 | 71.0848 | 71.4337 | 71.8313 | 72.1913
CA-Gladstone Rockhampton | 6051_Parkhurst - Keppel 66 kV | Contingency Outage | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV
CA-Gladstone Rockhampton | 6053_Parkhurst - Pandoin 66 kV | % of Rated A | 9.233% | 6.385% | 14.31% | 17.48% | 21.32%
CA-Gladstone Rockhampton | 6053_Parkhurst - Pandoin 66 kV | Limiting Line Name | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1
CA-Gladstone Rockhampton | 6053_Parkhurst - Pandoin 66 kV | Loading (A) | 48.2906 | 33.394 | 74.8196 | 91.3965 | 111.5061
CA-Gladstone Rockhampton | 6053_Parkhurst - Pandoin 66 kV | Loading (MVA) | 5.8132 | 4.0245 | 9.0021 | 10.9992 | 13.4332
CA-Gladstone Rockhampton | 6053_Parkhurst - Pandoin 66 kV | Loading (MW) | 5.7373 | 3.8804 | 5.6933 | 8.4969 | 11.486
CA-Gladstone Rockhampton | 6053_Parkhurst - Pandoin 66 kV | Power Factor | 0.98694 | 0.9642 | 0.63113 | 0.77091 | 0.85432
CA-Gladstone Rockhampton | 6053_Parkhurst - Pandoin 66 kV | Rating (A) | 523 | 523 | 523 | 523 | 523
CA-Gladstone Rockhampton | 6053_Parkhurst - Pandoin 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6053_Parkhurst - Pandoin 66 kV | Min Voltage at Constrained Conductor | 69.4739 | 69.5761 | 69.4649 | 69.4818 | 69.4543
CA-Gladstone Rockhampton | 6053_Parkhurst - Pandoin 66 kV | Contingency Outage | 6052_Pandoin - Kunwarara 66 kV | 6052_Pandoin - Kunwarara 66 kV | 6089_QMAG Tee - QMAG 66 kV | 6089_QMAG Tee - QMAG 66 kV | 6089_QMAG Tee - QMAG 66 kV
CA-Gladstone Rockhampton | 6066_Bocoolima Tee -Wooderson 66 kV | % of Rated A | 3.253% | 3.218% | 3.218% | 3.249% | 3.246%
CA-Gladstone Rockhampton | 6066_Bocoolima Tee -Wooderson 66 kV | Limiting Line Name | TR_LINE 22217_1 | TR_LINE 22217_1 | TR_LINE 22217_1 | TR_LINE 22217_1 | TR_LINE 22217_1
CA-Gladstone Rockhampton | 6066_Bocoolima Tee -Wooderson 66 kV | Loading (A) | 5.4977 | 5.4378 | 5.4392 | 5.4908 | 5.4851
CA-Gladstone Rockhampton | 6066_Bocoolima Tee -Wooderson 66 kV | Loading (MVA) | 0.66524 | 0.65082 | 0.65115 | 0.66359 | 0.66219
CA-Gladstone Rockhampton | 6066_Bocoolima Tee -Wooderson 66 kV | Loading (MW) | 0.03316 | 0.033154 | 0.033175 | 0.033179 | 0.033178
CA-Gladstone Rockhampton | 6066_Bocoolima Tee -Wooderson 66 kV | Power Factor | 0.049846 | 0.050943 | 0.050948 | 0.05 | 0.050104
CA-Gladstone Rockhampton | 6066_Bocoolima Tee -Wooderson 66 kV | Rating (A) | 169 | 169 | 169 | 169 | 169
CA-Gladstone Rockhampton | 6066_Bocoolima Tee -Wooderson 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6066_Bocoolima Tee -Wooderson 66 kV | Min Voltage at Constrained Conductor | 69.8621 | 69.099 | 69.1168 | 69.7748 | 69.701
CA-Gladstone Rockhampton | 6066_Bocoolima Tee -Wooderson 66 kV | Contingency Outage | 6019_Gladstone South - Friend St 66 kV | 6019_Gladstone South - Friend St 66 kV | 6022_Gladstone South - Calliope 66 kV | 6019_Gladstone South - Friend St 66 kV | 6019_Gladstone South - Friend St 66 kV
CA-Gladstone Rockhampton | 6074_Lakes Creek - Tanby 66 kV | % of Rated A | 19.21% | 18.24% | 24.92% | 31.57% | 38.74%
CA-Gladstone Rockhampton | 6074_Lakes Creek - Tanby 66 kV | Limiting Line Name | TR_LINE 19802_1 | TR_LINE 19802_1 | TR_LINE 19802_1 | TR_LINE 19802_1 | TR_LINE 19802_1
CA-Gladstone Rockhampton | 6074_Lakes Creek - Tanby 66 kV | Loading (A) | 46.4975 | 72.7878 | 99.4359 | 125.9533 | 154.5763
CA-Gladstone Rockhampton | 6074_Lakes Creek - Tanby 66 kV | Loading (MVA) | 5.6235 | 8.8207 | 12.0852 | 15.3297 | 18.8278
CA-Gladstone Rockhampton | 6074_Lakes Creek - Tanby 66 kV | Loading (MW) | 4.33 | 8.1172 | 11.6495 | 15.0591 | 18.6781
CA-Gladstone Rockhampton | 6074_Lakes Creek - Tanby 66 kV | Power Factor | 0.76988 | 0.92018 | 0.9639 | 0.9823 | 0.99201
CA-Gladstone Rockhampton | 6074_Lakes Creek - Tanby 66 kV | Rating (A) | 399 | 399 | 399 | 399 | 399
CA-Gladstone Rockhampton | 6074_Lakes Creek - Tanby 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6074_Lakes Creek - Tanby 66 kV | Min Voltage at Constrained Conductor | 69.8257 | 69.9654 | 70.1696 | 70.269 | 70.3226
CA-Gladstone Rockhampton | 6074_Lakes Creek - Tanby 66 kV | Contingency Outage | 6051_Parkhurst - Keppel 66 kV | 6051_Parkhurst - Keppel 66 kV | 6051_Parkhurst - Keppel 66 kV | 6051_Parkhurst - Keppel 66 kV | 6051_Parkhurst - Keppel 66 kV
CA-Gladstone Rockhampton | 6075_Keppel - Farnborough 66 kV | % of Rated A | 0.3257% | 0.3289% | 0.3321% | 0.3346% | 0.337%
CA-Gladstone Rockhampton | 6075_Keppel - Farnborough 66 kV | Limiting Line Name | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2
CA-Gladstone Rockhampton | 6075_Keppel - Farnborough 66 kV | Loading (A) | 1.2312 | 1.2431 | 1.2552 | 1.2649 | 1.274
CA-Gladstone Rockhampton | 6075_Keppel - Farnborough 66 kV | Loading (MVA) | 0.15207 | 0.15502 | 0.15804 | 0.16049 | 0.16282
CA-Gladstone Rockhampton | 6075_Keppel - Farnborough 66 kV | Loading (MW) | 3.7894e-06 | 3.8628e-06 | 3.9381e-06 | 3.9992e-06 | 4.0571e-06
CA-Gladstone Rockhampton | 6075_Keppel - Farnborough 66 kV | Power Factor | 2.1948e-06 | 2.1903e-06 | 2.19e-06 | 2.188e-06 | 2.1899e-06
CA-Gladstone Rockhampton | 6075_Keppel - Farnborough 66 kV | Rating (A) | 378 | 378 | 378 | 378 | 378
CA-Gladstone Rockhampton | 6075_Keppel - Farnborough 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6075_Keppel - Farnborough 66 kV | Min Voltage at Constrained Conductor | 71.3065 | 71.9955 | 72.6937 | 73.2558 | 73.7837
CA-Gladstone Rockhampton | 6075_Keppel - Farnborough 66 kV | Contingency Outage | 6051_Parkhurst - Keppel 66 kV | 6051_Parkhurst - Keppel 66 kV | 6051_Parkhurst - Keppel 66 kV | 6051_Parkhurst - Keppel 66 kV | 6051_Parkhurst - Keppel 66 kV
CA-Gladstone Rockhampton | 6077_Farnborough - Capricorn Resort 66kV | % of Rated A | 0.07184% | 0.07253% | 0.07324% | 0.0738% | 0.07434%
CA-Gladstone Rockhampton | 6077_Farnborough - Capricorn Resort 66kV | Limiting Line Name | TR_LINE FARB-FARE | TR_LINE FARB-FARE | TR_LINE FARB-FARE | TR_LINE FARB-FARE | TR_LINE FARB-FARE
CA-Gladstone Rockhampton | 6077_Farnborough - Capricorn Resort 66kV | Loading (A) | 0.27299 | 0.27563 | 0.2783 | 0.28045 | 0.28247
CA-Gladstone Rockhampton | 6077_Farnborough - Capricorn Resort 66kV | Loading (MVA) | 0.033718 | 0.034373 | 0.035043 | 0.035587 | 0.036102
CA-Gladstone Rockhampton | 6077_Farnborough - Capricorn Resort 66kV | Loading (MW) | 4.7677e-08 | 4.8602e-08 | 4.9549e-08 | 5.0319e-08 | 5.1046e-08
CA-Gladstone Rockhampton | 6077_Farnborough - Capricorn Resort 66kV | Power Factor | 1.414e-06 | 1.414e-06 | 1.4139e-06 | 1.414e-06 | 1.414e-06
CA-Gladstone Rockhampton | 6077_Farnborough - Capricorn Resort 66kV | Rating (A) | 380 | 380 | 380 | 380 | 380
CA-Gladstone Rockhampton | 6077_Farnborough - Capricorn Resort 66kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6077_Farnborough - Capricorn Resort 66kV | Min Voltage at Constrained Conductor | 71.3107 | 71.9998 | 72.6981 | 73.2601 | 73.7881
CA-Gladstone Rockhampton | 6077_Farnborough - Capricorn Resort 66kV | Contingency Outage | 6051_Parkhurst - Keppel 66 kV | 6051_Parkhurst - Keppel 66 kV | 6051_Parkhurst - Keppel 66 kV | 6051_Parkhurst - Keppel 66 kV | 6051_Parkhurst - Keppel 66 kV
CA-Gladstone Rockhampton | 6082_Farnborough Tee - Yeppoon 66 kV | % of Rated A | 20.36% | 33.42% | 46.44% | 59.24% | 73.01%
CA-Gladstone Rockhampton | 6082_Farnborough Tee - Yeppoon 66 kV | Limiting Line Name | TR_LINE 19629_1 | TR_LINE 19629_1 | TR_LINE 19629_1 | TR_LINE 19629_1 | TR_LINE 19629_1
CA-Gladstone Rockhampton | 6082_Farnborough Tee - Yeppoon 66 kV | Loading (A) | 43.1716 | 70.8503 | 98.4585 | 125.5884 | 154.7819
CA-Gladstone Rockhampton | 6082_Farnborough Tee - Yeppoon 66 kV | Loading (MVA) | 5.2831 | 8.7393 | 12.2107 | 15.6693 | 19.4177
CA-Gladstone Rockhampton | 6082_Farnborough Tee - Yeppoon 66 kV | Loading (MW) | 4.3757 | 8.2334 | 11.8742 | 15.4293 | 19.2482
CA-Gladstone Rockhampton | 6082_Farnborough Tee - Yeppoon 66 kV | Power Factor | 0.82823 | 0.94208 | 0.97244 | 0.98468 | 0.99127
CA-Gladstone Rockhampton | 6082_Farnborough Tee - Yeppoon 66 kV | Rating (A) | 212 | 212 | 212 | 212 | 212
CA-Gladstone Rockhampton | 6082_Farnborough Tee - Yeppoon 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6082_Farnborough Tee - Yeppoon 66 kV | Min Voltage at Constrained Conductor | 70.6524 | 71.2153 | 71.5989 | 72.0294 | 72.4237
CA-Gladstone Rockhampton | 6082_Farnborough Tee - Yeppoon 66 kV | Contingency Outage | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV
CA-Gladstone Rockhampton | 6090_Egan's Hill - Raglan 66 kV | % of Rated A | 6.495% | 5.98% | 5.624% | 5.362% | 5.173%
CA-Gladstone Rockhampton | 6090_Egan's Hill - Raglan 66 kV | Limiting Line Name | TR_LINE 160589_1 | TR_LINE 160589_1 | TR_LINE 160589_1 | TR_LINE 160589_1 | TR_LINE 160589_1
CA-Gladstone Rockhampton | 6090_Egan's Hill - Raglan 66 kV | Loading (A) | 8.5736 | 7.8932 | 7.4242 | 7.0783 | 6.8282
CA-Gladstone Rockhampton | 6090_Egan's Hill - Raglan 66 kV | Loading (MVA) | 1.0308 | 0.94946 | 0.8982 | 0.85651 | 0.82604
CA-Gladstone Rockhampton | 6090_Egan's Hill - Raglan 66 kV | Loading (MW) | 0.78987 | 0.67776 | 0.59368 | 0.527 | 0.47544
CA-Gladstone Rockhampton | 6090_Egan's Hill - Raglan 66 kV | Power Factor | 0.76623 | 0.71384 | 0.66097 | 0.61529 | 0.57556
CA-Gladstone Rockhampton | 6090_Egan's Hill - Raglan 66 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
CA-Gladstone Rockhampton | 6090_Egan's Hill - Raglan 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6090_Egan's Hill - Raglan 66 kV | Min Voltage at Constrained Conductor | 69.4157 | 69.4476 | 69.8494 | 69.8629 | 69.8455
CA-Gladstone Rockhampton | 6090_Egan's Hill - Raglan 66 kV | Contingency Outage | 6091_Egan's Hill - Gavial 66 kV | 6096_Egan's Hill - Lakes Creek 66 kV | 6046_Mt Morgan - Wowan 66 kV | 6005_Rockhampton Glenmore-Canning 66 kV | 6005_Rockhampton Glenmore-Canning 66 kV
CA-Gladstone Rockhampton | 6091_Egan's Hill - Gavial 66 kV | % of Rated A | 35.36% | 41.65% | 79.28% | 79.79% | 79.81%
CA-Gladstone Rockhampton | 6091_Egan's Hill - Gavial 66 kV | Limiting Line Name | TR_LINE 13465_1 | TR_LINE 13465_1 | TR_LINE 13465_1 | TR_LINE 22265_1 | TR_LINE 22265_1
CA-Gladstone Rockhampton | 6091_Egan's Hill - Gavial 66 kV | Loading (A) | 50.5617 | 59.5528 | 113.3746 | 114.1045 | 114.1322
CA-Gladstone Rockhampton | 6091_Egan's Hill - Gavial 66 kV | Loading (MVA) | 6.0835 | 7.1729 | 13.6679 | 13.6245 | 13.6247
CA-Gladstone Rockhampton | 6091_Egan's Hill - Gavial 66 kV | Loading (MW) | 6.0738 | 7.1679 | 13.6598 | 13.6174 | 13.6176
CA-Gladstone Rockhampton | 6091_Egan's Hill - Gavial 66 kV | Power Factor | 0.9984 | 0.9993 | 0.9994 | 0.99948 | 0.99948
CA-Gladstone Rockhampton | 6091_Egan's Hill - Gavial 66 kV | Rating (A) | 143 | 143 | 143 | 143 | 143
CA-Gladstone Rockhampton | 6091_Egan's Hill - Gavial 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6091_Egan's Hill - Gavial 66 kV | Min Voltage at Constrained Conductor | 69.4639 | 69.5372 | 69.5983 | 68.9167 | 68.9009
CA-Gladstone Rockhampton | 6091_Egan's Hill - Gavial 66 kV | Contingency Outage | 6046_Mt Morgan - Wowan 66 kV | 6046_Mt Morgan - Wowan 66 kV | 6094_Malchi Tee - Malchi 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV
CA-Gladstone Rockhampton | 6093_Gavial - Mt Morgan 66 kV | % of Rated A | 5.28% | 43.76% | 85.85% | 86.42% | 86.44%
CA-Gladstone Rockhampton | 6093_Gavial - Mt Morgan 66 kV | Limiting Line Name | TR_LINE 19113_1 | TR_LINE 19767_1 | TR_LINE 19767_1 | TR_LINE 19767_1 | TR_LINE 19767_1
CA-Gladstone Rockhampton | 6093_Gavial - Mt Morgan 66 kV | Loading (A) | 7.5499 | 57.7589 | 113.3249 | 114.0722 | 114.0999
CA-Gladstone Rockhampton | 6093_Gavial - Mt Morgan 66 kV | Loading (MVA) | 0.91226 | 6.9037 | 13.4761 | 13.4792 | 13.4793
CA-Gladstone Rockhampton | 6093_Gavial - Mt Morgan 66 kV | Loading (MW) | 0.30157 | 6.8696 | 13.4675 | 13.4711 | 13.4712
CA-Gladstone Rockhampton | 6093_Gavial - Mt Morgan 66 kV | Power Factor | 0.33058 | 0.99507 | 0.99918 | 0.99921 | 0.99921
CA-Gladstone Rockhampton | 6093_Gavial - Mt Morgan 66 kV | Rating (A) | 143 | 132 | 132 | 132 | 132
CA-Gladstone Rockhampton | 6093_Gavial - Mt Morgan 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6093_Gavial - Mt Morgan 66 kV | Min Voltage at Constrained Conductor | 69.7613 | 68.5067 | 67.6119 | 67.17 | 67.1537
CA-Gladstone Rockhampton | 6093_Gavial - Mt Morgan 66 kV | Contingency Outage | 6003_Glenmore - Berserker 66 kV | 6094_Malchi Tee - Malchi 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV
CA-Gladstone Rockhampton | 6094_Malchi Tee - Malchi 66 kV | % of Rated A | 29.89% | 35.34% | 40.1% | 44.66% | 48.96%
CA-Gladstone Rockhampton | 6094_Malchi Tee - Malchi 66 kV | Limiting Line Name | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1
CA-Gladstone Rockhampton | 6094_Malchi Tee - Malchi 66 kV | Loading (A) | 50.5063 | 59.7271 | 67.7735 | 75.4743 | 82.7409
CA-Gladstone Rockhampton | 6094_Malchi Tee - Malchi 66 kV | Loading (MVA) | 6.1047 | 7.2112 | 8.1772 | 9.0543 | 9.9279
CA-Gladstone Rockhampton | 6094_Malchi Tee - Malchi 66 kV | Loading (MW) | 6.1029 | 7.2083 | 8.1731 | 9.0485 | 9.9203
CA-Gladstone Rockhampton | 6094_Malchi Tee - Malchi 66 kV | Power Factor | 0.99972 | 0.99961 | 0.99949 | 0.99936 | 0.99923
CA-Gladstone Rockhampton | 6094_Malchi Tee - Malchi 66 kV | Rating (A) | 169 | 169 | 169 | 169 | 169
CA-Gladstone Rockhampton | 6094_Malchi Tee - Malchi 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6094_Malchi Tee - Malchi 66 kV | Min Voltage at Constrained Conductor | 69.5642 | 69.4496 | 69.3708 | 68.9424 | 68.9269
CA-Gladstone Rockhampton | 6094_Malchi Tee - Malchi 66 kV | Contingency Outage | 6093_Gavial - Mt Morgan 66 kV | 6096_Egan's Hill - Lakes Creek 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV
CA-Gladstone Rockhampton | 6095_Egan's Hill-Rockhampton South 66 kV | % of Rated A | 19.56% | 11.28% | 14.31% | 14.34% | 14.45%
CA-Gladstone Rockhampton | 6095_Egan's Hill-Rockhampton South 66 kV | Limiting Line Name | TR_LINE 20983_1 | TR_LINE 20983_1 | TR_LINE 20972_1 | TR_LINE 20972_1 | TR_LINE 20972_1
CA-Gladstone Rockhampton | 6095_Egan's Hill-Rockhampton South 66 kV | Loading (A) | 48.5204 | 27.9837 | 35.483 | 35.5641 | 35.8322
CA-Gladstone Rockhampton | 6095_Egan's Hill-Rockhampton South 66 kV | Loading (MVA) | 5.8377 | 3.3694 | 4.2794 | 4.2906 | 4.3224
CA-Gladstone Rockhampton | 6095_Egan's Hill-Rockhampton South 66 kV | Loading (MW) | 5.1797 | 3.0531 | 0.058069 | 0.20025 | 0.58837
CA-Gladstone Rockhampton | 6095_Egan's Hill-Rockhampton South 66 kV | Power Factor | 0.88728 | 0.90613 | 0.012919 | 0.046167 | 0.13601
CA-Gladstone Rockhampton | 6095_Egan's Hill-Rockhampton South 66 kV | Rating (A) | 248 | 248 | 248 | 248 | 248
CA-Gladstone Rockhampton | 6095_Egan's Hill-Rockhampton South 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6095_Egan's Hill-Rockhampton South 66 kV | Min Voltage at Constrained Conductor | 69.4501 | 69.5082 | 69.6306 | 69.6543 | 69.6455
CA-Gladstone Rockhampton | 6095_Egan's Hill-Rockhampton South 66 kV | Contingency Outage | 6097_Egan's Hill - Canning 66 kV | 6093_Gavial - Mt Morgan 66 kV | 6005_Rockhampton Glenmore-Canning 66 kV | 6005_Rockhampton Glenmore-Canning 66 kV | 6005_Rockhampton Glenmore-Canning 66 kV
CA-Gladstone Rockhampton | 6097_Egan's Hill - Canning 66 kV | % of Rated A | 21.09% | 17.41% | 16.26% | 16.07% | 17.03%
CA-Gladstone Rockhampton | 6097_Egan's Hill - Canning 66 kV | Limiting Line Name | TR_LINE 20992_1 | TR_LINE 20992_1 | TR_LINE 20992_1 | TR_LINE 20992_1 | TR_LINE 20992_1
CA-Gladstone Rockhampton | 6097_Egan's Hill - Canning 66 kV | Loading (A) | 52.2989 | 43.1763 | 40.3338 | 39.8518 | 42.245
CA-Gladstone Rockhampton | 6097_Egan's Hill - Canning 66 kV | Loading (MVA) | 6.2958 | 5.2068 | 4.8823 | 4.8265 | 5.1161
CA-Gladstone Rockhampton | 6097_Egan's Hill - Canning 66 kV | Loading (MW) | 5.3575 | 2.1353 | 0.89118 | 0.37038 | 1.7448
CA-Gladstone Rockhampton | 6097_Egan's Hill - Canning 66 kV | Power Factor | 0.85096 | 0.41009 | 0.18249 | 0.076448 | 0.34073
CA-Gladstone Rockhampton | 6097_Egan's Hill - Canning 66 kV | Rating (A) | 248 | 248 | 248 | 248 | 248
CA-Gladstone Rockhampton | 6097_Egan's Hill - Canning 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6097_Egan's Hill - Canning 66 kV | Min Voltage at Constrained Conductor | 69.4921 | 69.6257 | 69.8871 | 69.9234 | 69.9206
CA-Gladstone Rockhampton | 6097_Egan's Hill - Canning 66 kV | Contingency Outage | 6095_Egan's Hill-Rockhampton South 66 kV | 6005_Rockhampton Glenmore-Canning 66 kV | 6005_Rockhampton Glenmore-Canning 66 kV | 6005_Rockhampton Glenmore-Canning 66 kV | 6005_Rockhampton Glenmore-Canning 66 kV
CA-Gladstone Rockhampton | 6100_Boat Creek - ICI 66 kV | % of Rated A | 1.614% | 1.598% | 1.598% | 1.598% | 1.613%
CA-Gladstone Rockhampton | 6100_Boat Creek - ICI 66 kV | Limiting Line Name | TR_LINE 50343_1 | TR_LINE 50343_1 | TR_LINE 50343_1 | TR_LINE 50343_1 | TR_LINE 50343_1
CA-Gladstone Rockhampton | 6100_Boat Creek - ICI 66 kV | Loading (A) | 11.9449 | 11.8234 | 11.8265 | 11.826 | 11.9394
CA-Gladstone Rockhampton | 6100_Boat Creek - ICI 66 kV | Loading (MVA) | 1.3864 | 1.3864 | 1.3864 | 1.3864 | 1.3864
CA-Gladstone Rockhampton | 6100_Boat Creek - ICI 66 kV | Loading (MW) | 1.3864 | 1.3864 | 1.3864 | 1.3864 | 1.3864
CA-Gladstone Rockhampton | 6100_Boat Creek - ICI 66 kV | Power Factor | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 0.99999
CA-Gladstone Rockhampton | 6100_Boat Creek - ICI 66 kV | Rating (A) | 740 | 740 | 740 | 740 | 740
CA-Gladstone Rockhampton | 6100_Boat Creek - ICI 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6100_Boat Creek - ICI 66 kV | Min Voltage at Constrained Conductor | 67.0112 | 67.7002 | 67.6824 | 67.6851 | 67.0421
CA-Gladstone Rockhampton | 6100_Boat Creek - ICI 66 kV | Contingency Outage | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV
CA-Gladstone Rockhampton | 6101_Boat Creek - Orica 66 kV | % of Rated A | 15.84% | 15.68% | 15.68% | 15.68% | 15.83%
CA-Gladstone Rockhampton | 6101_Boat Creek - Orica 66 kV | Limiting Line Name | TR_LINE pole4158700 to ORIC | TR_LINE pole4158700 to ORIC | TR_LINE pole4158700 to ORIC | TR_LINE pole4158700 to ORIC | TR_LINE pole4158700 to ORIC
CA-Gladstone Rockhampton | 6101_Boat Creek - Orica 66 kV | Loading (A) | 117.1964 | 116.0034 | 116.0338 | 116.0292 | 117.1424
CA-Gladstone Rockhampton | 6101_Boat Creek - Orica 66 kV | Loading (MVA) | 13.6011 | 13.6011 | 13.6011 | 13.6011 | 13.6011
CA-Gladstone Rockhampton | 6101_Boat Creek - Orica 66 kV | Loading (MW) | 13.6011 | 13.6011 | 13.6011 | 13.6011 | 13.6011
CA-Gladstone Rockhampton | 6101_Boat Creek - Orica 66 kV | Power Factor | 1 | 1 | 1 | 1 | 1
CA-Gladstone Rockhampton | 6101_Boat Creek - Orica 66 kV | Rating (A) | 740 | 740 | 740 | 740 | 740
CA-Gladstone Rockhampton | 6101_Boat Creek - Orica 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6101_Boat Creek - Orica 66 kV | Min Voltage at Constrained Conductor | 66.9983 | 67.6874 | 67.6696 | 67.6723 | 67.0292
CA-Gladstone Rockhampton | 6101_Boat Creek - Orica 66 kV | Contingency Outage | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV
CA-Gladstone Rockhampton | 6102_Boat Creek - Yarwun 66 kV | % of Rated A | 2.842% | 2.763% | 4.087% | 5.417% | 5.432%
CA-Gladstone Rockhampton | 6102_Boat Creek - Yarwun 66 kV | Limiting Line Name | TR_LINE 16859_1 | TR_LINE 16859_1 | TR_LINE 16861_2 | TR_LINE 16861_2 | TR_LINE 16861_2
CA-Gladstone Rockhampton | 6102_Boat Creek - Yarwun 66 kV | Loading (A) | 21.0288 | 20.4472 | 30.2421 | 40.0871 | 40.1985
CA-Gladstone Rockhampton | 6102_Boat Creek - Yarwun 66 kV | Loading (MVA) | 2.4408 | 2.3977 | 3.5451 | 4.6989 | 4.6672
CA-Gladstone Rockhampton | 6102_Boat Creek - Yarwun 66 kV | Loading (MW) | 2.4403 | 2.3971 | 3.5451 | 4.6985 | 4.6667
CA-Gladstone Rockhampton | 6102_Boat Creek - Yarwun 66 kV | Power Factor | 0.99981 | 0.99977 | 0.99996 | 0.99979 | 0.99978
CA-Gladstone Rockhampton | 6102_Boat Creek - Yarwun 66 kV | Rating (A) | 740 | 740 | 740 | 740 | 740
CA-Gladstone Rockhampton | 6102_Boat Creek - Yarwun 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6102_Boat Creek - Yarwun 66 kV | Min Voltage at Constrained Conductor | 67.0114 | 67.7003 | 67.6671 | 67.6635 | 67.0205
CA-Gladstone Rockhampton | 6102_Boat Creek - Yarwun 66 kV | Contingency Outage | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV
CA-Gladstone Rockhampton | 6103_Fisherman Landing-Boat Creek 66 kV | % of Rated A | 84.05% | 83.18% | 83.2% | 83.2% | 84.01%
CA-Gladstone Rockhampton | 6103_Fisherman Landing-Boat Creek 66 kV | Limiting Line Name | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1
CA-Gladstone Rockhampton | 6103_Fisherman Landing-Boat Creek 66 kV | Loading (A) | 235.3266 | 232.9116 | 232.9731 | 232.9639 | 235.2172
CA-Gladstone Rockhampton | 6103_Fisherman Landing-Boat Creek 66 kV | Loading (MVA) | 27.2031 | 27.2031 | 27.2031 | 27.2031 | 27.2031
CA-Gladstone Rockhampton | 6103_Fisherman Landing-Boat Creek 66 kV | Loading (MW) | 27.2031 | 27.2031 | 27.2031 | 27.2031 | 27.2031
CA-Gladstone Rockhampton | 6103_Fisherman Landing-Boat Creek 66 kV | Power Factor | 1 | 1 | 1 | 1 | 1
CA-Gladstone Rockhampton | 6103_Fisherman Landing-Boat Creek 66 kV | Rating (A) | 280 | 280 | 280 | 280 | 280
CA-Gladstone Rockhampton | 6103_Fisherman Landing-Boat Creek 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6103_Fisherman Landing-Boat Creek 66 kV | Min Voltage at Constrained Conductor | 66.7325 | 67.4244 | 67.4066 | 67.4093 | 66.7635
CA-Gladstone Rockhampton | 6103_Fisherman Landing-Boat Creek 66 kV | Contingency Outage | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV
CA-Gladstone Rockhampton | 6106_Shale Oil Tee - Shale Oil 66kV | % of Rated A | 1.178% | 1.166% | 1.167% | 1.167% | 1.178%
CA-Gladstone Rockhampton | 6106_Shale Oil Tee - Shale Oil 66kV | Limiting Line Name | TR_LINE 21402_1 | TR_LINE 21402_1 | TR_LINE 21402_1 | TR_LINE 21402_1 | TR_LINE 21402_1
CA-Gladstone Rockhampton | 6106_Shale Oil Tee - Shale Oil 66kV | Loading (A) | 5.1728 | 5.12 | 5.1218 | 5.1221 | 5.1713
CA-Gladstone Rockhampton | 6106_Shale Oil Tee - Shale Oil 66kV | Loading (MVA) | 0.6002 | 0.60019 | 0.60019 | 0.6002 | 0.6002
CA-Gladstone Rockhampton | 6106_Shale Oil Tee - Shale Oil 66kV | Loading (MW) | 0.60019 | 0.60018 | 0.60018 | 0.60019 | 0.60019
CA-Gladstone Rockhampton | 6106_Shale Oil Tee - Shale Oil 66kV | Power Factor | 0.99996 | 0.99996 | 0.99996 | 0.99996 | 0.99996
CA-Gladstone Rockhampton | 6106_Shale Oil Tee - Shale Oil 66kV | Rating (A) | 439 | 439 | 439 | 439 | 439
CA-Gladstone Rockhampton | 6106_Shale Oil Tee - Shale Oil 66kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6106_Shale Oil Tee - Shale Oil 66kV | Min Voltage at Constrained Conductor | 66.9903 | 67.6797 | 67.6561 | 67.6525 | 67.0094
CA-Gladstone Rockhampton | 6106_Shale Oil Tee - Shale Oil 66kV | Contingency Outage | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV
CA-Gladstone Rockhampton | 6109_Gladstone North - Clinton 66 kV | % of Rated A | 38.36% | 35.67% | 32.31% | 29.03% | 27.22%
CA-Gladstone Rockhampton | 6109_Gladstone North - Clinton 66 kV | Limiting Line Name | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 61921_1
CA-Gladstone Rockhampton | 6109_Gladstone North - Clinton 66 kV | Loading (A) | 139.2626 | 129.4897 | 117.2851 | 105.3699 | 98.7974
CA-Gladstone Rockhampton | 6109_Gladstone North - Clinton 66 kV | Loading (MVA) | 16.4974 | 15.3644 | 13.9157 | 12.4646 | 11.7758
CA-Gladstone Rockhampton | 6109_Gladstone North - Clinton 66 kV | Loading (MW) | 16.0949 | 14.9235 | 13.4458 | 11.9709 | 11.6853
CA-Gladstone Rockhampton | 6109_Gladstone North - Clinton 66 kV | Power Factor | 0.97548 | 0.97121 | 0.96619 | 0.9604 | 0.99226
CA-Gladstone Rockhampton | 6109_Gladstone North - Clinton 66 kV | Rating (A) | 363 | 363 | 363 | 363 | 363
CA-Gladstone Rockhampton | 6109_Gladstone North - Clinton 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6109_Gladstone North - Clinton 66 kV | Min Voltage at Constrained Conductor | 68.388 | 68.5004 | 68.4996 | 68.2964 | 68.7952
CA-Gladstone Rockhampton | 6109_Gladstone North - Clinton 66 kV | Contingency Outage | 6111_Gladstone North - Port Curtis 66 kV | 6111_Gladstone North - Port Curtis 66 kV | 6111_Gladstone North - Port Curtis 66 kV | 6111_Gladstone North - Port Curtis 66 kV | 6111_Gladstone North - Port Curtis 66 kV
CA-Gladstone Rockhampton | 6196_Callide Mine 66 kV | % of Rated A | 57.73% | 57.7% | 57.7% | 57.72% | 57.74%
CA-Gladstone Rockhampton | 6196_Callide Mine 66 kV | Limiting Line Name | TR_LINE 22328_1 | TR_LINE 22328_1 | TR_LINE 22328_1 | TR_LINE 22328_1 | TR_LINE 22328_1
CA-Gladstone Rockhampton | 6196_Callide Mine 66 kV | Loading (A) | 77.3599 | 77.3197 | 77.3205 | 77.3446 | 77.376
CA-Gladstone Rockhampton | 6196_Callide Mine 66 kV | Loading (MVA) | 9.2008 | 9.2008 | 9.2008 | 9.2008 | 9.2008
CA-Gladstone Rockhampton | 6196_Callide Mine 66 kV | Loading (MW) | 9.2008 | 9.2008 | 9.2008 | 9.2008 | 9.2008
CA-Gladstone Rockhampton | 6196_Callide Mine 66 kV | Power Factor | 1 | 1 | 1 | 1 | 1
CA-Gladstone Rockhampton | 6196_Callide Mine 66 kV | Rating (A) | 134 | 134 | 134 | 134 | 134
CA-Gladstone Rockhampton | 6196_Callide Mine 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6196_Callide Mine 66 kV | Min Voltage at Constrained Conductor | 68.6611 | 68.6969 | 68.6962 | 68.6748 | 68.6469
CA-Gladstone Rockhampton | 6196_Callide Mine 66 kV | Contingency Outage | 6027_TDM Mine 66 kV | 6027_TDM Mine 66 kV | 6027_TDM Mine 66 kV | 6027_TDM Mine 66 kV | 6027_TDM Mine 66 kV
CA-Gladstone Rockhampton | 6298_Tanby - Yeppoon 66 kV | % of Rated A | 7.208% | 10.84% | 15.39% | 20.26% | 25.69%
CA-Gladstone Rockhampton | 6298_Tanby - Yeppoon 66 kV | Limiting Line Name | TR_LINE 112499_1 | TR_LINE 112499_1 | TR_LINE 112499_1 | TR_LINE 112499_1 | TR_LINE 112499_1
CA-Gladstone Rockhampton | 6298_Tanby - Yeppoon 66 kV | Loading (A) | 27.2453 | 40.9811 | 58.1769 | 76.5781 | 97.1155
CA-Gladstone Rockhampton | 6298_Tanby - Yeppoon 66 kV | Loading (MVA) | 3.3606 | 5.101 | 7.3081 | 9.6899 | 12.3721
CA-Gladstone Rockhampton | 6298_Tanby - Yeppoon 66 kV | Loading (MW) | 1.422 | 4.0724 | 6.6313 | 9.2031 | 12.0147
CA-Gladstone Rockhampton | 6298_Tanby - Yeppoon 66 kV | Power Factor | 0.4231 | 0.79828 | 0.9073 | 0.94968 | 0.97108
CA-Gladstone Rockhampton | 6298_Tanby - Yeppoon 66 kV | Rating (A) | 378 | 378 | 378 | 378 | 378
CA-Gladstone Rockhampton | 6298_Tanby - Yeppoon 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6298_Tanby - Yeppoon 66 kV | Min Voltage at Constrained Conductor | 71.2139 | 71.8637 | 72.5254 | 73.0518 | 73.5418
CA-Gladstone Rockhampton | 6298_Tanby - Yeppoon 66 kV | Contingency Outage | 6051_Parkhurst - Keppel 66 kV | 6051_Parkhurst - Keppel 66 kV | 6051_Parkhurst - Keppel 66 kV | 6051_Parkhurst - Keppel 66 kV | 6051_Parkhurst - Keppel 66 kV
CA-Gladstone Rockhampton | 6310_Lakes Creek - Berserker 66 kV | % of Rated A | 15.9% | 14.88% | 17.47% | 20.61% | 24.25%
CA-Gladstone Rockhampton | 6310_Lakes Creek - Berserker 66 kV | Limiting Line Name | TR_CABLE 51_1 | TR_CABLE 51_1 | TR_CABLE 51_1 | TR_CABLE 51_1 | TR_CABLE 51_1
CA-Gladstone Rockhampton | 6310_Lakes Creek - Berserker 66 kV | Loading (A) | 59.1341 | 55.3607 | 64.974 | 76.6818 | 90.205
CA-Gladstone Rockhampton | 6310_Lakes Creek - Berserker 66 kV | Loading (MVA) | 7.2054 | 6.766 | 7.8968 | 9.3329 | 10.9872
CA-Gladstone Rockhampton | 6310_Lakes Creek - Berserker 66 kV | Loading (MW) | 3.0424 | 1.4759 | 6.2591 | 8.1045 | 10.0922
CA-Gladstone Rockhampton | 6310_Lakes Creek - Berserker 66 kV | Power Factor | 0.42224 | 0.21813 | 0.79258 | 0.86836 | 0.91852
CA-Gladstone Rockhampton | 6310_Lakes Creek - Berserker 66 kV | Rating (A) | 372 | 372 | 372 | 372 | 372
CA-Gladstone Rockhampton | 6310_Lakes Creek - Berserker 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6310_Lakes Creek - Berserker 66 kV | Min Voltage at Constrained Conductor | 70.3495 | 70.5619 | 70.1695 | 70.2688 | 70.3225
CA-Gladstone Rockhampton | 6310_Lakes Creek - Berserker 66 kV | Contingency Outage | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6051_Parkhurst - Keppel 66 kV | 6051_Parkhurst - Keppel 66 kV | 6051_Parkhurst - Keppel 66 kV
CA-Gladstone Rockhampton | 7290_Boat Creek - Yarwun 132 kV | % of Rated A | 21.15% | 21.17% | 21.72% | 22.27% | 22.19%
CA-Gladstone Rockhampton | 7290_Boat Creek - Yarwun 132 kV | Limiting Line Name | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1
CA-Gladstone Rockhampton | 7290_Boat Creek - Yarwun 132 kV | Loading (A) | 188.0398 | 188.2322 | 193.1187 | 197.9714 | 197.3086
CA-Gladstone Rockhampton | 7290_Boat Creek - Yarwun 132 kV | Loading (MVA) | 44.877 | 44.8298 | 45.9887 | 47.1546 | 47.1258
CA-Gladstone Rockhampton | 7290_Boat Creek - Yarwun 132 kV | Loading (MW) | 44.8094 | 44.7626 | 45.9142 | 47.0712 | 47.0427
CA-Gladstone Rockhampton | 7290_Boat Creek - Yarwun 132 kV | Power Factor | 0.99849 | 0.9985 | 0.99838 | 0.99823 | 0.99823
CA-Gladstone Rockhampton | 7290_Boat Creek - Yarwun 132 kV | Rating (A) | 889 | 889 | 889 | 889 | 889
CA-Gladstone Rockhampton | 7290_Boat Creek - Yarwun 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 7290_Boat Creek - Yarwun 132 kV | Min Voltage at Constrained Conductor | 137.7824 | 137.4968 | 137.482 | 137.5118 | 137.8895
CA-Gladstone Rockhampton | 7290_Boat Creek - Yarwun 132 kV | Contingency Outage | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV
CA-Gladstone Rockhampton | 7291_Boat Creek - Yarwun 132 kV | % of Rated A | 21.15% | 21.17% | 21.72% | 22.27% | 22.19%
CA-Gladstone Rockhampton | 7291_Boat Creek - Yarwun 132 kV | Limiting Line Name | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1
CA-Gladstone Rockhampton | 7291_Boat Creek - Yarwun 132 kV | Loading (A) | 188.0329 | 188.2255 | 193.1116 | 197.9637 | 197.3008
CA-Gladstone Rockhampton | 7291_Boat Creek - Yarwun 132 kV | Loading (MVA) | 44.876 | 44.8289 | 45.9877 | 47.1535 | 47.1247
CA-Gladstone Rockhampton | 7291_Boat Creek - Yarwun 132 kV | Loading (MW) | 44.8089 | 44.7621 | 45.9136 | 47.0706 | 47.0421
CA-Gladstone Rockhampton | 7291_Boat Creek - Yarwun 132 kV | Power Factor | 0.9985 | 0.99851 | 0.99839 | 0.99824 | 0.99824
CA-Gladstone Rockhampton | 7291_Boat Creek - Yarwun 132 kV | Rating (A) | 889 | 889 | 889 | 889 | 889
CA-Gladstone Rockhampton | 7291_Boat Creek - Yarwun 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 7291_Boat Creek - Yarwun 132 kV | Min Voltage at Constrained Conductor | 137.7859 | 137.5003 | 137.4856 | 137.5156 | 137.8933
CA-Gladstone Rockhampton | 7291_Boat Creek - Yarwun 132 kV | Contingency Outage | 7290_Boat Creek - Yarwun 132 kV | 7290_Boat Creek - Yarwun 132 kV | 7290_Boat Creek - Yarwun 132 kV | 7290_Boat Creek - Yarwun 132 kV | 7290_Boat Creek - Yarwun 132 kV
CA-Gladstone Rockhampton | 7414_Gladstone North - Wiggins Is 132 kV | % of Rated A | 5.124% | 5.116% | 5.116% | 5.131% | 5.138%
CA-Gladstone Rockhampton | 7414_Gladstone North - Wiggins Is 132 kV | Limiting Line Name | TR_LINE 193931_1 | TR_LINE 193931_1 | TR_LINE 193931_1 | TR_LINE 193931_1 | TR_LINE 193931_1
CA-Gladstone Rockhampton | 7414_Gladstone North - Wiggins Is 132 kV | Loading (A) | 41.2993 | 41.2344 | 41.2359 | 41.3592 | 41.4112
CA-Gladstone Rockhampton | 7414_Gladstone North - Wiggins Is 132 kV | Loading (MVA) | 10.0093 | 10.0092 | 10.0092 | 10.0093 | 10.0093
CA-Gladstone Rockhampton | 7414_Gladstone North - Wiggins Is 132 kV | Loading (MW) | 10.0078 | 10.0078 | 10.0078 | 10.0079 | 10.0079
CA-Gladstone Rockhampton | 7414_Gladstone North - Wiggins Is 132 kV | Power Factor | 0.99985 | 0.99985 | 0.99985 | 0.99985 | 0.99984
CA-Gladstone Rockhampton | 7414_Gladstone North - Wiggins Is 132 kV | Rating (A) | 806 | 806 | 806 | 806 | 806
CA-Gladstone Rockhampton | 7414_Gladstone North - Wiggins Is 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 7414_Gladstone North - Wiggins Is 132 kV | Min Voltage at Constrained Conductor | 139.926 | 140.1459 | 140.1407 | 139.7239 | 139.549
CA-Gladstone Rockhampton | 7414_Gladstone North - Wiggins Is 132 kV | Contingency Outage | 7415_Gladstone North - Wiggins Is 132 kV | 7415_Gladstone North - Wiggins Is 132 kV | 7415_Gladstone North - Wiggins Is 132 kV | 7415_Gladstone North - Wiggins Is 132 kV | 7415_Gladstone North - Wiggins Is 132 kV
CA-Gladstone Rockhampton | 7415_Gladstone North - Wiggins Is 132 kV | % of Rated A | 4.646% | 4.639% | 4.639% | 4.653% | 4.659%
CA-Gladstone Rockhampton | 7415_Gladstone North - Wiggins Is 132 kV | Limiting Line Name | TR_LINE 184976_2 | TR_LINE 184976_2 | TR_LINE 184976_2 | TR_LINE 184976_2 | TR_LINE 184976_2
CA-Gladstone Rockhampton | 7415_Gladstone North - Wiggins Is 132 kV | Loading (A) | 41.3042 | 41.2393 | 41.2408 | 41.3641 | 41.4161
CA-Gladstone Rockhampton | 7415_Gladstone North - Wiggins Is 132 kV | Loading (MVA) | 10.01 | 10.0099 | 10.0099 | 10.01 | 10.01
CA-Gladstone Rockhampton | 7415_Gladstone North - Wiggins Is 132 kV | Loading (MW) | 10.0076 | 10.0076 | 10.0076 | 10.0077 | 10.0077
CA-Gladstone Rockhampton | 7415_Gladstone North - Wiggins Is 132 kV | Power Factor | 0.99973 | 0.99973 | 0.99973 | 0.99973 | 0.99973
CA-Gladstone Rockhampton | 7415_Gladstone North - Wiggins Is 132 kV | Rating (A) | 889 | 889 | 889 | 889 | 889
CA-Gladstone Rockhampton | 7415_Gladstone North - Wiggins Is 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 7415_Gladstone North - Wiggins Is 132 kV | Min Voltage at Constrained Conductor | 139.9192 | 140.1391 | 140.1339 | 139.717 | 139.5421
CA-Gladstone Rockhampton | 7415_Gladstone North - Wiggins Is 132 kV | Contingency Outage | 7414_Gladstone North - Wiggins Is 132 kV | 7414_Gladstone North - Wiggins Is 132 kV | 7414_Gladstone North - Wiggins Is 132 kV | 7414_Gladstone North - Wiggins Is 132 kV | 7414_Gladstone North - Wiggins Is 132 kV
CA-Gladstone Rockhampton | AW113_Awoonga Rurals 11 kV | % of Rated A | 6.048% | 6.047% | 6.046% | 6.045% | 6.059%
CA-Gladstone Rockhampton | AW113_Awoonga Rurals 11 kV | Limiting Line Name | HV_LINE 235473_1 | HV_LINE 235473_1 | HV_LINE 235473_1 | HV_LINE 235473_1 | HV_LINE 235473_1
CA-Gladstone Rockhampton | AW113_Awoonga Rurals 11 kV | Loading (A) | 12.8222 | 12.819 | 12.8167 | 12.8157 | 12.8448
CA-Gladstone Rockhampton | AW113_Awoonga Rurals 11 kV | Loading (MVA) | 0.24842 | 0.24842 | 0.24842 | 0.24842 | 0.24845
CA-Gladstone Rockhampton | AW113_Awoonga Rurals 11 kV | Loading (MW) | 0.20453 | 0.20453 | 0.20453 | 0.20453 | 0.20454
CA-Gladstone Rockhampton | AW113_Awoonga Rurals 11 kV | Power Factor | 0.82315 | 0.82316 | 0.82317 | 0.82317 | 0.82309
CA-Gladstone Rockhampton | AW113_Awoonga Rurals 11 kV | Rating (A) | 212 | 212 | 212 | 212 | 212
CA-Gladstone Rockhampton | AW113_Awoonga Rurals 11 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | AW113_Awoonga Rurals 11 kV | Min Voltage at Constrained Conductor | 11.1859 | 11.1886 | 11.1905 | 11.1913 | 11.1673
CA-Gladstone Rockhampton | AW113_Awoonga Rurals 11 kV | Contingency Outage | 6019_Gladstone South - Friend St 66 kV | 6019_Gladstone South - Friend St 66 kV | 6019_Gladstone South - Friend St 66 kV | 6024_Awoonga - Calliope 66kV | 6022_Gladstone South - Calliope 66 kV
CA-Gladstone Rockhampton | CN101_Base Hospital No.1 11kV | % of Rated A | 0.1948% | 0.1931% | 0.194% | 0.1942% | 0.1943%
CA-Gladstone Rockhampton | CN101_Base Hospital No.1 11kV | Limiting Line Name | HV_CABLE 393680_1 | HV_CABLE 393680_1 | HV_CABLE 393680_1 | HV_CABLE 393680_1 | HV_CABLE 393680_1
CA-Gladstone Rockhampton | CN101_Base Hospital No.1 11kV | Loading (A) | 0.77903 | 0.77257 | 0.77592 | 0.77676 | 0.77719
CA-Gladstone Rockhampton | CN101_Base Hospital No.1 11kV | Loading (MVA) | 0.014691 | 0.014448 | 0.014574 | 0.014605 | 0.014622
CA-Gladstone Rockhampton | CN101_Base Hospital No.1 11kV | Loading (MW) | 0.0041177 | 0.0040496 | 0.0040848 | 0.0040936 | 0.0040982
CA-Gladstone Rockhampton | CN101_Base Hospital No.1 11kV | Power Factor | 0.27966 | 0.27966 | 0.27966 | 0.27966 | 0.27966
CA-Gladstone Rockhampton | CN101_Base Hospital No.1 11kV | Rating (A) | 400 | 400 | 400 | 400 | 400
CA-Gladstone Rockhampton | CN101_Base Hospital No.1 11kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | CN101_Base Hospital No.1 11kV | Min Voltage at Constrained Conductor | 10.8877 | 10.7974 | 10.8441 | 10.8559 | 10.8619
CA-Gladstone Rockhampton | CN101_Base Hospital No.1 11kV | Contingency Outage | 6082_Farnborough Tee - Yeppoon 66 kV | 6005_Rockhampton Glenmore-Canning 66 kV | 6005_Rockhampton Glenmore-Canning 66 kV | 6005_Rockhampton Glenmore-Canning 66 kV | 6005_Rockhampton Glenmore-Canning 66 kV
CA-Gladstone Rockhampton | CN109_Base Hospital No.2 11kV | % of Rated A | 0.7144% | 0.7145% | 0.7154% | 0.7183% | 0.7181%
CA-Gladstone Rockhampton | CN109_Base Hospital No.2 11kV | Limiting Line Name | HV_CABLE 536964_1 | HV_CABLE 536964_1 | HV_CABLE 536964_1 | HV_CABLE 536964_1 | HV_CABLE 536964_1
CA-Gladstone Rockhampton | CN109_Base Hospital No.2 11kV | Loading (A) | 3.4578 | 3.4584 | 3.4627 | 3.4767 | 3.4756
CA-Gladstone Rockhampton | CN109_Base Hospital No.2 11kV | Loading (MVA) | 0.064486 | 0.064486 | 0.064479 | 0.064459 | 0.06446
CA-Gladstone Rockhampton | CN109_Base Hospital No.2 11kV | Loading (MW) | 0.058655 | 0.058655 | 0.058653 | 0.058647 | 0.058647
CA-Gladstone Rockhampton | CN109_Base Hospital No.2 11kV | Power Factor | 0.90717 | 0.90718 | 0.90724 | 0.90746 | 0.90744
CA-Gladstone Rockhampton | CN109_Base Hospital No.2 11kV | Rating (A) | 484 | 484 | 484 | 484 | 484
CA-Gladstone Rockhampton | CN109_Base Hospital No.2 11kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | CN109_Base Hospital No.2 11kV | Min Voltage at Constrained Conductor | 10.7674 | 10.7654 | 10.7509 | 10.7042 | 10.7077
CA-Gladstone Rockhampton | CN109_Base Hospital No.2 11kV | Contingency Outage | 6089_QMAG Tee - QMAG 66 kV | 6088_QMAG Tee - Parkhurst 66 kV | 6003_Glenmore - Berserker 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV
CA-Gladstone Rockhampton | 6096_Egan's Hill - Lakes Creek 66 kV | % of Rated A | 30.14% | 29.25% | 30.4% | 33.86% | 39.33%
CA-Gladstone Rockhampton | 6096_Egan's Hill - Lakes Creek 66 kV | Limiting Line Name | TR_LINE 19756_1 | TR_LINE 19756_1 | TR_LINE 19756_1 | TR_LINE 19756_1 | TR_LINE 19756_1
CA-Gladstone Rockhampton | 6096_Egan's Hill - Lakes Creek 66 kV | Loading (A) | 96.7337 | 93.889 | 97.5706 | 108.6815 | 126.2626
CA-Gladstone Rockhampton | 6096_Egan's Hill - Lakes Creek 66 kV | Loading (MVA) | 11.7868 | 11.4747 | 11.9212 | 13.3125 | 15.5007
CA-Gladstone Rockhampton | 6096_Egan's Hill - Lakes Creek 66 kV | Loading (MW) | 3.0218 | 0.61384 | 4.0693 | 7.3397 | 10.8732
CA-Gladstone Rockhampton | 6096_Egan's Hill - Lakes Creek 66 kV | Power Factor | 0.25637 | 0.053406 | 0.34126 | 0.55126 | 0.70139
CA-Gladstone Rockhampton | 6096_Egan's Hill - Lakes Creek 66 kV | Rating (A) | 321 | 321 | 321 | 321 | 321
CA-Gladstone Rockhampton | 6096_Egan's Hill - Lakes Creek 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6096_Egan's Hill - Lakes Creek 66 kV | Min Voltage at Constrained Conductor | 70.3492 | 70.5613 | 70.5411 | 70.7203 | 70.8787
CA-Gladstone Rockhampton | 6096_Egan's Hill - Lakes Creek 66 kV | Contingency Outage | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV
CA-Moura | 6026_Moura - Theodore 66 kV | % of Rated A | 5.212% | 5.096% | 5.006% | 4.934% | 4.879%
CA-Moura | 6026_Moura - Theodore 66 kV | Limiting Line Name | TR_LINE 59683_1 | TR_LINE 59683_1 | TR_LINE 59683_1 | TR_LINE 59683_1 | TR_LINE 59683_1
CA-Moura | 6026_Moura - Theodore 66 kV | Loading (A) | 37.9921 | 37.1518 | 36.4967 | 35.9696 | 35.5643
CA-Moura | 6026_Moura - Theodore 66 kV | Loading (MVA) | 4.5525 | 4.452 | 4.3736 | 4.3104 | 4.2619
CA-Moura | 6026_Moura - Theodore 66 kV | Loading (MW) | 4.4854 | 4.3821 | 4.3012 | 4.2361 | 4.1859
CA-Moura | 6026_Moura - Theodore 66 kV | Power Factor | 0.98524 | 0.98431 | 0.98346 | 0.98275 | 0.98218
CA-Moura | 6026_Moura - Theodore 66 kV | Rating (A) | 729 | 729 | 729 | 729 | 729
CA-Moura | 6026_Moura - Theodore 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Moura | 6026_Moura - Theodore 66 kV | Min Voltage at Constrained Conductor | 69.183 | 69.1851 | 69.1861 | 69.1866 | 69.1869
CA-Moura | 6026_Moura - Theodore 66 kV | Contingency Outage | 6007_Biloela - Coominglah Tee 66 kV | 6007_Biloela - Coominglah Tee 66 kV | 6007_Biloela - Coominglah Tee 66 kV | 6007_Biloela - Coominglah Tee 66 kV | 6007_Biloela - Coominglah Tee 66 kV
FN-Cairns Area | 7206 Woree-Cairns Terminal-Cairns City | % of Rated A | 19.41% | 18.92% | 18.47% | 18.02% | 17.6%
FN-Cairns Area | 7206 Woree-Cairns Terminal-Cairns City | Limiting Line Name | TR_CABLE 11_1 | TR_CABLE 11_1 | TR_CABLE 11_1 | TR_CABLE 11_1 | TR_CABLE 11_1
FN-Cairns Area | 7206 Woree-Cairns Terminal-Cairns City | Loading (A) | 92.9889 | 90.6352 | 88.4799 | 86.3352 | 84.3087
FN-Cairns Area | 7206 Woree-Cairns Terminal-Cairns City | Loading (MVA) | 24.7147 | 24.0998 | 23.5316 | 22.9611 | 22.4165
FN-Cairns Area | 7206 Woree-Cairns Terminal-Cairns City | Loading (MW) | 24.6459 | 24.0378 | 23.4755 | 22.9106 | 22.3709
FN-Cairns Area | 7206 Woree-Cairns Terminal-Cairns City | Power Factor | 0.99631 | 0.9965 | 0.99667 | 0.99683 | 0.99697
FN-Cairns Area | 7206 Woree-Cairns Terminal-Cairns City | Rating (A) | 479 | 479 | 479 | 479 | 479
FN-Cairns Area | 7206 Woree-Cairns Terminal-Cairns City | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Cairns Area | 7206 Woree-Cairns Terminal-Cairns City | Min Voltage at Constrained Conductor | 153.449 | 153.5164 | 153.5485 | 153.5479 | 153.5095
FN-Cairns Area | 7206 Woree-Cairns Terminal-Cairns City | Contingency Outage | 7227 Woree-Cairns Terminal-Cairns City | 7227 Woree-Cairns Terminal-Cairns City | 7227 Woree-Cairns Terminal-Cairns City | 7227 Woree-Cairns Terminal-Cairns City | 7227 Woree-Cairns Terminal-Cairns City
FN-Cairns Area | 7227 Woree-Cairns Terminal-Cairns City | % of Rated A | 22.2% | 21.64% | 21.12% | 20.61% | 20.13%
FN-Cairns Area | 7227 Woree-Cairns Terminal-Cairns City | Limiting Line Name | TR_LINE 176513_1 | TR_LINE 176513_1 | TR_LINE 176513_1 | TR_LINE 176513_1 | TR_LINE 176513_1
FN-Cairns Area | 7227 Woree-Cairns Terminal-Cairns City | Loading (A) | 92.7811 | 90.4403 | 88.2969 | 86.1644 | 84.1493
FN-Cairns Area | 7227 Woree-Cairns Terminal-Cairns City | Loading (MVA) | 24.6765 | 24.0643 | 23.4987 | 22.9309 | 22.3888
FN-Cairns Area | 7227 Woree-Cairns Terminal-Cairns City | Loading (MW) | 24.6617 | 24.0528 | 23.4898 | 22.9242 | 22.3839
FN-Cairns Area | 7227 Woree-Cairns Terminal-Cairns City | Power Factor | 0.99939 | 0.99951 | 0.99961 | 0.9997 | 0.99977
FN-Cairns Area | 7227 Woree-Cairns Terminal-Cairns City | Rating (A) | 418 | 418 | 418 | 418 | 418
FN-Cairns Area | 7227 Woree-Cairns Terminal-Cairns City | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Cairns Area | 7227 Woree-Cairns Terminal-Cairns City | Min Voltage at Constrained Conductor | 153.5522 | 153.6183 | 153.6491 | 153.6472 | 153.6076
FN-Cairns Area | 7227 Woree-Cairns Terminal-Cairns City | Contingency Outage | 7206 Woree-Cairns Terminal-Cairns City | 7206 Woree-Cairns Terminal-Cairns City | 7206 Woree-Cairns Terminal-Cairns City | 7206 Woree-Cairns Terminal-Cairns City | 7206 Woree-Cairns Terminal-Cairns City
FN-Cairns Area | 7332_Cairns North 132 kV | % of Rated A | 17.2% | 16.73% | 16.73% | 17.14% | 17.99%
FN-Cairns Area | 7332_Cairns North 132 kV | Limiting Line Name | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2
FN-Cairns Area | 7332_Cairns North 132 kV | Loading (A) | 81.3661 | 79.1401 | 79.1276 | 81.0624 | 85.0766
FN-Cairns Area | 7332_Cairns North 132 kV | Loading (MVA) | 21.6632 | 21.0791 | 21.0793 | 21.5937 | 22.6561
FN-Cairns Area | 7332_Cairns North 132 kV | Loading (MW) | 5.7545 | 1.9209 | 1.6704 | 5.1917 | 8.9269
FN-Cairns Area | 7332_Cairns North 132 kV | Power Factor | 0.26563 | 0.091128 | 0.079236 | 0.24042 | 0.39401
FN-Cairns Area | 7332_Cairns North 132 kV | Rating (A) | 473 | 473 | 473 | 473 | 473
FN-Cairns Area | 7332_Cairns North 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Cairns Area | 7332_Cairns North 132 kV | Min Voltage at Constrained Conductor | 153.7159 | 153.7781 | 153.8042 | 153.7965 | 153.7498
FN-Cairns Area | 7332_Cairns North 132 kV | Contingency Outage | 7333_Cairns North 132 kV | 7333_Cairns North 132 kV | 7333_Cairns North 132 kV | 7333_Cairns North 132 kV | 7333_Cairns North 132 kV
FN-Cairns Area | 7333_Cairns North 132 kV | % of Rated A | 17.29% | 16.83% | 16.82% | 17.23% | 18.07%
FN-Cairns Area | 7333_Cairns North 132 kV | Limiting Line Name | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2
FN-Cairns Area | 7333_Cairns North 132 kV | Loading (A) | 81.7881 | 79.5889 | 79.5769 | 81.4887 | 85.4576
FN-Cairns Area | 7333_Cairns North 132 kV | Loading (MVA) | 21.7763 | 21.1993 | 21.1997 | 21.7079 | 22.7583
FN-Cairns Area | 7333_Cairns North 132 kV | Loading (MW) | 5.7562 | 1.9226 | 1.6687 | 5.19 | 8.9252
FN-Cairns Area | 7333_Cairns North 132 kV | Power Factor | 0.26433 | 0.090694 | 0.078704 | 0.23907 | 0.39216
FN-Cairns Area | 7333_Cairns North 132 kV | Rating (A) | 473 | 473 | 473 | 473 | 473
FN-Cairns Area | 7333_Cairns North 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Cairns Area | 7333_Cairns North 132 kV | Min Voltage at Constrained Conductor | 153.7208 | 153.7833 | 153.8093 | 153.8015 | 153.7546
FN-Cairns Area | 7333_Cairns North 132 kV | Contingency Outage | 7332_Cairns North 132 kV | 7332_Cairns North 132 kV | 7332_Cairns North 132 kV | 7332_Cairns North 132 kV | 7332_Cairns North 132 kV
FN-Cairns Area | EDMO-2GO1_Gordonvale 1 22kV | % of Rated A | 58.89% | 58.93% | 58.94% | 58.92% | 58.88%
FN-Cairns Area | EDMO-2GO1_Gordonvale 1 22kV | Limiting Line Name | HV_LINE 1182348_1 | HV_LINE 1182348_1 | HV_LINE 1182348_1 | HV_LINE 1182348_1 | HV_LINE 1182348_1
FN-Cairns Area | EDMO-2GO1_Gordonvale 1 22kV | Loading (A) | 45.9369 | 45.9636 | 45.9711 | 45.9609 | 45.93
FN-Cairns Area | EDMO-2GO1_Gordonvale 1 22kV | Loading (MVA) | 2.0055 | 2.0078 | 2.0084 | 2.0076 | 2.0049
FN-Cairns Area | EDMO-2GO1_Gordonvale 1 22kV | Loading (MW) | 0.024385 | 0.024209 | 0.02416 | 0.024227 | 0.02443
FN-Cairns Area | EDMO-2GO1_Gordonvale 1 22kV | Power Factor | 0.011237 | 0.011136 | 0.011107 | 0.011146 | 0.011264
FN-Cairns Area | EDMO-2GO1_Gordonvale 1 22kV | Rating (A) | 78 | 78 | 78 | 78 | 78
FN-Cairns Area | EDMO-2GO1_Gordonvale 1 22kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Cairns Area | EDMO-2GO1_Gordonvale 1 22kV | Min Voltage at Constrained Conductor | 25.2034 | 25.2181 | 25.2222 | 25.2166 | 25.1996
FN-Cairns Area | EDMO-2GO1_Gordonvale 1 22kV | Contingency Outage | EDMO-2GO3_Gordonvale 3 22kV | EDMO-2GO3_Gordonvale 3 22kV | EDMO-2GO3_Gordonvale 3 22kV | EDMO-2GO3_Gordonvale 3 22kV | EDMO-2GO3_Gordonvale 3 22kV
FN-Cairns Area | EDMO-2GO2_Gordonvale 2 22kV | % of Rated A | 48.94% | 48.97% | 48.98% | 48.97% | 48.94%
FN-Cairns Area | EDMO-2GO2_Gordonvale 2 22kV | Limiting Line Name | HV_LINE 650000_1 | HV_LINE 650000_1 | HV_LINE 650000_1 | HV_LINE 650000_1 | HV_LINE 650000_1
FN-Cairns Area | EDMO-2GO2_Gordonvale 2 22kV | Loading (A) | 38.1758 | 38.1998 | 38.2065 | 38.1974 | 38.1696
FN-Cairns Area | EDMO-2GO2_Gordonvale 2 22kV | Loading (MVA) | 1.6638 | 1.6658 | 1.6664 | 1.6656 | 1.6633
FN-Cairns Area | EDMO-2GO2_Gordonvale 2 22kV | Loading (MW) | 0.35728 | 0.35715 | 0.35711 | 0.35716 | 0.35731
FN-Cairns Area | EDMO-2GO2_Gordonvale 2 22kV | Power Factor | 0.21062 | 0.21028 | 0.21019 | 0.21032 | 0.21071
FN-Cairns Area | EDMO-2GO2_Gordonvale 2 22kV | Rating (A) | 78 | 78 | 78 | 78 | 78
FN-Cairns Area | EDMO-2GO2_Gordonvale 2 22kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Cairns Area | EDMO-2GO2_Gordonvale 2 22kV | Min Voltage at Constrained Conductor | 25.1545 | 25.169 | 25.1731 | 25.1675 | 25.1507
FN-Cairns Area | EDMO-2GO2_Gordonvale 2 22kV | Contingency Outage | EDMO-2GO3_Gordonvale 3 22kV | EDMO-2GO3_Gordonvale 3 22kV | EDMO-2GO3_Gordonvale 3 22kV | EDMO-2GO3_Gordonvale 3 22kV | EDMO-2GO3_Gordonvale 3 22kV
FN-Cairns Area | EDMO-2GO3_Gordonvale 3 22kV | % of Rated A | 43.24% | 43.27% | 43.27% | 43.26% | 43.23%
FN-Cairns Area | EDMO-2GO3_Gordonvale 3 22kV | Limiting Line Name | HV_LINE 36762_1 | HV_LINE 36762_1 | HV_LINE 36762_1 | HV_LINE 36762_1 | HV_LINE 36762_1
FN-Cairns Area | EDMO-2GO3_Gordonvale 3 22kV | Loading (A) | 57.077 | 57.1109 | 57.1199 | 57.1059 | 57.065
FN-Cairns Area | EDMO-2GO3_Gordonvale 3 22kV | Loading (MVA) | 2.5029 | 2.5058 | 2.5065 | 2.5053 | 2.5019
FN-Cairns Area | EDMO-2GO3_Gordonvale 3 22kV | Loading (MW) | 0.18257 | 0.18265 | 0.18267 | 0.18263 | 0.18255
FN-Cairns Area | EDMO-2GO3_Gordonvale 3 22kV | Power Factor | 0.072872 | 0.072817 | 0.072803 | 0.072826 | 0.072892
FN-Cairns Area | EDMO-2GO3_Gordonvale 3 22kV | Rating (A) | 132 | 132 | 132 | 132 | 132
FN-Cairns Area | EDMO-2GO3_Gordonvale 3 22kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Cairns Area | EDMO-2GO3_Gordonvale 3 22kV | Min Voltage at Constrained Conductor | 25.3167 | 25.3309 | 25.3346 | 25.3288 | 25.3116
FN-Cairns Area | EDMO-2GO3_Gordonvale 3 22kV | Contingency Outage | EDMO-2GO1_Gordonvale 1 22kV | EDMO-2GO1_Gordonvale 1 22kV | EDMO-2GO1_Gordonvale 1 22kV | EDMO-2GO1_Gordonvale 1 22kV | EDMO-2GO1_Gordonvale 1 22kV
FN-Cairns Area | GORD-2RIV_Riverstone Rd 22kV | % of Rated A | 4.358% | 4.355% | 4.354% | 4.355% | 4.357%
FN-Cairns Area | GORD-2RIV_Riverstone Rd 22kV | Limiting Line Name | HV_LINE 53928_1 | HV_LINE 53928_1 | HV_LINE 53928_1 | HV_LINE 53928_1 | HV_LINE 53928_1
FN-Cairns Area | GORD-2RIV_Riverstone Rd 22kV | Loading (A) | 5.752 | 5.7484 | 5.7472 | 5.7482 | 5.7518
FN-Cairns Area | GORD-2RIV_Riverstone Rd 22kV | Loading (MVA) | 0.25069 | 0.25069 | 0.25069 | 0.25069 | 0.25069
FN-Cairns Area | GORD-2RIV_Riverstone Rd 22kV | Loading (MW) | 0.21538 | 0.21538 | 0.21538 | 0.21538 | 0.21538
FN-Cairns Area | GORD-2RIV_Riverstone Rd 22kV | Power Factor | 0.85912 | 0.85913 | 0.85913 | 0.85913 | 0.85912
FN-Cairns Area | GORD-2RIV_Riverstone Rd 22kV | Rating (A) | 132 | 132 | 132 | 132 | 132
FN-Cairns Area | GORD-2RIV_Riverstone Rd 22kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Cairns Area | GORD-2RIV_Riverstone Rd 22kV | Min Voltage at Constrained Conductor | 25.1628 | 25.1787 | 25.1839 | 25.1794 | 25.1637
FN-Cairns Area | GORD-2RIV_Riverstone Rd 22kV | Contingency Outage | 7206 Woree-Cairns Terminal-Cairns City | 7206 Woree-Cairns Terminal-Cairns City | 7227 Woree-Cairns Terminal-Cairns City | 7227 Woree-Cairns Terminal-Cairns City | 7227 Woree-Cairns Terminal-Cairns City
FN-Cairns Area | KAME-2CO1 Cook No 1 22kV | % of Rated A | 44.37% | 44.37% | 44.36% | 44.35% | 44.35%
FN-Cairns Area | KAME-2CO1 Cook No 1 22kV | Limiting Line Name | HV_CABLE_38741076_1 | HV_CABLE_38741076_1 | HV_CABLE_38741076_1 | HV_CABLE_38741076_1 | HV_CABLE_38741076_1
FN-Cairns Area | KAME-2CO1 Cook No 1 22kV | Loading (A) | 59.9007 | 59.8969 | 59.8803 | 59.8703 | 59.8677
FN-Cairns Area | KAME-2CO1 Cook No 1 22kV | Loading (MVA) | 2.5964 | 2.5995 | 2.6011 | 2.6021 | 2.6024
FN-Cairns Area | KAME-2CO1 Cook No 1 22kV | Loading (MW) | 2.3773 | 2.3776 | 2.3776 | 2.3777 | 2.3777
FN-Cairns Area | KAME-2CO1 Cook No 1 22kV | Power Factor | 0.91564 | 0.91462 | 0.91408 | 0.91375 | 0.91366
FN-Cairns Area | KAME-2CO1 Cook No 1 22kV | Rating (A) | 135 | 135 | 135 | 135 | 135
FN-Cairns Area | KAME-2CO1 Cook No 1 22kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Cairns Area | KAME-2CO1 Cook No 1 22kV | Min Voltage at Constrained Conductor | 25.0109 | 25.0429 | 25.0655 | 25.0791 | 25.0827
FN-Cairns Area | KAME-2CO1 Cook No 1 22kV | Contingency Outage | KAME-2CO3 Cook No 3 22kV | KAME-2CO3 Cook No 3 22kV | KAME-2CO3 Cook No 3 22kV | KAME-2CO3 Cook No 3 22kV | KAME-2CO3 Cook No 3 22kV
FN-Cairns Area | KAME-2CO2 Cook No 2 22kV | % of Rated A | 27.97% | 28.03% | 28.06% | 28.07% | 28.07%
FN-Cairns Area | KAME-2CO2 Cook No 2 22kV | Limiting Line Name | HV_CABLE_12173517_1 | HV_CABLE_12173517_1 | HV_CABLE_12173517_1 | HV_CABLE_12173517_1 | HV_CABLE_12173517_1
FN-Cairns Area | KAME-2CO2 Cook No 2 22kV | Loading (A) | 37.7629 | 37.8448 | 37.876 | 37.8937 | 37.8959
FN-Cairns Area | KAME-2CO2 Cook No 2 22kV | Loading (MVA) | 1.6407 | 1.6462 | 1.6489 | 1.6504 | 1.6506
FN-Cairns Area | KAME-2CO2 Cook No 2 22kV | Loading (MW) | 0.015568 | 0.015675 | 0.0157 | 0.015715 | 0.015717
FN-Cairns Area | KAME-2CO2 Cook No 2 22kV | Power Factor | 0.0089152 | 0.0089478 | 0.0089477 | 0.0089477 | 0.0089476
FN-Cairns Area | KAME-2CO2 Cook No 2 22kV | Rating (A) | 135 | 135 | 135 | 135 | 135
FN-Cairns Area | KAME-2CO2 Cook No 2 22kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Cairns Area | KAME-2CO2 Cook No 2 22kV | Min Voltage at Constrained Conductor | 25.0838 | 25.1138 | 25.1344 | 25.1461 | 25.1475
FN-Cairns Area | KAME-2CO2 Cook No 2 22kV | Contingency Outage | KAME-2CO1 Cook No 1 22kV | KAME-2CO1 Cook No 1 22kV | KAME-2CO1 Cook No 1 22kV | KAME-2CO1 Cook No 1 22kV | KAME-2CO1 Cook No 1 22kV
FN-Cairns Area | KAME-2CO3 Cook No 3 22kV | % of Rated A | 27.75% | 27.81% | 27.83% | 27.84% | 27.84%
FN-Cairns Area | KAME-2CO3 Cook No 3 22kV | Limiting Line Name | HV_CABLE_12128762_1 | HV_CABLE_12128762_1 | HV_CABLE_12128762_1 | HV_CABLE_12128762_1 | HV_CABLE_12128762_1
FN-Cairns Area | KAME-2CO3 Cook No 3 22kV | Loading (A) | 37.4569 | 37.5381 | 37.5692 | 37.5869 | 37.589
FN-Cairns Area | KAME-2CO3 Cook No 3 22kV | Loading (MVA) | 1.6274 | 1.6328 | 1.6355 | 1.6371 | 1.6373
FN-Cairns Area | KAME-2CO3 Cook No 3 22kV | Loading (MW) | 0.068465 | 0.068714 | 0.068808 | 0.068861 | 0.068868
FN-Cairns Area | KAME-2CO3 Cook No 3 22kV | Power Factor | 0.041718 | 0.041728 | 0.041716 | 0.04171 | 0.041709
FN-Cairns Area | KAME-2CO3 Cook No 3 22kV | Rating (A) | 135 | 135 | 135 | 135 | 135
FN-Cairns Area | KAME-2CO3 Cook No 3 22kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Cairns Area | KAME-2CO3 Cook No 3 22kV | Min Voltage at Constrained Conductor | 25.0838 | 25.1138 | 25.1344 | 25.1461 | 25.1475
FN-Cairns Area | KAME-2CO3 Cook No 3 22kV | Contingency Outage | KAME-2CO1 Cook No 1 22kV | KAME-2CO1 Cook No 1 22kV | KAME-2CO1 Cook No 1 22kV | KAME-2CO1 Cook No 1 22kV | KAME-2CO1 Cook No 1 22kV
FN-Gulf | 3CRO_Croydon 66 kV | % of Rated A | 4.3% | 4.06% | 3.888% | 3.888% | 3.888%
FN-Gulf | 3CRO_Croydon 66 kV | Limiting Line Name | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1
FN-Gulf | 3CRO_Croydon 66 kV | Loading (A) | 19.6505 | 18.5562 | 17.7695 | 17.7681 | 17.7676
FN-Gulf | 3CRO_Croydon 66 kV | Loading (MVA) | 2.362 | 2.2309 | 2.1396 | 2.1396 | 2.1398
FN-Gulf | 3CRO_Croydon 66 kV | Loading (MW) | 1.0235 | 0.82938 | 0.10121 | 0.087433 | 0.076396
FN-Gulf | 3CRO_Croydon 66 kV | Power Factor | 0.43333 | 0.37176 | 0.047306 | 0.040863 | 0.035702
FN-Gulf | 3CRO_Croydon 66 kV | Rating (A) | 457 | 457 | 457 | 457 | 457
FN-Gulf | 3CRO_Croydon 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Gulf | 3CRO_Croydon 66 kV | Min Voltage at Constrained Conductor | 69.3975 | 69.4129 | 69.5169 | 69.5249 | 69.5319
FN-Gulf | 3CRO_Croydon 66 kV | Contingency Outage | Kidston Solar Farm (Genex) | Kidston Solar Farm (Genex) | 3NOR_Normanton 66 kV | 3NOR_Normanton 66 kV | 3NOR_Normanton 66 kV
FN-Gulf | 3NOR_Normanton 66 kV | % of Rated A | 4.493% | 4.51% | 4.539% | 4.575% | 4.614%
FN-Gulf | 3NOR_Normanton 66 kV | Limiting Line Name | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1
FN-Gulf | 3NOR_Normanton 66 kV | Loading (A) | 20.5351 | 20.6112 | 20.7442 | 20.9062 | 21.0841
FN-Gulf | 3NOR_Normanton 66 kV | Loading (MVA) | 2.4419 | 2.4517 | 2.4682 | 2.4879 | 2.5095
FN-Gulf | 3NOR_Normanton 66 kV | Loading (MW) | 0.87801 | 0.70869 | 0.57354 | 0.4596 | 0.35989
FN-Gulf | 3NOR_Normanton 66 kV | Power Factor | 0.35547 | 0.2852 | 0.22863 | 0.18103 | 0.1397
FN-Gulf | 3NOR_Normanton 66 kV | Rating (A) | 457 | 457 | 457 | 457 | 457
FN-Gulf | 3NOR_Normanton 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Gulf | 3NOR_Normanton 66 kV | Min Voltage at Constrained Conductor | 68.6552 | 68.6766 | 68.6934 | 68.7072 | 68.7192
FN-Gulf | 3NOR_Normanton 66 kV | Contingency Outage | 3DIM_Dimbulah 66 kV | 3DIM_Dimbulah 66 kV | 3DIM_Dimbulah 66 kV | 3DIM_Dimbulah 66 kV | 3DIM_Dimbulah 66 kV
FN-Gulf | 4KID_Ross - Kidston 132 kV | % of Rated A | 19.23% | 19.23% | 19.23% | 19.23% | 19.23%
FN-Gulf | 4KID_Ross - Kidston 132 kV | Limiting Line Name | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1
FN-Gulf | 4KID_Ross - Kidston 132 kV | Loading (A) | 68.2684 | 68.268 | 68.2681 | 68.2682 | 68.2682
FN-Gulf | 4KID_Ross - Kidston 132 kV | Loading (MVA) | 16.3903 | 16.3903 | 16.3903 | 16.3904 | 16.3904
FN-Gulf | 4KID_Ross - Kidston 132 kV | Loading (MW) | 1.2842 | 1.275 | 1.275 | 1.275 | 1.275
FN-Gulf | 4KID_Ross - Kidston 132 kV | Power Factor | 0.078352 | 0.07779 | 0.07779 | 0.07779 | 0.07779
FN-Gulf | 4KID_Ross - Kidston 132 kV | Rating (A) | 355 | 355 | 355 | 355 | 355
FN-Gulf | 4KID_Ross - Kidston 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Gulf | 4KID_Ross - Kidston 132 kV | Min Voltage at Constrained Conductor | 138.6141 | 138.6144 | 138.6146 | 138.6147 | 138.6148
FN-Gulf | 4KID_Ross - Kidston 132 kV | Contingency Outage | 7216_4GEO (Georgetown) 132 kV | 7216_4GEO (Georgetown) 132 kV | 7216_4GEO (Georgetown) 132 kV | 7216_4GEO (Georgetown) 132 kV | 7216_4GEO (Georgetown) 132 kV
FN-Gulf | 7216_4GEO (Georgetown) 132 kV | % of Rated A | 9.883% | 9.913% | 9.937% | 9.959% | 9.979%
FN-Gulf | 7216_4GEO (Georgetown) 132 kV | Limiting Line Name | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1
FN-Gulf | 7216_4GEO (Georgetown) 132 kV | Loading (A) | 29.4523 | 29.5409 | 29.6123 | 29.6769 | 29.7381
FN-Gulf | 7216_4GEO (Georgetown) 132 kV | Loading (MVA) | 7.2632 | 7.2865 | 7.3052 | 7.322 | 7.338
FN-Gulf | 7216_4GEO (Georgetown) 132 kV | Loading (MW) | 0.34891 | 0.2564 | 0.17942 | 0.1128 | 0.051843
FN-Gulf | 7216_4GEO (Georgetown) 132 kV | Power Factor | 0.045415 | 0.032554 | 0.021916 | 0.012751 | 0.0044017
FN-Gulf | 7216_4GEO (Georgetown) 132 kV | Rating (A) | 298 | 298 | 298 | 298 | 298
FN-Gulf | 7216_4GEO (Georgetown) 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Gulf | 7216_4GEO (Georgetown) 132 kV | Min Voltage at Constrained Conductor | 142.3791 | 142.407 | 142.4285 | 142.4469 | 142.4637
FN-Gulf | 7216_4GEO (Georgetown) 132 kV | Contingency Outage | 3CRO_Croydon 66 kV | 3CRO_Croydon 66 kV | 3CRO_Croydon 66 kV | 3CRO_Croydon 66 kV | 3CRO_Croydon 66 kV
FN-Gulf | Kidston Solar Farm (Genex) | % of Rated A | 0.0289% | 0.0289% | 0.0289% | 0.0289% | 0.0289%
FN-Gulf | Kidston Solar Farm (Genex) | Limiting Line Name | Genex_Interconnection | Genex_Interconnection | Genex_Interconnection | Genex_Interconnection | Genex_Interconnection
FN-Gulf | Kidston Solar Farm (Genex) | Loading (A) | 0.28903 | 0.28903 | 0.28903 | 0.28903 | 0.28903
FN-Gulf | Kidston Solar Farm (Genex) | Loading (MVA) | 0.072776 | 0.07278 | 0.072781 | 0.072781 | 0.072781
FN-Gulf | Kidston Solar Farm (Genex) | Loading (MW) | 5.2886e-08 | 5.2888e-08 | 5.2889e-08 | 5.2887e-08 | 5.2885e-08
FN-Gulf | Kidston Solar Farm (Genex) | Power Factor | 7.267e-07 | 7.2668e-07 | 7.2669e-07 | 7.2667e-07 | 7.2664e-07
FN-Gulf | Kidston Solar Farm (Genex) | Rating (A) | 1000 | 1000 | 1000 | 1000 | 1000
FN-Gulf | Kidston Solar Farm (Genex) | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Gulf | Kidston Solar Farm (Genex) | Min Voltage at Constrained Conductor | 145.3759 | 145.3802 | 145.3804 | 145.3805 | 145.3806
FN-Gulf | Kidston Solar Farm (Genex) | Contingency Outage | 7216_4GEO (Georgetown) 132 kV | 7216_4GEO (Georgetown) 132 kV | 7216_4GEO (Georgetown) 132 kV | 7216_4GEO (Georgetown) 132 kV | 7216_4GEO (Georgetown) 132 kV
FN-Innisfail | 2BA1_Babinda No 1 22 kV | % of Rated A | 3.606% | 3.604% | 3.602% | 3.602% | 3.602%
FN-Innisfail | 2BA1_Babinda No 1 22 kV | Limiting Line Name | HV_LINE 20534_1 | HV_LINE 20534_1 | HV_LINE 20534_1 | HV_LINE 20534_1 | HV_LINE 20534_1
FN-Innisfail | 2BA1_Babinda No 1 22 kV | Loading (A) | 4.7599 | 4.7567 | 4.7548 | 4.7542 | 4.7548
FN-Innisfail | 2BA1_Babinda No 1 22 kV | Loading (MVA) | 0.19729 | 0.19728 | 0.19728 | 0.19727 | 0.19728
FN-Innisfail | 2BA1_Babinda No 1 22 kV | Loading (MW) | 0.19419 | 0.1942 | 0.1942 | 0.1942 | 0.1942
FN-Innisfail | 2BA1_Babinda No 1 22 kV | Power Factor | 0.98423 | 0.9843 | 0.98434 | 0.98435 | 0.98434
FN-Innisfail | 2BA1_Babinda No 1 22 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
FN-Innisfail | 2BA1_Babinda No 1 22 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Innisfail | 2BA1_Babinda No 1 22 kV | Min Voltage at Constrained Conductor | 23.9306 | 23.9455 | 23.9541 | 23.9572 | 23.9543
FN-Innisfail | 2BA1_Babinda No 1 22 kV | Contingency Outage | 2BA2_Babinda No 2 22 kV | 2BA2_Babinda No 2 22 kV | 2BA2_Babinda No 2 22 kV | 2BA2_Babinda No 2 22 kV | 2BA2_Babinda No 2 22 kV
FN-Innisfail | 2BA2_Babinda No 2 22 kV | % of Rated A | 3.59% | 3.588% | 3.587% | 3.587% | 3.587%
FN-Innisfail | 2BA2_Babinda No 2 22 kV | Limiting Line Name | HV_LINE 38931_1 | HV_LINE 38931_1 | HV_LINE 38931_1 | HV_LINE 38931_1 | HV_LINE 38931_1
FN-Innisfail | 2BA2_Babinda No 2 22 kV | Loading (A) | 4.7385 | 4.7361 | 4.7347 | 4.7342 | 4.7347
FN-Innisfail | 2BA2_Babinda No 2 22 kV | Loading (MVA) | 0.19644 | 0.19646 | 0.19647 | 0.19648 | 0.19647
FN-Innisfail | 2BA2_Babinda No 2 22 kV | Loading (MW) | 0.19518 | 0.19519 | 0.19519 | 0.19519 | 0.19519
FN-Innisfail | 2BA2_Babinda No 2 22 kV | Power Factor | 0.99362 | 0.99353 | 0.99348 | 0.99346 | 0.99348
FN-Innisfail | 2BA2_Babinda No 2 22 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
FN-Innisfail | 2BA2_Babinda No 2 22 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Innisfail | 2BA2_Babinda No 2 22 kV | Min Voltage at Constrained Conductor | 23.9338 | 23.9488 | 23.9574 | 23.9605 | 23.9577
FN-Innisfail | 2BA2_Babinda No 2 22 kV | Contingency Outage | 2BA1_Babinda No 1 22 kV | 2BA1_Babinda No 1 22 kV | 2BA1_Babinda No 1 22 kV | 2BA1_Babinda No 1 22 kV | 2BA1_Babinda No 1 22 kV
FN-Innisfail | 2MOU_Mourilyan 22 kV | % of Rated A | 4.575% | 4.575% | 4.576% | 4.576% | 4.576%
FN-Innisfail | 2MOU_Mourilyan 22 kV | Limiting Line Name | HV_CABLE 1415_1 | HV_CABLE 1415_1 | HV_CABLE 1415_1 | HV_CABLE 1415_1 | HV_CABLE 1415_1
FN-Innisfail | 2MOU_Mourilyan 22 kV | Loading (A) | 4.5749 | 4.5754 | 4.5757 | 4.5758 | 4.5757
FN-Innisfail | 2MOU_Mourilyan 22 kV | Loading (MVA) | 0.18967 | 0.18981 | 0.18989 | 0.18992 | 0.1899
FN-Innisfail | 2MOU_Mourilyan 22 kV | Loading (MW) | 0.083409 | 0.083408 | 0.083408 | 0.083408 | 0.083408
FN-Innisfail | 2MOU_Mourilyan 22 kV | Power Factor | 0.43971 | 0.43938 | 0.43919 | 0.43912 | 0.43918
FN-Innisfail | 2MOU_Mourilyan 22 kV | Rating (A) | 100 | 100 | 100 | 100 | 100
FN-Innisfail | 2MOU_Mourilyan 22 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Innisfail | 2MOU_Mourilyan 22 kV | Min Voltage at Constrained Conductor | 23.9366 | 23.9516 | 23.9602 | 23.9633 | 23.9605
FN-Innisfail | 2MOU_Mourilyan 22 kV | Contingency Outage | 2SI2_Silkwood No 2 22 kV | 2SI2_Silkwood No 2 22 kV | 2SI2_Silkwood No 2 22 kV | 2SI2_Silkwood No 2 22 kV | 2SI2_Silkwood No 2 22 kV
FN-Innisfail | 2SI1_Silkwood No 1 22 kV | % of Rated A | 1.169% | 1.169% | 1.169% | 1.169% | 1.169%
FN-Innisfail | 2SI1_Silkwood No 1 22 kV | Limiting Line Name | HV_LINE 54592_1 | HV_LINE 54592_1 | HV_LINE 54592_1 | HV_LINE 54592_1 | HV_LINE 54592_1
FN-Innisfail | 2SI1_Silkwood No 1 22 kV | Loading (A) | 1.5436 | 1.543 | 1.5427 | 1.5425 | 1.5427
FN-Innisfail | 2SI1_Silkwood No 1 22 kV | Loading (MVA) | 0.063979 | 0.063994 | 0.064003 | 0.064007 | 0.064004
FN-Innisfail | 2SI1_Silkwood No 1 22 kV | Loading (MW) | 0.052947 | 0.052951 | 0.052954 | 0.052955 | 0.052954
FN-Innisfail | 2SI1_Silkwood No 1 22 kV | Power Factor | 0.82757 | 0.82744 | 0.82736 | 0.82733 | 0.82736
FN-Innisfail | 2SI1_Silkwood No 1 22 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
FN-Innisfail | 2SI1_Silkwood No 1 22 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Innisfail | 2SI1_Silkwood No 1 22 kV | Min Voltage at Constrained Conductor | 23.9299 | 23.9449 | 23.9536 | 23.9566 | 23.9538
FN-Innisfail | 2SI1_Silkwood No 1 22 kV | Contingency Outage | 2SI2_Silkwood No 2 22 kV | 2SI2_Silkwood No 2 22 kV | 2SI2_Silkwood No 2 22 kV | 2SI2_Silkwood No 2 22 kV | 2SI2_Silkwood No 2 22 kV
FN-Innisfail | 2SI2_Silkwood No 2 22 kV | % of Rated A | 1.491% | 1.49% | 1.489% | 1.489% | 1.489%
FN-Innisfail | 2SI2_Silkwood No 2 22 kV | Limiting Line Name | HV_CABLE 217_1 | HV_CABLE 217_1 | HV_CABLE 217_1 | HV_CABLE 217_1 | HV_CABLE 217_1
FN-Innisfail | 2SI2_Silkwood No 2 22 kV | Loading (A) | 1.4907 | 1.4897 | 1.4892 | 1.489 | 1.4891
FN-Innisfail | 2SI2_Silkwood No 2 22 kV | Loading (MVA) | 0.061804 | 0.061802 | 0.061802 | 0.061801 | 0.061802
FN-Innisfail | 2SI2_Silkwood No 2 22 kV | Loading (MW) | 0.05951 | 0.059512 | 0.059513 | 0.059514 | 0.059513
FN-Innisfail | 2SI2_Silkwood No 2 22 kV | Power Factor | 0.96011 | 0.96015 | 0.96018 | 0.96019 | 0.96018
FN-Innisfail | 2SI2_Silkwood No 2 22 kV | Rating (A) | 100 | 100 | 100 | 100 | 100
FN-Innisfail | 2SI2_Silkwood No 2 22 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Innisfail | 2SI2_Silkwood No 2 22 kV | Min Voltage at Constrained Conductor | 23.9369 | 23.9519 | 23.9606 | 23.9636 | 23.9608
FN-Innisfail | 2SI2_Silkwood No 2 22 kV | Contingency Outage | 2SI1_Silkwood No 1 22 kV | 2SI1_Silkwood No 1 22 kV | 2SI1_Silkwood No 1 22 kV | 2SI1_Silkwood No 1 22 kV | 2SI1_Silkwood No 1 22 kV
FN-Tablelands Cooktown | 2HEL_Helenvale 22 kV | % of Rated A | 1.794% | 1.794% | 1.795% | 1.794% | 1.793%
FN-Tablelands Cooktown | 2HEL_Helenvale 22 kV | Limiting Line Name | HV_LINE 42881_2 | HV_LINE 42881_2 | HV_LINE 42881_2 | HV_LINE 42881_2 | HV_LINE 42881_2
FN-Tablelands Cooktown | 2HEL_Helenvale 22 kV | Loading (A) | 1.5605 | 1.561 | 1.5619 | 1.5606 | 1.5603
FN-Tablelands Cooktown | 2HEL_Helenvale 22 kV | Loading (MVA) | 0.060159 | 0.060196 | 0.060271 | 0.060169 | 0.060141
FN-Tablelands Cooktown | 2HEL_Helenvale 22 kV | Loading (MW) | 2.5911e-05 | 2.5927e-05 | 2.5959e-05 | 2.5916e-05 | 2.5904e-05
FN-Tablelands Cooktown | 2HEL_Helenvale 22 kV | Power Factor | 0.00040912 | 0.00040912 | 0.00040912 | 0.00040912 | 0.00040912
FN-Tablelands Cooktown | 2HEL_Helenvale 22 kV | Rating (A) | 87 | 87 | 87 | 87 | 87
FN-Tablelands Cooktown | 2HEL_Helenvale 22 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Tablelands Cooktown | 2HEL_Helenvale 22 kV | Min Voltage at Constrained Conductor | 22.2578 | 22.2645 | 22.2783 | 22.2595 | 22.2544
FN-Tablelands Cooktown | 2HEL_Helenvale 22 kV | Contingency Outage | Mungana 66 kV | 3EVE_Evelyn 66 kV | Mungana 66 kV | 3MTG_Mt Garnet 66 kV | 3COO_Cooktown 66 kV
FN-Tablelands Cooktown | 2KAT_Atherton 22 kV | % of Rated A | 1.457% | 1.453% | 1.461% | 1.458% | 1.455%
FN-Tablelands Cooktown | 2KAT_Atherton 22 kV | Limiting Line Name | HV_CABLE 122_1 | HV_CABLE 122_1 | HV_CABLE 122_1 | HV_CABLE 122_1 | HV_CABLE 122_1
FN-Tablelands Cooktown | 2KAT_Atherton 22 kV | Loading (A) | 1.457 | 1.4525 | 1.4609 | 1.4577 | 1.4547
FN-Tablelands Cooktown | 2KAT_Atherton 22 kV | Loading (MVA) | 0.055671 | 0.055659 | 0.055682 | 0.055673 | 0.055663
FN-Tablelands Cooktown | 2KAT_Atherton 22 kV | Loading (MW) | 0.054295 | 0.054305 | 0.054286 | 0.054293 | 0.054299
FN-Tablelands Cooktown | 2KAT_Atherton 22 kV | Power Factor | 0.9689 | 0.96925 | 0.9686 | 0.96885 | 0.96909
FN-Tablelands Cooktown | 2KAT_Atherton 22 kV | Rating (A) | 100 | 100 | 100 | 100 | 100
FN-Tablelands Cooktown | 2KAT_Atherton 22 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Tablelands Cooktown | 2KAT_Atherton 22 kV | Min Voltage at Constrained Conductor | 22.0604 | 22.1236 | 22.006 | 22.0511 | 22.0926
FN-Tablelands Cooktown | 2KAT_Atherton 22 kV | Contingency Outage | 7285_4LAK (Lakeland) 132kV | 7285_4LAK (Lakeland) 132kV | 7285_4LAK (Lakeland) 132kV | 7285_4LAK (Lakeland) 132kV | 7285_4LAK (Lakeland) 132kV
FN-Tablelands Cooktown | 2MOS_Mossman 22 kV | % of Rated A | 5.369% | 5.342% | 5.051% | 5.038% | 5.027%
FN-Tablelands Cooktown | 2MOS_Mossman 22 kV | Limiting Line Name | HV_LINE 27084_1 | HV_LINE 27084_1 | HV_LINE 27084_1 | HV_LINE 27084_1 | HV_LINE 27084_1
FN-Tablelands Cooktown | 2MOS_Mossman 22 kV | Loading (A) | 7.0875 | 7.0512 | 6.6669 | 6.6507 | 6.635
FN-Tablelands Cooktown | 2MOS_Mossman 22 kV | Loading (MVA) | 0.27266 | 0.2728 | 0.27446 | 0.27454 | 0.27462
FN-Tablelands Cooktown | 2MOS_Mossman 22 kV | Loading (MW) | 0.23627 | 0.23638 | 0.23773 | 0.23779 | 0.23785
FN-Tablelands Cooktown | 2MOS_Mossman 22 kV | Power Factor | 0.86651 | 0.86648 | 0.86614 | 0.86612 | 0.8661
FN-Tablelands Cooktown | 2MOS_Mossman 22 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
FN-Tablelands Cooktown | 2MOS_Mossman 22 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Tablelands Cooktown | 2MOS_Mossman 22 kV | Min Voltage at Constrained Conductor | 22.2111 | 22.3368 | 23.7683 | 23.8329 | 23.8958
FN-Tablelands Cooktown | 2MOS_Mossman 22 kV | Contingency Outage | 7285_4LAK (Lakeland) 132kV | 7285_4LAK (Lakeland) 132kV | 7285_4LAK (Lakeland) 132kV | 7285_4LAK (Lakeland) 132kV | 7285_4LAK (Lakeland) 132kV
FN-Tablelands Cooktown | 2WH1_Ravenshoe 22 kV | % of Rated A | 0.8637% | 0.8668% | 0.8653% | 0.8674% | 0.8695%
FN-Tablelands Cooktown | 2WH1_Ravenshoe 22 kV | Limiting Line Name | HV_CABLE 272_1 | HV_CABLE 272_1 | HV_CABLE 272_1 | HV_CABLE 272_1 | HV_CABLE 272_1
FN-Tablelands Cooktown | 2WH1_Ravenshoe 22 kV | Loading (A) | 0.86373 | 0.86676 | 0.86525 | 0.86735 | 0.86949
FN-Tablelands Cooktown | 2WH1_Ravenshoe 22 kV | Loading (MVA) | 0.034329 | 0.03457 | 0.03445 | 0.034618 | 0.034788
FN-Tablelands Cooktown | 2WH1_Ravenshoe 22 kV | Loading (MW) | 0.00068648 | 0.00069129 | 0.00068889 | 0.00069224 | 0.00069565
FN-Tablelands Cooktown | 2WH1_Ravenshoe 22 kV | Power Factor | 0.019997 | 0.019997 | 0.019997 | 0.019997 | 0.019997
FN-Tablelands Cooktown | 2WH1_Ravenshoe 22 kV | Rating (A) | 100 | 100 | 100 | 100 | 100
FN-Tablelands Cooktown | 2WH1_Ravenshoe 22 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Tablelands Cooktown | 2WH1_Ravenshoe 22 kV | Min Voltage at Constrained Conductor | 22.947 | 23.0274 | 22.9874 | 23.0432 | 23.0999
FN-Tablelands Cooktown | 2WH1_Ravenshoe 22 kV | Contingency Outage | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | Mungana 66 kV | Mungana 66 kV | Mungana 66 kV
FN-Tablelands Cooktown | 2WH2_Ravenshoe 22kV | % of Rated A | 0.2417% | 0.2426% | 0.2421% | 0.2427% | 0.2433%
FN-Tablelands Cooktown | 2WH2_Ravenshoe 22kV | Limiting Line Name | HV_LINE 35947_1 | HV_LINE 35947_1 | HV_LINE 35947_1 | HV_LINE 35947_1 | HV_LINE 35947_1
FN-Tablelands Cooktown | 2WH2_Ravenshoe 22kV | Loading (A) | 0.60188 | 0.60398 | 0.60293 | 0.6044 | 0.60589
FN-Tablelands Cooktown | 2WH2_Ravenshoe 22kV | Loading (MVA) | 0.023921 | 0.024089 | 0.024005 | 0.024122 | 0.02424
FN-Tablelands Cooktown | 2WH2_Ravenshoe 22kV | Loading (MW) | 0.00037646 | 0.0003791 | 0.00037778 | 0.00037962 | 0.00038149
FN-Tablelands Cooktown | 2WH2_Ravenshoe 22kV | Power Factor | 0.015738 | 0.015738 | 0.015738 | 0.015738 | 0.015738
FN-Tablelands Cooktown | 2WH2_Ravenshoe 22kV | Rating (A) | 249 | 249 | 249 | 249 | 249
FN-Tablelands Cooktown | 2WH2_Ravenshoe 22kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Tablelands Cooktown | 2WH2_Ravenshoe 22kV | Min Voltage at Constrained Conductor | 22.9459 | 23.0263 | 22.9862 | 23.042 | 23.0987
FN-Tablelands Cooktown | 2WH2_Ravenshoe 22kV | Contingency Outage | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | Mungana 66 kV | Mungana 66 kV | Mungana 66 kV
FN-Tablelands Cooktown | 3AT1_Atherton No 1 66 kV | % of Rated A | 9.105% | 7.344% | 6.169% | 5.54% | 5.553%
FN-Tablelands Cooktown | 3AT1_Atherton No 1 66 kV | Limiting Line Name | TR_LINE 4407_1 | TR_LINE 4407_1 | TR_LINE 4407_1 | TR_LINE 4407_1 | TR_LINE 4407_1
FN-Tablelands Cooktown | 3AT1_Atherton No 1 66 kV | Loading (A) | 49.8962 | 40.2451 | 33.8034 | 30.3581 | 30.4329
FN-Tablelands Cooktown | 3AT1_Atherton No 1 66 kV | Loading (MVA) | 5.9611 | 4.819 | 4.0473 | 3.6407 | 3.6555
FN-Tablelands Cooktown | 3AT1_Atherton No 1 66 kV | Loading (MW) | 4.8739 | 3.3167 | 1.992 | 0.80923 | 0.31126
FN-Tablelands Cooktown | 3AT1_Atherton No 1 66 kV | Power Factor | 0.81762 | 0.68826 | 0.49218 | 0.22228 | 0.085049
FN-Tablelands Cooktown | 3AT1_Atherton No 1 66 kV | Rating (A) | 548 | 548 | 548 | 548 | 548
FN-Tablelands Cooktown | 3AT1_Atherton No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Tablelands Cooktown | 3AT1_Atherton No 1 66 kV | Min Voltage at Constrained Conductor | 68.976 | 69.1323 | 69.1272 | 69.2379 | 69.3495
FN-Tablelands Cooktown | 3AT1_Atherton No 1 66 kV | Contingency Outage | 3AT2_Atherton No 2 66 kV | 3AT2_Atherton No 2 66 kV | 3AT2_Atherton No 2 66 kV | 3AT2_Atherton No 2 66 kV | 3AT2_Atherton No 2 66 kV
FN-Tablelands Cooktown | 3AT2_Atherton No 2 66 kV | % of Rated A | 9.108% | 7.348% | 6.173% | 5.545% | 5.558%
FN-Tablelands Cooktown | 3AT2_Atherton No 2 66 kV | Limiting Line Name | TR_LINE 4672_1 | TR_LINE 4672_1 | TR_LINE 4672_1 | TR_LINE 4672_1 | TR_LINE 4672_1
FN-Tablelands Cooktown | 3AT2_Atherton No 2 66 kV | Loading (A) | 49.9117 | 40.2647 | 33.8268 | 30.3843 | 30.4596
FN-Tablelands Cooktown | 3AT2_Atherton No 2 66 kV | Loading (MVA) | 5.963 | 4.8213 | 4.0502 | 3.6438 | 3.6587
FN-Tablelands Cooktown | 3AT2_Atherton No 2 66 kV | Loading (MW) | 4.874 | 3.3168 | 1.9921 | 0.8093 | 0.31119
FN-Tablelands Cooktown | 3AT2_Atherton No 2 66 kV | Power Factor | 0.81738 | 0.68793 | 0.49186 | 0.2221 | 0.084957
FN-Tablelands Cooktown | 3AT2_Atherton No 2 66 kV | Rating (A) | 548 | 548 | 548 | 548 | 548
FN-Tablelands Cooktown | 3AT2_Atherton No 2 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Tablelands Cooktown | 3AT2_Atherton No 2 66 kV | Min Voltage at Constrained Conductor | 68.9764 | 69.1327 | 69.1276 | 69.2383 | 69.3499
FN-Tablelands Cooktown | 3AT2_Atherton No 2 66 kV | Contingency Outage | 3AT1_Atherton No 1 66 kV | 3AT1_Atherton No 1 66 kV | 3AT1_Atherton No 1 66 kV | 3AT1_Atherton No 1 66 kV | 3AT1_Atherton No 1 66 kV
FN-Tablelands Cooktown | 3CHI_Chillagoe 66 kV | % of Rated A | 8.383% | 8.092% | 7.766% | 7.363% | 6.858%
FN-Tablelands Cooktown | 3CHI_Chillagoe 66 kV | Limiting Line Name | TR_LINE 104006_1 | TR_LINE 104006_1 | TR_LINE 104006_1 | TR_LINE 104006_1 | TR_LINE 104006_1
FN-Tablelands Cooktown | 3CHI_Chillagoe 66 kV | Loading (A) | 45.9402 | 44.3466 | 42.5571 | 40.3488 | 37.5827
FN-Tablelands Cooktown | 3CHI_Chillagoe 66 kV | Loading (MVA) | 5.3684 | 5.1993 | 4.9957 | 4.7494 | 4.436
FN-Tablelands Cooktown | 3CHI_Chillagoe 66 kV | Loading (MW) | 5.2202 | 5.0394 | 4.8236 | 4.5606 | 4.2252
FN-Tablelands Cooktown | 3CHI_Chillagoe 66 kV | Power Factor | 0.97239 | 0.96925 | 0.96556 | 0.96025 | 0.95248
FN-Tablelands Cooktown | 3CHI_Chillagoe 66 kV | Rating (A) | 548 | 548 | 548 | 548 | 548
FN-Tablelands Cooktown | 3CHI_Chillagoe 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Tablelands Cooktown | 3CHI_Chillagoe 66 kV | Min Voltage at Constrained Conductor | 67.4672 | 67.6903 | 67.7737 | 67.9594 | 68.147
FN-Tablelands Cooktown | 3CHI_Chillagoe 66 kV | Contingency Outage | 7285_4LAK (Lakeland) 132kV | 7285_4LAK (Lakeland) 132kV | 7285_4LAK (Lakeland) 132kV | 7285_4LAK (Lakeland) 132kV | 7285_4LAK (Lakeland) 132kV
FN-Tablelands Cooktown | 3COO_Cooktown 66 kV | % of Rated A | 3.257% | 2.47% | 1.807% | 1.247% | 1.09%
FN-Tablelands Cooktown | 3COO_Cooktown 66 kV | Limiting Line Name | TR_CABLE 12_1 | TR_CABLE 12_1 | TR_CABLE 12_1 | TR_LINE 138000_1 | TR_LINE 138000_1
FN-Tablelands Cooktown | 3COO_Cooktown 66 kV | Loading (A) | 8.0764 | 6.1252 | 4.4816 | 4.9772 | 4.3496
FN-Tablelands Cooktown | 3COO_Cooktown 66 kV | Loading (MVA) | 0.95769 | 0.72964 | 0.53515 | 0.59883 | 0.52474
FN-Tablelands Cooktown | 3COO_Cooktown 66 kV | Loading (MW) | 0.94877 | 0.71729 | 0.5177 | 0.33762 | 0.16524
FN-Tablelands Cooktown | 3COO_Cooktown 66 kV | Power Factor | 0.99069 | 0.98307 | 0.96739 | 0.5638 | 0.3149
FN-Tablelands Cooktown | 3COO_Cooktown 66 kV | Rating (A) | 248 | 248 | 248 | 399 | 399
FN-Tablelands Cooktown | 3COO_Cooktown 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Tablelands Cooktown | 3COO_Cooktown 66 kV | Min Voltage at Constrained Conductor | 68.4613 | 68.7744 | 68.9412 | 69.4632 | 69.6524
FN-Tablelands Cooktown | 3COO_Cooktown 66 kV | Contingency Outage | 7201_Craiglie No 1 132 kV | 7201_Craiglie No 1 132 kV | 7201_Craiglie No 1 132 kV | Mungana 66 kV | Mungana 66 kV
FN-Tablelands Cooktown | 3DIM_Dimbulah 66 kV | % of Rated A | 35.61% | 34.07% | 32.59% | 30.98% | 29.16%
FN-Tablelands Cooktown | 3DIM_Dimbulah 66 kV | Limiting Line Name | TR_LINE 88168_1 | TR_LINE 88168_1 | TR_LINE 88168_1 | TR_LINE 88168_1 | TR_LINE 88168_1
FN-Tablelands Cooktown | 3DIM_Dimbulah 66 kV | Loading (A) | 77.6257 | 74.2774 | 71.0539 | 67.5395 | 63.5671
FN-Tablelands Cooktown | 3DIM_Dimbulah 66 kV | Loading (MVA) | 9.1701 | 8.793 | 8.4123 | 8.0081 | 7.5474
FN-Tablelands Cooktown | 3DIM_Dimbulah 66 kV | Loading (MW) | 9.0191 | 8.6259 | 8.2295 | 7.8057 | 7.321
FN-Tablelands Cooktown | 3DIM_Dimbulah 66 kV | Power Factor | 0.98353 | 0.981 | 0.97828 | 0.97473 | 0.97
FN-Tablelands Cooktown | 3DIM_Dimbulah 66 kV | Rating (A) | 218 | 218 | 218 | 218 | 218
FN-Tablelands Cooktown | 3DIM_Dimbulah 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Tablelands Cooktown | 3DIM_Dimbulah 66 kV | Min Voltage at Constrained Conductor | 68.2003 | 68.3439 | 68.351 | 68.4534 | 68.5474
FN-Tablelands Cooktown | 3DIM_Dimbulah 66 kV | Contingency Outage | 7285_4LAK (Lakeland) 132kV | 7285_4LAK (Lakeland) 132kV | 7285_4LAK (Lakeland) 132kV | 7285_4LAK (Lakeland) 132kV | 7285_4LAK (Lakeland) 132kV
FN-Tablelands Cooktown | 3EVE_Evelyn 66 kV | % of Rated A | 2.687% | 2.822% | 3.171% | 4.175% | 5.23%
FN-Tablelands Cooktown | 3EVE_Evelyn 66 kV | Limiting Line Name | TR_LINE 4423_1 | TR_LINE 4423_1 | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1
FN-Tablelands Cooktown | 3EVE_Evelyn 66 kV | Loading (A) | 6.9852 | 7.338 | 5.3596 | 7.0552 | 8.8379
FN-Tablelands Cooktown | 3EVE_Evelyn 66 kV | Loading (MVA) | 0.84139 | 0.88639 | 0.63748 | 0.84119 | 1.0561
FN-Tablelands Cooktown | 3EVE_Evelyn 66 kV | Loading (MW) | 0.021276 | 0.26517 | 0.51969 | 0.75571 | 0.98958
FN-Tablelands Cooktown | 3EVE_Evelyn 66 kV | Power Factor | 0.025286 | 0.29826 | 0.81522 | 0.89838 | 0.937
FN-Tablelands Cooktown | 3EVE_Evelyn 66 kV | Rating (A) | 260 | 260 | 169 | 169 | 169
FN-Tablelands Cooktown | 3EVE_Evelyn 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Tablelands Cooktown | 3EVE_Evelyn 66 kV | Min Voltage at Constrained Conductor | 69.5436 | 69.7407 | 68.6717 | 68.8377 | 68.9925
FN-Tablelands Cooktown | 3EVE_Evelyn 66 kV | Contingency Outage | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7285_4LAK (Lakeland) 132kV | 7285_4LAK (Lakeland) 132kV | 7285_4LAK (Lakeland) 132kV
FN-Tablelands Cooktown | 3HLA_Helenvale 66 kV | % of Rated A | 3.827% | 3.504% | 3.276% | 3.122% | 3.028%
FN-Tablelands Cooktown | 3HLA_Helenvale 66 kV | Limiting Line Name | TR_LINE 39200_1 | TR_LINE 39200_1 | TR_LINE 39200_1 | TR_LINE 39200_1 | TR_LINE 39200_1
FN-Tablelands Cooktown | 3HLA_Helenvale 66 kV | Loading (A) | 14.4675 | 13.2466 | 12.3835 | 11.8024 | 11.447
FN-Tablelands Cooktown | 3HLA_Helenvale 66 kV | Loading (MVA) | 1.7315 | 1.5898 | 1.4817 | 1.4155 | 1.376
FN-Tablelands Cooktown | 3HLA_Helenvale 66 kV | Loading (MW) | 1.1174 | 0.86323 | 0.64721 | 0.45432 | 0.27154
FN-Tablelands Cooktown | 3HLA_Helenvale 66 kV | Power Factor | 0.64535 | 0.54298 | 0.43679 | 0.32097 | 0.19734
FN-Tablelands Cooktown | 3HLA_Helenvale 66 kV | Rating (A) | 378 | 378 | 378 | 378 | 378
FN-Tablelands Cooktown | 3HLA_Helenvale 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Tablelands Cooktown | 3HLA_Helenvale 66 kV | Min Voltage at Constrained Conductor | 69.0973 | 69.2913 | 69.0823 | 69.2422 | 69.4019
FN-Tablelands Cooktown | 3HLA_Helenvale 66 kV | Contingency Outage | Mungana 66 kV | Mungana 66 kV | Mungana 66 kV | Mungana 66 kV | Mungana 66 kV
FN-Tablelands Cooktown | 3MA2_Mareeba No 2 66 kV | % of Rated A | 37.44% | 37.68% | 38.32% | 39.24% | 40.36%
FN-Tablelands Cooktown | 3MA2_Mareeba No 2 66 kV | Limiting Line Name | TR_LINE 5351_1 | TR_LINE 5351_1 | TR_LINE 5351_1 | TR_LINE 5351_1 | TR_LINE 5351_1
FN-Tablelands Cooktown | 3MA2_Mareeba No 2 66 kV | Loading (A) | 63.2759 | 63.6807 | 64.7582 | 66.3176 | 68.2137
FN-Tablelands Cooktown | 3MA2_Mareeba No 2 66 kV | Loading (MVA) | 7.563 | 7.6269 | 7.7626 | 7.962 | 8.2026
FN-Tablelands Cooktown | 3MA2_Mareeba No 2 66 kV | Loading (MW) | 0.31814 | 0.70644 | 1.5607 | 2.3159 | 3.0173
FN-Tablelands Cooktown | 3MA2_Mareeba No 2 66 kV | Power Factor | 0.041862 | 0.092394 | 0.20081 | 0.29064 | 0.3676
FN-Tablelands Cooktown | 3MA2_Mareeba No 2 66 kV | Rating (A) | 169 | 169 | 169 | 169 | 169
FN-Tablelands Cooktown | 3MA2_Mareeba No 2 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Tablelands Cooktown | 3MA2_Mareeba No 2 66 kV | Min Voltage at Constrained Conductor | 69.0073 | 69.1479 | 69.2071 | 69.3158 | 69.4257
FN-Tablelands Cooktown | 3MA2_Mareeba No 2 66 kV | Contingency Outage | 3MO1_Mossman No 1 66 kV | 3MO1_Mossman No 1 66 kV | 3MO1_Mossman No 1 66 kV | 3MO1_Mossman No 1 66 kV | 3MO1_Mossman No 1 66 kV
FN-Tablelands Cooktown | 3MO1_Mossman No 1 66 kV | % of Rated A | 47.49% | 47.82% | 48.57% | 49.77% | 51.22%
FN-Tablelands Cooktown | 3MO1_Mossman No 1 66 kV | Limiting Line Name | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1
FN-Tablelands Cooktown | 3MO1_Mossman No 1 66 kV | Loading (A) | 62.6853 | 63.1196 | 64.1185 | 65.6959 | 67.6041
FN-Tablelands Cooktown | 3MO1_Mossman No 1 66 kV | Loading (MVA) | 7.541 | 7.6148 | 7.7336 | 7.9387 | 8.1845
FN-Tablelands Cooktown | 3MO1_Mossman No 1 66 kV | Loading (MW) | 0.3004 | 0.72464 | 1.5795 | 2.3358 | 3.0383
FN-Tablelands Cooktown | 3MO1_Mossman No 1 66 kV | Power Factor | 0.039587 | 0.094898 | 0.20397 | 0.29395 | 0.37094
FN-Tablelands Cooktown | 3MO1_Mossman No 1 66 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
FN-Tablelands Cooktown | 3MO1_Mossman No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Tablelands Cooktown | 3MO1_Mossman No 1 66 kV | Min Voltage at Constrained Conductor | 69.4545 | 69.6517 | 69.6363 | 69.7668 | 69.8967
FN-Tablelands Cooktown | 3MO1_Mossman No 1 66 kV | Contingency Outage | 3MA2_Mareeba No 2 66 kV | 3MA2_Mareeba No 2 66 kV | 3MA2_Mareeba No 2 66 kV | 3MA2_Mareeba No 2 66 kV | 3MA2_Mareeba No 2 66 kV
FN-Tablelands Cooktown | 3MO2_Mossman No 2 66 kV | % of Rated A | 5.824% | 7.802% | 3.68% | 3.685% | 3.69%
FN-Tablelands Cooktown | 3MO2_Mossman No 2 66 kV | Limiting Line Name | TR_LINE 2062_3 | TR_LINE 167072_1 | TR_LINE 2062_3 | TR_LINE 2062_3 | TR_LINE 2062_3
FN-Tablelands Cooktown | 3MO2_Mossman No 2 66 kV | Loading (A) | 9.8421 | 10.2989 | 6.2188 | 6.2276 | 6.2364
FN-Tablelands Cooktown | 3MO2_Mossman No 2 66 kV | Loading (MVA) | 1.1792 | 1.2415 | 0.74787 | 0.74999 | 0.75212
FN-Tablelands Cooktown | 3MO2_Mossman No 2 66 kV | Loading (MW) | 0.39092 | 1.0253 | 0.00059101 | 0.00059268 | 0.00059437
FN-Tablelands Cooktown | 3MO2_Mossman No 2 66 kV | Power Factor | 0.33151 | 0.82539 | 0.00078611 | 0.00078611 | 0.00078611
FN-Tablelands Cooktown | 3MO2_Mossman No 2 66 kV | Rating (A) | 169 | 132 | 169 | 169 | 169
FN-Tablelands Cooktown | 3MO2_Mossman No 2 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Tablelands Cooktown | 3MO2_Mossman No 2 66 kV | Min Voltage at Constrained Conductor | 69.1715 | 69.5987 | 69.432 | 69.5303 | 69.6291
FN-Tablelands Cooktown | 3MO2_Mossman No 2 66 kV | Contingency Outage | 2MOS_Mossman 22 kV | 2MOS_Mossman 22 kV | Mungana 66 kV | Mungana 66 kV | Mungana 66 kV
FN-Tablelands Cooktown | 3MTG_Mt Garnet 66 kV | % of Rated A | 5.774% | 5.638% | 5.516% | 5.432% | 5.365%
FN-Tablelands Cooktown | 3MTG_Mt Garnet 66 kV | Limiting Line Name | TR_LINE 169447_1 | TR_LINE 169447_1 | TR_LINE 169447_1 | TR_LINE 169447_1 | TR_LINE 169447_1
FN-Tablelands Cooktown | 3MTG_Mt Garnet 66 kV | Loading (A) | 9.7573 | 9.5284 | 9.3225 | 9.1798 | 9.0666
FN-Tablelands Cooktown | 3MTG_Mt Garnet 66 kV | Loading (MVA) | 1.1782 | 1.154 | 1.1265 | 1.1115 | 1.1
FN-Tablelands Cooktown | 3MTG_Mt Garnet 66 kV | Loading (MW) | 0.57665 | 0.51156 | 0.4554 | 0.40523 | 0.35958
FN-Tablelands Cooktown | 3MTG_Mt Garnet 66 kV | Power Factor | 0.48943 | 0.4433 | 0.40425 | 0.36458 | 0.32689
FN-Tablelands Cooktown | 3MTG_Mt Garnet 66 kV | Rating (A) | 169 | 169 | 169 | 169 | 169
FN-Tablelands Cooktown | 3MTG_Mt Garnet 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Tablelands Cooktown | 3MTG_Mt Garnet 66 kV | Min Voltage at Constrained Conductor | 69.716 | 69.9225 | 69.767 | 69.9062 | 70.0486
FN-Tablelands Cooktown | 3MTG_Mt Garnet 66 kV | Contingency Outage | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | Mungana 66 kV | Mungana 66 kV | Mungana 66 kV
FN-Tablelands Cooktown | 3RA1_Ravenshoe No 1 66 kV | % of Rated A | 1.868% | 1.964% | 2.203% | 2.511% | 2.861%
FN-Tablelands Cooktown | 3RA1_Ravenshoe No 1 66 kV | Limiting Line Name | TR_LINE 178964_1 | TR_LINE 178964_1 | TR_LINE 178964_1 | TR_LINE 178964_1 | TR_LINE 178964_1
FN-Tablelands Cooktown | 3RA1_Ravenshoe No 1 66 kV | Loading (A) | 3.1575 | 3.3188 | 3.7236 | 4.2442 | 4.8351
FN-Tablelands Cooktown | 3RA1_Ravenshoe No 1 66 kV | Loading (MVA) | 0.38092 | 0.40173 | 0.44988 | 0.51397 | 0.57779
FN-Tablelands Cooktown | 3RA1_Ravenshoe No 1 66 kV | Loading (MW) | 0.017395 | 0.12113 | 0.2387 | 0.3431 | 0.44207
FN-Tablelands Cooktown | 3RA1_Ravenshoe No 1 66 kV | Power Factor | 0.045665 | 0.30153 | 0.53058 | 0.66754 | 0.7651
FN-Tablelands Cooktown | 3RA1_Ravenshoe No 1 66 kV | Rating (A) | 169 | 169 | 169 | 169 | 169
FN-Tablelands Cooktown | 3RA1_Ravenshoe No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Tablelands Cooktown | 3RA1_Ravenshoe No 1 66 kV | Min Voltage at Constrained Conductor | 69.6524 | 69.8854 | 69.7547 | 69.916 | 68.9928
FN-Tablelands Cooktown | 3RA1_Ravenshoe No 1 66 kV | Contingency Outage | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | Mungana 66 kV | Mungana 66 kV | 7285_4LAK (Lakeland) 132kV
FN-Tablelands Cooktown | 7200_Craiglie No 2 132 kV | % of Rated A | 14.78% | 14.22% | 13.89% | 13.68% | 13.65%
FN-Tablelands Cooktown | 7200_Craiglie No 2 132 kV | Limiting Line Name | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1
FN-Tablelands Cooktown | 7200_Craiglie No 2 132 kV | Loading (A) | 66.8107 | 64.2744 | 62.7754 | 61.825 | 61.6808
FN-Tablelands Cooktown | 7200_Craiglie No 2 132 kV | Loading (MVA) | 16.5383 | 15.9456 | 15.5785 | 15.363 | 15.3473
FN-Tablelands Cooktown | 7200_Craiglie No 2 132 kV | Loading (MW) | 7.5317 | 5.5495 | 3.6444 | 1.739 | 0.31822
FN-Tablelands Cooktown | 7200_Craiglie No 2 132 kV | Power Factor | 0.45541 | 0.34803 | 0.23394 | 0.1132 | 0.020265
FN-Tablelands Cooktown | 7200_Craiglie No 2 132 kV | Rating (A) | 452 | 452 | 452 | 452 | 452
FN-Tablelands Cooktown | 7200_Craiglie No 2 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Tablelands Cooktown | 7200_Craiglie No 2 132 kV | Min Voltage at Constrained Conductor | 142.9167 | 143.2323 | 143.2763 | 143.4665 | 143.6557
FN-Tablelands Cooktown | 7200_Craiglie No 2 132 kV | Contingency Outage | 7201_Craiglie No 1 132 kV | 7201_Craiglie No 1 132 kV | 7201_Craiglie No 1 132 kV | 7201_Craiglie No 1 132 kV | 7201_Craiglie No 1 132 kV
FN-Tablelands Cooktown | 7201_Craiglie No 1 132 kV | % of Rated A | 6.973% | 5.906% | 2.928% | 4.072% | 6.476%
FN-Tablelands Cooktown | 7201_Craiglie No 1 132 kV | Limiting Line Name | TR_LINE 3957_2 | TR_LINE 3957_2 | TR_LINE 38737_a | TR_LINE 38738_a | TR_LINE 38738_a
FN-Tablelands Cooktown | 7201_Craiglie No 1 132 kV | Loading (A) | 31.5158 | 26.696 | 11.5663 | 15.4319 | 24.5437
FN-Tablelands Cooktown | 7201_Craiglie No 1 132 kV | Loading (MVA) | 7.7068 | 6.5416 | 2.909 | 3.8983 | 6.2083
FN-Tablelands Cooktown | 7201_Craiglie No 1 132 kV | Loading (MW) | 6.19 | 4.5153 | 2.858 | 3.5962 | 6.0498
FN-Tablelands Cooktown | 7201_Craiglie No 1 132 kV | Power Factor | 0.80319 | 0.69025 | 0.98248 | 0.92243 | 0.97436
FN-Tablelands Cooktown | 7201_Craiglie No 1 132 kV | Rating (A) | 452 | 452 | 395 | 379 | 379
FN-Tablelands Cooktown | 7201_Craiglie No 1 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Tablelands Cooktown | 7201_Craiglie No 1 132 kV | Min Voltage at Constrained Conductor | 141.1843 | 141.4745 | 145.1994 | 145.8478 | 146.0402
FN-Tablelands Cooktown | 7201_Craiglie No 1 132 kV | Contingency Outage | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 2MOS_Mossman 22 kV | 7200_Craiglie No 2 132 kV
FN-Tablelands Cooktown | 7285_4LAK (Lakeland) 132kV | % of Rated A | 7.994% | 7.997% | 7.962% | 7.973% | 7.988%
FN-Tablelands Cooktown | 7285_4LAK (Lakeland) 132kV | Limiting Line Name | TR_LINE 37686_1 | TR_LINE 37686_1 | TR_LINE 37686_1 | TR_LINE 37686_1 | TR_LINE 37686_1
FN-Tablelands Cooktown | 7285_4LAK (Lakeland) 132kV | Loading (A) | 40.6107 | 40.6227 | 40.4495 | 40.5017 | 40.577
FN-Tablelands Cooktown | 7285_4LAK (Lakeland) 132kV | Loading (MVA) | 10.2628 | 10.2916 | 10.2142 | 10.2489 | 10.2895
FN-Tablelands Cooktown | 7285_4LAK (Lakeland) 132kV | Loading (MW) | 1.2523 | 0.94598 | 0.68552 | 0.45261 | 0.23225
FN-Tablelands Cooktown | 7285_4LAK (Lakeland) 132kV | Power Factor | 0.12202 | 0.091918 | 0.067114 | 0.044162 | 0.022571
FN-Tablelands Cooktown | 7285_4LAK (Lakeland) 132kV | Rating (A) | 508 | 508 | 508 | 508 | 508
FN-Tablelands Cooktown | 7285_4LAK (Lakeland) 132kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Tablelands Cooktown | 7285_4LAK (Lakeland) 132kV | Min Voltage at Constrained Conductor | 145.9033 | 146.2691 | 145.791 | 146.0975 | 146.4047
FN-Tablelands Cooktown | 7285_4LAK (Lakeland) 132kV | Contingency Outage | Mungana 66 kV | Mungana 66 kV | Mungana 66 kV | Mungana 66 kV | Mungana 66 kV
FN-Tablelands Cooktown | Mungana 66 kV | % of Rated A | 9.864% | 9.824% | 9.805% | 9.769% | 9.731%
FN-Tablelands Cooktown | Mungana 66 kV | Limiting Line Name | TR_LINE 104012_1 | TR_LINE 104012_1 | TR_LINE 104012_1 | TR_LINE 104012_1 | TR_LINE 104012_1
FN-Tablelands Cooktown | Mungana 66 kV | Loading (A) | 45.0787 | 44.8975 | 44.8087 | 44.6448 | 44.4725
FN-Tablelands Cooktown | Mungana 66 kV | Loading (MVA) | 5.2158 | 5.2157 | 5.2157 | 5.2157 | 5.2157
FN-Tablelands Cooktown | Mungana 66 kV | Loading (MW) | 5.2131 | 5.213 | 5.2129 | 5.2128 | 5.2127
FN-Tablelands Cooktown | Mungana 66 kV | Power Factor | 0.99948 | 0.99947 | 0.99946 | 0.99945 | 0.99944
FN-Tablelands Cooktown | Mungana 66 kV | Rating (A) | 457 | 457 | 457 | 457 | 457
FN-Tablelands Cooktown | Mungana 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Tablelands Cooktown | Mungana 66 kV | Min Voltage at Constrained Conductor | 66.789 | 67.0582 | 67.1909 | 67.4372 | 67.6981
FN-Tablelands Cooktown | Mungana 66 kV | Contingency Outage | 7285_4LAK (Lakeland) 132kV | 7285_4LAK (Lakeland) 132kV | 7285_4LAK (Lakeland) 132kV | 7285_4LAK (Lakeland) 132kV | 7285_4LAK (Lakeland) 132kV
FN-Tablelands Cooktown | TURK_YALK (Ex 7201) | % of Rated A |  |  | 12.98% | 13.2% | 13.97%
FN-Tablelands Cooktown | TURK_YALK (Ex 7201) | Limiting Line Name |  |  | TR_LINE 3957_2 | TR_LINE 3957_2 | TR_LINE 3957_2
FN-Tablelands Cooktown | TURK_YALK (Ex 7201) | Loading (A) |  |  | 58.6615 | 59.6741 | 63.154
FN-Tablelands Cooktown | TURK_YALK (Ex 7201) | Loading (MVA) |  |  | 14.558 | 14.8323 | 15.7208
FN-Tablelands Cooktown | TURK_YALK (Ex 7201) | Loading (MW) |  |  | 0.61585 | 2.451 | 5.7159
FN-Tablelands Cooktown | TURK_YALK (Ex 7201) | Power Factor |  |  | 0.042303 | 0.16524 | 0.36357
FN-Tablelands Cooktown | TURK_YALK (Ex 7201) | Rating (A) |  |  | 452 | 452 | 452
FN-Tablelands Cooktown | TURK_YALK (Ex 7201) | Time |  |  | 12:00:00 | 12:00:00 | 12:00:00
FN-Tablelands Cooktown | TURK_YALK (Ex 7201) | Min Voltage at Constrained Conductor |  |  | 143.2806 | 143.5036 | 143.7188
FN-Tablelands Cooktown | TURK_YALK (Ex 7201) | Contingency Outage |  |  | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV
Interstitial Grid | 7194_Gladstone PS - Boat Creek 132 kV | % of Rated A | 2.226% | 2.127% | 2.005% | 1.889% | 1.835%
Interstitial Grid | 7194_Gladstone PS - Boat Creek 132 kV | Limiting Line Name | Subtrans_GLNO_CALI_LINE_1 | Subtrans_GLNO_CALI_LINE_1 | Subtrans_GLNO_CALI_LINE_1 | Subtrans_GLNO_CALI_LINE_1 | Subtrans_GLNO_CALI_LINE_1
Interstitial Grid | 7194_Gladstone PS - Boat Creek 132 kV | Loading (A) | 111.2872 | 106.3464 | 100.2654 | 94.4403 | 91.7413
Interstitial Grid | 7194_Gladstone PS - Boat Creek 132 kV | Loading (MVA) | 26.9786 | 25.8215 | 24.3442 | 22.8618 | 22.1781
Interstitial Grid | 7194_Gladstone PS - Boat Creek 132 kV | Loading (MW) | 26.6313 | 25.4487 | 23.9568 | 22.4677 | 22.1656
Interstitial Grid | 7194_Gladstone PS - Boat Creek 132 kV | Power Factor | 0.98713 | 0.98556 | 0.98409 | 0.98276 | 0.99944
Interstitial Grid | 7194_Gladstone PS - Boat Creek 132 kV | Rating (A) | 5000 | 5000 | 5000 | 5000 | 5000
Interstitial Grid | 7194_Gladstone PS - Boat Creek 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
Interstitial Grid | 7194_Gladstone PS - Boat Creek 132 kV | Min Voltage at Constrained Conductor | 139.9631 | 140.1838 | 140.1794 | 139.7632 | 139.5719
Interstitial Grid | 7194_Gladstone PS - Boat Creek 132 kV | Contingency Outage | 7195_Gladstone PS - Boat Creek 132 kV | 7195_Gladstone PS - Boat Creek 132 kV | 7195_Gladstone PS - Boat Creek 132 kV | 7195_Gladstone PS - Boat Creek 132 kV | 7195_Gladstone PS - Boat Creek 132 kV
Interstitial Grid | 7195_Gladstone PS - Boat Creek 132 kV | % of Rated A | 2.229% | 2.13% | 2.008% | 1.892% | 1.837%
Interstitial Grid | 7195_Gladstone PS - Boat Creek 132 kV | Limiting Line Name | Subtrans_GLNO_CALI_LINE_2 | Subtrans_GLNO_CALI_LINE_2 | Subtrans_GLNO_CALI_LINE_2 | Subtrans_GLNO_CALI_LINE_2 | Subtrans_GLNO_CALI_LINE_2
Interstitial Grid | 7195_Gladstone PS - Boat Creek 132 kV | Loading (A) | 111.448 | 106.5001 | 100.4104 | 94.5769 | 91.8735
Interstitial Grid | 7195_Gladstone PS - Boat Creek 132 kV | Loading (MVA) | 27.0173 | 25.8586 | 24.3792 | 22.8947 | 22.2102
Interstitial Grid | 7195_Gladstone PS - Boat Creek 132 kV | Loading (MW) | 26.6684 | 25.4842 | 23.9901 | 22.4989 | 22.1979
Interstitial Grid | 7195_Gladstone PS - Boat Creek 132 kV | Power Factor | 0.98709 | 0.98552 | 0.98404 | 0.98271 | 0.99945
Interstitial Grid | 7195_Gladstone PS - Boat Creek 132 kV | Rating (A) | 5000 | 5000 | 5000 | 5000 | 5000
Interstitial Grid | 7195_Gladstone PS - Boat Creek 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
Interstitial Grid | 7195_Gladstone PS - Boat Creek 132 kV | Min Voltage at Constrained Conductor | 139.9619 | 140.1825 | 140.1781 | 139.7618 | 139.5729
Interstitial Grid | 7195_Gladstone PS - Boat Creek 132 kV | Contingency Outage | 7194_Gladstone PS - Boat Creek 132 kV | 7194_Gladstone PS - Boat Creek 132 kV | 7194_Gladstone PS - Boat Creek 132 kV | 7194_Gladstone PS - Boat Creek 132 kV | 7194_Gladstone PS - Boat Creek 132 kV
MK-Mackay Area | 14109_Marian Mill 11 kV | % of Rated A | 0.2693% | 0.2696% | 0.2698% | 0.27% | 0.2701%
MK-Mackay Area | 14109_Marian Mill 11 kV | Limiting Line Name | HV_CABLE 461202_1 | HV_CABLE 461202_1 | HV_CABLE 461202_1 | HV_CABLE 461202_1 | HV_CABLE 461202_1
MK-Mackay Area | 14109_Marian Mill 11 kV | Loading (A) | 0.8482 | 0.84918 | 0.84992 | 0.85052 | 0.85093
MK-Mackay Area | 14109_Marian Mill 11 kV | Loading (MVA) | 0.0163 | 0.016337 | 0.016366 | 0.016389 | 0.016405
MK-Mackay Area | 14109_Marian Mill 11 kV | Loading (MW) | 0.00032221 | 0.00032295 | 0.00032351 | 0.00032397 | 0.00032429
MK-Mackay Area | 14109_Marian Mill 11 kV | Power Factor | 0.019651 | 0.019651 | 0.019651 | 0.019651 | 0.019651
MK-Mackay Area | 14109_Marian Mill 11 kV | Rating (A) | 315 | 315 | 315 | 315 | 315
MK-Mackay Area | 14109_Marian Mill 11 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK-Mackay Area | 14109_Marian Mill 11 kV | Min Voltage at Constrained Conductor | 11.0949 | 11.1077 | 11.1173 | 11.1252 | 11.1306
MK-Mackay Area | 14109_Marian Mill 11 kV | Contingency Outage | PV 6/5_Glenella No 1 66 kV | PV 6/5_Glenella No 1 66 kV | 6333_Hail Creek 66 kV | 6333_Hail Creek 66 kV | 6333_Hail Creek 66 kV
MK-Mackay Area | 231_Carmila 33 kV | % of Rated A | 5.73% | 5.71% | 5.693% | 5.678% | 5.665%
MK-Mackay Area | 231_Carmila 33 kV | Limiting Line Name | TR_LINE 211924_1 | TR_LINE 211924_1 | TR_LINE 211924_1 | TR_LINE 211924_1 | TR_LINE 211924_1
MK-Mackay Area | 231_Carmila 33 kV | Loading (A) | 11.0582 | 11.02 | 10.9877 | 10.9595 | 10.9329
MK-Mackay Area | 231_Carmila 33 kV | Loading (MVA) | 0.65769 | 0.65779 | 0.65787 | 0.65795 | 0.65802
MK-Mackay Area | 231_Carmila 33 kV | Loading (MW) | 0.54399 | 0.54402 | 0.54404 | 0.54407 | 0.54409
MK-Mackay Area | 231_Carmila 33 kV | Power Factor | 0.82708 | 0.82701 | 0.82694 | 0.82688 | 0.82683
MK-Mackay Area | 231_Carmila 33 kV | Rating (A) | 193 | 193 | 193 | 193 | 193
MK-Mackay Area | 231_Carmila 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK-Mackay Area | 231_Carmila 33 kV | Min Voltage at Constrained Conductor | 34.3379 | 34.4623 | 34.5679 | 34.661 | 34.7491
MK-Mackay Area | 231_Carmila 33 kV | Contingency Outage | 3045_Sarina No 1 33 kV | 3045_Sarina No 1 33 kV | 3045_Sarina No 1 33 kV | 3045_Sarina No 1 33 kV | 3045_Sarina No 1 33 kV
MK-Mackay Area | 247_Mill 11 kV | % of Rated A | 1.854% | 1.86% | 1.857% | 1.853% | 1.85%
MK-Mackay Area | 247_Mill 11 kV | Limiting Line Name | HV_LINE 141313_1 | HV_LINE 141313_1 | HV_LINE 141313_1 | HV_LINE 141313_1 | HV_LINE 141313_1
MK-Mackay Area | 247_Mill 11 kV | Loading (A) | 6.2676 | 6.2876 | 6.2751 | 6.2641 | 6.2538
MK-Mackay Area | 247_Mill 11 kV | Loading (MVA) | 0.12153 | 0.12153 | 0.12153 | 0.12153 | 0.12153
MK-Mackay Area | 247_Mill 11 kV | Loading (MW) | 0.10141 | 0.10141 | 0.10141 | 0.10141 | 0.10141
MK-Mackay Area | 247_Mill 11 kV | Power Factor | 0.83441 | 0.83444 | 0.83442 | 0.83441 | 0.8344
MK-Mackay Area | 247_Mill 11 kV | Rating (A) | 338 | 338 | 338 | 338 | 338
MK-Mackay Area | 247_Mill 11 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK-Mackay Area | 247_Mill 11 kV | Min Voltage at Constrained Conductor | 11.1952 | 11.1594 | 11.1818 | 11.2015 | 11.22
MK-Mackay Area | 247_Mill 11 kV | Contingency Outage | 231_Carmila 33 kV | 3045_Sarina No 1 33 kV | 3045_Sarina No 1 33 kV | 3045_Sarina No 1 33 kV | 3045_Sarina No 1 33 kV
MK-Mackay Area | 3045_Sarina No 1 33 kV | % of Rated A | 26.13% | 26.53% | 26.96% | 27.38% | 27.84%
MK-Mackay Area | 3045_Sarina No 1 33 kV | Limiting Line Name | TR_LINE 12173_1 | TR_LINE 12173_1 | TR_LINE 12173_1 | TR_LINE 12173_1 | TR_LINE 12173_1
MK-Mackay Area | 3045_Sarina No 1 33 kV | Loading (A) | 78.1399 | 79.3362 | 80.6001 | 81.8811 | 83.2479
MK-Mackay Area | 3045_Sarina No 1 33 kV | Loading (MVA) | 4.8498 | 4.9322 | 5.0179 | 5.1039 | 5.1951
MK-Mackay Area | 3045_Sarina No 1 33 kV | Loading (MW) | 0.83179 | 1.1485 | 1.4253 | 1.6707 | 1.9067
MK-Mackay Area | 3045_Sarina No 1 33 kV | Power Factor | 0.17134 | 0.23269 | 0.2839 | 0.32719 | 0.36687
MK-Mackay Area | 3045_Sarina No 1 33 kV | Rating (A) | 299 | 299 | 299 | 299 | 299
MK-Mackay Area | 3045_Sarina No 1 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK-Mackay Area | 3045_Sarina No 1 33 kV | Min Voltage at Constrained Conductor | 35.8295 | 35.8888 | 35.9393 | 35.9831 | 36.0242
MK-Mackay Area | 3045_Sarina No 1 33 kV | Contingency Outage | 3047_Sarina No 2 33 kV | 3047_Sarina No 2 33 kV | 3047_Sarina No 2 33 kV | 3047_Sarina No 2 33 kV | 3047_Sarina No 2 33 kV
MK-Mackay Area | 3046_Rosella 33 kV | % of Rated A | 0.3101% | 1.346% | 2.715% | 4.176% | 5.789%
MK-Mackay Area | 3046_Rosella 33 kV | Limiting Line Name | TR_CABLE 6962_1 | TR_CABLE 6962_1 | TR_CABLE 6962_1 | TR_CABLE 6962_1 | TR_CABLE 7121_1
MK-Mackay Area | 3046_Rosella 33 kV | Loading (A) | 1.2683 | 5.5069 | 11.1054 | 17.0818 | 23.6754
MK-Mackay Area | 3046_Rosella 33 kV | Loading (MVA) | 0.076356 | 0.33051 | 0.66653 | 1.0252 | 1.4264
MK-Mackay Area | 3046_Rosella 33 kV | Loading (MW) | 0.0029357 | 0.32239 | 0.6633 | 1.0239 | 1.4262
MK-Mackay Area | 3046_Rosella 33 kV | Power Factor | 0.038447 | 0.97452 | 0.9947 | 0.9984 | 0.99983
MK-Mackay Area | 3046_Rosella 33 kV | Rating (A) | 409 | 409 | 409 | 409 | 409
MK-Mackay Area | 3046_Rosella 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK-Mackay Area | 3046_Rosella 33 kV | Min Voltage at Constrained Conductor | 34.7575 | 34.6518 | 34.6519 | 34.6518 | 34.7845
MK-Mackay Area | 3046_Rosella 33 kV | Contingency Outage | 247_Mill 11 kV | 3045_Sarina No 1 33 kV | 3045_Sarina No 1 33 kV | 3045_Sarina No 1 33 kV | 3045_Sarina No 1 33 kV
MK-Mackay Area | 3047_Sarina No 2 33 kV | % of Rated A | 2.777% | 4.831% | 7.736% | 10.34% | 12.84%
MK-Mackay Area | 3047_Sarina No 2 33 kV | Limiting Line Name | TR_LINE 11717_1 | TR_LINE 11717_1 | TR_LINE 11717_1 | TR_LINE 11717_1 | TR_LINE 11717_1
MK-Mackay Area | 3047_Sarina No 2 33 kV | Loading (A) | 10.5538 | 18.3569 | 29.3961 | 39.3055 | 48.788
MK-Mackay Area | 3047_Sarina No 2 33 kV | Loading (MVA) | 0.63704 | 1.1045 | 1.7715 | 2.3721 | 2.9483
MK-Mackay Area | 3047_Sarina No 2 33 kV | Loading (MW) | 0.53833 | 1.0997 | 1.7681 | 2.369 | 2.9452
MK-Mackay Area | 3047_Sarina No 2 33 kV | Power Factor | 0.845 | 0.99571 | 0.99805 | 0.99869 | 0.99895
MK-Mackay Area | 3047_Sarina No 2 33 kV | Rating (A) | 380 | 380 | 380 | 380 | 380
MK-Mackay Area | 3047_Sarina No 2 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK-Mackay Area | 3047_Sarina No 2 33 kV | Min Voltage at Constrained Conductor | 34.8497 | 34.7343 | 34.7892 | 34.8375 | 34.8829
MK-Mackay Area | 3047_Sarina No 2 33 kV | Contingency Outage | 231_Carmila 33 kV | 3045_Sarina No 1 33 kV | 3045_Sarina No 1 33 kV | 3045_Sarina No 1 33 kV | 3045_Sarina No 1 33 kV
MK-Mackay Area | 3053_Mt Bassett 33 kV | % of Rated A | 3.721% | 2.339% | 8.011% | 13.72% | 19.89%
MK-Mackay Area | 3053_Mt Bassett 33 kV | Limiting Line Name | TR_LINE 11627_1 | TR_LINE 11627_1 | TR_LINE 11627_1 | TR_LINE 11627_1 | TR_LINE 11627_1
MK-Mackay Area | 3053_Mt Bassett 33 kV | Loading (A) | 8.7438 | 5.4959 | 18.8264 | 32.2341 | 46.7413
MK-Mackay Area | 3053_Mt Bassett 33 kV | Loading (MVA) | 0.51908 | 0.32691 | 1.1225 | 1.9257 | 2.7976
MK-Mackay Area | 3053_Mt Bassett 33 kV | Loading (MW) | 0.51897 | 0.32677 | 1.1225 | 1.9256 | 2.7975
MK-Mackay Area | 3053_Mt Bassett 33 kV | Power Factor | 0.99979 | 0.99935 | 0.99999 | 0.99998 | 0.99994
MK-Mackay Area | 3053_Mt Bassett 33 kV | Rating (A) | 235 | 235 | 235 | 235 | 235
MK-Mackay Area | 3053_Mt Bassett 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK-Mackay Area | 3053_Mt Bassett 33 kV | Min Voltage at Constrained Conductor | 34.2638 | 34.3427 | 34.3997 | 34.4505 | 34.4983
MK-Mackay Area | 3053_Mt Bassett 33 kV | Contingency Outage | 347_Mt Bassett 33 kV | 347_Mt Bassett 33 kV | 347_Mt Bassett 33 kV | 347_Mt Bassett 33 kV | 347_Mt Bassett 33 kV
MK-Mackay Area | 340_MK3-1 Farleigh 33 kV | % of Rated A | 2.298% | 2.305% | 2.31% | 2.309% | 2.316%
MK-Mackay Area | 340_MK3-1 Farleigh 33 kV | Limiting Line Name | TR_LINE 11332_1 | TR_LINE 11332_1 | TR_LINE 11332_1 | TR_LINE 11332_1 | TR_LINE 11332_1
MK-Mackay Area | 340_MK3-1 Farleigh 33 kV | Loading (A) | 3.9531 | 3.9646 | 3.974 | 3.9707 | 3.9828
MK-Mackay Area | 340_MK3-1 Farleigh 33 kV | Loading (MVA) | 0.23983 | 0.24123 | 0.24237 | 0.24198 | 0.24345
MK-Mackay Area | 340_MK3-1 Farleigh 33 kV | Loading (MW) | 0.0044065 | 0.0044322 | 0.0044532 | 0.004446 | 0.004473
MK-Mackay Area | 340_MK3-1 Farleigh 33 kV | Power Factor | 0.018374 | 0.018374 | 0.018374 | 0.018374 | 0.018374
MK-Mackay Area | 340_MK3-1 Farleigh 33 kV | Rating (A) | 172 | 172 | 172 | 172 | 172
MK-Mackay Area | 340_MK3-1 Farleigh 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK-Mackay Area | 340_MK3-1 Farleigh 33 kV | Min Voltage at Constrained Conductor | 35.0272 | 35.1291 | 35.2124 | 35.1837 | 35.2903
MK-Mackay Area | 340_MK3-1 Farleigh 33 kV | Contingency Outage | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 343_Pleystowe 33 kV | 343_Pleystowe 33 kV
MK-Mackay Area | 341_Tennyson St No 2 33 kV | % of Rated A | 22.84% | 20.98% | 19.52% | 18.34% | 17.41%
MK-Mackay Area | 341_Tennyson St No 2 33 kV | Limiting Line Name | TR_CABLE 253_1 | TR_CABLE 253_1 | TR_CABLE 253_1 | TR_CABLE 253_1 | TR_CABLE 253_1
MK-Mackay Area | 341_Tennyson St No 2 33 kV | Loading (A) | 79.953 | 73.4311 | 68.3374 | 64.2017 | 60.9384
MK-Mackay Area | 341_Tennyson St No 2 33 kV | Loading (MVA) | 4.7466 | 4.3645 | 4.0656 | 3.8224 | 3.6304
MK-Mackay Area | 341_Tennyson St No 2 33 kV | Loading (MW) | 3.0855 | 2.4809 | 1.9416 | 1.4196 | 0.88646
MK-Mackay Area | 341_Tennyson St No 2 33 kV | Power Factor | 0.65004 | 0.56841 | 0.47758 | 0.37139 | 0.24418
MK-Mackay Area | 341_Tennyson St No 2 33 kV | Rating (A) | 350 | 350 | 350 | 350 | 350
MK-Mackay Area | 341_Tennyson St No 2 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK-Mackay Area | 341_Tennyson St No 2 33 kV | Min Voltage at Constrained Conductor | 34.2756 | 34.3161 | 34.348 | 34.374 | 34.3955
MK-Mackay Area | 341_Tennyson St No 2 33 kV | Contingency Outage | 387_Mackay-Alfred Street 1 33 kV | 387_Mackay-Alfred Street 1 33 kV | 387_Mackay-Alfred Street 1 33 kV | 387_Mackay-Alfred Street 1 33 kV | 387_Mackay-Alfred Street 1 33 kV
MK-Mackay Area | 342_South Mackay 33 kV | % of Rated A | 55.09% | 54.99% | 55.91% | 57.72% | 60.43%
MK-Mackay Area | 342_South Mackay 33 kV | Limiting Line Name | TR_LINE 12122806_1 | TR_LINE 12122806_1 | TR_LINE 12122806_1 | TR_LINE 12122806_1 | TR_LINE 12122806_1
MK-Mackay Area | 342_South Mackay 33 kV | Loading (A) | 186.1982 | 185.8546 | 188.9686 | 195.0992 | 204.2551
MK-Mackay Area | 342_South Mackay 33 kV | Loading (MVA) | 11.07 | 11.0616 | 11.2563 | 11.6291 | 12.1816
MK-Mackay Area | 342_South Mackay 33 kV | Loading (MW) | 1.2481 | 0.40666 | 1.9773 | 3.5152 | 5.0915
MK-Mackay Area | 342_South Mackay 33 kV | Power Factor | 0.11263 | 0.036659 | 0.1756 | 0.30224 | 0.41797
MK-Mackay Area | 342_South Mackay 33 kV | Rating (A) | 338 | 338 | 338 | 338 | 338
MK-Mackay Area | 342_South Mackay 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK-Mackay Area | 342_South Mackay 33 kV | Min Voltage at Constrained Conductor | 34.3165 | 34.3534 | 34.3815 | 34.4034 | 34.4219
MK-Mackay Area | 342_South Mackay 33 kV | Contingency Outage | PV 6/5_Glenella No 1 66 kV | PV 6/5_Glenella No 1 66 kV | PV 6/5_Glenella No 1 66 kV | PV 6/5_Glenella No 1 66 kV | 6333_Hail Creek 66 kV
MK-Mackay Area | 343_Pleystowe 33 kV | % of Rated A | 13.54% | 18% | 21.77% | 25.1% | 28.25%
MK-Mackay Area | 343_Pleystowe 33 kV | Limiting Line Name | TR_LINE 114413_2 | TR_LINE 114413_2 | TR_LINE 114413_2 | TR_LINE 114413_2 | TR_LINE 114413_2
MK-Mackay Area | 343_Pleystowe 33 kV | Loading (A) | 29.7792 | 39.5891 | 47.895 | 55.2195 | 62.149
MK-Mackay Area | 343_Pleystowe 33 kV | Loading (MVA) | 1.7686 | 2.354 | 2.8506 | 3.289 | 3.7041
MK-Mackay Area | 343_Pleystowe 33 kV | Loading (MW) | 1.7278 | 2.3265 | 2.8306 | 3.274 | 3.6928
MK-Mackay Area | 343_Pleystowe 33 kV | Power Factor | 0.97691 | 0.98832 | 0.99298 | 0.99544 | 0.99696
MK-Mackay Area | 343_Pleystowe 33 kV | Rating (A) | 220 | 220 | 220 | 220 | 220
MK-Mackay Area | 343_Pleystowe 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK-Mackay Area | 343_Pleystowe 33 kV | Min Voltage at Constrained Conductor | 34.2882 | 34.3285 | 34.3601 | 34.3859 | 34.4072
MK-Mackay Area | 343_Pleystowe 33 kV | Contingency Outage | 346_Ritchies Rd 33 kV | 346_Ritchies Rd 33 kV | 346_Ritchies Rd 33 kV | 346_Ritchies Rd 33 kV | 346_Ritchies Rd 33 kV
MK-Mackay Area | 344_West Mackay 2 33 kV | % of Rated A | 4.319% | 3.536% | 2.888% | 2.318% | 1.797%
MK-Mackay Area | 344_West Mackay 2 33 kV | Limiting Line Name | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1
MK-Mackay Area | 344_West Mackay 2 33 kV | Loading (A) | 26.9927 | 22.1015 | 18.048 | 14.486 | 11.2313
MK-Mackay Area | 344_West Mackay 2 33 kV | Loading (MVA) | 1.5999 | 1.3114 | 1.0719 | 0.86096 | 0.66799
MK-Mackay Area | 344_West Mackay 2 33 kV | Loading (MW) | 1.5997 | 1.3111 | 1.0713 | 0.86012 | 0.66679
MK-Mackay Area | 344_West Mackay 2 33 kV | Power Factor | 0.99987 | 0.99971 | 0.99945 | 0.99902 | 0.9982
MK-Mackay Area | 344_West Mackay 2 33 kV | Rating (A) | 625 | 625 | 625 | 625 | 625
MK-Mackay Area | 344_West Mackay 2 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK-Mackay Area | 344_West Mackay 2 33 kV | Min Voltage at Constrained Conductor | 34.2201 | 34.2574 | 34.2883 | 34.3138 | 34.338
MK-Mackay Area | 344_West Mackay 2 33 kV | Contingency Outage | 422_North Mackay No 1 33 kV | 422_North Mackay No 1 33 kV | 422_North Mackay No 1 33 kV | 422_North Mackay No 1 33 kV | 422_North Mackay No 1 33 kV
MK-Mackay Area | 346_Ritchies Rd 33 kV | % of Rated A | 13.55% | 17.97% | 21.71% | 25.01% | 28.13%
MK-Mackay Area | 346_Ritchies Rd 33 kV | Limiting Line Name | TR_LINE 11501_1 | TR_LINE 11501_1 | TR_LINE 11501_1 | TR_LINE 11501_1 | TR_LINE 11501_1
MK-Mackay Area | 346_Ritchies Rd 33 kV | Loading (A) | 29.7998 | 39.5311 | 47.769 | 55.0301 | 61.8933
MK-Mackay Area | 346_Ritchies Rd 33 kV | Loading (MVA) | 1.7698 | 2.3506 | 2.8431 | 3.2778 | 3.6889
MK-Mackay Area | 346_Ritchies Rd 33 kV | Loading (MW) | 1.7247 | 2.3205 | 2.8215 | 3.2618 | 3.6772
MK-Mackay Area | 346_Ritchies Rd 33 kV | Power Factor | 0.97445 | 0.98718 | 0.99239 | 0.99512 | 0.99682
MK-Mackay Area | 346_Ritchies Rd 33 kV | Rating (A) | 220 | 220 | 220 | 220 | 220
MK-Mackay Area | 346_Ritchies Rd 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK-Mackay Area | 346_Ritchies Rd 33 kV | Min Voltage at Constrained Conductor | 34.2889 | 34.329 | 34.3605 | 34.3862 | 34.4073
MK-Mackay Area | 346_Ritchies Rd 33 kV | Contingency Outage | 343_Pleystowe 33 kV | 343_Pleystowe 33 kV | 343_Pleystowe 33 kV | 343_Pleystowe 33 kV | 343_Pleystowe 33 kV
MK-Mackay Area | 347_Mt Bassett 33 kV | % of Rated A | 3.624% | 2.951% | 7.447% | 12.68% | 18.36%
MK-Mackay Area | 347_Mt Bassett 33 kV | Limiting Line Name | TR_CABLE 22_1 | TR_CABLE 4883_1 | TR_CABLE 22_1 | TR_CABLE 22_1 | TR_CABLE 4883_1
MK-Mackay Area | 347_Mt Bassett 33 kV | Loading (A) | 9.242 | 7.5254 | 18.9908 | 32.3221 | 46.823
MK-Mackay Area | 347_Mt Bassett 33 kV | Loading (MVA) | 0.54886 | 0.44738 | 1.1305 | 1.9257 | 2.7927
MK-Mackay Area | 347_Mt Bassett 33 kV | Loading (MW) | 0.52206 | 0.43021 | 1.1185 | 1.9199 | 2.7926
MK-Mackay Area | 347_Mt Bassett 33 kV | Power Factor | 0.95117 | 0.96162 | 0.9893 | 0.99687 | 0.99996
MK-Mackay Area | 347_Mt Bassett 33 kV | Rating (A) | 255 | 255 | 255 | 255 | 255
MK-Mackay Area | 347_Mt Bassett 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK-Mackay Area | 347_Mt Bassett 33 kV | Min Voltage at Constrained Conductor | 34.2878 | 34.3225 | 34.3683 | 34.398 | 34.435
MK-Mackay Area | 347_Mt Bassett 33 kV | Contingency Outage | 3053_Mt Bassett 33 kV | 387_Mackay-Alfred Street 1 33 kV | 3053_Mt Bassett 33 kV | 3053_Mt Bassett 33 kV | 3053_Mt Bassett 33 kV
MK-Mackay Area | 348_Farleigh 33 kV | % of Rated A | 5.641% | 7.692% | 9.474% | 11.08% | 12.62%
MK-Mackay Area | 348_Farleigh 33 kV | Limiting Line Name | TR_LINE 13162_1 | TR_LINE 13162_1 | TR_LINE 13162_1 | TR_LINE 13162_1 | TR_LINE 13162_1
MK-Mackay Area | 348_Farleigh 33 kV | Loading (A) | 10.9439 | 14.9228 | 18.3801 | 21.4891 | 24.4797
MK-Mackay Area | 348_Farleigh 33 kV | Loading (MVA) | 0.65204 | 0.89124 | 1.0999 | 1.2882 | 1.4698
MK-Mackay Area | 348_Farleigh 33 kV | Loading (MW) | 0.59601 | 0.85237 | 1.0699 | 1.2639 | 1.4497
MK-Mackay Area | 348_Farleigh 33 kV | Power Factor | 0.91404 | 0.95634 | 0.97265 | 0.9811 | 0.98628
MK-Mackay Area | 348_Farleigh 33 kV | Rating (A) | 194 | 194 | 194 | 194 | 194
MK-Mackay Area | 348_Farleigh 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK-Mackay Area | 348_Farleigh 33 kV | Min Voltage at Constrained Conductor | 34.3985 | 34.4815 | 34.5506 | 34.6094 | 34.6648
MK-Mackay Area | 348_Farleigh 33 kV | Contingency Outage | 422_North Mackay No 1 33 kV | 422_North Mackay No 1 33 kV | 422_North Mackay No 1 33 kV | 422_North Mackay No 1 33 kV | 422_North Mackay No 1 33 kV
MK-Mackay Area | 349_Pioneer Valley - Pinnacle 66 kV | % of Rated A | 9.318% | 12.09% | 14.62% | 16.95% | 19.29%
MK-Mackay Area | 349_Pioneer Valley - Pinnacle 66 kV | Limiting Line Name | TR_LINE 9735_1 | TR_LINE 9735_1 | TR_LINE 9735_1 | TR_LINE 9735_1 | TR_LINE 9735_1
MK-Mackay Area | 349_Pioneer Valley - Pinnacle 66 kV | Loading (A) | 20.4987 | 26.5981 | 32.1619 | 37.2837 | 42.4411
MK-Mackay Area | 349_Pioneer Valley - Pinnacle 66 kV | Loading (MVA) | 2.4713 | 3.2088 | 3.8816 | 4.5007 | 5.1233
MK-Mackay Area | 349_Pioneer Valley - Pinnacle 66 kV | Loading (MW) | 2.2417 | 3.0438 | 3.754 | 4.3982 | 5.0405
MK-Mackay Area | 349_Pioneer Valley - Pinnacle 66 kV | Power Factor | 0.90707 | 0.94855 | 0.96711 | 0.97722 | 0.98384
MK-Mackay Area | 349_Pioneer Valley - Pinnacle 66 kV | Rating (A) | 220 | 220 | 220 | 220 | 220
MK-Mackay Area | 349_Pioneer Valley - Pinnacle 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK-Mackay Area | 349_Pioneer Valley - Pinnacle 66 kV | Min Voltage at Constrained Conductor | 69.6059 | 69.6523 | 69.6806 | 69.6949 | 69.6949
MK-Mackay Area | 349_Pioneer Valley - Pinnacle 66 kV | Contingency Outage | 360_Pinnacle-Crediton/Eungella Dam 66 kV | 360_Pinnacle-Crediton/Eungella Dam 66 kV | 360_Pinnacle-Crediton/Eungella Dam 66 kV | 360_Pinnacle-Crediton/Eungella Dam 66 kV | 360_Pinnacle-Crediton/Eungella Dam 66 kV
MK-Mackay Area | 351_Alligator Creek 33 kV | % of Rated A | 0.2411% | 2.297% | 4.706% | 7.255% | 10.06%
MK-Mackay Area | 351_Alligator Creek 33 kV | Limiting Line Name | TR_LINE 66244_3 | TR_LINE 93922_3 | TR_LINE 93922_3 | TR_CABLE 7120_1 | TR_CABLE 7120_1
MK-Mackay Area | 351_Alligator Creek 33 kV | Loading (A) | 0.61481 | 5.3754 | 11.0123 | 16.9773 | 23.5335
MK-Mackay Area | 351_Alligator Creek 33 kV | Loading (MVA) | 0.037054 | 0.32378 | 0.66459 | 1.027 | 1.4264
MK-Mackay Area | 351_Alligator Creek 33 kV | Loading (MW) | 0.0026232 | 0.32261 | 0.66421 | 1.027 | 1.4262
MK-Mackay Area | 351_Alligator Creek 33 kV | Power Factor | 0.070795 | 0.99639 | 0.99941 | 0.99991 | 0.99983
MK-Mackay Area | 351_Alligator Creek 33 kV | Rating (A) | 255 | 234 | 234 | 234 | 234
MK-Mackay Area | 351_Alligator Creek 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK-Mackay Area | 351_Alligator Creek 33 kV | Min Voltage at Constrained Conductor | 34.7959 | 34.7758 | 34.843 | 34.9268 | 34.9945
MK-Mackay Area | 351_Alligator Creek 33 kV | Contingency Outage | PV 6/5_Glenella No 1 66 kV | 422_North Mackay No 1 33 kV | 422_North Mackay No 1 33 kV | 422_North Mackay No 1 33 kV | 422_North Mackay No 1 33 kV
MK-Mackay Area | 360_Pinnacle-Crediton/Eungella Dam 66 kV | % of Rated A | 9.578% | 9.285% | 9.026% | 8.794% | 8.571%
MK-Mackay Area | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Limiting Line Name | TR_LINE 10229_1 | TR_LINE 10229_1 | TR_LINE 10229_1 | TR_LINE 10229_1 | TR_LINE 10229_1
MK-Mackay Area | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Loading (A) | 8.8115 | 8.5418 | 8.3037 | 8.0904 | 7.8851
MK-Mackay Area | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Loading (MVA) | 1.0622 | 1.0313 | 1.0037 | 0.97887 | 0.95467
MK-Mackay Area | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Loading (MW) | 0.88076 | 0.84173 | 0.80671 | 0.77484 | 0.74367
MK-Mackay Area | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Power Factor | 0.82915 | 0.81622 | 0.8037 | 0.79156 | 0.77898
MK-Mackay Area | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Rating (A) | 92 | 92 | 92 | 92 | 92
MK-Mackay Area | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK-Mackay Area | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Min Voltage at Constrained Conductor | 69.5998 | 69.7028 | 69.7891 | 69.8537 | 69.9008
MK-Mackay Area | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Contingency Outage | 422_North Mackay No 1 33 kV | 422_North Mackay No 1 33 kV | 422_North Mackay No 1 33 kV | 423_North Mackay No 2 33 kV | 423_North Mackay No 2 33 kV
MK-Mackay Area | 364_West Mackay No 1 33 kV | % of Rated A | 9.302% | 7.615% | 6.215% | 4.985% | 3.861%
MK-Mackay Area | 364_West Mackay No 1 33 kV | Limiting Line Name | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1
MK-Mackay Area | 364_West Mackay No 1 33 kV | Loading (A) | 26.9772 | 22.0821 | 18.0246 | 14.4578 | 11.1969
MK-Mackay Area | 364_West Mackay No 1 33 kV | Loading (MVA) | 1.5989 | 1.3102 | 1.0704 | 0.85926 | 0.66593
MK-Mackay Area | 364_West Mackay No 1 33 kV | Loading (MW) | 1.5988 | 1.3102 | 1.0704 | 0.85925 | 0.66592
MK-Mackay Area | 364_West Mackay No 1 33 kV | Power Factor | 0.99995 | 0.99996 | 0.99998 | 0.99998 | 0.99999
MK-Mackay Area | 364_West Mackay No 1 33 kV | Rating (A) | 290 | 290 | 290 | 290 | 290
MK-Mackay Area | 364_West Mackay No 1 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK-Mackay Area | 364_West Mackay No 1 33 kV | Min Voltage at Constrained Conductor | 34.2189 | 34.2564 | 34.2875 | 34.3131 | 34.3375
MK-Mackay Area | 364_West Mackay No 1 33 kV | Contingency Outage | 422_North Mackay No 1 33 kV | 422_North Mackay No 1 33 kV | 422_North Mackay No 1 33 kV | 422_North Mackay No 1 33 kV | 422_North Mackay No 1 33 kV
MK-Mackay Area | 365_Tennyson St No 1 33 kV | % of Rated A | 2.905% | 2.66% | 2.47% | 2.317% | 2.199%
MK-Mackay Area | 365_Tennyson St No 1 33 kV | Limiting Line Name | TR_CABLE 7286_1 | TR_CABLE 7286_1 | TR_CABLE 7286_1 | TR_CABLE 7286_1 | TR_CABLE 7286_1
MK-Mackay Area | 365_Tennyson St No 1 33 kV | Loading (A) | 19.3187 | 17.6876 | 16.4224 | 15.4078 | 14.6264
MK-Mackay Area | 365_Tennyson St No 1 33 kV | Loading (MVA) | 1.1469 | 1.0513 | 0.97701 | 0.91734 | 0.87136
MK-Mackay Area | 365_Tennyson St No 1 33 kV | Loading (MW) | 1.0685 | 0.93305 | 0.81167 | 0.69363 | 0.5725
MK-Mackay Area | 365_Tennyson St No 1 33 kV | Power Factor | 0.93168 | 0.88752 | 0.83077 | 0.75614 | 0.65701
MK-Mackay Area | 365_Tennyson St No 1 33 kV | Rating (A) | 665 | 665 | 665 | 665 | 665
MK-Mackay Area | 365_Tennyson St No 1 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK-Mackay Area | 365_Tennyson St No 1 33 kV | Min Voltage at Constrained Conductor | 34.2754 | 34.316 | 34.3479 | 34.3739 | 34.3955
MK-Mackay Area | 365_Tennyson St No 1 33 kV | Contingency Outage | 387_Mackay-Alfred Street 1 33 kV | 387_Mackay-Alfred Street 1 33 kV | 387_Mackay-Alfred Street 1 33 kV | 387_Mackay-Alfred Street 1 33 kV | 387_Mackay-Alfred Street 1 33 kV
MK-Mackay Area | 367_Pioneer Valley - Greenmount 66 kV | % of Rated A | 0.06494% | 0.06497% | 0.06499% | 0.065% | 0.065%
MK-Mackay Area | 367_Pioneer Valley - Greenmount 66 kV | Limiting Line Name | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1
MK-Mackay Area | 367_Pioneer Valley - Greenmount 66 kV | Loading (A) | 0.16364 | 0.16372 | 0.16376 | 0.1638 | 0.1638
MK-Mackay Area | 367_Pioneer Valley - Greenmount 66 kV | Loading (MVA) | 0.019749 | 0.019768 | 0.019779 | 0.019787 | 0.019787
MK-Mackay Area | 367_Pioneer Valley - Greenmount 66 kV | Loading (MW) | 8.0335e-08 | 8.0492e-08 | 8.0535e-08 | 8.0574e-08 | 8.0559e-08
MK-Mackay Area | 367_Pioneer Valley - Greenmount 66 kV | Power Factor | 4.0677e-06 | 4.0719e-06 | 4.0718e-06 | 4.072e-06 | 4.0712e-06
MK-Mackay Area | 367_Pioneer Valley - Greenmount 66 kV | Rating (A) | 252 | 252 | 252 | 252 | 252
MK-Mackay Area | 367_Pioneer Valley - Greenmount 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK-Mackay Area | 367_Pioneer Valley - Greenmount 66 kV | Min Voltage at Constrained Conductor | 69.6788 | 69.7112 | 69.7313 | 69.7459 | 69.7462
MK-Mackay Area | 367_Pioneer Valley - Greenmount 66 kV | Contingency Outage | PV 6/5_Glenella No 1 66 kV | PV 6/5_Glenella No 1 66 kV | 6333_Hail Creek 66 kV | 6333_Hail Creek 66 kV | 6333_Hail Creek 66 kV
MK-Mackay Area | 372_Pioneer Valley-McKinley Creek 33 kV | % of Rated A | 2.744% | 3.452% | 4.059% | 4.611% | 5.144%
MK-Mackay Area | 372_Pioneer Valley-McKinley Creek 33 kV | Limiting Line Name | TR_LINE 9963_1 | TR_LINE 9963_1 | TR_LINE 9963_1 | TR_LINE 9963_1 | TR_LINE 9963_1
MK-Mackay Area | 372_Pioneer Valley-McKinley Creek 33 kV | Loading (A) | 5.3504 | 6.7316 | 7.9146 | 8.9912 | 10.0302
MK-Mackay Area | 372_Pioneer Valley-McKinley Creek 33 kV | Loading (MVA) | 0.64265 | 0.8092 | 0.95203 | 1.082 | 1.2072
MK-Mackay Area | 372_Pioneer Valley-McKinley Creek 33 kV | Loading (MW) | 0.62897 | 0.79877 | 0.94354 | 1.0749 | 1.2012
MK-Mackay Area | 372_Pioneer Valley-McKinley Creek 33 kV | Power Factor | 0.97853 | 0.98688 | 0.99082 | 0.99313 | 0.99469
MK-Mackay Area | 372_Pioneer Valley-McKinley Creek 33 kV | Rating (A) | 195 | 195 | 195 | 195 | 195
MK-Mackay Area | 372_Pioneer Valley-McKinley Creek 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK-Mackay Area | 372_Pioneer Valley-McKinley Creek 33 kV | Min Voltage at Constrained Conductor | 69.3469 | 69.4027 | 69.448 | 69.4765 | 69.4883
MK-Mackay Area | 372_Pioneer Valley-McKinley Creek 33 kV | Contingency Outage | 422_North Mackay No 1 33 kV | 422_North Mackay No 1 33 kV | 422_North Mackay No 1 33 kV | 423_North Mackay No 2 33 kV | 423_North Mackay No 2 33 kV
MK-Mackay Area | 387_Mackay-Alfred Street 1 33 kV | % of Rated A | 37.75% | 35.85% | 34.32% | 33% | 31.81%
MK-Mackay Area | 387_Mackay-Alfred Street 1 33 kV | Limiting Line Name | TR_CABLE 2967_1 | TR_CABLE 2967_1 | TR_CABLE 2967_1 | TR_CABLE 2967_1 | TR_CABLE 2967_1
MK-Mackay Area | 387_Mackay-Alfred Street 1 33 kV | Loading (A) | 162.7146 | 154.5279 | 147.9387 | 142.2129 | 137.0826
MK-Mackay Area | 387_Mackay-Alfred Street 1 33 kV | Loading (MVA) | 9.6598 | 9.1846 | 8.8011 | 8.4669 | 8.1666
MK-Mackay Area | 387_Mackay-Alfred Street 1 33 kV | Loading (MW) | 6.0049 | 5.2177 | 4.5323 | 3.8834 | 3.2431
MK-Mackay Area | 387_Mackay-Alfred Street 1 33 kV | Power Factor | 0.62164 | 0.5681 | 0.51497 | 0.45866 | 0.39712
MK-Mackay Area | 387_Mackay-Alfred Street 1 33 kV | Rating (A) | 431 | 431 | 431 | 431 | 431
MK-Mackay Area | 387_Mackay-Alfred Street 1 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK-Mackay Area | 387_Mackay-Alfred Street 1 33 kV | Min Voltage at Constrained Conductor | 34.2751 | 34.3156 | 34.3475 | 34.3735 | 34.395
MK-Mackay Area | 387_Mackay-Alfred Street 1 33 kV | Contingency Outage | 430_Mackay-Alfred Street 2 33 kV | 430_Mackay-Alfred Street 2 33 kV | 430_Mackay-Alfred Street 2 33 kV | 430_Mackay-Alfred Street 2 33 kV | 430_Mackay-Alfred Street 2 33 kV
MK-Mackay Area | 395_Tennyson Street-Alfred Street 33 kV | % of Rated A | 9.222% | 9.77% | 10.33% | 10.95% | 11.68%
MK-Mackay Area | 395_Tennyson Street-Alfred Street 33 kV | Limiting Line Name | TR_CABLE 2960_1 | TR_CABLE 2960_1 | TR_CABLE 2960_1 | TR_CABLE 2960_1 | TR_CABLE 2960_1
MK-Mackay Area | 395_Tennyson Street-Alfred Street 33 kV | Loading (A) | 61.9725 | 65.6548 | 69.4467 | 73.5953 | 78.4717
MK-Mackay Area | 395_Tennyson Street-Alfred Street 33 kV | Loading (MVA) | 3.6792 | 3.9029 | 4.1326 | 4.3832 | 4.6771
MK-Mackay Area | 395_Tennyson Street-Alfred Street 33 kV | Loading (MW) | 1.77 | 2.1046 | 2.4305 | 2.7704 | 3.1545
MK-Mackay Area | 395_Tennyson Street-Alfred Street 33 kV | Power Factor | 0.48108 | 0.53924 | 0.58814 | 0.63203 | 0.67444
MK-Mackay Area | 395_Tennyson Street-Alfred Street 33 kV | Rating (A) | 672 | 672 | 672 | 672 | 672
MK-Mackay Area | 395_Tennyson Street-Alfred Street 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK-Mackay Area | 395_Tennyson Street-Alfred Street 33 kV | Min Voltage at Constrained Conductor | 34.276 | 34.3208 | 34.3565 | 34.3862 | 34.4112
MK-Mackay Area | 395_Tennyson Street-Alfred Street 33 kV | Contingency Outage | 387_Mackay-Alfred Street 1 33 kV | 387_Mackay-Alfred Street 1 33 kV | 387_Mackay-Alfred Street 1 33 kV | 387_Mackay-Alfred Street 1 33 kV | 387_Mackay-Alfred Street 1 33 kV
MK-Mackay Area | 422_North Mackay No 1 33 kV | % of Rated A | 23.14% | 30.18% | 37.03% | 43.41% | 49.91%
MK-Mackay Area | 422_North Mackay No 1 33 kV | Limiting Line Name | TR_LINE 97201_1 | TR_LINE 97201_1 | TR_LINE 11650_2 | TR_LINE 11650_2 | TR_LINE 11650_2
MK-Mackay Area | 422_North Mackay No 1 33 kV | Loading (A) | 144.5972 | 188.6496 | 135.8848 | 159.3301 | 183.176
MK-Mackay Area | 422_North Mackay No 1 33 kV | Loading (MVA) | 8.6493 | 11.2821 | 8.2289 | 9.6754 | 11.147
MK-Mackay Area | 422_North Mackay No 1 33 kV | Loading (MW) | 7.5947 | 10.5539 | 8.2256 | 9.6701 | 11.139
MK-Mackay Area | 422_North Mackay No 1 33 kV | Power Factor | 0.87807 | 0.93546 | 0.9996 | 0.99945 | 0.99928
MK-Mackay Area | 422_North Mackay No 1 33 kV | Rating (A) | 625 | 625 | 367 | 367 | 367
MK-Mackay Area | 422_North Mackay No 1 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK-Mackay Area | 422_North Mackay No 1 33 kV | Min Voltage at Constrained Conductor | 34.5306 | 34.5228 | 34.9608 | 35.0572 | 35.1311
MK-Mackay Area | 422_North Mackay No 1 33 kV | Contingency Outage | 342_South Mackay 33 kV | PV 6/4_Glenella No 2 66 kV | PV 6/4_Glenella No 2 66 kV | PV 6/4_Glenella No 2 66 kV | 342_South Mackay 33 kV
MK-Mackay Area | 423_North Mackay No 2 33 kV | % of Rated A | 13.97% | 15.83% | 17.93% | 20.3% | 23.03%
MK-Mackay Area | 423_North Mackay No 2 33 kV | Limiting Line Name | TR_CABLE 6563_1 | TR_CABLE 6563_1 | TR_CABLE 6563_1 | TR_CABLE 6563_1 | TR_CABLE 6563_1
MK-Mackay Area | 423_North Mackay No 2 33 kV | Loading (A) | 85.4856 | 96.8591 | 109.7451 | 124.2466 | 140.9249
MK-Mackay Area | 423_North Mackay No 2 33 kV | Loading (MVA) | 5.1628 | 5.8347 | 6.5705 | 7.4058 | 8.4067
MK-Mackay Area | 423_North Mackay No 2 33 kV | Loading (MW) | 2.8265 | 3.9857 | 5.0862 | 6.1941 | 7.4017
MK-Mackay Area | 423_North Mackay No 2 33 kV | Power Factor | 0.54743 | 0.68307 | 0.77407 | 0.83636 | 0.88043
MK-Mackay Area | 423_North Mackay No 2 33 kV | Rating (A) | 612 | 612 | 612 | 612 | 612
MK-Mackay Area | 423_North Mackay No 2 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK-Mackay Area | 423_North Mackay No 2 33 kV | Min Voltage at Constrained Conductor | 34.8686 | 34.7793 | 34.5662 | 34.4136 | 34.4412
MK-Mackay Area | 423_North Mackay No 2 33 kV | Contingency Outage | PV 6/4_Glenella No 2 66 kV | 422_North Mackay No 1 33 kV | PV 6/4_Glenella No 2 66 kV | 422_North Mackay No 1 33 kV | 422_North Mackay No 1 33 kV
MK-Mackay Area | 430_Mackay-Alfred Street 2 33 kV | % of Rated A | 27.86% | 26.46% | 25.34% | 24.36% | 23.48%
MK-Mackay Area | 430_Mackay-Alfred Street 2 33 kV | Limiting Line Name | TR_CABLE 8887_1 | TR_CABLE 8887_1 | TR_CABLE 8887_1 | TR_CABLE 8887_1 | TR_CABLE 8887_1
MK-Mackay Area | 430_Mackay-Alfred Street 2 33 kV | Loading (A) | 161.3018 | 153.2059 | 146.6905 | 141.0291 | 135.9568
MK-Mackay Area | 430_Mackay-Alfred Street 2 33 kV | Loading (MVA) | 9.576 | 9.1061 | 8.727 | 8.3965 | 8.0996
MK-Mackay Area | 430_Mackay-Alfred Street 2 33 kV | Loading (MW) | 5.9421 | 5.1626 | 4.484 | 3.8415 | 3.2075
MK-Mackay Area | 430_Mackay-Alfred Street 2 33 kV | Power Factor | 0.62052 | 0.56694 | 0.5138 | 0.45751 | 0.39601
MK-Mackay Area | 430_Mackay-Alfred Street 2 33 kV | Rating (A) | 579 | 579 | 579 | 579 | 579
MK-Mackay Area | 430_Mackay-Alfred Street 2 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK-Mackay Area | 430_Mackay-Alfred Street 2 33 kV | Min Voltage at Constrained Conductor | 34.2756 | 34.3161 | 34.348 | 34.374 | 34.3955
MK-Mackay Area | 430_Mackay-Alfred Street 2 33 kV | Contingency Outage | 387_Mackay-Alfred Street 1 33 kV | 387_Mackay-Alfred Street 1 33 kV | 387_Mackay-Alfred Street 1 33 kV | 387_Mackay-Alfred Street 1 33 kV | 387_Mackay-Alfred Street 1 33 kV
MK-Mackay Area | PV 6/4_Glenella No 2 66 kV | % of Rated A | 14.39% | 18.66% | 23.07% | 27.61% | 32.51%
MK-Mackay Area | PV 6/4_Glenella No 2 66 kV | Limiting Line Name | TR_LINE 105536_1 | TR_LINE 105536_1 | TR_LINE 105536_1 | TR_LINE 105536_1 | TR_LINE 105536_1
MK-Mackay Area | PV 6/4_Glenella No 2 66 kV | Loading (A) | 116.413 | 150.937 | 186.6732 | 223.3362 | 263.0189
MK-Mackay Area | PV 6/4_Glenella No 2 66 kV | Loading (MVA) | 14.0496 | 18.2248 | 22.5441 | 26.9707 | 31.7536
MK-Mackay Area | PV 6/4_Glenella No 2 66 kV | Loading (MW) | 10.644 | 16.0274 | 21.0639 | 25.9794 | 31.1368
MK-Mackay Area | PV 6/4_Glenella No 2 66 kV | Power Factor | 0.7576 | 0.87943 | 0.93434 | 0.96325 | 0.98057
MK-Mackay Area | PV 6/4_Glenella No 2 66 kV | Rating (A) | 809 | 809 | 809 | 809 | 809
MK-Mackay Area | PV 6/4_Glenella No 2 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK-Mackay Area | PV 6/4_Glenella No 2 66 kV | Min Voltage at Constrained Conductor | 69.6788 | 69.7112 | 69.7242 | 69.7213 | 69.7008
MK-Mackay Area | PV 6/4_Glenella No 2 66 kV | Contingency Outage | PV 6/5_Glenella No 1 66 kV | PV 6/5_Glenella No 1 66 kV | PV 6/5_Glenella No 1 66 kV | PV 6/5_Glenella No 1 66 kV | PV 6/5_Glenella No 1 66 kV
MK-Mackay Area | PV 6/5_Glenella No 1 66 kV | % of Rated A | 14.37% | 18.55% | 23.02% | 27.6% | 32.54%
MK-Mackay Area | PV 6/5_Glenella No 1 66 kV | Limiting Line Name | TR_LINE 105066_1 | TR_LINE 105066_1 | TR_LINE 105066_1 | TR_LINE 105066_1 | TR_LINE 105066_1
MK-Mackay Area | PV 6/5_Glenella No 1 66 kV | Loading (A) | 116.2156 | 150.1064 | 186.2702 | 223.2839 | 263.2382
MK-Mackay Area | PV 6/5_Glenella No 1 66 kV | Loading (MVA) | 14.1863 | 18.3517 | 22.8071 | 27.3681 | 32.2869
MK-Mackay Area | PV 6/5_Glenella No 1 66 kV | Loading (MW) | 10.7124 | 16.1397 | 21.2332 | 26.2262 | 31.4795
MK-Mackay Area | PV 6/5_Glenella No 1 66 kV | Power Factor | 0.75511 | 0.87947 | 0.93099 | 0.95828 | 0.97499
MK-Mackay Area | PV 6/5_Glenella No 1 66 kV | Rating (A) | 809 | 809 | 809 | 809 | 809
MK-Mackay Area | PV 6/5_Glenella No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK-Mackay Area | PV 6/5_Glenella No 1 66 kV | Min Voltage at Constrained Conductor | 70.4757 | 70.5834 | 70.6882 | 70.7628 | 70.8097
MK-Mackay Area | PV 6/5_Glenella No 1 66 kV | Contingency Outage | PV 6/4_Glenella No 2 66 kV | PV 6/4_Glenella No 2 66 kV | PV 6/4_Glenella No 2 66 kV | PV 6/4_Glenella No 2 66 kV | PV 6/4_Glenella No 2 66 kV
MK-Moranbah | 6328_Broadlea - Moorvale 66 kV | % of Rated A | 5.41% | 5.41% | 5.411% | 5.412% | 5.418%
MK-Moranbah | 6328_Broadlea - Moorvale 66 kV | Limiting Line Name | TR_LINE 36093_1 | TR_LINE 36093_1 | TR_LINE 36093_1 | TR_LINE 36093_1 | TR_LINE 36093_1
MK-Moranbah | 6328_Broadlea - Moorvale 66 kV | Loading (A) | 20.8841 | 20.8815 | 20.8851 | 20.8913 | 20.9135
MK-Moranbah | 6328_Broadlea - Moorvale 66 kV | Loading (MVA) | 2.5038 | 2.5035 | 2.5039 | 2.5047 | 2.5073
MK-Moranbah | 6328_Broadlea - Moorvale 66 kV | Loading (MW) | 2.5033 | 2.503 | 2.5035 | 2.5042 | 2.5069
MK-Moranbah | 6328_Broadlea - Moorvale 66 kV | Power Factor | 0.9998 | 0.9998 | 0.9998 | 0.9998 | 0.9998
MK-Moranbah | 6328_Broadlea - Moorvale 66 kV | Rating (A) | 386 | 386 | 386 | 386 | 386
MK-Moranbah | 6328_Broadlea - Moorvale 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK-Moranbah | 6328_Broadlea - Moorvale 66 kV | Min Voltage at Constrained Conductor | 69.2195 | 69.2195 | 69.2195 | 69.2194 | 69.2193
MK-Moranbah | 6328_Broadlea - Moorvale 66 kV | Contingency Outage | 6269_South Walker 66 kV | 3046_Rosella 33 kV | 6269_South Walker 66 kV | 232_Newlands-Glenden 66 kV | 232_Newlands-Glenden 66 kV
MK-Moranbah | 6330 Broadlea - Millennium 66 kV | % of Rated A | 39.43% | 39.43% | 39.43% | 39.43% | 39.43%
MK-Moranbah | 6330 Broadlea - Millennium 66 kV | Limiting Line Name | TR_LINE 63688_1 | TR_LINE 63688_1 | TR_LINE 63688_1 | TR_LINE 63688_1 | TR_LINE 63688_1
MK-Moranbah | 6330 Broadlea - Millennium 66 kV | Loading (A) | 277.9832 | 277.9832 | 277.9832 | 277.9833 | 277.9835
MK-Moranbah | 6330 Broadlea - Millennium 66 kV | Loading (MVA) | 33.3516 | 33.3516 | 33.3516 | 33.3516 | 33.3516
MK-Moranbah | 6330 Broadlea - Millennium 66 kV | Loading (MW) | 33.3514 | 33.3514 | 33.3514 | 33.3514 | 33.3514
MK-Moranbah | 6330 Broadlea - Millennium 66 kV | Power Factor | 1 | 1 | 1 | 1 | 1
MK-Moranbah | 6330 Broadlea - Millennium 66 kV | Rating (A) | 705 | 705 | 705 | 705 | 705
MK-Moranbah | 6330 Broadlea - Millennium 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK-Moranbah | 6330 Broadlea - Millennium 66 kV | Min Voltage at Constrained Conductor | 69.2076 | 69.2076 | 69.2076 | 69.2076 | 69.2075
MK-Moranbah | 6330 Broadlea - Millennium 66 kV | Contingency Outage | 6269_South Walker 66 kV | 3046_Rosella 33 kV | 6269_South Walker 66 kV | 232_Newlands-Glenden 66 kV | 232_Newlands-Glenden 66 kV
MK-Moranbah | 7366_Moranbah - Broadlea 132 kV | % of Rated A | 31.81% | 31.81% | 31.81% | 31.81% | 31.81%
MK-Moranbah | 7366_Moranbah - Broadlea 132 kV | Limiting Line Name | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1
MK-Moranbah | 7366_Moranbah - Broadlea 132 kV | Loading (A) | 224.2411 | 224.2398 | 224.2415 | 224.2448 | 224.256
MK-Moranbah | 7366_Moranbah - Broadlea 132 kV | Loading (MVA) | 53.8906 | 53.8903 | 53.8907 | 53.8915 | 53.8942
MK-Moranbah | 7366_Moranbah - Broadlea 132 kV | Loading (MW) | 53.8656 | 53.8653 | 53.8657 | 53.8665 | 53.8691
MK-Moranbah | 7366_Moranbah - Broadlea 132 kV | Power Factor | 0.99954 | 0.99954 | 0.99954 | 0.99954 | 0.99954
MK-Moranbah | 7366_Moranbah - Broadlea 132 kV | Rating (A) | 705 | 705 | 705 | 705 | 705
MK-Moranbah | 7366_Moranbah - Broadlea 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK-Moranbah | 7366_Moranbah - Broadlea 132 kV | Min Voltage at Constrained Conductor | 138.7478 | 138.7478 | 138.7478 | 138.7478 | 138.7477
MK-Moranbah | 7366_Moranbah - Broadlea 132 kV | Contingency Outage | 6269_South Walker 66 kV | 3046_Rosella 33 kV | 6269_South Walker 66 kV | 232_Newlands-Glenden 66 kV | 232_Newlands-Glenden 66 kV
MK-Newlands | 232_Newlands-Glenden 66 kV | % of Rated A | 3.742% | 3.731% | 3.726% | 3.735% | 3.758%
MK-Newlands | 232_Newlands-Glenden 66 kV | Limiting Line Name | TR_LINE 10181_1 | TR_LINE 10181_1 | TR_LINE 10181_1 | TR_LINE 10181_1 | TR_LINE 10181_1
MK-Newlands | 232_Newlands-Glenden 66 kV | Loading (A) | 4.3412 | 4.3282 | 4.3222 | 4.3322 | 4.3592
MK-Newlands | 232_Newlands-Glenden 66 kV | Loading (MVA) | 0.51481 | 0.51327 | 0.51258 | 0.51377 | 0.51698
MK-Newlands | 232_Newlands-Glenden 66 kV | Loading (MW) | 0.42959 | 0.42773 | 0.42688 | 0.42832 | 0.43219
MK-Newlands | 232_Newlands-Glenden 66 kV | Power Factor | 0.83447 | 0.83333 | 0.83281 | 0.83367 | 0.83598
MK-Newlands | 232_Newlands-Glenden 66 kV | Rating (A) | 116 | 116 | 116 | 116 | 116
MK-Newlands | 232_Newlands-Glenden 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK-Newlands | 232_Newlands-Glenden 66 kV | Min Voltage at Constrained Conductor | 68.4659 | 68.4676 | 68.4689 | 68.4699 | 68.4707
MK-Newlands | 232_Newlands-Glenden 66 kV | Contingency Outage | 422_North Mackay No 1 33 kV | 422_North Mackay No 1 33 kV | 422_North Mackay No 1 33 kV | 422_North Mackay No 1 33 kV | 422_North Mackay No 1 33 kV
MK-Newlands | NL-WR-1_Newlands-Wirralie 1 66 kV | % of Rated A | 5.205% | 5.204% | 5.204% | 5.204% | 5.204%
MK-Newlands | NL-WR-1_Newlands-Wirralie 1 66 kV | Limiting Line Name | TR_LINE 180753_1 | TR_LINE 180753_1 | TR_LINE 180753_1 | TR_LINE 180753_1 | TR_LINE 180753_1
MK-Newlands | NL-WR-1_Newlands-Wirralie 1 66 kV | Loading (A) | 9.7848 | 9.783 | 9.7828 | 9.7829 | 9.783
MK-Newlands | NL-WR-1_Newlands-Wirralie 1 66 kV | Loading (MVA) | 1.1704 | 1.1702 | 1.1702 | 1.1702 | 1.1702
MK-Newlands | NL-WR-1_Newlands-Wirralie 1 66 kV | Loading (MW) | 0.043455 | 0.026213 | 0.017379 | 0.013099 | 0.011288
MK-Newlands | NL-WR-1_Newlands-Wirralie 1 66 kV | Power Factor | 0.037129 | 0.0224 | 0.014852 | 0.011193 | 0.0096462
MK-Newlands | NL-WR-1_Newlands-Wirralie 1 66 kV | Rating (A) | 188 | 188 | 188 | 188 | 188
MK-Newlands | NL-WR-1_Newlands-Wirralie 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK-Newlands | NL-WR-1_Newlands-Wirralie 1 66 kV | Min Voltage at Constrained Conductor | 69.0579 | 69.0596 | 69.0609 | 69.0619 | 69.0627
MK-Newlands | NL-WR-1_Newlands-Wirralie 1 66 kV | Contingency Outage | NL-NM-1 Newlands-Newlands Mine 1 66 kV | NL-NM-1 Newlands-Newlands Mine 1 66 kV | NL-NM-1 Newlands-Newlands Mine 1 66 kV | NL-NM-1 Newlands-Newlands Mine 1 66 kV | NL-NM-1 Newlands-Newlands Mine 1 66 kV
NQ-Collinsville | 2031 Collinsville-PS-Collinsville 33 kV | % of Rated A | 24.89% | 24.04% | 23.27% | 22.55% | 21.79%
NQ-Collinsville | 2031 Collinsville-PS-Collinsville 33 kV | Limiting Line Name | TR_CABLE 4177_1 | TR_CABLE 4177_1 | TR_CABLE 4177_1 | TR_CABLE 4177_1 | TR_CABLE 4177_1
NQ-Collinsville | 2031 Collinsville-PS-Collinsville 33 kV | Loading (A) | 172.484 | 166.6145 | 161.2377 | 156.2516 | 151.0072
NQ-Collinsville | 2031 Collinsville-PS-Collinsville 33 kV | Loading (MVA) | 10.3332 | 9.9857 | 9.6624 | 9.3581 | 9.0425
NQ-Collinsville | 2031 Collinsville-PS-Collinsville 33 kV | Loading (MW) | 10.3267 | 9.979 | 9.6554 | 9.3509 | 9.0351
NQ-Collinsville | 2031 Collinsville-PS-Collinsville 33 kV | Power Factor | 0.99937 | 0.99933 | 0.99928 | 0.99924 | 0.99918
NQ-Collinsville | 2031 Collinsville-PS-Collinsville 33 kV | Rating (A) | 693 | 693 | 693 | 693 | 693
NQ-Collinsville | 2031 Collinsville-PS-Collinsville 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Collinsville | 2031 Collinsville-PS-Collinsville 33 kV | Min Voltage at Constrained Conductor | 34.5828 | 34.5974 | 34.5936 | 34.5734 | 34.5679
NQ-Collinsville | 2031 Collinsville-PS-Collinsville 33 kV | Contingency Outage | 119_Cannonvale No 1 66 kV | 119_Cannonvale No 1 66 kV | 119_Cannonvale No 1 66 kV | 119_Cannonvale No 1 66 kV | 119_Cannonvale No 1 66 kV
NQ-Collinsville | 3000 Collinsville No 1 33 kV | % of Rated A | 1.687e-07% | 1.616e-07% | 1.551e-07% | 1.491e-07% | 1.427e-07%
NQ-Collinsville | 3000 Collinsville No 1 33 kV | Limiting Line Name | Link_COLL_EB04Q02_COLLINSVILLE NO 1 | Link_COLL_EB04Q02_COLLINSVILLE NO 1 | Link_COLL_EB04Q02_COLLINSVILLE NO 1 | Link_COLL_EB04Q02_COLLINSVILLE NO 1 | Link_COLL_EB04Q02_COLLINSVILLE NO 1
NQ-Collinsville | 3000 Collinsville No 1 33 kV | Loading (A) | 8.4358e-06 | 8.0813e-06 | 7.7557e-06 | 7.453e-06 | 7.1354e-06
NQ-Collinsville | 3000 Collinsville No 1 33 kV | Loading (MVA) | 5.053e-07 | 4.8427e-07 | 4.6471e-07 | 4.4631e-07 | 4.2722e-07
NQ-Collinsville | 3000 Collinsville No 1 33 kV | Loading (MW) | 5.0512e-07 | 4.8408e-07 | 4.6451e-07 | 4.461e-07 | 4.2701e-07
NQ-Collinsville | 3000 Collinsville No 1 33 kV | Power Factor | 0.99964 | 0.99961 | 0.99957 | 0.99954 | 0.9995
NQ-Collinsville | 3000 Collinsville No 1 33 kV | Rating (A) | 5000 | 5000 | 5000 | 5000 | 5000
NQ-Collinsville | 3000 Collinsville No 1 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Collinsville | 3000 Collinsville No 1 33 kV | Min Voltage at Constrained Conductor | 34.5828 | 34.5974 | 34.5936 | 34.5734 | 34.5679
NQ-Collinsville | 3000 Collinsville No 1 33 kV | Contingency Outage | 119_Cannonvale No 1 66 kV | 119_Cannonvale No 1 66 kV | 118_Cannonvale No 2 66 kV | 119_Cannonvale No 1 66 kV | 118_Cannonvale No 2 66 kV
NQ-Collinsville | 3001 Collinsville No 1 33 kV | % of Rated A | 2.17% | 2.169% | 2.17% | 2.171% | 2.171%
NQ-Collinsville | 3001 Collinsville No 1 33 kV | Limiting Line Name | Link_COLL_EB06Q02_COLLINSVILLE NO 3 | Link_COLL_EB06Q02_COLLINSVILLE NO 3 | Link_COLL_EB06Q02_COLLINSVILLE NO 3 | Link_COLL_EB06Q02_COLLINSVILLE NO 3 | Link_COLL_EB06Q02_COLLINSVILLE NO 3
NQ-Collinsville | 3001 Collinsville No 1 33 kV | Loading (A) | 108.5156 | 108.4698 | 108.4819 | 108.5452 | 108.5625
NQ-Collinsville | 3001 Collinsville No 1 33 kV | Loading (MVA) | 6.5 | 6.5 | 6.5 | 6.5 | 6.5
NQ-Collinsville | 3001 Collinsville No 1 33 kV | Loading (MW) | 6.5 | 6.5 | 6.5 | 6.5 | 6.5
NQ-Collinsville | 3001 Collinsville No 1 33 kV | Power Factor | 1 | 1 | 1 | 1 | 1
NQ-Collinsville | 3001 Collinsville No 1 33 kV | Rating (A) | 5000 | 5000 | 5000 | 5000 | 5000
NQ-Collinsville | 3001 Collinsville No 1 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Collinsville | 3001 Collinsville No 1 33 kV | Min Voltage at Constrained Conductor | 34.5828 | 34.5974 | 34.5936 | 34.5734 | 34.5679
NQ-Collinsville | 3001 Collinsville No 1 33 kV | Contingency Outage | 119_Cannonvale No 1 66 kV | 119_Cannonvale No 1 66 kV | 119_Cannonvale No 1 66 kV | 119_Cannonvale No 1 66 kV | 118_Cannonvale No 2 66 kV
NQ-Collinsville | 3218 Collinsville No 4 33 kV | % of Rated A | 1.687e-07% | 1.616e-07% | 1.551e-07% | 1.491e-07% | 1.427e-07%
NQ-Collinsville | 3218 Collinsville No 4 33 kV | Limiting Line Name | Link_COLL_EB02Q02_COLLINSVILLE NO 4 | Link_COLL_EB02Q02_COLLINSVILLE NO 4 | Link_COLL_EB02Q02_COLLINSVILLE NO 4 | Link_COLL_EB02Q02_COLLINSVILLE NO 4 | Link_COLL_EB02Q02_COLLINSVILLE NO 4
NQ-Collinsville | 3218 Collinsville No 4 33 kV | Loading (A) | 8.4358e-06 | 8.0813e-06 | 7.7557e-06 | 7.453e-06 | 7.1354e-06
NQ-Collinsville | 3218 Collinsville No 4 33 kV | Loading (MVA) | 5.053e-07 | 4.8427e-07 | 4.6471e-07 | 4.4631e-07 | 4.2722e-07
NQ-Collinsville | 3218 Collinsville No 4 33 kV | Loading (MW) | 5.0512e-07 | 4.8408e-07 | 4.6451e-07 | 4.461e-07 | 4.2701e-07
NQ-Collinsville | 3218 Collinsville No 4 33 kV | Power Factor | 0.99964 | 0.99961 | 0.99957 | 0.99954 | 0.9995
NQ-Collinsville | 3218 Collinsville No 4 33 kV | Rating (A) | 5000 | 5000 | 5000 | 5000 | 5000
NQ-Collinsville | 3218 Collinsville No 4 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Collinsville | 3218 Collinsville No 4 33 kV | Min Voltage at Constrained Conductor | 34.5828 | 34.5974 | 34.5936 | 34.5734 | 34.5679
NQ-Collinsville | 3218 Collinsville No 4 33 kV | Contingency Outage | 119_Cannonvale No 1 66 kV | 119_Cannonvale No 1 66 kV | 119_Cannonvale No 1 66 kV | 119_Cannonvale No 1 66 kV | 119_Cannonvale No 1 66 kV
NQ-Collinsville | 7308_Stony Creek - Havilah 132 kV | % of Rated A | 1.001% | 1.001% | 1.001% | 1% | 1%
NQ-Collinsville | 7308_Stony Creek - Havilah 132 kV | Limiting Line Name | TR_LINE 67629_1 | TR_LINE 67629_1 | TR_LINE 67629_1 | TR_LINE 67629_1 | TR_LINE 67629_1
NQ-Collinsville | 7308_Stony Creek - Havilah 132 kV | Loading (A) | 4.3733 | 4.3732 | 4.3724 | 4.3716 | 4.3707
NQ-Collinsville | 7308_Stony Creek - Havilah 132 kV | Loading (MVA) | 1.0657 | 1.0656 | 1.0652 | 1.0647 | 1.0642
NQ-Collinsville | 7308_Stony Creek - Havilah 132 kV | Loading (MW) | 0.39484 | 0.39484 | 0.39484 | 0.39484 | 0.39484
NQ-Collinsville | 7308_Stony Creek - Havilah 132 kV | Power Factor | 0.37049 | 0.37053 | 0.37068 | 0.37084 | 0.37102
NQ-Collinsville | 7308_Stony Creek - Havilah 132 kV | Rating (A) | 437 | 437 | 437 | 437 | 437
NQ-Collinsville | 7308_Stony Creek - Havilah 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Collinsville | 7308_Stony Creek - Havilah 132 kV | Min Voltage at Constrained Conductor | 140.6899 | 140.6825 | 140.6497 | 140.6144 | 140.5748
NQ-Collinsville | 7308_Stony Creek - Havilah 132 kV | Contingency Outage | 6308_Merinda - Abbot Point 66 kV | 6308_Merinda - Abbot Point 66 kV | 6308_Merinda - Abbot Point 66 kV | 6308_Merinda - Abbot Point 66 kV | 6308_Merinda - Abbot Point 66 kV
NQ-Collinsville | 7309_Stony Creek - Fig Tree 132 kV | % of Rated A | 0.9559% | 0.9558% | 0.9556% | 0.9554% | 0.9552%
NQ-Collinsville | 7309_Stony Creek - Fig Tree 132 kV | Limiting Line Name | TR_LINE 67630_1 | TR_LINE 67630_1 | TR_LINE 67630_1 | TR_LINE 67630_1 | TR_LINE 67630_1
NQ-Collinsville | 7309_Stony Creek - Fig Tree 132 kV | Loading (A) | 4.3205 | 4.3203 | 4.3194 | 4.3185 | 4.3175
NQ-Collinsville | 7309_Stony Creek - Fig Tree 132 kV | Loading (MVA) | 1.0528 | 1.0527 | 1.0523 | 1.0518 | 1.0512
NQ-Collinsville | 7309_Stony Creek - Fig Tree 132 kV | Loading (MW) | 0.29422 | 0.29422 | 0.29422 | 0.29422 | 0.29422
NQ-Collinsville | 7309_Stony Creek - Fig Tree 132 kV | Power Factor | 0.27946 | 0.27948 | 0.2796 | 0.27973 | 0.27988
NQ-Collinsville | 7309_Stony Creek - Fig Tree 132 kV | Rating (A) | 452 | 452 | 452 | 452 | 452
NQ-Collinsville | 7309_Stony Creek - Fig Tree 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Collinsville | 7309_Stony Creek - Fig Tree 132 kV | Min Voltage at Constrained Conductor | 140.6892 | 140.6819 | 140.6491 | 140.6138 | 140.5742
NQ-Collinsville | 7309_Stony Creek - Fig Tree 132 kV | Contingency Outage | 6308_Merinda - Abbot Point 66 kV | 6308_Merinda - Abbot Point 66 kV | 6308_Merinda - Abbot Point 66 kV | 6308_Merinda - Abbot Point 66 kV | 6308_Merinda - Abbot Point 66 kV
NQ-Collinsville | COLL-02 Collinsville No 2 (33 kV) | % of Rated A | 2.672% | 2.674% | 2.674% | 2.674% | 2.674%
NQ-Collinsville | COLL-02 Collinsville No 2 (33 kV) | Limiting Line Name | HV_LINE 2010332_1 | HV_LINE 2010332_1 | HV_LINE 2010332_1 | HV_LINE 2010332_1 | HV_LINE 2010332_1
NQ-Collinsville | COLL-02 Collinsville No 2 (33 kV) | Loading (A) | 5.211 | 5.2136 | 5.2142 | 5.2136 | 5.2138
NQ-Collinsville | COLL-02 Collinsville No 2 (33 kV) | Loading (MVA) | 0.31323 | 0.31354 | 0.31362 | 0.31355 | 0.31357
NQ-Collinsville | COLL-02 Collinsville No 2 (33 kV) | Loading (MW) | 0.00049845 | 0.00049888 | 0.00049906 | 0.00049895 | 0.00049897
NQ-Collinsville | COLL-02 Collinsville No 2 (33 kV) | Power Factor | 0.0015175 | 0.0015173 | 0.0015174 | 0.0015174 | 0.0015174
NQ-Collinsville | COLL-02 Collinsville No 2 (33 kV) | Rating (A) | 195 | 195 | 195 | 195 | 195
NQ-Collinsville | COLL-02 Collinsville No 2 (33 kV) | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Collinsville | COLL-02 Collinsville No 2 (33 kV) | Min Voltage at Constrained Conductor | 34.7043 | 34.7212 | 34.7258 | 34.7218 | 34.7229
NQ-Collinsville | COLL-02 Collinsville No 2 (33 kV) | Contingency Outage | 3001 Collinsville No 1 33 kV | 3001 Collinsville No 1 33 kV | 3001 Collinsville No 1 33 kV | 3001 Collinsville No 1 33 kV | 3001 Collinsville No 1 33 kV
NQ-Ingham | 6321_Lucinda 66 kV | % of Rated A | 1.381% | 1.417% | 1.463% | 1.517% | 1.568%
NQ-Ingham | 6321_Lucinda 66 kV | Limiting Line Name | TR_LINE 135526_1 | TR_LINE 135526_1 | TR_LINE 135526_1 | TR_LINE 135526_1 | TR_LINE 135526_1
NQ-Ingham | 6321_Lucinda 66 kV | Loading (A) | 2.7476 | 2.8189 | 2.9116 | 3.0191 | 3.1205
NQ-Ingham | 6321_Lucinda 66 kV | Loading (MVA) | 0.32593 | 0.33448 | 0.34488 | 0.35756 | 0.36949
NQ-Ingham | 6321_Lucinda 66 kV | Loading (MW) | 0.036401 | 0.083344 | 0.12115 | 0.15387 | 0.1802
NQ-Ingham | 6321_Lucinda 66 kV | Power Factor | 0.11168 | 0.24918 | 0.35128 | 0.43034 | 0.48769
NQ-Ingham | 6321_Lucinda 66 kV | Rating (A) | 199 | 199 | 199 | 199 | 199
NQ-Ingham | 6321_Lucinda 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Ingham | 6321_Lucinda 66 kV | Min Voltage at Constrained Conductor | 68.4872 | 68.5055 | 68.3863 | 68.3764 | 68.3625
NQ-Ingham | 6321_Lucinda 66 kV | Contingency Outage | 6325_Oonoonba-Stuart 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV
NQ-Ingham | 6322 66kV VICTORIA SUGAR MILL FDR | % of Rated A | 1.199e-08% | 1.199e-08% | 1.196e-08% | 1.196e-08% | 1.196e-08%
NQ-Ingham | 6322 66kV VICTORIA SUGAR MILL FDR | Limiting Line Name | Line | Line | Line | Line | Line
NQ-Ingham | 6322 66kV VICTORIA SUGAR MILL FDR | Loading (A) | 5.993e-07 | 5.9927e-07 | 5.9823e-07 | 5.9814e-07 | 5.9802e-07
NQ-Ingham | 6322 66kV VICTORIA SUGAR MILL FDR | Loading (MVA) | 1.1852e-08 | 1.1851e-08 | 1.181e-08 | 1.1806e-08 | 1.1802e-08
NQ-Ingham | 6322 66kV VICTORIA SUGAR MILL FDR | Loading (MW) | 1.1852e-08 | 1.1851e-08 | 1.181e-08 | 1.1806e-08 | 1.1802e-08
NQ-Ingham | 6322 66kV VICTORIA SUGAR MILL FDR | Power Factor | 1 | 1 | 1 | 1 | 1
NQ-Ingham | 6322 66kV VICTORIA SUGAR MILL FDR | Rating (A) | 5000 | 5000 | 5000 | 5000 | 5000
NQ-Ingham | 6322 66kV VICTORIA SUGAR MILL FDR | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Ingham | 6322 66kV VICTORIA SUGAR MILL FDR | Min Voltage at Constrained Conductor | 11.4182 | 11.4176 | 11.3977 | 11.3961 | 11.3937
NQ-Ingham | 6322 66kV VICTORIA SUGAR MILL FDR | Contingency Outage | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV
NQ-Ingham | IN-GR_Ingham-Black River/Greenvale 66 kV | % of Rated A | 22.84% | 22.84% | 22.8% | 22.8% | 22.8%
NQ-Ingham | IN-GR_Ingham-Black River/Greenvale 66 kV | Limiting Line Name | TR_LINE 217286_1 | TR_LINE 217286_1 | TR_LINE 217286_1 | TR_LINE 217286_1 | TR_LINE 217286_1
NQ-Ingham | IN-GR_Ingham-Black River/Greenvale 66 kV | Loading (A) | 15.7622 | 15.7595 | 15.7347 | 15.732 | 15.7288
NQ-Ingham | IN-GR_Ingham-Black River/Greenvale 66 kV | Loading (MVA) | 1.8853 | 1.8849 | 1.8792 | 1.8786 | 1.878
NQ-Ingham | IN-GR_Ingham-Black River/Greenvale 66 kV | Loading (MW) | 0.099428 | 0.088666 | 0.080632 | 0.074324 | 0.069458
NQ-Ingham | IN-GR_Ingham-Black River/Greenvale 66 kV | Power Factor | 0.052733 | 0.047033 | 0.042901 | 0.039555 | 0.036977
NQ-Ingham | IN-GR_Ingham-Black River/Greenvale 66 kV | Rating (A) | 69 | 69 | 69 | 69 | 69
NQ-Ingham | IN-GR_Ingham-Black River/Greenvale 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Ingham | IN-GR_Ingham-Black River/Greenvale 66 kV | Min Voltage at Constrained Conductor | 69.056 | 69.0545 | 68.952 | 68.9447 | 68.9339
NQ-Ingham | IN-GR_Ingham-Black River/Greenvale 66 kV | Contingency Outage | IN-VC-1_Ingham-Victoria No 1 66 kV | IN-VC-1_Ingham-Victoria No 1 66 kV | IN-VC-1_Ingham-Victoria No 1 66 kV | IN-VC-1_Ingham-Victoria No 1 66 kV | IN-VC-1_Ingham-Victoria No 1 66 kV
NQ-Ingham | IN-LA-1_Ingham-Lannercost No 1 66 kV | % of Rated A | 1.344% | 1.308% | 1.291% | 1.285% | 1.283%
NQ-Ingham | IN-LA-1_Ingham-Lannercost No 1 66 kV | Limiting Line Name | TR_LINE 31685_1 | TR_LINE 31685_1 | TR_LINE 31685_1 | TR_LINE 31685_1 | TR_LINE 31685_1
NQ-Ingham | IN-LA-1_Ingham-Lannercost No 1 66 kV | Loading (A) | 2.6212 | 2.5504 | 2.5168 | 2.5049 | 2.5009
NQ-Ingham | IN-LA-1_Ingham-Lannercost No 1 66 kV | Loading (MVA) | 0.31251 | 0.30404 | 0.29957 | 0.29809 | 0.29755
NQ-Ingham | IN-LA-1_Ingham-Lannercost No 1 66 kV | Loading (MW) | 0.092208 | 0.057113 | 0.033066 | 0.016294 | 0.004163
NQ-Ingham | IN-LA-1_Ingham-Lannercost No 1 66 kV | Power Factor | 0.29505 | 0.18785 | 0.11038 | 0.05466 | 0.013991
NQ-Ingham | IN-LA-1_Ingham-Lannercost No 1 66 kV | Rating (A) | 195 | 195 | 195 | 195 | 195
NQ-Ingham | IN-LA-1_Ingham-Lannercost No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Ingham | IN-LA-1_Ingham-Lannercost No 1 66 kV | Min Voltage at Constrained Conductor | 68.8345 | 68.827 | 68.7191 | 68.7064 | 68.6904
NQ-Ingham | IN-LA-1_Ingham-Lannercost No 1 66 kV | Contingency Outage | IN-VC-1_Ingham-Victoria No 1 66 kV | IN-VC-1_Ingham-Victoria No 1 66 kV | IN-VC-1_Ingham-Victoria No 1 66 kV | IN-VC-1_Ingham-Victoria No 1 66 kV | IN-VC-1_Ingham-Victoria No 1 66 kV
NQ-Ingham | IN-VC-1_Ingham-Victoria No 1 66 kV | % of Rated A | 27.19% | 27.15% | 27.19% | 27.19% | 27.2%
NQ-Ingham | IN-VC-1_Ingham-Victoria No 1 66 kV | Limiting Line Name | TR_LINE 31692_2 | TR_LINE 31692_2 | TR_LINE 31692_2 | TR_LINE 31692_2 | TR_LINE 31692_2
NQ-Ingham | IN-VC-1_Ingham-Victoria No 1 66 kV | Loading (A) | 54.1129 | 54.0208 | 54.1063 | 54.1161 | 54.1285
NQ-Ingham | IN-VC-1_Ingham-Victoria No 1 66 kV | Loading (MVA) | 6.4049 | 6.4296 | 6.4297 | 6.4297 | 6.4297
NQ-Ingham | IN-VC-1_Ingham-Victoria No 1 66 kV | Loading (MW) | 6.3929 | 6.4292 | 6.4293 | 6.4293 | 6.4293
NQ-Ingham | IN-VC-1_Ingham-Victoria No 1 66 kV | Power Factor | 0.99813 | 0.99993 | 0.99994 | 0.99994 | 0.99994
NQ-Ingham | IN-VC-1_Ingham-Victoria No 1 66 kV | Rating (A) | 199 | 199 | 199 | 199 | 199
NQ-Ingham | IN-VC-1_Ingham-Victoria No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Ingham | IN-VC-1_Ingham-Victoria No 1 66 kV | Min Voltage at Constrained Conductor | 68.3351 | 68.7152 | 68.6077 | 68.5955 | 68.5799
NQ-Ingham | IN-VC-1_Ingham-Victoria No 1 66 kV | Contingency Outage | IN-GR_Ingham-Black River/Greenvale 66 kV | 6321_Lucinda 66 kV | 6321_Lucinda 66 kV | 6321_Lucinda 66 kV | 6321_Lucinda 66 kV
NQ-Ingham | MACN-02_Macknade Mill 11 kV | % of Rated A | 0.07059% | 0.07014% | 0.0705% | 0.0705% | 0.07049%
NQ-Ingham | MACN-02_Macknade Mill 11 kV | Limiting Line Name | HV_CABLE MACN-02 12148046 | HV_CABLE MACN-02 12148046 | HV_CABLE MACN-02 12148046 | HV_CABLE MACN-02 12148046 | HV_CABLE MACN-02 12148046
NQ-Ingham | MACN-02_Macknade Mill 11 kV | Loading (A) | 0.28238 | 0.28054 | 0.28201 | 0.28198 | 0.28194
NQ-Ingham | MACN-02_Macknade Mill 11 kV | Loading (MVA) | 0.0054484 | 0.0053778 | 0.0054341 | 0.0054332 | 0.0054316
NQ-Ingham | MACN-02_Macknade Mill 11 kV | Loading (MW) | 0.00010741 | 0.00010602 | 0.00010713 | 0.00010711 | 0.00010708
NQ-Ingham | MACN-02_Macknade Mill 11 kV | Power Factor | 0.019005 | 0.019005 | 0.019005 | 0.019005 | 0.019005
NQ-Ingham | MACN-02_Macknade Mill 11 kV | Rating (A) | 400 | 400 | 400 | 400 | 400
NQ-Ingham | MACN-02_Macknade Mill 11 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Ingham | MACN-02_Macknade Mill 11 kV | Min Voltage at Constrained Conductor | 11.1399 | 11.0675 | 11.1253 | 11.1243 | 11.1226
NQ-Ingham | MACN-02_Macknade Mill 11 kV | Contingency Outage | 6325_Oonoonba-Stuart 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV
NQ-King Creek | 7307_King Creek - Blue Valley 132 kV | % of Rated A | 0.9529% | 0.9529% | 0.9527% | 0.9526% | 0.9524%
NQ-King Creek | 7307_King Creek - Blue Valley 132 kV | Limiting Line Name | TR_LINE 62480_2 | TR_LINE 62480_2 | TR_LINE 62480_2 | TR_LINE 62480_2 | TR_LINE 62480_2
NQ-King Creek | 7307_King Creek - Blue Valley 132 kV | Loading (A) | 4.3071 | 4.307 | 4.3064 | 4.3057 | 4.3048
NQ-King Creek | 7307_King Creek - Blue Valley 132 kV | Loading (MVA) | 1.052 | 1.052 | 1.0517 | 1.0513 | 1.0509
NQ-King Creek | 7307_King Creek - Blue Valley 132 kV | Loading (MW) | 0.0023114 | 0.0023114 | 0.0023114 | 0.0023114 | 0.0023113
NQ-King Creek | 7307_King Creek - Blue Valley 132 kV | Power Factor | 0.0021971 | 0.0021972 | 0.0021978 | 0.0021985 | 0.0021995
NQ-King Creek | 7307_King Creek - Blue Valley 132 kV | Rating (A) | 452 | 452 | 452 | 452 | 452
NQ-King Creek | 7307_King Creek - Blue Valley 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-King Creek | 7307_King Creek - Blue Valley 132 kV | Min Voltage at Constrained Conductor | 141.0168 | 141.0145 | 140.9944 | 140.9717 | 140.9412
NQ-King Creek | 7307_King Creek - Blue Valley 132 kV | Contingency Outage | 6308_Merinda - Abbot Point 66 kV | 6308_Merinda - Abbot Point 66 kV | 6308_Merinda - Abbot Point 66 kV | 6308_Merinda - Abbot Point 66 kV | 6308_Merinda - Abbot Point 66 kV
NQ-MK-Proserpine Bowen | 118_Cannonvale No 2 66 kV | % of Rated A | 45.91% | 28.23% | 31.45% | 35.98% | 41.86%
NQ-MK-Proserpine Bowen | 118_Cannonvale No 2 66 kV | Limiting Line Name | TR_CABLE 7280_1 | TR_CABLE 7280_1 | TR_CABLE 7280_1 | TR_CABLE 7280_1 | TR_CABLE 7280_1
NQ-MK-Proserpine Bowen | 118_Cannonvale No 2 66 kV | Loading (A) | 88.6146 | 54.4792 | 60.7059 | 69.4448 | 80.787
NQ-MK-Proserpine Bowen | 118_Cannonvale No 2 66 kV | Loading (MVA) | 10.3074 | 6.3699 | 7.1125 | 8.1232 | 9.466
NQ-MK-Proserpine Bowen | 118_Cannonvale No 2 66 kV | Loading (MW) | 0.42111 | 2.0122 | 3.7697 | 5.5583 | 7.4843
NQ-MK-Proserpine Bowen | 118_Cannonvale No 2 66 kV | Power Factor | 0.04039 | 0.31517 | 0.52936 | 0.68367 | 0.79015
NQ-MK-Proserpine Bowen | 118_Cannonvale No 2 66 kV | Rating (A) | 193 | 193 | 193 | 193 | 193
NQ-MK-Proserpine Bowen | 118_Cannonvale No 2 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-MK-Proserpine Bowen | 118_Cannonvale No 2 66 kV | Min Voltage at Constrained Conductor | 67.1556 | 67.5055 | 67.6446 | 67.5344 | 67.6495
NQ-MK-Proserpine Bowen | 118_Cannonvale No 2 66 kV | Contingency Outage | 6308_Merinda - Abbot Point 66 kV | 426_Mt Rooper 66 kV | 426_Mt Rooper 66 kV | 426_Mt Rooper 66 kV | 426_Mt Rooper 66 kV
NQ-MK-Proserpine Bowen | 119_Cannonvale No 1 66 kV | % of Rated A | 28.78% | 30.27% | 34.41% | 39.85% | 46.63%
NQ-MK-Proserpine Bowen | 119_Cannonvale No 1 66 kV | Limiting Line Name | TR_LINE 13015_1 | TR_LINE 13015_1 | TR_LINE 13015_1 | TR_LINE 13015_1 | TR_LINE 13015_1
NQ-MK-Proserpine Bowen | 119_Cannonvale No 1 66 kV | Loading (A) | 53.2511 | 56.0042 | 63.6665 | 73.7275 | 86.2708
NQ-MK-Proserpine Bowen | 119_Cannonvale No 1 66 kV | Loading (MVA) | 6.1191 | 6.5639 | 7.4807 | 8.6525 | 10.1493
NQ-MK-Proserpine Bowen | 119_Cannonvale No 1 66 kV | Loading (MW) | 5.8787 | 2.7306 | 4.5629 | 6.4288 | 8.4412
NQ-MK-Proserpine Bowen | 119_Cannonvale No 1 66 kV | Power Factor | 0.96071 | 0.41557 | 0.60946 | 0.74242 | 0.83127
NQ-MK-Proserpine Bowen | 119_Cannonvale No 1 66 kV | Rating (A) | 185 | 185 | 185 | 185 | 185
NQ-MK-Proserpine Bowen | 119_Cannonvale No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-MK-Proserpine Bowen | 119_Cannonvale No 1 66 kV | Min Voltage at Constrained Conductor | 66.3289 | 67.6676 | 67.8375 | 67.7567 | 67.9023
NQ-MK-Proserpine Bowen | 119_Cannonvale No 1 66 kV | Contingency Outage | ME-BN-1_Merinda - Bowen No 1 66 kV | 426_Mt Rooper 66 kV | 426_Mt Rooper 66 kV | 426_Mt Rooper 66 kV | 426_Mt Rooper 66 kV
NQ-MK-Proserpine Bowen | 120_Prosperpine - Calen 66 kV | % of Rated A | 10.58% | 11.99% | 13.24% | 14.34% | 15.44%
NQ-MK-Proserpine Bowen | 120_Prosperpine - Calen 66 kV | Limiting Line Name | TR_LINE 89457_1 | TR_LINE 89457_1 | TR_LINE 89457_1 | TR_LINE 89457_1 | TR_LINE 89457_1
NQ-MK-Proserpine Bowen | 120_Prosperpine - Calen 66 kV | Loading (A) | 13.9637 | 15.8206 | 17.4799 | 18.9334 | 20.3783
NQ-MK-Proserpine Bowen | 120_Prosperpine - Calen 66 kV | Loading (MVA) | 1.6071 | 1.8185 | 2.0099 | 2.1945 | 2.3664
NQ-MK-Proserpine Bowen | 120_Prosperpine - Calen 66 kV | Loading (MW) | 1.2257 | 1.4954 | 1.7241 | 1.9284 | 2.1214
NQ-MK-Proserpine Bowen | 120_Prosperpine - Calen 66 kV | Power Factor | 0.76268 | 0.82232 | 0.85781 | 0.87874 | 0.89646
NQ-MK-Proserpine Bowen | 120_Prosperpine - Calen 66 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
NQ-MK-Proserpine Bowen | 120_Prosperpine - Calen 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-MK-Proserpine Bowen | 120_Prosperpine - Calen 66 kV | Min Voltage at Constrained Conductor | 66.4476 | 66.3638 | 66.3847 | 66.9176 | 67.0437
NQ-MK-Proserpine Bowen | 120_Prosperpine - Calen 66 kV | Contingency Outage | ME-BN-1_Merinda - Bowen No 1 66 kV | 119_Cannonvale No 1 66 kV | 119_Cannonvale No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV
NQ-MK-Proserpine Bowen | 122_Daydream/South Molle 11 kV | % of Rated A | 2.417% | 2.44% | 2.453% | 2.459% | 2.462%
NQ-MK-Proserpine Bowen | 122_Daydream/South Molle 11 kV | Limiting Line Name | HV_LINE 2563705_1 | HV_LINE 2563705_1 | HV_LINE 2563705_1 | HV_LINE 2563705_1 | HV_LINE 2563705_1
NQ-MK-Proserpine Bowen | 122_Daydream/South Molle 11 kV | Loading (A) | 1.8854 | 1.9035 | 1.9134 | 1.9179 | 1.9207
NQ-MK-Proserpine Bowen | 122_Daydream/South Molle 11 kV | Loading (MVA) | 0.036311 | 0.037012 | 0.037396 | 0.037575 | 0.037681
NQ-MK-Proserpine Bowen | 122_Daydream/South Molle 11 kV | Loading (MW) | 0.00072767 | 0.00074172 | 0.00074942 | 0.000753 | 0.00075512
NQ-MK-Proserpine Bowen | 122_Daydream/South Molle 11 kV | Power Factor | 0.020029 | 0.020029 | 0.020029 | 0.020029 | 0.020029
NQ-MK-Proserpine Bowen | 122_Daydream/South Molle 11 kV | Rating (A) | 78 | 78 | 78 | 78 | 78
NQ-MK-Proserpine Bowen | 122_Daydream/South Molle 11 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-MK-Proserpine Bowen | 122_Daydream/South Molle 11 kV | Min Voltage at Constrained Conductor | 11.1191 | 11.2259 | 11.284 | 11.311 | 11.3269
NQ-MK-Proserpine Bowen | 122_Daydream/South Molle 11 kV | Contingency Outage | ME-BN-1_Merinda - Bowen No 1 66 kV | 125_Hayman Island 22 kV | 125_Hayman Island 22 kV | 6308_Merinda - Abbot Point 66 kV | 7182 Ross - Milchester
NQ-MK-Proserpine Bowen | 124_Hamilton Island 22 kV | % of Rated A | 1.58% | 1.596% | 1.604% | 1.607% | 1.61%
NQ-MK-Proserpine Bowen | 124_Hamilton Island 22 kV | Limiting Line Name | HV_LINE 136005_1 | HV_LINE 136005_1 | HV_LINE 136005_1 | HV_LINE 136005_1 | HV_LINE 136005_1
NQ-MK-Proserpine Bowen | 124_Hamilton Island 22 kV | Loading (A) | 1.2327 | 1.245 | 1.2513 | 1.2538 | 1.2555
NQ-MK-Proserpine Bowen | 124_Hamilton Island 22 kV | Loading (MVA) | 0.047416 | 0.048362 | 0.048858 | 0.049054 | 0.049184
NQ-MK-Proserpine Bowen | 124_Hamilton Island 22 kV | Loading (MW) | 0.00094784 | 0.00096674 | 0.00097667 | 0.00098058 | 0.00098319
NQ-MK-Proserpine Bowen | 124_Hamilton Island 22 kV | Power Factor | 0.01999 | 0.01999 | 0.01999 | 0.01999 | 0.01999
NQ-MK-Proserpine Bowen | 124_Hamilton Island 22 kV | Rating (A) | 78 | 78 | 78 | 78 | 78
NQ-MK-Proserpine Bowen | 124_Hamilton Island 22 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-MK-Proserpine Bowen | 124_Hamilton Island 22 kV | Min Voltage at Constrained Conductor | 22.2073 | 22.4277 | 22.5425 | 22.5876 | 22.6177
NQ-MK-Proserpine Bowen | 124_Hamilton Island 22 kV | Contingency Outage | ME-BN-1_Merinda - Bowen No 1 66 kV | 125_Hayman Island 22 kV | 125_Hayman Island 22 kV | 6308_Merinda - Abbot Point 66 kV | 7182 Ross - Milchester
NQ-MK-Proserpine Bowen | 125_Hayman Island 22 kV | % of Rated A | 48.71% | 48.31% | 48.05% | 47.98% | 47.84%
NQ-MK-Proserpine Bowen | 125_Hayman Island 22 kV | Limiting Line Name | HV_LINE 11597319_1 | HV_LINE 11597319_1 | HV_LINE 11597319_1 | HV_LINE 11597319_1 | HV_LINE 11597319_1
NQ-MK-Proserpine Bowen | 125_Hayman Island 22 kV | Loading (A) | 37.9942 | 37.6801 | 37.4814 | 37.4264 | 37.3138
NQ-MK-Proserpine Bowen | 125_Hayman Island 22 kV | Loading (MVA) | 1.4495 | 1.4491 | 1.4489 | 1.4489 | 1.4487
NQ-MK-Proserpine Bowen | 125_Hayman Island 22 kV | Loading (MW) | 1.4494 | 1.4491 | 1.4489 | 1.4488 | 1.4487
NQ-MK-Proserpine Bowen | 125_Hayman Island 22 kV | Power Factor | 0.99999 | 0.99999 | 0.99998 | 0.99998 | 0.99998
NQ-MK-Proserpine Bowen | 125_Hayman Island 22 kV | Rating (A) | 78 | 78 | 78 | 78 | 78
NQ-MK-Proserpine Bowen | 125_Hayman Island 22 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-MK-Proserpine Bowen | 125_Hayman Island 22 kV | Min Voltage at Constrained Conductor | 22.0129 | 22.1915 | 22.3062 | 22.3381 | 22.4037
NQ-MK-Proserpine Bowen | 125_Hayman Island 22 kV | Contingency Outage | 120_Prosperpine - Calen 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | 6308_Merinda - Abbot Point 66 kV
NQ-MK-Proserpine Bowen | 426_Mt Rooper 66 kV | % of Rated A | 22.79% | 21.92% | 21.46% | 21.04% | 20.47%
NQ-MK-Proserpine Bowen | 426_Mt Rooper 66 kV | Limiting Line Name | TR_LINE 97526_1 | TR_LINE 97526_1 | TR_LINE 97526_1 | TR_LINE 97526_1 | TR_LINE 97526_1
NQ-MK-Proserpine Bowen | 426_Mt Rooper 66 kV | Loading (A) | 56.7453 | 54.5769 | 53.4379 | 52.3904 | 50.977
NQ-MK-Proserpine Bowen | 426_Mt Rooper 66 kV | Loading (MVA) | 6.488 | 6.3961 | 6.2945 | 6.1796 | 6.0415
NQ-MK-Proserpine Bowen | 426_Mt Rooper 66 kV | Loading (MW) | 6.475 | 6.3812 | 6.2785 | 6.1631 | 6.0239
NQ-MK-Proserpine Bowen | 426_Mt Rooper 66 kV | Power Factor | 0.99801 | 0.99766 | 0.99747 | 0.99733 | 0.99709
NQ-MK-Proserpine Bowen | 426_Mt Rooper 66 kV | Rating (A) | 249 | 249 | 249 | 249 | 249
NQ-MK-Proserpine Bowen | 426_Mt Rooper 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-MK-Proserpine Bowen | 426_Mt Rooper 66 kV | Min Voltage at Constrained Conductor | 66.0109 | 67.6622 | 68.0058 | 68.0995 | 68.4236
NQ-MK-Proserpine Bowen | 426_Mt Rooper 66 kV | Contingency Outage | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV
NQ-MK-Proserpine Bowen | CANN_JUPO (Ex119&118) | % of Rated A |  | 15.54% | 12.7% | 10.05% | 12.61%
NQ-MK-Proserpine Bowen | CANN_JUPO (Ex119&118) | Limiting Line Name |  | TR_CABLE 17_1 | TR_CABLE 17_1 | TR_CABLE 17_1 | TR_CABLE 17_1
NQ-MK-Proserpine Bowen | CANN_JUPO (Ex119&118) | Loading (A) |  | 43.5127 | 35.5621 | 28.1415 | 35.3178
NQ-MK-Proserpine Bowen | CANN_JUPO (Ex119&118) | Loading (MVA) |  | 5.1019 | 4.1904 | 3.3653 | 4.2413
NQ-MK-Proserpine Bowen | CANN_JUPO (Ex119&118) | Loading (MW) |  | 4.8978 | 3.939 | 3.2337 | 4.1492
NQ-MK-Proserpine Bowen | CANN_JUPO (Ex119&118) | Power Factor |  | 0.95999 | 0.94 | 0.95625 | 0.97454
NQ-MK-Proserpine Bowen | CANN_JUPO (Ex119&118) | Rating (A) |  | 280 | 280 | 280 | 280
NQ-MK-Proserpine Bowen | CANN_JUPO (Ex119&118) | Time |  | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-MK-Proserpine Bowen | CANN_JUPO (Ex119&118) | Min Voltage at Constrained Conductor |  | 67.6913 | 68.0283 | 69.0432 | 69.3338
NQ-MK-Proserpine Bowen | CANN_JUPO (Ex119&118) | Contingency Outage |  | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | 426_Mt Rooper 66 kV | 426_Mt Rooper 66 kV
NQ-MK-Proserpine Bowen | ME-BN-1_Merinda - Bowen No 1 66 kV | % of Rated A | 29.89% | 30.25% | 30.72% | 31.25% | 31.86%
NQ-MK-Proserpine Bowen | ME-BN-1_Merinda - Bowen No 1 66 kV | Limiting Line Name | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1
NQ-MK-Proserpine Bowen | ME-BN-1_Merinda - Bowen No 1 66 kV | Loading (A) | 58.29 | 58.9807 | 59.8957 | 60.9438 | 62.1265
NQ-MK-Proserpine Bowen | ME-BN-1_Merinda - Bowen No 1 66 kV | Loading (MVA) | 6.8401 | 6.9317 | 7.0468 | 7.1763 | 7.3209
NQ-MK-Proserpine Bowen | ME-BN-1_Merinda - Bowen No 1 66 kV | Loading (MW) | 0.40707 | 1.0396 | 1.5737 | 2.0432 | 2.4853
NQ-MK-Proserpine Bowen | ME-BN-1_Merinda - Bowen No 1 66 kV | Power Factor | 0.059478 | 0.14995 | 0.22329 | 0.28467 | 0.33944
NQ-MK-Proserpine Bowen | ME-BN-1_Merinda - Bowen No 1 66 kV | Rating (A) | 195 | 195 | 195 | 195 | 195
NQ-MK-Proserpine Bowen | ME-BN-1_Merinda - Bowen No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-MK-Proserpine Bowen | ME-BN-1_Merinda - Bowen No 1 66 kV | Min Voltage at Constrained Conductor | 67.7495 | 67.8533 | 67.9257 | 67.9849 | 68.0346
NQ-MK-Proserpine Bowen | ME-BN-1_Merinda - Bowen No 1 66 kV | Contingency Outage | 6308_Merinda - Abbot Point 66 kV | 6308_Merinda - Abbot Point 66 kV | 6308_Merinda - Abbot Point 66 kV | 6308_Merinda - Abbot Point 66 kV | 6308_Merinda - Abbot Point 66 kV
NQ-MK-Proserpine Bowen | ME-PR-1_Merinda - Proserpine No 1 66 kV | % of Rated A | 8.169% | 11.54% | 11.42% | 8.239% | 9.138%
NQ-MK-Proserpine Bowen | ME-PR-1_Merinda - Proserpine No 1 66 kV | Limiting Line Name | TR_LINE 175214_1 | TR_LINE 175214_1 | TR_LINE 175214_1 | TR_LINE 175214_1 | TR_LINE 175214_1
NQ-MK-Proserpine Bowen | ME-PR-1_Merinda - Proserpine No 1 66 kV | Loading (A) | 15.7659 | 22.2693 | 22.0376 | 15.9005 | 17.6363
NQ-MK-Proserpine Bowen | ME-PR-1_Merinda - Proserpine No 1 66 kV | Loading (MVA) | 1.8339 | 2.5598 | 2.534 | 1.8599 | 2.0665
NQ-MK-Proserpine Bowen | ME-PR-1_Merinda - Proserpine No 1 66 kV | Loading (MW) | 1.5307 | 0.99658 | 0.96007 | 1.613 | 1.8603
NQ-MK-Proserpine Bowen | ME-PR-1_Merinda - Proserpine No 1 66 kV | Power Factor | 0.83465 | 0.38932 | 0.37888 | 0.86722 | 0.90022
NQ-MK-Proserpine Bowen | ME-PR-1_Merinda - Proserpine No 1 66 kV | Rating (A) | 193 | 193 | 193 | 193 | 193
NQ-MK-Proserpine Bowen | ME-PR-1_Merinda - Proserpine No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-MK-Proserpine Bowen | ME-PR-1_Merinda - Proserpine No 1 66 kV | Min Voltage at Constrained Conductor | 67.1565 | 66.3646 | 66.3855 | 67.5344 | 67.6494
NQ-MK-Proserpine Bowen | ME-PR-1_Merinda - Proserpine No 1 66 kV | Contingency Outage | 6308_Merinda - Abbot Point 66 kV | 119_Cannonvale No 1 66 kV | 119_Cannonvale No 1 66 kV | 426_Mt Rooper 66 kV | 426_Mt Rooper 66 kV
NQ-MK-Proserpine Bowen | PR-BN-1_Proserpine - Bowen No 1 66 kV | % of Rated A | 2.712% | 2.718% | 2.722% | 2.725% | 2.729%
NQ-MK-Proserpine Bowen | PR-BN-1_Proserpine - Bowen No 1 66 kV | Limiting Line Name | TR_LINE 175048_1 | TR_LINE 175048_1 | TR_LINE 175048_1 | TR_LINE 175048_1 | TR_LINE 175048_1
NQ-MK-Proserpine Bowen | PR-BN-1_Proserpine - Bowen No 1 66 kV | Loading (A) | 8.0276 | 8.0445 | 8.0569 | 8.0673 | 8.0764
NQ-MK-Proserpine Bowen | PR-BN-1_Proserpine - Bowen No 1 66 kV | Loading (MVA) | 0.94788 | 0.95188 | 0.95482 | 0.95728 | 0.95943
NQ-MK-Proserpine Bowen | PR-BN-1_Proserpine - Bowen No 1 66 kV | Loading (MW) | 0.0011189 | 0.0011236 | 0.0011271 | 0.00113 | 0.0011325
NQ-MK-Proserpine Bowen | PR-BN-1_Proserpine - Bowen No 1 66 kV | Power Factor | 0.0011794 | 0.0011794 | 0.0011794 | 0.0011794 | 0.0011794
NQ-MK-Proserpine Bowen | PR-BN-1_Proserpine - Bowen No 1 66 kV | Rating (A) | 296 | 296 | 296 | 296 | 296
NQ-MK-Proserpine Bowen | PR-BN-1_Proserpine - Bowen No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-MK-Proserpine Bowen | PR-BN-1_Proserpine - Bowen No 1 66 kV | Min Voltage at Constrained Conductor | 68.1722 | 68.3158 | 68.4214 | 68.5095 | 68.5863
NQ-MK-Proserpine Bowen | PR-BN-1_Proserpine - Bowen No 1 66 kV | Contingency Outage | 6308_Merinda - Abbot Point 66 kV | 6308_Merinda - Abbot Point 66 kV | 6308_Merinda - Abbot Point 66 kV | 6308_Merinda - Abbot Point 66 kV | 6308_Merinda - Abbot Point 66 kV
NQ-MK-Proserpine Bowen | PROS-KECR-1_Proserpine No 1 66 kV | % of Rated A | 5.133% | 6.32% | 7.32% | 8.138% | 8.951%
NQ-MK-Proserpine Bowen | PROS-KECR-1_Proserpine No 1 66 kV | Limiting Line Name | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1
NQ-MK-Proserpine Bowen | PROS-KECR-1_Proserpine No 1 66 kV | Loading (A) | 9.0848 | 11.1871 | 12.9559 | 14.4045 | 15.8427
NQ-MK-Proserpine Bowen | PROS-KECR-1_Proserpine No 1 66 kV | Loading (MVA) | 1.0456 | 1.2859 | 1.4897 | 1.6696 | 1.8397
NQ-MK-Proserpine Bowen | PROS-KECR-1_Proserpine No 1 66 kV | Loading (MW) | 1.0455 | 1.2858 | 1.4896 | 1.6694 | 1.8395
NQ-MK-Proserpine Bowen | PROS-KECR-1_Proserpine No 1 66 kV | Power Factor | 0.99996 | 0.99994 | 0.99991 | 0.99989 | 0.99987
NQ-MK-Proserpine Bowen | PROS-KECR-1_Proserpine No 1 66 kV | Rating (A) | 177 | 177 | 177 | 177 | 177
NQ-MK-Proserpine Bowen | PROS-KECR-1_Proserpine No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-MK-Proserpine Bowen | PROS-KECR-1_Proserpine No 1 66 kV | Min Voltage at Constrained Conductor | 66.4482 | 66.3645 | 66.3855 | 66.9184 | 67.0446
NQ-MK-Proserpine Bowen | PROS-KECR-1_Proserpine No 1 66 kV | Contingency Outage | ME-BN-1_Merinda - Bowen No 1 66 kV | 119_Cannonvale No 1 66 kV | 119_Cannonvale No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV
NQ-MK-Proserpine Bowen | PROS-KECR-2_Proserpine No 2 66 kV | % of Rated A | 10.26% | 12.63% | 14.63% | 16.26% | 17.89%
NQ-MK-Proserpine Bowen | PROS-KECR-2_Proserpine No 2 66 kV | Limiting Line Name | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1
NQ-MK-Proserpine Bowen | PROS-KECR-2_Proserpine No 2 66 kV | Loading (A) | 18.1603 | 22.3602 | 25.893 | 28.7855 | 31.6569
NQ-MK-Proserpine Bowen | PROS-KECR-2_Proserpine No 2 66 kV | Loading (MVA) | 2.0901 | 2.5703 | 2.9773 | 3.3365 | 3.6762
NQ-MK-Proserpine Bowen | PROS-KECR-2_Proserpine No 2 66 kV | Loading (MW) | 2.09 | 2.5701 | 2.9771 | 3.3361 | 3.6757
NQ-MK-Proserpine Bowen | PROS-KECR-2_Proserpine No 2 66 kV | Power Factor | 0.99996 | 0.99994 | 0.99991 | 0.99989 | 0.99987
NQ-MK-Proserpine Bowen | PROS-KECR-2_Proserpine No 2 66 kV | Rating (A) | 177 | 177 | 177 | 177 | 177
NQ-MK-Proserpine Bowen | PROS-KECR-2_Proserpine No 2 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-MK-Proserpine Bowen | PROS-KECR-2_Proserpine No 2 66 kV | Min Voltage at Constrained Conductor | 66.4485 | 66.3649 | 66.386 | 66.9191 | 67.0453
NQ-MK-Proserpine Bowen | PROS-KECR-2_Proserpine No 2 66 kV | Contingency Outage | ME-BN-1_Merinda - Bowen No 1 66 kV | 119_Cannonvale No 1 66 kV | 119_Cannonvale No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV
NQ-Mount Isa | 7018_Mica Creek C - Chumvale 220 kV | % of Rated A | 15.1% | 14.99% | 14.91% | 14.91% | 14.91%
NQ-Mount Isa | 7018_Mica Creek C - Chumvale 220 kV | Limiting Line Name | TR_LINE 3024_1 | TR_LINE 3024_1 | TR_LINE 3024_1 | TR_LINE 3024_1 | TR_LINE 3024_1
NQ-Mount Isa | 7018_Mica Creek C - Chumvale 220 kV | Loading (A) | 129.1428 | 128.1744 | 127.471 | 127.4712 | 127.473
NQ-Mount Isa | 7018_Mica Creek C - Chumvale 220 kV | Loading (MVA) | 51.8304 | 51.4451 | 53.0056 | 53.006 | 52.9499
NQ-Mount Isa | 7018_Mica Creek C - Chumvale 220 kV | Loading (MW) | 41.8875 | 41.3781 | 41.3242 | 41.3243 | 41.3249
NQ-Mount Isa | 7018_Mica Creek C - Chumvale 220 kV | Power Factor | 0.80816 | 0.80432 | 0.77962 | 0.77962 | 0.78045
NQ-Mount Isa | 7018_Mica Creek C - Chumvale 220 kV | Rating (A) | 855 | 855 | 855 | 855 | 855
NQ-Mount Isa | 7018_Mica Creek C - Chumvale 220 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Mount Isa | 7018_Mica Creek C - Chumvale 220 kV | Min Voltage at Constrained Conductor | 231.7147 | 231.7298 | 240.0764 | 240.0778 | 239.8203
NQ-Mount Isa | 7018_Mica Creek C - Chumvale 220 kV | Contingency Outage | MI-GP-1_Mica Creek C-Gunpowder 1 220 kV | MI-GP-1_Mica Creek C-Gunpowder 1 220 kV | CH-CC-1_Chumvale-Cloncurry 66 kV | CH-CC-1_Chumvale-Cloncurry 66 kV | CH-CC-1_Chumvale-Cloncurry 66 kV
NQ-Mount Isa | CH-CC-1_Chumvale-Cloncurry 66 kV | % of Rated A | 2.988% | 2.021% | 4.159% | 7.009% | 10.74%
NQ-Mount Isa | CH-CC-1_Chumvale-Cloncurry 66 kV | Limiting Line Name | TR_LINE 34857_1 | TR_LINE 172154_1 | TR_LINE 34531_1 | TR_LINE 34531_1 | TR_LINE 34857_1
NQ-Mount Isa | CH-CC-1_Chumvale-Cloncurry 66 kV | Loading (A) | 4.8702 | 3.2939 | 7.0702 | 11.9155 | 17.5066
NQ-Mount Isa | CH-CC-1_Chumvale-Cloncurry 66 kV | Loading (MVA) | 0.56601 | 0.3829 | 0.8225 | 1.3872 | 2.0299
NQ-Mount Isa | CH-CC-1_Chumvale-Cloncurry 66 kV | Loading (MW) | 0.54521 | 0.38289 | 0.82151 | 1.3868 | 2.0265
NQ-Mount Isa | CH-CC-1_Chumvale-Cloncurry 66 kV | Power Factor | 0.96326 | 0.99998 | 0.9988 | 0.99975 | 0.99829
NQ-Mount Isa | CH-CC-1_Chumvale-Cloncurry 66 kV | Rating (A) | 163 | 163 | 170 | 170 | 163
NQ-Mount Isa | CH-CC-1_Chumvale-Cloncurry 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Mount Isa | CH-CC-1_Chumvale-Cloncurry 66 kV | Min Voltage at Constrained Conductor | 67.0982 | 67.1144 | 67.1646 | 67.2142 | 66.9426
NQ-Mount Isa | CH-CC-1_Chumvale-Cloncurry 66 kV | Contingency Outage | MI-GP-1_Mica Creek C-Gunpowder 1 220 kV | MI-GP-1_Mica Creek C-Gunpowder 1 220 kV | MI-GP-1_Mica Creek C-Gunpowder 1 220 kV | MI-GP-1_Mica Creek C-Gunpowder 1 220 kV | MI-GP-1_Mica Creek C-Gunpowder 1 220 kV
NQ-Mount Isa | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | % of Rated A | 15.58% | 15.58% | 15.58% | 15.58% | 15.74%
NQ-Mount Isa | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Limiting Line Name | TR_LINE 234732_1 | TR_LINE 234732_1 | TR_LINE 234732_1 | TR_LINE 234732_1 | TR_LINE 234732_1
NQ-Mount Isa | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Loading (A) | 12.9285 | 12.9295 | 12.9303 | 12.9312 | 13.0654
NQ-Mount Isa | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Loading (MVA) | 1.6199 | 1.6201 | 1.6203 | 1.6205 | 1.6544
NQ-Mount Isa | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Loading (MW) | 0.10933 | 0.10933 | 0.10934 | 0.10934 | 0.10952
NQ-Mount Isa | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Power Factor | 0.067495 | 0.067486 | 0.067478 | 0.06747 | 0.066202
NQ-Mount Isa | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Rating (A) | 83 | 83 | 83 | 83 | 83
NQ-Mount Isa | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Mount Isa | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Min Voltage at Constrained Conductor | 72.3386 | 72.3437 | 72.3486 | 72.3533 | 73.1062
NQ-Mount Isa | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Contingency Outage | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV | _NNC
NQ-Mount Isa | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | % of Rated A | 1.34% | 1.101% | 0.9147% | 0.7687% | 0.6594%
NQ-Mount Isa | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Limiting Line Name | TR_LINE 174405_1 | TR_LINE 174405_1 | TR_LINE 174405_1 | TR_LINE 174405_1 | TR_LINE 174405_1
NQ-Mount Isa | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Loading (A) | 5.1473 | 4.2282 | 3.5124 | 2.9517 | 2.532
NQ-Mount Isa | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Loading (MVA) | 1.2226 | 1.0043 | 0.83433 | 0.70116 | 0.60967
NQ-Mount Isa | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Loading (MW) | 1.1397 | 0.90112 | 0.70629 | 0.54221 | 0.40345
NQ-Mount Isa | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Power Factor | 0.93221 | 0.89723 | 0.84654 | 0.7733 | 0.66175
NQ-Mount Isa | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Rating (A) | 384 | 384 | 384 | 384 | 384
NQ-Mount Isa | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Mount Isa | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Min Voltage at Constrained Conductor | 137.1331 | 137.1382 | 137.1432 | 137.1458 | 139.0209
NQ-Mount Isa | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Contingency Outage | MI-GP-1_Mica Creek C-Gunpowder 1 220 kV | MI-GP-1_Mica Creek C-Gunpowder 1 220 kV | MI-GP-1_Mica Creek C-Gunpowder 1 220 kV | MI-GP-1_Mica Creek C-Gunpowder 1 220 kV | MICC-MICB No 2 132 kV
NQ-Mount Isa | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | % of Rated A | 3.321% | 3.138% | 3.01% | 2.921% | 2.911%
NQ-Mount Isa | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Limiting Line Name | TR_LINE 174422_1 | TR_LINE 174422_1 | TR_LINE 174422_1 | TR_LINE 174422_1 | TR_LINE 174422_1
NQ-Mount Isa | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Loading (A) | 9.267 | 8.7545 | 8.3992 | 8.15 | 8.1206
NQ-Mount Isa | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Loading (MVA) | 2.2332 | 2.1098 | 2.0242 | 1.9643 | 1.9537
NQ-Mount Isa | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Loading (MW) | 1.2522 | 1.0136 | 0.81881 | 0.65473 | 0.51622
NQ-Mount Isa | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Power Factor | 0.56074 | 0.48045 | 0.4045 | 0.33332 | 0.26423
NQ-Mount Isa | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Rating (A) | 279 | 279 | 279 | 279 | 279
NQ-Mount Isa | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Mount Isa | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Min Voltage at Constrained Conductor | 139.1314 | 139.1372 | 139.1431 | 139.1493 | 138.8997
NQ-Mount Isa | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Contingency Outage | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV | _NNC
NQ-Mount Isa | MICC-MICB No 1 132 kV | % of Rated A | 73.44% | 73.29% | 73.13% | 72.93% | 72.63%
NQ-Mount Isa | MICC-MICB No 1 132 kV | Limiting Line Name | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1
NQ-Mount Isa | MICC-MICB No 1 132 kV | Loading (A) | 383.343 | 382.593 | 381.7211 | 380.686 | 379.1453
NQ-Mount Isa | MICC-MICB No 1 132 kV | Loading (MVA) | 92.3923 | 92.2152 | 92.0088 | 91.7633 | 91.3094
NQ-Mount Isa | MICC-MICB No 1 132 kV | Loading (MW) | 45.5696 | 45.06 | 44.4746 | 43.7889 | 42.9714
NQ-Mount Isa | MICC-MICB No 1 132 kV | Power Factor | 0.49316 | 0.48858 | 0.48332 | 0.47714 | 0.47056
NQ-Mount Isa | MICC-MICB No 1 132 kV | Rating (A) | 522 | 522 | 522 | 522 | 522
NQ-Mount Isa | MICC-MICB No 1 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Mount Isa | MICC-MICB No 1 132 kV | Min Voltage at Constrained Conductor | 139.1286 | 139.1342 | 139.1399 | 139.1459 | 139.0202
NQ-Mount Isa | MICC-MICB No 1 132 kV | Contingency Outage | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV
NQ-Mount Isa | MICC-MICB No 2 132 kV | % of Rated A | 73.42% | 73.28% | 73.11% | 72.91% | 72.62%
NQ-Mount Isa | MICC-MICB No 2 132 kV | Limiting Line Name | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1
NQ-Mount Isa | MICC-MICB No 2 132 kV | Loading (A) | 383.2628 | 382.512 | 381.6393 | 380.6033 | 379.0614
NQ-Mount Isa | MICC-MICB No 2 132 kV | Loading (MVA) | 92.3711 | 92.1939 | 91.9873 | 91.7415 | 91.2873
NQ-Mount Isa | MICC-MICB No 2 132 kV | Loading (MW) | 45.5688 | 45.0592 | 44.4738 | 43.7881 | 42.9706
NQ-Mount Isa | MICC-MICB No 2 132 kV | Power Factor | 0.49327 | 0.48869 | 0.48343 | 0.47725 | 0.47067
NQ-Mount Isa | MICC-MICB No 2 132 kV | Rating (A) | 522 | 522 | 522 | 522 | 522
NQ-Mount Isa | MICC-MICB No 2 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Mount Isa | MICC-MICB No 2 132 kV | Min Voltage at Constrained Conductor | 139.1278 | 139.1333 | 139.139 | 139.145 | 139.0192
NQ-Mount Isa | MICC-MICB No 2 132 kV | Contingency Outage | MICC-MICB No 1 132 kV | MICC-MICB No 1 132 kV | MICC-MICB No 1 132 kV | MICC-MICB No 1 132 kV | MICC-MICB No 1 132 kV
NQ-Townsville Burdekin West | 6127_Bohle-Black River 1 66 kV | % of Rated A | 15.85% | 21.78% | 27.64% | 34.1% | 41.14%
NQ-Townsville Burdekin West | 6127_Bohle-Black River 1 66 kV | Limiting Line Name | TR_LINE 162720_1 | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1
NQ-Townsville Burdekin West | 6127_Bohle-Black River 1 66 kV | Loading (A) | 115.5761 | 158.7537 | 201.4954 | 248.5595 | 299.9211
NQ-Townsville Burdekin West | 6127_Bohle-Black River 1 66 kV | Loading (MVA) | 13.8232 | 19.0496 | 24.4531 | 30.1836 | 36.4297
NQ-Townsville Burdekin West | 6127_Bohle-Black River 1 66 kV | Loading (MW) | 13.8226 | 19.0453 | 24.4284 | 30.1116 | 36.2696
NQ-Townsville Burdekin West | 6127_Bohle-Black River 1 66 kV | Power Factor | 0.99996 | 0.99977 | 0.99899 | 0.99761 | 0.9956
NQ-Townsville Burdekin West | 6127_Bohle-Black River 1 66 kV | Rating (A) | 729 | 729 | 729 | 729 | 729
NQ-Townsville Burdekin West | 6127_Bohle-Black River 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | 6127_Bohle-Black River 1 66 kV | Min Voltage at Constrained Conductor | 69.0518 | 69.279 | 70.0658 | 70.1099 | 70.1272
NQ-Townsville Burdekin West | 6127_Bohle-Black River 1 66 kV | Contingency Outage | 6266_Bohle-Black River No 2 66 kV | 6266_Bohle-Black River No 2 66 kV | 6266_Bohle-Black River No 2 66 kV | 6266_Bohle-Black River No 2 66 kV | 6266_Bohle-Black River No 2 66 kV
NQ-Townsville Burdekin West | 6266_Bohle-Black River No 2 66 kV | % of Rated A | 15.85% | 21.78% | 27.64% | 34.09% | 41.14%
NQ-Townsville Burdekin West | 6266_Bohle-Black River No 2 66 kV | Limiting Line Name | TR_LINE 96351_1 | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1
NQ-Townsville Burdekin West | 6266_Bohle-Black River No 2 66 kV | Loading (A) | 115.5738 | 158.7496 | 201.4882 | 248.5468 | 299.8997
NQ-Townsville Burdekin West | 6266_Bohle-Black River No 2 66 kV | Loading (MVA) | 13.8435 | 19.05 | 24.4536 | 30.1843 | 36.4304
NQ-Townsville Burdekin West | 6266_Bohle-Black River No 2 66 kV | Loading (MW) | 13.8429 | 19.0456 | 24.429 | 30.1125 | 36.2708
NQ-Townsville Burdekin West | 6266_Bohle-Black River No 2 66 kV | Power Factor | 0.99996 | 0.99977 | 0.99899 | 0.99761 | 0.99559
NQ-Townsville Burdekin West | 6266_Bohle-Black River No 2 66 kV | Rating (A) | 729 | 729 | 729 | 729 | 729
NQ-Townsville Burdekin West | 6266_Bohle-Black River No 2 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | 6266_Bohle-Black River No 2 66 kV | Min Voltage at Constrained Conductor | 69.0525 | 69.2797 | 70.0672 | 70.1121 | 70.1305
NQ-Townsville Burdekin West | 6266_Bohle-Black River No 2 66 kV | Contingency Outage | 6127_Bohle-Black River 1 66 kV | 6127_Bohle-Black River 1 66 kV | 6127_Bohle-Black River 1 66 kV | 6127_Bohle-Black River 1 66 kV | 6127_Bohle-Black River 1 66 kV
NQ-Townsville Burdekin West | 6299_Townsville Port 66 kV | % of Rated A | 18.85% | 17.74% | 10.71% | 9.259% | 7.937%
NQ-Townsville Burdekin West | 6299_Townsville Port 66 kV | Limiting Line Name | TR_LINE 96490_1 | TR_LINE 96490_1 | TR_LINE 96490_1 | TR_LINE 96490_1 | TR_LINE 96490_1
NQ-Townsville Burdekin West | 6299_Townsville Port 66 kV | Loading (A) | 205.8675 | 193.6665 | 116.9909 | 101.1084 | 86.6758
NQ-Townsville Burdekin West | 6299_Townsville Port 66 kV | Loading (MVA) | 24.5039 | 23.0459 | 14.106 | 12.1755 | 10.4342
NQ-Townsville Burdekin West | 6299_Townsville Port 66 kV | Loading (MW) | 15.617 | 13.6912 | 10.657 | 9.3137 | 7.2632
NQ-Townsville Burdekin West | 6299_Townsville Port 66 kV | Power Factor | 0.63733 | 0.59408 | 0.75549 | 0.76495 | 0.69609
NQ-Townsville Burdekin West | 6299_Townsville Port 66 kV | Rating (A) | 1092 | 1092 | 1092 | 1092 | 1092
NQ-Townsville Burdekin West | 6299_Townsville Port 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | 6299_Townsville Port 66 kV | Min Voltage at Constrained Conductor | 68.7201 | 68.703 | 69.6133 | 69.5247 | 69.5025
NQ-Townsville Burdekin West | 6299_Townsville Port 66 kV | Contingency Outage | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | ST-TOPO-1_Stuart-Townsville Port 66 kV | ST-TOPO-1_Stuart-Townsville Port 66 kV
NQ-Townsville Burdekin West | 6312_Merinda - Home Hill 66 kV | % of Rated A | 6.761% | 6.48% | 6.474% | 6.467% | 6.462%
NQ-Townsville Burdekin West | 6312_Merinda - Home Hill 66 kV | Limiting Line Name | TR_LINE 32515_1 | TR_LINE 180012_1 | TR_LINE 180012_1 | TR_LINE 180012_1 | TR_LINE 180012_1
NQ-Townsville Burdekin West | 6312_Merinda - Home Hill 66 kV | Loading (A) | 17.4441 | 11.3405 | 11.3288 | 11.3174 | 11.308
NQ-Townsville Burdekin West | 6312_Merinda - Home Hill 66 kV | Loading (MVA) | 2.0552 | 1.3401 | 1.3417 | 1.3435 | 1.3459
NQ-Townsville Burdekin West | 6312_Merinda - Home Hill 66 kV | Loading (MW) | 1.5039 | 1.0823 | 1.0817 | 1.0812 | 1.081
NQ-Townsville Burdekin West | 6312_Merinda - Home Hill 66 kV | Power Factor | 0.73173 | 0.80767 | 0.80622 | 0.80473 | 0.80318
NQ-Townsville Burdekin West | 6312_Merinda - Home Hill 66 kV | Rating (A) | 258 | 175 | 175 | 175 | 175
NQ-Townsville Burdekin West | 6312_Merinda - Home Hill 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | 6312_Merinda - Home Hill 66 kV | Min Voltage at Constrained Conductor | 68.0225 | 68.2246 | 68.3789 | 68.5382 | 68.7194
NQ-Townsville Burdekin West | 6312_Merinda - Home Hill 66 kV | Contingency Outage | GI-AY-1_Giru - Ayr 1 66 kV | GI-AY-1_Giru - Ayr 1 66 kV | GI-AY-1_Giru - Ayr 1 66 kV | GI-AY-1_Giru - Ayr 1 66 kV | GI-AY-1_Giru - Ayr 1 66 kV
NQ-Townsville Burdekin West | 6325_Oonoonba-Stuart 66 kV | % of Rated A | 20.54% | 16.56% | 16.41% | 14.73% | 16.95%
NQ-Townsville Burdekin West | 6325_Oonoonba-Stuart 66 kV | Limiting Line Name | TR_LINE 31738_1 | TR_LINE 31738_1 | TR_LINE 31738_1 | TR_LINE 31738_1 | TR_LINE 31738_1
NQ-Townsville Burdekin West | 6325_Oonoonba-Stuart 66 kV | Loading (A) | 66.754 | 53.8177 | 53.338 | 47.8635 | 55.0902
NQ-Townsville Burdekin West | 6325_Oonoonba-Stuart 66 kV | Loading (MVA) | 7.9741 | 6.429 | 6.4212 | 5.7613 | 6.6269
NQ-Townsville Burdekin West | 6325_Oonoonba-Stuart 66 kV | Loading (MW) | 5.4336 | 3.4198 | 4.988 | 4.1088 | 6.6268
NQ-Townsville Burdekin West | 6325_Oonoonba-Stuart 66 kV | Power Factor | 0.6814 | 0.53193 | 0.7768 | 0.71317 | 0.99999
NQ-Townsville Burdekin West | 6325_Oonoonba-Stuart 66 kV | Rating (A) | 325 | 325 | 325 | 325 | 325
NQ-Townsville Burdekin West | 6325_Oonoonba-Stuart 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | 6325_Oonoonba-Stuart 66 kV | Min Voltage at Constrained Conductor | 68.9675 | 68.9697 | 69.5058 | 69.4956 | 69.4484
NQ-Townsville Burdekin West | 6325_Oonoonba-Stuart 66 kV | Contingency Outage | GA-TP-1_Garbutt-Townsville Port 1 66 kV | GA-TP-1_Garbutt-Townsville Port 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | GA-HP-1_Garbutt-Hermit Park No 1 66 kV
NQ-Townsville Burdekin West | 6382 JACR-HUGH 132kV | % of Rated A | 42.39% | 44% | 41.72% | 40.74% | 39.77%
NQ-Townsville Burdekin West | 6382 JACR-HUGH 132kV | Limiting Line Name | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line
NQ-Townsville Burdekin West | 6382 JACR-HUGH 132kV | Loading (A) | 60.1965 | 62.4793 | 59.2372 | 57.8554 | 56.4784
NQ-Townsville Burdekin West | 6382 JACR-HUGH 132kV | Loading (MVA) | 7.0825 | 7.3539 | 6.9647 | 6.8034 | 6.6426
NQ-Townsville Burdekin West | 6382 JACR-HUGH 132kV | Loading (MW) | 0.21356 | 0.22032 | 3.9355 | 3.5943 | 3.2379
NQ-Townsville Burdekin West | 6382 JACR-HUGH 132kV | Power Factor | 0.020142 | 0.019555 | 0.56506 | 0.52831 | 0.48745
NQ-Townsville Burdekin West | 6382 JACR-HUGH 132kV | Rating (A) | 142 | 142 | 142 | 142 | 142
NQ-Townsville Burdekin West | 6382 JACR-HUGH 132kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | 6382 JACR-HUGH 132kV | Min Voltage at Constrained Conductor | 67.9285 | 67.9552 | 67.8811 | 67.8926 | 67.9037
NQ-Townsville Burdekin West | 6382 JACR-HUGH 132kV | Contingency Outage | 6383 CARI-CPRE 66kV | 6383 CARI-CPRE 66kV | CR-HU-1_Cape River-Hughenden No 1 66 kV | CR-HU-1_Cape River-Hughenden No 1 66 kV | CR-HU-1_Cape River-Hughenden No 1 66 kV
NQ-Townsville Burdekin West | 6383 CARI-CPRE 66kV | % of Rated A | 28.2% | 29.2% | 23.23% | 24.14% | 25%
NQ-Townsville Burdekin West | 6383 CARI-CPRE 66kV | Limiting Line Name | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1
NQ-Townsville Burdekin West | 6383 CARI-CPRE 66kV | Loading (A) | 87.9964 | 91.0892 | 72.4871 | 75.3087 | 77.9922
NQ-Townsville Burdekin West | 6383 CARI-CPRE 66kV | Loading (MVA) | 10.4009 | 10.7707 | 8.5509 | 8.8869 | 9.2068
NQ-Townsville Burdekin West | 6383 CARI-CPRE 66kV | Loading (MW) | 0.11272 | 0.11407 | 0.10676 | 0.10774 | 0.10872
NQ-Townsville Burdekin West | 6383 CARI-CPRE 66kV | Power Factor | 0.010794 | 0.010545 | 0.012449 | 0.012086 | 0.01177
NQ-Townsville Burdekin West | 6383 CARI-CPRE 66kV | Rating (A) | 312 | 312 | 312 | 312 | 312
NQ-Townsville Burdekin West | 6383 CARI-CPRE 66kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | 6383 CARI-CPRE 66kV | Min Voltage at Constrained Conductor | 68.2413 | 68.2681 | 68.1068 | 68.1313 | 68.1545
NQ-Townsville Burdekin West | 6383 CARI-CPRE 66kV | Contingency Outage | 6382 JACR-HUGH 132kV | 6382 JACR-HUGH 132kV | 6382 JACR-HUGH 132kV | 6382 JACR-HUGH 132kV | 6382 JACR-HUGH 132kV
NQ-Townsville Burdekin West | 7182 Ross - Milchester | % of Rated A | 30.71% | 30.01% | 31.8% | 31.08% | 30.34%
NQ-Townsville Burdekin West | 7182 Ross - Milchester | Limiting Line Name | TR_LINE 31626_1 | TR_LINE 31626_1 | TR_LINE 31626_1 | TR_LINE 31626_1 | TR_LINE 31626_1
NQ-Townsville Burdekin West | 7182 Ross - Milchester | Loading (A) | 102.2662 | 99.9171 | 105.8939 | 103.5067 | 101.0282
NQ-Townsville Burdekin West | 7182 Ross - Milchester | Loading (MVA) | 24.5579 | 23.9933 | 25.4219 | 24.848 | 24.2521
NQ-Townsville Burdekin West | 7182 Ross - Milchester | Loading (MW) | 16.0369 | 15.1477 | 16.7825 | 15.9945 | 15.1833
NQ-Townsville Burdekin West | 7182 Ross - Milchester | Power Factor | 0.65302 | 0.63133 | 0.66016 | 0.64369 | 0.62606
NQ-Townsville Burdekin West | 7182 Ross - Milchester | Rating (A) | 333 | 333 | 333 | 333 | 333
NQ-Townsville Burdekin West | 7182 Ross - Milchester | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | 7182 Ross - Milchester | Min Voltage at Constrained Conductor | 138.6433 | 138.6405 | 138.6041 | 138.5997 | 138.5943
NQ-Townsville Burdekin West | 7182 Ross - Milchester | Contingency Outage | ST-WO-1_Stuart-Woodstock South 1 66 kV | ST-WO-1_Stuart-Woodstock South 1 66 kV | ST-WO-1_Stuart-Woodstock South 1 66 kV | ST-WO-1_Stuart-Woodstock South 1 66 kV | ST-WO-1_Stuart-Woodstock South 1 66 kV
NQ-Townsville Burdekin West | 7460 CPRE-JACR 132kV | % of Rated A | 23.53% | 23.65% | 22% | 21.42% | 20.85%
NQ-Townsville Burdekin West | 7460 CPRE-JACR 132kV | Limiting Line Name | TR_LINE 51339257_1 | TR_LINE 51339257_1 | TR_LINE 51339257_1 | TR_LINE 51339257_1 | TR_LINE 51339257_1
NQ-Townsville Burdekin West | 7460 CPRE-JACR 132kV | Loading (A) | 40.7115 | 40.914 | 38.0589 | 37.0652 | 36.0679
NQ-Townsville Burdekin West | 7460 CPRE-JACR 132kV | Loading (MVA) | 9.6079 | 9.6565 | 8.9662 | 8.7321 | 8.4971
NQ-Townsville Burdekin West | 7460 CPRE-JACR 132kV | Loading (MW) | 0.051072 | 0.051188 | 4.0296 | 3.6838 | 3.3229
NQ-Townsville Burdekin West | 7460 CPRE-JACR 132kV | Power Factor | 0.0050157 | 0.0049995 | 0.44942 | 0.42187 | 0.39106
NQ-Townsville Burdekin West | 7460 CPRE-JACR 132kV | Rating (A) | 173 | 173 | 173 | 173 | 173
NQ-Townsville Burdekin West | 7460 CPRE-JACR 132kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | 7460 CPRE-JACR 132kV | Min Voltage at Constrained Conductor | 136.2541 | 136.2657 | 136.0164 | 136.0165 | 136.015
NQ-Townsville Burdekin West | 7460 CPRE-JACR 132kV | Contingency Outage | 6383 CARI-CPRE 66kV | 6383 CARI-CPRE 66kV | CR-HU-1_Cape River-Hughenden No 1 66 kV | CR-HU-1_Cape River-Hughenden No 1 66 kV | CR-HU-1_Cape River-Hughenden No 1 66 kV
NQ-Townsville Burdekin West | AV-CB-1_Aitkenvale-Cranbrook 66 kV | % of Rated A | 14.72% | 18.02% | 17.79% | 20.71% | 23.82%
NQ-Townsville Burdekin West | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Limiting Line Name | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1
NQ-Townsville Burdekin West | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Loading (A) | 49.0292 | 60.0097 | 59.2564 | 68.9663 | 79.3356
NQ-Townsville Burdekin West | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Loading (MVA) | 5.8547 | 7.1684 | 7.1523 | 8.3246 | 9.575
NQ-Townsville Burdekin West | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Loading (MW) | 4.1983 | 5.5638 | 7.1416 | 8.3236 | 9.5454
NQ-Townsville Burdekin West | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Power Factor | 0.71709 | 0.77616 | 0.99849 | 0.99988 | 0.99691
NQ-Townsville Burdekin West | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Rating (A) | 333 | 333 | 333 | 333 | 333
NQ-Townsville Burdekin West | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Min Voltage at Constrained Conductor | 68.9423 | 68.9664 | 69.6834 | 69.6851 | 69.6756
NQ-Townsville Burdekin West | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Contingency Outage | GA-BO-1_Garbutt-Bohle No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV
NQ-Townsville Burdekin West | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | % of Rated A | 16.48% | 16.02% | 15.73% | 15.73% | 17.45%
NQ-Townsville Burdekin West | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Limiting Line Name | TR_LINE 34618_1 | TR_LINE 34618_1 | TR_LINE 34618_1 | TR_LINE 34618_1 | TR_LINE 34618_1
NQ-Townsville Burdekin West | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Loading (A) | 75.8011 | 73.6987 | 72.3397 | 72.3593 | 80.2768
NQ-Townsville Burdekin West | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Loading (MVA) | 9.0739 | 8.8262 | 8.7256 | 8.7294 | 9.6606
NQ-Townsville Burdekin West | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Loading (MW) | 2.645 | 1.4803 | 0.48027 | 0.43792 | 9.2426
NQ-Townsville Burdekin West | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Power Factor | 0.2915 | 0.16767 | 0.054931 | 0.050024 | 0.9566
NQ-Townsville Burdekin West | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Rating (A) | 460 | 460 | 460 | 460 | 460
NQ-Townsville Burdekin West | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Min Voltage at Constrained Conductor | 69.1129 | 69.1439 | 69.6401 | 69.6514 | 69.4767
NQ-Townsville Burdekin West | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Contingency Outage | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV
NQ-Townsville Burdekin West | AY-EA-1_Ayr - East Ayr No 1 66 kV | % of Rated A | 12.79% | 12.24% | 11.66% | 11.07% | 11.7%
NQ-Townsville Burdekin West | AY-EA-1_Ayr - East Ayr No 1 66 kV | Limiting Line Name | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1
NQ-Townsville Burdekin West | AY-EA-1_Ayr - East Ayr No 1 66 kV | Loading (A) | 33.1316 | 31.6954 | 30.2099 | 28.6654 | 30.2996
NQ-Townsville Burdekin West | AY-EA-1_Ayr - East Ayr No 1 66 kV | Loading (MVA) | 3.904 | 3.7416 | 3.5726 | 3.3953 | 3.6175
NQ-Townsville Burdekin West | AY-EA-1_Ayr - East Ayr No 1 66 kV | Loading (MW) | 3.5536 | 3.3753 | 3.1858 | 2.9844 | 2.4678
NQ-Townsville Burdekin West | AY-EA-1_Ayr - East Ayr No 1 66 kV | Power Factor | 0.90995 | 0.90181 | 0.89147 | 0.87873 | 0.68193
NQ-Townsville Burdekin West | AY-EA-1_Ayr - East Ayr No 1 66 kV | Rating (A) | 259 | 259 | 259 | 259 | 259
NQ-Townsville Burdekin West | AY-EA-1_Ayr - East Ayr No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | AY-EA-1_Ayr - East Ayr No 1 66 kV | Min Voltage at Constrained Conductor | 68.0315 | 68.1562 | 68.2775 | 68.3848 | 68.9312
NQ-Townsville Burdekin West | AY-EA-1_Ayr - East Ayr No 1 66 kV | Contingency Outage | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | EAAY_Clare South - East Ayr 66 kV
NQ-Townsville Burdekin West | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | % of Rated A | 19.28% | 18.24% | 17.54% | 19.02% | 23.64%
NQ-Townsville Burdekin West | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Limiting Line Name | TR_LINE 33601_1 | TR_LINE 33601_1 | TR_LINE 33601_1 | TR_LINE 33601_1 | TR_LINE 33601_1
NQ-Townsville Burdekin West | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Loading (A) | 49.7518 | 47.0598 | 45.2433 | 49.0693 | 60.9946
NQ-Townsville Burdekin West | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Loading (MVA) | 5.8691 | 5.5656 | 5.3647 | 5.852 | 7.3001
NQ-Townsville Burdekin West | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Loading (MW) | 4.7486 | 4.3858 | 4.1396 | 5.6399 | 7.1031
NQ-Townsville Burdekin West | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Power Factor | 0.80907 | 0.78802 | 0.77164 | 0.96376 | 0.97302
NQ-Townsville Burdekin West | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Rating (A) | 258 | 258 | 258 | 258 | 258
NQ-Townsville Burdekin West | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Min Voltage at Constrained Conductor | 68.1093 | 68.2812 | 68.4586 | 68.8217 | 69.0547
NQ-Townsville Burdekin West | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Contingency Outage | MP-AY-1 Mona Park - Ayr No 1 66 kV | MP-AY-1 Mona Park - Ayr No 1 66 kV | MP-AY-1 Mona Park - Ayr No 1 66 kV | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV
NQ-Townsville Burdekin West | BC-IN-1_Black River - Ingham No 1 66 kV | % of Rated A | 7.45% | 9.81% | 11.79% | 13.7% | 15.61%
NQ-Townsville Burdekin West | BC-IN-1_Black River - Ingham No 1 66 kV | Limiting Line Name | TR_LINE 214252_1 | TR_LINE 214252_1 | TR_LINE 214252_1 | TR_LINE 214252_1 | TR_LINE 214252_1
NQ-Townsville Burdekin West | BC-IN-1_Black River - Ingham No 1 66 kV | Loading (A) | 14.08 | 18.5413 | 22.2816 | 25.8894 | 29.4941
NQ-Townsville Burdekin West | BC-IN-1_Black River - Ingham No 1 66 kV | Loading (MVA) | 1.6851 | 2.222 | 2.7008 | 3.1403 | 3.5791
NQ-Townsville Burdekin West | BC-IN-1_Black River - Ingham No 1 66 kV | Loading (MW) | 1.624 | 2.1799 | 2.6683 | 3.1161 | 3.5615
NQ-Townsville Burdekin West | BC-IN-1_Black River - Ingham No 1 66 kV | Power Factor | 0.96332 | 0.98053 | 0.98733 | 0.99156 | 0.99427
NQ-Townsville Burdekin West | BC-IN-1_Black River - Ingham No 1 66 kV | Rating (A) | 189 | 189 | 189 | 189 | 189
NQ-Townsville Burdekin West | BC-IN-1_Black River - Ingham No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | BC-IN-1_Black River - Ingham No 1 66 kV | Min Voltage at Constrained Conductor | 69.0978 | 69.1901 | 69.9819 | 70.031 | 70.0597
NQ-Townsville Burdekin West | BC-IN-1_Black River - Ingham No 1 66 kV | Contingency Outage | PA-RP-1_Peter Arlett-Ross Plains 66 kV | PA-RP-1_Peter Arlett-Ross Plains 66 kV | MF-TP-2_Max Fulton-TOPO No 2 66 kV | MF-TP-2_Max Fulton-TOPO No 2 66 kV | MF-TP-2_Max Fulton-TOPO No 2 66 kV
NQ-Townsville Burdekin West | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | % of Rated A | 3.11% | 2.981% | 2.933% | 2.906% | 2.903%
NQ-Townsville Burdekin West | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | Limiting Line Name | TR_CABLE 4808_1 | TR_CABLE 4808_1 | TR_CABLE 4808_1 | TR_CABLE 4808_1 | TR_CABLE 4808_1
NQ-Townsville Burdekin West | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | Loading (A) | 24.6906 | 23.6702 | 23.2866 | 23.0761 | 23.0522
NQ-Townsville Burdekin West | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | Loading (MVA) | 2.9476 | 2.8269 | 2.8037 | 2.7861 | 2.7831
NQ-Townsville Burdekin West | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | Loading (MW) | 1.1512 | 0.76987 | 0.45332 | 0.1271 | 0.01039
NQ-Townsville Burdekin West | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | Power Factor | 0.39055 | 0.27234 | 0.16169 | 0.045618 | 0.0010261
NQ-Townsville Burdekin West | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | Rating (A) | 794 | 794 | 794 | 794 | 794
NQ-Townsville Burdekin West | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | Min Voltage at Constrained Conductor | 68.9244 | 68.9511 | 69.5118 | 69.7062 | 69.7047
NQ-Townsville Burdekin West | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | Contingency Outage | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV
NQ-Townsville Burdekin West | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | % of Rated A | 3.093% | 2.963% | 2.914% | 2.888% | 2.885%
NQ-Townsville Burdekin West | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | Limiting Line Name | TR_CABLE 16086_1 | TR_CABLE 16086_1 | TR_CABLE 16086_1 | TR_CABLE 16086_1 | TR_CABLE 16086_1
NQ-Townsville Burdekin West | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | Loading (A) | 24.5553 | 23.5291 | 23.141 | 22.93 | 22.9057
NQ-Townsville Burdekin West | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | Loading (MVA) | 2.9314 | 2.81 | 2.7861 | 2.7684 | 2.7655
NQ-Townsville Burdekin West | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | Loading (MW) | 1.1508 | 0.76952 | 0.45296 | 0.12683 | 0.010175
NQ-Townsville Burdekin West | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | Power Factor | 0.39259 | 0.27385 | 0.16258 | 0.045811 | 0.00067241
NQ-Townsville Burdekin West | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | Rating (A) | 794 | 794 | 794 | 794 | 794
NQ-Townsville Burdekin West | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | Min Voltage at Constrained Conductor | 68.924 | 68.9507 | 69.5114 | 69.7062 | 69.7047
NQ-Townsville Burdekin West | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | Contingency Outage | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV
NQ-Townsville Burdekin West | BO-DG-1_Bohle-Dan Gleeson 66 kV | % of Rated A | 29.19% | 41.3% | 52.86% | 65.4% | 78.92%
NQ-Townsville Burdekin West | BO-DG-1_Bohle-Dan Gleeson 66 kV | Limiting Line Name | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1
NQ-Townsville Burdekin West | BO-DG-1_Bohle-Dan Gleeson 66 kV | Loading (A) | 130.4864 | 184.6027 | 236.3007 | 292.3439 | 352.771
NQ-Townsville Burdekin West | BO-DG-1_Bohle-Dan Gleeson 66 kV | Loading (MVA) | 15.5445 | 22.0052 | 28.5727 | 35.3565 | 42.6602
NQ-Townsville Burdekin West | BO-DG-1_Bohle-Dan Gleeson 66 kV | Loading (MW) | 15.0728 | 21.7911 | 28.4873 | 35.3487 | 42.648
NQ-Townsville Burdekin West | BO-DG-1_Bohle-Dan Gleeson 66 kV | Power Factor | 0.96929 | 0.98997 | 0.99674 | 0.99961 | 0.99971
NQ-Townsville Burdekin West | BO-DG-1_Bohle-Dan Gleeson 66 kV | Rating (A) | 447 | 447 | 447 | 447 | 447
NQ-Townsville Burdekin West | BO-DG-1_Bohle-Dan Gleeson 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | BO-DG-1_Bohle-Dan Gleeson 66 kV | Min Voltage at Constrained Conductor | 68.7781 | 68.8218 | 69.8112 | 69.8197 | 69.8092
NQ-Townsville Burdekin West | BO-DG-1_Bohle-Dan Gleeson 66 kV | Contingency Outage | GA-BO-1_Garbutt-Bohle No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV
NQ-Townsville Burdekin West | CHTO_Clare South - Charters Towers 66 kV | % of Rated A | 59.53% | 57.13% | 61.35% | 59.45% | 57.68%
NQ-Townsville Burdekin West | CHTO_Clare South - Charters Towers 66 kV | Limiting Line Name | TR_LINE 102297_1 | TR_LINE 102297_1 | TR_LINE 102297_1 | TR_LINE 102297_1 | TR_LINE 102297_1
NQ-Townsville Burdekin West | CHTO_Clare South - Charters Towers 66 kV | Loading (A) | 153.5757 | 147.3852 | 158.2854 | 153.3783 | 148.8248
NQ-Townsville Burdekin West | CHTO_Clare South - Charters Towers 66 kV | Loading (MVA) | 18.0571 | 17.3296 | 18.6142 | 18.036 | 17.4983
NQ-Townsville Burdekin West | CHTO_Clare South - Charters Towers 66 kV | Loading (MW) | 16.92 | 16.1842 | 17.4041 | 16.8174 | 16.2709
NQ-Townsville Burdekin West | CHTO_Clare South - Charters Towers 66 kV | Power Factor | 0.93701 | 0.93389 | 0.93497 | 0.93241 | 0.92983
NQ-Townsville Burdekin West | CHTO_Clare South - Charters Towers 66 kV | Rating (A) | 258 | 258 | 258 | 258 | 258
NQ-Townsville Burdekin West | CHTO_Clare South - Charters Towers 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | CHTO_Clare South - Charters Towers 66 kV | Min Voltage at Constrained Conductor | 67.8822 | 67.8834 | 67.8942 | 67.8902 | 67.8815
NQ-Townsville Burdekin West | CHTO_Clare South - Charters Towers 66 kV | Contingency Outage | 7182 Ross - Milchester | 7182 Ross - Milchester | 7182 Ross - Milchester | 7182 Ross - Milchester | 7182 Ross - Milchester
NQ-Townsville Burdekin West | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | % of Rated A | 9.596% | 9.016% | 11.21% | 14.71% | 20.38%
NQ-Townsville Burdekin West | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Limiting Line Name | TR_LINE 102266_1 | TR_LINE 102266_1 | TR_LINE 102266_1 | TR_LINE 102266_1 | TR_LINE 102266_1
NQ-Townsville Burdekin West | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Loading (A) | 29.9409 | 28.129 | 34.963 | 45.8826 | 63.5803
NQ-Townsville Burdekin West | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Loading (MVA) | 3.5133 | 3.3008 | 4.1044 | 5.3846 | 7.4607
NQ-Townsville Burdekin West | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Loading (MW) | 1.2799 | 0.48475 | 3.4202 | 4.3962 | 6.8669
NQ-Townsville Burdekin West | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Power Factor | 0.3643 | 0.14683 | 0.83327 | 0.8164 | 0.92035
NQ-Townsville Burdekin West | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Rating (A) | 312 | 312 | 312 | 312 | 312
NQ-Townsville Burdekin West | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Min Voltage at Constrained Conductor | 67.7472 | 67.7501 | 67.7769 | 67.756 | 67.7484
NQ-Townsville Burdekin West | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Contingency Outage | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | AY-PIMI_Ayr - Pioneer Mill 66 kV | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV
NQ-Townsville Burdekin West | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | % of Rated A | 16.12% | 15% | 19.21% | 25.88% | 36.38%
NQ-Townsville Burdekin West | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Limiting Line Name | TR_LINE 147761_2 | TR_LINE 147761_2 | TR_LINE 147761_2 | TR_LINE 147761_2 | TR_LINE 147761_2
NQ-Townsville Burdekin West | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Loading (A) | 27.2411 | 25.3474 | 32.4627 | 43.7307 | 61.4746
NQ-Townsville Burdekin West | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Loading (MVA) | 3.2094 | 2.9923 | 3.8388 | 5.1841 | 7.3047
NQ-Townsville Burdekin West | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Loading (MW) | 1.1552 | 0.57257 | 3.4161 | 4.4209 | 6.8653
NQ-Townsville Burdekin West | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Power Factor | 0.35995 | 0.1913 | 0.88982 | 0.85269 | 0.93972
NQ-Townsville Burdekin West | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Rating (A) | 169 | 169 | 169 | 169 | 169
NQ-Townsville Burdekin West | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Min Voltage at Constrained Conductor | 68.0206 | 68.1567 | 68.2725 | 68.4432 | 68.6036
NQ-Townsville Burdekin West | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Contingency Outage | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | AY-PIMI_Ayr - Pioneer Mill 66 kV | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV
NQ-Townsville Burdekin West | CR-HU-1_Cape River-Hughenden No 1 66 kV | % of Rated A | 50.45% | 50.38% | 51.58% | 51.08% | 50.6%
NQ-Townsville Burdekin West | CR-HU-1_Cape River-Hughenden No 1 66 kV | Limiting Line Name | TR_LINE 53284_2 | TR_LINE 53284_2 | TR_LINE 53284_2 | TR_LINE 53284_2 | TR_LINE 53284_2
NQ-Townsville Burdekin West | CR-HU-1_Cape River-Hughenden No 1 66 kV | Loading (A) | 72.1446 | 72.0458 | 73.7595 | 73.0456 | 72.3509
NQ-Townsville Burdekin West | CR-HU-1_Cape River-Hughenden No 1 66 kV | Loading (MVA) | 8.528 | 8.5197 | 8.7016 | 8.6205 | 8.5415
NQ-Townsville Burdekin West | CR-HU-1_Cape River-Hughenden No 1 66 kV | Loading (MW) | 2.2327 | 1.8463 | 4.4196 | 4.0675 | 3.7008
NQ-Townsville Burdekin West | CR-HU-1_Cape River-Hughenden No 1 66 kV | Power Factor | 0.26179 | 0.21669 | 0.5079 | 0.47184 | 0.43326
NQ-Townsville Burdekin West | CR-HU-1_Cape River-Hughenden No 1 66 kV | Rating (A) | 143 | 143 | 143 | 143 | 143
NQ-Townsville Burdekin West | CR-HU-1_Cape River-Hughenden No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | CR-HU-1_Cape River-Hughenden No 1 66 kV | Min Voltage at Constrained Conductor | 68.2472 | 68.2743 | 68.1117 | 68.1364 | 68.1598
NQ-Townsville Burdekin West | CR-HU-1_Cape River-Hughenden No 1 66 kV | Contingency Outage | 6382 JACR-HUGH 132kV | 6382 JACR-HUGH 132kV | 6382 JACR-HUGH 132kV | 6382 JACR-HUGH 132kV | 6382 JACR-HUGH 132kV
NQ-Townsville Burdekin West | CS-ML-1_Clare South - Millaroo 66 kV | % of Rated A | 2.626% | 3.197% | 3.973% | 4.891% | 5.939%
NQ-Townsville Burdekin West | CS-ML-1_Clare South - Millaroo 66 kV | Limiting Line Name | TR_LINE 102260_1 | TR_LINE 102260_1 | TR_LINE 102260_1 | TR_LINE 102260_1 | TR_LINE 102260_1
NQ-Townsville Burdekin West | CS-ML-1_Clare South - Millaroo 66 kV | Loading (A) | 5.1216 | 6.2349 | 7.7464 | 9.5376 | 11.5801
NQ-Townsville Burdekin West | CS-ML-1_Clare South - Millaroo 66 kV | Loading (MVA) | 0.60219 | 0.73209 | 0.90859 | 1.1186 | 1.358
NQ-Townsville Burdekin West | CS-ML-1_Clare South - Millaroo 66 kV | Loading (MW) | 0.30204 | 0.51716 | 0.74877 | 0.99509 | 1.2605
NQ-Townsville Burdekin West | CS-ML-1_Clare South - Millaroo 66 kV | Power Factor | 0.50158 | 0.70641 | 0.8241 | 0.88956 | 0.92817
NQ-Townsville Burdekin West | CS-ML-1_Clare South - Millaroo 66 kV | Rating (A) | 195 | 195 | 195 | 195 | 195
NQ-Townsville Burdekin West | CS-ML-1_Clare South - Millaroo 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | CS-ML-1_Clare South - Millaroo 66 kV | Min Voltage at Constrained Conductor | 67.8837 | 67.7911 | 67.7185 | 67.7151 | 67.7073
NQ-Townsville Burdekin West | CS-ML-1_Clare South - Millaroo 66 kV | Contingency Outage | 7182 Ross - Milchester | ST-WO-1_Stuart-Woodstock South 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV
NQ-Townsville Burdekin West | CT-CR-1_Charters Towers-CARI No 1 66 kV | % of Rated A | 10.07% | 9.654% | 23.12% | 20.84% | 18.52%
NQ-Townsville Burdekin West | CT-CR-1_Charters Towers-CARI No 1 66 kV | Limiting Line Name | TR_LINE 31871_1 | TR_LINE 64805_1 | TR_LINE 31871_1 | TR_LINE 31871_1 | TR_LINE 31871_1
NQ-Townsville Burdekin West | CT-CR-1_Charters Towers-CARI No 1 66 kV | Loading (A) | 18.5371 | 18.1498 | 42.5462 | 38.3418 | 34.0844
NQ-Townsville Burdekin West | CT-CR-1_Charters Towers-CARI No 1 66 kV | Loading (MVA) | 2.2174 | 2.1111 | 5.104 | 4.5988 | 4.087
NQ-Townsville Burdekin West | CT-CR-1_Charters Towers-CARI No 1 66 kV | Loading (MW) | 2.0246 | 0.76182 | 4.3592 | 3.9635 | 3.5593
NQ-Townsville Burdekin West | CT-CR-1_Charters Towers-CARI No 1 66 kV | Power Factor | 0.91302 | 0.35926 | 0.85408 | 0.86185 | 0.87088
NQ-Townsville Burdekin West | CT-CR-1_Charters Towers-CARI No 1 66 kV | Rating (A) | 184 | 188 | 184 | 184 | 184
NQ-Townsville Burdekin West | CT-CR-1_Charters Towers-CARI No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | CT-CR-1_Charters Towers-CARI No 1 66 kV | Min Voltage at Constrained Conductor | 69.0573 | 67.1549 | 69.2501 | 69.2393 | 69.2198
NQ-Townsville Burdekin West | CT-CR-1_Charters Towers-CARI No 1 66 kV | Contingency Outage | MR-CR-1_Millchester-Cape River 1 66 kV | 7460 CPRE-JACR 132kV | MR-CR-1_Millchester-Cape River 1 66 kV | MR-CR-1_Millchester-Cape River 1 66 kV | MR-CR-1_Millchester-Cape River 1 66 kV
NQ-Townsville Burdekin West | CT-MR-1_Millchester-CHTO No 1 66 kV | % of Rated A | 54.26% | 52.82% | 56.86% | 55.63% | 54.44%
NQ-Townsville Burdekin West | CT-MR-1_Millchester-CHTO No 1 66 kV | Limiting Line Name | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1
NQ-Townsville Burdekin West | CT-MR-1_Millchester-CHTO No 1 66 kV | Loading (A) | 150.8457 | 146.846 | 158.0661 | 154.6496 | 151.3433
NQ-Townsville Burdekin West | CT-MR-1_Millchester-CHTO No 1 66 kV | Loading (MVA) | 18.0192 | 17.5828 | 18.899 | 18.5239 | 18.158
NQ-Townsville Burdekin West | CT-MR-1_Millchester-CHTO No 1 66 kV | Loading (MW) | 8.0242 | 7.5415 | 8.9248 | 8.5212 | 8.1219
NQ-Townsville Burdekin West | CT-MR-1_Millchester-CHTO No 1 66 kV | Power Factor | 0.44523 | 0.42884 | 0.47215 | 0.45992 | 0.44721
NQ-Townsville Burdekin West | CT-MR-1_Millchester-CHTO No 1 66 kV | Rating (A) | 278 | 278 | 278 | 278 | 278
NQ-Townsville Burdekin West | CT-MR-1_Millchester-CHTO No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | CT-MR-1_Millchester-CHTO No 1 66 kV | Min Voltage at Constrained Conductor | 68.9655 | 69.128 | 69.0283 | 69.1532 | 69.2682
NQ-Townsville Burdekin West | CT-MR-1_Millchester-CHTO No 1 66 kV | Contingency Outage | 7182 Ross - Milchester | 7182 Ross - Milchester | 7182 Ross - Milchester | 7182 Ross - Milchester | 7182 Ross - Milchester
NQ-Townsville Burdekin West | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | % of Rated A | 19.44% | 20.4% | 15.84% | 16.22% | 18.15%
NQ-Townsville Burdekin West | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Limiting Line Name | TR_LINE 126322_1 | TR_LINE 126322_1 | TR_LINE 126322_1 | TR_LINE 126322_1 | TR_LINE 126322_1
NQ-Townsville Burdekin West | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Loading (A) | 87.8492 | 92.2199 | 71.5763 | 73.3222 | 82.0388
NQ-Townsville Burdekin West | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Loading (MVA) | 10.5117 | 11.0008 | 8.6617 | 8.8527 | 9.9031
NQ-Townsville Burdekin West | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Loading (MW) | 2.5614 | 5.1561 | 0.46852 | 7.0753 | 7.9299
NQ-Townsville Burdekin West | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Power Factor | 0.24359 | 0.46865 | 0.05401 | 0.79923 | 0.80075
NQ-Townsville Burdekin West | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Rating (A) | 452 | 452 | 452 | 452 | 452
NQ-Townsville Burdekin West | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Min Voltage at Constrained Conductor | 69.0836 | 68.8716 | 69.8674 | 69.7072 | 69.6934
NQ-Townsville Burdekin West | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Contingency Outage | 6299_Townsville Port 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV
NQ-Townsville Burdekin West | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | % of Rated A | 9.535% | 8.225% | 7.305% | 7.815% | 8.803%
NQ-Townsville Burdekin West | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Limiting Line Name | TR_LINE 172527_2 | TR_LINE 172527_2 | TR_LINE 32461_1 | TR_LINE 32461_1 | TR_LINE 32461_1
NQ-Townsville Burdekin West | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Loading (A) | 52.5377 | 45.3193 | 40.249 | 43.0607 | 48.5042
NQ-Townsville Burdekin West | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Loading (MVA) | 6.2486 | 5.3932 | 4.8498 | 5.1857 | 5.8407
NQ-Townsville Burdekin West | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Loading (MW) | 5.202 | 3.2282 | 4.7956 | 5.1157 | 5.7762
NQ-Townsville Burdekin West | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Power Factor | 0.83251 | 0.59849 | 0.98883 | 0.98651 | 0.98896
NQ-Townsville Burdekin West | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Rating (A) | 551 | 551 | 551 | 551 | 551
NQ-Townsville Burdekin West | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Min Voltage at Constrained Conductor | 68.667 | 68.7071 | 69.5674 | 69.5286 | 69.5215
NQ-Townsville Burdekin West | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Contingency Outage | ST-RP-1_Stuart-Ross Plains 66 kV | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV
NQ-Townsville Burdekin West | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | % of Rated A | 26.26% | 27% | 27.34% | 29.06% | 31.16%
NQ-Townsville Burdekin West | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Limiting Line Name | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1
NQ-Townsville Burdekin West | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Loading (A) | 65.9222 | 67.7692 | 68.6307 | 72.9531 | 78.2066
NQ-Townsville Burdekin West | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Loading (MVA) | 7.8277 | 8.0496 | 8.2704 | 8.7826 | 9.4133
NQ-Townsville Burdekin West | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Loading (MW) | 6.9876 | 7.1958 | 8.2622 | 8.7664 | 9.4011
NQ-Townsville Burdekin West | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Power Factor | 0.89268 | 0.89393 | 0.99901 | 0.99815 | 0.9987
NQ-Townsville Burdekin West | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Rating (A) | 251 | 251 | 251 | 251 | 251
NQ-Townsville Burdekin West | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Min Voltage at Constrained Conductor | 68.5552 | 68.5777 | 69.5741 | 69.5056 | 69.4926
NQ-Townsville Burdekin West | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Contingency Outage | PA-RP-1_Peter Arlett-Ross Plains 66 kV | PA-RP-1_Peter Arlett-Ross Plains 66 kV | PA-RP-1_Peter Arlett-Ross Plains 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV
NQ-Townsville Burdekin West | EAAY_Clare South - East Ayr 66 kV | % of Rated A | 19.78% | 17.46% | 15.71% | 17.55% | 21.58%
NQ-Townsville Burdekin West | EAAY_Clare South - East Ayr 66 kV | Limiting Line Name | TR_LINE 183529_1 | TR_LINE 183529_1 | TR_LINE 183529_1 | TR_LINE 183529_1 | TR_LINE 183529_1
NQ-Townsville Burdekin West | EAAY_Clare South - East Ayr 66 kV | Loading (A) | 41.5484 | 36.67 | 32.9805 | 36.8609 | 45.3083
NQ-Townsville Burdekin West | EAAY_Clare South - East Ayr 66 kV | Loading (MVA) | 4.9027 | 4.3333 | 3.9029 | 4.3847 | 5.3976
NQ-Townsville Burdekin West | EAAY_Clare South - East Ayr 66 kV | Loading (MW) | 3.4948 | 2.6066 | 1.7724 | 3.6189 | 4.8068
NQ-Townsville Burdekin West | EAAY_Clare South - East Ayr 66 kV | Power Factor | 0.71283 | 0.60153 | 0.45413 | 0.82529 | 0.89047
NQ-Townsville Burdekin West | EAAY_Clare South - East Ayr 66 kV | Rating (A) | 210 | 210 | 210 | 210 | 210
NQ-Townsville Burdekin West | EAAY_Clare South - East Ayr 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | EAAY_Clare South - East Ayr 66 kV | Min Voltage at Constrained Conductor | 68.127 | 68.226 | 68.3231 | 68.6774 | 68.78
NQ-Townsville Burdekin West | EAAY_Clare South - East Ayr 66 kV | Contingency Outage | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | AY-PIMI_Ayr - Pioneer Mill 66 kV | AY-PIMI_Ayr - Pioneer Mill 66 kV
NQ-Townsville Burdekin West | GA-BO-1_Garbutt-Bohle No 1 66 kV | % of Rated A | 23.49% | 33.28% | 42.89% | 53.08% | 64.04%
NQ-Townsville Burdekin West | GA-BO-1_Garbutt-Bohle No 1 66 kV | Limiting Line Name | TR_LINE 128084_1 | TR_LINE 128084_1 | TR_LINE 128084_1 | TR_LINE 128084_1 | TR_LINE 32140_1
NQ-Townsville Burdekin West | GA-BO-1_Garbutt-Bohle No 1 66 kV | Loading (A) | 129.4424 | 183.3709 | 236.3371 | 292.4599 | 352.8511
NQ-Townsville Burdekin West | GA-BO-1_Garbutt-Bohle No 1 66 kV | Loading (MVA) | 15.4917 | 21.9579 | 28.5106 | 35.2869 | 43.0014
NQ-Townsville Burdekin West | GA-BO-1_Garbutt-Bohle No 1 66 kV | Loading (MW) | 15.0608 | 21.7671 | 28.4438 | 35.2822 | 43.0012
NQ-Townsville Burdekin West | GA-BO-1_Garbutt-Bohle No 1 66 kV | Power Factor | 0.97218 | 0.99131 | 0.99766 | 0.99987 | 0.99999
NQ-Townsville Burdekin West | GA-BO-1_Garbutt-Bohle No 1 66 kV | Rating (A) | 551 | 551 | 551 | 551 | 551
NQ-Townsville Burdekin West | GA-BO-1_Garbutt-Bohle No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | GA-BO-1_Garbutt-Bohle No 1 66 kV | Min Voltage at Constrained Conductor | 69.0948 | 69.1311 | 69.6437 | 69.6548 | 70.3581
NQ-Townsville Burdekin West | GA-BO-1_Garbutt-Bohle No 1 66 kV | Contingency Outage | BO-DG-1_Bohle-Dan Gleeson 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV
NQ-Townsville Burdekin West | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | % of Rated A | 17.64% | 16.92% | 21.33% | 23.38% | 25.62%
NQ-Townsville Burdekin West | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Limiting Line Name | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1
NQ-Townsville Burdekin West | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Loading (A) | 60.8613 | 58.3657 | 73.5943 | 80.6488 | 88.4009
NQ-Townsville Burdekin West | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Loading (MVA) | 7.2889 | 6.9937 | 8.8584 | 9.7082 | 10.6409
NQ-Townsville Burdekin West | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Loading (MW) | 4.4567 | 4.4965 | 7.9114 | 8.8432 | 9.8419
NQ-Townsville Burdekin West | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Power Factor | 0.61144 | 0.64293 | 0.8931 | 0.9109 | 0.92492
NQ-Townsville Burdekin West | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Rating (A) | 345 | 345 | 345 | 345 | 345
NQ-Townsville Burdekin West | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Min Voltage at Constrained Conductor | 69.1449 | 69.1816 | 69.4918 | 69.4951 | 69.4908
NQ-Townsville Burdekin West | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Contingency Outage | GA-TP-1_Garbutt-Townsville Port 1 66 kV | GA-TP-1_Garbutt-Townsville Port 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV
NQ-Townsville Burdekin West | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | % of Rated A | 18.51% | 18.22% | 17.88% | 17.72% | 17.63%
NQ-Townsville Burdekin West | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Limiting Line Name | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1
NQ-Townsville Burdekin West | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Loading (A) | 31.2842 | 30.7921 | 30.2172 | 29.9389 | 29.7871
NQ-Townsville Burdekin West | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Loading (MVA) | 3.7341 | 3.6769 | 3.6362 | 3.6027 | 3.5841
NQ-Townsville Burdekin West | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Loading (MW) | 3.6515 | 3.5923 | 3.5471 | 3.5124 | 3.4932
NQ-Townsville Burdekin West | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Power Factor | 0.97787 | 0.97699 | 0.97548 | 0.97494 | 0.97464
NQ-Townsville Burdekin West | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Rating (A) | 169 | 169 | 169 | 169 | 169
NQ-Townsville Burdekin West | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Min Voltage at Constrained Conductor | 68.913 | 68.9402 | 69.4753 | 69.4755 | 69.4679
NQ-Townsville Burdekin West | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Contingency Outage | MF-TP-2_Max Fulton-TOPO No 2 66 kV | MF-TP-2_Max Fulton-TOPO No 2 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV
NQ-Townsville Burdekin West | GA-TP-1_Garbutt-Townsville Port 1 66 kV | % of Rated A | 44.75% | 40.75% | 25.47% | 22.08% | 19.81%
NQ-Townsville Burdekin West | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Limiting Line Name | TR_LINE 161962_1 | TR_LINE 161962_1 | TR_LINE 161962_1 | TR_LINE 161962_1 | TR_LINE 161962_1
NQ-Townsville Burdekin West | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Loading (A) | 115.4494 | 105.1246 | 65.7017 | 56.9681 | 51.1167
NQ-Townsville Burdekin West | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Loading (MVA) | 13.7578 | 12.5008 | 7.9163 | 6.857 | 6.1511
NQ-Townsville Burdekin West | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Loading (MW) | 7.9971 | 4.7677 | 5.8931 | 5.7715 | 5.0405
NQ-Townsville Burdekin West | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Power Factor | 0.58119 | 0.3813 | 0.74442 | 0.84169 | 0.81945
NQ-Townsville Burdekin West | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Rating (A) | 258 | 258 | 258 | 258 | 258
NQ-Townsville Burdekin West | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Min Voltage at Constrained Conductor | 68.8013 | 68.6549 | 69.5642 | 69.4932 | 69.4745
NQ-Townsville Burdekin West | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Contingency Outage | HP-OO_Hermit park - Oonoonba 66 kV | MF-TP-2_Max Fulton-TOPO No 2 66 kV | HP-OO_Hermit park - Oonoonba 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV
NQ-Townsville Burdekin West | GARB-12 11kV | % of Rated A | 0.697% | 0.6973% | 0.6929% | 0.6931% | 0.6932%
NQ-Townsville Burdekin West | GARB-12 11kV | Limiting Line Name | HV_CABLE 14927_1 | HV_CABLE 14927_1 | HV_CABLE 14927_1 | HV_CABLE 14927_1 | HV_CABLE 14927_1
NQ-Townsville Burdekin West | GARB-12 11kV | Loading (A) | 2.7879 | 2.7893 | 2.7717 | 2.7724 | 2.7727
NQ-Townsville Burdekin West | GARB-12 11kV | Loading (MVA) | 0.052486 | 0.052538 | 0.05188 | 0.051906 | 0.051917
NQ-Townsville Burdekin West | GARB-12 11kV | Loading (MW) | 0.0010512 | 0.0010522 | 0.001039 | 0.0010395 | 0.0010398
NQ-Townsville Burdekin West | GARB-12 11kV | Power Factor | 0.020021 | 0.020021 | 0.020021 | 0.020021 | 0.020021
NQ-Townsville Burdekin West | GARB-12 11kV | Rating (A) | 400 | 400 | 400 | 400 | 400
NQ-Townsville Burdekin West | GARB-12 11kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | GARB-12 11kV | Min Voltage at Constrained Conductor | 10.8695 | 10.8749 | 10.8065 | 10.8092 | 10.8104
NQ-Townsville Burdekin West | GARB-12 11kV | Contingency Outage | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV
NQ-Townsville Burdekin West | GI-AY-1_Giru - Ayr 1 66 kV | % of Rated A | 4.34% | 5.533% | 6.93% | 8.441% | 10.07%
NQ-Townsville Burdekin West | GI-AY-1_Giru - Ayr 1 66 kV | Limiting Line Name | TR_LINE 170050_1 | TR_LINE 170050_1 | TR_LINE 170050_1 | TR_LINE 170050_1 | TR_LINE 170050_1
NQ-Townsville Burdekin West | GI-AY-1_Giru - Ayr 1 66 kV | Loading (A) | 8.2031 | 10.4568 | 13.0972 | 15.9533 | 19.0415
NQ-Townsville Burdekin West | GI-AY-1_Giru - Ayr 1 66 kV | Loading (MVA) | 0.97261 | 1.2323 | 1.5467 | 1.8878 | 2.2583
NQ-Townsville Burdekin West | GI-AY-1_Giru - Ayr 1 66 kV | Loading (MW) | 0.59827 | 0.97522 | 1.3531 | 1.7359 | 2.1366
NQ-Townsville Burdekin West | GI-AY-1_Giru - Ayr 1 66 kV | Power Factor | 0.61511 | 0.79141 | 0.87487 | 0.91952 | 0.9461
NQ-Townsville Burdekin West | GI-AY-1_Giru - Ayr 1 66 kV | Rating (A) | 189 | 189 | 189 | 189 | 189
NQ-Townsville Burdekin West | GI-AY-1_Giru - Ayr 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | GI-AY-1_Giru - Ayr 1 66 kV | Min Voltage at Constrained Conductor | 68.4544 | 68.0365 | 68.1803 | 68.3208 | 68.4721
NQ-Townsville Burdekin West | GI-AY-1_Giru - Ayr 1 66 kV | Contingency Outage | AY-PIMI_Ayr - Pioneer Mill 66 kV | AY-EA-1_Ayr - East Ayr No 1 66 kV | AY-EA-1_Ayr - East Ayr No 1 66 kV | AY-EA-1_Ayr - East Ayr No 1 66 kV | AY-EA-1_Ayr - East Ayr No 1 66 kV
NQ-Townsville Burdekin West | HP-OO_Hermit park - Oonoonba 66 kV | % of Rated A | 22.25% | 20.09% | 23.59% | 24.04% | 24.65%
NQ-Townsville Burdekin West | HP-OO_Hermit park - Oonoonba 66 kV | Limiting Line Name | TR_LINE 106404_1 | TR_LINE 106404_1 | TR_LINE 106404_1 | TR_LINE 106404_1 | TR_LINE 106404_1
NQ-Townsville Burdekin West | HP-OO_Hermit park - Oonoonba 66 kV | Loading (A) | 76.7745 | 69.2972 | 81.3926 | 82.9478 | 85.0551
NQ-Townsville Burdekin West | HP-OO_Hermit park - Oonoonba 66 kV | Loading (MVA) | 9.1848 | 8.2946 | 9.8037 | 9.9926 | 10.2471
NQ-Townsville Burdekin West | HP-OO_Hermit park - Oonoonba 66 kV | Loading (MW) | 7.1292 | 6.2942 | 8.9399 | 9.1376 | 9.4006
NQ-Townsville Burdekin West | HP-OO_Hermit park - Oonoonba 66 kV | Power Factor | 0.77619 | 0.75883 | 0.91189 | 0.91444 | 0.91739
NQ-Townsville Burdekin West | HP-OO_Hermit park - Oonoonba 66 kV | Rating (A) | 345 | 345 | 345 | 345 | 345
NQ-Townsville Burdekin West | HP-OO_Hermit park - Oonoonba 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | HP-OO_Hermit park - Oonoonba 66 kV | Min Voltage at Constrained Conductor | 69.0704 | 69.1064 | 69.5383 | 69.549 | 69.5532
NQ-Townsville Burdekin West | HP-OO_Hermit park - Oonoonba 66 kV | Contingency Outage | GA-TP-1_Garbutt-Townsville Port 1 66 kV | GA-TP-1_Garbutt-Townsville Port 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV
NQ-Townsville Burdekin West | HU-RI-1_Hughenden-Richmond No 1 66 kV | % of Rated A | 11.91% | 11.93% | 14.03% | 13.86% | 13.7%
NQ-Townsville Burdekin West | HU-RI-1_Hughenden-Richmond No 1 66 kV | Limiting Line Name | TR_LINE 163222_1 | TR_LINE 163222_1 | TR_LINE 163222_1 | TR_LINE 163222_1 | TR_LINE 163222_1
NQ-Townsville Burdekin West | HU-RI-1_Hughenden-Richmond No 1 66 kV | Loading (A) | 33.9495 | 33.995 | 39.9873 | 39.4874 | 39.0355
NQ-Townsville Burdekin West | HU-RI-1_Hughenden-Richmond No 1 66 kV | Loading (MVA) | 4.3438 | 4.3681 | 4.9767 | 4.9354 | 4.8996
NQ-Townsville Burdekin West | HU-RI-1_Hughenden-Richmond No 1 66 kV | Loading (MW) | 0.60369 | 0.44937 | 3.1872 | 3.0603 | 2.9387
NQ-Townsville Burdekin West | HU-RI-1_Hughenden-Richmond No 1 66 kV | Power Factor | 0.13898 | 0.10288 | 0.64044 | 0.62008 | 0.59979
NQ-Townsville Burdekin West | HU-RI-1_Hughenden-Richmond No 1 66 kV | Rating (A) | 285 | 285 | 285 | 285 | 285
NQ-Townsville Burdekin West | HU-RI-1_Hughenden-Richmond No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | HU-RI-1_Hughenden-Richmond No 1 66 kV | Min Voltage at Constrained Conductor | 73.8706 | 74.185 | 71.8549 | 72.1607 | 72.4667
NQ-Townsville Burdekin West | HU-RI-1_Hughenden-Richmond No 1 66 kV | Contingency Outage | 6382 JACR-HUGH 132kV | 6382 JACR-HUGH 132kV | 6382 JACR-HUGH 132kV | 6382 JACR-HUGH 132kV | 6382 JACR-HUGH 132kV
NQ-Townsville Burdekin West | HU-WI-1 Hughenden-Winton No 1 66 kV | % of Rated A | 11.05% | 11.03% | 10.64% | 10.62% | 10.59%
NQ-Townsville Burdekin West | HU-WI-1 Hughenden-Winton No 1 66 kV | Limiting Line Name | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2
NQ-Townsville Burdekin West | HU-WI-1 Hughenden-Winton No 1 66 kV | Loading (A) | 28.9481 | 28.888 | 27.8761 | 27.8132 | 27.7434
NQ-Townsville Burdekin West | HU-WI-1 Hughenden-Winton No 1 66 kV | Loading (MVA) | 3.6967 | 3.7046 | 3.4653 | 3.472 | 3.4779
NQ-Townsville Burdekin West | HU-WI-1 Hughenden-Winton No 1 66 kV | Loading (MW) | 0.88406 | 0.7575 | 0.62047 | 0.4685 | 0.28299
NQ-Townsville Burdekin West | HU-WI-1 Hughenden-Winton No 1 66 kV | Power Factor | 0.23915 | 0.20448 | 0.17905 | 0.13494 | 0.081368
NQ-Townsville Burdekin West | HU-WI-1 Hughenden-Winton No 1 66 kV | Rating (A) | 262 | 262 | 262 | 262 | 262
NQ-Townsville Burdekin West | HU-WI-1 Hughenden-Winton No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | HU-WI-1 Hughenden-Winton No 1 66 kV | Min Voltage at Constrained Conductor | 73.7283 | 74.0392 | 71.771 | 72.0732 | 72.3757
NQ-Townsville Burdekin West | HU-WI-1 Hughenden-Winton No 1 66 kV | Contingency Outage | 6382 JACR-HUGH 132kV | 6382 JACR-HUGH 132kV | 6382 JACR-HUGH 132kV | 6382 JACR-HUGH 132kV | 6382 JACR-HUGH 132kV
NQ-Townsville Burdekin West | HUGH-HU-20 | % of Rated A | 2.961e-08% | 2.916e-08% | 2.453e-06% | 4.377e-06% | 3.498e-06%
NQ-Townsville Burdekin West | HUGH-HU-20 | Limiting Line Name | Link_HUGH_B624_HU-20 TORRENS CK | Link_HUGH_B624_HU-20 TORRENS CK | Link_HUGH_B624_HU-20 TORRENS CK | Link_HUGH_B624_HU-20 TORRENS CK | Link_HUGH_B624_HU-20 TORRENS CK
NQ-Townsville Burdekin West | HUGH-HU-20 | Loading (A) | 1.4804e-06 | 1.4581e-06 | 0.00012265 | 0.00021883 | 0.00017489
NQ-Townsville Burdekin West | HUGH-HU-20 | Loading (MVA) | 8.8961e-08 | 8.7993e-08 | 7.0034e-06 | 1.2504e-05 | 1.0005e-05
NQ-Townsville Burdekin West | HUGH-HU-20 | Loading (MW) | 8.8961e-08 | 8.7993e-08 | 6.788e-07 | 3.663e-06 | 2.2418e-06
NQ-Townsville Burdekin West | HUGH-HU-20 | Power Factor | 1 | 1 | 0.096923 | 0.29295 | 0.22407
NQ-Townsville Burdekin West | HUGH-HU-20 | Rating (A) | 5000 | 5000 | 5000 | 5000 | 5000
NQ-Townsville Burdekin West | HUGH-HU-20 | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | HUGH-HU-20 | Min Voltage at Constrained Conductor | 34.6933 | 34.8406 | 32.967 | 32.9894 | 33.028
NQ-Townsville Burdekin West | HUGH-HU-20 | Contingency Outage | 6382 JACR-HUGH 132kV | 6382 JACR-HUGH 132kV | _NNC | _NNC | _NNC
NQ-Townsville Burdekin West | HUGH-HU-40 | % of Rated A | 4.047e-09% | 4.064e-09% | 3.939e-09% | 3.956e-09% | 3.973e-09%
NQ-Townsville Burdekin West | HUGH-HU-40 | Limiting Line Name | Link_HUGH_D624_HU-40 RICHMOND | Link_HUGH_D624_HU-40 RICHMOND | Link_HUGH_D624_HU-40 RICHMOND | Link_HUGH_D624_HU-40 RICHMOND | Link_HUGH_D624_HU-40 RICHMOND
NQ-Townsville Burdekin West | HUGH-HU-40 | Loading (A) | 2.0233e-07 | 2.0318e-07 | 1.9696e-07 | 1.978e-07 | 1.9863e-07
NQ-Townsville Burdekin West | HUGH-HU-40 | Loading (MVA) | 1.2158e-08 | 1.2261e-08 | 1.1522e-08 | 1.162e-08 | 1.1718e-08
NQ-Townsville Burdekin West | HUGH-HU-40 | Loading (MW) | 1.2158e-08 | 1.2261e-08 | 1.1522e-08 | 1.162e-08 | 1.1718e-08
NQ-Townsville Burdekin West | HUGH-HU-40 | Power Factor | 1 | 1 | 1 | 1 | 1
NQ-Townsville Burdekin West | HUGH-HU-40 | Rating (A) | 5000 | 5000 | 5000 | 5000 | 5000
NQ-Townsville Burdekin West | HUGH-HU-40 | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | HUGH-HU-40 | Min Voltage at Constrained Conductor | 34.6933 | 34.8406 | 33.774 | 33.9168 | 34.0596
NQ-Townsville Burdekin West | HUGH-HU-40 | Contingency Outage | 6382 JACR-HUGH 132kV | 6382 JACR-HUGH 132kV | 6382 JACR-HUGH 132kV | 6382 JACR-HUGH 132kV | 6382 JACR-HUGH 132kV
NQ-Townsville Burdekin West | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | % of Rated A | 14.01% | 13.57% | 13.32% | 13.39% | 18.1%
NQ-Townsville Burdekin West | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Limiting Line Name | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1
NQ-Townsville Burdekin West | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Loading (A) | 23.6714 | 22.9404 | 22.5165 | 22.621 | 30.5817
NQ-Townsville Burdekin West | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Loading (MVA) | 2.7991 | 2.7209 | 2.6787 | 2.6925 | 3.6492
NQ-Townsville Burdekin West | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Loading (MW) | 1.4202 | 1.2911 | 1.2238 | 2.4952 | 3.475
NQ-Townsville Burdekin West | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Power Factor | 0.5074 | 0.47453 | 0.45686 | 0.9267 | 0.95226
NQ-Townsville Burdekin West | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Rating (A) | 169 | 169 | 169 | 169 | 169
NQ-Townsville Burdekin West | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Min Voltage at Constrained Conductor | 68.2701 | 68.4775 | 68.6842 | 68.7193 | 68.8912
NQ-Townsville Burdekin West | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Contingency Outage | EAAY_Clare South - East Ayr 66 kV | EAAY_Clare South - East Ayr 66 kV | EAAY_Clare South - East Ayr 66 kV | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV
NQ-Townsville Burdekin West | KA-AY-01_Ayr - Kalamia No 1 66 kV | % of Rated A | 0.8039% | 0.8256% | 0.8847% | 0.9595% | 1.041%
NQ-Townsville Burdekin West | KA-AY-01_Ayr - Kalamia No 1 66 kV | Limiting Line Name | TR_LINE 31747_1 | TR_LINE 31747_1 | TR_LINE 31747_1 | TR_LINE 31747_1 | TR_LINE 31747_1
NQ-Townsville Burdekin West | KA-AY-01_Ayr - Kalamia No 1 66 kV | Loading (A) | 1.5997 | 1.6429 | 1.7605 | 1.9095 | 2.0724
NQ-Townsville Burdekin West | KA-AY-01_Ayr - Kalamia No 1 66 kV | Loading (MVA) | 0.18967 | 0.19516 | 0.20952 | 0.22746 | 0.24661
NQ-Townsville Burdekin West | KA-AY-01_Ayr - Kalamia No 1 66 kV | Loading (MW) | 0.0083679 | 0.043773 | 0.086418 | 0.12328 | 0.15641
NQ-Townsville Burdekin West | KA-AY-01_Ayr - Kalamia No 1 66 kV | Power Factor | 0.044119 | 0.22429 | 0.41245 | 0.54198 | 0.63422
NQ-Townsville Burdekin West | KA-AY-01_Ayr - Kalamia No 1 66 kV | Rating (A) | 199 | 199 | 199 | 199 | 199
NQ-Townsville Burdekin West | KA-AY-01_Ayr - Kalamia No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | KA-AY-01_Ayr - Kalamia No 1 66 kV | Min Voltage at Constrained Conductor | 68.4541 | 68.5822 | 68.7128 | 68.7763 | 68.7036
NQ-Townsville Burdekin West | KA-AY-01_Ayr - Kalamia No 1 66 kV | Contingency Outage | AY-PIMI_Ayr - Pioneer Mill 66 kV | AY-PIMI_Ayr - Pioneer Mill 66 kV | AY-PIMI_Ayr - Pioneer Mill 66 kV | MOPA_Clare South - Mona Park 66 kV | 7182 Ross - Milchester
NQ-Townsville Burdekin West | MAFU-07_Max Fulton No 7 11 kV | % of Rated A | 1.182% | 1.181% | 1.183% | 1.184% | 1.184%
NQ-Townsville Burdekin West | MAFU-07_Max Fulton No 7 11 kV | Limiting Line Name | HV_CABLE MF-07A 12159603 | HV_CABLE MF-07A 12159603 | HV_CABLE MF-07A 12159603 | HV_CABLE MF-07A 12159603 | HV_CABLE MF-07A 12159603
NQ-Townsville Burdekin West | MAFU-07_Max Fulton No 7 11 kV | Loading (A) | 3.7228 | 3.7215 | 3.7272 | 3.7282 | 3.7288
NQ-Townsville Burdekin West | MAFU-07_Max Fulton No 7 11 kV | Loading (MVA) | 0.072887 | 0.072837 | 0.073062 | 0.073103 | 0.073123
NQ-Townsville Burdekin West | MAFU-07_Max Fulton No 7 11 kV | Loading (MW) | 0.0014592 | 0.0014582 | 0.0014627 | 0.0014636 | 0.001464
NQ-Townsville Burdekin West | MAFU-07_Max Fulton No 7 11 kV | Power Factor | 0.020019 | 0.020019 | 0.020019 | 0.020019 | 0.020019
NQ-Townsville Burdekin West | MAFU-07_Max Fulton No 7 11 kV | Rating (A) | 315 | 315 | 315 | 315 | 315
NQ-Townsville Burdekin West | MAFU-07_Max Fulton No 7 11 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | MAFU-07_Max Fulton No 7 11 kV | Min Voltage at Constrained Conductor | 11.3039 | 11.3 | 11.3174 | 11.3206 | 11.3221
NQ-Townsville Burdekin West | MAFU-07_Max Fulton No 7 11 kV | Contingency Outage | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV
NQ-Townsville Burdekin West | MF-TP-1_Max Fulton-TOPO No 1 66 kV | % of Rated A | 3.587% | 5.347% | 4.536% | 3.844% | 3.145%
NQ-Townsville Burdekin West | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Limiting Line Name | TR_LINE 121605_1 | TR_LINE 121605_1 | TR_LINE 121605_1 | TR_LINE 121605_1 | TR_LINE 121605_1
NQ-Townsville Burdekin West | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Loading (A) | 9.2545 | 13.7952 | 11.704 | 9.9173 | 8.1151
NQ-Townsville Burdekin West | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Loading (MVA) | 1.0946 | 1.631 | 1.4064 | 1.1914 | 0.9746
NQ-Townsville Burdekin West | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Loading (MW) | 1.071 | 1.6164 | 1.3875 | 1.1685 | 0.94593
NQ-Townsville Burdekin West | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Power Factor | 0.97844 | 0.99102 | 0.9866 | 0.9808 | 0.97058
NQ-Townsville Burdekin West | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Rating (A) | 258 | 258 | 258 | 258 | 258
NQ-Townsville Burdekin West | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Min Voltage at Constrained Conductor | 68.2876 | 68.2584 | 69.3742 | 69.3598 | 69.3375
NQ-Townsville Burdekin West | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Contingency Outage | GA-TP-1_Garbutt-Townsville Port 1 66 kV | GA-TP-1_Garbutt-Townsville Port 1 66 kV | MF-TP-2_Max Fulton-TOPO No 2 66 kV | MF-TP-2_Max Fulton-TOPO No 2 66 kV | MF-TP-2_Max Fulton-TOPO No 2 66 kV
NQ-Townsville Burdekin West | MF-TP-2_Max Fulton-TOPO No 2 66 kV | % of Rated A | 15.03% | 15.51% | 15.14% | 14.96% | 14.81%
NQ-Townsville Burdekin West | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Limiting Line Name | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1
NQ-Townsville Burdekin West | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Loading (A) | 38.7682 | 40.0073 | 39.0638 | 38.6014 | 38.2051
NQ-Townsville Burdekin West | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Loading (MVA) | 4.6187 | 4.7654 | 4.7161 | 4.6613 | 4.6138
NQ-Townsville Burdekin West | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Loading (MW) | 1.0779 | 1.6232 | 1.3944 | 1.1754 | 0.95283
NQ-Townsville Burdekin West | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Power Factor | 0.23337 | 0.34062 | 0.29567 | 0.25217 | 0.20652
NQ-Townsville Burdekin West | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Rating (A) | 258 | 258 | 258 | 258 | 258
NQ-Townsville Burdekin West | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Min Voltage at Constrained Conductor | 68.7839 | 68.77 | 69.7019 | 69.7173 | 69.7231
NQ-Townsville Burdekin West | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Contingency Outage | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV
NQ-Townsville Burdekin West | MOPA_Clare South - Mona Park 66 kV | % of Rated A | 19.77% | 17.34% | 16.74% | 20.43% | 25.03%
NQ-Townsville Burdekin West | MOPA_Clare South - Mona Park 66 kV | Limiting Line Name | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1
NQ-Townsville Burdekin West | MOPA_Clare South - Mona Park 66 kV | Loading (A) | 41.5171 | 36.4193 | 35.1563 | 42.8991 | 52.5549
NQ-Townsville Burdekin West | MOPA_Clare South - Mona Park 66 kV | Loading (MVA) | 4.8718 | 4.2737 | 4.1269 | 5.0354 | 6.1679
NQ-Townsville Burdekin West | MOPA_Clare South - Mona Park 66 kV | Loading (MW) | 3.365 | 2.398 | 3.2261 | 4.3559 | 5.6637
NQ-Townsville Burdekin West | MOPA_Clare South - Mona Park 66 kV | Power Factor | 0.6907 | 0.5611 | 0.78172 | 0.86505 | 0.91824
NQ-Townsville Burdekin West | MOPA_Clare South - Mona Park 66 kV | Rating (A) | 210 | 210 | 210 | 210 | 210
NQ-Townsville Burdekin West | MOPA_Clare South - Mona Park 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | MOPA_Clare South - Mona Park 66 kV | Min Voltage at Constrained Conductor | 67.7492 | 67.751 | 67.774 | 67.7685 | 67.7584
NQ-Townsville Burdekin West | MOPA_Clare South - Mona Park 66 kV | Contingency Outage | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | AY-PIMI_Ayr - Pioneer Mill 66 kV | AY-PIMI_Ayr - Pioneer Mill 66 kV | AY-PIMI_Ayr - Pioneer Mill 66 kV
NQ-Townsville Burdekin West | MP-AY-1 Mona Park - Ayr No 1 66 kV | % of Rated A | 21.71% | 19.27% | 17.23% | 15.54% | 18.5%
NQ-Townsville Burdekin West | MP-AY-1 Mona Park - Ayr No 1 66 kV | Limiting Line Name | TR_LINE 32534_1 | TR_LINE 32534_1 | TR_LINE 32534_1 | TR_LINE 32534_1 | TR_LINE 32534_1
NQ-Townsville Burdekin West | MP-AY-1 Mona Park - Ayr No 1 66 kV | Loading (A) | 43.2106 | 38.3488 | 34.2941 | 30.9293 | 36.8111
NQ-Townsville Burdekin West | MP-AY-1 Mona Park - Ayr No 1 66 kV | Loading (MVA) | 5.0848 | 4.5172 | 4.0437 | 3.6501 | 4.3625
NQ-Townsville Burdekin West | MP-AY-1 Mona Park - Ayr No 1 66 kV | Loading (MW) | 4.0631 | 3.3192 | 2.6353 | 1.9853 | 3.8586
NQ-Townsville Burdekin West | MP-AY-1 Mona Park - Ayr No 1 66 kV | Power Factor | 0.79906 | 0.7348 | 0.6517 | 0.54391 | 0.88449
NQ-Townsville Burdekin West | MP-AY-1 Mona Park - Ayr No 1 66 kV | Rating (A) | 199 | 199 | 199 | 199 | 199
NQ-Townsville Burdekin West | MP-AY-1 Mona Park - Ayr No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | MP-AY-1 Mona Park - Ayr No 1 66 kV | Min Voltage at Constrained Conductor | 67.9394 | 68.0071 | 68.0764 | 68.1353 | 68.4215
NQ-Townsville Burdekin West | MP-AY-1 Mona Park - Ayr No 1 66 kV | Contingency Outage | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | AY-PIMI_Ayr - Pioneer Mill 66 kV
NQ-Townsville Burdekin West | MR-CR-1_Millchester-Cape River 1 66 kV | % of Rated A | 21.35% | 20.68% | 24.73% | 23.7% | 22.74%
NQ-Townsville Burdekin West | MR-CR-1_Millchester-Cape River 1 66 kV | Limiting Line Name | TR_LINE 198899_1 | TR_LINE 198899_1 | TR_LINE 198899_1 | TR_LINE 198899_1 | TR_LINE 198899_1
NQ-Townsville Burdekin West | MR-CR-1_Millchester-Cape River 1 66 kV | Loading (A) | 33.089 | 32.052 | 38.3302 | 36.7304 | 35.243
NQ-Townsville Burdekin West | MR-CR-1_Millchester-Cape River 1 66 kV | Loading (MVA) | 3.8975 | 3.7769 | 4.5075 | 4.3203 | 4.1465
NQ-Townsville Burdekin West | MR-CR-1_Millchester-Cape River 1 66 kV | Loading (MW) | 2.8785 | 2.5114 | 3.9587 | 3.6294 | 3.286
NQ-Townsville Burdekin West | MR-CR-1_Millchester-Cape River 1 66 kV | Power Factor | 0.73845 | 0.66484 | 0.87814 | 0.83999 | 0.79238
NQ-Townsville Burdekin West | MR-CR-1_Millchester-Cape River 1 66 kV | Rating (A) | 155 | 155 | 155 | 155 | 155
NQ-Townsville Burdekin West | MR-CR-1_Millchester-Cape River 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | MR-CR-1_Millchester-Cape River 1 66 kV | Min Voltage at Constrained Conductor | 68.006 | 68.0338 | 67.8948 | 67.9087 | 67.9286
NQ-Townsville Burdekin West | MR-CR-1_Millchester-Cape River 1 66 kV | Contingency Outage | CT-MR-1_Millchester-CHTO No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV
NQ-Townsville Burdekin West | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | % of Rated A | 30.19% | 30.18% | 30.16% | 30.15% | 30.15%
NQ-Townsville Burdekin West | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Limiting Line Name | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 49923_1
NQ-Townsville Burdekin West | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Loading (A) | 56.7554 | 56.7364 | 56.697 | 56.6879 | 56.6869
NQ-Townsville Burdekin West | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Loading (MVA) | 6.6766 | 6.6765 | 6.6763 | 6.6762 | 6.6762
NQ-Townsville Burdekin West | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Loading (MW) | 6.6761 | 6.676 | 6.6758 | 6.6758 | 6.6758
NQ-Townsville Burdekin West | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Power Factor | 0.99849 | 0.99849 | 0.99849 | 0.99849 | 0.99849
NQ-Townsville Burdekin West | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Rating (A) | 188 | 188 | 188 | 188 | 188
NQ-Townsville Burdekin West | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Min Voltage at Constrained Conductor | 66.6294 | 66.6515 | 66.6972 | 66.7078 | 66.7089
NQ-Townsville Burdekin West | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Contingency Outage | 7460 CPRE-JACR 132kV | 7460 CPRE-JACR 132kV | 7460 CPRE-JACR 132kV | 7460 CPRE-JACR 132kV | 7460 CPRE-JACR 132kV
NQ-Townsville Burdekin West | PA-RP-1_Peter Arlett-Ross Plains 66 kV | % of Rated A | 30.04% | 27.93% | 26.56% | 24.97% | 24.18%
NQ-Townsville Burdekin West | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Limiting Line Name | TR_LINE 32958_1 | TR_LINE 32958_1 | TR_LINE 45760_1 | TR_LINE 45760_1 | TR_LINE 45760_1
NQ-Townsville Burdekin West | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Loading (A) | 77.499 | 72.064 | 68.5143 | 64.412 | 62.3854
NQ-Townsville Burdekin West | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Loading (MVA) | 9.2392 | 8.5932 | 8.2654 | 7.7651 | 7.5197
NQ-Townsville Burdekin West | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Loading (MW) | 8.258 | 7.473 | 8.2244 | 7.7036 | 7.4511
NQ-Townsville Burdekin West | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Power Factor | 0.89367 | 0.86947 | 0.99504 | 0.99208 | 0.99089
NQ-Townsville Burdekin West | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Rating (A) | 258 | 258 | 258 | 258 | 258
NQ-Townsville Burdekin West | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Min Voltage at Constrained Conductor | 68.8253 | 68.8452 | 69.6476 | 69.5999 | 69.5892
NQ-Townsville Burdekin West | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Contingency Outage | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV
NQ-Townsville Burdekin West | PEAR-01_Hospital 3 11kV | % of Rated A | 0.3985% | 0.3987% | 0.3988% | 0.3989% | 0.3989%
NQ-Townsville Burdekin West | PEAR-01_Hospital 3 11kV | Limiting Line Name | PEAR-01 FEEDER C | PEAR-01 FEEDER C | PEAR-01 FEEDER C | PEAR-01 FEEDER C | PEAR-01 FEEDER C
NQ-Townsville Burdekin West | PEAR-01_Hospital 3 11kV | Loading (A) | 1.9287 | 1.9296 | 1.93 | 1.9306 | 1.9308
NQ-Townsville Burdekin West | PEAR-01_Hospital 3 11kV | Loading (MVA) | 0.037814 | 0.037851 | 0.037867 | 0.037887 | 0.037897
NQ-Townsville Burdekin West | PEAR-01_Hospital 3 11kV | Loading (MW) | 0.00075645 | 0.0007572 | 0.00075752 | 0.00075793 | 0.00075813
NQ-Townsville Burdekin West | PEAR-01_Hospital 3 11kV | Power Factor | 0.020005 | 0.020005 | 0.020005 | 0.020005 | 0.020005
NQ-Townsville Burdekin West | PEAR-01_Hospital 3 11kV | Rating (A) | 484 | 484 | 484 | 484 | 484
NQ-Townsville Burdekin West | PEAR-01_Hospital 3 11kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | PEAR-01_Hospital 3 11kV | Min Voltage at Constrained Conductor | 11.3194 | 11.325 | 11.3274 | 11.3305 | 11.332
NQ-Townsville Burdekin West | PEAR-01_Hospital 3 11kV | Contingency Outage | GA-TP-1_Garbutt-Townsville Port 1 66 kV | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV
NQ-Townsville Burdekin West | PEAR-06_Hospital 1 11kV | % of Rated A | 0.5626% | 0.5628% | 0.563% | 0.5631% | 0.5632%
NQ-Townsville Burdekin West | PEAR-06_Hospital 1 11kV | Limiting Line Name | PEAR-06 FEEDER A | PEAR-06 FEEDER A | PEAR-06 FEEDER A | PEAR-06 FEEDER A | PEAR-06 FEEDER A
NQ-Townsville Burdekin West | PEAR-06_Hospital 1 11kV | Loading (A) | 2.7228 | 2.7242 | 2.7247 | 2.7255 | 2.7258
NQ-Townsville Burdekin West | PEAR-06_Hospital 1 11kV | Loading (MVA) | 0.053383 | 0.053436 | 0.053458 | 0.053487 | 0.053502
NQ-Townsville Burdekin West | PEAR-06_Hospital 1 11kV | Loading (MW) | 0.0032757 | 0.0032789 | 0.0032803 | 0.003282 | 0.0032829
NQ-Townsville Burdekin West | PEAR-06_Hospital 1 11kV | Power Factor | 0.061361 | 0.061361 | 0.061361 | 0.061361 | 0.061361
NQ-Townsville Burdekin West | PEAR-06_Hospital 1 11kV | Rating (A) | 484 | 484 | 484 | 484 | 484
NQ-Townsville Burdekin West | PEAR-06_Hospital 1 11kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | PEAR-06_Hospital 1 11kV | Min Voltage at Constrained Conductor | 11.3194 | 11.325 | 11.3274 | 11.3305 | 11.332
NQ-Townsville Burdekin West | PEAR-06_Hospital 1 11kV | Contingency Outage | GA-TP-1_Garbutt-Townsville Port 1 66 kV | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV
NQ-Townsville Burdekin West | PEAR-12_Hospital 2 11kV | % of Rated A | 0.3933% | 0.3935% | 0.3936% | 0.3937% | 0.3938%
NQ-Townsville Burdekin West | PEAR-12_Hospital 2 11kV | Limiting Line Name | PEAR-12 FEEDER B | PEAR-12 FEEDER B | PEAR-12 FEEDER B | PEAR-12 FEEDER B | PEAR-12 FEEDER B
NQ-Townsville Burdekin West | PEAR-12_Hospital 2 11kV | Loading (A) | 1.9038 | 1.9047 | 1.9051 | 1.9056 | 1.9059
NQ-Townsville Burdekin West | PEAR-12_Hospital 2 11kV | Loading (MVA) | 0.037325 | 0.037362 | 0.037378 | 0.037398 | 0.037408
NQ-Townsville Burdekin West | PEAR-12_Hospital 2 11kV | Loading (MW) | 0.00074667 | 0.0007474 | 0.00074772 | 0.00074812 | 0.00074832
NQ-Townsville Burdekin West | PEAR-12_Hospital 2 11kV | Power Factor | 0.020004 | 0.020004 | 0.020004 | 0.020004 | 0.020004
NQ-Townsville Burdekin West | PEAR-12_Hospital 2 11kV | Rating (A) | 484 | 484 | 484 | 484 | 484
NQ-Townsville Burdekin West | PEAR-12_Hospital 2 11kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | PEAR-12_Hospital 2 11kV | Min Voltage at Constrained Conductor | 11.3194 | 11.325 | 11.3274 | 11.3305 | 11.332
NQ-Townsville Burdekin West | PEAR-12_Hospital 2 11kV | Contingency Outage | GA-TP-1_Garbutt-Townsville Port 1 66 kV | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV
NQ-Townsville Burdekin West | RI-10_Richmond No 10 33 kV | % of Rated A | 4.156e-09% | 4.177e-09% | 3.992e-09% | 4.012e-09% | 4.032e-09%
NQ-Townsville Burdekin West | RI-10_Richmond No 10 33 kV | Limiting Line Name | Link_RICH_RICH-A624_RI-10 RICHMOND 33KV | Link_RICH_RICH-A624_RI-10 RICHMOND 33KV | Link_RICH_RICH-A624_RI-10 RICHMOND 33KV | Link_RICH_RICH-A624_RI-10 RICHMOND 33KV | Link_RICH_RICH-A624_RI-10 RICHMOND 33KV
NQ-Townsville Burdekin West | RI-10_Richmond No 10 33 kV | Loading (A) | 2.078e-07 | 2.0883e-07 | 1.9961e-07 | 2.0061e-07 | 2.0161e-07
NQ-Townsville Burdekin West | RI-10_Richmond No 10 33 kV | Loading (MVA) | 1.2825e-08 | 1.2952e-08 | 1.1833e-08 | 1.1953e-08 | 1.2072e-08
NQ-Townsville Burdekin West | RI-10_Richmond No 10 33 kV | Loading (MW) | 1.2825e-08 | 1.2952e-08 | 1.1833e-08 | 1.1953e-08 | 1.2072e-08
NQ-Townsville Burdekin West | RI-10_Richmond No 10 33 kV | Power Factor | 1 | 1 | 1 | 1 | 1
NQ-Townsville Burdekin West | RI-10_Richmond No 10 33 kV | Rating (A) | 5000 | 5000 | 5000 | 5000 | 5000
NQ-Townsville Burdekin West | RI-10_Richmond No 10 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | RI-10_Richmond No 10 33 kV | Min Voltage at Constrained Conductor | 35.632 | 35.808 | 34.2274 | 34.3999 | 34.5711
NQ-Townsville Burdekin West | RI-10_Richmond No 10 33 kV | Contingency Outage | 6382 JACR-HUGH 132kV | 6382 JACR-HUGH 132kV | 6382 JACR-HUGH 132kV | 6382 JACR-HUGH 132kV | 6382 JACR-HUGH 132kV
NQ-Townsville Burdekin West | RI-20_Richmond No 20 33 kV | % of Rated A | 4.156e-09% | 4.177e-09% | 3.992e-09% | 4.012e-09% | 4.032e-09%
NQ-Townsville Burdekin West | RI-20_Richmond No 20 33 kV | Limiting Line Name | Link_RICH_RICH-B624_RI-20 JULIA CREEK 33 | Link_RICH_RICH-B624_RI-20 JULIA CREEK 33 | Link_RICH_RICH-B624_RI-20 JULIA CREEK 33 | Link_RICH_RICH-B624_RI-20 JULIA CREEK 33 | Link_RICH_RICH-B624_RI-20 JULIA CREEK 33
NQ-Townsville Burdekin West | RI-20_Richmond No 20 33 kV | Loading (A) | 2.078e-07 | 2.0883e-07 | 1.9961e-07 | 2.0061e-07 | 2.0161e-07
NQ-Townsville Burdekin West | RI-20_Richmond No 20 33 kV | Loading (MVA) | 1.2825e-08 | 1.2952e-08 | 1.1833e-08 | 1.1953e-08 | 1.2072e-08
NQ-Townsville Burdekin West | RI-20_Richmond No 20 33 kV | Loading (MW) | 1.2825e-08 | 1.2952e-08 | 1.1833e-08 | 1.1953e-08 | 1.2072e-08
NQ-Townsville Burdekin West | RI-20_Richmond No 20 33 kV | Power Factor | 1 | 1 | 1 | 1 | 1
NQ-Townsville Burdekin West | RI-20_Richmond No 20 33 kV | Rating (A) | 5000 | 5000 | 5000 | 5000 | 5000
NQ-Townsville Burdekin West | RI-20_Richmond No 20 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | RI-20_Richmond No 20 33 kV | Min Voltage at Constrained Conductor | 35.632 | 35.808 | 34.2274 | 34.3999 | 34.5711
NQ-Townsville Burdekin West | RI-20_Richmond No 20 33 kV | Contingency Outage | 6382 JACR-HUGH 132kV | 6382 JACR-HUGH 132kV | 6382 JACR-HUGH 132kV | 6382 JACR-HUGH 132kV | 6382 JACR-HUGH 132kV
NQ-Townsville Burdekin West | RI-50_Richmond No 50 33 kV | % of Rated A | 4.156e-09% | 4.177e-09% | 3.992e-09% | 4.012e-09% | 4.032e-09%
NQ-Townsville Burdekin West | RI-50_Richmond No 50 33 kV | Limiting Line Name | Link_RICH_RICH E624_RI-50 JULIA CREEK NO | Link_RICH_RICH E624_RI-50 JULIA CREEK NO | Link_RICH_RICH E624_RI-50 JULIA CREEK NO | Link_RICH_RICH E624_RI-50 JULIA CREEK NO | Link_RICH_RICH E624_RI-50 JULIA CREEK NO
NQ-Townsville Burdekin West | RI-50_Richmond No 50 33 kV | Loading (A) | 2.078e-07 | 2.0883e-07 | 1.9961e-07 | 2.0061e-07 | 2.0161e-07
NQ-Townsville Burdekin West | RI-50_Richmond No 50 33 kV | Loading (MVA) | 1.2825e-08 | 1.2952e-08 | 1.1833e-08 | 1.1953e-08 | 1.2072e-08
NQ-Townsville Burdekin West | RI-50_Richmond No 50 33 kV | Loading (MW) | 1.2825e-08 | 1.2952e-08 | 1.1833e-08 | 1.1953e-08 | 1.2072e-08
NQ-Townsville Burdekin West | RI-50_Richmond No 50 33 kV | Power Factor | 1 | 1 | 1 | 1 | 1
NQ-Townsville Burdekin West | RI-50_Richmond No 50 33 kV | Rating (A) | 5000 | 5000 | 5000 | 5000 | 5000
NQ-Townsville Burdekin West | RI-50_Richmond No 50 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | RI-50_Richmond No 50 33 kV | Min Voltage at Constrained Conductor | 35.632 | 35.808 | 34.2274 | 34.3999 | 34.5711
NQ-Townsville Burdekin West | RI-50_Richmond No 50 33 kV | Contingency Outage | 6382 JACR-HUGH 132kV | 6382 JACR-HUGH 132kV | 6382 JACR-HUGH 132kV | 6382 JACR-HUGH 132kV | 6382 JACR-HUGH 132kV
NQ-Townsville Burdekin West | RI-JC-1_Richmond-Julia Creek No 1 66 kV | % of Rated A | 5.543% | 5.564% | 6.406% | 6.401% | 6.403%
NQ-Townsville Burdekin West | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Limiting Line Name | TR_LINE 32331_1 | TR_LINE 32331_1 | TR_LINE 32331_1 | TR_LINE 32331_1 | TR_LINE 32331_1
NQ-Townsville Burdekin West | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Loading (A) | 19.6781 | 19.7505 | 22.7418 | 22.724 | 22.7321
NQ-Townsville Burdekin West | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Loading (MVA) | 2.581 | 2.6031 | 2.867 | 2.879 | 2.8941
NQ-Townsville Burdekin West | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Loading (MW) | 0.35605 | 0.32881 | 1.741 | 1.7273 | 1.7194
NQ-Townsville Burdekin West | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Power Factor | 0.13795 | 0.12632 | 0.60726 | 0.59998 | 0.59408
NQ-Townsville Burdekin West | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Rating (A) | 355 | 355 | 355 | 355 | 355
NQ-Townsville Burdekin West | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Min Voltage at Constrained Conductor | 75.7247 | 76.0945 | 72.7847 | 73.1464 | 73.5057
NQ-Townsville Burdekin West | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Contingency Outage | 6382 JACR-HUGH 132kV | 6382 JACR-HUGH 132kV | 6382 JACR-HUGH 132kV | 6382 JACR-HUGH 132kV | 6382 JACR-HUGH 132kV
NQ-Townsville Burdekin West | ST-GI-1_Stuart-Giru 66 kV | % of Rated A | 2.966% | 2.922% | 2.895% | 2.879% | 2.868%
NQ-Townsville Burdekin West | ST-GI-1_Stuart-Giru 66 kV | Limiting Line Name | TR_LINE 162083_1 | TR_LINE 162083_1 | TR_LINE 162083_1 | TR_LINE 162083_1 | TR_LINE 162083_1
NQ-Townsville Burdekin West | ST-GI-1_Stuart-Giru 66 kV | Loading (A) | 2.9066 | 2.864 | 2.8369 | 2.8216 | 2.8106
NQ-Townsville Burdekin West | ST-GI-1_Stuart-Giru 66 kV | Loading (MVA) | 0.34701 | 0.34194 | 0.3411 | 0.3392 | 0.33781
NQ-Townsville Burdekin West | ST-GI-1_Stuart-Giru 66 kV | Loading (MW) | 0.25958 | 0.25269 | 0.24843 | 0.24586 | 0.24402
NQ-Townsville Burdekin West | ST-GI-1_Stuart-Giru 66 kV | Power Factor | 0.74806 | 0.73897 | 0.72831 | 0.7248 | 0.72235
NQ-Townsville Burdekin West | ST-GI-1_Stuart-Giru 66 kV | Rating (A) | 98 | 98 | 98 | 98 | 98
NQ-Townsville Burdekin West | ST-GI-1_Stuart-Giru 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | ST-GI-1_Stuart-Giru 66 kV | Min Voltage at Constrained Conductor | 68.9269 | 68.9297 | 69.4174 | 69.4073 | 69.3911
NQ-Townsville Burdekin West | ST-GI-1_Stuart-Giru 66 kV | Contingency Outage | ST-WO-1_Stuart-Woodstock South 1 66 kV | ST-WO-1_Stuart-Woodstock South 1 66 kV | ST-WO-1_Stuart-Woodstock South 1 66 kV | ST-WO-1_Stuart-Woodstock South 1 66 kV | ST-WO-1_Stuart-Woodstock South 1 66 kV
NQ-Townsville Burdekin West | ST-GI-1_Stuart-Giru 66 kV To T Only | % of Rated A | 1.993% | 2% | 2.007% | 2.014% | 2.022%
NQ-Townsville Burdekin West | ST-GI-1_Stuart-Giru 66 kV To T Only | Limiting Line Name | TR_LINE 195987_1 | TR_LINE 195987_1 | TR_LINE 195987_1 | TR_LINE 195987_1 | TR_LINE 195987_1
NQ-Townsville Burdekin West | ST-GI-1_Stuart-Giru 66 kV To T Only | Loading (A) | 2.6306 | 2.6398 | 2.6492 | 2.6584 | 2.6693
NQ-Townsville Burdekin West | ST-GI-1_Stuart-Giru 66 kV To T Only | Loading (MVA) | 0.31327 | 0.31547 | 0.31771 | 0.31993 | 0.32254
NQ-Townsville Burdekin West | ST-GI-1_Stuart-Giru 66 kV To T Only | Loading (MW) | 8.1665e-05 | 8.2239e-05 | 8.2823e-05 | 8.3403e-05 | 8.4084e-05
NQ-Townsville Burdekin West | ST-GI-1_Stuart-Giru 66 kV To T Only | Power Factor | 0.00024573 | 0.00024573 | 0.00024573 | 0.00024573 | 0.00024573
NQ-Townsville Burdekin West | ST-GI-1_Stuart-Giru 66 kV To T Only | Rating (A) | 132 | 132 | 132 | 132 | 132
NQ-Townsville Burdekin West | ST-GI-1_Stuart-Giru 66 kV To T Only | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | ST-GI-1_Stuart-Giru 66 kV To T Only | Min Voltage at Constrained Conductor | 68.7547 | 68.9959 | 69.2404 | 69.4823 | 69.7653
NQ-Townsville Burdekin West | ST-GI-1_Stuart-Giru 66 kV To T Only | Contingency Outage | AY-PIMI_Ayr - Pioneer Mill 66 kV | AY-PIMI_Ayr - Pioneer Mill 66 kV | AY-PIMI_Ayr - Pioneer Mill 66 kV | AY-PIMI_Ayr - Pioneer Mill 66 kV | MOPA_Clare South - Mona Park 66 kV
NQ-Townsville Burdekin West | ST-RM-1_Stuart-Rasmussen 66 kV | % of Rated A | 7.49% | 8.905% | 10.18% | 11.41% | 12.68%
NQ-Townsville Burdekin West | ST-RM-1_Stuart-Rasmussen 66 kV | Limiting Line Name | TR_LINE 32428_1 | TR_LINE 32428_1 | TR_LINE 32428_1 | TR_LINE 32428_1 | TR_LINE 32428_1
NQ-Townsville Burdekin West | ST-RM-1_Stuart-Rasmussen 66 kV | Loading (A) | 41.2723 | 49.0677 | 56.0721 | 62.8775 | 69.8538
NQ-Townsville Burdekin West | ST-RM-1_Stuart-Rasmussen 66 kV | Loading (MVA) | 4.9382 | 5.8712 | 6.7539 | 7.5727 | 8.4113
NQ-Townsville Burdekin West | ST-RM-1_Stuart-Rasmussen 66 kV | Loading (MW) | 4.066 | 5.1919 | 6.1852 | 7.1005 | 8.0202
NQ-Townsville Burdekin West | ST-RM-1_Stuart-Rasmussen 66 kV | Power Factor | 0.82103 | 0.88148 | 0.91259 | 0.93402 | 0.94948
NQ-Townsville Burdekin West | ST-RM-1_Stuart-Rasmussen 66 kV | Rating (A) | 551 | 551 | 551 | 551 | 551
NQ-Townsville Burdekin West | ST-RM-1_Stuart-Rasmussen 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | ST-RM-1_Stuart-Rasmussen 66 kV | Min Voltage at Constrained Conductor | 69.0789 | 69.0832 | 69.5417 | 69.5336 | 69.5201
NQ-Townsville Burdekin West | ST-RM-1_Stuart-Rasmussen 66 kV | Contingency Outage | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV
NQ-Townsville Burdekin West | ST-RP-1_Stuart-Ross Plains 66 kV | % of Rated A | 10.37% | 9.002% | 10.87% | 10.15% | 9.66%
NQ-Townsville Burdekin West | ST-RP-1_Stuart-Ross Plains 66 kV | Limiting Line Name | TR_LINE 32392_1 | TR_LINE 32392_1 | TR_LINE 32425_1 | TR_LINE 32425_1 | TR_LINE 32425_1
NQ-Townsville Burdekin West | ST-RP-1_Stuart-Ross Plains 66 kV | Loading (A) | 70.394 | 61.1203 | 73.7817 | 68.9298 | 65.5917
NQ-Townsville Burdekin West | ST-RP-1_Stuart-Ross Plains 66 kV | Loading (MVA) | 8.4048 | 7.2991 | 8.887 | 8.2947 | 7.8908
NQ-Townsville Burdekin West | ST-RP-1_Stuart-Ross Plains 66 kV | Loading (MW) | 8.374 | 7.2536 | 7.7246 | 6.936 | 6.4195
NQ-Townsville Burdekin West | ST-RP-1_Stuart-Ross Plains 66 kV | Power Factor | 0.99633 | 0.99375 | 0.8692 | 0.83619 | 0.81354
NQ-Townsville Burdekin West | ST-RP-1_Stuart-Ross Plains 66 kV | Rating (A) | 679 | 679 | 679 | 679 | 679
NQ-Townsville Burdekin West | ST-RP-1_Stuart-Ross Plains 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | ST-RP-1_Stuart-Ross Plains 66 kV | Min Voltage at Constrained Conductor | 68.933 | 68.9481 | 69.5417 | 69.4757 | 69.4562
NQ-Townsville Burdekin West | ST-RP-1_Stuart-Ross Plains 66 kV | Contingency Outage | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV
NQ-Townsville Burdekin West | ST-TOPO-1_Stuart-Townsville Port 66 kV | % of Rated A | 28.48% | 27.4% | 27.83% | 25.42% | 23.04%
NQ-Townsville Burdekin West | ST-TOPO-1_Stuart-Townsville Port 66 kV | Limiting Line Name | TR_LINE 31745_2 | TR_LINE 31745_2 | TR_LINE 31745_2 | TR_LINE 31745_2 | TR_LINE 31745_2
NQ-Townsville Burdekin West | ST-TOPO-1_Stuart-Townsville Port 66 kV | Loading (A) | 71.4732 | 68.767 | 69.8468 | 63.797 | 57.8228
NQ-Townsville Burdekin West | ST-TOPO-1_Stuart-Townsville Port 66 kV | Loading (MVA) | 8.5757 | 8.2514 | 8.4268 | 7.6984 | 6.978
NQ-Townsville Burdekin West | ST-TOPO-1_Stuart-Townsville Port 66 kV | Loading (MW) | 7.0784 | 6.7792 | 6.8235 | 6.0244 | 5.2341
NQ-Townsville Burdekin West | ST-TOPO-1_Stuart-Townsville Port 66 kV | Power Factor | 0.8254 | 0.82158 | 0.80973 | 0.78254 | 0.7501
NQ-Townsville Burdekin West | ST-TOPO-1_Stuart-Townsville Port 66 kV | Rating (A) | 251 | 251 | 251 | 251 | 251
NQ-Townsville Burdekin West | ST-TOPO-1_Stuart-Townsville Port 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | ST-TOPO-1_Stuart-Townsville Port 66 kV | Min Voltage at Constrained Conductor | 69.2731 | 69.2763 | 69.6559 | 69.6694 | 69.6737
NQ-Townsville Burdekin West | ST-TOPO-1_Stuart-Townsville Port 66 kV | Contingency Outage | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV
NQ-Townsville Burdekin West | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | % of Rated A | 19.53% | 16.55% | 13.24% | 11.63% | 10.57%
NQ-Townsville Burdekin West | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Limiting Line Name | TR_LINE 157896_1 | TR_LINE 157896_1 | TR_LINE 157896_1 | TR_LINE 157896_1 | TR_LINE 157896_1
NQ-Townsville Burdekin West | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Loading (A) | 179.8794 | 152.4554 | 121.9312 | 107.109 | 97.3669
NQ-Townsville Burdekin West | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Loading (MVA) | 21.4971 | 18.2223 | 14.7101 | 12.9208 | 11.7436
NQ-Townsville Burdekin West | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Loading (MW) | 21.2961 | 17.9963 | 8.1397 | 4.7619 | 1.1015
NQ-Townsville Burdekin West | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Power Factor | 0.99064 | 0.98759 | 0.55333 | 0.36854 | 0.093789
NQ-Townsville Burdekin West | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Rating (A) | 921 | 921 | 921 | 921 | 921
NQ-Townsville Burdekin West | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Min Voltage at Constrained Conductor | 68.9978 | 69.0078 | 69.6528 | 69.6473 | 69.6354
NQ-Townsville Burdekin West | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Contingency Outage | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV
NQ-Townsville Burdekin West | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | % of Rated A | 19.72% | 16.71% | 13.37% | 11.74% | 10.67%
NQ-Townsville Burdekin West | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Limiting Line Name | TR_LINE 157898_1 | TR_LINE 157898_1 | TR_LINE 157898_1 | TR_LINE 157898_1 | TR_LINE 157898_1
NQ-Townsville Burdekin West | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Loading (A) | 181.6085 | 153.9213 | 123.1079 | 108.1454 | 98.3139
NQ-Townsville Burdekin West | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Loading (MVA) | 21.7057 | 18.3988 | 14.8515 | 13.0452 | 11.857
NQ-Townsville Burdekin West | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Loading (MW) | 21.5142 | 18.1817 | 8.2646 | 4.853 | 1.1558
NQ-Townsville Burdekin West | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Power Factor | 0.99117 | 0.98819 | 0.55647 | 0.37201 | 0.097469
NQ-Townsville Burdekin West | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Rating (A) | 921 | 921 | 921 | 921 | 921
NQ-Townsville Burdekin West | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Min Voltage at Constrained Conductor | 69.0039 | 69.0128 | 69.6503 | 69.6437 | 69.6307
NQ-Townsville Burdekin West | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Contingency Outage | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV
NQ-Townsville Burdekin West | ST-WO-1_Stuart-Woodstock South 1 66 kV | % of Rated A | 86.17% | 82.99% | 91.98% | 89.29% | 86.6%
NQ-Townsville Burdekin West | ST-WO-1_Stuart-Woodstock South 1 66 kV | Limiting Line Name | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1
NQ-Townsville Burdekin West | ST-WO-1_Stuart-Woodstock South 1 66 kV | Loading (A) | 113.7509 | 109.5418 | 121.4178 | 117.8624 | 114.3119
NQ-Townsville Burdekin West | ST-WO-1_Stuart-Woodstock South 1 66 kV | Loading (MVA) | 13.5606 | 13.074 | 14.5526 | 14.1379 | 13.7214
NQ-Townsville Burdekin West | ST-WO-1_Stuart-Woodstock South 1 66 kV | Loading (MW) | 9.7159 | 9.2116 | 10.6582 | 10.233 | 9.8091
NQ-Townsville Burdekin West | ST-WO-1_Stuart-Woodstock South 1 66 kV | Power Factor | 0.71169 | 0.70005 | 0.72718 | 0.7188 | 0.71009
NQ-Townsville Burdekin West | ST-WO-1_Stuart-Woodstock South 1 66 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
NQ-Townsville Burdekin West | ST-WO-1_Stuart-Woodstock South 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | ST-WO-1_Stuart-Woodstock South 1 66 kV | Min Voltage at Constrained Conductor | 68.7954 | 68.8883 | 69.1465 | 69.2131 | 69.2714
NQ-Townsville Burdekin West | ST-WO-1_Stuart-Woodstock South 1 66 kV | Contingency Outage | 7182 Ross - Milchester | 7182 Ross - Milchester | 7182 Ross - Milchester | 7182 Ross - Milchester | 7182 Ross - Milchester
NQ-Townsville Burdekin West | TOPO-08_Townsville Port No 8 11 kV | % of Rated A | 0.3288% | 0.3288% | 0.3307% | 0.3308% | 0.3308%
NQ-Townsville Burdekin West | TOPO-08_Townsville Port No 8 11 kV | Limiting Line Name | HV_CABLE TOPO-08A 12159494 | HV_CABLE TOPO-08A 12159494 | HV_CABLE TOPO-08A 12159494 | HV_CABLE TOPO-08A 12159494 | HV_CABLE TOPO-08A 12159494
NQ-Townsville Burdekin West | TOPO-08_Townsville Port No 8 11 kV | Loading (A) | 1.8413 | 1.8416 | 1.8518 | 1.8523 | 1.8526
NQ-Townsville Burdekin West | TOPO-08_Townsville Port No 8 11 kV | Loading (MVA) | 0.035066 | 0.035074 | 0.035466 | 0.035486 | 0.035496
NQ-Townsville Burdekin West | TOPO-08_Townsville Port No 8 11 kV | Loading (MW) | 0.0007015 | 0.00070166 | 0.00070952 | 0.00070991 | 0.00071011
NQ-Townsville Burdekin West | TOPO-08_Townsville Port No 8 11 kV | Power Factor | 0.020001 | 0.020001 | 0.020001 | 0.020001 | 0.020001
NQ-Townsville Burdekin West | TOPO-08_Townsville Port No 8 11 kV | Rating (A) | 560 | 560 | 560 | 560 | 560
NQ-Townsville Burdekin West | TOPO-08_Townsville Port No 8 11 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | TOPO-08_Townsville Port No 8 11 kV | Min Voltage at Constrained Conductor | 10.9948 | 10.996 | 11.0574 | 11.0605 | 11.062
NQ-Townsville Burdekin West | TOPO-08_Townsville Port No 8 11 kV | Contingency Outage | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV
NQ-Townsville Burdekin West | TP-NS-1_Townsville Port-NESM No 1 66 kV | % of Rated A | 12.23% | 12.05% | 11.74% | 11.63% | 11.58%
NQ-Townsville Burdekin West | TP-NS-1_Townsville Port-NESM No 1 66 kV | Limiting Line Name | TR_LINE 56322_1 | TR_LINE 56322_1 | TR_LINE 56322_1 | TR_LINE 56322_1 | TR_LINE 56322_1
NQ-Townsville Burdekin West | TP-NS-1_Townsville Port-NESM No 1 66 kV | Loading (A) | 31.5634 | 31.0893 | 30.2825 | 30.0101 | 29.864
NQ-Townsville Burdekin West | TP-NS-1_Townsville Port-NESM No 1 66 kV | Loading (MVA) | 3.7332 | 3.6756 | 3.6387 | 3.6052 | 3.5865
NQ-Townsville Burdekin West | TP-NS-1_Townsville Port-NESM No 1 66 kV | Loading (MW) | 3.6503 | 3.591 | 3.5461 | 3.5116 | 3.4923
NQ-Townsville Burdekin West | TP-NS-1_Townsville Port-NESM No 1 66 kV | Power Factor | 0.97779 | 0.97699 | 0.97455 | 0.97402 | 0.97374
NQ-Townsville Burdekin West | TP-NS-1_Townsville Port-NESM No 1 66 kV | Rating (A) | 258 | 258 | 258 | 258 | 258
NQ-Townsville Burdekin West | TP-NS-1_Townsville Port-NESM No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | TP-NS-1_Townsville Port-NESM No 1 66 kV | Min Voltage at Constrained Conductor | 68.282 | 68.2544 | 69.37 | 69.3552 | 69.3324
NQ-Townsville Burdekin West | TP-NS-1_Townsville Port-NESM No 1 66 kV | Contingency Outage | GA-TP-1_Garbutt-Townsville Port 1 66 kV | GA-TP-1_Garbutt-Townsville Port 1 66 kV | MF-TP-2_Max Fulton-TOPO No 2 66 kV | MF-TP-2_Max Fulton-TOPO No 2 66 kV | MF-TP-2_Max Fulton-TOPO No 2 66 kV
NQ-Townsville Burdekin West | WO-CT-1_Woodstock-CHTO No 1 66 kV | % of Rated A | 60.37% | 58.48% | 65.12% | 63.51% | 61.88%
NQ-Townsville Burdekin West | WO-CT-1_Woodstock-CHTO No 1 66 kV | Limiting Line Name | TR_LINE 32389_1 | TR_LINE 32389_1 | TR_LINE 32389_1 | TR_LINE 32389_1 | TR_LINE 32389_1
NQ-Townsville Burdekin West | WO-CT-1_Woodstock-CHTO No 1 66 kV | Loading (A) | 114.0951 | 110.5273 | 123.0765 | 120.026 | 116.9499
NQ-Townsville Burdekin West | WO-CT-1_Woodstock-CHTO No 1 66 kV | Loading (MVA) | 13.5936 | 13.1868 | 14.7369 | 14.3859 | 14.0295
NQ-Townsville Burdekin West | WO-CT-1_Woodstock-CHTO No 1 66 kV | Loading (MW) | 9.7279 | 9.3448 | 10.859 | 10.5297 | 10.198
NQ-Townsville Burdekin West | WO-CT-1_Woodstock-CHTO No 1 66 kV | Power Factor | 0.70104 | 0.69487 | 0.72079 | 0.71652 | 0.71213
NQ-Townsville Burdekin West | WO-CT-1_Woodstock-CHTO No 1 66 kV | Rating (A) | 189 | 189 | 189 | 189 | 189
NQ-Townsville Burdekin West | WO-CT-1_Woodstock-CHTO No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | WO-CT-1_Woodstock-CHTO No 1 66 kV | Min Voltage at Constrained Conductor | 68.7082 | 68.8258 | 68.9755 | 69.0636 | 69.1429
NQ-Townsville Burdekin West | WO-CT-1_Woodstock-CHTO No 1 66 kV | Contingency Outage | 7182 Ross - Milchester | 7182 Ross - Milchester | 7182 Ross - Milchester | 7182 Ross - Milchester | 7182 Ross - Milchester
SW-Bulli Creek Waggamba | 7235_Bulli Creek - Waggamba 132 kV | % of Rated A | 5.852% | 5.852% | 5.308% | 5.334% | 5.334%
SW-Bulli Creek Waggamba | 7235_Bulli Creek - Waggamba 132 kV | Limiting Line Name | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1
SW-Bulli Creek Waggamba | 7235_Bulli Creek - Waggamba 132 kV | Loading (A) | 38.0381 | 38.0377 | 34.5 | 34.6707 | 34.6713
SW-Bulli Creek Waggamba | 7235_Bulli Creek - Waggamba 132 kV | Loading (MVA) | 9.1214 | 9.1205 | 8.2704 | 8.4217 | 8.4223
SW-Bulli Creek Waggamba | 7235_Bulli Creek - Waggamba 132 kV | Loading (MW) | 6.1836 | 6.1836 | 4.7826 | 4.7824 | 4.7824
SW-Bulli Creek Waggamba | 7235_Bulli Creek - Waggamba 132 kV | Power Factor | 0.67791 | 0.67798 | 0.57827 | 0.56785 | 0.56781
SW-Bulli Creek Waggamba | 7235_Bulli Creek - Waggamba 132 kV | Rating (A) | 650 | 650 | 650 | 650 | 650
SW-Bulli Creek Waggamba | 7235_Bulli Creek - Waggamba 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Bulli Creek Waggamba | 7235_Bulli Creek - Waggamba 132 kV | Min Voltage at Constrained Conductor | 138.4462 | 138.4343 | 138.4035 | 140.2413 | 140.2481
SW-Bulli Creek Waggamba | 7235_Bulli Creek - Waggamba 132 kV | Contingency Outage | F099D_Warra 33 kV | F099D_Warra 33 kV | F099D_Warra 33 kV | F099D_Warra 33 kV | F3820_Boundary Road 33 kV
SW-Chinchilla Western Network | 3196_Tara 33 kV | % of Rated A | 8.867% | 8.667% | 8.529% | 8.43% | 8.357%
SW-Chinchilla Western Network | 3196_Tara 33 kV | Limiting Line Name | TR_LINE 27355_1 | TR_LINE 27355_1 | TR_LINE 27355_1 | TR_LINE 27355_1 | TR_LINE 27355_1
SW-Chinchilla Western Network | 3196_Tara 33 kV | Loading (A) | 8.2463 | 8.0599 | 7.932 | 7.8401 | 7.7721
SW-Chinchilla Western Network | 3196_Tara 33 kV | Loading (MVA) | 0.47547 | 0.46516 | 0.45811 | 0.45312 | 0.44953
SW-Chinchilla Western Network | 3196_Tara 33 kV | Loading (MW) | 0.20517 | 0.17544 | 0.15182 | 0.13203 | 0.1145
SW-Chinchilla Western Network | 3196_Tara 33 kV | Power Factor | 0.4315 | 0.37717 | 0.33141 | 0.29138 | 0.2547
SW-Chinchilla Western Network | 3196_Tara 33 kV | Rating (A) | 93 | 93 | 93 | 93 | 93
SW-Chinchilla Western Network | 3196_Tara 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Chinchilla Western Network | 3196_Tara 33 kV | Min Voltage at Constrained Conductor | 33.2892 | 33.3204 | 33.3447 | 33.3677 | 33.3933
SW-Chinchilla Western Network | 3196_Tara 33 kV | Contingency Outage | F099D_Warra 33 kV | F099D_Warra 33 kV | F099D_Warra 33 kV | F099D_Warra 33 kV | F099D_Warra 33 kV
SW-Chinchilla Western Network | 3203_Miles 33 kV | % of Rated A | 14.33% | 9.309% | 5.072% | 7.283% | 10.46%
SW-Chinchilla Western Network | 3203_Miles 33 kV | Limiting Line Name | HV_CABLE 219934_1 | HV_CABLE 219934_1 | HV_CABLE 219934_1 | HV_CABLE 219934_1 | HV_CABLE 219934_1
SW-Chinchilla Western Network | 3203_Miles 33 kV | Loading (A) | 25.9308 | 16.8501 | 9.1809 | 13.1813 | 18.9389
SW-Chinchilla Western Network | 3203_Miles 33 kV | Loading (MVA) | 1.5016 | 0.97598 | 0.53205 | 0.76436 | 1.0983
SW-Chinchilla Western Network | 3203_Miles 33 kV | Loading (MW) | 1.486 | 0.95124 | 0.48649 | 0.70838 | 1.0642
SW-Chinchilla Western Network | 3203_Miles 33 kV | Power Factor | 0.98963 | 0.97465 | 0.91436 | 0.92642 | 0.9687
SW-Chinchilla Western Network | 3203_Miles 33 kV | Rating (A) | 181 | 181 | 181 | 181 | 181
SW-Chinchilla Western Network | 3203_Miles 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Chinchilla Western Network | 3203_Miles 33 kV | Min Voltage at Constrained Conductor | 33.4325 | 33.4409 | 33.4587 | 33.4795 | 33.4821
SW-Chinchilla Western Network | 3203_Miles 33 kV | Contingency Outage | F069C_Brigalow 33 kV | F067C_Kogan 33 kV | 3166_Cameby Downs 33 kV | F077C_Wandoan 33 kV | F077C_Wandoan 33 kV
SW-Chinchilla Western Network | F001R_Yuleba 33 kV | % of Rated A | 16.27% | 16.26% | 16.25% | 16.24% | 16.24%
SW-Chinchilla Western Network | F001R_Yuleba 33 kV | Limiting Line Name | TR_LINE 28050_1 | TR_LINE 28050_1 | TR_LINE 28050_1 | TR_LINE 28050_1 | TR_LINE 28050_1
SW-Chinchilla Western Network | F001R_Yuleba 33 kV | Loading (A) | 15.1302 | 15.1255 | 15.117 | 15.1075 | 15.1034
SW-Chinchilla Western Network | F001R_Yuleba 33 kV | Loading (MVA) | 0.84357 | 0.84352 | 0.84344 | 0.84335 | 0.84331
SW-Chinchilla Western Network | F001R_Yuleba 33 kV | Loading (MW) | 0.7966 | 0.7966 | 0.7966 | 0.79661 | 0.79661
SW-Chinchilla Western Network | F001R_Yuleba 33 kV | Power Factor | 0.94432 | 0.94437 | 0.94447 | 0.94458 | 0.94462
SW-Chinchilla Western Network | F001R_Yuleba 33 kV | Rating (A) | 93 | 93 | 93 | 93 | 93
SW-Chinchilla Western Network | F001R_Yuleba 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Chinchilla Western Network | F001R_Yuleba 33 kV | Min Voltage at Constrained Conductor | 32.1895 | 32.1977 | 32.2127 | 32.2295 | 32.2367
SW-Chinchilla Western Network | F001R_Yuleba 33 kV | Contingency Outage | F217R_St George 66 kV | F217R_St George 66 kV | F217R_St George 66 kV | F217R_St George 66 kV | F217R_St George 66 kV
SW-Chinchilla Western Network | F022R_Brucedale 33 kV | % of Rated A | 11.52% | 11.51% | 11.51% | 11.5% | 11.5%
SW-Chinchilla Western Network | F022R_Brucedale 33 kV | Limiting Line Name | TR_LINE 22816_1 | TR_LINE 22816_1 | TR_LINE 22816_1 | TR_LINE 22816_1 | TR_LINE 22816_1
SW-Chinchilla Western Network | F022R_Brucedale 33 kV | Loading (A) | 10.711 | 10.7077 | 10.7017 | 10.6949 | 10.6921
SW-Chinchilla Western Network | F022R_Brucedale 33 kV | Loading (MVA) | 0.59704 | 0.59701 | 0.59695 | 0.59689 | 0.59686
SW-Chinchilla Western Network | F022R_Brucedale 33 kV | Loading (MW) | 0.58835 | 0.58835 | 0.58834 | 0.58833 | 0.58832
SW-Chinchilla Western Network | F022R_Brucedale 33 kV | Power Factor | 0.98522 | 0.98526 | 0.98534 | 0.98543 | 0.98546
SW-Chinchilla Western Network | F022R_Brucedale 33 kV | Rating (A) | 93 | 93 | 93 | 93 | 93
SW-Chinchilla Western Network | F022R_Brucedale 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Chinchilla Western Network | F022R_Brucedale 33 kV | Min Voltage at Constrained Conductor | 32.1819 | 32.1901 | 32.2051 | 32.222 | 32.2292
SW-Chinchilla Western Network | F022R_Brucedale 33 kV | Contingency Outage | F217R_St George 66 kV | F217R_St George 66 kV | F217R_St George 66 kV | F217R_St George 66 kV | F217R_St George 66 kV
SW-Chinchilla Western Network | F049R_Roma North 33 kV | % of Rated A | 26.94% | 26.94% | 26.94% | 26.94% | 26.94%
SW-Chinchilla Western Network | F049R_Roma North 33 kV | Limiting Line Name | TR_LINE 22900_1 | TR_LINE 22900_1 | TR_LINE 22900_1 | TR_LINE 22900_1 | TR_LINE 22900_1
SW-Chinchilla Western Network | F049R_Roma North 33 kV | Loading (A) | 25.0516 | 25.0516 | 25.0516 | 25.0516 | 25.0516
SW-Chinchilla Western Network | F049R_Roma North 33 kV | Loading (MVA) | 1.3997 | 1.3997 | 1.3997 | 1.3997 | 1.3997
SW-Chinchilla Western Network | F049R_Roma North 33 kV | Loading (MW) | 1.3346 | 1.3346 | 1.3346 | 1.3346 | 1.3346
SW-Chinchilla Western Network | F049R_Roma North 33 kV | Power Factor | 0.95355 | 0.95355 | 0.95355 | 0.95355 | 0.95355
SW-Chinchilla Western Network | F049R_Roma North 33 kV | Rating (A) | 93 | 93 | 93 | 93 | 93
SW-Chinchilla Western Network | F049R_Roma North 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Chinchilla Western Network | F049R_Roma North 33 kV | Min Voltage at Constrained Conductor | 32.2 | 32.2 | 32.2 | 32.2 | 32.2
SW-Chinchilla Western Network | F049R_Roma North 33 kV | Contingency Outage | F077S_Main Camp 33 kV | F077S_Main Camp 33 kV | F077S_Main Camp 33 kV | F077S_Main Camp 33 kV | F077S_Main Camp 33 kV
SW-Chinchilla Western Network | F060T_Tara 33 kV | % of Rated A | 8.951% | 8.784% | 8.674% | 8.599% | 8.547%
SW-Chinchilla Western Network | F060T_Tara 33 kV | Limiting Line Name | TR_LINE 104801_2 | TR_LINE 104801_2 | TR_LINE 104801_2 | TR_LINE 104801_2 | TR_LINE 104801_2
SW-Chinchilla Western Network | F060T_Tara 33 kV | Loading (A) | 8.3247 | 8.1694 | 8.067 | 7.997 | 7.9484
SW-Chinchilla Western Network | F060T_Tara 33 kV | Loading (MVA) | 0.47724 | 0.46878 | 0.46325 | 0.45955 | 0.45711
SW-Chinchilla Western Network | F060T_Tara 33 kV | Loading (MW) | 0.17708 | 0.14736 | 0.12374 | 0.10395 | 0.086418
SW-Chinchilla Western Network | F060T_Tara 33 kV | Power Factor | 0.37105 | 0.31435 | 0.26712 | 0.2262 | 0.18905
SW-Chinchilla Western Network | F060T_Tara 33 kV | Rating (A) | 93 | 93 | 93 | 93 | 93
SW-Chinchilla Western Network | F060T_Tara 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Chinchilla Western Network | F060T_Tara 33 kV | Min Voltage at Constrained Conductor | 33.0984 | 33.1298 | 33.1542 | 33.1773 | 33.203
SW-Chinchilla Western Network | F060T_Tara 33 kV | Contingency Outage | F099D_Warra 33 kV | F099D_Warra 33 kV | F099D_Warra 33 kV | F099D_Warra 33 kV | F099D_Warra 33 kV
SW-Chinchilla Western Network | F067C_Kogan 33 kV | % of Rated A | 52.04% | 52.01% | 51.99% | 51.96% | 52.78%
SW-Chinchilla Western Network | F067C_Kogan 33 kV | Limiting Line Name | TR_LINE 28354_1 | TR_LINE 28354_1 | TR_LINE 28354_1 | TR_LINE 28354_1 | TR_LINE 28354_1
SW-Chinchilla Western Network | F067C_Kogan 33 kV | Loading (A) | 48.3965 | 48.3705 | 48.3477 | 48.3268 | 49.0825
SW-Chinchilla Western Network | F067C_Kogan 33 kV | Loading (MVA) | 2.7606 | 2.7605 | 2.7603 | 2.7602 | 2.7632
SW-Chinchilla Western Network | F067C_Kogan 33 kV | Loading (MW) | 2.7364 | 2.7363 | 2.7362 | 2.7361 | 2.7386
SW-Chinchilla Western Network | F067C_Kogan 33 kV | Power Factor | 0.99121 | 0.99122 | 0.99124 | 0.99125 | 0.99109
SW-Chinchilla Western Network | F067C_Kogan 33 kV | Rating (A) | 93 | 93 | 93 | 93 | 93
SW-Chinchilla Western Network | F067C_Kogan 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Chinchilla Western Network | F067C_Kogan 33 kV | Min Voltage at Constrained Conductor | 32.921 | 32.9369 | 32.9509 | 32.9638 | 32.4905
SW-Chinchilla Western Network | F067C_Kogan 33 kV | Contingency Outage | F069C_Brigalow 33 kV | F069C_Brigalow 33 kV | F069C_Brigalow 33 kV | F069C_Brigalow 33 kV | F069C_Brigalow 33 kV
SW-Chinchilla Western Network | F069C_Brigalow 33 kV | % of Rated A | 9.684% | 20.73% | 31.66% | 42.77% | 55.17%
SW-Chinchilla Western Network | F069C_Brigalow 33 kV | Limiting Line Name | TR_LINE 28408_1 | TR_LINE 28408_1 | TR_LINE 28408_1 | TR_LINE 27354_1 | TR_LINE 27354_1
SW-Chinchilla Western Network | F069C_Brigalow 33 kV | Loading (A) | 8.5224 | 18.2448 | 27.8637 | 37.636 | 48.5492
SW-Chinchilla Western Network | F069C_Brigalow 33 kV | Loading (MVA) | 0.49135 | 1.0543 | 1.6136 | 2.1839 | 2.8093
SW-Chinchilla Western Network | F069C_Brigalow 33 kV | Loading (MW) | 0.48832 | 1.0537 | 1.6136 | 2.1834 | 2.8068
SW-Chinchilla Western Network | F069C_Brigalow 33 kV | Power Factor | 0.99384 | 0.99945 | 1 | 0.99977 | 0.99912
SW-Chinchilla Western Network | F069C_Brigalow 33 kV | Rating (A) | 88 | 88 | 88 | 88 | 88
SW-Chinchilla Western Network | F069C_Brigalow 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Chinchilla Western Network | F069C_Brigalow 33 kV | Min Voltage at Constrained Conductor | 33.2864 | 33.3635 | 33.4338 | 33.5 | 33.4062
SW-Chinchilla Western Network | F069C_Brigalow 33 kV | Contingency Outage | F067C_Kogan 33 kV | F067C_Kogan 33 kV | F067C_Kogan 33 kV | F067C_Kogan 33 kV | F083C_Chinchilla 33 kV
SW-Chinchilla Western Network | F071C RYWUNG | % of Rated A | 3.137% | 3.14% | 3.151% | 3.153% | 3.147%
SW-Chinchilla Western Network | F071C RYWUNG | Limiting Line Name | TR_LINE 199202_1 | TR_LINE 199202_1 | TR_LINE 199202_1 | TR_LINE 199202_1 | TR_LINE 199202_1
SW-Chinchilla Western Network | F071C RYWUNG | Loading (A) | 2.7601 | 2.7628 | 2.7726 | 2.7747 | 2.769
SW-Chinchilla Western Network | F071C RYWUNG | Loading (MVA) | 0.15866 | 0.15896 | 0.15965 | 0.15988 | 0.15967
SW-Chinchilla Western Network | F071C RYWUNG | Loading (MW) | 0.0081959 | 0.0081988 | 0.0076029 | 0.0076039 | 0.0082056
SW-Chinchilla Western Network | F071C RYWUNG | Power Factor | 0.051656 | 0.051577 | 0.047621 | 0.047559 | 0.051393
SW-Chinchilla Western Network | F071C RYWUNG | Rating (A) | 88 | 88 | 88 | 88 | 88
SW-Chinchilla Western Network | F071C RYWUNG | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Chinchilla Western Network | F071C RYWUNG | Min Voltage at Constrained Conductor | 33.1877 | 33.2185 | 33.2451 | 33.2686 | 33.2908
SW-Chinchilla Western Network | F071C RYWUNG | Contingency Outage | F067C_Kogan 33 kV | F067C_Kogan 33 kV | F067C_Kogan 33 kV | F067C_Kogan 33 kV | F067C_Kogan 33 kV
SW-Chinchilla Western Network | F073C_Fairymeadow 33 kV | % of Rated A | 3.892% | 3.89% | 3.888% | 3.882% | 3.906%
SW-Chinchilla Western Network | F073C_Fairymeadow 33 kV | Limiting Line Name | TR_LINE 174241_1 | TR_LINE 174241_1 | TR_LINE 174241_1 | TR_LINE 174241_1 | TR_LINE 174241_1
SW-Chinchilla Western Network | F073C_Fairymeadow 33 kV | Loading (A) | 3.6198 | 3.6177 | 3.616 | 3.6099 | 3.633
SW-Chinchilla Western Network | F073C_Fairymeadow 33 kV | Loading (MVA) | 0.20805 | 0.2081 | 0.20815 | 0.20793 | 0.20811
SW-Chinchilla Western Network | F073C_Fairymeadow 33 kV | Loading (MW) | 0.20356 | 0.20356 | 0.20357 | 0.20353 | 0.20358
SW-Chinchilla Western Network | F073C_Fairymeadow 33 kV | Power Factor | 0.97839 | 0.97818 | 0.978 | 0.97883 | 0.97826
SW-Chinchilla Western Network | F073C_Fairymeadow 33 kV | Rating (A) | 93 | 93 | 93 | 93 | 93
SW-Chinchilla Western Network | F073C_Fairymeadow 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Chinchilla Western Network | F073C_Fairymeadow 33 kV | Min Voltage at Constrained Conductor | 33.183 | 33.2103 | 33.2337 | 33.2539 | 33.0713
SW-Chinchilla Western Network | F073C_Fairymeadow 33 kV | Contingency Outage | F067C_Kogan 33 kV | F067C_Kogan 33 kV | F067C_Kogan 33 kV | F067C_Kogan 33 kV | F069C_Brigalow 33 kV
SW-Chinchilla Western Network | F074C_Miles-Condamine 33 kV | % of Rated A | 8.524% | 8.406% | 8.312% | 8.238% | 8.179%
SW-Chinchilla Western Network | F074C_Miles-Condamine 33 kV | Limiting Line Name | TR_LINE 138809_5 | TR_LINE 138809_5 | TR_LINE 138809_5 | TR_LINE 138809_5 | TR_LINE 138809_5
SW-Chinchilla Western Network | F074C_Miles-Condamine 33 kV | Loading (A) | 12.19 | 12.0207 | 11.8861 | 11.7799 | 11.6962
SW-Chinchilla Western Network | F074C_Miles-Condamine 33 kV | Loading (MVA) | 0.68988 | 0.6804 | 0.67337 | 0.66785 | 0.66355
SW-Chinchilla Western Network | F074C_Miles-Condamine 33 kV | Loading (MW) | 0.68789 | 0.67834 | 0.67123 | 0.66562 | 0.66124
SW-Chinchilla Western Network | F074C_Miles-Condamine 33 kV | Power Factor | 0.99711 | 0.99698 | 0.99682 | 0.99666 | 0.99652
SW-Chinchilla Western Network | F074C_Miles-Condamine 33 kV | Rating (A) | 143 | 143 | 143 | 143 | 143
SW-Chinchilla Western Network | F074C_Miles-Condamine 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Chinchilla Western Network | F074C_Miles-Condamine 33 kV | Min Voltage at Constrained Conductor | 32.6671 | 32.6719 | 32.7006 | 32.7252 | 32.7472
SW-Chinchilla Western Network | F074C_Miles-Condamine 33 kV | Contingency Outage | F069C_Brigalow 33 kV | F076C_Dulacca 33 kV | F076C_Dulacca 33 kV | F076C_Dulacca 33 kV | F076C_Dulacca 33 kV
SW-Chinchilla Western Network | F075S_St George Town 33 kV | % of Rated A | 3.412% | 2.923% | 2.556% | 2.259% | 2.039%
SW-Chinchilla Western Network | F075S_St George Town 33 kV | Limiting Line Name | TR_CABLE 16563_1 | TR_CABLE 16563_1 | TR_CABLE 16563_1 | TR_CABLE 16563_1 | TR_CABLE 16563_1
SW-Chinchilla Western Network | F075S_St George Town 33 kV | Loading (A) | 5.5952 | 4.7945 | 4.1918 | 3.7043 | 3.3439
SW-Chinchilla Western Network | F075S_St George Town 33 kV | Loading (MVA) | 0.31729 | 0.27184 | 0.23764 | 0.20998 | 0.18953
SW-Chinchilla Western Network | F075S_St George Town 33 kV | Loading (MW) | 0.31503 | 0.26916 | 0.23454 | 0.20644 | 0.18559
SW-Chinchilla Western Network | F075S_St George Town 33 kV | Power Factor | 0.99288 | 0.99015 | 0.98697 | 0.98318 | 0.97923
SW-Chinchilla Western Network | F075S_St George Town 33 kV | Rating (A) | 164 | 164 | 164 | 164 | 164
SW-Chinchilla Western Network | F075S_St George Town 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Chinchilla Western Network | F075S_St George Town 33 kV | Min Voltage at Constrained Conductor | 32.7401 | 32.7344 | 32.7312 | 32.7265 | 32.7227
SW-Chinchilla Western Network | F075S_St George Town 33 kV | Contingency Outage | F077S_Main Camp 33 kV | F077S_Main Camp 33 kV | F077S_Main Camp 33 kV | F077S_Main Camp 33 kV | F077S_Main Camp 33 kV
SW-Chinchilla Western Network | F076C_Dulacca 33 kV | % of Rated A | 2.458% | 2.435% | 2.436% | 2.438% | 2.439%
SW-Chinchilla Western Network | F076C_Dulacca 33 kV | Limiting Line Name | TR_LINE 27218_1 | TR_LINE 27218_1 | TR_LINE 27218_1 | TR_LINE 27218_1 | TR_LINE 27218_1
SW-Chinchilla Western Network | F076C_Dulacca 33 kV | Loading (A) | 2.8514 | 2.8245 | 2.8262 | 2.8277 | 2.8291
SW-Chinchilla Western Network | F076C_Dulacca 33 kV | Loading (MVA) | 0.16698 | 0.16384 | 0.16405 | 0.16423 | 0.16439
SW-Chinchilla Western Network | F076C_Dulacca 33 kV | Loading (MW) | 0.080506 | 0.080488 | 0.080489 | 0.08049 | 0.080491
SW-Chinchilla Western Network | F076C_Dulacca 33 kV | Power Factor | 0.48212 | 0.49125 | 0.49064 | 0.49011 | 0.48963
SW-Chinchilla Western Network | F076C_Dulacca 33 kV | Rating (A) | 116 | 116 | 116 | 116 | 116
SW-Chinchilla Western Network | F076C_Dulacca 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Chinchilla Western Network | F076C_Dulacca 33 kV | Min Voltage at Constrained Conductor | 33.8114 | 33.4915 | 33.5127 | 33.5309 | 33.5475
SW-Chinchilla Western Network | F076C_Dulacca 33 kV | Contingency Outage | F074C_Miles-Condamine 33 kV | F077C_Wandoan 33 kV | F077C_Wandoan 33 kV | F077C_Wandoan 33 kV | F077C_Wandoan 33 kV
SW-Chinchilla Western Network | F077C_Wandoan 33 kV | % of Rated A | 12.51% | 12.49% | 12.48% | 12.47% | 12.45%
SW-Chinchilla Western Network | F077C_Wandoan 33 kV | Limiting Line Name | TR_CABLE 126_1 | TR_CABLE 126_1 | TR_CABLE 126_1 | TR_CABLE 126_1 | TR_CABLE 126_1
SW-Chinchilla Western Network | F077C_Wandoan 33 kV | Loading (A) | 12.5107 | 12.4938 | 12.4788 | 12.4658 | 12.4541
SW-Chinchilla Western Network | F077C_Wandoan 33 kV | Loading (MVA) | 0.70805 | 0.70805 | 0.70805 | 0.70805 | 0.70805
SW-Chinchilla Western Network | F077C_Wandoan 33 kV | Loading (MW) | 0.58834 | 0.58834 | 0.58834 | 0.58834 | 0.58834
SW-Chinchilla Western Network | F077C_Wandoan 33 kV | Power Factor | 0.83068 | 0.83068 | 0.83068 | 0.83068 | 0.83068
SW-Chinchilla Western Network | F077C_Wandoan 33 kV | Rating (A) | 100 | 100 | 100 | 100 | 100
SW-Chinchilla Western Network | F077C_Wandoan 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Chinchilla Western Network | F077C_Wandoan 33 kV | Min Voltage at Constrained Conductor | 32.6758 | 32.7198 | 32.7592 | 32.7933 | 32.8242
SW-Chinchilla Western Network | F077C_Wandoan 33 kV | Contingency Outage | F076C_Dulacca 33 kV | F076C_Dulacca 33 kV | F076C_Dulacca 33 kV | F076C_Dulacca 33 kV | F076C_Dulacca 33 kV
SW-Chinchilla Western Network | F077S_Main Camp 33 kV | % of Rated A | 81.37% | 81.38% | 81.4% | 81.41% | 81.43%
SW-Chinchilla Western Network | F077S_Main Camp 33 kV | Limiting Line Name | TR_CABLE 16560_1 | TR_CABLE 16560_1 | TR_CABLE 16560_1 | TR_CABLE 16560_1 | TR_CABLE 16560_1
SW-Chinchilla Western Network | F077S_Main Camp 33 kV | Loading (A) | 81.3652 | 81.3849 | 81.3962 | 81.4123 | 81.4255
SW-Chinchilla Western Network | F077S_Main Camp 33 kV | Loading (MVA) | 4.6239 | 4.6241 | 4.6242 | 4.6244 | 4.6246
SW-Chinchilla Western Network | F077S_Main Camp 33 kV | Loading (MW) | 4.0945 | 4.0946 | 4.0946 | 4.0946 | 4.0947
SW-Chinchilla Western Network | F077S_Main Camp 33 kV | Power Factor | 0.88547 | 0.88543 | 0.88541 | 0.88538 | 0.88536
SW-Chinchilla Western Network | F077S_Main Camp 33 kV | Rating (A) | 100 | 100 | 100 | 100 | 100
SW-Chinchilla Western Network | F077S_Main Camp 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Chinchilla Western Network | F077S_Main Camp 33 kV | Min Voltage at Constrained Conductor | 32.8099 | 32.8036 | 32.8 | 32.7949 | 32.7907
SW-Chinchilla Western Network | F077S_Main Camp 33 kV | Contingency Outage | F081S_Noondoo 33 kV | F081S_Noondoo 33 kV | F081S_Noondoo 33 kV | F081S_Noondoo 33 kV | F081S_Noondoo 33 kV
SW-Chinchilla Western Network | F078S_Beardmore Dam 33 kV | % of Rated A | 3.532% | 3.532% | 3.533% | 3.533% | 3.533%
SW-Chinchilla Western Network | F078S_Beardmore Dam 33 kV | Limiting Line Name | TR_CABLE 4960_1 | TR_CABLE 4960_1 | TR_CABLE 4960_1 | TR_CABLE 4960_1 | TR_CABLE 4960_1
SW-Chinchilla Western Network | F078S_Beardmore Dam 33 kV | Loading (A) | 3.532 | 3.5324 | 3.5326 | 3.533 | 3.5332
SW-Chinchilla Western Network | F078S_Beardmore Dam 33 kV | Loading (MVA) | 0.19983 | 0.19983 | 0.19983 | 0.19983 | 0.19983
SW-Chinchilla Western Network | F078S_Beardmore Dam 33 kV | Loading (MW) | 0.18025 | 0.18025 | 0.18025 | 0.18025 | 0.18025
SW-Chinchilla Western Network | F078S_Beardmore Dam 33 kV | Power Factor | 0.90177 | 0.90177 | 0.90178 | 0.90178 | 0.90179
SW-Chinchilla Western Network | F078S_Beardmore Dam 33 kV | Rating (A) | 100 | 100 | 100 | 100 | 100
SW-Chinchilla Western Network | F078S_Beardmore Dam 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Chinchilla Western Network | F078S_Beardmore Dam 33 kV | Min Voltage at Constrained Conductor | 32.665 | 32.6609 | 32.659 | 32.6555 | 32.6529
SW-Chinchilla Western Network | F078S_Beardmore Dam 33 kV | Contingency Outage | F077S_Main Camp 33 kV | F077S_Main Camp 33 kV | F077S_Main Camp 33 kV | F077S_Main Camp 33 kV | F077S_Main Camp 33 kV
SW-Chinchilla Western Network | F079S_St George Meatworks 33 kV | % of Rated A | 24.68% | 23.59% | 22.62% | 21.74% | 20.88%
SW-Chinchilla Western Network | F079S_St George Meatworks 33 kV | Limiting Line Name | TR_CABLE 16561_1 | TR_CABLE 16561_1 | TR_CABLE 16561_1 | TR_CABLE 16561_1 | TR_CABLE 16561_1
SW-Chinchilla Western Network | F079S_St George Meatworks 33 kV | Loading (A) | 24.6774 | 23.5868 | 22.6229 | 21.7421 | 20.878
SW-Chinchilla Western Network | F079S_St George Meatworks 33 kV | Loading (MVA) | 1.3994 | 1.3373 | 1.2825 | 1.2324 | 1.1833
SW-Chinchilla Western Network | F079S_St George Meatworks 33 kV | Loading (MW) | 1.3471 | 1.2828 | 1.2258 | 1.1736 | 1.1223
SW-Chinchilla Western Network | F079S_St George Meatworks 33 kV | Power Factor | 0.96262 | 0.9592 | 0.95576 | 0.95227 | 0.94842
SW-Chinchilla Western Network | F079S_St George Meatworks 33 kV | Rating (A) | 100 | 100 | 100 | 100 | 100
SW-Chinchilla Western Network | F079S_St George Meatworks 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Chinchilla Western Network | F079S_St George Meatworks 33 kV | Min Voltage at Constrained Conductor | 32.7401 | 32.7344 | 32.7312 | 32.7265 | 32.7227
SW-Chinchilla Western Network | F079S_St George Meatworks 33 kV | Contingency Outage | F077S_Main Camp 33 kV | F077S_Main Camp 33 kV | F077S_Main Camp 33 kV | F077S_Main Camp 33 kV | F077S_Main Camp 33 kV
SW-Chinchilla Western Network | F081S_Noondoo 33 kV | % of Rated A | 45.77% | 45.78% | 45.78% | 45.8% | 45.8%
SW-Chinchilla Western Network | F081S_Noondoo 33 kV | Limiting Line Name | TR_CABLE 16562_1 | TR_CABLE 16562_1 | TR_CABLE 16562_1 | TR_CABLE 16562_1 | TR_CABLE 16562_1
SW-Chinchilla Western Network | F081S_Noondoo 33 kV | Loading (A) | 45.7664 | 45.7753 | 45.7843 | 45.7982 | 45.8032
SW-Chinchilla Western Network | F081S_Noondoo 33 kV | Loading (MVA) | 2.5953 | 2.5954 | 2.5956 | 2.596 | 2.596
SW-Chinchilla Western Network | F081S_Noondoo 33 kV | Loading (MW) | 2.5694 | 2.5695 | 2.5695 | 2.5696 | 2.5696
SW-Chinchilla Western Network | F081S_Noondoo 33 kV | Power Factor | 0.99001 | 0.99004 | 0.98995 | 0.98982 | 0.98984
SW-Chinchilla Western Network | F081S_Noondoo 33 kV | Rating (A) | 100 | 100 | 100 | 100 | 100
SW-Chinchilla Western Network | F081S_Noondoo 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Chinchilla Western Network | F081S_Noondoo 33 kV | Min Voltage at Constrained Conductor | 32.7399 | 32.7342 | 32.731 | 32.7263 | 32.7225
SW-Chinchilla Western Network | F081S_Noondoo 33 kV | Contingency Outage | F077S_Main Camp 33 kV | F077S_Main Camp 33 kV | F077S_Main Camp 33 kV | F077S_Main Camp 33 kV | F077S_Main Camp 33 kV
SW-Chinchilla Western Network | F083C_Chinchilla 33 kV | % of Rated A | 1.001% | 2.802% | 5.586% | 8.255% | 11.02%
SW-Chinchilla Western Network | F083C_Chinchilla 33 kV | Limiting Line Name | TR_LINE 195206_2 | TR_LINE 27121_1 | TR_LINE 27121_1 | TR_LINE 27121_1 | TR_LINE 27121_1
SW-Chinchilla Western Network | F083C_Chinchilla 33 kV | Loading (A) | 3.3441 | 9.3596 | 18.658 | 27.571 | 36.818
SW-Chinchilla Western Network | F083C_Chinchilla 33 kV | Loading (MVA) | 0.19222 | 0.53842 | 1.0741 | 1.5882 | 2.1092
SW-Chinchilla Western Network | F083C_Chinchilla 33 kV | Loading (MW) | 0.10456 | 0.51379 | 1.0624 | 1.5809 | 2.1046
SW-Chinchilla Western Network | F083C_Chinchilla 33 kV | Power Factor | 0.54398 | 0.95425 | 0.98914 | 0.99542 | 0.99778
SW-Chinchilla Western Network | F083C_Chinchilla 33 kV | Rating (A) | 334 | 334 | 334 | 334 | 334
SW-Chinchilla Western Network | F083C_Chinchilla 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Chinchilla Western Network | F083C_Chinchilla 33 kV | Min Voltage at Constrained Conductor | 33.1856 | 33.2125 | 33.2358 | 33.2562 | 33.0738
SW-Chinchilla Western Network | F083C_Chinchilla 33 kV | Contingency Outage | F067C_Kogan 33 kV | F067C_Kogan 33 kV | F067C_Kogan 33 kV | F067C_Kogan 33 kV | F069C_Brigalow 33 kV
SW-Chinchilla Western Network | F083S_Dirrabandi Town 33 kV | % of Rated A | 12.79% | 12.79% | 12.8% | 12.8% | 12.8%
SW-Chinchilla Western Network | F083S_Dirrabandi Town 33 kV | Limiting Line Name | TR_LINE 27419_1 | TR_LINE 27419_1 | TR_LINE 27419_1 | TR_LINE 27419_1 | TR_LINE 27419_1
SW-Chinchilla Western Network | F083S_Dirrabandi Town 33 kV | Loading (A) | 9.338 | 9.3399 | 9.3404 | 9.3413 | 9.3425
SW-Chinchilla Western Network | F083S_Dirrabandi Town 33 kV | Loading (MVA) | 0.51662 | 0.51662 | 0.51662 | 0.51662 | 0.51663
SW-Chinchilla Western Network | F083S_Dirrabandi Town 33 kV | Loading (MW) | 0.45763 | 0.45763 | 0.45763 | 0.45763 | 0.45763
SW-Chinchilla Western Network | F083S_Dirrabandi Town 33 kV | Power Factor | 0.88519 | 0.88518 | 0.88518 | 0.88518 | 0.88517
SW-Chinchilla Western Network | F083S_Dirrabandi Town 33 kV | Rating (A) | 73 | 73 | 73 | 73 | 73
SW-Chinchilla Western Network | F083S_Dirrabandi Town 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Chinchilla Western Network | F083S_Dirrabandi Town 33 kV | Min Voltage at Constrained Conductor | 31.9414 | 31.9352 | 31.9333 | 31.9306 | 31.9265
SW-Chinchilla Western Network | F083S_Dirrabandi Town 33 kV | Contingency Outage | F077S_Main Camp 33 kV | F077S_Main Camp 33 kV | F077S_Main Camp 33 kV | F077S_Main Camp 33 kV | F077S_Main Camp 33 kV
SW-Chinchilla Western Network | F106R_Roma East 33 kV | % of Rated A | 4.489% | 3.393% | 12.4% | 11.62% | 10.95%
SW-Chinchilla Western Network | F106R_Roma East 33 kV | Limiting Line Name | TR_LINE 44567_2 | TR_LINE 44567_2 | TR_LINE 44567_2 | TR_LINE 44567_2 | TR_LINE 44567_2
SW-Chinchilla Western Network | F106R_Roma East 33 kV | Loading (A) | 11.4929 | 8.6871 | 31.7544 | 29.7557 | 28.0255
SW-Chinchilla Western Network | F106R_Roma East 33 kV | Loading (MVA) | 0.64029 | 0.48419 | 1.768 | 1.6578 | 1.562
SW-Chinchilla Western Network | F106R_Roma East 33 kV | Loading (MW) | 0.63994 | 0.48376 | 1.7676 | 1.6575 | 1.5616
SW-Chinchilla Western Network | F106R_Roma East 33 kV | Power Factor | 0.99942 | 0.99907 | 0.99976 | 0.99976 | 0.99976
SW-Chinchilla Western Network | F106R_Roma East 33 kV | Rating (A) | 256 | 256 | 256 | 256 | 256
SW-Chinchilla Western Network | F106R_Roma East 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Chinchilla Western Network | F106R_Roma East 33 kV | Min Voltage at Constrained Conductor | 32.1647 | 32.1793 | 32.1417 | 32.1632 | 32.1743
SW-Chinchilla Western Network | F106R_Roma East 33 kV | Contingency Outage | F217R_St George 66 kV | F217R_St George 66 kV | F217R_St George 66 kV | F217R_St George 66 kV | F217R_St George 66 kV
SW-Chinchilla Western Network | F127R_Roma West 33 kV | % of Rated A | 4.667% | 3.394% | 2.332% | 1.398% | 0.595%
SW-Chinchilla Western Network | F127R_Roma West 33 kV | Limiting Line Name | TR_LINE 125467_1 | TR_LINE 125467_1 | TR_LINE 125467_1 | TR_LINE 125467_1 | TR_LINE 125467_1
SW-Chinchilla Western Network | F127R_Roma West 33 kV | Loading (A) | 5.4132 | 3.937 | 2.7051 | 1.6215 | 0.69019
SW-Chinchilla Western Network | F127R_Roma West 33 kV | Loading (MVA) | 0.30174 | 0.21953 | 0.15092 | 0.090516 | 0.038539
SW-Chinchilla Western Network | F127R_Roma West 33 kV | Loading (MW) | 0.30113 | 0.21864 | 0.14957 | 0.088206 | 0.032684
SW-Chinchilla Western Network | F127R_Roma West 33 kV | Power Factor | 0.99799 | 0.99595 | 0.99109 | 0.97448 | 0.84807
SW-Chinchilla Western Network | F127R_Roma West 33 kV | Rating (A) | 116 | 116 | 116 | 116 | 116
SW-Chinchilla Western Network | F127R_Roma West 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Chinchilla Western Network | F127R_Roma West 33 kV | Min Voltage at Constrained Conductor | 32.1819 | 32.193 | 32.2104 | 32.2294 | 32.2385
SW-Chinchilla Western Network | F127R_Roma West 33 kV | Contingency Outage | F217R_St George 66 kV | F217R_St George 66 kV | F217R_St George 66 kV | F217R_St George 66 kV | F217R_St George 66 kV
SW-Chinchilla Western Network | F187R_Mungallala 33 kV | % of Rated A | 0.0007853% | 0.0007877% | 0.0007985% | 0.0008041% | 0.0008075%
SW-Chinchilla Western Network | F187R_Mungallala 33 kV | Limiting Line Name | TR_LINE 12064483_1 | TR_LINE 12064483_1 | TR_LINE 12064483_1 | TR_LINE 12064483_1 | TR_LINE 12064483_1
SW-Chinchilla Western Network | F187R_Mungallala 33 kV | Loading (A) | 0.0020103 | 0.0020166 | 0.0020442 | 0.0020586 | 0.0020671
SW-Chinchilla Western Network | F187R_Mungallala 33 kV | Loading (MVA) | 0.00011343 | 0.00011414 | 0.00011728 | 0.00011894 | 0.00011993
SW-Chinchilla Western Network | F187R_Mungallala 33 kV | Loading (MW) | 1.0724e-08 | 1.0787e-08 | 1.1092e-08 | 1.1262e-08 | 1.134e-08
SW-Chinchilla Western Network | F187R_Mungallala 33 kV | Power Factor | 9.4541e-05 | 9.4506e-05 | 9.4561e-05 | 9.4687e-05 | 9.4557e-05
SW-Chinchilla Western Network | F187R_Mungallala 33 kV | Rating (A) | 256 | 256 | 256 | 256 | 256
SW-Chinchilla Western Network | F187R_Mungallala 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Chinchilla Western Network | F187R_Mungallala 33 kV | Min Voltage at Constrained Conductor | 32.5757 | 32.6782 | 33.1251 | 33.3583 | 33.4969
SW-Chinchilla Western Network | F187R_Mungallala 33 kV | Contingency Outage | F077S_Main Camp 33 kV | F077S_Main Camp 33 kV | F077S_Main Camp 33 kV | F077S_Main Camp 33 kV | F077S_Main Camp 33 kV
SW-Chinchilla Western Network | F217R_St George 66 kV | % of Rated A | 21.51% | 21.23% | 21.02% | 20.81% | 20.62%
SW-Chinchilla Western Network | F217R_St George 66 kV | Limiting Line Name | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1
SW-Chinchilla Western Network | F217R_St George 66 kV | Loading (A) | 96.1446 | 94.8774 | 93.9609 | 93.0057 | 92.1814
SW-Chinchilla Western Network | F217R_St George 66 kV | Loading (MVA) | 10.7826 | 10.643 | 10.5383 | 10.434 | 10.3431
SW-Chinchilla Western Network | F217R_St George 66 kV | Loading (MW) | 9.2591 | 9.1228 | 9.0123 | 8.9128 | 8.8242
SW-Chinchilla Western Network | F217R_St George 66 kV | Power Factor | 0.8587 | 0.85716 | 0.85519 | 0.8542 | 0.85314
SW-Chinchilla Western Network | F217R_St George 66 kV | Rating (A) | 447 | 447 | 447 | 447 | 447
SW-Chinchilla Western Network | F217R_St George 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Chinchilla Western Network | F217R_St George 66 kV | Min Voltage at Constrained Conductor | 64.7497 | 64.7651 | 64.7535 | 64.7712 | 64.781
SW-Chinchilla Western Network | F217R_St George 66 kV | Contingency Outage | 7374_Roma Power Station 132 kV | 7374_Roma Power Station 132 kV | F127R_Roma West 33 kV | F127R_Roma West 33 kV | F127R_Roma West 33 kV
SW-Toowoomba Dalby Warwick | 3153_Cecil Plains Road 33 kV | % of Rated A | 66.02% | 66.42% | 66.38% | 66.34% | 66.3%
SW-Toowoomba Dalby Warwick | 3153_Cecil Plains Road 33 kV | Limiting Line Name | TR_LINE 183124_2 | TR_LINE 183124_2 | TR_LINE 183124_2 | TR_LINE 183124_2 | TR_LINE 183124_2
SW-Toowoomba Dalby Warwick | 3153_Cecil Plains Road 33 kV | Loading (A) | 61.3987 | 61.7714 | 61.7346 | 61.6994 | 61.6584
SW-Toowoomba Dalby Warwick | 3153_Cecil Plains Road 33 kV | Loading (MVA) | 3.5872 | 3.5881 | 3.588 | 3.5879 | 3.5878
SW-Toowoomba Dalby Warwick | 3153_Cecil Plains Road 33 kV | Loading (MW) | 3.5691 | 3.5695 | 3.5695 | 3.5694 | 3.5694
SW-Toowoomba Dalby Warwick | 3153_Cecil Plains Road 33 kV | Power Factor | 0.99495 | 0.99483 | 0.99484 | 0.99485 | 0.99486
SW-Toowoomba Dalby Warwick | 3153_Cecil Plains Road 33 kV | Rating (A) | 93 | 93 | 93 | 93 | 93
SW-Toowoomba Dalby Warwick | 3153_Cecil Plains Road 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | 3153_Cecil Plains Road 33 kV | Min Voltage at Constrained Conductor | 33.7286 | 33.5338 | 33.5529 | 33.5712 | 33.5926
SW-Toowoomba Dalby Warwick | 3153_Cecil Plains Road 33 kV | Contingency Outage | F5545_7245 Tangkam-Dalby 110 kV | F099D_Warra 33 kV | F099D_Warra 33 kV | F099D_Warra 33 kV | F099D_Warra 33 kV
SW-Toowoomba Dalby Warwick | 3154_Central Dalby 1 33 kV | % of Rated A | 6.534% | 4.465% | 4.843% | 5.777% | 6.689%
SW-Toowoomba Dalby Warwick | 3154_Central Dalby 1 33 kV | Limiting Line Name | TR_CABLE 4402_1 | TR_CABLE 4402_1 | TR_CABLE 4402_1 | TR_CABLE 4402_1 | TR_CABLE 4402_1
SW-Toowoomba Dalby Warwick | 3154_Central Dalby 1 33 kV | Loading (A) | 29.4019 | 20.0909 | 21.7918 | 25.9976 | 30.0997
SW-Toowoomba Dalby Warwick | 3154_Central Dalby 1 33 kV | Loading (MVA) | 1.7216 | 1.178 | 1.2815 | 1.5301 | 1.7731
SW-Toowoomba Dalby Warwick | 3154_Central Dalby 1 33 kV | Loading (MW) | 1.7216 | 1.1769 | 1.2786 | 1.5261 | 1.768
SW-Toowoomba Dalby Warwick | 3154_Central Dalby 1 33 kV | Power Factor | 0.99982 | 0.99834 | 0.99771 | 0.99743 | 0.99716
SW-Toowoomba Dalby Warwick | 3154_Central Dalby 1 33 kV | Rating (A) | 450 | 450 | 450 | 450 | 450
SW-Toowoomba Dalby Warwick | 3154_Central Dalby 1 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | 3154_Central Dalby 1 33 kV | Min Voltage at Constrained Conductor | 33.8059 | 33.8514 | 33.9519 | 33.979 | 34.0087
SW-Toowoomba Dalby Warwick | 3154_Central Dalby 1 33 kV | Contingency Outage | F019D_West Dalby No 1 33 kV | F019D_West Dalby No 1 33 kV | F039D_West Dalby No 2 33 kV | F039D_West Dalby No 2 33 kV | F039D_West Dalby No 2 33 kV
SW-Toowoomba Dalby Warwick | 3178_Wilkie Creek 33 kV | % of Rated A | 4.163% | 4.166% | 4.169% | 4.171% | 4.174%
SW-Toowoomba Dalby Warwick | 3178_Wilkie Creek 33 kV | Limiting Line Name | TR_CABLE 3771_1 | TR_CABLE 3771_1 | TR_CABLE 3771_1 | TR_CABLE 3771_1 | TR_CABLE 3771_1
SW-Toowoomba Dalby Warwick | 3178_Wilkie Creek 33 kV | Loading (A) | 3.8715 | 3.8745 | 3.8769 | 3.8791 | 3.8818
SW-Toowoomba Dalby Warwick | 3178_Wilkie Creek 33 kV | Loading (MVA) | 0.22289 | 0.22323 | 0.2235 | 0.22376 | 0.22406
SW-Toowoomba Dalby Warwick | 3178_Wilkie Creek 33 kV | Loading (MW) | 0.0082378 | 0.0082402 | 0.008242 | 0.0082438 | 0.0082459
SW-Toowoomba Dalby Warwick | 3178_Wilkie Creek 33 kV | Power Factor | 0.036959 | 0.036913 | 0.036877 | 0.036843 | 0.036802
SW-Toowoomba Dalby Warwick | 3178_Wilkie Creek 33 kV | Rating (A) | 93 | 93 | 93 | 93 | 93
SW-Toowoomba Dalby Warwick | 3178_Wilkie Creek 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | 3178_Wilkie Creek 33 kV | Min Voltage at Constrained Conductor | 33.2389 | 33.2643 | 33.284 | 33.3031 | 33.3253
SW-Toowoomba Dalby Warwick | 3178_Wilkie Creek 33 kV | Contingency Outage | F099D_Warra 33 kV | F099D_Warra 33 kV | F099D_Warra 33 kV | F099D_Warra 33 kV | F099D_Warra 33 kV
SW-Toowoomba Dalby Warwick | 3282_Killarney 33kV | % of Rated A | 5.021% | 5.718% | 6.285% | 6.767% | 7.181%
SW-Toowoomba Dalby Warwick | 3282_Killarney 33kV | Limiting Line Name | TR_LINE 23736_3 | TR_LINE 23736_3 | TR_LINE 23736_3 | TR_LINE 23736_3 | TR_LINE 23736_3
SW-Toowoomba Dalby Warwick | 3282_Killarney 33kV | Loading (A) | 5.8247 | 6.6327 | 7.291 | 7.8502 | 8.3301
SW-Toowoomba Dalby Warwick | 3282_Killarney 33kV | Loading (MVA) | 0.3516 | 0.40046 | 0.44019 | 0.47397 | 0.50309
SW-Toowoomba Dalby Warwick | 3282_Killarney 33kV | Loading (MW) | 0.3193 | 0.37288 | 0.41567 | 0.45165 | 0.48242
SW-Toowoomba Dalby Warwick | 3282_Killarney 33kV | Power Factor | 0.90711 | 0.92993 | 0.94298 | 0.95148 | 0.95738
SW-Toowoomba Dalby Warwick | 3282_Killarney 33kV | Rating (A) | 116 | 116 | 116 | 116 | 116
SW-Toowoomba Dalby Warwick | 3282_Killarney 33kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | 3282_Killarney 33kV | Min Voltage at Constrained Conductor | 34.8507 | 34.8584 | 34.8568 | 34.8587 | 34.869
SW-Toowoomba Dalby Warwick | 3282_Killarney 33kV | Contingency Outage | 790_Warwick-Stanthorpe 110 kV | 790_Warwick-Stanthorpe 110 kV | 790_Warwick-Stanthorpe 110 kV | 790_Warwick-Stanthorpe 110 kV | 790_Warwick-Stanthorpe 110 kV
SW-Toowoomba Dalby Warwick | 3283_Allora 33kV | % of Rated A | 13.68% | 14.98% | 16.01% | 16.85% | 17.56%
SW-Toowoomba Dalby Warwick | 3283_Allora 33kV | Limiting Line Name | TR_LINE ALLORA-pole2134509_a | TR_LINE ALLORA-pole2134509_a | TR_LINE ALLORA-pole2134509_a | TR_LINE ALLORA-pole2134509_a | TR_LINE ALLORA-pole2134509_a
SW-Toowoomba Dalby Warwick | 3283_Allora 33kV | Loading (A) | 22.5741 | 24.7241 | 26.4112 | 27.8096 | 28.9744
SW-Toowoomba Dalby Warwick | 3283_Allora 33kV | Loading (MVA) | 1.3836 | 1.5178 | 1.6231 | 1.7107 | 1.7843
SW-Toowoomba Dalby Warwick | 3283_Allora 33kV | Loading (MW) | 1.3835 | 1.5177 | 1.623 | 1.7105 | 1.784
SW-Toowoomba Dalby Warwick | 3283_Allora 33kV | Power Factor | 0.99993 | 0.99991 | 0.9999 | 0.99989 | 0.99988
SW-Toowoomba Dalby Warwick | 3283_Allora 33kV | Rating (A) | 165 | 165 | 165 | 165 | 165
SW-Toowoomba Dalby Warwick | 3283_Allora 33kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | 3283_Allora 33kV | Min Voltage at Constrained Conductor | 35.3853 | 35.4434 | 35.4813 | 35.5158 | 35.5532
SW-Toowoomba Dalby Warwick | 3283_Allora 33kV | Contingency Outage | 790_Warwick-Stanthorpe 110 kV | 790_Warwick-Stanthorpe 110 kV | 790_Warwick-Stanthorpe 110 kV | 790_Warwick-Stanthorpe 110 kV | 790_Warwick-Stanthorpe 110 kV
SW-Toowoomba Dalby Warwick | 3900_Peranga 33 kV | % of Rated A | 5.983% | 6.171% | 6.319% | 6.445% | 6.532%
SW-Toowoomba Dalby Warwick | 3900_Peranga 33 kV | Limiting Line Name | TR_CABLE 9120_1 | TR_CABLE 9120_1 | TR_CABLE 9120_1 | TR_CABLE 9120_1 | TR_CABLE 9120_1
SW-Toowoomba Dalby Warwick | 3900_Peranga 33 kV | Loading (A) | 5.9834 | 6.1713 | 6.3195 | 6.4453 | 6.5317
SW-Toowoomba Dalby Warwick | 3900_Peranga 33 kV | Loading (MVA) | 0.34807 | 0.35899 | 0.36757 | 0.37487 | 0.37991
SW-Toowoomba Dalby Warwick | 3900_Peranga 33 kV | Loading (MW) | 0.27893 | 0.29262 | 0.30323 | 0.31216 | 0.31826
SW-Toowoomba Dalby Warwick | 3900_Peranga 33 kV | Power Factor | 0.80084 | 0.81462 | 0.82446 | 0.83222 | 0.83725
SW-Toowoomba Dalby Warwick | 3900_Peranga 33 kV | Rating (A) | 100 | 100 | 100 | 100 | 100
SW-Toowoomba Dalby Warwick | 3900_Peranga 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | 3900_Peranga 33 kV | Min Voltage at Constrained Conductor | 33.586 | 33.5851 | 33.5817 | 33.5798 | 33.5809
SW-Toowoomba Dalby Warwick | 3900_Peranga 33 kV | Contingency Outage | 790_Warwick-Stanthorpe 110 kV | 790_Warwick-Stanthorpe 110 kV | 790_Warwick-Stanthorpe 110 kV | 790_Warwick-Stanthorpe 110 kV | 790_Warwick-Stanthorpe 110 kV
SW-Toowoomba Dalby Warwick | 7233_Middle Ridge-Torrington 110 kV | % of Rated A | 4.483% | 6.786% | 9.033% | 8.877% | 7.041%
SW-Toowoomba Dalby Warwick | 7233_Middle Ridge-Torrington 110 kV | Limiting Line Name | TR_LINE 27024_1 | TR_LINE 27024_1 | TR_LINE 27024_1 | TR_LINE 27024_1 | TR_LINE 27024_1
SW-Toowoomba Dalby Warwick | 7233_Middle Ridge-Torrington 110 kV | Loading (A) | 39.3631 | 59.5783 | 79.3106 | 77.9381 | 61.8191
SW-Toowoomba Dalby Warwick | 7233_Middle Ridge-Torrington 110 kV | Loading (MVA) | 7.8636 | 11.8995 | 15.8343 | 15.5566 | 12.3399
SW-Toowoomba Dalby Warwick | 7233_Middle Ridge-Torrington 110 kV | Loading (MW) | 6.3247 | 11.1217 | 15.4098 | 15.2217 | 11.1209
SW-Toowoomba Dalby Warwick | 7233_Middle Ridge-Torrington 110 kV | Power Factor | 0.80395 | 0.93411 | 0.97249 | 0.97778 | 0.90067
SW-Toowoomba Dalby Warwick | 7233_Middle Ridge-Torrington 110 kV | Rating (A) | 878 | 878 | 878 | 878 | 878
SW-Toowoomba Dalby Warwick | 7233_Middle Ridge-Torrington 110 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | 7233_Middle Ridge-Torrington 110 kV | Min Voltage at Constrained Conductor | 115.3383 | 115.3136 | 115.2678 | 115.2399 | 115.2463
SW-Toowoomba Dalby Warwick | 7233_Middle Ridge-Torrington 110 kV | Contingency Outage | 7234_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV
SW-Toowoomba Dalby Warwick | 7234_Middle Ridge-Torrington 110 kV | % of Rated A | 4.483% | 6.787% | 9.035% | 8.878% | 7.054%
SW-Toowoomba Dalby Warwick | 7234_Middle Ridge-Torrington 110 kV | Limiting Line Name | TR_LINE 27022_1 | TR_LINE 27022_1 | TR_LINE 27022_1 | TR_LINE 27022_1 | TR_LINE 27022_1
SW-Toowoomba Dalby Warwick | 7234_Middle Ridge-Torrington 110 kV | Loading (A) | 39.3624 | 59.5871 | 79.324 | 77.9495 | 61.9366
SW-Toowoomba Dalby Warwick | 7234_Middle Ridge-Torrington 110 kV | Loading (MVA) | 7.8635 | 11.9013 | 15.837 | 15.5589 | 12.3633
SW-Toowoomba Dalby Warwick | 7234_Middle Ridge-Torrington 110 kV | Loading (MW) | 6.3246 | 11.1215 | 15.4093 | 15.2212 | 11.147
SW-Toowoomba Dalby Warwick | 7234_Middle Ridge-Torrington 110 kV | Power Factor | 0.80396 | 0.93395 | 0.97229 | 0.97761 | 0.90107
SW-Toowoomba Dalby Warwick | 7234_Middle Ridge-Torrington 110 kV | Rating (A) | 878 | 878 | 878 | 878 | 878
SW-Toowoomba Dalby Warwick | 7234_Middle Ridge-Torrington 110 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | 7234_Middle Ridge-Torrington 110 kV | Min Voltage at Constrained Conductor | 115.3383 | 115.3137 | 115.2681 | 115.2401 | 115.2463
SW-Toowoomba Dalby Warwick | 7234_Middle Ridge-Torrington 110 kV | Contingency Outage | 7233_Middle Ridge-Torrington 110 kV | 7233_Middle Ridge-Torrington 110 kV | 7233_Middle Ridge-Torrington 110 kV | 7233_Middle Ridge-Torrington 110 kV | 7233_Middle Ridge-Torrington 110 kV
SW-Toowoomba Dalby Warwick | 728_Middle Ridge-South Toowoomba 110 kV | % of Rated A | 18.66% | 18.29% | 17.98% | 17.67% | 17.4%
SW-Toowoomba Dalby Warwick | 728_Middle Ridge-South Toowoomba 110 kV | Limiting Line Name | TR_LINE 12070761_1 | TR_LINE 12070761_1 | TR_LINE 12070761_1 | TR_LINE 12070761_1 | TR_LINE 12070761_1
SW-Toowoomba Dalby Warwick | 728_Middle Ridge-South Toowoomba 110 kV | Loading (A) | 192.0007 | 188.1918 | 185.0465 | 181.8141 | 179.0489
SW-Toowoomba Dalby Warwick | 728_Middle Ridge-South Toowoomba 110 kV | Loading (MVA) | 38.41 | 37.641 | 36.9981 | 36.3431 | 35.7915
SW-Toowoomba Dalby Warwick | 728_Middle Ridge-South Toowoomba 110 kV | Loading (MW) | 17.3255 | 15.3811 | 13.6262 | 11.545 | 9.3993
SW-Toowoomba Dalby Warwick | 728_Middle Ridge-South Toowoomba 110 kV | Power Factor | 0.45047 | 0.40808 | 0.36778 | 0.31717 | 0.26212
SW-Toowoomba Dalby Warwick | 728_Middle Ridge-South Toowoomba 110 kV | Rating (A) | 1029 | 1029 | 1029 | 1029 | 1029
SW-Toowoomba Dalby Warwick | 728_Middle Ridge-South Toowoomba 110 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | 728_Middle Ridge-South Toowoomba 110 kV | Min Voltage at Constrained Conductor | 115.4998 | 115.4782 | 115.4351 | 115.4075 | 115.4111
SW-Toowoomba Dalby Warwick | 728_Middle Ridge-South Toowoomba 110 kV | Contingency Outage | 730_Middle Ridge-South Toowoomba 110 kV | 730_Middle Ridge-South Toowoomba 110 kV | 730_Middle Ridge-South Toowoomba 110 kV | 730_Middle Ridge-South Toowoomba 110 kV | 730_Middle Ridge-South Toowoomba 110 kV
SW-Toowoomba Dalby Warwick | 730_Middle Ridge-South Toowoomba 110 kV | % of Rated A | 18.66% | 18.29% | 17.98% | 17.67% | 17.4%
SW-Toowoomba Dalby Warwick | 730_Middle Ridge-South Toowoomba 110 kV | Limiting Line Name | TR_LINE 12070768_1 | TR_LINE 12070768_1 | TR_LINE 12070768_1 | TR_LINE 12070768_1 | TR_LINE 12070768_1
SW-Toowoomba Dalby Warwick | 730_Middle Ridge-South Toowoomba 110 kV | Loading (A) | 191.9999 | 188.1909 | 185.0456 | 181.8133 | 179.0481
SW-Toowoomba Dalby Warwick | 730_Middle Ridge-South Toowoomba 110 kV | Loading (MVA) | 38.41 | 37.641 | 36.9981 | 36.3431 | 35.7915
SW-Toowoomba Dalby Warwick | 730_Middle Ridge-South Toowoomba 110 kV | Loading (MW) | 17.3255 | 15.3811 | 13.6262 | 11.545 | 9.3992
SW-Toowoomba Dalby Warwick | 730_Middle Ridge-South Toowoomba 110 kV | Power Factor | 0.45047 | 0.40808 | 0.36778 | 0.31717 | 0.26212
SW-Toowoomba Dalby Warwick | 730_Middle Ridge-South Toowoomba 110 kV | Rating (A) | 1029 | 1029 | 1029 | 1029 | 1029
SW-Toowoomba Dalby Warwick | 730_Middle Ridge-South Toowoomba 110 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | 730_Middle Ridge-South Toowoomba 110 kV | Min Voltage at Constrained Conductor | 115.5003 | 115.4787 | 115.4357 | 115.4081 | 115.4118
SW-Toowoomba Dalby Warwick | 730_Middle Ridge-South Toowoomba 110 kV | Contingency Outage | 728_Middle Ridge-South Toowoomba 110 kV | 728_Middle Ridge-South Toowoomba 110 kV | 728_Middle Ridge-South Toowoomba 110 kV | 728_Middle Ridge-South Toowoomba 110 kV | 728_Middle Ridge-South Toowoomba 110 kV
SW-Toowoomba Dalby Warwick | 7314_Dalby East 110 kV | % of Rated A | 4.591% | 4.591% | 4.591% | 4.592% | 4.593%
SW-Toowoomba Dalby Warwick | 7314_Dalby East 110 kV | Limiting Line Name | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1
SW-Toowoomba Dalby Warwick | 7314_Dalby East 110 kV | Loading (A) | 12.7183 | 12.7175 | 12.7176 | 12.7195 | 12.7239
SW-Toowoomba Dalby Warwick | 7314_Dalby East 110 kV | Loading (MVA) | 2.5338 | 2.5355 | 2.5369 | 2.5387 | 2.5412
SW-Toowoomba Dalby Warwick | 7314_Dalby East 110 kV | Loading (MW) | 0.31483 | 0.28505 | 0.2614 | 0.24158 | 0.22403
SW-Toowoomba Dalby Warwick | 7314_Dalby East 110 kV | Power Factor | 0.12425 | 0.11243 | 0.10304 | 0.095159 | 0.088161
SW-Toowoomba Dalby Warwick | 7314_Dalby East 110 kV | Rating (A) | 277 | 277 | 277 | 277 | 277
SW-Toowoomba Dalby Warwick | 7314_Dalby East 110 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | 7314_Dalby East 110 kV | Min Voltage at Constrained Conductor | 115.0226 | 115.1055 | 115.1698 | 115.2326 | 115.3066
SW-Toowoomba Dalby Warwick | 7314_Dalby East 110 kV | Contingency Outage | F099D_Warra 33 kV | F099D_Warra 33 kV | F099D_Warra 33 kV | F099D_Warra 33 kV | F099D_Warra 33 kV
SW-Toowoomba Dalby Warwick | 7448_South Toowoomba-TWCE 110 kV | % of Rated A | 11.55% | 11.17% | 10.77% | 10.32% | 9.83%
SW-Toowoomba Dalby Warwick | 7448_South Toowoomba-TWCE 110 kV | Limiting Line Name | TR_CABLE 13760_1 | TR_CABLE 13760_1 | TR_CABLE 13760_1 | TR_CABLE 13760_1 | TR_CABLE 13760_1
SW-Toowoomba Dalby Warwick | 7448_South Toowoomba-TWCE 110 kV | Loading (A) | 48.5185 | 46.9309 | 45.2333 | 43.3605 | 41.2847
SW-Toowoomba Dalby Warwick | 7448_South Toowoomba-TWCE 110 kV | Loading (MVA) | 9.7034 | 9.3842 | 9.0415 | 8.6974 | 8.2817
SW-Toowoomba Dalby Warwick | 7448_South Toowoomba-TWCE 110 kV | Loading (MW) | 7.7725 | 7.3413 | 6.8677 | 6.3269 | 5.6942
SW-Toowoomba Dalby Warwick | 7448_South Toowoomba-TWCE 110 kV | Power Factor | 0.80101 | 0.7823 | 0.75958 | 0.72745 | 0.68756
SW-Toowoomba Dalby Warwick | 7448_South Toowoomba-TWCE 110 kV | Rating (A) | 420 | 420 | 420 | 420 | 420
SW-Toowoomba Dalby Warwick | 7448_South Toowoomba-TWCE 110 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | 7448_South Toowoomba-TWCE 110 kV | Min Voltage at Constrained Conductor | 115.466 | 115.4459 | 115.404 | 115.8068 | 115.816
SW-Toowoomba Dalby Warwick | 7448_South Toowoomba-TWCE 110 kV | Contingency Outage | 7449 South Toowoomba-TWCE 110 kV | 7449 South Toowoomba-TWCE 110 kV | 7449 South Toowoomba-TWCE 110 kV | 728_Middle Ridge-South Toowoomba 110 kV | 728_Middle Ridge-South Toowoomba 110 kV
SW-Toowoomba Dalby Warwick | 7449 South Toowoomba-TWCE 110 kV | % of Rated A | 8.632% | 8.506% | 8.372% | 8.228% | 8.072%
SW-Toowoomba Dalby Warwick | 7449 South Toowoomba-TWCE 110 kV | Limiting Line Name | TR_CABLE 13761_1 | TR_CABLE 13761_1 | TR_CABLE 13761_1 | TR_CABLE 13761_1 | TR_CABLE 13761_1
SW-Toowoomba Dalby Warwick | 7449 South Toowoomba-TWCE 110 kV | Loading (A) | 36.2565 | 35.7244 | 35.1619 | 34.5561 | 33.9041
SW-Toowoomba Dalby Warwick | 7449 South Toowoomba-TWCE 110 kV | Loading (MVA) | 7.2773 | 7.1695 | 7.0543 | 6.9314 | 6.8011
SW-Toowoomba Dalby Warwick | 7449 South Toowoomba-TWCE 110 kV | Loading (MW) | 3.9464 | 3.731 | 3.4945 | 3.2239 | 2.9078
SW-Toowoomba Dalby Warwick | 7449 South Toowoomba-TWCE 110 kV | Power Factor | 0.54229 | 0.5204 | 0.49537 | 0.46512 | 0.42755
SW-Toowoomba Dalby Warwick | 7449 South Toowoomba-TWCE 110 kV | Rating (A) | 420 | 420 | 420 | 420 | 420
SW-Toowoomba Dalby Warwick | 7449 South Toowoomba-TWCE 110 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | 7449 South Toowoomba-TWCE 110 kV | Min Voltage at Constrained Conductor | 115.8843 | 115.8679 | 115.8292 | 115.8069 | 115.816
SW-Toowoomba Dalby Warwick | 7449 South Toowoomba-TWCE 110 kV | Contingency Outage | 728_Middle Ridge-South Toowoomba 110 kV | 728_Middle Ridge-South Toowoomba 110 kV | 728_Middle Ridge-South Toowoomba 110 kV | 728_Middle Ridge-South Toowoomba 110 kV | 728_Middle Ridge-South Toowoomba 110 kV
SW-Toowoomba Dalby Warwick | 790_Warwick-Stanthorpe 110 kV | % of Rated A | 21.29% | 21.45% | 21.59% | 21.72% | 21.83%
SW-Toowoomba Dalby Warwick | 790_Warwick-Stanthorpe 110 kV | Limiting Line Name | TR_LINE 198182_1 | TR_LINE 198182_1 | TR_LINE 198182_1 | TR_LINE 198182_1 | TR_LINE 198182_1
SW-Toowoomba Dalby Warwick | 790_Warwick-Stanthorpe 110 kV | Loading (A) | 27.0349 | 27.2464 | 27.4247 | 27.5876 | 27.7269
SW-Toowoomba Dalby Warwick | 790_Warwick-Stanthorpe 110 kV | Loading (MVA) | 5.756 | 5.8107 | 5.855 | 5.8958 | 5.932
SW-Toowoomba Dalby Warwick | 790_Warwick-Stanthorpe 110 kV | Loading (MW) | 0.92862 | 1.1373 | 1.2974 | 1.4294 | 1.5297
SW-Toowoomba Dalby Warwick | 790_Warwick-Stanthorpe 110 kV | Power Factor | 0.16132 | 0.19572 | 0.22158 | 0.24243 | 0.25786
SW-Toowoomba Dalby Warwick | 790_Warwick-Stanthorpe 110 kV | Rating (A) | 127 | 127 | 127 | 127 | 127
SW-Toowoomba Dalby Warwick | 790_Warwick-Stanthorpe 110 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | 790_Warwick-Stanthorpe 110 kV | Min Voltage at Constrained Conductor | 122.9246 | 123.1276 | 123.2615 | 123.3865 | 123.5216
SW-Toowoomba Dalby Warwick | 790_Warwick-Stanthorpe 110 kV | Contingency Outage | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV
SW-Toowoomba Dalby Warwick | F008D_Central Dalby 2 33 kV | % of Rated A | 6.253% | 4.283% | 4.642% | 5.526% | 6.389%
SW-Toowoomba Dalby Warwick | F008D_Central Dalby 2 33 kV | Limiting Line Name | TR_CABLE 4401_1 | TR_CABLE 4401_1 | TR_CABLE 5204_1 | TR_CABLE 5204_1 | TR_CABLE 5204_1
SW-Toowoomba Dalby Warwick | F008D_Central Dalby 2 33 kV | Loading (A) | 31.2673 | 21.4132 | 23.2103 | 27.6282 | 31.9449
SW-Toowoomba Dalby Warwick | F008D_Central Dalby 2 33 kV | Loading (MVA) | 1.8308 | 1.2555 | 1.3633 | 1.6238 | 1.8788
SW-Toowoomba Dalby Warwick | F008D_Central Dalby 2 33 kV | Loading (MW) | 1.8179 | 1.2398 | 1.3493 | 1.6122 | 1.8692
SW-Toowoomba Dalby Warwick | F008D_Central Dalby 2 33 kV | Power Factor | 0.99231 | 0.9866 | 0.98825 | 0.99164 | 0.99381
SW-Toowoomba Dalby Warwick | F008D_Central Dalby 2 33 kV | Rating (A) | 500 | 500 | 500 | 500 | 500
SW-Toowoomba Dalby Warwick | F008D_Central Dalby 2 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F008D_Central Dalby 2 33 kV | Min Voltage at Constrained Conductor | 33.8059 | 33.8514 | 33.9119 | 33.9324 | 33.9557
SW-Toowoomba Dalby Warwick | F008D_Central Dalby 2 33 kV | Contingency Outage | F019D_West Dalby No 1 33 kV | F019D_West Dalby No 1 33 kV | F039D_West Dalby No 2 33 kV | F039D_West Dalby No 2 33 kV | F039D_West Dalby No 2 33 kV
SW-Toowoomba Dalby Warwick | F019D_West Dalby No 1 33 kV | % of Rated A | 22.72% | 20.5% | 18.58% | 16.81% | 15.08%
SW-Toowoomba Dalby Warwick | F019D_West Dalby No 1 33 kV | Limiting Line Name | TR_LINE 58890_1 | TR_LINE 58890_1 | TR_LINE 58890_1 | TR_LINE 58890_1 | TR_LINE 58890_1
SW-Toowoomba Dalby Warwick | F019D_West Dalby No 1 33 kV | Loading (A) | 85.1944 | 76.8849 | 69.6695 | 63.0461 | 56.5549
SW-Toowoomba Dalby Warwick | F019D_West Dalby No 1 33 kV | Loading (MVA) | 4.988 | 4.506 | 4.0861 | 3.7003 | 3.3218
SW-Toowoomba Dalby Warwick | F019D_West Dalby No 1 33 kV | Loading (MW) | 4.9773 | 4.4948 | 4.0741 | 3.6871 | 3.3072
SW-Toowoomba Dalby Warwick | F019D_West Dalby No 1 33 kV | Power Factor | 0.99786 | 0.99751 | 0.99706 | 0.99646 | 0.99557
SW-Toowoomba Dalby Warwick | F019D_West Dalby No 1 33 kV | Rating (A) | 375 | 375 | 375 | 375 | 375
SW-Toowoomba Dalby Warwick | F019D_West Dalby No 1 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F019D_West Dalby No 1 33 kV | Min Voltage at Constrained Conductor | 33.7618 | 33.8001 | 33.829 | 33.8564 | 33.8866
SW-Toowoomba Dalby Warwick | F019D_West Dalby No 1 33 kV | Contingency Outage | F039D_West Dalby No 2 33 kV | F039D_West Dalby No 2 33 kV | F039D_West Dalby No 2 33 kV | F039D_West Dalby No 2 33 kV | F039D_West Dalby No 2 33 kV
SW-Toowoomba Dalby Warwick | F039D_West Dalby No 2 33 kV | % of Rated A | 29.93% | 27.01% | 24.47% | 22.14% | 19.87%
SW-Toowoomba Dalby Warwick | F039D_West Dalby No 2 33 kV | Limiting Line Name | TR_CABLE 139_1 | TR_CABLE 139_1 | TR_CABLE 139_1 | TR_CABLE 139_1 | TR_CABLE 139_1
SW-Toowoomba Dalby Warwick | F039D_West Dalby No 2 33 kV | Loading (A) | 84.9965 | 76.703 | 69.504 | 62.8918 | 56.4215
SW-Toowoomba Dalby Warwick | F039D_West Dalby No 2 33 kV | Loading (MVA) | 4.9679 | 4.49 | 4.0733 | 3.6898 | 3.3141
SW-Toowoomba Dalby Warwick | F039D_West Dalby No 2 33 kV | Loading (MW) | 4.9585 | 4.4795 | 4.0616 | 3.6763 | 3.2987
SW-Toowoomba Dalby Warwick | F039D_West Dalby No 2 33 kV | Power Factor | 0.99799 | 0.99755 | 0.99698 | 0.9962 | 0.99519
SW-Toowoomba Dalby Warwick | F039D_West Dalby No 2 33 kV | Rating (A) | 284 | 284 | 284 | 284 | 284
SW-Toowoomba Dalby Warwick | F039D_West Dalby No 2 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F039D_West Dalby No 2 33 kV | Min Voltage at Constrained Conductor | 33.7452 | 33.7963 | 33.836 | 33.8729 | 33.9125
SW-Toowoomba Dalby Warwick | F039D_West Dalby No 2 33 kV | Contingency Outage | F019D_West Dalby No 1 33 kV | F019D_West Dalby No 1 33 kV | F019D_West Dalby No 1 33 kV | F019D_West Dalby No 1 33 kV | F019D_West Dalby No 1 33 kV
SW-Toowoomba Dalby Warwick | F095D_Kaimkillenbun 33 kV | % of Rated A | 4.387% | 4.197% | 4.121% | 4.116% | 4.512%
SW-Toowoomba Dalby Warwick | F095D_Kaimkillenbun 33 kV | Limiting Line Name | TR_CABLE 5206_1 | TR_CABLE 5206_1 | TR_CABLE 5206_1 | TR_LINE 23047_1 | TR_LINE 23047_1
SW-Toowoomba Dalby Warwick | F095D_Kaimkillenbun 33 kV | Loading (A) | 4.3872 | 4.1972 | 4.1211 | 3.8277 | 4.1959
SW-Toowoomba Dalby Warwick | F095D_Kaimkillenbun 33 kV | Loading (MVA) | 0.25843 | 0.24662 | 0.24228 | 0.22287 | 0.24454
SW-Toowoomba Dalby Warwick | F095D_Kaimkillenbun 33 kV | Loading (MW) | 0.08619 | 0.048058 | 0.018597 | 0.22284 | 0.24451
SW-Toowoomba Dalby Warwick | F095D_Kaimkillenbun 33 kV | Power Factor | 0.33351 | 0.19487 | 0.076757 | 0.9999 | 0.99989
SW-Toowoomba Dalby Warwick | F095D_Kaimkillenbun 33 kV | Rating (A) | 100 | 100 | 100 | 93 | 93
SW-Toowoomba Dalby Warwick | F095D_Kaimkillenbun 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F095D_Kaimkillenbun 33 kV | Min Voltage at Constrained Conductor | 34.0095 | 33.9238 | 33.9429 | 33.6161 | 33.6483
SW-Toowoomba Dalby Warwick | F095D_Kaimkillenbun 33 kV | Contingency Outage | F099D_Warra 33 kV | F097D_Jandowae 33 kV | F097D_Jandowae 33 kV | 3153_Cecil Plains Road 33 kV | 3153_Cecil Plains Road 33 kV
SW-Toowoomba Dalby Warwick | F097D_Jandowae 33 kV | % of Rated A | 5.757% | 5.322% | 5.219% | 5.215% | 5.21%
SW-Toowoomba Dalby Warwick | F097D_Jandowae 33 kV | Limiting Line Name | TR_LINE 102880_1 | TR_LINE 102880_1 | TR_CABLE 130_1 | TR_CABLE 130_1 | TR_CABLE 130_1
SW-Toowoomba Dalby Warwick | F097D_Jandowae 33 kV | Loading (A) | 13.9886 | 12.9335 | 8.3507 | 8.3434 | 8.3355
SW-Toowoomba Dalby Warwick | F097D_Jandowae 33 kV | Loading (MVA) | 0.8154 | 0.74964 | 0.48444 | 0.48443 | 0.48443
SW-Toowoomba Dalby Warwick | F097D_Jandowae 33 kV | Loading (MW) | 0.81354 | 0.7474 | 0.40984 | 0.40984 | 0.40984
SW-Toowoomba Dalby Warwick | F097D_Jandowae 33 kV | Power Factor | 0.99771 | 0.99701 | 0.84576 | 0.84577 | 0.84578
SW-Toowoomba Dalby Warwick | F097D_Jandowae 33 kV | Rating (A) | 243 | 243 | 160 | 160 | 160
SW-Toowoomba Dalby Warwick | F097D_Jandowae 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F097D_Jandowae 33 kV | Min Voltage at Constrained Conductor | 33.654 | 33.4636 | 33.4929 | 33.5219 | 33.5535
SW-Toowoomba Dalby Warwick | F097D_Jandowae 33 kV | Contingency Outage | F039D_West Dalby No 2 33 kV | 3153_Cecil Plains Road 33 kV | 3153_Cecil Plains Road 33 kV | 3153_Cecil Plains Road 33 kV | 3153_Cecil Plains Road 33 kV
SW-Toowoomba Dalby Warwick | F099D_Warra 33 kV | % of Rated A | 58.96% | 59.31% | 59.25% | 59.2% | 59.14%
SW-Toowoomba Dalby Warwick | F099D_Warra 33 kV | Limiting Line Name | TR_CABLE 132_1 | TR_CABLE 132_1 | TR_CABLE 132_1 | TR_CABLE 132_1 | TR_CABLE 132_1
SW-Toowoomba Dalby Warwick | F099D_Warra 33 kV | Loading (A) | 58.9645 | 59.307 | 59.2523 | 59.2003 | 59.1438
SW-Toowoomba Dalby Warwick | F099D_Warra 33 kV | Loading (MVA) | 3.403 | 3.403 | 3.403 | 3.403 | 3.403
SW-Toowoomba Dalby Warwick | F099D_Warra 33 kV | Loading (MW) | 3.4006 | 3.4006 | 3.4006 | 3.4006 | 3.4006
SW-Toowoomba Dalby Warwick | F099D_Warra 33 kV | Power Factor | 0.99916 | 0.99916 | 0.99916 | 0.99916 | 0.99916
SW-Toowoomba Dalby Warwick | F099D_Warra 33 kV | Rating (A) | 100 | 100 | 100 | 100 | 100
SW-Toowoomba Dalby Warwick | F099D_Warra 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F099D_Warra 33 kV | Min Voltage at Constrained Conductor | 33.3209 | 33.1284 | 33.159 | 33.1881 | 33.2199
SW-Toowoomba Dalby Warwick | F099D_Warra 33 kV | Contingency Outage | F039D_West Dalby No 2 33 kV | 3153_Cecil Plains Road 33 kV | 3153_Cecil Plains Road 33 kV | 3153_Cecil Plains Road 33 kV | 3153_Cecil Plains Road 33 kV
SW-Toowoomba Dalby Warwick | F2060_Sladevale 1 33kV | % of Rated A | 7.157% | 7.314% | 7.444% | 7.556% | 7.653%
SW-Toowoomba Dalby Warwick | F2060_Sladevale 1 33kV | Limiting Line Name | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1
SW-Toowoomba Dalby Warwick | F2060_Sladevale 1 33kV | Loading (A) | 45.4443 | 46.4469 | 47.2685 | 47.9795 | 48.5977
SW-Toowoomba Dalby Warwick | F2060_Sladevale 1 33kV | Loading (MVA) | 2.8349 | 2.9014 | 2.9552 | 3.0022 | 3.0438
SW-Toowoomba Dalby Warwick | F2060_Sladevale 1 33kV | Loading (MW) | 1.3636 | 1.494 | 1.596 | 1.6807 | 1.7517
SW-Toowoomba Dalby Warwick | F2060_Sladevale 1 33kV | Power Factor | 0.48099 | 0.5149 | 0.54003 | 0.5598 | 0.57548
SW-Toowoomba Dalby Warwick | F2060_Sladevale 1 33kV | Rating (A) | 635 | 635 | 635 | 635 | 635
SW-Toowoomba Dalby Warwick | F2060_Sladevale 1 33kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F2060_Sladevale 1 33kV | Min Voltage at Constrained Conductor | 36.0157 | 36.0648 | 36.0962 | 36.1263 | 36.1611
SW-Toowoomba Dalby Warwick | F2060_Sladevale 1 33kV | Contingency Outage | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV
SW-Toowoomba Dalby Warwick | F2325_Broxburn 33 kV | % of Rated A | 2.044% | 1.159% | 0.5081% | 0.7922% | 1.348%
SW-Toowoomba Dalby Warwick | F2325_Broxburn 33 kV | Limiting Line Name | TR_LINE 23767_1 | TR_LINE 60091_1 | TR_LINE 60091_1 | TR_LINE 23767_1 | TR_LINE 23767_1
SW-Toowoomba Dalby Warwick | F2325_Broxburn 33 kV | Loading (A) | 7.9512 | 3.8719 | 1.6971 | 3.0816 | 5.2428
SW-Toowoomba Dalby Warwick | F2325_Broxburn 33 kV | Loading (MVA) | 0.45474 | 0.22146 | 0.097061 | 0.17623 | 0.3035
SW-Toowoomba Dalby Warwick | F2325_Broxburn 33 kV | Loading (MW) | 0.44285 | 0.21296 | 0.075301 | 0.14157 | 0.28397
SW-Toowoomba Dalby Warwick | F2325_Broxburn 33 kV | Power Factor | 0.97385 | 0.9616 | 0.77582 | 0.80331 | 0.93564
SW-Toowoomba Dalby Warwick | F2325_Broxburn 33 kV | Rating (A) | 389 | 334 | 334 | 389 | 389
SW-Toowoomba Dalby Warwick | F2325_Broxburn 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F2325_Broxburn 33 kV | Min Voltage at Constrained Conductor | 33.0191 | 33.0168 | 33.0189 | 33.0178 | 33.4221
SW-Toowoomba Dalby Warwick | F2325_Broxburn 33 kV | Contingency Outage | F2460_Cecil Plains 33 kV | F2460_Cecil Plains 33 kV | F2460_Cecil Plains 33 kV | F2460_Cecil Plains 33 kV | F2460_Cecil Plains 33 kV
SW-Toowoomba Dalby Warwick | F2450_Carrington Road 33 kV | % of Rated A | 1.822% | 2.179% | 2.457% | 2.688% | 2.866%
SW-Toowoomba Dalby Warwick | F2450_Carrington Road 33 kV | Limiting Line Name | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1
SW-Toowoomba Dalby Warwick | F2450_Carrington Road 33 kV | Loading (A) | 6.1385 | 7.3426 | 8.2817 | 9.0571 | 9.6589
SW-Toowoomba Dalby Warwick | F2450_Carrington Road 33 kV | Loading (MVA) | 0.35966 | 0.43017 | 0.48499 | 0.53007 | 0.56627
SW-Toowoomba Dalby Warwick | F2450_Carrington Road 33 kV | Loading (MW) | 0.35962 | 0.43013 | 0.48495 | 0.53003 | 0.56622
SW-Toowoomba Dalby Warwick | F2450_Carrington Road 33 kV | Power Factor | 0.99989 | 0.99991 | 0.99992 | 0.99992 | 0.99992
SW-Toowoomba Dalby Warwick | F2450_Carrington Road 33 kV | Rating (A) | 337 | 337 | 337 | 337 | 337
SW-Toowoomba Dalby Warwick | F2450_Carrington Road 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F2450_Carrington Road 33 kV | Min Voltage at Constrained Conductor | 33.8276 | 33.8246 | 33.8107 | 33.7895 | 33.848
SW-Toowoomba Dalby Warwick | F2450_Carrington Road 33 kV | Contingency Outage | F3980_Purrawunda 33 kV | F3980_Purrawunda 33 kV | F3980_Purrawunda 33 kV | F3980_Purrawunda 33 kV | F3980_Purrawunda 33 kV
SW-Toowoomba Dalby Warwick | F2460_Cecil Plains 33 kV | % of Rated A | 25.18% | 25.23% | 25.29% | 25.37% | 25.75%
SW-Toowoomba Dalby Warwick | F2460_Cecil Plains 33 kV | Limiting Line Name | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1
SW-Toowoomba Dalby Warwick | F2460_Cecil Plains 33 kV | Loading (A) | 36.0027 | 36.0824 | 36.1691 | 36.2724 | 36.821
SW-Toowoomba Dalby Warwick | F2460_Cecil Plains 33 kV | Loading (MVA) | 2.1364 | 2.1433 | 2.1498 | 2.1574 | 2.218
SW-Toowoomba Dalby Warwick | F2460_Cecil Plains 33 kV | Loading (MW) | 0.037637 | 0.10341 | 0.16082 | 0.21347 | 0.26471
SW-Toowoomba Dalby Warwick | F2460_Cecil Plains 33 kV | Power Factor | 0.012092 | 0.042716 | 0.069265 | 0.093392 | 0.11378
SW-Toowoomba Dalby Warwick | F2460_Cecil Plains 33 kV | Rating (A) | 143 | 143 | 143 | 143 | 143
SW-Toowoomba Dalby Warwick | F2460_Cecil Plains 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F2460_Cecil Plains 33 kV | Min Voltage at Constrained Conductor | 34.2592 | 34.2946 | 34.3167 | 34.3393 | 34.7786
SW-Toowoomba Dalby Warwick | F2460_Cecil Plains 33 kV | Contingency Outage | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV
SW-Toowoomba Dalby Warwick | F2520_Clifton 33 kV | % of Rated A | 23.78% | 23.2% | 22.99% | 23.02% | 23.09%
SW-Toowoomba Dalby Warwick | F2520_Clifton 33 kV | Limiting Line Name | TR_LINE 188412_1 | TR_LINE 188412_1 | TR_LINE 188412_1 | TR_LINE 188412_1 | TR_LINE 188412_1
SW-Toowoomba Dalby Warwick | F2520_Clifton 33 kV | Loading (A) | 29.0165 | 28.302 | 28.0516 | 28.0855 | 28.1676
SW-Toowoomba Dalby Warwick | F2520_Clifton 33 kV | Loading (MVA) | 1.795 | 1.7489 | 1.7306 | 1.7348 | 1.7422
SW-Toowoomba Dalby Warwick | F2520_Clifton 33 kV | Loading (MW) | 0.42001 | 0.18573 | 0.072619 | 0.0066398 | 0.075278
SW-Toowoomba Dalby Warwick | F2520_Clifton 33 kV | Power Factor | 0.23365 | 0.10586 | 0.041667 | 0.0034943 | 0.042875
SW-Toowoomba Dalby Warwick | F2520_Clifton 33 kV | Rating (A) | 122 | 122 | 122 | 122 | 122
SW-Toowoomba Dalby Warwick | F2520_Clifton 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F2520_Clifton 33 kV | Min Voltage at Constrained Conductor | 35.7154 | 35.6777 | 35.6178 | 35.6619 | 35.7096
SW-Toowoomba Dalby Warwick | F2520_Clifton 33 kV | Contingency Outage | 728_Middle Ridge-South Toowoomba 110 kV | 728_Middle Ridge-South Toowoomba 110 kV | 728_Middle Ridge-South Toowoomba 110 kV | 728_Middle Ridge-South Toowoomba 110 kV | 728_Middle Ridge-South Toowoomba 110 kV
SW-Toowoomba Dalby Warwick | F2777_East Stanthorpe 33 kV | % of Rated A | 1.683% | 1.685% | 1.686% | 1.687% | 1.689%
SW-Toowoomba Dalby Warwick | F2777_East Stanthorpe 33 kV | Limiting Line Name | TR_LINE 140241_1 | TR_LINE 140241_1 | TR_LINE 140241_1 | TR_LINE 140241_1 | TR_LINE 140241_1
SW-Toowoomba Dalby Warwick | F2777_East Stanthorpe 33 kV | Loading (A) | 2.5918 | 2.5954 | 2.5961 | 2.5984 | 2.601
SW-Toowoomba Dalby Warwick | F2777_East Stanthorpe 33 kV | Loading (MVA) | 0.16162 | 0.16208 | 0.16227 | 0.16255 | 0.16288
SW-Toowoomba Dalby Warwick | F2777_East Stanthorpe 33 kV | Loading (MW) | 7.6115e-05 | 7.633e-05 | 7.6322e-05 | 7.6455e-05 | 7.6607e-05
SW-Toowoomba Dalby Warwick | F2777_East Stanthorpe 33 kV | Power Factor | 0.00046892 | 0.00046892 | 0.00046832 | 0.00046832 | 0.00046832
SW-Toowoomba Dalby Warwick | F2777_East Stanthorpe 33 kV | Rating (A) | 154 | 154 | 154 | 154 | 154
SW-Toowoomba Dalby Warwick | F2777_East Stanthorpe 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F2777_East Stanthorpe 33 kV | Min Voltage at Constrained Conductor | 36.0036 | 36.0543 | 36.087 | 36.1185 | 36.1545
SW-Toowoomba Dalby Warwick | F2777_East Stanthorpe 33 kV | Contingency Outage | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV
SW-Toowoomba Dalby Warwick | F2780_East Warwick No 1 33 kV | % of Rated A | 17.05% | 16.97% | 16.98% | 17.05% | 17.18%
SW-Toowoomba Dalby Warwick | F2780_East Warwick No 1 33 kV | Limiting Line Name | TR_LINE 23896_1 | TR_LINE 23896_1 | TR_LINE 23896_1 | TR_LINE 23896_1 | TR_LINE 23896_1
SW-Toowoomba Dalby Warwick | F2780_East Warwick No 1 33 kV | Loading (A) | 90.349 | 89.9249 | 89.9765 | 90.3756 | 91.0502
SW-Toowoomba Dalby Warwick | F2780_East Warwick No 1 33 kV | Loading (MVA) | 5.4967 | 5.4726 | 5.4758 | 5.5007 | 5.5436
SW-Toowoomba Dalby Warwick | F2780_East Warwick No 1 33 kV | Loading (MW) | 0.60412 | 0.16611 | 0.20582 | 0.54361 | 0.85514
SW-Toowoomba Dalby Warwick | F2780_East Warwick No 1 33 kV | Power Factor | 0.10986 | 0.030307 | 0.037543 | 0.098785 | 0.15422
SW-Toowoomba Dalby Warwick | F2780_East Warwick No 1 33 kV | Rating (A) | 530 | 530 | 530 | 530 | 530
SW-Toowoomba Dalby Warwick | F2780_East Warwick No 1 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F2780_East Warwick No 1 33 kV | Min Voltage at Constrained Conductor | 35.1233 | 35.1338 | 35.1343 | 35.138 | 35.1495
SW-Toowoomba Dalby Warwick | F2780_East Warwick No 1 33 kV | Contingency Outage | F2785_East Warwick No 2 33 kV | F2785_East Warwick No 2 33 kV | F2785_East Warwick No 2 33 kV | F2785_East Warwick No 2 33 kV | F2785_East Warwick No 2 33 kV
SW-Toowoomba Dalby Warwick | F2785_East Warwick No 2 33 kV | % of Rated A | 17.04% | 16.96% | 16.97% | 17.04% | 17.17%
SW-Toowoomba Dalby Warwick | F2785_East Warwick No 2 33 kV | Limiting Line Name | TR_LINE 23891_1 | TR_LINE 23891_1 | TR_LINE 23891_1 | TR_LINE 23891_1 | TR_LINE 23891_1
SW-Toowoomba Dalby Warwick | F2785_East Warwick No 2 33 kV | Loading (A) | 90.3094 | 89.8852 | 89.9369 | 90.3363 | 91.0113
SW-Toowoomba Dalby Warwick | F2785_East Warwick No 2 33 kV | Loading (MVA) | 5.4943 | 5.4702 | 5.4734 | 5.4983 | 5.5412
SW-Toowoomba Dalby Warwick | F2785_East Warwick No 2 33 kV | Loading (MW) | 0.6041 | 0.16609 | 0.20588 | 0.54368 | 0.85521
SW-Toowoomba Dalby Warwick | F2785_East Warwick No 2 33 kV | Power Factor | 0.10989 | 0.030308 | 0.037563 | 0.098833 | 0.15429
SW-Toowoomba Dalby Warwick | F2785_East Warwick No 2 33 kV | Rating (A) | 530 | 530 | 530 | 530 | 530
SW-Toowoomba Dalby Warwick | F2785_East Warwick No 2 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F2785_East Warwick No 2 33 kV | Min Voltage at Constrained Conductor | 35.1231 | 35.1336 | 35.1341 | 35.1378 | 35.1493
SW-Toowoomba Dalby Warwick | F2785_East Warwick No 2 33 kV | Contingency Outage | F2780_East Warwick No 1 33 kV | F2780_East Warwick No 1 33 kV | F2780_East Warwick No 1 33 kV | F2780_East Warwick No 1 33 kV | F2780_East Warwick No 1 33 kV
SW-Toowoomba Dalby Warwick | F3040 Hampton Street | % of Rated A | 0.3089% | 0.3089% | 0.3088% | 0.3088% | 0.3088%
SW-Toowoomba Dalby Warwick | F3040 Hampton Street | Limiting Line Name | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1
SW-Toowoomba Dalby Warwick | F3040 Hampton Street | Loading (A) | 1.5446 | 1.5444 | 1.544 | 1.5438 | 1.544
SW-Toowoomba Dalby Warwick | F3040 Hampton Street | Loading (MVA) | 0.093455 | 0.093441 | 0.093387 | 0.093363 | 0.093387
SW-Toowoomba Dalby Warwick | F3040 Hampton Street | Loading (MW) | 0.0013171 | 0.0013169 | 0.0013161 | 0.0013158 | 0.0013161
SW-Toowoomba Dalby Warwick | F3040 Hampton Street | Power Factor | 0.011534 | 0.011534 | 0.011534 | 0.011534 | 0.011534
SW-Toowoomba Dalby Warwick | F3040 Hampton Street | Rating (A) | 500 | 500 | 500 | 500 | 500
SW-Toowoomba Dalby Warwick | F3040 Hampton Street | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F3040 Hampton Street | Min Voltage at Constrained Conductor | 34.933 | 34.9304 | 34.9204 | 34.9158 | 34.9203
SW-Toowoomba Dalby Warwick | F3040 Hampton Street | Contingency Outage | 728_Middle Ridge-South Toowoomba 110 kV | 728_Middle Ridge-South Toowoomba 110 kV | 728_Middle Ridge-South Toowoomba 110 kV | 728_Middle Ridge-South Toowoomba 110 kV | 728_Middle Ridge-South Toowoomba 110 kV
SW-Toowoomba Dalby Warwick | F3095_Highfields 33 kV | % of Rated A | 3.437% | 2.112% | 1.542% | 1.242% | 1.181%
SW-Toowoomba Dalby Warwick | F3095_Highfields 33 kV | Limiting Line Name | TR_LINE 194642_1 | TR_LINE 194642_1 | TR_LINE 24220_1 | TR_LINE 24220_1 | TR_LINE 194642_1
SW-Toowoomba Dalby Warwick | F3095_Highfields 33 kV | Loading (A) | 5.8084 | 3.5697 | 3.3307 | 2.6832 | 1.996
SW-Toowoomba Dalby Warwick | F3095_Highfields 33 kV | Loading (MVA) | 0.34161 | 0.20995 | 0.19582 | 0.15777 | 0.11713
SW-Toowoomba Dalby Warwick | F3095_Highfields 33 kV | Loading (MW) | 0.33995 | 0.20709 | 0.19093 | 0.15154 | 0.11711
SW-Toowoomba Dalby Warwick | F3095_Highfields 33 kV | Power Factor | 0.99516 | 0.9864 | 0.97503 | 0.96052 | 0.99985
SW-Toowoomba Dalby Warwick | F3095_Highfields 33 kV | Rating (A) | 169 | 169 | 216 | 216 | 169
SW-Toowoomba Dalby Warwick | F3095_Highfields 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F3095_Highfields 33 kV | Min Voltage at Constrained Conductor | 33.9544 | 33.9555 | 33.9436 | 33.9465 | 33.8807
SW-Toowoomba Dalby Warwick | F3095_Highfields 33 kV | Contingency Outage | 790_Warwick-Stanthorpe 110 kV | 790_Warwick-Stanthorpe 110 kV | 790_Warwick-Stanthorpe 110 kV | 790_Warwick-Stanthorpe 110 kV | 790_Warwick-Stanthorpe 110 kV
SW-Toowoomba Dalby Warwick | F3253_Jellicoe Street 33 kV | % of Rated A | 0.9724% | 0.9725% | 0.9721% | 0.9692% | 0.9705%
SW-Toowoomba Dalby Warwick | F3253_Jellicoe Street 33 kV | Limiting Line Name | TR_LINE 23977_2 | TR_LINE 23977_2 | TR_LINE 23977_2 | TR_LINE 23977_2 | TR_LINE 23977_2
SW-Toowoomba Dalby Warwick | F3253_Jellicoe Street 33 kV | Loading (A) | 2.1489 | 2.1492 | 2.1484 | 2.1419 | 2.1448
SW-Toowoomba Dalby Warwick | F3253_Jellicoe Street 33 kV | Loading (MVA) | 0.12686 | 0.12689 | 0.12679 | 0.12603 | 0.12638
SW-Toowoomba Dalby Warwick | F3253_Jellicoe Street 33 kV | Loading (MW) | 0.0022473 | 0.0022478 | 0.0022461 | 0.0022326 | 0.0022387
SW-Toowoomba Dalby Warwick | F3253_Jellicoe Street 33 kV | Power Factor | 0.017714 | 0.017714 | 0.017714 | 0.017714 | 0.017714
SW-Toowoomba Dalby Warwick | F3253_Jellicoe Street 33 kV | Rating (A) | 221 | 221 | 221 | 221 | 221
SW-Toowoomba Dalby Warwick | F3253_Jellicoe Street 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F3253_Jellicoe Street 33 kV | Min Voltage at Constrained Conductor | 34.0838 | 34.0878 | 34.0748 | 33.9725 | 34.0189
SW-Toowoomba Dalby Warwick | F3253_Jellicoe Street 33 kV | Contingency Outage | 7234_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV
SW-Toowoomba Dalby Warwick | F3255_Jennings Street 33 kV | % of Rated A | 4.551% | 2.238% | 0.4694% | 1.648% | 3.414%
SW-Toowoomba Dalby Warwick | F3255_Jennings Street 33 kV | Limiting Line Name | TR_LINE 123294_1 | TR_CABLE 81_1 | TR_CABLE 81_1 | TR_CABLE 81_1 | TR_CABLE 7923_1
SW-Toowoomba Dalby Warwick | F3255_Jennings Street 33 kV | Loading (A) | 28.0815 | 13.9871 | 2.9335 | 10.3022 | 21.0625
SW-Toowoomba Dalby Warwick | F3255_Jennings Street 33 kV | Loading (MVA) | 1.6948 | 0.84419 | 0.177 | 0.62152 | 1.2715
SW-Toowoomba Dalby Warwick | F3255_Jennings Street 33 kV | Loading (MW) | 1.6947 | 0.83124 | 0.087483 | 0.60458 | 1.2714
SW-Toowoomba Dalby Warwick | F3255_Jennings Street 33 kV | Power Factor | 0.99994 | 0.98466 | 0.49426 | 0.97034 | 0.99988
SW-Toowoomba Dalby Warwick | F3255_Jennings Street 33 kV | Rating (A) | 617 | 625 | 625 | 625 | 617
SW-Toowoomba Dalby Warwick | F3255_Jennings Street 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F3255_Jennings Street 33 kV | Min Voltage at Constrained Conductor | 34.8438 | 34.8452 | 34.8354 | 34.8305 | 34.853
SW-Toowoomba Dalby Warwick | F3255_Jennings Street 33 kV | Contingency Outage | F4015_Ramsay Street 33 kV | F4015_Ramsay Street 33 kV | F4015_Ramsay Street 33 kV | F4015_Ramsay Street 33 kV | F4015_Ramsay Street 33 kV
SW-Toowoomba Dalby Warwick | F3315_Sladevale 2 33kV | % of Rated A | 7.286% | 7.309% | 7.328% | 7.345% | 7.363%
SW-Toowoomba Dalby Warwick | F3315_Sladevale 2 33kV | Limiting Line Name | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1
SW-Toowoomba Dalby Warwick | F3315_Sladevale 2 33kV | Loading (A) | 46.2636 | 46.4133 | 46.5322 | 46.6431 | 46.7534
SW-Toowoomba Dalby Warwick | F3315_Sladevale 2 33kV | Loading (MVA) | 2.8864 | 2.8997 | 2.9096 | 2.9189 | 2.9286
SW-Toowoomba Dalby Warwick | F3315_Sladevale 2 33kV | Loading (MW) | 0.31582 | 0.36931 | 0.41202 | 0.44793 | 0.47864
SW-Toowoomba Dalby Warwick | F3315_Sladevale 2 33kV | Power Factor | 0.1082 | 0.12615 | 0.14039 | 0.15224 | 0.16222
SW-Toowoomba Dalby Warwick | F3315_Sladevale 2 33kV | Rating (A) | 635 | 635 | 635 | 635 | 635
SW-Toowoomba Dalby Warwick | F3315_Sladevale 2 33kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F3315_Sladevale 2 33kV | Min Voltage at Constrained Conductor | 36.021 | 36.0697 | 36.1007 | 36.1306 | 36.1651
SW-Toowoomba Dalby Warwick | F3315_Sladevale 2 33kV | Contingency Outage | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV
SW-Toowoomba Dalby Warwick | F3530_Millmerran 33 kV | % of Rated A | 3.112% | 2.095% | 1.451% | 1.279% | 1.555%
SW-Toowoomba Dalby Warwick | F3530_Millmerran 33 kV | Limiting Line Name | TR_LINE 24237_1 | TR_LINE 24237_1 | TR_LINE 24237_1 | TR_LINE 24237_1 | TR_LINE 24237_1
SW-Toowoomba Dalby Warwick | F3530_Millmerran 33 kV | Loading (A) | 3.9526 | 2.6611 | 1.8426 | 1.6242 | 1.9749
SW-Toowoomba Dalby Warwick | F3530_Millmerran 33 kV | Loading (MVA) | 0.22889 | 0.15418 | 0.10843 | 0.095633 | 0.11628
SW-Toowoomba Dalby Warwick | F3530_Millmerran 33 kV | Loading (MW) | 0.21008 | 0.124 | 0.052544 | 0.01045 | 0.067021
SW-Toowoomba Dalby Warwick | F3530_Millmerran 33 kV | Power Factor | 0.91782 | 0.80423 | 0.4846 | 0.10927 | 0.57635
SW-Toowoomba Dalby Warwick | F3530_Millmerran 33 kV | Rating (A) | 127 | 127 | 127 | 127 | 127
SW-Toowoomba Dalby Warwick | F3530_Millmerran 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F3530_Millmerran 33 kV | Min Voltage at Constrained Conductor | 33.4331 | 33.4521 | 33.9736 | 33.9935 | 33.9954
SW-Toowoomba Dalby Warwick | F3530_Millmerran 33 kV | Contingency Outage | F2460_Cecil Plains 33 kV | F2460_Cecil Plains 33 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV
SW-Toowoomba Dalby Warwick | F3815 North Street No 1 33 kV | % of Rated A | 1.315% | 1.314% | 1.314% | 1.314% | 1.313%
SW-Toowoomba Dalby Warwick | F3815 North Street No 1 33 kV | Limiting Line Name | TR_LINE 181524_1 | TR_LINE 181524_1 | TR_LINE 181524_1 | TR_LINE 181524_1 | TR_LINE 181524_1
SW-Toowoomba Dalby Warwick | F3815 North Street No 1 33 kV | Loading (A) | 2.3269 | 2.3265 | 2.3256 | 2.3252 | 2.3245
SW-Toowoomba Dalby Warwick | F3815 North Street No 1 33 kV | Loading (MVA) | 0.13706 | 0.13702 | 0.13691 | 0.13687 | 0.13679
SW-Toowoomba Dalby Warwick | F3815 North Street No 1 33 kV | Loading (MW) | 0.0004376 | 0.00043745 | 0.00043712 | 0.00043698 | 0.00043671
SW-Toowoomba Dalby Warwick | F3815 North Street No 1 33 kV | Power Factor | 0.0031927 | 0.0031927 | 0.0031927 | 0.0031927 | 0.0031927
SW-Toowoomba Dalby Warwick | F3815 North Street No 1 33 kV | Rating (A) | 177 | 177 | 177 | 177 | 177
SW-Toowoomba Dalby Warwick | F3815 North Street No 1 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F3815 North Street No 1 33 kV | Min Voltage at Constrained Conductor | 34.0086 | 34.0027 | 33.9899 | 33.9843 | 33.9741
SW-Toowoomba Dalby Warwick | F3815 North Street No 1 33 kV | Contingency Outage | F067C_Kogan 33 kV | F067C_Kogan 33 kV | F067C_Kogan 33 kV | F4132_Shirley Road 33 kV | F3910_Perseverence Creek 1 33 kV
SW-Toowoomba Dalby Warwick | F3820_Boundary Road 33 kV | % of Rated A | 2.13% | 2.37% | 3.342% | 6.797% | 15.83%
SW-Toowoomba Dalby Warwick | F3820_Boundary Road 33 kV | Limiting Line Name | TR_CABLE 73_1 | TR_CABLE 73_1 | TR_CABLE 73_1 | TR_CABLE 73_1 | TR_CABLE 73_1
SW-Toowoomba Dalby Warwick | F3820_Boundary Road 33 kV | Loading (A) | 14.6939 | 16.3551 | 23.059 | 46.8993 | 109.223
SW-Toowoomba Dalby Warwick | F3820_Boundary Road 33 kV | Loading (MVA) | 0.86703 | 0.96483 | 1.3495 | 2.7427 | 6.3983
SW-Toowoomba Dalby Warwick | F3820_Boundary Road 33 kV | Loading (MW) | 0.21658 | 0.478 | 1.0716 | 2.6256 | 6.3657
SW-Toowoomba Dalby Warwick | F3820_Boundary Road 33 kV | Power Factor | 0.2498 | 0.49443 | 0.79339 | 0.95728 | 0.99491
SW-Toowoomba Dalby Warwick | F3820_Boundary Road 33 kV | Rating (A) | 690 | 690 | 690 | 690 | 690
SW-Toowoomba Dalby Warwick | F3820_Boundary Road 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F3820_Boundary Road 33 kV | Min Voltage at Constrained Conductor | 34.0672 | 34.0593 | 33.7876 | 33.7633 | 33.8181
SW-Toowoomba Dalby Warwick | F3820_Boundary Road 33 kV | Contingency Outage | 7234_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV | F3980_Purrawunda 33 kV | F3980_Purrawunda 33 kV | F3980_Purrawunda 33 kV
SW-Toowoomba Dalby Warwick | F3830_Norwin 33 kV | % of Rated A | 6.782% | 6.818% | 6.847% | 6.873% | 6.827%
SW-Toowoomba Dalby Warwick | F3830_Norwin 33 kV | Limiting Line Name | TR_LINE 23942_1 | TR_LINE 23942_1 | TR_LINE 23942_1 | TR_LINE 23942_1 | TR_LINE 23942_1
SW-Toowoomba Dalby Warwick | F3830_Norwin 33 kV | Loading (A) | 7.8666 | 7.9087 | 7.9423 | 7.9728 | 7.9189
SW-Toowoomba Dalby Warwick | F3830_Norwin 33 kV | Loading (MVA) | 0.4499 | 0.45236 | 0.45423 | 0.45596 | 0.45842
SW-Toowoomba Dalby Warwick | F3830_Norwin 33 kV | Loading (MW) | 0.40764 | 0.41035 | 0.41245 | 0.41438 | 0.41483
SW-Toowoomba Dalby Warwick | F3830_Norwin 33 kV | Power Factor | 0.9053 | 0.90638 | 0.90727 | 0.90805 | 0.90416
SW-Toowoomba Dalby Warwick | F3830_Norwin 33 kV | Rating (A) | 116 | 116 | 116 | 116 | 116
SW-Toowoomba Dalby Warwick | F3830_Norwin 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F3830_Norwin 33 kV | Min Voltage at Constrained Conductor | 33.0197 | 33.0234 | 33.0191 | 33.0182 | 33.4225
SW-Toowoomba Dalby Warwick | F3830_Norwin 33 kV | Contingency Outage | F2460_Cecil Plains 33 kV | F2460_Cecil Plains 33 kV | F2460_Cecil Plains 33 kV | F2460_Cecil Plains 33 kV | F2460_Cecil Plains 33 kV
SW-Toowoomba Dalby Warwick | F3855 Omaras Road 33 kV | % of Rated A | 18.38% | 18.38% | 18.39% | 18.4% | 18.37%
SW-Toowoomba Dalby Warwick | F3855 Omaras Road 33 kV | Limiting Line Name | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1
SW-Toowoomba Dalby Warwick | F3855 Omaras Road 33 kV | Loading (A) | 42.8167 | 42.8244 | 42.8452 | 42.8749 | 42.8023
SW-Toowoomba Dalby Warwick | F3855 Omaras Road 33 kV | Loading (MVA) | 2.5004 | 2.5004 | 2.5004 | 2.5004 | 2.5004
SW-Toowoomba Dalby Warwick | F3855 Omaras Road 33 kV | Loading (MW) | 2.5004 | 2.5004 | 2.5004 | 2.5004 | 2.5004
SW-Toowoomba Dalby Warwick | F3855 Omaras Road 33 kV | Power Factor | 0.99997 | 0.99997 | 0.99997 | 0.99998 | 0.99997
SW-Toowoomba Dalby Warwick | F3855 Omaras Road 33 kV | Rating (A) | 233 | 233 | 233 | 233 | 233
SW-Toowoomba Dalby Warwick | F3855 Omaras Road 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F3855 Omaras Road 33 kV | Min Voltage at Constrained Conductor | 33.7162 | 33.7101 | 33.6938 | 33.6704 | 33.7275
SW-Toowoomba Dalby Warwick | F3855 Omaras Road 33 kV | Contingency Outage | F3980_Purrawunda 33 kV | F3980_Purrawunda 33 kV | F3980_Purrawunda 33 kV | F3980_Purrawunda 33 kV | F3980_Purrawunda 33 kV
SW-Toowoomba Dalby Warwick | F3867_Pampas 33 kV | % of Rated A | 2.666% | 1.815% | 1.15% | 0.695% | 0.6721%
SW-Toowoomba Dalby Warwick | F3867_Pampas 33 kV | Limiting Line Name | TR_CABLE 106_1 | TR_CABLE 106_1 | TR_CABLE 106_1 | TR_LINE 177041_1 | TR_LINE 177041_1
SW-Toowoomba Dalby Warwick | F3867_Pampas 33 kV | Loading (A) | 7.9993 | 5.4454 | 3.4499 | 3.6836 | 3.5623
SW-Toowoomba Dalby Warwick | F3867_Pampas 33 kV | Loading (MVA) | 0.4574 | 0.31154 | 0.19742 | 0.21396 | 0.20949
SW-Toowoomba Dalby Warwick | F3867_Pampas 33 kV | Loading (MW) | 0.44728 | 0.29614 | 0.17181 | 0.062949 | 0.030308
SW-Toowoomba Dalby Warwick | F3867_Pampas 33 kV | Power Factor | 0.97788 | 0.95057 | 0.87024 | 0.29422 | 0.14463
SW-Toowoomba Dalby Warwick | F3867_Pampas 33 kV | Rating (A) | 300 | 300 | 300 | 530 | 530
SW-Toowoomba Dalby Warwick | F3867_Pampas 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F3867_Pampas 33 kV | Min Voltage at Constrained Conductor | 33.0131 | 33.0315 | 33.0392 | 33.5342 | 33.9523
SW-Toowoomba Dalby Warwick | F3867_Pampas 33 kV | Contingency Outage | F2460_Cecil Plains 33 kV | F2460_Cecil Plains 33 kV | F2460_Cecil Plains 33 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV
SW-Toowoomba Dalby Warwick | F3910_Perseverence Creek 1 33 kV | % of Rated A | 9.558% | 9.558% | 9.558% | 9.558% | 9.558%
SW-Toowoomba Dalby Warwick | F3910_Perseverence Creek 1 33 kV | Limiting Line Name | TR_LINE 27829_1 | TR_LINE 27829_1 | TR_LINE 27829_1 | TR_LINE 27829_1 | TR_LINE 27829_1
SW-Toowoomba Dalby Warwick | F3910_Perseverence Creek 1 33 kV | Loading (A) | 13.66 | 13.66 | 13.66 | 13.66 | 13.66
SW-Toowoomba Dalby Warwick | F3910_Perseverence Creek 1 33 kV | Loading (MVA) | 0.80432 | 0.80432 | 0.80432 | 0.80432 | 0.80432
SW-Toowoomba Dalby Warwick | F3910_Perseverence Creek 1 33 kV | Loading (MW) | 0.80375 | 0.80375 | 0.80375 | 0.80375 | 0.80375
SW-Toowoomba Dalby Warwick | F3910_Perseverence Creek 1 33 kV | Power Factor | 0.99929 | 0.99929 | 0.99929 | 0.99929 | 0.99929
SW-Toowoomba Dalby Warwick | F3910_Perseverence Creek 1 33 kV | Rating (A) | 143 | 143 | 143 | 143 | 143
SW-Toowoomba Dalby Warwick | F3910_Perseverence Creek 1 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F3910_Perseverence Creek 1 33 kV | Min Voltage at Constrained Conductor | 34 | 34 | 34 | 34 | 34
SW-Toowoomba Dalby Warwick | F3910_Perseverence Creek 1 33 kV | Contingency Outage | 790_Warwick-Stanthorpe 110 kV | 790_Warwick-Stanthorpe 110 kV | 790_Warwick-Stanthorpe 110 kV | 790_Warwick-Stanthorpe 110 kV | F4132_Shirley Road 33 kV
SW-Toowoomba Dalby Warwick | F3970_Pozieres 33 kV | % of Rated A | 1.564% | 1.361% | 1.247% | 1.184% | 1.159%
SW-Toowoomba Dalby Warwick | F3970_Pozieres 33 kV | Limiting Line Name | TR_LINE 23786_1 | TR_LINE 23786_1 | TR_LINE 23786_1 | TR_LINE 23786_1 | TR_LINE 23786_1
SW-Toowoomba Dalby Warwick | F3970_Pozieres 33 kV | Loading (A) | 2.5811 | 2.2452 | 2.058 | 1.9532 | 1.9121
SW-Toowoomba Dalby Warwick | F3970_Pozieres 33 kV | Loading (MVA) | 0.16449 | 0.15052 | 0.13812 | 0.13122 | 0.1286
SW-Toowoomba Dalby Warwick | F3970_Pozieres 33 kV | Loading (MW) | 0.1195 | 0.083485 | 0.057509 | 0.03708 | 0.024897
SW-Toowoomba Dalby Warwick | F3970_Pozieres 33 kV | Power Factor | 0.72649 | 0.55465 | 0.41637 | 0.28259 | 0.19361
SW-Toowoomba Dalby Warwick | F3970_Pozieres 33 kV | Rating (A) | 165 | 165 | 165 | 165 | 165
SW-Toowoomba Dalby Warwick | F3970_Pozieres 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F3970_Pozieres 33 kV | Min Voltage at Constrained Conductor | 36.794 | 38.7048 | 38.7472 | 38.7868 | 38.8294
SW-Toowoomba Dalby Warwick | F3970_Pozieres 33 kV | Contingency Outage | F4245_Stanthorpe 33 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV
SW-Toowoomba Dalby Warwick | F3980_Purrawunda 33 kV | % of Rated A | 23.35% | 23.2% | 23.08% | 22.99% | 23.01%
SW-Toowoomba Dalby Warwick | F3980_Purrawunda 33 kV | Limiting Line Name | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1
SW-Toowoomba Dalby Warwick | F3980_Purrawunda 33 kV | Loading (A) | 49.2661 | 48.9432 | 48.6999 | 48.4994 | 48.5577
SW-Toowoomba Dalby Warwick | F3980_Purrawunda 33 kV | Loading (MVA) | 2.907 | 2.8873 | 2.871 | 2.856 | 2.8691
SW-Toowoomba Dalby Warwick | F3980_Purrawunda 33 kV | Loading (MW) | 0.67341 | 0.56285 | 0.4706 | 0.39017 | 0.31855
SW-Toowoomba Dalby Warwick | F3980_Purrawunda 33 kV | Power Factor | 0.23165 | 0.19494 | 0.16391 | 0.13662 | 0.11103
SW-Toowoomba Dalby Warwick | F3980_Purrawunda 33 kV | Rating (A) | 211 | 211 | 211 | 211 | 211
SW-Toowoomba Dalby Warwick | F3980_Purrawunda 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F3980_Purrawunda 33 kV | Min Voltage at Constrained Conductor | 34.0672 | 34.0593 | 34.0363 | 33.9986 | 34.1138
SW-Toowoomba Dalby Warwick | F3980_Purrawunda 33 kV | Contingency Outage | 7234_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV
SW-Toowoomba Dalby Warwick | F4005_Racecourse 33 kV | % of Rated A | 5.027% | 3.255% | 1.74% | 0.3983% | 1.019%
SW-Toowoomba Dalby Warwick | F4005_Racecourse 33 kV | Limiting Line Name | TR_CABLE 67_1 | TR_CABLE 67_1 | TR_CABLE 67_1 | TR_CABLE 67_1 | TR_CABLE 67_1
SW-Toowoomba Dalby Warwick | F4005_Racecourse 33 kV | Loading (A) | 35.4888 | 22.977 | 12.2847 | 2.8121 | 7.1908
SW-Toowoomba Dalby Warwick | F4005_Racecourse 33 kV | Loading (MVA) | 2.0845 | 1.3494 | 0.72111 | 0.16496 | 0.4225
SW-Toowoomba Dalby Warwick | F4005_Racecourse 33 kV | Loading (MW) | 2.0832 | 1.3468 | 0.71576 | 0.13859 | 0.41418
SW-Toowoomba Dalby Warwick | F4005_Racecourse 33 kV | Power Factor | 0.99939 | 0.99813 | 0.99259 | 0.84013 | 0.97748
SW-Toowoomba Dalby Warwick | F4005_Racecourse 33 kV | Rating (A) | 706 | 706 | 706 | 706 | 706
SW-Toowoomba Dalby Warwick | F4005_Racecourse 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F4005_Racecourse 33 kV | Min Voltage at Constrained Conductor | 33.9102 | 33.9051 | 33.8898 | 33.8675 | 33.9221
SW-Toowoomba Dalby Warwick | F4005_Racecourse 33 kV | Contingency Outage | F4685_Wyalla Street 33 kV | F4685_Wyalla Street 33 kV | F4685_Wyalla Street 33 kV | F4685_Wyalla Street 33 kV | F4685_Wyalla Street 33 kV
SW-Toowoomba Dalby Warwick | F4015_Ramsay Street 33 kV | % of Rated A | 4.681% | 2.292% | 0.3559% | 1.676% | 3.51%
SW-Toowoomba Dalby Warwick | F4015_Ramsay Street 33 kV | Limiting Line Name | TR_LINE 23917_1 | TR_LINE 23917_1 | TR_CABLE 86_1 | TR_LINE 23917_1 | TR_CABLE 7922_1
SW-Toowoomba Dalby Warwick | F4015_Ramsay Street 33 kV | Loading (A) | 28.0852 | 13.7526 | 2.2242 | 10.0571 | 21.062
SW-Toowoomba Dalby Warwick | F4015_Ramsay Street 33 kV | Loading (MVA) | 1.6951 | 0.82998 | 0.1342 | 0.6067 | 1.2715
SW-Toowoomba Dalby Warwick | F4015_Ramsay Street 33 kV | Loading (MW) | 1.695 | 0.82908 | 0.086433 | 0.60527 | 1.2714
SW-Toowoomba Dalby Warwick | F4015_Ramsay Street 33 kV | Power Factor | 0.99995 | 0.99891 | 0.64408 | 0.99762 | 0.99991
SW-Toowoomba Dalby Warwick | F4015_Ramsay Street 33 kV | Rating (A) | 600 | 600 | 625 | 600 | 600
SW-Toowoomba Dalby Warwick | F4015_Ramsay Street 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F4015_Ramsay Street 33 kV | Min Voltage at Constrained Conductor | 34.8444 | 34.8429 | 34.8336 | 34.8292 | 34.8538
SW-Toowoomba Dalby Warwick | F4015_Ramsay Street 33 kV | Contingency Outage | F3255_Jennings Street 33 kV | F3255_Jennings Street 33 kV | F3255_Jennings Street 33 kV | F3255_Jennings Street 33 kV | F3255_Jennings Street 33 kV
SW-Toowoomba Dalby Warwick | F4132_Shirley Road 33 kV | % of Rated A | 29.2% | 37.03% | 44.56% | 52.12% | 45.78%
SW-Toowoomba Dalby Warwick | F4132_Shirley Road 33 kV | Limiting Line Name | TR_LINE 108727_1 | TR_LINE 108727_1 | TR_LINE 108727_1 | TR_LINE 108727_1 | TR_LINE 157941_1
SW-Toowoomba Dalby Warwick | F4132_Shirley Road 33 kV | Loading (A) | 122.6201 | 155.5197 | 187.1468 | 218.9161 | 192.2812
SW-Toowoomba Dalby Warwick | F4132_Shirley Road 33 kV | Loading (MVA) | 7.2241 | 9.17 | 11.0385 | 12.9117 | 11.272
SW-Toowoomba Dalby Warwick | F4132_Shirley Road 33 kV | Loading (MW) | 7.2238 | 9.1696 | 11.0351 | 12.9016 | 11.207
SW-Toowoomba Dalby Warwick | F4132_Shirley Road 33 kV | Power Factor | 0.99996 | 0.99996 | 0.99969 | 0.99922 | 0.99424
SW-Toowoomba Dalby Warwick | F4132_Shirley Road 33 kV | Rating (A) | 420 | 420 | 420 | 420 | 420
SW-Toowoomba Dalby Warwick | F4132_Shirley Road 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F4132_Shirley Road 33 kV | Min Voltage at Constrained Conductor | 34.0142 | 34.0426 | 34.0537 | 34.0521 | 33.8451
SW-Toowoomba Dalby Warwick | F4132_Shirley Road 33 kV | Contingency Outage | F3980_Purrawunda 33 kV | F3980_Purrawunda 33 kV | F3980_Purrawunda 33 kV | F3980_Purrawunda 33 kV | F3980_Purrawunda 33 kV
SW-Toowoomba Dalby Warwick | F4245_Stanthorpe 33 kV | % of Rated A | 29.03% | 29.25% | 29.43% | 29.59% | 29.73%
SW-Toowoomba Dalby Warwick | F4245_Stanthorpe 33 kV | Limiting Line Name | TR_CABLE 107_1 | TR_CABLE 107_1 | TR_CABLE 107_1 | TR_CABLE 107_1 | TR_CABLE 107_1
SW-Toowoomba Dalby Warwick | F4245_Stanthorpe 33 kV | Loading (A) | 84.7703 | 85.4012 | 85.9214 | 86.3917 | 86.8037
SW-Toowoomba Dalby Warwick | F4245_Stanthorpe 33 kV | Loading (MVA) | 5.7025 | 5.7551 | 5.7969 | 5.835 | 5.8695
SW-Toowoomba Dalby Warwick | F4245_Stanthorpe 33 kV | Loading (MW) | 1.0696 | 1.2426 | 1.377 | 1.4888 | 1.5771
SW-Toowoomba Dalby Warwick | F4245_Stanthorpe 33 kV | Power Factor | 0.18749 | 0.21583 | 0.23746 | 0.25507 | 0.26862
SW-Toowoomba Dalby Warwick | F4245_Stanthorpe 33 kV | Rating (A) | 292 | 292 | 292 | 292 | 292
SW-Toowoomba Dalby Warwick | F4245_Stanthorpe 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F4245_Stanthorpe 33 kV | Min Voltage at Constrained Conductor | 38.8385 | 38.9069 | 38.9525 | 38.9947 | 39.0395
SW-Toowoomba Dalby Warwick | F4245_Stanthorpe 33 kV | Contingency Outage | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV
SW-Toowoomba Dalby Warwick | F4470 Vacy Street | % of Rated A | 0.4538% | 0.4538% | 0.4536% | 0.4536% | 0.4536%
SW-Toowoomba Dalby Warwick | F4470 Vacy Street | Limiting Line Name | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2
SW-Toowoomba Dalby Warwick | F4470 Vacy Street | Loading (A) | 2.2691 | 2.2689 | 2.2682 | 2.2679 | 2.2682
SW-Toowoomba Dalby Warwick | F4470 Vacy Street | Loading (MVA) | 0.13729 | 0.13727 | 0.13719 | 0.13716 | 0.13719
SW-Toowoomba Dalby Warwick | F4470 Vacy Street | Loading (MW) | 0.0023866 | 0.0023862 | 0.0023848 | 0.0023842 | 0.0023848
SW-Toowoomba Dalby Warwick | F4470 Vacy Street | Power Factor | 0.0077605 | 0.0077605 | 0.0077605 | 0.0077605 | 0.0077605
SW-Toowoomba Dalby Warwick | F4470 Vacy Street | Rating (A) | 500 | 500 | 500 | 500 | 500
SW-Toowoomba Dalby Warwick | F4470 Vacy Street | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F4470 Vacy Street | Min Voltage at Constrained Conductor | 34.933 | 34.9304 | 34.9204 | 34.9158 | 34.9203
SW-Toowoomba Dalby Warwick | F4470 Vacy Street | Contingency Outage | 728_Middle Ridge-South Toowoomba 110 kV | 728_Middle Ridge-South Toowoomba 110 kV | 728_Middle Ridge-South Toowoomba 110 kV | 728_Middle Ridge-South Toowoomba 110 kV | 728_Middle Ridge-South Toowoomba 110 kV
SW-Toowoomba Dalby Warwick | F4605_West Warwick 33 kV | % of Rated A | 2.44% | 3.276% | 3.96% | 4.547% | 5.069%
SW-Toowoomba Dalby Warwick | F4605_West Warwick 33 kV | Limiting Line Name | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1
SW-Toowoomba Dalby Warwick | F4605_West Warwick 33 kV | Loading (A) | 9.4906 | 12.7449 | 15.4034 | 17.6885 | 19.7185
SW-Toowoomba Dalby Warwick | F4605_West Warwick 33 kV | Loading (MVA) | 0.57123 | 0.76725 | 0.92724 | 1.0648 | 1.1874
SW-Toowoomba Dalby Warwick | F4605_West Warwick 33 kV | Loading (MW) | 0.56239 | 0.76095 | 0.92225 | 1.0607 | 1.1838
SW-Toowoomba Dalby Warwick | F4605_West Warwick 33 kV | Power Factor | 0.98451 | 0.99177 | 0.9946 | 0.99608 | 0.99699
SW-Toowoomba Dalby Warwick | F4605_West Warwick 33 kV | Rating (A) | 389 | 389 | 389 | 389 | 389
SW-Toowoomba Dalby Warwick | F4605_West Warwick 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F4605_West Warwick 33 kV | Min Voltage at Constrained Conductor | 34.7502 | 34.7569 | 34.7547 | 34.7559 | 34.7657
SW-Toowoomba Dalby Warwick | F4605_West Warwick 33 kV | Contingency Outage | 790_Warwick-Stanthorpe 110 kV | 790_Warwick-Stanthorpe 110 kV | 790_Warwick-Stanthorpe 110 kV | 790_Warwick-Stanthorpe 110 kV | 790_Warwick-Stanthorpe 110 kV
SW-Toowoomba Dalby Warwick | F4685_Wyalla Street 33 kV | % of Rated A | 5.139% | 3.321% | 1.765% | 0.3887% | 1.023%
SW-Toowoomba Dalby Warwick | F4685_Wyalla Street 33 kV | Limiting Line Name | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 72_1 | TR_CABLE 71_1
SW-Toowoomba Dalby Warwick | F4685_Wyalla Street 33 kV | Loading (A) | 35.4586 | 22.9163 | 12.179 | 2.7444 | 7.0564
SW-Toowoomba Dalby Warwick | F4685_Wyalla Street 33 kV | Loading (MVA) | 2.0811 | 1.3451 | 0.71473 | 0.16099 | 0.41467
SW-Toowoomba Dalby Warwick | F4685_Wyalla Street 33 kV | Loading (MW) | 2.0811 | 1.345 | 0.71445 | 0.13841 | 0.41458
SW-Toowoomba Dalby Warwick | F4685_Wyalla Street 33 kV | Power Factor | 0.99998 | 0.99993 | 0.99962 | 0.85972 | 0.99875
SW-Toowoomba Dalby Warwick | F4685_Wyalla Street 33 kV | Rating (A) | 690 | 690 | 690 | 706 | 690
SW-Toowoomba Dalby Warwick | F4685_Wyalla Street 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F4685_Wyalla Street 33 kV | Min Voltage at Constrained Conductor | 33.8846 | 33.889 | 33.8817 | 33.8673 | 33.9282
SW-Toowoomba Dalby Warwick | F4685_Wyalla Street 33 kV | Contingency Outage | F4005_Racecourse 33 kV | F4005_Racecourse 33 kV | F4005_Racecourse 33 kV | F4005_Racecourse 33 kV | F4005_Racecourse 33 kV
SW-Toowoomba Dalby Warwick | F5540_7244 Tangkam-Dalby 110 kV | % of Rated A | 16.64% | 14.72% | 13.15% | 11.82% | 10.65%
SW-Toowoomba Dalby Warwick | F5540_7244 Tangkam-Dalby 110 kV | Limiting Line Name | TR_LINE 24297_1 | TR_LINE 24297_1 | TR_LINE 24297_1 | TR_LINE 24297_1 | TR_LINE 24297_1
SW-Toowoomba Dalby Warwick | F5540_7244 Tangkam-Dalby 110 kV | Loading (A) | 43.9292 | 38.8622 | 34.7205 | 31.1973 | 28.118
SW-Toowoomba Dalby Warwick | F5540_7244 Tangkam-Dalby 110 kV | Loading (MVA) | 8.731 | 7.7233 | 6.8991 | 6.1984 | 5.5867
SW-Toowoomba Dalby Warwick | F5540_7244 Tangkam-Dalby 110 kV | Loading (MW) | 7.6216 | 6.4044 | 5.3555 | 4.401 | 3.475
SW-Toowoomba Dalby Warwick | F5540_7244 Tangkam-Dalby 110 kV | Power Factor | 0.87294 | 0.82923 | 0.77626 | 0.71001 | 0.62201
SW-Toowoomba Dalby Warwick | F5540_7244 Tangkam-Dalby 110 kV | Rating (A) | 264 | 264 | 264 | 264 | 264
SW-Toowoomba Dalby Warwick | F5540_7244 Tangkam-Dalby 110 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F5540_7244 Tangkam-Dalby 110 kV | Min Voltage at Constrained Conductor | 114.6309 | 114.678 | 114.7067 | 114.7107 | 114.7132
SW-Toowoomba Dalby Warwick | F5540_7244 Tangkam-Dalby 110 kV | Contingency Outage | F5545_7245 Tangkam-Dalby 110 kV | F5545_7245 Tangkam-Dalby 110 kV | F5545_7245 Tangkam-Dalby 110 kV | F5545_7245 Tangkam-Dalby 110 kV | F5545_7245 Tangkam-Dalby 110 kV
SW-Toowoomba Dalby Warwick | F5545_7245 Tangkam-Dalby 110 kV | % of Rated A | 34.52% | 30.52% | 27.25% | 24.47% | 22.03%
SW-Toowoomba Dalby Warwick | F5545_7245 Tangkam-Dalby 110 kV | Limiting Line Name | TR_LINE 140801_1 | TR_LINE 140801_1 | TR_LINE 140801_1 | TR_LINE 140801_1 | TR_LINE 140801_1
SW-Toowoomba Dalby Warwick | F5545_7245 Tangkam-Dalby 110 kV | Loading (A) | 43.8374 | 38.7636 | 34.6124 | 31.0775 | 27.984
SW-Toowoomba Dalby Warwick | F5545_7245 Tangkam-Dalby 110 kV | Loading (MVA) | 8.7127 | 7.7037 | 6.8776 | 6.1746 | 5.5601
SW-Toowoomba Dalby Warwick | F5545_7245 Tangkam-Dalby 110 kV | Loading (MW) | 7.6148 | 6.3993 | 5.3516 | 4.398 | 3.4728
SW-Toowoomba Dalby Warwick | F5545_7245 Tangkam-Dalby 110 kV | Power Factor | 0.87399 | 0.83068 | 0.77812 | 0.71228 | 0.62459
SW-Toowoomba Dalby Warwick | F5545_7245 Tangkam-Dalby 110 kV | Rating (A) | 127 | 127 | 127 | 127 | 127
SW-Toowoomba Dalby Warwick | F5545_7245 Tangkam-Dalby 110 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F5545_7245 Tangkam-Dalby 110 kV | Min Voltage at Constrained Conductor | 114.6774 | 114.7032 | 114.7138 | 114.71 | 114.7124
SW-Toowoomba Dalby Warwick | F5545_7245 Tangkam-Dalby 110 kV | Contingency Outage | F5540_7244 Tangkam-Dalby 110 kV | F5540_7244 Tangkam-Dalby 110 kV | F5540_7244 Tangkam-Dalby 110 kV | F5540_7244 Tangkam-Dalby 110 kV | F5540_7244 Tangkam-Dalby 110 kV
SW-Toowoomba Dalby Warwick | F5550_733(Middle Ridge-Yarranlea) 110 kV | % of Rated A | 7.443% | 7.407% | 7.431% | 7.492% | 7.677%
SW-Toowoomba Dalby Warwick | F5550_733(Middle Ridge-Yarranlea) 110 kV | Limiting Line Name | TR_LINE 224266_1 | TR_LINE 224266_1 | TR_LINE 224266_1 | TR_LINE 224266_1 | TR_LINE 224266_1
SW-Toowoomba Dalby Warwick | F5550_733(Middle Ridge-Yarranlea) 110 kV | Loading (A) | 22.0309 | 21.926 | 21.9953 | 22.1756 | 22.7246
SW-Toowoomba Dalby Warwick | F5550_733(Middle Ridge-Yarranlea) 110 kV | Loading (MVA) | 4.4003 | 4.3785 | 4.3906 | 4.4256 | 4.5353
SW-Toowoomba Dalby Warwick | F5550_733(Middle Ridge-Yarranlea) 110 kV | Loading (MW) | 0.53887 | 0.0861 | 0.2863 | 0.61203 | 0.89593
SW-Toowoomba Dalby Warwick | F5550_733(Middle Ridge-Yarranlea) 110 kV | Power Factor | 0.12246 | 0.019664 | 0.065192 | 0.13828 | 0.19753
SW-Toowoomba Dalby Warwick | F5550_733(Middle Ridge-Yarranlea) 110 kV | Rating (A) | 296 | 296 | 296 | 296 | 296
SW-Toowoomba Dalby Warwick | F5550_733(Middle Ridge-Yarranlea) 110 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F5550_733(Middle Ridge-Yarranlea) 110 kV | Min Voltage at Constrained Conductor | 115.3159 | 115.2927 | 115.2489 | 115.2209 | 115.2249
SW-Toowoomba Dalby Warwick | F5550_733(Middle Ridge-Yarranlea) 110 kV | Contingency Outage | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV
SW-Toowoomba Dalby Warwick | F5555_734(Middle Ridge-Yarranlea) 110 kV | % of Rated A | 7.713% | 7.676% | 7.7% | 7.763% | 7.954%
SW-Toowoomba Dalby Warwick | F5555_734(Middle Ridge-Yarranlea) 110 kV | Limiting Line Name | TR_LINE 225682_1 | TR_LINE 225682_1 | TR_LINE 225682_1 | TR_LINE 225682_1 | TR_LINE 225682_1
SW-Toowoomba Dalby Warwick | F5555_734(Middle Ridge-Yarranlea) 110 kV | Loading (A) | 22.1352 | 22.0311 | 22.1003 | 22.2799 | 22.8279
SW-Toowoomba Dalby Warwick | F5555_734(Middle Ridge-Yarranlea) 110 kV | Loading (MVA) | 4.4211 | 4.3995 | 4.4116 | 4.4464 | 4.5559
SW-Toowoomba Dalby Warwick | F5555_734(Middle Ridge-Yarranlea) 110 kV | Loading (MW) | 0.53892 | 0.086148 | 0.30304 | 0.62918 | 0.91425
SW-Toowoomba Dalby Warwick | F5555_734(Middle Ridge-Yarranlea) 110 kV | Power Factor | 0.1219 | 0.019581 | 0.064871 | 0.13762 | 0.19663
SW-Toowoomba Dalby Warwick | F5555_734(Middle Ridge-Yarranlea) 110 kV | Rating (A) | 287 | 287 | 287 | 287 | 287
SW-Toowoomba Dalby Warwick | F5555_734(Middle Ridge-Yarranlea) 110 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F5555_734(Middle Ridge-Yarranlea) 110 kV | Min Voltage at Constrained Conductor | 115.3163 | 115.2931 | 115.2493 | 115.2213 | 115.2253
SW-Toowoomba Dalby Warwick | F5555_734(Middle Ridge-Yarranlea) 110 kV | Contingency Outage | F5550_733(Middle Ridge-Yarranlea) 110 kV | F5550_733(Middle Ridge-Yarranlea) 110 kV | F5550_733(Middle Ridge-Yarranlea) 110 kV | F5550_733(Middle Ridge-Yarranlea) 110 kV | F5550_733(Middle Ridge-Yarranlea) 110 kV
SW-Toowoomba Dalby Warwick | F5560_735(Middle Ridge-Warwick) 110 kV | % of Rated A | 41.21% | 41.51% | 41.79% | 42.09% | 42.38%
SW-Toowoomba Dalby Warwick | F5560_735(Middle Ridge-Warwick) 110 kV | Limiting Line Name | TR_LINE 94897_1 | TR_LINE 94897_1 | TR_LINE 94897_1 | TR_LINE 94897_1 | TR_LINE 94897_1
SW-Toowoomba Dalby Warwick | F5560_735(Middle Ridge-Warwick) 110 kV | Loading (A) | 105.9082 | 106.6705 | 107.4092 | 108.1624 | 108.9175
SW-Toowoomba Dalby Warwick | F5560_735(Middle Ridge-Warwick) 110 kV | Loading (MVA) | 21.1592 | 21.3075 | 21.447 | 21.5923 | 21.7439
SW-Toowoomba Dalby Warwick | F5560_735(Middle Ridge-Warwick) 110 kV | Loading (MW) | 1.9135 | 2.9323 | 3.7601 | 4.4787 | 5.1053
SW-Toowoomba Dalby Warwick | F5560_735(Middle Ridge-Warwick) 110 kV | Power Factor | 0.08906 | 0.13623 | 0.17392 | 0.20602 | 0.23338
SW-Toowoomba Dalby Warwick | F5560_735(Middle Ridge-Warwick) 110 kV | Rating (A) | 257 | 257 | 257 | 257 | 257
SW-Toowoomba Dalby Warwick | F5560_735(Middle Ridge-Warwick) 110 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F5560_735(Middle Ridge-Warwick) 110 kV | Min Voltage at Constrained Conductor | 115.3475 | 115.3263 | 115.2828 | 115.2556 | 115.2603
SW-Toowoomba Dalby Warwick | F5560_735(Middle Ridge-Warwick) 110 kV | Contingency Outage | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV
SW-Toowoomba Dalby Warwick | F5565_736(Middle Ridge-Warwick) 110 kV | % of Rated A | 13.98% | 14.06% | 14.15% | 14.24% | 14.33%
SW-Toowoomba Dalby Warwick | F5565_736(Middle Ridge-Warwick) 110 kV | Limiting Line Name | TR_LINE 141691_1 | TR_LINE 141691_1 | TR_LINE 141691_1 | TR_LINE 141691_1 | TR_LINE 141691_1
SW-Toowoomba Dalby Warwick | F5565_736(Middle Ridge-Warwick) 110 kV | Loading (A) | 106.6492 | 107.3075 | 107.967 | 108.6539 | 109.3546
SW-Toowoomba Dalby Warwick | F5565_736(Middle Ridge-Warwick) 110 kV | Loading (MVA) | 21.4072 | 21.5361 | 21.6612 | 21.7944 | 21.9364
SW-Toowoomba Dalby Warwick | F5565_736(Middle Ridge-Warwick) 110 kV | Loading (MW) | 2.3014 | 3.327 | 4.1614 | 4.8867 | 5.52
SW-Toowoomba Dalby Warwick | F5565_736(Middle Ridge-Warwick) 110 kV | Power Factor | 0.10725 | 0.15422 | 0.19185 | 0.22395 | 0.25137
SW-Toowoomba Dalby Warwick | F5565_736(Middle Ridge-Warwick) 110 kV | Rating (A) | 763 | 763 | 763 | 763 | 763
SW-Toowoomba Dalby Warwick | F5565_736(Middle Ridge-Warwick) 110 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F5565_736(Middle Ridge-Warwick) 110 kV | Min Voltage at Constrained Conductor | 115.8889 | 115.8716 | 115.8325 | 115.8083 | 115.8157
SW-Toowoomba Dalby Warwick | F5565_736(Middle Ridge-Warwick) 110 kV | Contingency Outage | F5560_735(Middle Ridge-Warwick) 110 kV | F5560_735(Middle Ridge-Warwick) 110 kV | F5560_735(Middle Ridge-Warwick) 110 kV | F5560_735(Middle Ridge-Warwick) 110 kV | F5560_735(Middle Ridge-Warwick) 110 kV
WB-Korenan | 6112_Agnes Water 66 kV | % of Rated A | 3.474% | 5.356% | 7.364% | 9.388% | 11.59%
WB-Korenan | 6112_Agnes Water 66 kV | Limiting Line Name | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1
WB-Korenan | 6112_Agnes Water 66 kV | Loading (A) | 9.8656 | 15.2108 | 20.9131 | 26.6609 | 32.9087
WB-Korenan | 6112_Agnes Water 66 kV | Loading (MVA) | 1.1429 | 1.7646 | 2.4071 | 3.069 | 3.7893
WB-Korenan | 6112_Agnes Water 66 kV | Loading (MW) | 0.88122 | 1.6134 | 2.3092 | 2.9998 | 3.7406
WB-Korenan | 6112_Agnes Water 66 kV | Power Factor | 0.77104 | 0.9143 | 0.95931 | 0.97743 | 0.98713
WB-Korenan | 6112_Agnes Water 66 kV | Rating (A) | 284 | 284 | 284 | 284 | 284
WB-Korenan | 6112_Agnes Water 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Korenan | 6112_Agnes Water 66 kV | Min Voltage at Constrained Conductor | 66.8829 | 66.9768 | 66.4534 | 66.4611 | 66.4799
WB-Korenan | 6112_Agnes Water 66 kV | Contingency Outage | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 7187_Gin Gin - Bundaberg 132 kV | 7187_Gin Gin - Bundaberg 132 kV | 7187_Gin Gin - Bundaberg 132 kV
WB-Korenan | 7188_Gin Gin - Korenan QR 132 kV | % of Rated A | 4.515% | 4.414% | 4.459% | 4.603% | 4.875%
WB-Korenan | 7188_Gin Gin - Korenan QR 132 kV | Limiting Line Name | TR_LINE 88330_1 | TR_LINE 88330_1 | TR_LINE 88330_1 | TR_LINE 88330_1 | TR_LINE 88330_1
WB-Korenan | 7188_Gin Gin - Korenan QR 132 kV | Loading (A) | 17.0669 | 16.6836 | 16.8545 | 17.399 | 18.4288
WB-Korenan | 7188_Gin Gin - Korenan QR 132 kV | Loading (MVA) | 4.0973 | 4.009 | 4.0666 | 4.1975 | 4.4454
WB-Korenan | 7188_Gin Gin - Korenan QR 132 kV | Loading (MW) | 0.79651 | 0.046926 | 0.66666 | 1.3694 | 2.1213
WB-Korenan | 7188_Gin Gin - Korenan QR 132 kV | Power Factor | 0.1944 | 0.011705 | 0.16301 | 0.32517 | 0.47587
WB-Korenan | 7188_Gin Gin - Korenan QR 132 kV | Rating (A) | 378 | 378 | 378 | 378 | 378
WB-Korenan | 7188_Gin Gin - Korenan QR 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Korenan | 7188_Gin Gin - Korenan QR 132 kV | Min Voltage at Constrained Conductor | 138.6068 | 138.7353 | 139.2996 | 139.2841 | 139.269
WB-Korenan | 7188_Gin Gin - Korenan QR 132 kV | Contingency Outage | 7315_Aramara 132 kV | 7315_Aramara 132 kV | M041_West Bundaberg-Meadowvale 66 kV | M041_West Bundaberg-Meadowvale 66 kV | M041_West Bundaberg-Meadowvale 66 kV
WB-Wide Bay | 6205_East Bundaberg-BUCE 66 kV | % of Rated A | 33.76% | 39.7% | 45.58% | 51.11% | 56.69%
WB-Wide Bay | 6205_East Bundaberg-BUCE 66 kV | Limiting Line Name | TR_LINE 176527_1 | TR_LINE 176527_1 | TR_LINE 176527_1 | TR_LINE 176527_1 | TR_LINE 176527_1
WB-Wide Bay | 6205_East Bundaberg-BUCE 66 kV | Loading (A) | 134.0265 | 157.591 | 180.9505 | 202.9026 | 225.0691
WB-Wide Bay | 6205_East Bundaberg-BUCE 66 kV | Loading (MVA) | 15.672 | 18.4906 | 21.0148 | 23.5849 | 26.1864
WB-Wide Bay | 6205_East Bundaberg-BUCE 66 kV | Loading (MW) | 11.6428 | 15.3181 | 18.5192 | 21.482 | 24.3997
WB-Wide Bay | 6205_East Bundaberg-BUCE 66 kV | Power Factor | 0.74288 | 0.82842 | 0.88124 | 0.91084 | 0.93177
WB-Wide Bay | 6205_East Bundaberg-BUCE 66 kV | Rating (A) | 397 | 397 | 397 | 397 | 397
WB-Wide Bay | 6205_East Bundaberg-BUCE 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | 6205_East Bundaberg-BUCE 66 kV | Min Voltage at Constrained Conductor | 67.4996 | 67.7275 | 67.0332 | 67.0898 | 67.1516
WB-Wide Bay | 6205_East Bundaberg-BUCE 66 kV | Contingency Outage | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV
WB-Wide Bay | 6302_Bundaberg Central - WEBU 66 kV | % of Rated A | 47.02% | 50.68% | 54.56% | 59% | 63.78%
WB-Wide Bay | 6302_Bundaberg Central - WEBU 66 kV | Limiting Line Name | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1
WB-Wide Bay | 6302_Bundaberg Central - WEBU 66 kV | Loading (A) | 186.6746 | 201.1829 | 216.5962 | 234.2458 | 253.1958
WB-Wide Bay | 6302_Bundaberg Central - WEBU 66 kV | Loading (MVA) | 21.7831 | 23.56 | 25.11 | 27.1831 | 29.413
WB-Wide Bay | 6302_Bundaberg Central - WEBU 66 kV | Loading (MW) | 7.862 | 12.0295 | 15.6498 | 18.9805 | 22.2374
WB-Wide Bay | 6302_Bundaberg Central - WEBU 66 kV | Power Factor | 0.35899 | 0.50959 | 0.6231 | 0.69824 | 0.75604
WB-Wide Bay | 6302_Bundaberg Central - WEBU 66 kV | Rating (A) | 397 | 397 | 397 | 397 | 397
WB-Wide Bay | 6302_Bundaberg Central - WEBU 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | 6302_Bundaberg Central - WEBU 66 kV | Min Voltage at Constrained Conductor | 67.0322 | 67.2125 | 66.4803 | 66.5002 | 66.527
WB-Wide Bay | 6302_Bundaberg Central - WEBU 66 kV | Contingency Outage | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV
WB-Wide Bay | 6366_Gootchie 66 kV | % of Rated A | 22.64% | 70.78% | 77.86% | 84.15% | 91.33%
WB-Wide Bay | 6366_Gootchie 66 kV | Limiting Line Name | TR_LINE 7245_1 | TR_LINE 139374_1 | TR_LINE 139374_1 | TR_LINE 139374_1 | TR_LINE 139374_1
WB-Wide Bay | 6366_Gootchie 66 kV | Loading (A) | 29.8841 | 93.4247 | 102.7779 | 111.0739 | 120.5615
WB-Wide Bay | 6366_Gootchie 66 kV | Loading (MVA) | 3.5138 | 11.1875 | 12.3073 | 13.3074 | 14.4628
WB-Wide Bay | 6366_Gootchie 66 kV | Loading (MW) | 3.4554 | 8.4993 | 9.451 | 10.35 | 11.4571
WB-Wide Bay | 6366_Gootchie 66 kV | Power Factor | 0.97179 | 0.75956 | 0.76772 | 0.77752 | 0.7919
WB-Wide Bay | 6366_Gootchie 66 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
WB-Wide Bay | 6366_Gootchie 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | 6366_Gootchie 66 kV | Min Voltage at Constrained Conductor | 67.8852 | 69.1325 | 69.1303 | 69.1642 | 69.252
WB-Wide Bay | 6366_Gootchie 66 kV | Contingency Outage | T014_Maryborough-Pialba Tee Howard 66 kV | 7315_Aramara 132 kV | 7315_Aramara 132 kV | 7315_Aramara 132 kV | 7315_Aramara 132 kV
WB-Wide Bay | 7187_Gin Gin - Bundaberg 132 kV | % of Rated A | 29.65% | 28.46% | 55.32% | 55.45% | 55.72%
WB-Wide Bay | 7187_Gin Gin - Bundaberg 132 kV | Limiting Line Name | TR_LINE 6941_1 | TR_LINE 6941_1 | TR_LINE 6941_d | TR_LINE 6941_d | TR_LINE 6941_d
WB-Wide Bay | 7187_Gin Gin - Bundaberg 132 kV | Loading (A) | 201.331 | 193.232 | 403.2849 | 404.2413 | 406.2199
WB-Wide Bay | 7187_Gin Gin - Bundaberg 132 kV | Loading (MVA) | 48.1445 | 46.2493 | 94.9877 | 95.213 | 95.6792
WB-Wide Bay | 7187_Gin Gin - Bundaberg 132 kV | Loading (MW) | 34.3618 | 30.2833 | 9.999 | 9.999 | 9.999
WB-Wide Bay | 7187_Gin Gin - Bundaberg 132 kV | Power Factor | 0.71372 | 0.65479 | 0.1052 | 0.10495 | 0.10444
WB-Wide Bay | 7187_Gin Gin - Bundaberg 132 kV | Rating (A) | 679 | 679 | 729 | 729 | 729
WB-Wide Bay | 7187_Gin Gin - Bundaberg 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | 7187_Gin Gin - Bundaberg 132 kV | Min Voltage at Constrained Conductor | 138.0624 | 138.1863 | 135.96 | 135.96 | 135.96
WB-Wide Bay | 7187_Gin Gin - Bundaberg 132 kV | Contingency Outage | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 7315_Aramara 132 kV | 7315_Aramara 132 kV | 7315_Aramara 132 kV
WB-Wide Bay | 7190_Woolooga-Mungar 132 kV | % of Rated A | 3.006% | 3.006% | 3.006% | 3.006% | 3.006%
WB-Wide Bay | 7190_Woolooga-Mungar 132 kV | Limiting Line Name | TR_LINE 223602_1 | TR_LINE 223602_1 | TR_LINE 223602_1 | TR_LINE 223602_1 | TR_LINE 223602_1
WB-Wide Bay | 7190_Woolooga-Mungar 132 kV | Loading (A) | 7.4858 | 7.4858 | 7.4858 | 7.4858 | 7.4858
WB-Wide Bay | 7190_Woolooga-Mungar 132 kV | Loading (MVA) | 1.8 | 1.8 | 1.8 | 1.8 | 1.8
WB-Wide Bay | 7190_Woolooga-Mungar 132 kV | Loading (MW) | 1.8 | 1.8 | 1.8 | 1.8 | 1.8
WB-Wide Bay | 7190_Woolooga-Mungar 132 kV | Power Factor | 1 | 1 | 1 | 1 | 1
WB-Wide Bay | 7190_Woolooga-Mungar 132 kV | Rating (A) | 249 | 249 | 249 | 249 | 249
WB-Wide Bay | 7190_Woolooga-Mungar 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | 7190_Woolooga-Mungar 132 kV | Min Voltage at Constrained Conductor | 138.8284 | 138.8284 | 138.8284 | 138.8284 | 138.8284
WB-Wide Bay | 7190_Woolooga-Mungar 132 kV | Contingency Outage | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | M036_Bundaberg-South Bundaberg 66 kV
WB-Wide Bay | 7204_Bundaberg - Clayton 132 kV | % of Rated A | 1.138% | 1.135% | 1.145% | 1.145% | 1.145%
WB-Wide Bay | 7204_Bundaberg - Clayton 132 kV | Limiting Line Name | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1
WB-Wide Bay | 7204_Bundaberg - Clayton 132 kV | Loading (A) | 10.0783 | 10.0559 | 10.1488 | 10.1463 | 10.1433
WB-Wide Bay | 7204_Bundaberg - Clayton 132 kV | Loading (MVA) | 2.4536 | 2.4542 | 2.452 | 2.4521 | 2.4522
WB-Wide Bay | 7204_Bundaberg - Clayton 132 kV | Loading (MW) | 2.4002 | 2.4002 | 2.4002 | 2.4002 | 2.4002
WB-Wide Bay | 7204_Bundaberg - Clayton 132 kV | Power Factor | 0.97814 | 0.97793 | 0.97877 | 0.97875 | 0.97872
WB-Wide Bay | 7204_Bundaberg - Clayton 132 kV | Rating (A) | 886 | 886 | 886 | 886 | 886
WB-Wide Bay | 7204_Bundaberg - Clayton 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | 7204_Bundaberg - Clayton 132 kV | Min Voltage at Constrained Conductor | 140.5598 | 140.9039 | 139.4933 | 139.5317 | 139.5763
WB-Wide Bay | 7204_Bundaberg - Clayton 132 kV | Contingency Outage | T014_Maryborough-Pialba Tee Howard 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV | 7215_Bundaberg - ISIS No 1 132 kV | 7215_Bundaberg - ISIS No 1 132 kV | 7215_Bundaberg - ISIS No 1 132 kV
WB-Wide Bay | 7215_Bundaberg - ISIS No 1 132 kV | % of Rated A | 72.06% | 75.41% | 87.23% | 85.89% | 84.46%
WB-Wide Bay | 7215_Bundaberg - ISIS No 1 132 kV | Limiting Line Name | TR_LINE 6780_2 | TR_LINE 6780_2 | TR_LINE 6780_2 | TR_LINE 6780_2 | TR_LINE 6780_2
WB-Wide Bay | 7215_Bundaberg - ISIS No 1 132 kV | Loading (A) | 178.7068 | 187.0111 | 216.3385 | 213.0047 | 209.4549
WB-Wide Bay | 7215_Bundaberg - ISIS No 1 132 kV | Loading (MVA) | 43.6149 | 45.7424 | 52.2777 | 51.4871 | 50.6444
WB-Wide Bay | 7215_Bundaberg - ISIS No 1 132 kV | Loading (MW) | 42.9864 | 44.921 | 47.3347 | 46.6551 | 45.8252
WB-Wide Bay | 7215_Bundaberg - ISIS No 1 132 kV | Power Factor | 0.98559 | 0.98204 | 0.90239 | 0.90367 | 0.90294
WB-Wide Bay | 7215_Bundaberg - ISIS No 1 132 kV | Rating (A) | 248 | 248 | 248 | 248 | 248
WB-Wide Bay | 7215_Bundaberg - ISIS No 1 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | 7215_Bundaberg - ISIS No 1 132 kV | Min Voltage at Constrained Conductor | 140.0808 | 140.4709 | 139.5154 | 139.5559 | 139.5983
WB-Wide Bay | 7215_Bundaberg - ISIS No 1 132 kV | Contingency Outage | 7328_Bundaberg - ISIS No 2 132 kV | 7328_Bundaberg - ISIS No 2 132 kV | 7328_Bundaberg - ISIS No 2 132 kV | 7328_Bundaberg - ISIS No 2 132 kV | 7328_Bundaberg - ISIS No 2 132 kV
WB-Wide Bay | 7315_Aramara 132 kV | % of Rated A | 24.05% | 25.53% | 26.8% | 30.17% | 33.76%
WB-Wide Bay | 7315_Aramara 132 kV | Limiting Line Name | TR_LINE 88000_1 | TR_LINE 88000_1 | TR_LINE 88000_1 | TR_LINE 88000_1 | TR_LINE 88000_1
WB-Wide Bay | 7315_Aramara 132 kV | Loading (A) | 262.6185 | 278.8019 | 292.6116 | 329.4861 | 368.706
WB-Wide Bay | 7315_Aramara 132 kV | Loading (MVA) | 62.7014 | 66.6751 | 70.4269 | 79.2826 | 88.7137
WB-Wide Bay | 7315_Aramara 132 kV | Loading (MW) | 56.5018 | 59.2531 | 69.0851 | 78.2832 | 87.911
WB-Wide Bay | 7315_Aramara 132 kV | Power Factor | 0.90113 | 0.88868 | 0.98095 | 0.98739 | 0.99095
WB-Wide Bay | 7315_Aramara 132 kV | Rating (A) | 1092 | 1092 | 1092 | 1092 | 1092
WB-Wide Bay | 7315_Aramara 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | 7315_Aramara 132 kV | Min Voltage at Constrained Conductor | 137.838 | 138.0636 | 138.9517 | 138.9165 | 138.9058
WB-Wide Bay | 7315_Aramara 132 kV | Contingency Outage | 7316_Aramara 132 kV | 7316_Aramara 132 kV | 7316_Aramara 132 kV | 7316_Aramara 132 kV | 7316_Aramara 132 kV
WB-Wide Bay | 7316_Aramara 132 kV | % of Rated A | 24.05% | 25.53% | 26.8% | 30.17% | 33.76%
WB-Wide Bay | 7316_Aramara 132 kV | Limiting Line Name | TR_LINE 88004_1 | TR_LINE 88004_1 | TR_LINE 88004_1 | TR_LINE 88004_1 | TR_LINE 88004_1
WB-Wide Bay | 7316_Aramara 132 kV | Loading (A) | 262.6118 | 278.7942 | 292.6032 | 329.4766 | 368.6953
WB-Wide Bay | 7316_Aramara 132 kV | Loading (MVA) | 62.6997 | 66.6732 | 70.4247 | 79.2802 | 88.711
WB-Wide Bay | 7316_Aramara 132 kV | Loading (MW) | 56.5002 | 59.2513 | 69.083 | 78.2808 | 87.9083
WB-Wide Bay | 7316_Aramara 132 kV | Power Factor | 0.90112 | 0.88868 | 0.98095 | 0.98739 | 0.99095
WB-Wide Bay | 7316_Aramara 132 kV | Rating (A) | 1092 | 1092 | 1092 | 1092 | 1092
WB-Wide Bay | 7316_Aramara 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | 7316_Aramara 132 kV | Min Voltage at Constrained Conductor | 137.838 | 138.0636 | 138.9517 | 138.9165 | 138.9058
WB-Wide Bay | 7316_Aramara 132 kV | Contingency Outage | 7315_Aramara 132 kV | 7315_Aramara 132 kV | 7315_Aramara 132 kV | 7315_Aramara 132 kV | 7315_Aramara 132 kV
WB-Wide Bay | 7328_Bundaberg - ISIS No 2 132 kV | % of Rated A | 72.01% | 75.35% | 87.17% | 85.8% | 84.4%
WB-Wide Bay | 7328_Bundaberg - ISIS No 2 132 kV | Limiting Line Name | TR_LINE 98484_1 | TR_LINE 98484_1 | TR_LINE 98484_1 | TR_LINE 98484_1 | TR_LINE 98484_1
WB-Wide Bay | 7328_Bundaberg - ISIS No 2 132 kV | Loading (A) | 178.5813 | 186.8796 | 216.1932 | 212.7905 | 209.3156
WB-Wide Bay | 7328_Bundaberg - ISIS No 2 132 kV | Loading (MVA) | 43.5849 | 45.7109 | 52.2419 | 51.4338 | 50.61
WB-Wide Bay | 7328_Bundaberg - ISIS No 2 132 kV | Loading (MW) | 42.9564 | 44.8896 | 47.3034 | 46.6234 | 45.795
WB-Wide Bay | 7328_Bundaberg - ISIS No 2 132 kV | Power Factor | 0.98558 | 0.98203 | 0.90529 | 0.90633 | 0.90474
WB-Wide Bay | 7328_Bundaberg - ISIS No 2 132 kV | Rating (A) | 248 | 248 | 248 | 248 | 248
WB-Wide Bay | 7328_Bundaberg - ISIS No 2 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | 7328_Bundaberg - ISIS No 2 132 kV | Min Voltage at Constrained Conductor | 140.8668 | 141.1815 | 139.5134 | 139.5518 | 139.5964
WB-Wide Bay | 7328_Bundaberg - ISIS No 2 132 kV | Contingency Outage | 7215_Bundaberg - ISIS No 1 132 kV | 7215_Bundaberg - ISIS No 1 132 kV | 7215_Bundaberg - ISIS No 1 132 kV | 7215_Bundaberg - ISIS No 1 132 kV | 7215_Bundaberg - ISIS No 1 132 kV
WB-Wide Bay | 7329_Maryborough 132 kV | % of Rated A | 19.34% | 22.68% | 25.52% | 29.5% | 34.89%
WB-Wide Bay | 7329_Maryborough 132 kV | Limiting Line Name | TR_LINE 120325_1 | TR_LINE 120325_1 | TR_LINE 120325_1 | TR_LINE 120325_1 | TR_LINE 120325_1
WB-Wide Bay | 7329_Maryborough 132 kV | Loading (A) | 109.0737 | 127.894 | 143.918 | 166.3748 | 196.7941
WB-Wide Bay | 7329_Maryborough 132 kV | Loading (MVA) | 26.327 | 30.9639 | 34.8969 | 40.335 | 47.7622
WB-Wide Bay | 7329_Maryborough 132 kV | Loading (MW) | 15.8366 | 16.1319 | 23.6503 | 32.0598 | 41.1239
WB-Wide Bay | 7329_Maryborough 132 kV | Power Factor | 0.60062 | 0.51992 | 0.67651 | 0.79344 | 0.86014
WB-Wide Bay | 7329_Maryborough 132 kV | Rating (A) | 564 | 564 | 564 | 564 | 564
WB-Wide Bay | 7329_Maryborough 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | 7329_Maryborough 132 kV | Min Voltage at Constrained Conductor | 139.3544 | 139.78 | 139.9944 | 139.9697 | 139.9955
WB-Wide Bay | 7329_Maryborough 132 kV | Contingency Outage | 7330_Maryborough 132 kV | 7330_Maryborough 132 kV | 7330_Maryborough 132 kV | 7330_Maryborough 132 kV | 7330_Maryborough 132 kV
WB-Wide Bay | 7330_Maryborough 132 kV | % of Rated A | 19.34% | 22.68% | 25.52% | 29.5% | 34.89%
WB-Wide Bay | 7330_Maryborough 132 kV | Limiting Line Name | TR_LINE 7684_1 | TR_LINE 7684_1 | TR_LINE 7684_1 | TR_LINE 7684_1 | TR_LINE 7684_1
WB-Wide Bay | 7330_Maryborough 132 kV | Loading (A) | 109.0724 | 127.89 | 143.9135 | 166.3696 | 196.788
WB-Wide Bay | 7330_Maryborough 132 kV | Loading (MVA) | 26.3271 | 30.9635 | 34.8963 | 40.3344 | 47.7614
WB-Wide Bay | 7330_Maryborough 132 kV | Loading (MW) | 15.8365 | 16.1312 | 23.6495 | 32.0588 | 41.1225
WB-Wide Bay | 7330_Maryborough 132 kV | Power Factor | 0.60062 | 0.51991 | 0.6765 | 0.79343 | 0.86014
WB-Wide Bay | 7330_Maryborough 132 kV | Rating (A) | 564 | 564 | 564 | 564 | 564
WB-Wide Bay | 7330_Maryborough 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | 7330_Maryborough 132 kV | Min Voltage at Constrained Conductor | 139.3563 | 139.7823 | 139.9967 | 139.972 | 139.998
WB-Wide Bay | 7330_Maryborough 132 kV | Contingency Outage | 7329_Maryborough 132 kV | 7329_Maryborough 132 kV | 7329_Maryborough 132 kV | 7329_Maryborough 132 kV | 7329_Maryborough 132 kV
WB-Wide Bay | 764_Woolooga-Kilkivan No 1 132 kV | % of Rated A | 3.629% | 10.27% | 11.91% | 13.4% | 15.02%
WB-Wide Bay | 764_Woolooga-Kilkivan No 1 132 kV | Limiting Line Name | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1
WB-Wide Bay | 764_Woolooga-Kilkivan No 1 132 kV | Loading (A) | 8.9992 | 25.4601 | 29.5278 | 33.2245 | 37.2397
WB-Wide Bay | 764_Woolooga-Kilkivan No 1 132 kV | Loading (MVA) | 2.1604 | 6.1111 | 7.087 | 7.9739 | 8.9372
WB-Wide Bay | 764_Woolooga-Kilkivan No 1 132 kV | Loading (MW) | 0.12103 | 5.44 | 6.3113 | 7.1138 | 7.9915
WB-Wide Bay | 764_Woolooga-Kilkivan No 1 132 kV | Power Factor | 0.055849 | 0.89019 | 0.89054 | 0.89213 | 0.89419
WB-Wide Bay | 764_Woolooga-Kilkivan No 1 132 kV | Rating (A) | 248 | 248 | 248 | 248 | 248
WB-Wide Bay | 764_Woolooga-Kilkivan No 1 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | 764_Woolooga-Kilkivan No 1 132 kV | Min Voltage at Constrained Conductor | 138.6 | 138.5793 | 138.5707 | 138.5644 | 138.5583
WB-Wide Bay | 764_Woolooga-Kilkivan No 1 132 kV | Contingency Outage | M036_Bundaberg-South Bundaberg 66 kV | 7315_Aramara 132 kV | 7315_Aramara 132 kV | 7315_Aramara 132 kV | 7315_Aramara 132 kV
WB-Wide Bay | 765_Woolooga-Kilkivan No 2 132 kV | % of Rated A | 3.629% | 10.27% | 11.91% | 13.4% | 15.02%
WB-Wide Bay | 765_Woolooga-Kilkivan No 2 132 kV | Limiting Line Name | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1
WB-Wide Bay | 765_Woolooga-Kilkivan No 2 132 kV | Loading (A) | 8.9989 | 25.46 | 29.5276 | 33.2243 | 37.2395
WB-Wide Bay | 765_Woolooga-Kilkivan No 2 132 kV | Loading (MVA) | 2.1603 | 6.1111 | 7.087 | 7.9738 | 8.9371
WB-Wide Bay | 765_Woolooga-Kilkivan No 2 132 kV | Loading (MW) | 0.12102 | 5.44 | 6.3112 | 7.1137 | 7.9915
WB-Wide Bay | 765_Woolooga-Kilkivan No 2 132 kV | Power Factor | 0.055847 | 0.89019 | 0.89054 | 0.89213 | 0.89419
WB-Wide Bay | 765_Woolooga-Kilkivan No 2 132 kV | Rating (A) | 248 | 248 | 248 | 248 | 248
WB-Wide Bay | 765_Woolooga-Kilkivan No 2 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | 765_Woolooga-Kilkivan No 2 132 kV | Min Voltage at Constrained Conductor | 138.6 | 138.5793 | 138.5707 | 138.5644 | 138.5583
WB-Wide Bay | 765_Woolooga-Kilkivan No 2 132 kV | Contingency Outage | M036_Bundaberg-South Bundaberg 66 kV | 7315_Aramara 132 kV | 7315_Aramara 132 kV | 7315_Aramara 132 kV | 7315_Aramara 132 kV
WB-Wide Bay | 784_ISIS 132 kV | % of Rated A | 68.77% | 72.37% | 80.06% | 82.25% | 84.28%
WB-Wide Bay | 784_ISIS 132 kV | Limiting Line Name | TR_LINE 118475_1 | TR_LINE 118475_1 | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1
WB-Wide Bay | 784_ISIS 132 kV | Loading (A) | 170.5446 | 179.478 | 198.5517 | 203.9698 | 209.0236
WB-Wide Bay | 784_ISIS 132 kV | Loading (MVA) | 41.1182 | 43.3847 | 48.199 | 49.5261 | 50.7734
WB-Wide Bay | 784_ISIS 132 kV | Loading (MW) | 40.9658 | 43.3443 | 46.2871 | 47.7563 | 49.0527
WB-Wide Bay | 784_ISIS 132 kV | Power Factor | 0.99629 | 0.99907 | 0.96033 | 0.96426 | 0.96609
WB-Wide Bay | 784_ISIS 132 kV | Rating (A) | 248 | 248 | 248 | 248 | 248
WB-Wide Bay | 784_ISIS 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | 784_ISIS 132 kV | Min Voltage at Constrained Conductor | 139.1941 | 139.5558 | 140.1251 | 140.149 | 140.1994
WB-Wide Bay | 784_ISIS 132 kV | Contingency Outage | 785_ISIS 132 kV | 785_ISIS 132 kV | 785_ISIS 132 kV | 785_ISIS 132 kV | 785_ISIS 132 kV
WB-Wide Bay | 785_ISIS 132 kV | % of Rated A | 68.8% | 72.57% | 80.35% | 82.55% | 84.59%
WB-Wide Bay | 785_ISIS 132 kV | Limiting Line Name | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1
WB-Wide Bay | 785_ISIS 132 kV | Loading (A) | 170.6208 | 179.9708 | 199.2743 | 204.7121 | 209.7842
WB-Wide Bay | 785_ISIS 132 kV | Loading (MVA) | 41.5716 | 43.9606 | 48.3724 | 49.7043 | 50.9561
WB-Wide Bay | 785_ISIS 132 kV | Loading (MW) | 41.4684 | 43.9279 | 46.4631 | 47.9378 | 49.2392
WB-Wide Bay | 785_ISIS 132 kV | Power Factor | 0.99751 | 0.99925 | 0.96053 | 0.96446 | 0.9663
WB-Wide Bay | 785_ISIS 132 kV | Rating (A) | 248 | 248 | 248 | 248 | 248
WB-Wide Bay | 785_ISIS 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | 785_ISIS 132 kV | Min Voltage at Constrained Conductor | 140.6654 | 141.0203 | 140.1465 | 140.1798 | 140.2355
WB-Wide Bay | 785_ISIS 132 kV | Contingency Outage | 784_ISIS 132 kV | 784_ISIS 132 kV | 784_ISIS 132 kV | 784_ISIS 132 kV | 784_ISIS 132 kV
WB-Wide Bay | 786_Gin Gin - Bundaberg 132 kV | % of Rated A | 71.18% | 68.31% | 67.05% | 61.93% | 57.72%
WB-Wide Bay | 786_Gin Gin - Bundaberg 132 kV | Limiting Line Name | TR_LINE 112963_1 | TR_LINE 112963_1 | TR_LINE 112963_1 | TR_LINE 112963_1 | TR_LINE 112963_1
WB-Wide Bay | 786_Gin Gin - Bundaberg 132 kV | Loading (A) | 201.4268 | 193.3251 | 189.7593 | 175.2667 | 163.3393
WB-Wide Bay | 786_Gin Gin - Bundaberg 132 kV | Loading (MVA) | 48.1679 | 46.272 | 45.0434 | 41.5921 | 38.7586
WB-Wide Bay | 786_Gin Gin - Bundaberg 132 kV | Loading (MW) | 34.3582 | 30.277 | 24.0742 | 18.4371 | 12.6447
WB-Wide Bay | 786_Gin Gin - Bundaberg 132 kV | Power Factor | 0.71305 | 0.65433 | 0.53418 | 0.44328 | 0.32624
WB-Wide Bay | 786_Gin Gin - Bundaberg 132 kV | Rating (A) | 283 | 283 | 283 | 283 | 283
WB-Wide Bay | 786_Gin Gin - Bundaberg 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | 786_Gin Gin - Bundaberg 132 kV | Min Voltage at Constrained Conductor | 138.0639 | 138.1878 | 137.0464 | 137.0095 | 136.9989
WB-Wide Bay | 786_Gin Gin - Bundaberg 132 kV | Contingency Outage | 7187_Gin Gin - Bundaberg 132 kV | 7187_Gin Gin - Bundaberg 132 kV | 7187_Gin Gin - Bundaberg 132 kV | 7187_Gin Gin - Bundaberg 132 kV | 7187_Gin Gin - Bundaberg 132 kV
WB-Wide Bay | M001_Tarong-Kingaroy East 66 kV | % of Rated A | 4.408% | 3.249% | 3.339% | 4.223% | 5.427%
WB-Wide Bay | M001_Tarong-Kingaroy East 66 kV | Limiting Line Name | TR_LINE 7977_1 | TR_LINE 7977_1 | TR_LINE 7977_1 | TR_LINE 7977_1 | TR_LINE 7977_1
WB-Wide Bay | M001_Tarong-Kingaroy East 66 kV | Loading (A) | 24.1554 | 17.8053 | 18.2964 | 23.1423 | 29.7374
WB-Wide Bay | M001_Tarong-Kingaroy East 66 kV | Loading (MVA) | 2.9265 | 2.1574 | 2.2174 | 2.8049 | 3.6045
WB-Wide Bay | M001_Tarong-Kingaroy East 66 kV | Loading (MW) | 2.0502 | 0.52191 | 0.76272 | 1.9046 | 2.9811
WB-Wide Bay | M001_Tarong-Kingaroy East 66 kV | Power Factor | 0.70058 | 0.24192 | 0.3437 | 0.6787 | 0.82661
WB-Wide Bay | M001_Tarong-Kingaroy East 66 kV | Rating (A) | 548 | 548 | 548 | 548 | 548
WB-Wide Bay | M001_Tarong-Kingaroy East 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M001_Tarong-Kingaroy East 66 kV | Min Voltage at Constrained Conductor | 69.9471 | 69.9552 | 69.97 | 69.9753 | 69.9803
WB-Wide Bay | M001_Tarong-Kingaroy East 66 kV | Contingency Outage | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV
WB-Wide Bay | M002_Tarong-Kingaroy West 66 kV | % of Rated A | 4.403% | 3.242% | 3.332% | 4.218% | 5.423%
WB-Wide Bay | M002_Tarong-Kingaroy West 66 kV | Limiting Line Name | TR_LINE 7252_2 | TR_LINE 7252_2 | TR_LINE 7252_2 | TR_LINE 7252_2 | TR_LINE 7252_2
WB-Wide Bay | M002_Tarong-Kingaroy West 66 kV | Loading (A) | 24.1277 | 17.7676 | 18.2599 | 23.1138 | 29.7156
WB-Wide Bay | M002_Tarong-Kingaroy West 66 kV | Loading (MVA) | 2.9231 | 2.1528 | 2.2129 | 2.8014 | 3.6018
WB-Wide Bay | M002_Tarong-Kingaroy West 66 kV | Loading (MW) | 2.0502 | 0.5219 | 0.76576 | 1.91 | 2.9905
WB-Wide Bay | M002_Tarong-Kingaroy West 66 kV | Power Factor | 0.70138 | 0.24243 | 0.34439 | 0.67954 | 0.82722
WB-Wide Bay | M002_Tarong-Kingaroy West 66 kV | Rating (A) | 548 | 548 | 548 | 548 | 548
WB-Wide Bay | M002_Tarong-Kingaroy West 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M002_Tarong-Kingaroy West 66 kV | Min Voltage at Constrained Conductor | 69.947 | 69.9551 | 69.9698 | 69.9752 | 69.9802
WB-Wide Bay | M002_Tarong-Kingaroy West 66 kV | Contingency Outage | M001_Tarong-Kingaroy East 66 kV | M001_Tarong-Kingaroy East 66 kV | M001_Tarong-Kingaroy East 66 kV | M001_Tarong-Kingaroy East 66 kV | M001_Tarong-Kingaroy East 66 kV
WB-Wide Bay | M003_Kingaroy- Yarraman 66 kV | % of Rated A | 14.94% | 18.19% | 20.91% | 23.31% | 25.57%
WB-Wide Bay | M003_Kingaroy- Yarraman 66 kV | Limiting Line Name | TR_LINE 7254_1 | TR_LINE 7254_1 | TR_LINE 7254_1 | TR_LINE 7254_1 | TR_LINE 7254_1
WB-Wide Bay | M003_Kingaroy- Yarraman 66 kV | Loading (A) | 19.7229 | 24.0162 | 27.6073 | 30.7724 | 33.751
WB-Wide Bay | M003_Kingaroy- Yarraman 66 kV | Loading (MVA) | 2.3926 | 2.9158 | 3.3544 | 3.7411 | 4.1089
WB-Wide Bay | M003_Kingaroy- Yarraman 66 kV | Loading (MW) | 2.3171 | 2.8629 | 3.3167 | 3.7152 | 4.0897
WB-Wide Bay | M003_Kingaroy- Yarraman 66 kV | Power Factor | 0.96539 | 0.97811 | 0.98444 | 0.98826 | 0.99088
WB-Wide Bay | M003_Kingaroy- Yarraman 66 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
WB-Wide Bay | M003_Kingaroy- Yarraman 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M003_Kingaroy- Yarraman 66 kV | Min Voltage at Constrained Conductor | 70.0399 | 70.096 | 70.1505 | 70.1908 | 70.2283
WB-Wide Bay | M003_Kingaroy- Yarraman 66 kV | Contingency Outage | M046_Tarong-Caboonbah 66 kV | M046_Tarong-Caboonbah 66 kV | M046_Tarong-Caboonbah 66 kV | M046_Tarong-Caboonbah 66 kV | M046_Tarong-Caboonbah 66 kV
WB-Wide Bay | M004_Murgon-Kingaroy 66 kV | % of Rated A | 5.171% | 5.446% | 5.573% | 5.692% | 5.807%
WB-Wide Bay | M004_Murgon-Kingaroy 66 kV | Limiting Line Name | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1
WB-Wide Bay | M004_Murgon-Kingaroy 66 kV | Loading (A) | 8.7385 | 9.2031 | 9.4186 | 9.6201 | 9.8141
WB-Wide Bay | M004_Murgon-Kingaroy 66 kV | Loading (MVA) | 1.0249 | 1.1171 | 1.1438 | 1.1686 | 1.1923
WB-Wide Bay | M004_Murgon-Kingaroy 66 kV | Loading (MW) | 0.35476 | 0.43641 | 0.50271 | 0.55903 | 0.6096
WB-Wide Bay | M004_Murgon-Kingaroy 66 kV | Power Factor | 0.34612 | 0.39063 | 0.43951 | 0.47838 | 0.51125
WB-Wide Bay | M004_Murgon-Kingaroy 66 kV | Rating (A) | 169 | 169 | 169 | 169 | 169
WB-Wide Bay | M004_Murgon-Kingaroy 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M004_Murgon-Kingaroy 66 kV | Min Voltage at Constrained Conductor | 67.7172 | 70.0834 | 70.1115 | 70.132 | 70.1432
WB-Wide Bay | M004_Murgon-Kingaroy 66 kV | Contingency Outage | M036_Bundaberg-South Bundaberg 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV
WB-Wide Bay | M005 KINGAROY-BOONDOOMA | % of Rated A | 10.1% | 9.482% | 8.943% | 8.449% | 7.96%
WB-Wide Bay | M005 KINGAROY-BOONDOOMA | Limiting Line Name | TR_LINE 65620_1 | TR_LINE 65620_1 | TR_LINE 65620_1 | TR_LINE 65620_1 | TR_LINE 65620_1
WB-Wide Bay | M005 KINGAROY-BOONDOOMA | Loading (A) | 13.529 | 12.706 | 11.9833 | 11.3211 | 10.6658
WB-Wide Bay | M005 KINGAROY-BOONDOOMA | Loading (MVA) | 1.6377 | 1.539 | 1.4525 | 1.3729 | 1.294
WB-Wide Bay | M005 KINGAROY-BOONDOOMA | Loading (MW) | 1.6377 | 1.539 | 1.4525 | 1.3729 | 1.294
WB-Wide Bay | M005 KINGAROY-BOONDOOMA | Power Factor | 0.99995 | 0.99996 | 0.99996 | 0.99997 | 0.99997
WB-Wide Bay | M005 KINGAROY-BOONDOOMA | Rating (A) | 134 | 134 | 134 | 134 | 134
WB-Wide Bay | M005 KINGAROY-BOONDOOMA | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M005 KINGAROY-BOONDOOMA | Min Voltage at Constrained Conductor | 69.8793 | 69.9252 | 69.9721 | 70.0064 | 70.0389
WB-Wide Bay | M005 KINGAROY-BOONDOOMA | Contingency Outage | M003_Kingaroy- Yarraman 66 kV | M003_Kingaroy- Yarraman 66 kV | M003_Kingaroy- Yarraman 66 kV | M003_Kingaroy- Yarraman 66 kV | M003_Kingaroy- Yarraman 66 kV
WB-Wide Bay | M007_Proston 66 kV | % of Rated A | 4.929% | 5.395% | 5.776% | 6.129% | 6.461%
WB-Wide Bay | M007_Proston 66 kV | Limiting Line Name | TR_LINE 7264_1 | TR_LINE 7264_1 | TR_LINE 7264_1 | TR_LINE 7264_1 | TR_LINE 7264_1
WB-Wide Bay | M007_Proston 66 kV | Loading (A) | 4.8792 | 5.3407 | 5.718 | 6.0678 | 6.3961
WB-Wide Bay | M007_Proston 66 kV | Loading (MVA) | 0.57243 | 0.64847 | 0.68017 | 0.72098 | 0.75908
WB-Wide Bay | M007_Proston 66 kV | Loading (MW) | 0.35504 | 0.43671 | 0.50295 | 0.55926 | 0.6098
WB-Wide Bay | M007_Proston 66 kV | Power Factor | 0.62021 | 0.67342 | 0.73943 | 0.77567 | 0.80332
WB-Wide Bay | M007_Proston 66 kV | Rating (A) | 99 | 99 | 99 | 99 | 99
WB-Wide Bay | M007_Proston 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M007_Proston 66 kV | Min Voltage at Constrained Conductor | 67.7349 | 70.1024 | 68.677 | 68.601 | 68.5183
WB-Wide Bay | M007_Proston 66 kV | Contingency Outage | M036_Bundaberg-South Bundaberg 66 kV | M010_Maryborough - Owanyilla 66 kV | 7315_Aramara 132 kV | 7315_Aramara 132 kV | 7315_Aramara 132 kV
WB-Wide Bay | M008_Kilkivan-Murgon No 1 66 kV | % of Rated A | 4.85% | 5.231% | 5.797% | 6.437% | 7.121%
WB-Wide Bay | M008_Kilkivan-Murgon No 1 66 kV | Limiting Line Name | TR_LINE 116487_1 | TR_LINE 116487_1 | TR_LINE 7214_1 | TR_LINE 7214_1 | TR_LINE 7214_1
WB-Wide Bay | M008_Kilkivan-Murgon No 1 66 kV | Loading (A) | 8.7777 | 9.4684 | 10.4927 | 11.6512 | 12.8884
WB-Wide Bay | M008_Kilkivan-Murgon No 1 66 kV | Loading (MVA) | 1.0264 | 1.1452 | 1.2688 | 1.4086 | 1.5211
WB-Wide Bay | M008_Kilkivan-Murgon No 1 66 kV | Loading (MW) | 0.086597 | 0.33636 | 0.71731 | 0.94519 | 1.1555
WB-Wide Bay | M008_Kilkivan-Murgon No 1 66 kV | Power Factor | 0.083011 | 0.29221 | 0.56526 | 0.67089 | 0.7595
WB-Wide Bay | M008_Kilkivan-Murgon No 1 66 kV | Rating (A) | 181 | 181 | 181 | 181 | 181
WB-Wide Bay | M008_Kilkivan-Murgon No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M008_Kilkivan-Murgon No 1 66 kV | Min Voltage at Constrained Conductor | 67.5116 | 69.831 | 69.8121 | 69.8017 | 68.1407
WB-Wide Bay | M008_Kilkivan-Murgon No 1 66 kV | Contingency Outage | M036_Bundaberg-South Bundaberg 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | 7315_Aramara 132 kV
WB-Wide Bay | M009_Kilkivan-Murgon No 2 66 kV | % of Rated A | 5.333% | 5.75% | 6.134% | 6.588% | 7.083%
WB-Wide Bay | M009_Kilkivan-Murgon No 2 66 kV | Limiting Line Name | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1
WB-Wide Bay | M009_Kilkivan-Murgon No 2 66 kV | Loading (A) | 9.0132 | 9.718 | 10.3667 | 11.1333 | 11.9711
WB-Wide Bay | M009_Kilkivan-Murgon No 2 66 kV | Loading (MVA) | 1.0538 | 1.1752 | 1.2535 | 1.346 | 1.447
WB-Wide Bay | M009_Kilkivan-Murgon No 2 66 kV | Loading (MW) | 0.097756 | 0.35406 | 0.56838 | 0.75684 | 0.9306
WB-Wide Bay | M009_Kilkivan-Murgon No 2 66 kV | Power Factor | 0.091303 | 0.29965 | 0.45153 | 0.56008 | 0.64062
WB-Wide Bay | M009_Kilkivan-Murgon No 2 66 kV | Rating (A) | 169 | 169 | 169 | 169 | 169
WB-Wide Bay | M009_Kilkivan-Murgon No 2 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M009_Kilkivan-Murgon No 2 66 kV | Min Voltage at Constrained Conductor | 67.502 | 69.8194 | 69.8121 | 69.8017 | 69.7846
WB-Wide Bay | M009_Kilkivan-Murgon No 2 66 kV | Contingency Outage | M036_Bundaberg-South Bundaberg 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV
WB-Wide Bay | M010_Maryborough - Owanyilla 66 kV | % of Rated A | 15.4% | 30.78% | 33.94% | 36.85% | 38.56%
WB-Wide Bay | M010_Maryborough - Owanyilla 66 kV | Limiting Line Name | TR_LINE 199623_1 | TR_LINE 199623_1 | TR_LINE 199623_1 | TR_LINE 199623_1 | TR_LINE 199623_1
WB-Wide Bay | M010_Maryborough - Owanyilla 66 kV | Loading (A) | 38.3459 | 76.64 | 84.5008 | 91.758 | 96.0257
WB-Wide Bay | M010_Maryborough - Owanyilla 66 kV | Loading (MVA) | 4.4935 | 9.0565 | 10.0215 | 10.8858 | 11.4112
WB-Wide Bay | M010_Maryborough - Owanyilla 66 kV | Loading (MW) | 4.3781 | 4.8785 | 6.0784 | 6.9813 | 7.3784
WB-Wide Bay | M010_Maryborough - Owanyilla 66 kV | Power Factor | 0.97427 | 0.53868 | 0.60654 | 0.64132 | 0.64657
WB-Wide Bay | M010_Maryborough - Owanyilla 66 kV | Rating (A) | 249 | 249 | 249 | 249 | 249
WB-Wide Bay | M010_Maryborough - Owanyilla 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M010_Maryborough - Owanyilla 66 kV | Min Voltage at Constrained Conductor | 67.6558 | 68.2253 | 68.4716 | 68.4947 | 68.6096
WB-Wide Bay | M010_Maryborough - Owanyilla 66 kV | Contingency Outage | T014_Maryborough-Pialba Tee Howard 66 kV | M019_Maryborough City-Walkers 66 kV | 7315_Aramara 132 kV | 7315_Aramara 132 kV | 7315_Aramara 132 kV
WB-Wide Bay | M011_Kilkivan-Maryborough 66 kV | % of Rated A | 10.39% | 80.28% | 89.84% | 98.53% | 108.3%
WB-Wide Bay | M011_Kilkivan-Maryborough 66 kV | Limiting Line Name | TR_LINE 33838_1 | TR_LINE 42252_1 | TR_LINE 42252_1 | TR_LINE 42252_1 | TR_LINE 42252_1
WB-Wide Bay | M011_Kilkivan-Maryborough 66 kV | Loading (A) | 13.7188 | 105.974 | 118.5918 | 130.0611 | 142.935
WB-Wide Bay | M011_Kilkivan-Maryborough 66 kV | Loading (MVA) | 1.6435 | 12.6377 | 14.13 | 15.4884 | 17.0165
WB-Wide Bay | M011_Kilkivan-Maryborough 66 kV | Loading (MW) | 1.6432 | 10.3178 | 11.6494 | 12.9019 | 14.3522
WB-Wide Bay | M011_Kilkivan-Maryborough 66 kV | Power Factor | 0.9998 | 0.8164 | 0.8244 | 0.83295 | 0.84337
WB-Wide Bay | M011_Kilkivan-Maryborough 66 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
WB-Wide Bay | M011_Kilkivan-Maryborough 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M011_Kilkivan-Maryborough 66 kV | Min Voltage at Constrained Conductor | 69.1672 | 68.8488 | 68.7885 | 68.752 | 68.7311
WB-Wide Bay | M011_Kilkivan-Maryborough 66 kV | Contingency Outage | T014_Maryborough-Pialba Tee Howard 66 kV | 7315_Aramara 132 kV | 7315_Aramara 132 kV | 7315_Aramara 132 kV | 7315_Aramara 132 kV
WB-Wide Bay | M012_Maryborough-Rocky St 66 kV | % of Rated A | 18.23% | 17.41% | 16.9% | 15.78% | 15.03%
WB-Wide Bay | M012_Maryborough-Rocky St 66 kV | Limiting Line Name | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1
WB-Wide Bay | M012_Maryborough-Rocky St 66 kV | Loading (A) | 99.9099 | 95.3955 | 92.6342 | 86.4615 | 82.3536
WB-Wide Bay | M012_Maryborough-Rocky St 66 kV | Loading (MVA) | 11.8257 | 11.2318 | 10.9256 | 10.1994 | 9.7282
WB-Wide Bay | M012_Maryborough-Rocky St 66 kV | Loading (MW) | 6.6156 | 5.7594 | 5.1902 | 3.4992 | 1.8388
WB-Wide Bay | M012_Maryborough-Rocky St 66 kV | Power Factor | 0.55872 | 0.5122 | 0.47457 | 0.34258 | 0.18819
WB-Wide Bay | M012_Maryborough-Rocky St 66 kV | Rating (A) | 548 | 548 | 548 | 548 | 548
WB-Wide Bay | M012_Maryborough-Rocky St 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M012_Maryborough-Rocky St 66 kV | Min Voltage at Constrained Conductor | 68.3375 | 67.9769 | 68.0944 | 68.1068 | 68.2004
WB-Wide Bay | M012_Maryborough-Rocky St 66 kV | Contingency Outage | M018_Maryborough-Maryborough City 66 kV | M018_Maryborough-Maryborough City 66 kV | M018_Maryborough-Maryborough City 66 kV | M018_Maryborough-Maryborough City 66 kV | M018_Maryborough-Maryborough City 66 kV
WB-Wide Bay | M014_Torquay-Pialba 66 kV | % of Rated A | 6.34% | 7.122% | 8.039% | 9.059% | 10.6%
WB-Wide Bay | M014_Torquay-Pialba 66 kV | Limiting Line Name | TR_LINE 7168_1 | TR_LINE 7168_1 | TR_LINE 7168_1 | TR_LINE 7168_1 | TR_LINE 7168_1
WB-Wide Bay | M014_Torquay-Pialba 66 kV | Loading (A) | 38.5476 | 43.3002 | 48.8787 | 55.0777 | 64.4393
WB-Wide Bay | M014_Torquay-Pialba 66 kV | Loading (MVA) | 4.6287 | 5.2258 | 5.8209 | 6.5668 | 7.7112
WB-Wide Bay | M014_Torquay-Pialba 66 kV | Loading (MW) | 2.8795 | 3.8946 | 4.8738 | 5.8525 | 6.8682
WB-Wide Bay | M014_Torquay-Pialba 66 kV | Power Factor | 0.62209 | 0.74525 | 0.83728 | 0.89121 | 0.89067
WB-Wide Bay | M014_Torquay-Pialba 66 kV | Rating (A) | 608 | 608 | 608 | 608 | 608
WB-Wide Bay | M014_Torquay-Pialba 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M014_Torquay-Pialba 66 kV | Min Voltage at Constrained Conductor | 69.3267 | 69.6795 | 68.7561 | 68.8364 | 69.0891
WB-Wide Bay | M014_Torquay-Pialba 66 kV | Contingency Outage | M041_West Bundaberg-Meadowvale 66 kV | 7329_Maryborough 132 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV
WB-Wide Bay | M015_Maryborough-Howard No 1 66 kV | % of Rated A | 1.889% | 1.894% | 1.899% | 1.901% | 1.905%
WB-Wide Bay | M015_Maryborough-Howard No 1 66 kV | Limiting Line Name | TR_LINE 112139_1 | TR_LINE 112139_1 | TR_LINE 112139_1 | TR_LINE 112139_1 | TR_LINE 112139_1
WB-Wide Bay | M015_Maryborough-Howard No 1 66 kV | Loading (A) | 2.4931 | 2.5007 | 2.507 | 2.5091 | 2.5151
WB-Wide Bay | M015_Maryborough-Howard No 1 66 kV | Loading (MVA) | 0.29544 | 0.29724 | 0.29875 | 0.29924 | 0.30067
WB-Wide Bay | M015_Maryborough-Howard No 1 66 kV | Loading (MW) | 5.3442e-05 | 5.3767e-05 | 5.4041e-05 | 5.413e-05 | 5.4388e-05
WB-Wide Bay | M015_Maryborough-Howard No 1 66 kV | Power Factor | 0.00017813 | 0.00017813 | 0.00017813 | 0.00017813 | 0.00017813
WB-Wide Bay | M015_Maryborough-Howard No 1 66 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
WB-Wide Bay | M015_Maryborough-Howard No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M015_Maryborough-Howard No 1 66 kV | Min Voltage at Constrained Conductor | 68.4178 | 68.6255 | 68.8 | 68.8567 | 69.0206
WB-Wide Bay | M015_Maryborough-Howard No 1 66 kV | Contingency Outage | M041_West Bundaberg-Meadowvale 66 kV | 7329_Maryborough 132 kV | 7329_Maryborough 132 kV | 7329_Maryborough 132 kV | 7329_Maryborough 132 kV
WB-Wide Bay | M017_Rocky St - Maryborough City 66 kV | % of Rated A | 14.52% | 15.7% | 16.96% | 16.54% | 16.14%
WB-Wide Bay | M017_Rocky St - Maryborough City 66 kV | Limiting Line Name | TR_LINE 7924_1 | TR_LINE 7924_1 | TR_LINE 7924_1 | TR_LINE 7924_1 | TR_LINE 7924_1
WB-Wide Bay | M017_Rocky St - Maryborough City 66 kV | Loading (A) | 79.5533 | 86.0316 | 92.968 | 90.6259 | 88.4688
WB-Wide Bay | M017_Rocky St - Maryborough City 66 kV | Loading (MVA) | 9.4447 | 10.1609 | 10.9998 | 10.7272 | 10.4887
WB-Wide Bay | M017_Rocky St - Maryborough City 66 kV | Loading (MW) | 8.2868 | 9.1334 | 10.0608 | 9.7563 | 9.4827
WB-Wide Bay | M017_Rocky St - Maryborough City 66 kV | Power Factor | 0.8774 | 0.89888 | 0.91464 | 0.90949 | 0.90409
WB-Wide Bay | M017_Rocky St - Maryborough City 66 kV | Rating (A) | 548 | 548 | 548 | 548 | 548
WB-Wide Bay | M017_Rocky St - Maryborough City 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M017_Rocky St - Maryborough City 66 kV | Min Voltage at Constrained Conductor | 68.5438 | 68.1887 | 68.3109 | 68.3399 | 68.4497
WB-Wide Bay | M017_Rocky St - Maryborough City 66 kV | Contingency Outage | M018_Maryborough-Maryborough City 66 kV | M018_Maryborough-Maryborough City 66 kV | M018_Maryborough-Maryborough City 66 kV | M018_Maryborough-Maryborough City 66 kV | M018_Maryborough-Maryborough City 66 kV
WB-Wide Bay | M018_Maryborough-Maryborough City 66 kV | % of Rated A | 18.85% | 17.9% | 17.32% | 16.54% | 16.14%
WB-Wide Bay | M018_Maryborough-Maryborough City 66 kV | Limiting Line Name | TR_LINE 122162_1 | TR_LINE 122162_1 | TR_LINE 122162_1 | TR_LINE 122105_1 | TR_LINE 122105_1
WB-Wide Bay | M018_Maryborough-Maryborough City 66 kV | Loading (A) | 103.3239 | 98.1181 | 94.8875 | 90.6154 | 88.4534
WB-Wide Bay | M018_Maryborough-Maryborough City 66 kV | Loading (MVA) | 12.2348 | 11.5571 | 11.196 | 10.701 | 10.4613
WB-Wide Bay | M018_Maryborough-Maryborough City 66 kV | Loading (MW) | 6.8111 | 5.7725 | 5.0478 | 9.7454 | 9.4723
WB-Wide Bay | M018_Maryborough-Maryborough City 66 kV | Power Factor | 0.55596 | 0.49887 | 0.45033 | 0.9107 | 0.90546
WB-Wide Bay | M018_Maryborough-Maryborough City 66 kV | Rating (A) | 548 | 548 | 548 | 548 | 548
WB-Wide Bay | M018_Maryborough-Maryborough City 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M018_Maryborough-Maryborough City 66 kV | Min Voltage at Constrained Conductor | 68.3655 | 68.0048 | 68.1228 | 68.1804 | 68.2824
WB-Wide Bay | M018_Maryborough-Maryborough City 66 kV | Contingency Outage | M012_Maryborough-Rocky St 66 kV | M012_Maryborough-Rocky St 66 kV | M012_Maryborough-Rocky St 66 kV | M017_Rocky St - Maryborough City 66 kV | M017_Rocky St - Maryborough City 66 kV
WB-Wide Bay | M020_Maryborough-Torquay 66 kV | % of Rated A | 15.44% | 21.9% | 27.94% | 33.89% | 40.11%
WB-Wide Bay | M020_Maryborough-Torquay 66 kV | Limiting Line Name | TR_LINE 112154_1 | TR_LINE 112154_1 | TR_LINE 112154_1 | TR_LINE 112154_1 | TR_LINE 112154_1
WB-Wide Bay | M020_Maryborough-Torquay 66 kV | Loading (A) | 93.8644 | 133.1448 | 169.872 | 206.0548 | 243.8495
WB-Wide Bay | M020_Maryborough-Torquay 66 kV | Loading (MVA) | 11.0792 | 15.6875 | 20.0756 | 24.3598 | 28.8945
WB-Wide Bay | M020_Maryborough-Torquay 66 kV | Loading (MW) | 10.5231 | 15.3888 | 19.9071 | 24.2743 | 28.816
WB-Wide Bay | M020_Maryborough-Torquay 66 kV | Power Factor | 0.9498 | 0.98096 | 0.9916 | 0.99649 | 0.99728
WB-Wide Bay | M020_Maryborough-Torquay 66 kV | Rating (A) | 608 | 608 | 608 | 608 | 608
WB-Wide Bay | M020_Maryborough-Torquay 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M020_Maryborough-Torquay 66 kV | Min Voltage at Constrained Conductor | 68.1467 | 68.0246 | 68.231 | 68.2534 | 68.411
WB-Wide Bay | M020_Maryborough-Torquay 66 kV | Contingency Outage | M019_Maryborough City-Walkers 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV
WB-Wide Bay | M022_Howard - ISIS 66 kV | % of Rated A | 7.819% | 7.313% | 6.729% | 8.993% | 11.29%
WB-Wide Bay | M022_Howard - ISIS 66 kV | Limiting Line Name | TR_LINE 118970_1 | TR_LINE 118970_1 | TR_LINE 118970_1 | TR_LINE 118970_1 | TR_LINE 118970_1
WB-Wide Bay | M022_Howard - ISIS 66 kV | Loading (A) | 42.8501 | 40.0754 | 36.8776 | 49.2796 | 61.8573
WB-Wide Bay | M022_Howard - ISIS 66 kV | Loading (MVA) | 5.0306 | 4.7048 | 4.3378 | 5.8006 | 7.289
WB-Wide Bay | M022_Howard - ISIS 66 kV | Loading (MW) | 5.0237 | 4.699 | 4.333 | 5.7907 | 7.2705
WB-Wide Bay | M022_Howard - ISIS 66 kV | Power Factor | 0.99863 | 0.99876 | 0.99891 | 0.99829 | 0.99747
WB-Wide Bay | M022_Howard - ISIS 66 kV | Rating (A) | 548 | 548 | 548 | 548 | 548
WB-Wide Bay | M022_Howard - ISIS 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M022_Howard - ISIS 66 kV | Min Voltage at Constrained Conductor | 67.6312 | 67.6383 | 67.7781 | 67.7908 | 67.8331
WB-Wide Bay | M022_Howard - ISIS 66 kV | Contingency Outage | 7316_Aramara 132 kV | M047_Mount Rawdon Tee 66 kV | 7187_Gin Gin - Bundaberg 132 kV | 7187_Gin Gin - Bundaberg 132 kV | 7187_Gin Gin - Bundaberg 132 kV
WB-Wide Bay | M023_6242 (Pialba-Point Vernon) 66 kV | % of Rated A | 11.87% | 14.5% | 16.91% | 19.22% | 21.55%
WB-Wide Bay | M023_6242 (Pialba-Point Vernon) 66 kV | Limiting Line Name | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1
WB-Wide Bay | M023_6242 (Pialba-Point Vernon) 66 kV | Loading (A) | 71.8016 | 87.7047 | 102.2918 | 116.3008 | 130.3684
WB-Wide Bay | M023_6242 (Pialba-Point Vernon) 66 kV | Loading (MVA) | 8.5406 | 10.4258 | 12.2089 | 13.8981 | 15.6425
WB-Wide Bay | M023_6242 (Pialba-Point Vernon) 66 kV | Loading (MW) | 6.9486 | 9.2074 | 11.2015 | 13.0487 | 14.9104
WB-Wide Bay | M023_6242 (Pialba-Point Vernon) 66 kV | Power Factor | 0.81358 | 0.88312 | 0.91748 | 0.93888 | 0.95319
WB-Wide Bay | M023_6242 (Pialba-Point Vernon) 66 kV | Rating (A) | 605 | 605 | 605 | 605 | 605
WB-Wide Bay | M023_6242 (Pialba-Point Vernon) 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M023_6242 (Pialba-Point Vernon) 66 kV | Min Voltage at Constrained Conductor | 68.674 | 68.6319 | 68.9081 | 68.9928 | 69.2725
WB-Wide Bay | M023_6242 (Pialba-Point Vernon) 66 kV | Contingency Outage | M019_Maryborough City-Walkers 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV
WB-Wide Bay | M024_Gayndah - Mundubbera 66 kV | % of Rated A | 20.84% | 20.93% | 21.06% | 21.13% | 21.15%
WB-Wide Bay | M024_Gayndah - Mundubbera 66 kV | Limiting Line Name | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1
WB-Wide Bay | M024_Gayndah - Mundubbera 66 kV | Loading (A) | 27.5127 | 27.6226 | 27.7976 | 27.8865 | 27.9162
WB-Wide Bay | M024_Gayndah - Mundubbera 66 kV | Loading (MVA) | 3.202 | 3.1561 | 3.2489 | 3.2604 | 3.2593
WB-Wide Bay | M024_Gayndah - Mundubbera 66 kV | Loading (MW) | 0.2533 | 0.35542 | 0.43463 | 0.4996 | 0.54929
WB-Wide Bay | M024_Gayndah - Mundubbera 66 kV | Power Factor | 0.071488 | 0.1048 | 0.1261 | 0.14553 | 0.16081
WB-Wide Bay | M024_Gayndah - Mundubbera 66 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
WB-Wide Bay | M024_Gayndah - Mundubbera 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M024_Gayndah - Mundubbera 66 kV | Min Voltage at Constrained Conductor | 67.194 | 65.9662 | 67.4789 | 67.5028 | 67.4065
WB-Wide Bay | M024_Gayndah - Mundubbera 66 kV | Contingency Outage | 785_ISIS 132 kV | 784_ISIS 132 kV | 7215_Bundaberg - ISIS No 1 132 kV | 7328_Bundaberg - ISIS No 2 132 kV | M047_Mount Rawdon Tee 66 kV
WB-Wide Bay | M025_Eidsvold 66 kV | % of Rated A | 2.609% | 2.815% | 3.014% | 3.196% | 3.365%
WB-Wide Bay | M025_Eidsvold 66 kV | Limiting Line Name | TR_LINE 77926_1 | TR_LINE 77926_1 | TR_LINE 77926_1 | TR_LINE 77926_1 | TR_LINE 77926_1
WB-Wide Bay | M025_Eidsvold 66 kV | Loading (A) | 2.7918 | 3.0116 | 3.2247 | 3.42 | 3.6001
WB-Wide Bay | M025_Eidsvold 66 kV | Loading (MVA) | 0.32817 | 0.35507 | 0.38088 | 0.40417 | 0.42492
WB-Wide Bay | M025_Eidsvold 66 kV | Loading (MW) | 0.12178 | 0.18001 | 0.22596 | 0.26359 | 0.29574
WB-Wide Bay | M025_Eidsvold 66 kV | Power Factor | 0.37106 | 0.50695 | 0.59326 | 0.65216 | 0.69597
WB-Wide Bay | M025_Eidsvold 66 kV | Rating (A) | 107 | 107 | 107 | 107 | 107
WB-Wide Bay | M025_Eidsvold 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M025_Eidsvold 66 kV | Min Voltage at Constrained Conductor | 67.8659 | 68.0703 | 68.1927 | 68.2308 | 68.1446
WB-Wide Bay | M025_Eidsvold 66 kV | Contingency Outage | 785_ISIS 132 kV | M049_ISIS - Gayndah 66 kV | 7215_Bundaberg - ISIS No 1 132 kV | 7328_Bundaberg - ISIS No 2 132 kV | M047_Mount Rawdon Tee 66 kV
WB-Wide Bay | M026_ISIS - Bundaberg 66 kV | % of Rated A | 11.3% | 13.75% | 15.86% | 17.85% | 19.83%
WB-Wide Bay | M026_ISIS - Bundaberg 66 kV | Limiting Line Name | TR_CABLE 3770_1 | TR_CABLE 3770_1 | TR_CABLE 3770_1 | TR_CABLE 3770_1 | TR_CABLE 3770_1
WB-Wide Bay | M026_ISIS - Bundaberg 66 kV | Loading (A) | 11.2983 | 13.747 | 15.8606 | 17.8474 | 19.8341
WB-Wide Bay | M026_ISIS - Bundaberg 66 kV | Loading (MVA) | 1.3259 | 1.6143 | 1.8673 | 2.1018 | 2.3375
WB-Wide Bay | M026_ISIS - Bundaberg 66 kV | Loading (MW) | 1.3256 | 1.6138 | 1.8666 | 2.1008 | 2.3361
WB-Wide Bay | M026_ISIS - Bundaberg 66 kV | Power Factor | 0.99979 | 0.99969 | 0.9996 | 0.99949 | 0.99937
WB-Wide Bay | M026_ISIS - Bundaberg 66 kV | Rating (A) | 100 | 100 | 100 | 100 | 100
WB-Wide Bay | M026_ISIS - Bundaberg 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M026_ISIS - Bundaberg 66 kV | Min Voltage at Constrained Conductor | 67.7522 | 67.799 | 67.9742 | 67.9929 | 68.0432
WB-Wide Bay | M026_ISIS - Bundaberg 66 kV | Contingency Outage | 7316_Aramara 132 kV | M047_Mount Rawdon Tee 66 kV | 7187_Gin Gin - Bundaberg 132 kV | 7187_Gin Gin - Bundaberg 132 kV | 7187_Gin Gin - Bundaberg 132 kV
WB-Wide Bay | M026b_FORMER_ISIS - Bundaberg 66kV | % of Rated A | 0.2434% | 0.2436% | 0.2411% | 0.2411% | 0.2411%
WB-Wide Bay | M026b_FORMER_ISIS - Bundaberg 66kV | Limiting Line Name | TR_LINE 12084300_1 | TR_LINE 12084300_1 | TR_LINE 12084300_1 | TR_LINE 12084300_1 | TR_LINE 12084300_1
WB-Wide Bay | M026b_FORMER_ISIS - Bundaberg 66kV | Loading (A) | 1.0686 | 1.0696 | 1.0583 | 1.0584 | 1.0586
WB-Wide Bay | M026b_FORMER_ISIS - Bundaberg 66kV | Loading (MVA) | 0.12326 | 0.12349 | 0.1209 | 0.12092 | 0.12097
WB-Wide Bay | M026b_FORMER_ISIS - Bundaberg 66kV | Loading (MW) | 1.934e-06 | 1.9376e-06 | 1.897e-06 | 1.8973e-06 | 1.898e-06
WB-Wide Bay | M026b_FORMER_ISIS - Bundaberg 66kV | Power Factor | 1.569e-05 | 1.569e-05 | 1.569e-05 | 1.569e-05 | 1.569e-05
WB-Wide Bay | M026b_FORMER_ISIS - Bundaberg 66kV | Rating (A) | 439 | 439 | 439 | 439 | 439
WB-Wide Bay | M026b_FORMER_ISIS - Bundaberg 66kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M026b_FORMER_ISIS - Bundaberg 66kV | Min Voltage at Constrained Conductor | 66.5966 | 66.6583 | 65.9558 | 65.9627 | 65.9748
WB-Wide Bay | M026b_FORMER_ISIS - Bundaberg 66kV | Contingency Outage | 7315_Aramara 132 kV | 784_ISIS 132 kV | M041_West Bundaberg-Meadowvale 66 kV | M041_West Bundaberg-Meadowvale 66 kV | M041_West Bundaberg-Meadowvale 66 kV
WB-Wide Bay | M027_ISIS - Childers 66 kV | % of Rated A | 24.18% | 10.94% | 11.86% | 12.94% | 14.15%
WB-Wide Bay | M027_ISIS - Childers 66 kV | Limiting Line Name | TR_LINE 183684_1 | TR_LINE 183684_1 | TR_LINE 183684_1 | TR_LINE 183684_1 | TR_LINE 183684_1
WB-Wide Bay | M027_ISIS - Childers 66 kV | Loading (A) | 62.3838 | 28.229 | 30.5946 | 33.3799 | 36.5025
WB-Wide Bay | M027_ISIS - Childers 66 kV | Loading (MVA) | 7.3779 | 3.3434 | 3.6099 | 3.9393 | 4.309
WB-Wide Bay | M027_ISIS - Childers 66 kV | Loading (MW) | 0.011699 | 1.3619 | 1.9756 | 2.54 | 3.0944
WB-Wide Bay | M027_ISIS - Childers 66 kV | Power Factor | 0.00041427 | 0.40645 | 0.54629 | 0.64371 | 0.71694
WB-Wide Bay | M027_ISIS - Childers 66 kV | Rating (A) | 258 | 258 | 258 | 258 | 258
WB-Wide Bay | M027_ISIS - Childers 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M027_ISIS - Childers 66 kV | Min Voltage at Constrained Conductor | 68.2813 | 68.3798 | 68.1224 | 68.1351 | 68.1545
WB-Wide Bay | M027_ISIS - Childers 66 kV | Contingency Outage | M049_ISIS - Gayndah 66 kV | 6315_ISCM - ISCI 66 kV | 6315_ISCM - ISCI 66 kV | 6315_ISCM - ISCI 66 kV | 6315_ISCM - ISCI 66 kV
WB-Wide Bay | M028_Childers - Gayndah 66 kV | % of Rated A | 28.11% | 1.122e-08% | 1.175e-08% | 1.237e-08% | 1.307e-08%
WB-Wide Bay | M028_Childers - Gayndah 66 kV | Limiting Line Name | TR_LINE 33780_2 | 3-Phase Link 66kV_M028 GAYNDAH_Term(1) | 3-Phase Link 66kV_M028 GAYNDAH_Term(1) | 3-Phase Link 66kV_M028 GAYNDAH_Term(1) | 3-Phase Link 66kV_M028 GAYNDAH_Term(1)
WB-Wide Bay | M028_Childers - Gayndah 66 kV | Loading (A) | 37.0995 | 5.6103e-07 | 5.8732e-07 | 6.1832e-07 | 6.5351e-07
WB-Wide Bay | M028_Childers - Gayndah 66 kV | Loading (MVA) | 4.5144 | 6.6545e-08 | 6.956e-08 | 7.3265e-08 | 7.7492e-08
WB-Wide Bay | M028_Childers - Gayndah 66 kV | Loading (MW) | 0.43581 | 2.2673e-08 | 3.096e-08 | 3.8647e-08 | 4.6212e-08
WB-Wide Bay | M028_Childers - Gayndah 66 kV | Power Factor | 0.096526 | 0.34072 | 0.44508 | 0.52749 | 0.59634
WB-Wide Bay | M028_Childers - Gayndah 66 kV | Rating (A) | 132 | 5000 | 5000 | 5000 | 5000
WB-Wide Bay | M028_Childers - Gayndah 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M028_Childers - Gayndah 66 kV | Min Voltage at Constrained Conductor | 70.2535 | 68.4818 | 68.379 | 68.4108 | 68.4612
WB-Wide Bay | M028_Childers - Gayndah 66 kV | Contingency Outage | M027_ISIS - Childers 66 kV | 6315_ISCM - ISCI 66 kV | 7315_Aramara 132 kV | 7315_Aramara 132 kV | 7315_Aramara 132 kV
WB-Wide Bay | M029_Bundaberg - Farnsfield 66 kV | % of Rated A | 0.7674% | 0.7708% | 0.7658% | 0.7687% | 0.7716%
WB-Wide Bay | M029_Bundaberg - Farnsfield 66 kV | Limiting Line Name | TR_LINE 205843_1 | TR_LINE 205843_1 | TR_LINE 205843_1 | TR_LINE 205843_1 | TR_LINE 205843_1
WB-Wide Bay | M029_Bundaberg - Farnsfield 66 kV | Loading (A) | 3.9291 | 3.9464 | 3.9207 | 3.9358 | 3.9504
WB-Wide Bay | M029_Bundaberg - Farnsfield 66 kV | Loading (MVA) | 0.45321 | 0.45563 | 0.44789 | 0.44966 | 0.45142
WB-Wide Bay | M029_Bundaberg - Farnsfield 66 kV | Loading (MW) | 0.035063 | 0.051772 | 0.064822 | 0.075651 | 0.08468
WB-Wide Bay | M029_Bundaberg - Farnsfield 66 kV | Power Factor | 0.077195 | 0.11346 | 0.14455 | 0.16806 | 0.18741
WB-Wide Bay | M029_Bundaberg - Farnsfield 66 kV | Rating (A) | 512 | 512 | 512 | 512 | 512
WB-Wide Bay | M029_Bundaberg - Farnsfield 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M029_Bundaberg - Farnsfield 66 kV | Min Voltage at Constrained Conductor | 66.5966 | 66.6583 | 65.9558 | 65.9627 | 65.9748
WB-Wide Bay | M029_Bundaberg - Farnsfield 66 kV | Contingency Outage | 7315_Aramara 132 kV | 784_ISIS 132 kV | M041_West Bundaberg-Meadowvale 66 kV | M041_West Bundaberg-Meadowvale 66 kV | M041_West Bundaberg-Meadowvale 66 kV
WB-Wide Bay | M030_Farnsfield - Childers 66 kV | % of Rated A | 17.76% | 17.47% | 17.35% | 17.31% | 17.32%
WB-Wide Bay | M030_Farnsfield - Childers 66 kV | Limiting Line Name | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1
WB-Wide Bay | M030_Farnsfield - Childers 66 kV | Loading (A) | 23.4439 | 23.0589 | 22.9018 | 22.852 | 22.8617
WB-Wide Bay | M030_Farnsfield - Childers 66 kV | Loading (MVA) | 2.9483 | 2.741 | 2.7183 | 2.7138 | 2.7171
WB-Wide Bay | M030_Farnsfield - Childers 66 kV | Loading (MW) | 0.53523 | 0.37559 | 0.23283 | 0.099596 | 0.034131
WB-Wide Bay | M030_Farnsfield - Childers 66 kV | Power Factor | 0.18154 | 0.13703 | 0.08565 | 0.03636 | 0.011747
WB-Wide Bay | M030_Farnsfield - Childers 66 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
WB-Wide Bay | M030_Farnsfield - Childers 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M030_Farnsfield - Childers 66 kV | Min Voltage at Constrained Conductor | 72.6078 | 68.6285 | 68.5288 | 68.5638 | 68.6173
WB-Wide Bay | M030_Farnsfield - Childers 66 kV | Contingency Outage | M027_ISIS - Childers 66 kV | 6315_ISCM - ISCI 66 kV | 7315_Aramara 132 kV | 7315_Aramara 132 kV | 7315_Aramara 132 kV
WB-Wide Bay | M032_Bundaberg-South Kolan No 1 66 kV | % of Rated A | 22.5% | 23.71% | 25.1% | 26.46% | 27.63%
WB-Wide Bay | M032_Bundaberg-South Kolan No 1 66 kV | Limiting Line Name | TR_LINE 138990_1 | TR_LINE 138990_1 | TR_LINE 138990_1 | TR_LINE 138990_1 | TR_LINE 138990_1
WB-Wide Bay | M032_Bundaberg-South Kolan No 1 66 kV | Loading (A) | 29.7004 | 31.2926 | 33.1295 | 34.9257 | 36.468
WB-Wide Bay | M032_Bundaberg-South Kolan No 1 66 kV | Loading (MVA) | 3.401 | 3.5785 | 3.8015 | 3.9946 | 4.1873
WB-Wide Bay | M032_Bundaberg-South Kolan No 1 66 kV | Loading (MW) | 0.98531 | 1.5037 | 1.9435 | 2.3348 | 2.707
WB-Wide Bay | M032_Bundaberg-South Kolan No 1 66 kV | Power Factor | 0.28971 | 0.42021 | 0.51125 | 0.58449 | 0.64649
WB-Wide Bay | M032_Bundaberg-South Kolan No 1 66 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
WB-Wide Bay | M032_Bundaberg-South Kolan No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M032_Bundaberg-South Kolan No 1 66 kV | Min Voltage at Constrained Conductor | 66.112 | 66.0243 | 66.2494 | 66.0346 | 66.2918
WB-Wide Bay | M032_Bundaberg-South Kolan No 1 66 kV | Contingency Outage | 786_Gin Gin - Bundaberg 132 kV | 7315_Aramara 132 kV | M035_Bundaberg-South Kolan No 2 66 kV | M030_Farnsfield - Childers 66 kV | M035_Bundaberg-South Kolan No 2 66 kV
WB-Wide Bay | M033_Wallaville 66 kV | % of Rated A | 10.57% | 10.8% | 11.17% | 11.52% | 11.79%
WB-Wide Bay | M033_Wallaville 66 kV | Limiting Line Name | TR_LINE 214482_2 | TR_LINE 214482_2 | TR_LINE 214482_2 | TR_LINE 214482_2 | TR_LINE 214482_2
WB-Wide Bay | M033_Wallaville 66 kV | Loading (A) | 27.2685 | 27.8736 | 28.8102 | 29.7268 | 30.4111
WB-Wide Bay | M033_Wallaville 66 kV | Loading (MVA) | 3.1384 | 3.2059 | 3.3267 | 3.4232 | 3.5169
WB-Wide Bay | M033_Wallaville 66 kV | Loading (MW) | 0.3463 | 0.75594 | 1.1039 | 1.4142 | 1.7098
WB-Wide Bay | M033_Wallaville 66 kV | Power Factor | 0.11029 | 0.23574 | 0.33177 | 0.41306 | 0.4861
WB-Wide Bay | M033_Wallaville 66 kV | Rating (A) | 258 | 258 | 258 | 258 | 258
WB-Wide Bay | M033_Wallaville 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M033_Wallaville 66 kV | Min Voltage at Constrained Conductor | 66.4491 | 66.4048 | 66.6671 | 66.4845 | 66.7675
WB-Wide Bay | M033_Wallaville 66 kV | Contingency Outage | 786_Gin Gin - Bundaberg 132 kV | 7315_Aramara 132 kV | M035_Bundaberg-South Kolan No 2 66 kV | M030_Farnsfield - Childers 66 kV | M035_Bundaberg-South Kolan No 2 66 kV
WB-Wide Bay | M034_Monduran Dam 66 kV | % of Rated A | 1.647% | 1.649% | 1.635% | 1.644% | 1.657%
WB-Wide Bay | M034_Monduran Dam 66 kV | Limiting Line Name | TR_LINE 209283_1 | TR_LINE 209283_1 | TR_LINE 209283_1 | TR_LINE 209283_1 | TR_LINE 209283_1
WB-Wide Bay | M034_Monduran Dam 66 kV | Loading (A) | 2.1738 | 2.1764 | 2.1587 | 2.1701 | 2.1875
WB-Wide Bay | M034_Monduran Dam 66 kV | Loading (MVA) | 0.25356 | 0.25474 | 0.25023 | 0.25178 | 0.25408
WB-Wide Bay | M034_Monduran Dam 66 kV | Loading (MW) | 0.017436 | 0.00071286 | 0.013914 | 0.02753 | 0.040554
WB-Wide Bay | M034_Monduran Dam 66 kV | Power Factor | 0.068767 | 0.0027984 | 0.055476 | 0.10921 | 0.15947
WB-Wide Bay | M034_Monduran Dam 66 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
WB-Wide Bay | M034_Monduran Dam 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M034_Monduran Dam 66 kV | Min Voltage at Constrained Conductor | 67.342 | 67.5773 | 66.9255 | 66.9838 | 67.0604
WB-Wide Bay | M034_Monduran Dam 66 kV | Contingency Outage | 7315_Aramara 132 kV | M035_Bundaberg-South Kolan No 2 66 kV | M035_Bundaberg-South Kolan No 2 66 kV | M035_Bundaberg-South Kolan No 2 66 kV | M035_Bundaberg-South Kolan No 2 66 kV
WB-Wide Bay | M035_Bundaberg-South Kolan No 2 66 kV | % of Rated A | 3.361% | 3.766% | 4.145% | 4.501% | 4.825%
WB-Wide Bay | M035_Bundaberg-South Kolan No 2 66 kV | Limiting Line Name | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1
WB-Wide Bay | M035_Bundaberg-South Kolan No 2 66 kV | Loading (A) | 18.4193 | 20.6386 | 22.7136 | 24.6628 | 26.4401
WB-Wide Bay | M035_Bundaberg-South Kolan No 2 66 kV | Loading (MVA) | 2.1055 | 2.3515 | 2.5903 | 2.8131 | 3.0162
WB-Wide Bay | M035_Bundaberg-South Kolan No 2 66 kV | Loading (MW) | 1.317 | 1.7015 | 2.0249 | 2.3102 | 2.58
WB-Wide Bay | M035_Bundaberg-South Kolan No 2 66 kV | Power Factor | 0.62492 | 0.72295 | 0.78101 | 0.82043 | 0.85454
WB-Wide Bay | M035_Bundaberg-South Kolan No 2 66 kV | Rating (A) | 548 | 548 | 548 | 548 | 548
WB-Wide Bay | M035_Bundaberg-South Kolan No 2 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M035_Bundaberg-South Kolan No 2 66 kV | Min Voltage at Constrained Conductor | 65.9963 | 65.7815 | 65.8425 | 65.8545 | 65.8614
WB-Wide Bay | M035_Bundaberg-South Kolan No 2 66 kV | Contingency Outage | 786_Gin Gin - Bundaberg 132 kV | 785_ISIS 132 kV | 7215_Bundaberg - ISIS No 1 132 kV | 7215_Bundaberg - ISIS No 1 132 kV | 7215_Bundaberg - ISIS No 1 132 kV
WB-Wide Bay | M036_Bundaberg-South Bundaberg 66 kV | % of Rated A | 43.29% | 46.63% | 50.14% | 54.15% | 58.44%
WB-Wide Bay | M036_Bundaberg-South Bundaberg 66 kV | Limiting Line Name | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1
WB-Wide Bay | M036_Bundaberg-South Bundaberg 66 kV | Loading (A) | 190.037 | 204.6881 | 220.0946 | 237.7031 | 256.5602
WB-Wide Bay | M036_Bundaberg-South Bundaberg 66 kV | Loading (MVA) | 22.3236 | 24.1882 | 25.8034 | 27.9483 | 30.2476
WB-Wide Bay | M036_Bundaberg-South Bundaberg 66 kV | Loading (MW) | 7.8543 | 12.0594 | 15.7246 | 19.0993 | 22.405
WB-Wide Bay | M036_Bundaberg-South Bundaberg 66 kV | Power Factor | 0.34436 | 0.49481 | 0.60906 | 0.68338 | 0.74072
WB-Wide Bay | M036_Bundaberg-South Bundaberg 66 kV | Rating (A) | 439 | 439 | 439 | 439 | 439
WB-Wide Bay | M036_Bundaberg-South Bundaberg 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M036_Bundaberg-South Bundaberg 66 kV | Min Voltage at Constrained Conductor | 66.4504 | 66.6103 | 65.8592 | 65.8649 | 65.8738
WB-Wide Bay | M036_Bundaberg-South Bundaberg 66 kV | Contingency Outage | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV
WB-Wide Bay | M037_South - East Bundaberg 66 kV | % of Rated A | 57.34% | 57.21% | 57.62% | 64.93% | 72.34%
WB-Wide Bay | M037_South - East Bundaberg 66 kV | Limiting Line Name | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1
WB-Wide Bay | M037_South - East Bundaberg 66 kV | Loading (A) | 129.5819 | 129.2882 | 130.2107 | 146.7422 | 163.4863
WB-Wide Bay | M037_South - East Bundaberg 66 kV | Loading (MVA) | 15.3947 | 15.4431 | 15.2951 | 17.2738 | 19.2854
WB-Wide Bay | M037_South - East Bundaberg 66 kV | Loading (MW) | 1.6319 | 0.045651 | 14.3438 | 16.4793 | 18.6188
WB-Wide Bay | M037_South - East Bundaberg 66 kV | Power Factor | 0.1025 | 0.00052351 | 0.9378 | 0.954 | 0.96544
WB-Wide Bay | M037_South - East Bundaberg 66 kV | Rating (A) | 226 | 226 | 226 | 226 | 226
WB-Wide Bay | M037_South - East Bundaberg 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M037_South - East Bundaberg 66 kV | Min Voltage at Constrained Conductor | 68.4903 | 68.8398 | 67.5434 | 67.6402 | 67.7407
WB-Wide Bay | M037_South - East Bundaberg 66 kV | Contingency Outage | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV
WB-Wide Bay | M039_Bundaberg-West Bundaberg No 1 66 kV | % of Rated A | 20.11% | 21.5% | 23.15% | 25.33% | 27.91%
WB-Wide Bay | M039_Bundaberg-West Bundaberg No 1 66 kV | Limiting Line Name | TR_LINE 200241_1 | TR_LINE 200241_1 | TR_LINE 200241_1 | TR_LINE 200241_1 | TR_LINE 200241_1
WB-Wide Bay | M039_Bundaberg-West Bundaberg No 1 66 kV | Loading (A) | 162.1126 | 173.3044 | 186.6084 | 204.1742 | 224.9269
WB-Wide Bay | M039_Bundaberg-West Bundaberg No 1 66 kV | Loading (MVA) | 18.6509 | 19.9855 | 21.2791 | 23.2836 | 25.6545
WB-Wide Bay | M039_Bundaberg-West Bundaberg No 1 66 kV | Loading (MW) | 3.4014 | 7.4634 | 11.118 | 14.5585 | 18.07
WB-Wide Bay | M039_Bundaberg-West Bundaberg No 1 66 kV | Power Factor | 0.18235 | 0.37344 | 0.52248 | 0.62527 | 0.70436
WB-Wide Bay | M039_Bundaberg-West Bundaberg No 1 66 kV | Rating (A) | 806 | 806 | 806 | 806 | 806
WB-Wide Bay | M039_Bundaberg-West Bundaberg No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M039_Bundaberg-West Bundaberg No 1 66 kV | Min Voltage at Constrained Conductor | 66.4171 | 66.572 | 65.8264 | 65.8292 | 65.8391
WB-Wide Bay | M039_Bundaberg-West Bundaberg No 1 66 kV | Contingency Outage | M040_Bundaberg-West Bundaberg No 2 66 kV | M040_Bundaberg-West Bundaberg No 2 66 kV | M040_Bundaberg-West Bundaberg No 2 66 kV | M040_Bundaberg-West Bundaberg No 2 66 kV | M040_Bundaberg-West Bundaberg No 2 66 kV
WB-Wide Bay | M040_Bundaberg-West Bundaberg No 2 66 kV | % of Rated A | 19.98% | 21.36% | 23% | 25.16% | 27.72%
WB-Wide Bay | M040_Bundaberg-West Bundaberg No 2 66 kV | Limiting Line Name | TR_LINE 169764_1 | TR_LINE 169764_1 | TR_LINE 169764_1 | TR_LINE 169764_1 | TR_LINE 169764_1
WB-Wide Bay | M040_Bundaberg-West Bundaberg No 2 66 kV | Loading (A) | 161.0662 | 172.1727 | 185.37 | 202.7989 | 223.3908
WB-Wide Bay | M040_Bundaberg-West Bundaberg No 2 66 kV | Loading (MVA) | 18.5775 | 19.9156 | 21.2138 | 23.2209 | 25.5948
WB-Wide Bay | M040_Bundaberg-West Bundaberg No 2 66 kV | Loading (MW) | 3.3627 | 7.3988 | 11.0321 | 14.4535 | 17.9468
WB-Wide Bay | M040_Bundaberg-West Bundaberg No 2 66 kV | Power Factor | 0.18036 | 0.37147 | 0.52004 | 0.62243 | 0.70119
WB-Wide Bay | M040_Bundaberg-West Bundaberg No 2 66 kV | Rating (A) | 806 | 806 | 806 | 806 | 806
WB-Wide Bay | M040_Bundaberg-West Bundaberg No 2 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M040_Bundaberg-West Bundaberg No 2 66 kV | Min Voltage at Constrained Conductor | 66.418 | 66.573 | 65.8271 | 65.8298 | 65.8397
WB-Wide Bay | M040_Bundaberg-West Bundaberg No 2 66 kV | Contingency Outage | M039_Bundaberg-West Bundaberg No 1 66 kV | M039_Bundaberg-West Bundaberg No 1 66 kV | M039_Bundaberg-West Bundaberg No 1 66 kV | M039_Bundaberg-West Bundaberg No 1 66 kV | M039_Bundaberg-West Bundaberg No 1 66 kV
WB-Wide Bay | M041_West Bundaberg-Meadowvale 66 kV | % of Rated A | 15.06% | 17.92% | 20.7% | 23.42% | 26.27%
WB-Wide Bay | M041_West Bundaberg-Meadowvale 66 kV | Limiting Line Name | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1
WB-Wide Bay | M041_West Bundaberg-Meadowvale 66 kV | Loading (A) | 34.0369 | 40.493 | 46.7732 | 52.9374 | 59.3683
WB-Wide Bay | M041_West Bundaberg-Meadowvale 66 kV | Loading (MVA) | 3.9075 | 4.6387 | 5.3545 | 6.0656 | 6.8088
WB-Wide Bay | M041_West Bundaberg-Meadowvale 66 kV | Loading (MW) | 2.9762 | 3.8721 | 4.6874 | 5.4634 | 6.2551
WB-Wide Bay | M041_West Bundaberg-Meadowvale 66 kV | Power Factor | 0.76166 | 0.83475 | 0.8754 | 0.90072 | 0.91867
WB-Wide Bay | M041_West Bundaberg-Meadowvale 66 kV | Rating (A) | 226 | 226 | 226 | 226 | 226
WB-Wide Bay | M041_West Bundaberg-Meadowvale 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M041_West Bundaberg-Meadowvale 66 kV | Min Voltage at Constrained Conductor | 66.2811 | 66.1384 | 66.0861 | 66.1375 | 66.1923
WB-Wide Bay | M041_West Bundaberg-Meadowvale 66 kV | Contingency Outage | 7187_Gin Gin - Bundaberg 132 kV | 785_ISIS 132 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV
WB-Wide Bay | M042_Meadowvale-Gooburrum 66 kV | % of Rated A | 5.561% | 7.271% | 8.737% | 10.04% | 11.29%
WB-Wide Bay | M042_Meadowvale-Gooburrum 66 kV | Limiting Line Name | TR_LINE 7779_2 | TR_LINE 7779_2 | TR_LINE 7779_2 | TR_LINE 7779_2 | TR_LINE 7779_2
WB-Wide Bay | M042_Meadowvale-Gooburrum 66 kV | Loading (A) | 6.1731 | 8.0711 | 9.6984 | 11.1456 | 12.5291
WB-Wide Bay | M042_Meadowvale-Gooburrum 66 kV | Loading (MVA) | 0.7087 | 0.92461 | 1.1103 | 1.2771 | 1.437
WB-Wide Bay | M042_Meadowvale-Gooburrum 66 kV | Loading (MW) | 0.69668 | 0.91618 | 1.104 | 1.2722 | 1.4332
WB-Wide Bay | M042_Meadowvale-Gooburrum 66 kV | Power Factor | 0.98267 | 0.9904 | 0.9937 | 0.99547 | 0.99662
WB-Wide Bay | M042_Meadowvale-Gooburrum 66 kV | Rating (A) | 111 | 111 | 111 | 111 | 111
WB-Wide Bay | M042_Meadowvale-Gooburrum 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M042_Meadowvale-Gooburrum 66 kV | Min Voltage at Constrained Conductor | 66.2824 | 66.1402 | 66.0963 | 66.1553 | 66.2178
WB-Wide Bay | M042_Meadowvale-Gooburrum 66 kV | Contingency Outage | 7187_Gin Gin - Bundaberg 132 kV | 785_ISIS 132 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV
WB-Wide Bay | M046_Tarong-Caboonbah 66 kV | % of Rated A | 4.526% | 4.526% | 4.526% | 4.526% | 4.525%
WB-Wide Bay | M046_Tarong-Caboonbah 66 kV | Limiting Line Name | TR_LINE 9243_1 | TR_LINE 9243_1 | TR_LINE 9243_1 | TR_LINE 9243_1 | TR_LINE 9243_1
WB-Wide Bay | M046_Tarong-Caboonbah 66 kV | Loading (A) | 11.2703 | 11.2698 | 11.2689 | 11.2686 | 11.2683
WB-Wide Bay | M046_Tarong-Caboonbah 66 kV | Loading (MVA) | 1.3661 | 1.3661 | 1.3663 | 1.3664 | 1.3664
WB-Wide Bay | M046_Tarong-Caboonbah 66 kV | Loading (MW) | 1.151 | 1.151 | 1.151 | 1.151 | 1.151
WB-Wide Bay | M046_Tarong-Caboonbah 66 kV | Power Factor | 0.84256 | 0.84251 | 0.84241 | 0.84238 | 0.84234
WB-Wide Bay | M046_Tarong-Caboonbah 66 kV | Rating (A) | 249 | 249 | 249 | 249 | 249
WB-Wide Bay | M046_Tarong-Caboonbah 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M046_Tarong-Caboonbah 66 kV | Min Voltage at Constrained Conductor | 69.98 | 69.987 | 70.0011 | 70.0059 | 70.0106
WB-Wide Bay | M046_Tarong-Caboonbah 66 kV | Contingency Outage | M005 KINGAROY-BOONDOOMA | M005 KINGAROY-BOONDOOMA | M005 KINGAROY-BOONDOOMA | M005 KINGAROY-BOONDOOMA | M005 KINGAROY-BOONDOOMA
WB-Wide Bay | M049_ISIS - Gayndah 66 kV | % of Rated A | 28.61% | 15.18% | 15.33% | 15.19% | 15.04%
WB-Wide Bay | M049_ISIS - Gayndah 66 kV | Limiting Line Name | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2
WB-Wide Bay | M049_ISIS - Gayndah 66 kV | Loading (A) | 114.1364 | 60.585 | 61.1583 | 60.6083 | 60.0178
WB-Wide Bay | M049_ISIS - Gayndah 66 kV | Loading (MVA) | 13.451 | 7.0895 | 7.1988 | 7.1343 | 7.0659
WB-Wide Bay | M049_ISIS - Gayndah 66 kV | Loading (MW) | 10.8295 | 6.5016 | 6.6616 | 6.591 | 6.5341
WB-Wide Bay | M049_ISIS - Gayndah 66 kV | Power Factor | 0.79386 | 0.91707 | 0.92537 | 0.92384 | 0.92474
WB-Wide Bay | M049_ISIS - Gayndah 66 kV | Rating (A) | 399 | 399 | 399 | 399 | 399
WB-Wide Bay | M049_ISIS - Gayndah 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M049_ISIS - Gayndah 66 kV | Min Voltage at Constrained Conductor | 68.0406 | 67.2733 | 67.6297 | 67.6419 | 67.6499
WB-Wide Bay | M049_ISIS - Gayndah 66 kV | Contingency Outage | M027_ISIS - Childers 66 kV | 785_ISIS 132 kV | M025_Eidsvold 66 kV | M025_Eidsvold 66 kV | M025_Eidsvold 66 kV
WB-Wide Bay | M051_Tarong Tie 66 kV | % of Rated A | 8.818% | 10.53% | 11.97% | 13.25% | 14.47%
WB-Wide Bay | M051_Tarong Tie 66 kV | Limiting Line Name | TR_LINE 37804_1 | TR_LINE 37804_1 | TR_LINE 37804_1 | TR_LINE 37804_1 | TR_LINE 37804_1
WB-Wide Bay | M051_Tarong Tie 66 kV | Loading (A) | 9.4355 | 11.2619 | 12.8064 | 14.18 | 15.4862
WB-Wide Bay | M051_Tarong Tie 66 kV | Loading (MVA) | 1.1517 | 1.3774 | 1.569 | 1.7397 | 1.9025
WB-Wide Bay | M051_Tarong Tie 66 kV | Loading (MW) | 1.1017 | 1.3387 | 1.5378 | 1.7141 | 1.8816
WB-Wide Bay | M051_Tarong Tie 66 kV | Power Factor | 0.955 | 0.97003 | 0.97794 | 0.98288 | 0.98639
WB-Wide Bay | M051_Tarong Tie 66 kV | Rating (A) | 107 | 107 | 107 | 107 | 107
WB-Wide Bay | M051_Tarong Tie 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M051_Tarong Tie 66 kV | Min Voltage at Constrained Conductor | 70.4728 | 70.6115 | 70.734 | 70.8336 | 70.9265
WB-Wide Bay | M051_Tarong Tie 66 kV | Contingency Outage | M046_Tarong-Caboonbah 66 kV | M046_Tarong-Caboonbah 66 kV | M046_Tarong-Caboonbah 66 kV | M046_Tarong-Caboonbah 66 kV | M046_Tarong-Caboonbah 66 kV
WB-Wide Bay | SOBU-BARG-1_SOBU-Bargara-1 66 kV | % of Rated A | 13.38% | 16.82% | 19.84% | 22.67% | 25.53%
WB-Wide Bay | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Limiting Line Name | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1
WB-Wide Bay | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Loading (A) | 54.8482 | 68.9485 | 81.327 | 92.967 | 104.6906
WB-Wide Bay | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Loading (MVA) | 6.3467 | 7.9642 | 9.3969 | 10.7554 | 12.1265
WB-Wide Bay | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Loading (MW) | 6.3452 | 7.9612 | 9.3919 | 10.7479 | 12.1159
WB-Wide Bay | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Power Factor | 0.99976 | 0.99962 | 0.99947 | 0.99931 | 0.99912
WB-Wide Bay | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Rating (A) | 410 | 410 | 410 | 410 | 410
WB-Wide Bay | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Min Voltage at Constrained Conductor | 66.7998 | 66.6796 | 66.6987 | 66.7814 | 66.8618
WB-Wide Bay | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Contingency Outage | 7187_Gin Gin - Bundaberg 132 kV | 785_ISIS 132 kV | M032_Bundaberg-South Kolan No 1 66 kV | M032_Bundaberg-South Kolan No 1 66 kV | M032_Bundaberg-South Kolan No 1 66 kV
WB-Wide Bay | T014_Maryborough-Pialba Tee Howard 66 kV | % of Rated A | 18.09% | 23.69% | 29.21% | 34.77% | 40.91%
WB-Wide Bay | T014_Maryborough-Pialba Tee Howard 66 kV | Limiting Line Name | TR_LINE 224569_1 | TR_LINE 224569_1 | TR_LINE 224569_1 | TR_LINE 224569_1 | TR_LINE 224569_1
WB-Wide Bay | T014_Maryborough-Pialba Tee Howard 66 kV | Loading (A) | 109.4616 | 143.3026 | 176.7132 | 210.3623 | 247.4964
WB-Wide Bay | T014_Maryborough-Pialba Tee Howard 66 kV | Loading (MVA) | 13.2236 | 17.2533 | 21.3409 | 25.4395 | 30.0996
WB-Wide Bay | T014_Maryborough-Pialba Tee Howard 66 kV | Loading (MW) | 10.8506 | 15.6331 | 20.1329 | 24.5252 | 29.0529
WB-Wide Bay | T014_Maryborough-Pialba Tee Howard 66 kV | Power Factor | 0.8203 | 0.90609 | 0.94339 | 0.96406 | 0.96523
WB-Wide Bay | T014_Maryborough-Pialba Tee Howard 66 kV | Rating (A) | 605 | 605 | 605 | 605 | 605
WB-Wide Bay | T014_Maryborough-Pialba Tee Howard 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | T014_Maryborough-Pialba Tee Howard 66 kV | Min Voltage at Constrained Conductor | 69.7161 | 69.4353 | 69.6211 | 69.6973 | 70.0662
WB-Wide Bay | T014_Maryborough-Pialba Tee Howard 66 kV | Contingency Outage | M020_Maryborough-Torquay 66 kV | M020_Maryborough-Torquay 66 kV | M020_Maryborough-Torquay 66 kV | M020_Maryborough-Torquay 66 kV | M020_Maryborough-Torquay 66 kV