## Disclaimer
Distribution Feeder Limitations
(Ergon Energy Distribution Annual Planning Report 2023)
This workbook forms part of the Ergon Energy Distribution Annual Planning Report 2023 (DAPR) and should be read in conjunction with the report document.
Readers are encouraged to take into account the details and content portrayed in the ‘Introduction & Notes’ section of this workbook when reviewing the associated data.
Disclaimer
Ergon Energy’s Distribution Annual Planning Report (DAPR) is prepared and made available solely for information purposes. While care was taken in the preparation of the information in the DAPR, and it is provided in good faith, Ergon Energy accepts no responsibility or liability (including without limitation, liability to any person by reason of negligence or negligent mis-statement) for any loss or damage that may be incurred by any person acting in reliance on this information or assumptions drawn from it, except to the extent that liability under any applicable Queensland or Commonwealth of Australia statute cannot be excluded.
It contains assumptions regarding, among other things, economic growth and load forecasts which may or may not prove to be correct. The forecasts included in the DAPR involve subjective judgements and analysis which are subject to significant uncertainties and contingencies, many of which are out of the control of Ergon Energy. Ergon Energy makes no representation or warranty as to the accuracy, reliability, completeness or suitability for any particular purpose of the information in this document. All information should be independently investigated, reviewed, analysed and verified, and must not be relied upon in connection with any investment proposal or decision. The information contained in the DAPR is subject to annual review. Ergon Energy is obligated to publish future editions by 31st December, in accordance with the National Electricity Rules.
All financials presented in the DAPR or within this document are correct at the time of writing and represent the existing organisational accounting treatment, which may be subject to change. Energy Queensland is finalising the alignment of its Cost Allocation Methodology between Ergon Energy and Energex, potentially impacting the treatment of some Capital and Operational Project costs.
Forecasted data is subject to ongoing variation due to COVID 19 impacts.
All presented project costings and milestones (as of October 2023) are subject to change.

## Introduction & Notes
Distribution Feeder Limitations
(Ergon Energy Distribution Annual Planning Report 2023)
This workbook presents primary distribution feeders which are currently experiencing overload or are forecast to experience an overload in the next 2 years.
This workbook forms part of the Ergon Energy Distribution Annual Planning Report 2023 (DAPR) and should be read in conjunction with the report document.
Forecasted data is subject to ongoing variation due to COVID 19 impacts.
Contents
The 'Distribution Feeder Limitations' tab of this workbook includes the following information for each constrained distribution feeder:
- Ergon Energy region
- Distribution feeder name, ID & location
- Load exceedance after 2 yrs (MVA)
- Forecast season that exceedance occurs (Summer / Winter)
- Forecast year that exceedance occurs
- Forecast month/s that exceedance occurs
- Load reduction needed to delay the exceedance by 12 months (MW)
(assumed power factor of 0.9)
1. Potential Solutions
Suggested solutions, in order or preference, are included under the 'Potential Solutions' tab.
2. Committed Solutions:
Committed investments to address current distribution network limitations are included under the 'Committed Solutions' tab.
Connection points for possible load reduction:
In all cases, the connection point to apply load reduction would be downsteam of the substation exit feeder cable and/or first section of line.
Exclusions:
Dedicated customer connection assets are excluded from the analysis.
NOTE: All financials presented in this document are correct at the time of writing (i.e. October 2023) and represent the existing organisational accounting treatment, which may be subject to change. Energy Queensland is still finalising the alignment of its Cost Allocation Methodology between Ergon and Energex, potentially impacting the treatment of some Capital and Operational Project costs.

## Potential Solutions
Solutions:
Distribution feeder capacity problems can be solved in a number of ways, depending on the local characteristics of the distribution feeder. The constraints identified in this document are a trigger for further planning studies and in many cases do not constitute plant risk, are acceptable, and do not require augmentation due to multiple factors such as:
- Minimal load growth on the feeder and/or adjacent feeders.
- Customer density or feeder topology constraints that do not allow for planning constraints to be met.
- Feeder topology that allows for simple switching in a contingency but for regional depot support is configured in a certain manner.
- Short term customer behaviour changes (such as abnormal weather conditions).
- Medium term network topology changes due to planned works in a region.
Where action is required to solve a feeder constraint, possible solutions (in approximate order of preference based on network cost) include:
Network Reconfiguration
- Transferring existing load to adjacent feeders if capacity is available; and
- Re-rating or dynamic rating of the underground exit cable or overhead feeder.
Demand Management initiatives that reduce customer loading
- Energy efficient appliances
- Power factor correction
- Shift loads (e.g. pool pumps, HW storage etc.) to control load tariff
- Shift loads to a time-of-use tariff
- Air conditioning ‘Peak Smart’
- Customer EG units
- Call off load
- Commercial and industrial demand management
- Customer embedded generation to ‘peak lop’
- Network embedded generation to ‘peak lop’
- Energy storage.
Network Augmentation
- Replacing the underground exit cable or overhead feeder
- Creating new substations and/or feeders and transferring existing load.
In each instance, actual solutions are subject to a detailed study and business case. In some cases, a committed project is already in place.

## Distribution Feeder Limit 2023
Distribution Feeder Limitations (Ergon Energy Distribution Annual Planning Report 2023)
Region | Feeder name | Feeder ID | Feeder Location | Load exceedance after 2 yrs (MVA) | Season of exceedance | Year of exceedance | Month of exceedance | Load reduction to defer exceedance by 12 mths (MW) @ 0.9pf | Connection Point | Potenital Solutions
Southern | BF202 | 40001029 | BFSS BEDFORD WEIR 66/22KV SUB | 2.356 | Summer | 2022/2023 | Dec-Feb | 2.1348 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | MA108 | 40001110 | MASS MALCHI 66/11KV SUB | 2.5217 | Summer | 2022/2023 | Dec-Feb | 2.2376 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | CN108 | 40001094 | CANNING STREET 66/11KV SUB (CNSS) | 2.668 | Summer | 2022/2023 | Dec-Feb | 2.4308 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | MA105 | 40001109 | MASS MALCHI 66/11KV SUB | 2.1594 | Summer | 2022/2023 | Dec-Feb | 1.9148 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | DG-08 | 20004893 | DAN GLEESON 132/66/11KV SUB (DAGL) | 2.2733 | Summer | 2022/2023 | Dec-Feb | 2.0597 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | FB15 | 83877341 | BERSERKER 66/11KV SUB (BERS) | 1.5681 | Summer | 2022/2023 | Dec-Feb | 1.4241 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | 216 | 30053783 | MORANBAH 132/66/11KV SUB (MORA) | 1.7662 | Summer | 2022/2023 | Dec-Feb | 1.5748 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | BK206 | 40216323 | BKSS BLACKALL 66/22KV SUB | 0.8689 | Summer | 2022/2023 | Dec-Feb | 0.7865 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | GA-05 | 20005919 | GARBUTT (TO46) 132/66/11KV SUB (GA) | 1.1187 | Summer | 2022/2023 | Dec-Feb | 1.1567 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | LC107 | 40001105 | LAKES CREEK 66/11KV SUB (LCSS) | 1.3523 | Summer | 2022/2023 | Dec-Feb | 1.2276 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | RG114 | 40001135 | RTON GLENMORE RD 132/66/11KV SUB (RGBS) | 1.3946 | Summer | 2022/2023 | Dec-Feb | 1.2587 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | SB202 | 40200483 | SBSS SOUTH BLACKWATER 66/22KV SUB | 0.088 | Summer | 2022/2023 | Dec-Feb | 0.0792 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | FV111 | 40001100 | FRENCHVILLE 66/11KV SUB (FVSS) | 1.2916 | Summer | 2022/2023 | Dec-Feb | 1.1624 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | GC-C | 50000059 | GOOTCHIE 66/11KV SUB | 0.6868 | Summer | 2022/2023 | Dec-Feb | 0.633 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | CP103 | 40001232 | CPSS CALLIOPE 66/11KV SUB | 1.2236 | Summer | 2022/2023 | Dec-Feb | 1.0834 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | EM226 | 40001006 | EMSS EMERALD 66/22KV SUB | 1.8868 | Summer | 2022/2023 | Dec-Feb | 1.6922 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | EM212 | 40001001 | EMSS EMERALD 66/22KV SUB | 1.2876 | Summer | 2022/2023 | Dec-Feb | 1.1801 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | 2HAM | 83896573 | EDMONTON 132/22KV SUB (EDMONTON) | 2.3496 | Summer | 2022/2023 | Dec-Feb | 2.0356 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | BL103 | 40001246 | BLBS BILOELA 132/66/11KV SUB | 0.7901 | Summer | 2022/2023 | Dec-Feb | 0.7175 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | FV104 | 40001097 | FRENCHVILLE 66/11KV SUB (FVSS) | 0.9584 | Summer | 2022/2023 | Dec-Feb | 0.8761 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | FB16 | 84587749 | BERSERKER 66/11KV SUB (BERS) | 0.5776 | Summer | 2022/2023 | Dec-Feb | 0.5467 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | AL-11 | 25273354 | ALAN SHERRIFF 132/11KV SUB (ALSH) | 0.6977 | Summer | 2022/2023 | Dec-Feb | 0.6328 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | KR-C | 50000092 | KINGAROY 66/11KV SUB (KING) | 1.3986 | Summer | 2022/2023 | Dec-Feb | 1.2686 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | BW210 | 40001035 | BLACKWATER 132/66/22KV SUB (BWBS) | 1.5562 | Summer | 2022/2023 | Dec-Feb | 1.4174 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | CB-04 | 20003306 | CRANBROOK 66/11KV SUB (CB) | 0.9281 | Summer | 2022/2023 | Dec-Feb | 0.842 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | GF105 | 40001189 | GLADSTONE FRIEND ST 66/11KV SUB (GFSS) | 0.7851 | Summer | 2022/2023 | Dec-Feb | 0.7095 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | YP108 | 40001204 | YEPPOON 66/22/11KV SUB (YPSS) | 1.0635 | Summer | 2022/2023 | Dec-Feb | 0.9494 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | DG-10 | 20004903 | DAN GLEESON 132/66/11KV SUB (DAGL) | 0.9014 | Summer | 2022/2023 | Dec-Feb | 0.7948 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | AY-04 | 20001649 | AYR 66/11KV SUB (AYRZ) | 0.5741 | Summer | 2022/2023 | Dec-Feb | 0.5195 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | 369 | 30053878 | PLANELLA 33/11KV SUB (PLAN) | 0.8529 | Summer | 2022/2023 | Dec-Feb | 0.7545 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | NS-11 | 20011243 | NEIL SMITH STURT ST 66/11KV SUB (NESM) | 0.7045 | Summer | 2022/2023 | Dec-Feb | 0.6341 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | CN103 | 40001091 | CANNING STREET 66/11KV SUB (CNSS) | 0.7356 | Summer | 2022/2023 | Dec-Feb | 0.678 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | CI104 | 40001177 | CLINTON INDUSTRIAL 66/11KV SUB (CISS) | 0.9118 | Summer | 2022/2023 | Dec-Feb | 0.8021 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | 379 | 82647141 | NORTH MACKAY 33/11KV SUB (NOMA) | 0.8732 | Summer | 2022/2023 | Dec-Feb | 0.7715 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | BLRI-08 | 82914276 | BLACKRIVER 66/11KV SUB (BLRI) | 0.8308 | Summer | 2022/2023 | Dec-Feb | 0.6901 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | 2NOR | 10020673 | NORMANTON 66/22KV SUB (NORM) | 0.3958 | Summer | 2022/2023 | Dec-Feb | 0.3562 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | 2GO3 | 10020782 | EDMONTON 132/22KV SUB (EDMONTON) | 1.6905 | Summer | 2022/2023 | Dec-Feb | 1.4842 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | BLRI-05 | 84737242 | BLACKRIVER 66/11KV SUB (BLRI) | 0.7874 | Summer | 2022/2023 | Dec-Feb | 0.6549 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | TOPO-03 | 82564420 | TOWNSVILLE PORT 66/11KV SUB (TOPO) | 0.6406 | Summer | 2022/2023 | Dec-Feb | 0.5735 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | EM246 | 40001009 | EMSS EMERALD 66/22KV SUB | 1.064 | Summer | 2022/2023 | Dec-Feb | 0.9576 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | HP-03 | 20007314 | HERMIT PARK 66/11KV SUB (HP) | 0.4388 | Summer | 2022/2023 | Dec-Feb | 0.4395 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | BO-08 | 20003061 | BOHLE 66/11KV SUB (BOHL) | 0.6536 | Summer | 2022/2023 | Dec-Feb | 0.5668 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | EM214 | 40001004 | EMSS EMERALD 66/22KV SUB | 0.9632 | Summer | 2022/2023 | Dec-Feb | 0.8568 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | 14142 | 91445024 | T019 GLADSTONE SOUTH 132/66/11KV SUB | 0.7134 | Summer | 2022/2023 | Dec-Feb | 0.6307 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | PH106 | 40001122 | PARKHURST 66/11KV SUB (PHSS) | 0.5132 | Summer | 2022/2023 | Dec-Feb | 0.4919 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | HP-04 | 20007334 | HERMIT PARK 66/11KV SUB (HP) | 0.4637 | Summer | 2022/2023 | Dec-Feb | 0.4123 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | HU-20 | 20007634 | HUGHENDEN 66/33/6.6KV SUB (HUGH) | 0.9664 | Summer | 2022/2023 | Dec-Feb | 0.8951 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | CL204 | 40001010 | CLBS CLERMONT 132/66/22/11KV SUB (T071) | 0.5383 | Summer | 2022/2023 | Dec-Feb | 0.4801 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | WB-L | 50000213 | WEST BUNDABERG 66/11KV SUB (WEBU) | 0.473 | Summer | 2022/2023 | Dec-Feb | 0.4743 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | 389 | 30189394 | PLANELLA 33/11KV SUB (PLAN) | 0.9376 | Summer | 2022/2023 | Dec-Feb | 0.7996 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | GF111 | 40001194 | GLADSTONE FRIEND ST 66/11KV SUB (GFSS) | 0.566 | Summer | 2022/2023 | Dec-Feb | 0.5197 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | BO-07 | 20003026 | BOHLE 66/11KV SUB (BOHL) | 0.439 | Summer | 2022/2023 | Dec-Feb | 0.3874 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | CB-07 | 20003349 | CRANBROOK 66/11KV SUB (CB) | 0.471 | Summer | 2022/2023 | Dec-Feb | 0.4298 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | DG-07 | 20004796 | DAN GLEESON 132/66/11KV SUB (DAGL) | 0.5373 | Summer | 2022/2023 | Dec-Feb | 0.4539 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | RG107 | 40001131 | RTON GLENMORE RD 132/66/11KV SUB (RGBS) | 0.3768 | Summer | 2022/2023 | Dec-Feb | 0.3854 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | 385 | 30187535 | PLANELLA 33/11KV SUB (PLAN) | 0.6543 | Summer | 2022/2023 | Dec-Feb | 0.5623 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | 212 | 30187348 | MORANBAH 132/66/11KV SUB (MORA) | 0.4474 | Summer | 2022/2023 | Dec-Feb | 0.3972 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | F073C | 60026673 | T013 CHINCHILLA 132/110/33KV SUB | 1.0808 | Summer | 2022/2023 | Dec-Feb | 1.0765 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | 304 | 30053814 | TENNYSON STREET 33/11KV SUB (TEST) | 0.5256 | Summer | 2022/2023 | Dec-Feb | 0.4802 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | 386 | 30188733 | ROSELLA 33/11KV SUB (ROSE) | 0.2129 | Summer | 2022/2023 | Dec-Feb | 0.1945 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | 103 | 30053746 | KELSEY CREEK EAST 66/11KV SUB (KECE) | 0.4597 | Summer | 2022/2023 | Dec-Feb | 0.4137 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | RASM-01 | 83897502 | RASMUSSEN 66/11KV SUB (RASM) | 0.3269 | Summer | 2022/2023 | Dec-Feb | 0.2914 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | CB-05 | 20003317 | CRANBROOK 66/11KV SUB (CB) | 0.2537 | Summer | 2022/2023 | Dec-Feb | 0.238 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | BLRI-15 | 84737245 | BLACKRIVER 66/11KV SUB (BLRI) | 0.2693 | Summer | 2022/2023 | Dec-Feb | 0.3847 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | PA-16 | 25267836 | PETER ARLETT 66/11KV SUBSTATION (PEAR) | 0.3094 | Summer | 2022/2023 | Dec-Feb | 0.2618 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | FB04 | 83877404 | BERSERKER 66/11KV SUB (BERS) | 0.0862 | Summer | 2022/2023 | Dec-Feb | 0.15 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | WB-J | 50000211 | WEST BUNDABERG 66/11KV SUB (WEBU) | 0.4426 | Summer | 2022/2023 | Dec-Feb | 0.3984 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | FV113 | 82914591 | FRENCHVILLE 66/11KV SUB (FVSS) | 0.2604 | Summer | 2022/2023 | Dec-Feb | 0.2454 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | 3153 | 83921739 | DALBY EAST (T002) 110/33KV SUB (DAEA) | 0.0678 | Summer | 2022/2023 | Dec-Feb | 0.0649 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | AL-04 | 25273362 | ALAN SHERRIFF 132/11KV SUB (ALSH) | 0.2139 | Summer | 2022/2023 | Dec-Feb | 0.1795 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | F133R | 60026691 | ROMA WEST 33/11KV SUB | 0.1285 | Summer | 2022/2023 | Dec-Feb | 0.1127 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | 401 | 82563099 | ALFRED STREET 33/11KV SUB (ALST) | 0.2223 | Summer | 2022/2023 | Dec-Feb | 0.1947 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | 363 | 30053872 | PLANELLA 33/11KV SUB (PLAN) | 0.3496 | Summer | 2022/2023 | Dec-Feb | 0.269 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | F3465 | 60026781 | EAST TOOWOOMBA 33/11KV SUB | 0.3022 | Winter | 2022/2023 | Mar-Nov | 0.2677 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | RM-04 | 20011598 | RASMUSSEN 66/11KV SUB (RASM) | 0.1705 | Summer | 2022/2023 | Dec-Feb | 0.1535 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | F4610 | 60330968 | T116 TORRINGTON 110/33/11KV SUB | 0.5901 | Winter | 2022/2023 | Mar-Nov | 0.3991 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | FV110 | 40001099 | FRENCHVILLE 66/11KV SUB (FVSS) | 0.1976 | Summer | 2022/2023 | Dec-Feb | 0.19 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | PA-03 | 25267831 | PETER ARLETT 66/11KV SUBSTATION (PEAR) | 0.1167 | Summer | 2022/2023 | Dec-Feb | 0.0976 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | BL104 | 40001247 | BLBS BILOELA 132/66/11KV SUB | 0.1656 | Summer | 2022/2023 | Dec-Feb | 0.1558 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | AV-10 | 20001178 | AITKENVALE 66/11KV SUBSTATION (AITK) | 0.1332 | Summer | 2022/2023 | Dec-Feb | 0.1146 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | 417 | 83909007 | MORANBAH 132/66/11KV SUB (MORA) | 0.2088 | Summer | 2022/2023 | Dec-Feb | 0.1678 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | PB-D | 50000155 | PIALBA 66/11KV SUB (PB) | 0.086 | Summer | 2022/2023 | Dec-Feb | 0.0948 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | 320 | 30053830 | MOUNT BASSETT 33/11KV SUB (MOBA) | 0.1077 | Summer | 2022/2023 | Dec-Feb | 0.1005 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | CI110 | 40001180 | CLINTON INDUSTRIAL 66/11KV SUB (CISS) | 0.0083 | Summer | 2022/2023 | Dec-Feb | 0.0133 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | RS-J | 50000169 | ROCKY STREET 66/11KV SUB (RS) | 0.075 | Summer | 2022/2023 | Dec-Feb | 0.0741 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | CT-04 | 20004592 | CHARTERS TOWERS 66/11KV SUB (CHTO) | 0.0445 | Summer | 2022/2023 | Dec-Feb | 0.0627 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | 390 | 82647144 | NORTH MACKAY 33/11KV SUB (NOMA) | 0.0923 | Summer | 2022/2023 | Dec-Feb | 0.0791 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | 325 | 30053835 | NORTH MACKAY 33/11KV SUB (NOMA) | 0.061 | Summer | 2022/2023 | Dec-Feb | 0.0586 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | BL-02 | 20002331 | BLUEWATER 66/11KV SUB (BLUE) | 0.0595 | Summer | 2022/2023 | Dec-Feb | 0.0457 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | 2MNR | 84326665 | CAIRNS NORTH 132/22KV SUB (CANO) | 0.1295 | Summer | 2022/2023 | Dec-Feb | 0.1019 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | GS108 | 40001202 | T019 GLADSTONE SOUTH 132/66/11KV SUB | 0.1088 | Summer | 2022/2023 | Dec-Feb | 0.0677 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | 215 | 30053782 | MORANBAH 132/66/11KV SUB (MORA) | 0.0391 | Summer | 2022/2023 | Dec-Feb | 0.0257 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | AL-10 | 25274650 | ALAN SHERRIFF 132/11KV SUB (ALSH) | 0.0149 | Summer | 2022/2023 | Dec-Feb | 0.0134 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | PB-C | 50000154 | PIALBA 66/11KV SUB (PB) | 0.0188 | Winter | 2022/2023 | Mar-Nov | 0.0208 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | F3055 | 60026754 | NORTH STREET 33/11KV SUB (NOST) (ME020) | 0.0317 | Summer | 2022/2023 | Dec-Feb | 0.0221 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | ST05 | 20012587 | STUART 66/11KV SUB (STUA) | 0.1939 | Summer | 2022/2023 | Dec-Feb | 0.0773 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet

## Committed Solutions 2023
WR Ref. | Limitation | Location | Committed Solution | Region | Comment | Choose: | Selective
328478 | Distribution Feeder Limitation Address capacity constraints | GRAC - Gracemere | Gracemere Substation - New Feeder 3x Exits - Target Comissioning: Jan-24 - Cost: $1.9M ± 30% | Southern
1390805 | Distribution Feeder Limitation Address capacity and reliability constraints | SARI - Sarina | Construct 4km new OH line, install ACR & line fuses on 11kV Sarina Beach (424) Feeder - Target Comissioning: Jun-24 - Cost: $0.7M ± 30% | Northern
1401431 | Distribution Feeder Limitation Address capacity constraints | EDMO - Edmonton | Install 2km of underground cable and reconfigure 22kV Hambledon (2HAM) Feeder - Target Comissioning: Aug-24 - Cost: $1.5M ± 30% | Northern
1401523 | Distribution Feeder Limitation Address voltage, capacity and protection constraints | MOPA - Mona Park | Install voltage regulators, ACRs & line uprating on 11kV feeders supplied from Mona Park - Target Comissioning: Jan-24 - Cost: $0.8M ± 30% | Northern
1503629 | Distribution Feeder Limitation Address capacity constraints | PLAN - Planella | Install new RMU and conductor 11kV Blacks Beach Feeder - Target Comissioning: Sep-24 - Cost: $0.8M ± 30% | Northern
1524360 | Distribution Feeder Limitation Address capacity and reliability constraints | WOTO - Woolooga Town | Reconductor 3.7km, build 3km line, install regulators, ACR & RCGS on 11kV Bells Bridge (WL-A) Feeder - Target Comissioning: Jun-24 - Cost: $1.3M ± 30% | Southern
1603091 | Distribution Feeder Limitation Address voltage and reliability constraints | CANN - Cannonvale | Reconductor 2km, install ACR & voltage regulators on 11kV Paluma Rd (398) Feeder - Target Comissioning: Nov-25 - Cost: $0.5M ± 30% | Northern
1603258 | Distribution Feeder Limitation Address capacity constraints | MIRA - Mirani | Reroute and replace conductor for both Mirani and Wier 11kV Feeders - Target Comissioning: May-24 - Cost: $0.5M ± 30% | Northern
1614080 | Distribution Feeder Limitation Address voltage and capacity constraints | GOOT - Gootchie | Replace distribution transformers and reconductor line for Glenwood Feeder - Target Comissioning: Dec-23 - Cost: $0.4M ± 30% | Southern
1629313 | Distribution Feeder Limitation Addess load transfer constraints | MILM - Millmerran | Reconductor constrained distribution feeder (F3535) from Millmerran - Target Comissioning: Jun-24 - Cost: $0.9M ± 30% | Southern
1631438 | Distribution Feeder Limitation Address capacity constraints | WALL – Wallaville | Upgrade exit cable & re-rate 3km of overhead line on 11kV Drinan feeder (WV-D) - Target Comissioning: Oct-25 - Cost: $0.53M ± 30% | Southern
1631925 | Distribution Feeder Limitation Address voltage constraints | GLSO – Gladstone South | Reconductor 1.5km conductor on 11kV South Gladstone (GS105) feeder - Target Comissioning: Dec-23 - Cost: $0.22M ± 30% | Southern
1631928 | Distribution Feeder Limitation Address capacity and reliability constraints | CLER - Clermont | Upgrade line voltage regulators on 22kV Capella (CL204) Feeder - Target Comissioning: Feb-25 - Cost: $0.35M ± 30% | Southern
1631929 | Distribution Feeder Limitation Address voltage constraints | LONG – Longreach | Install voltage regulators on 22kV Morella (LR204) feeder - Target Comissioning: Dec-23 - Cost: $0.41M ± 30% | Southern
1631931 | Distribution Feeder Limitation Address capacity and protection constraints | FREN - Frenchville | Reconductor & construct feeder tie on 11kV Frenchville Rd (FV111) Feeder - Target Comissioning: Sep-25 - Cost: $0.4M ± 30% | Southern
1633476 | Distribution Feeder Limitation Address voltage, capacity and reliability constraints | INGH - Ingham | Reconfigure network, reconductor & install regulators & RCGS on 11kV Ingham No.8 (IN-08) Feeder - Target Comissioning: May-24 - Cost: $0.5M ± 30% | Northern
1635552 | Distribution Feeder Limitation Address capacity constraints | EDMO - Edmonton | Install recloser, gas switch and reconductor sections of 22kV Hambledon (2HAM) Feeder - Target Comissioning: Dec-23 - Cost: $0.3M ± 30% | Northern
1635558 | Distribution Feeder Limitation Address capacity constraints | KAME - Kamerunga | Replace 650m conductor of 22kV Cook No.1 (2CO1) Feeder - Target Comissioning: Dec-23 - Cost: $0.5M ± 30% | Northern
1636448 | Distribution Feeder Limitation Address capacity constraints | STUA - Stuart | Upgrade exit cables on 11kV ST-02 Feeder, 11kV ST-05 Feeder & 11kV ST-07 Feeder - Target Comissioning: Aug-24 - Cost: $0.6M ± 30% | Northern
1648790 | Distribution Feeder Limitation Address reliability issues | KAME - Kamerunga | Install ACRs & remote controlled gas switches on 22kV Kuranda Range (2KDA) Feeder - Target Comissioning: Nov-23 - Cost: $0.3M ± 30% | Northern
1652495 | Distribution Feeder Limitation Address capacity and reliability constraints | BLRI - Black River | Establish a new 11kV feeder to the East - Target Comissioning: Nov-24 - Cost: $1.06M ± 30% | Northern
1657610 | Distribution Feeder Limitation Address voltage and capacity constraints | BROX - Broxburn | Reconductor 2.2km & construct 3.1km of OH line on 11kV Copps Hill & Pittsworth Feeders - Target Comissioning: Mar-24 - Cost: $0.7M ± 30% | Southern
1661521 | Distribution Feeder Limitation Address capacity constraints | TOMA – Townsville Marina | Reconductor & recover sections of 11kV Townsville Marina Feeder (TM-03) - Target Comissioning: Dec-24 - Cost: $0.51M ± 30% | Northern
1677841 | Distribution Feeder Limitation Address capacity constraints | SOMA - South Mackay | Milton St Feeder Tie - Install new RMU and conductor rebuild - Target Comissioning: Jun-24 - Cost: $0.5M ± 30% | Northern
1683114 | Distribution Feeder Limitation Address voltage constraints | NANA - Nanango | Upgrade 1.5km of line to three-phase & install ACR on 11kV South Nanango (NN-E) Feeder - Target Comissioning: Oct-24 - Cost: $0.3M ± 30% | Southern
1683115 | Distribution Feeder Limitation Address voltage constraints | THEO - Theodore | Install voltage regulators on 22kV Taroom (FA08) Feeder - Target Comissioning: Nov-23 - Cost: $0.3M ± 30% | Southern
1699454 | Distribution Feeder Limitation Address capacity constraints | ROGL - Rockhampton Glenmore | Construct UG feeder tie & install gas switches on 11kV Wandal (RG114) Feeder - Target Comissioning: Mar-24 - Cost: $0.3M ± 30% | Southern
1699662 | Distribution Feeder Limitation Address capacity and protection constraints | TORR - Torrington | Construct 0.5km line, reconductor 2km & install fuses on 11kV Westbrook (F4610) Feeder - Target Comissioning: Sep-24 - Cost: $0.5M ± 30% | Southern
1700634 | Distribution Feeder Limitation Address voltage and capacity constraints | CRNE - Crows Nest | Construct 4km new line, install ACR & gas switches on 11kV Industrial Rd (F2661) Feeder - Target Comissioning: Nov-24 - Cost: $0.9M ± 30% | Southern
1701698 | Distribution Feeder Limitation Address protection and reliability constraints | CALE - Calen | Install ACR, RCGS & line fuses on 11kV Calen (112) Feeder - Target Comissioning: Aug-24 - Cost: $0.2M ± 30% | Northern
1701700 | Distribution Feeder Limitation Address reliability issues | BALB - Balberra | Install RCGS & install comms on voltage regulators on 11kV Mt Alice (338) Feeder - Target Comissioning: Sep-24 - Cost: $0.2M ± 30% | Northern
1704559 | Distribution Feeder Limitation Address voltage and capacity constraints | MALC - Malchi | Reconductor 5.6km SWER & upgrade isolator on 11kV Gracemere Rural (MA108) Feeder - Target Comissioning: Nov-24 - Cost: $0.3M ± 30% | Southern
1704560 | Distribution Feeder Limitation Address voltage and capacity constraints | RAGL - Raglan | Install voltage regulators & upgrade SWER isolator on 22kV Mt Larcom (RL202) Feeder - Target Comissioning: Dec-24 - Cost: $0.3M ± 30% | Southern
1704561 | Distribution Feeder Limitation Address voltage and protection constraints | BILO - Biloela | Reconductor sections of 11kV Thangool Rd (BL107) Feeder & install ACRs - Target Comissioning: Nov-23 - Cost: $0.5M ± 30% | Southern
1704562 | Distribution Feeder Limitation Address voltage and capacity constraints | WOWA - Wowan | Install voltage regulators & upgrade SWER isolator on 22kV Jambin (WN211) Feeder - Target Comissioning: Mar-24 - Cost: $0.3M ± 30% | Southern
1704563 | Distribution Feeder Limitation Address voltage and capacity constraints | CALE - Calen | Reconductor 7.5km conductor on 11kV Calen (112) Feeder - Target Comissioning: Nov-24 - Cost: $0.7M ± 30% | Northern
1704564 | Distribution Feeder Limitation Address capacity constraints | AYRZ - Ayr | Reconductor 2.4km & uprate 4.2km of overhead line on 11kV Ayr No.4 (AY-04) Feeder - Target Comissioning: Sep-24 - Cost: $0.3M ± 30% | Northern
1704565 | Distribution Feeder Limitation Address voltage, capacity and protection constraints | WOSO - Woodstock South | Reconductor 1.5km of overhead line & install line fuses on 11kV WOSO-03 Feeder - Target Comissioning: Oct-24 - Cost: $0.3M ± 30% | Northern
1704566 | Distribution Feeder Limitation Address voltage constraints | FARL - Farleigh | Reconductor 4.5km conductor on 11kV Wundaru (328) Feeder - Target Comissioning: Sep-24 - Cost: $0.5M ± 30% | Northern
1704567 | Distribution Feeder Limitation Address voltage and protection constraints | BALB - Balberra | Install voltage regulators, ACRs and line fuses on 11kV Munbura (205) Feeder - Target Comissioning: Oct-24 - Cost: $0.3M ± 30% | Northern
1704568 | Distribution Feeder Limitation Address voltage and capacity constraints | MIRA - Mirani | Reconductor 4.5km conductor on 11kV Weir (356) Feeder - Target Comissioning: Dec-24 - Cost: $0.7M ± 30% | Northern
1705911 | Distribution Feeder Limitation Address voltage and reliability constraints | MCCR - McKinley Creek | Reconductor 4.5km conductor & install voltage regulators on 11kV The Leap (373) Feeder - Target Comissioning: Dec-24 - Cost: $0.7M ± 30% | Northern
1705913 | Distribution Feeder Limitation Address voltage constraints | MOMG - Mount Morgan | Reconductor 4km SWER conductor on 11kV Bouldercombe (ML107) Feeder - Target Comissioning: Dec-24 - Cost: $0.2M ± 30% | Southern
1708366 | Distribution Feeder Limitation Address voltage and capacity constraints | SARI - Sarina | Rebuild 1.5km of overhead line on 11kV Southern (203) Feeder - Target Comissioning: Oct-24 - Cost: $0.3M ± 30% | Northern
1708367 | Distribution Feeder Limitation Address capacity constraints | CLER - Clermont | Upgrade exit cable on 22kV Capella (CL204) Feeder & 22kV Clermont Town (CL203) Feeder - Target Comissioning: Oct-24 - Cost: $0.5M ± 30% | Southern
1708369 | Distribution Feeder Limitation Address reliability issues | WOSO - Woodstock South | Construct a feeder tie between the 11kV WOSO-02 Feeder & the 11kV GI-02 Feeder - Target Comissioning: Oct-24 - Cost: $0.6M ± 30% | Northern
1711667 | Distribution Feeder Limitation Address protection constraints | PINN - Pinnacle | Reconductor 2km, install ACR & install line fuses on 11kV Gargett (352) Feeder - Target Comissioning: Mar-25 - Cost: $0.4M ± 30% | Northern
1711668 | Distribution Feeder Limitation Address protection constraints | PINN - Pinnacle | Reconductor 1km, install ACR & install line fuses on 11kV Kungurri (353) Feeder - Target Comissioning: Feb-25 - Cost: $0.4M ± 30% | Northern
1716716 | Distribution Feeder Limitation Address voltage and reliability constraints | BARG - Bargara | Construct feeder tie, reconfigure network & install ACRs on 11kV Riverview (BG-B) Feeder - Target Comissioning: Nov-23 - Cost: $0.3M ± 30% | Southern
1722760 | Distribution Feeder Limitation Address protection and reliability constraints | CAWD - Cawdor | Install ACRs, remote controlled gas switches & line fuses on 11kV Granada Rd Feeder - Target Comissioning: Oct-24 - Cost: $0.5M ± 30% | Southern
1722764 | Distribution Feeder Limitation Address reliability issues | WETO - West Toowoomba | Install ACR & remote controlled gas switch on 11kV Weetwood (F4555) Feeder - Target Comissioning: Jan-25 - Cost: $0.2M ± 30% | Southern
1723419 | Distribution Feeder Limitation Address reliability issues | CATE - Cairns Terminal | Install ACR & remote controlled gas switch on 22kV Brinsmead (2BRI) Feeder - Target Comissioning: Dec-24 - Cost: $0.2M ± 30% | Northern
1723612 | Distribution Feeder Limitation Address reliability issues | CATE - Cairns Terminal | Install ACR & remote controlled gas switches on 22kV Bayview (2BAY) Feeder - Target Comissioning: Nov-24 - Cost: $0.2M ± 30% | Northern
1723632 | Distribution Feeder Limitation Address reliability issues | KAME - Kamerunga | Install ACR & remote controlled gas switch on 22kV Cook 2 (2CO2) Feeder - Target Comissioning: Jan-25 - Cost: $0.2M ± 30% | Northern
1725181 | Distribution Feeder Limitation Address capacity and protection constraints | NOMA - North Mackay | Upgrade exit cable, reconductor 1km & install ACR on 11kV Bedford Rd (325) Feeder - Target Comissioning: Mar-25 - Cost: $0.8M ± 30% | Northern
1725364 | Distribution Feeder Limitation Address reliability issues | MOSS - Mossman | Install ACR & remote controlled gas switches on 22kV Daintree (2DAI) Feeder - Target Comissioning: Oct-24 - Cost: $0.3M ± 30% | Northern
1725403 | Distribution Feeder Limitation Address reliability issues | TULL - Tully | Install ACRs & remote controlled gas switch on 22kV Tully Town No.1 (2TT1) Feeder - Target Comissioning: Feb-25 - Cost: $0.3M ± 30% | Northern
1725851 | Distribution Feeder Limitation Address capacity constraints | CLIN - Clinton | Reconductor & uprate sections of line on 11kV Kin Kora (CI110) Feeder - Target Comissioning: Nov-25 - Cost: $0.3M ± 30% | Southern
1725854 | Distribution Feeder Limitation Address capacity and protection constraints | CAST - Canning Street | Upgrade exit cable & 700m conductor on 11kV Athelstane (CN103) Feeder - Target Comissioning: Nov-24 - Cost: $0.6M ± 30% | Southern
1725953 | Distribution Feeder Limitation Address reliability issues | CANO - Cairns North | Install ACR & remote controlled gas switch on 22kV Martyn St (2MAR) Feeder - Target Comissioning: Nov-24 - Cost: $0.2M ± 30% | Northern
1726138 | Distribution Feeder Limitation Address capacity and protection constraints | CAST - Canning Street | Upgrade exit cable & install ACR on 11kV Upper Dawson Rd (CN108) Feeder - Target Comissioning: Sep-24 - Cost: $0.6M ± 30% | Southern
1726636 | Distribution Feeder Limitation Address capacity constraints | HEPA - Hermit Park | Upgrade exit cables on 11kV HP-03 Feeder, 11kV HP-04 Feeder & 11kV HP-07 Feeder - Target Comissioning: Dec-24 - Cost: $0.7M ± 30% | Northern
1727052 | Distribution Feeder Limitation Address voltage and capacity constraints | TARA – Tara | Install voltage regulators on 33kV Tara (F060T) feeder - Target Comissioning: Mar-24 - Cost: $0.53M ± 30% | Southern
1727192 | Distribution Feeder Limitation Address reliability issues | BLOO - Bloomfield | Construct feeder tie, and install ACR & remote controlled gas switch on 22kV Ayton (2AYT) Feeder - Target Comissioning: Nov-24 - Cost: $0.6M ± 30% | Northern
1780238 | Distribution Feeder Limitation Address capacity and voltage constraints | SAGE – St George | Replace exisiting isolator, install SWER regulator on 33kV St George Meatworks (F079S) feeder - Target Comissioning: Aug-24 - Cost: $0.26M ± 30% | Southern
1783190 | Distribution Feeder Limitation Address capacity constraints | NOMA – North Mackay | Recover underground cable, install 0.27km of underground cable on 11kV Mansfield Drive (384) feeder - Target Comissioning: Jun-24 - Cost: $0.36M ± 30% | Northern
1784020 | Distribution Feeder Limitation Address voltage and capacity constraints | KECE – Kelsey Creek East | Reconductor 2.5km, install voltage regulators on 11kV Crystalbrook (101) feeder - Target Comissioning: Jun-24 - Cost: $0.80M ± 30% | Northern
1784078 | Distribution Feeder Limitation Address voltage and capacity constraints | KECE – Kelsey Creek East | Reconductor 1.9km, upgrade SWER OCR & isolator on 11kV Kelsey Creek (104) feeder - Target Comissioning: Jun-24 - Cost: $0.66M ± 30% | Northern
1784125 | Distribution Feeder Limitation Address protection constraints | WOSO – Woodstock South | Reconductor 1.6km, install ACR & replace line fuses on 11kV Woodstock South (WOSO-01) feeder - Target Comissioning: July-24 - Cost: $0.59M ± 30% | Northern
1784149 | Distribution Feeder Limitation Address capacity and reliability constraints | MORA - Moranbah | Install 100m of UG cable and uprate 0.9km of line on 11kV Town No.5 (417) Feeder - Target Comissioning: Dec-24 - Cost: $0.41M ± 30% | Northern
1786003 | Distribution Feeder Limitation Address reliability and protection constraints | BEGA – Belgian Gardens | Reconductor 0.5km, install ACRs and recover exisitng gas switch on 11kV BEGA-15 Feeder - Target Comissioning: Oct-24 - Cost: $0.34M ± 30% | Northern
1786005 | Distribution Feeder Limitation Address voltage, protection and capacity constraints | STUA – Stuart | Install ACR & LBS on 11kV ST-05 Feeder - Target Comissioning: Nov-24 - Cost: $0.91M ± 30% | Northern
1786006 | Distribution Feeder Limitation Address capacity and reliability constraints | MOBA - Mount Bassett | Reconductor 0.4km of line and install ACR and LBS on 11kV Slade Point (320) Feeder - Target Comissioning: Dec-25 - Cost: $0.3M ± 30% | Northern
1786017 | Distribution Feeder Limitation Address reliability constraints | KOUM - Koumala | Recover existing ABS, install ACRs and LBS on 11kV Mt Christian (242) feeder - Target Comissioning: Sep-24 - Cost: $0.36M ± 30% | Northern
1786019 | Distribution Feeder Limitation Address reliability constraints | PINN - Pinnacle | Install voltage regulators and LBS on 11kV Finchhatton (354) Feeder - Target Comissioning: Sep-24 - Cost: $0.45M ± 30% | Northern
1786208 | Distribution Feeder Limitation Address reliability constraints | TANB - Tanby | Replace ABS & links on 22kV GBRIR (TB212) feeder - Target Comissioning: Mar-25 - Cost: $0.21M ± 30% | Southern
1786209 | Distribution Feeder Limitation Address reliability and protection constraints | EMER - Emerald | Install ACR and LBS on 22kV Hospital Road (EM214) Feeder - Target Comissioning: Dec-24 - Cost: $0.29M ± 30% | Southern
1786210 | Distribution Feeder Limitation Address voltage constraints | COOM – Coominglah | Install regulator and install 1km OHEW on 19.1 kV Hainault (EL-01) SWER - Target Comissioning: Jul-24 - Cost: $0.22M ± 30% | Southern
1787717 | Distribution Feeder Limitation Address capacity and reliability constraints | FREN - Frenchville | Reconductor 0.7km and uprate 0.8km of existing line on 11kV Berserker St (FV104) Feeder - Target Comissioning: Dec-24 - Cost: $0.36M ± 30% | Southern
1787983 | Distribution Feeder Limitation Address voltage constraints | WINT - Winton | Install SWER regulator on 19.1 kV Elderslie SWER (EL-01) feeder - Target Comissioning: Jul-24 - Cost: $0.26M ± 30% | Southern
1788037 | Distribution Feeder Limitation Address capacity and reliability constraints | GLFS - Gladstone Friend St | Reconductor 1.2km and uprate 0.2km of line on 11kV West Gladstone (GF105) Feeder - Target Comissioning: Oct-25 - Cost: $0.34M ± 30% | Southern
1789792 | Distribution Feeder Limitation Address capacity and reliability constraints | EMER - Opal St | Reconductor 0.6km of existing line on 22kV Opal St (EM212) Feeder - Target Comissioning: Nov-24 - Cost: $0.33M ± 30% | Southern
1789933 | Distribution Feeder Limitation Address capacity and reliability constraints | BOHL - Bohle | Install a new feeder tie between the BO-02 and BO-04 11kV feeders, and permanetly reconfigure the network - Target Comissioning: Oct-24 - Cost: $0.32M ± 30% | Northern
1795601 | Distribution Feeder Limitation Address reliability constraints | GOOT – Gootchie | Replace regulators and gas switch on 11kV Glenwood (GC-C) feeder - Target Comissioning: Nov-23 - Cost: $0.41M ± 30% | Southern
1805435 | Distribution Feeder Limitation Address reliability constraints | INNI - Innisfail | Install ACRs and LBS on 22 kV Innisfail No. 1 (2IN1) feeder - Target Comissioning: Nov-24 - Cost: $0.34M ± 30% | Northern
1805894 | Distribution Feeder Limitation Address reliability constraints | INNI - Innisfail | Install ACRs & remote controlled load break switch on 22 kV Innisfail No. 2 (2IN2) feeder - Target Comissioning: Nov-24 - Cost: $0.46M ± 30% | Northern
1807906 | Distribution Feeder Limitation Address reliability constraints | INNI - Innisfail | Install ACRs and LBS on 22 kV Silkwood No. 2 (2SI2) feeder - Target Comissioning: Nov-24 - Cost: $0.34M ± 30% | Northern
1807918 | Distribution Feeder Limitation Address reliability constraints | MARE – Mareeba | Install voltage regulators on 22kV Kuranda Range (2KDA) feeder - Target Comissioning: Sep-24 - Cost: $0.43M ± 30% | Northern
1808067 | Distribution Feeder Limitation Address reliability constraints | MARE – Mareeba | Install ACRs and LBS on 22 kV Mareeba No. 2 (2MA2) and Biboohra (2BIB) feeders - Target Comissioning: Sep-24 - Cost: $0.44M ± 30% | Northern
1808070 | Distribution Feeder Limitation Address reliability constraints | KAMERUNGA – KAME | Construct a feeder tie, install ACR and LBS on 22kV 2CO3 spur tie - Target Comissioning: Sep-24 - Cost: $0.69M ± 30% | Northern
1808092 | Distribution Feeder Limitation Address reliability constraints | DUCH – Duchess Road | Install ACR & remote controlled load break switch on 11 kV Duchess Road No. 12 (DR-12) Feeder - Target Comissioning: Oct-24 - Cost: $0.48M ± 30% | Northern
1808237 | Distribution Feeder Limitation Address capacity and reliability constraints | BERS - Berserker | Reconductor 0.7km of line on 11kV Blanchard St (FB04) Feeder - Target Comissioning: Aug-25 - Cost: $0.32M ± 30% | Southern
1808240 | Distribution Feeder Limitation Address capacity and reliability constraints | BERS - Berserker | Reconductor 0.4km of existing line on 11kV Red Hill (FB16) Feeder - Target Comissioning: Nov-24 - Cost: $0.26M ± 30% | Southern
1808430 | Distribution Feeder Limitation Address capacity and reliability constraints | MOMO – Mount Molloy | Install ACR, reconductor sections of 66kV 2CAB (Carbine) feeder - Target Comissioning: Oct-24 - Cost: $0.83M ± 30% | Northern
1812492 | Distribution Feeder Limitation Address voltage constraints | MOSI – Mount Sibley | Install regulator, uprate 4km of overhead line on 11kV Nobby (F3765) feeder - Target Comissioning: Nov-24 - Cost: $0.22M ± 30% | Southern
1812831 | Distribution Feeder Limitation Address capacity and reliability constraints | LACR - Lakes Creek | Reconductor 0.6km and uprate 3.6km of existing line on 11kV Rockonia Rd (LC107) Feeder - Target Comissioning: Oct-25 - Cost: $0.37M ± 30% | Southern
1812835 | Distribution Feeder Limitation Address capacity and reliability constraints | BLAC - Blackwater | Reconductor 0.7km and uprate 6km of line on 22kV Blackwater Town (BW210) Feeder - Target Comissioning: Oct-25 - Cost: $0.38M ± 30% | Southern
1822714 | Distribution Feeder Limitation Address capacity and reliability constraints | GLFS - Gladstone Friend St | Reconductor 0.5km and uprate 2km of line on 22kV Hospital Tie (GF111) Feeder - Target Comissioning: Dec-25 - Cost: $0.32M ± 30% | Southern
1784148 | Distribution Feeder Limitation Address capacity and reliability constraints | MORA - Moranbah | Reconductor 3.3km and uprate 0.6km of line on 11kV Township No.3 (212) Feeder - Target Comissioning: Nov-24 - Cost: $0.63M ± 30% | Northern
1786004 | Distribution Feeder Limitation Address capacity, protection and reliability constraints | DAGL - Dan Gleeson | Reconductor 1km, uprate 1.3km and install ACR on 11kV Dan Gleeson No.8 (DG-08) Feeder - Target Comissioning: Nov-24 - Cost: $0.42M ± 30% | Northern
1808239 | Distribution Feeder Limitation Address capacity and reliability constraints | BERS - Berserker | Reconductor 0.9km line on 11kV Clifton St (FB15) Feeder - Target Comissioning: Aug-25 - Cost: $0.42M ± 30% | Southern
1812833 | Distribution Feeder Limitation Address capacity and reliability constraints | BEWE - Bedford Weir | Reconductor 1.7km and uprate 16.5km of existing line on 22kV Blackwater (BF202) Feeder - Target Comissioning: Oct-24 - Cost: $0.57M ± 30% | Southern
317031 | Distribution Feeder Limitation Address capacity and reliability constraints | GRAC - Gracemere | New 66/11kV 20MVA substation at an Ergon Engery owned site in Gracemere - Target Comissioning: Jan-24 - Cost: $10.82M ± 30% | Southern