## Disclaimer
Subtransmission Feeder Forecast
(Ergon Energy Distribution Annual Planning Report 2022)
This workbook forms part of the Ergon Energy Distribution Annual Planning Report 2022 (DAPR) and should be read in conjunction with the report document.
Readers are encouraged to take into account the details and content portrayed in the ‘Introduction & Notes’ section of this workbook when reviewing the associated data.
Disclaimer
Ergon Energy’s Distribution Annual Planning Report (DAPR) is prepared and made available solely for information purposes. While care was taken in the preparation of the information in the DAPR, and it is provided in good faith, Ergon Energy accepts no responsibility or liability (including without limitation, liability to any person by reason of negligence or negligent mis-statement) for any loss or damage that may be incurred by any person acting in reliance on this information or assumptions drawn from it, except to the extent that liability under any applicable Queensland or Commonwealth of Australia statute cannot be excluded.
It contains assumptions regarding, among other things, economic growth and load forecasts which may or may not prove to be correct. The forecasts included in the DAPR involve subjective judgements and analysis which are subject to significant uncertainties and contingencies, many of which are out of the control of Ergon Energy. Ergon Energy makes no representation or warranty as to the accuracy, reliability, completeness or suitability for any particular purpose of the information in this document. All information should be independently investigated, reviewed, analysed and verified, and must not be relied upon in connection with any investment proposal or decision. The information contained in the DAPR is subject to annual review. Ergon Energy is obligated to publish future editions by 31st December, in accordance with the National Electricity Rules.
All financials presented in the DAPR or within this document are correct at the time of writing and represent the existing organisational accounting treatment, which may be subject to change. Energy Queensland is finalising the alignment of its Cost Allocation Methodology between Ergon Energy and Energex, potentially impacting the treatment of some Capital and Operational Project costs.

## Introduction & Notes
Subtransmission Feeder Minimum Demand with DER Forecast
(Ergon Energy Distribution Annual Planning Report 2022)
This workbook provides a forecast of Subtransmission Capacity constraints based on EQLs substation minimum demand forecasts.
Process:
For each year in the 5 year forecast period:
1 - Apply the forecast minimum demand profile at each substation
2 - Run a load flow for every half hour period in a 24hr period
3 - Report for each feeder:
the element that has the highest % loading
the corresponding voltage and current information for that element
Note: All modelled embedded generators are in-service in this study
Limitations:
- Each Feeder reports the most constrained element, not the highest loaded element
- Runback schemes or dispatch constraints are not modelled. The results represent unconstrained generation.
- Some generator voltage control schemes are not modelled. Reported voltages may be outside of normal specification.
- 12pm loading was chosen to capture peak generation with minimum load in the majority of locations. In some locations the highest % loading of feeder elements occurs at times of day other than 12pm.
Exclusions:
- Distribution Feeders
- Feeders that supply single Customers
NOTES:
Charleville, Quilpie and Cunnamulla Feeders
The feeders supplying Charleville, Quilpie and Cunnamulla substations have been excluded from this report due to modelling limitations with the SVC for voltage control.
Operational Number Feeder Name
F214R Charleville
F257C Quilpe
F254C Cunnamulla
Woree to Cairns Terminal Feeder
This feeder is nominally owned in source data by Powerlink so is excluded by the data process. A section is owned by Ergon Energy but is not constrained.
Operational Number Feeder Name
7227 WORE - CATE Fdr
Internal Reference:
Minimum Demand Forecast Version:
MinimumDayLoadProfileForecastMediumZoneSubsNoEVs-20220928.csv
Model Version:
TransSubtrans_2022.IntPrj\Versions.IntVersionman\V-3-0-6 Updated Min and CF Chars.IntVersion
profile_type=Minimum Day
poe_marker=MinDay_Med
source=TABL

## MinTimeOfDaySubtransmission
[5 empty] | Year | 2023 |  |  | 2024 |  |  | 2025 |  |  | 2026 |  |  | 2027
[5 empty] | Ratings Period | SD | SE | SNM | SD | SE | SNM | SD | SE | SNM | SD | SE | SNM | SD | SE | SNM
Region | ECORP_ID | Operational Number | Feeder Name | Operational Number | Variable
CA | 40000958 | 6074 | From LCSS to TANB | 6074_Lakes Creek - Tanby 66 kV | % of Rated A | 5.0227 | 5.0261 | 5.0263 | 5.2466 | 5.2501 | 5.25 | 6.9983 | 6.9991 | 6.9989 | 9.2722 | 9.2718 | 9.2727 | 11.6415 | 11.6407 | 11.642
CA | 40000958 | 6074 | From LCSS to TANB | 6074_Lakes Creek - Tanby 66 kV | Limiting Line Name | TR_CABLE 170_1 | TR_CABLE 170_1 | TR_CABLE 170_1 | TR_CABLE 170_1 | TR_CABLE 170_1 | TR_CABLE 170_1 | TR_CABLE 170_1 | TR_CABLE 170_1 | TR_CABLE 170_1 | TR_CABLE 170_1 | TR_CABLE 170_1 | TR_CABLE 170_1 | TR_CABLE 170_1 | TR_CABLE 170_1 | TR_CABLE 170_1
CA | 40000958 | 6074 | From LCSS to TANB | 6074_Lakes Creek - Tanby 66 kV | Loading (A) | 12.1549 | 12.1632 | 12.1636 | 12.6968 | 12.7052 | 12.7051 | 16.9359 | 16.9377 | 16.9374 | 22.4387 | 22.4377 | 22.4399 | 28.1724 | 28.1706 | 28.1735
CA | 40000958 | 6074 | From LCSS to TANB | 6074_Lakes Creek - Tanby 66 kV | Loading (MVA) | 1.4622 | 1.4644 | 1.4645 | 1.5293 | 1.5315 | 1.5315 | 2.0418 | 2.0439 | 2.0438 | 2.7078 | 2.7081 | 2.708 | 3.4021 | 3.4024 | 3.4023
CA | 40000958 | 6074 | From LCSS to TANB | 6074_Lakes Creek - Tanby 66 kV | Loading (MW) | 0.42141 | 0.42126 | 0.42157 | 0.54458 | 0.54487 | 0.54483 | 1.4419 | 1.4422 | 1.4421 | 2.3024 | 2.3025 | 2.3026 | 3.0902 | 3.0903 | 3.0904
CA | 40000958 | 6074 | From LCSS to TANB | 6074_Lakes Creek - Tanby 66 kV | Power Factor | 0.2882 | 0.28767 | 0.28786 | 0.35611 | 0.35578 | 0.35576 | 0.70617 | 0.7056 | 0.70559 | 0.8503 | 0.85022 | 0.85031 | 0.90832 | 0.90828 | 0.90833
CA | 40000958 | 6074 | From LCSS to TANB | 6074_Lakes Creek - Tanby 66 kV | Rating (A) | 242 | 242 | 242 | 242 | 242 | 242 | 242 | 242 | 242 | 242 | 242 | 242 | 242 | 242 | 242
CA | 40000958 | 6074 | From LCSS to TANB | 6074_Lakes Creek - Tanby 66 kV | Time | 16:30 | 18:30 | 5:30 | 16:30 | 21:00 | 22:00 | 16:30 | 21:00 | 22:00 | 10:00 | 17:00 | 7:30 | 10:00 | 17:00 | 8:00
CA | 40000958 | 6074 | From LCSS to TANB | 6074_Lakes Creek - Tanby 66 kV | Voltage at Constrained Conductor | 69.4539 | 69.5114 | 69.5126 | 69.539 | 69.5934 | 69.5936 | 69.6062 | 69.669 | 69.6691 | 69.6712 | 69.6836 | 69.6725 | 69.7208 | 69.7313 | 69.7214
CA | 40000980 | 6047 | Coominglah Sub Tee | 6047_Coominglah Sub Tee 66 kV | % of Rated A | 0.37646 | 0.28072 | 0.29215 | 0.24373 | 0.18048 | 0.18861 | 0.11702 | 0.086661 | 0.090565 | 0.0067395 | 0.0049856 | 0.0052157 | 0.10199 | 0.075848 | 0.078912
CA | 40000980 | 6047 | Coominglah Sub Tee | 6047_Coominglah Sub Tee 66 kV | Limiting Line Name | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1
CA | 40000980 | 6047 | Coominglah Sub Tee | 6047_Coominglah Sub Tee 66 kV | Loading (A) | 0.57975 | 0.5811 | 0.58138 | 0.37535 | 0.37359 | 0.37533 | 0.18022 | 0.17939 | 0.18022 | 0.010379 | 0.01032 | 0.010379 | 0.15706 | 0.157 | 0.15703
CA | 40000980 | 6047 | Coominglah Sub Tee | 6047_Coominglah Sub Tee 66 kV | Loading (MVA) | 0.070215 | 0.070215 | 0.070215 | 0.045182 | 0.045182 | 0.045182 | 0.021716 | 0.021717 | 0.021716 | 0.0012667 | 0.0012524 | 0.0012667 | 0.018959 | 0.018959 | 0.018959
CA | 40000980 | 6047 | Coominglah Sub Tee | 6047_Coominglah Sub Tee 66 kV | Loading (MW) | 0.070206 | 0.070206 | 0.070206 | 0.045167 | 0.045167 | 0.045167 | 0.021682 | 0.021682 | 0.021682 | 3.0049e-05 | 3.0048e-05 | 3.0049e-05 | 0.018919 | 0.018919 | 0.018919
CA | 40000980 | 6047 | Coominglah Sub Tee | 6047_Coominglah Sub Tee 66 kV | Power Factor | 0.99988 | 0.99988 | 0.99988 | 0.99966 | 0.99966 | 0.99966 | 0.99842 | 0.99839 | 0.99842 | 0.023723 | 0.023993 | 0.023721 | 0.9979 | 0.9979 | 0.9979
CA | 40000980 | 6047 | Coominglah Sub Tee | 6047_Coominglah Sub Tee 66 kV | Rating (A) | 154 | 207 | 199 | 154 | 207 | 199 | 154 | 207 | 199 | 154 | 207 | 199 | 154 | 207 | 199
CA | 40000980 | 6047 | Coominglah Sub Tee | 6047_Coominglah Sub Tee 66 kV | Time | 9:30 | 17:30 | 6:30 | 9:30 | 17:30 | 8:30 | 16:00 | 17:30 | 8:00 | 15:30 | 21:30 | 8:00 | 16:30 | 17:00 | 7:00
CA | 40000980 | 6047 | Coominglah Sub Tee | 6047_Coominglah Sub Tee 66 kV | Voltage at Constrained Conductor | 69.9243 | 69.7615 | 69.7285 | 69.498 | 69.825 | 69.5 | 69.5694 | 69.8934 | 69.5669 | 70.4613 | 70.0626 | 70.4635 | 69.6926 | 69.7163 | 69.7031
CA | 40000983 | 6026 | From T27 to THSS | 6026_Moura - Theodore 66 kV | % of Rated A | 3.5637 | 3.3181 | 3.6592 | 3.3547 | 3.1235 | 3.4446 | 3.1783 | 2.9647 | 3.2696 | 3.0331 | 2.8291 | 3.12 | 2.9239 | 2.7272 | 3.0076
CA | 40000983 | 6026 | From T27 to THSS | 6026_Moura - Theodore 66 kV | Limiting Line Name | TR_LINE 59683_1 | TR_LINE 59683_1 | TR_LINE 59683_1 | TR_LINE 59683_1 | TR_LINE 59683_1 | TR_LINE 59683_1 | TR_LINE 59683_1 | TR_LINE 59683_1 | TR_LINE 59683_1 | TR_LINE 59683_1 | TR_LINE 59683_1 | TR_LINE 59683_1 | TR_LINE 59683_1 | TR_LINE 59683_1 | TR_LINE 59683_1
CA | 40000983 | 6026 | From T27 to THSS | 6026_Moura - Theodore 66 kV | Loading (A) | 25.9794 | 25.9806 | 25.9806 | 24.4557 | 24.4568 | 24.4568 | 23.1694 | 23.214 | 23.214 | 22.1112 | 22.152 | 22.152 | 21.3153 | 21.3542 | 21.3541
CA | 40000983 | 6026 | From T27 to THSS | 6026_Moura - Theodore 66 kV | Loading (MVA) | 3.1253 | 3.1252 | 3.1252 | 2.942 | 2.942 | 2.942 | 2.7941 | 2.7925 | 2.7925 | 2.6665 | 2.6647 | 2.6647 | 2.5706 | 2.5688 | 2.5688
CA | 40000983 | 6026 | From T27 to THSS | 6026_Moura - Theodore 66 kV | Loading (MW) | 2.9968 | 2.9968 | 2.9968 | 2.8019 | 2.8019 | 2.8019 | 2.6418 | 2.6418 | 2.6418 | 2.504 | 2.5041 | 2.5041 | 2.3999 | 2.3999 | 2.3999
CA | 40000983 | 6026 | From T27 to THSS | 6026_Moura - Theodore 66 kV | Power Factor | 0.9589 | 0.95891 | 0.95891 | 0.95238 | 0.95239 | 0.95239 | 0.94547 | 0.94604 | 0.94604 | 0.93908 | 0.9397 | 0.9397 | 0.93359 | 0.93426 | 0.93426
CA | 40000983 | 6026 | From T27 to THSS | 6026_Moura - Theodore 66 kV | Rating (A) | 729 | 783 | 710 | 729 | 783 | 710 | 729 | 783 | 710 | 729 | 783 | 710 | 729 | 783 | 710
CA | 40000983 | 6026 | From T27 to THSS | 6026_Moura - Theodore 66 kV | Time | 9:30 | 17:30 | 6:30 | 16:30 | 17:30 | 6:30 | 9:30 | 17:30 | 6:30 | 9:30 | 17:30 | 6:30 | 9:30 | 17:30 | 6:00
CA | 40000983 | 6026 | From T27 to THSS | 6026_Moura - Theodore 66 kV | Voltage at Constrained Conductor | 69.454 | 69.4501 | 69.4501 | 69.4548 | 69.4508 | 69.4508 | 69.6254 | 69.4511 | 69.451 | 69.6244 | 69.4516 | 69.4515 | 69.6284 | 69.4528 | 69.453
CA | 40000986 | 6056 | From EMSS to CMSS | 6056_Comet - Emerald 66 kV | % of Rated A | 106.2592 | 80.5507 | 111.5037 | 108.4866 | 82.695 | 113.8499 | 110.5799 | 84.6791 | 116.0549 | 112.4843 | 86.452 | 118.0607 | 114.2013 | 90.2366 | 119.8692
CA | 40000986 | 6056 | From EMSS to CMSS | 6056_Comet - Emerald 66 kV | Limiting Line Name | TR_LINE 33421_1 | TR_LINE 33421_1 | TR_LINE 33421_1 | TR_LINE 33421_1 | TR_LINE 33421_1 | TR_LINE 33421_1 | TR_LINE 33421_1 | TR_LINE 33421_1 | TR_LINE 33421_1 | TR_LINE 33421_1 | TR_LINE 33421_1 | TR_LINE 33421_1 | TR_LINE 33421_1 | TR_LINE 33421_1 | TR_LINE 33421_1
CA | 40000986 | 6056 | From EMSS to CMSS | 6056_Comet - Emerald 66 kV | Loading (A) | 294.338 | 237.6247 | 293.2548 | 300.5079 | 243.9503 | 299.4253 | 306.3065 | 249.8033 | 305.2244 | 311.5814 | 255.0334 | 310.4996 | 316.3377 | 266.1981 | 315.256
CA | 40000986 | 6056 | From EMSS to CMSS | 6056_Comet - Emerald 66 kV | Loading (MVA) | 34.2 | 27.6086 | 34.0742 | 34.9222 | 28.3483 | 34.7965 | 35.6008 | 29.0327 | 35.4751 | 36.2182 | 29.6445 | 36.0926 | 36.7749 | 30.6119 | 36.6493
CA | 40000986 | 6056 | From EMSS to CMSS | 6056_Comet - Emerald 66 kV | Loading (MW) | 28.9615 | 22.3821 | 28.8351 | 29.6959 | 23.1237 | 29.5693 | 30.3874 | 23.8116 | 30.2607 | 31.0164 | 24.4261 | 30.8895 | 31.5838 | 24.7609 | 31.4568
CA | 40000986 | 6056 | From EMSS to CMSS | 6056_Comet - Emerald 66 kV | Power Factor | 0.84683 | 0.81069 | 0.84624 | 0.85034 | 0.8157 | 0.84978 | 0.85356 | 0.82016 | 0.85301 | 0.85638 | 0.82397 | 0.85584 | 0.85884 | 0.80886 | 0.85832
CA | 40000986 | 6056 | From EMSS to CMSS | 6056_Comet - Emerald 66 kV | Rating (A) | 277 | 295 | 263 | 277 | 295 | 263 | 277 | 295 | 263 | 277 | 295 | 263 | 277 | 295 | 263
CA | 40000986 | 6056 | From EMSS to CMSS | 6056_Comet - Emerald 66 kV | Time | 9:30 | 17:00 | 8:30 | 9:30 | 17:00 | 8:30 | 9:30 | 17:00 | 8:30 | 9:30 | 17:00 | 8:30 | 9:30 | 17:00 | 8:30
CA | 40000986 | 6056 | From EMSS to CMSS | 6056_Comet - Emerald 66 kV | Voltage at Constrained Conductor | 67.084 | 67.0798 | 67.0841 | 67.0942 | 67.0911 | 67.0944 | 67.1031 | 67.101 | 67.1033 | 67.1112 | 67.11 | 67.1114 | 67.1182 | 66.3935 | 67.1184
CA | 40000987 | 6065 | From H15 to TMSS | 6065_Lilyvale - Tieri Tee 66 kV | % of Rated A | 62.0095 | 50.6301 | 61.1256 | 63.5092 | 51.9661 | 62.2267 | 65.7711 | 53.9842 | 64.4427 | 67.9651 | 55.9432 | 66.5923 | 69.7039 | 57.5361 | 68.2958
CA | 40000987 | 6065 | From H15 to TMSS | 6065_Lilyvale - Tieri Tee 66 kV | Limiting Line Name | TR_LINE 155365_1 | TR_LINE 155365_1 | TR_LINE 155365_1 | TR_LINE 155365_1 | TR_LINE 155365_1 | TR_LINE 155365_1 | TR_LINE 155365_1 | TR_LINE 155365_1 | TR_LINE 155365_1 | TR_LINE 155365_1 | TR_LINE 155365_1 | TR_LINE 155365_1 | TR_LINE 155365_1 | TR_LINE 155365_1 | TR_LINE 155365_1
CA | 40000987 | 6065 | From H15 to TMSS | 6065_Lilyvale - Tieri Tee 66 kV | Loading (A) | 150.6704 | 137.6989 | 151.5795 | 154.3151 | 141.3335 | 154.3097 | 159.8119 | 146.8233 | 159.8061 | 165.144 | 152.1523 | 165.1376 | 169.3697 | 156.4856 | 169.3628
CA | 40000987 | 6065 | From H15 to TMSS | 6065_Lilyvale - Tieri Tee 66 kV | Loading (MVA) | 18.43 | 16.6915 | 18.3391 | 18.8728 | 17.13 | 18.8733 | 19.5441 | 17.7953 | 19.5447 | 20.1952 | 18.4409 | 20.1957 | 20.7112 | 18.9427 | 20.7118
CA | 40000987 | 6065 | From H15 to TMSS | 6065_Lilyvale - Tieri Tee 66 kV | Loading (MW) | 17.6451 | 15.6988 | 17.6286 | 18.1186 | 16.1759 | 18.1187 | 18.8348 | 16.8974 | 18.8349 | 19.5302 | 17.598 | 19.5303 | 20.0802 | 18.1501 | 20.0804
CA | 40000987 | 6065 | From H15 to TMSS | 6065_Lilyvale - Tieri Tee 66 kV | Power Factor | 0.95741 | 0.94053 | 0.96126 | 0.96004 | 0.9443 | 0.96002 | 0.96371 | 0.94954 | 0.96369 | 0.96707 | 0.95429 | 0.96705 | 0.96953 | 0.95816 | 0.96952
CA | 40000987 | 6065 | From H15 to TMSS | 6065_Lilyvale - Tieri Tee 66 kV | Rating (A) | 243 | 272 | 248 | 243 | 272 | 248 | 243 | 272 | 248 | 243 | 272 | 248 | 243 | 272 | 248
CA | 40000987 | 6065 | From H15 to TMSS | 6065_Lilyvale - Tieri Tee 66 kV | Time | 9:30 | 17:00 | 7:30 | 9:30 | 17:00 | 8:30 | 9:30 | 17:00 | 8:30 | 9:30 | 17:00 | 8:30 | 9:30 | 17:00 | 8:30
CA | 40000987 | 6065 | From H15 to TMSS | 6065_Lilyvale - Tieri Tee 66 kV | Voltage at Constrained Conductor | 70.6215 | 69.9849 | 69.8519 | 70.6101 | 69.9765 | 70.6145 | 70.6068 | 69.976 | 70.6113 | 70.6033 | 69.9751 | 70.6079 | 70.6008 | 69.8888 | 70.6055
CA | 40000988 | 6067 | Emerald | 6067 Lilyvale - Emerald 66 kV | % of Rated A | 98.7918 | 56.4223 | 77.6493 | 101.2926 | 58.3112 | 79.6231 | 103.4599 | 59.9667 | 81.3336 | 105.5279 | 61.5672 | 82.9661 | 107.3334 | 65.1351 | 84.3914
CA | 40000988 | 6067 | Emerald | 6067 Lilyvale - Emerald 66 kV | Limiting Line Name | TR_LINE 12104746_1 | TR_LINE 12104746_1 | TR_LINE 12104746_1 | TR_LINE 12104746_1 | TR_LINE 12104746_1 | TR_LINE 12104746_1 | TR_LINE 12104746_1 | TR_LINE 12104746_1 | TR_LINE 12104746_1 | TR_LINE 12104746_1 | TR_LINE 12104746_1 | TR_LINE 12104746_1 | TR_LINE 12104746_1 | TR_LINE 12104746_1 | TR_LINE 12104746_1
CA | 40000988 | 6067 | Emerald | 6067 Lilyvale - Emerald 66 kV | Loading (A) | 336.8614 | 254.4436 | 335.4261 | 345.3896 | 262.963 | 343.9533 | 352.7802 | 270.43 | 351.3431 | 359.8325 | 277.6486 | 358.3957 | 365.9898 | 293.7388 | 364.5536
CA | 40000988 | 6067 | Emerald | 6067 Lilyvale - Emerald 66 kV | Loading (MVA) | 38.9484 | 29.4179 | 38.7825 | 39.9343 | 30.403 | 39.7684 | 40.7888 | 31.2664 | 40.6227 | 41.604 | 32.1011 | 41.438 | 42.3158 | 33.5821 | 42.1499
CA | 40000988 | 6067 | Emerald | 6067 Lilyvale - Emerald 66 kV | Loading (MW) | 36.1453 | 26.7764 | 35.9669 | 37.2055 | 27.8273 | 37.0271 | 38.1243 | 28.7481 | 37.946 | 39 | 29.6368 | 38.8218 | 39.7616 | 30.5837 | 39.5835
CA | 40000988 | 6067 | Emerald | 6067 Lilyvale - Emerald 66 kV | Power Factor | 0.92803 | 0.91021 | 0.9274 | 0.93167 | 0.91528 | 0.93107 | 0.93468 | 0.91946 | 0.93411 | 0.93741 | 0.92323 | 0.93686 | 0.93964 | 0.91071 | 0.93911
CA | 40000988 | 6067 | Emerald | 6067 Lilyvale - Emerald 66 kV | Rating (A) | 341 | 451 | 432 | 341 | 451 | 432 | 341 | 451 | 432 | 341 | 451 | 432 | 341 | 451 | 432
CA | 40000988 | 6067 | Emerald | 6067 Lilyvale - Emerald 66 kV | Time | 9:30 | 17:00 | 8:30 | 9:30 | 17:00 | 8:30 | 9:30 | 17:00 | 8:30 | 9:30 | 17:00 | 8:30 | 9:30 | 17:00 | 8:30
CA | 40000988 | 6067 | Emerald | 6067 Lilyvale - Emerald 66 kV | Voltage at Constrained Conductor | 66.754 | 66.7512 | 66.7542 | 66.7539 | 66.7515 | 66.7541 | 66.7537 | 66.7517 | 66.7539 | 66.7535 | 66.7519 | 66.7537 | 66.7533 | 66.0064 | 66.7535
CA | 40000997 | 7153 | Lilyvale - Clermont 132 kV | 7153_Lilyvale - Clermont 132 kV | % of Rated A | 67.4756 | 60.1663 | 74.008 | 67.9643 | 60.6565 | 74.5566 | 68.3595 | 61.0534 | 75.0005 | 68.6835 | 61.3794 | 75.3647 | 68.9745 | 61.67 | 75.6913
CA | 40000997 | 7153 | Lilyvale - Clermont 132 kV | 7153_Lilyvale - Clermont 132 kV | Limiting Line Name | TR_LINE 52803_1 | TR_LINE 52803_1 | TR_LINE 52803_1 | TR_LINE 52803_1 | TR_LINE 52803_1 | TR_LINE 52803_1 | TR_LINE 52803_1 | TR_LINE 52803_1 | TR_LINE 52803_1 | TR_LINE 52803_1 | TR_LINE 52803_1 | TR_LINE 52803_1 | TR_LINE 52803_1 | TR_LINE 52803_1 | TR_LINE 52803_1
CA | 40000997 | 7153 | Lilyvale - Clermont 132 kV | 7153_Lilyvale - Clermont 132 kV | Loading (A) | 477.7269 | 435.6037 | 471.4308 | 481.187 | 439.1529 | 474.9256 | 483.9851 | 442.0266 | 477.753 | 486.2791 | 444.3866 | 480.0729 | 488.3398 | 446.4905 | 482.1538
CA | 40000997 | 7153 | Lilyvale - Clermont 132 kV | 7153_Lilyvale - Clermont 132 kV | Loading (MVA) | 111.4748 | 102.0172 | 110.1363 | 112.229 | 102.804 | 110.9016 | 112.8361 | 103.4386 | 111.518 | 113.3314 | 103.9577 | 112.0215 | 113.7798 | 104.422 | 112.4764
CA | 40000997 | 7153 | Lilyvale - Clermont 132 kV | 7153_Lilyvale - Clermont 132 kV | Loading (MW) | 107.1814 | 97.8376 | 105.9373 | 107.908 | 98.5968 | 106.6758 | 108.4907 | 99.2072 | 107.2686 | 108.964 | 99.7046 | 107.7506 | 109.3972 | 100.1568 | 108.1907
CA | 40000997 | 7153 | Lilyvale - Clermont 132 kV | 7153_Lilyvale - Clermont 132 kV | Power Factor | 0.96149 | 0.95903 | 0.96187 | 0.9615 | 0.95908 | 0.9619 | 0.96149 | 0.95909 | 0.96189 | 0.96146 | 0.95909 | 0.96187 | 0.96148 | 0.95915 | 0.9619
CA | 40000997 | 7153 | Lilyvale - Clermont 132 kV | 7153_Lilyvale - Clermont 132 kV | Rating (A) | 708 | 724 | 637 | 708 | 724 | 637 | 708 | 724 | 637 | 708 | 724 | 637 | 708 | 724 | 637
CA | 40000997 | 7153 | Lilyvale - Clermont 132 kV | 7153_Lilyvale - Clermont 132 kV | Time | 13:30 | 17:00 | 8:30 | 13:30 | 17:00 | 8:30 | 13:30 | 17:00 | 8:30 | 13:30 | 17:00 | 8:30 | 13:30 | 17:00 | 8:30
CA | 40000997 | 7153 | Lilyvale - Clermont 132 kV | 7153_Lilyvale - Clermont 132 kV | Voltage at Constrained Conductor | 134.7213 | 135.2139 | 134.8813 | 134.6575 | 135.1555 | 134.8191 | 134.6033 | 135.1057 | 134.7662 | 134.5564 | 135.0625 | 134.7204 | 134.5187 | 135.0266 | 134.6837
CA | 40001012 | 6011 | From T32 to CMSS | 6011_Blackwater - Comet 66 kV | % of Rated A | 104.8087 | 79.1304 | 109.9749 | 107.0818 | 81.3182 | 112.3693 | 109.2042 | 83.3304 | 114.6048 | 111.1347 | 85.1287 | 116.6382 | 112.865 | 88.895 | 118.4607
CA | 40001012 | 6011 | From T32 to CMSS | 6011_Blackwater - Comet 66 kV | Limiting Line Name | TR_LINE 22145_1 | TR_LINE 22145_1 | TR_LINE 22145_1 | TR_LINE 22145_1 | TR_LINE 22145_1 | TR_LINE 22145_1 | TR_LINE 22145_1 | TR_LINE 22145_1 | TR_LINE 22145_1 | TR_LINE 22145_1 | TR_LINE 22145_1 | TR_LINE 22145_1 | TR_LINE 22145_1 | TR_LINE 22145_1 | TR_LINE 22145_1
CA | 40001012 | 6011 | From T32 to CMSS | 6011_Blackwater - Comet 66 kV | Loading (A) | 290.3175 | 233.4319 | 289.2315 | 296.6141 | 239.8861 | 295.5286 | 302.493 | 245.8221 | 301.4081 | 307.8406 | 251.1269 | 306.7559 | 312.6335 | 262.2374 | 311.549
CA | 40001012 | 6011 | From T32 to CMSS | 6011_Blackwater - Comet 66 kV | Loading (MVA) | 34.0004 | 27.4678 | 33.8766 | 34.7206 | 28.2158 | 34.5971 | 35.3914 | 28.9024 | 35.2681 | 36.0011 | 29.5157 | 35.878 | 36.5467 | 30.6541 | 36.4238
CA | 40001012 | 6011 | From T32 to CMSS | 6011_Blackwater - Comet 66 kV | Loading (MW) | 25.5619 | 20.1223 | 25.4595 | 26.1744 | 20.7658 | 26.0724 | 26.7428 | 21.3544 | 26.6411 | 27.2575 | 21.8781 | 27.1561 | 27.7155 | 21.998 | 27.6144
CA | 40001012 | 6011 | From T32 to CMSS | 6011_Blackwater - Comet 66 kV | Power Factor | 0.75181 | 0.73258 | 0.75154 | 0.75386 | 0.73596 | 0.7536 | 0.75563 | 0.73885 | 0.75539 | 0.75713 | 0.74124 | 0.7569 | 0.75836 | 0.71762 | 0.75814
CA | 40001012 | 6011 | From T32 to CMSS | 6011_Blackwater - Comet 66 kV | Rating (A) | 277 | 295 | 263 | 277 | 295 | 263 | 277 | 295 | 263 | 277 | 295 | 263 | 277 | 295 | 263
CA | 40001012 | 6011 | From T32 to CMSS | 6011_Blackwater - Comet 66 kV | Time | 9:30 | 17:00 | 8:30 | 9:30 | 17:00 | 8:30 | 9:30 | 17:00 | 8:30 | 9:30 | 17:00 | 8:30 | 9:30 | 17:00 | 8:30
CA | 40001012 | 6011 | From T32 to CMSS | 6011_Blackwater - Comet 66 kV | Voltage at Constrained Conductor | 67.6161 | 67.9365 | 67.6229 | 67.5826 | 67.9089 | 67.5895 | 67.5494 | 67.8817 | 67.5564 | 67.5195 | 67.8578 | 67.5266 | 67.492 | 67.4891 | 67.4992
CA | 40001013 | 6012 | From T32 to BFSS | 6012_Blackwater - Bedford Weir 66 kV | % of Rated A | 16.7527 | 15.7039 | 17.6404 | 16.2062 | 15.1917 | 17.065 | 16.0399 | 15.0356 | 16.8898 | 15.5853 | 14.6095 | 16.4112 | 15.2047 | 14.2607 | 16.0104
CA | 40001013 | 6012 | From T32 to BFSS | 6012_Blackwater - Bedford Weir 66 kV | Limiting Line Name | TR_LINE 22153_1 | TR_LINE 22153_1 | TR_LINE 22153_1 | TR_LINE 22153_1 | TR_LINE 22153_1 | TR_LINE 22153_1 | TR_LINE 22153_1 | TR_LINE 22153_1 | TR_LINE 22153_1 | TR_LINE 22153_1 | TR_LINE 22153_1 | TR_LINE 22153_1 | TR_LINE 22153_1 | TR_LINE 22153_1 | TR_LINE 22153_1
CA | 40001013 | 6012 | From T32 to BFSS | 6012_Blackwater - Bedford Weir 66 kV | Loading (A) | 46.5724 | 46.4835 | 46.5707 | 45.0532 | 44.9673 | 45.0515 | 44.5908 | 44.5054 | 44.5891 | 43.3272 | 43.2441 | 43.3255 | 42.269 | 42.2116 | 42.2674
CA | 40001013 | 6012 | From T32 to BFSS | 6012_Blackwater - Bedford Weir 66 kV | Loading (MVA) | 5.5693 | 5.5699 | 5.5693 | 5.3864 | 5.3871 | 5.3864 | 5.3299 | 5.3305 | 5.3299 | 5.1778 | 5.1786 | 5.1778 | 5.0505 | 5.0511 | 5.0506
CA | 40001013 | 6012 | From T32 to BFSS | 6012_Blackwater - Bedford Weir 66 kV | Loading (MW) | 5.4823 | 5.4821 | 5.4823 | 5.2953 | 5.2951 | 5.2953 | 5.2377 | 5.2375 | 5.2377 | 5.0821 | 5.0819 | 5.0821 | 4.9517 | 4.9515 | 4.9516
CA | 40001013 | 6012 | From T32 to BFSS | 6012_Blackwater - Bedford Weir 66 kV | Power Factor | 0.98438 | 0.98423 | 0.98438 | 0.98309 | 0.98293 | 0.98309 | 0.98271 | 0.98254 | 0.98271 | 0.98151 | 0.98133 | 0.9815 | 0.98042 | 0.98028 | 0.98042
CA | 40001013 | 6012 | From T32 to BFSS | 6012_Blackwater - Bedford Weir 66 kV | Rating (A) | 278 | 296 | 264 | 278 | 296 | 264 | 278 | 296 | 264 | 278 | 296 | 264 | 278 | 296 | 264
CA | 40001013 | 6012 | From T32 to BFSS | 6012_Blackwater - Bedford Weir 66 kV | Time | 9:30 | 17:00 | 8:30 | 9:30 | 17:00 | 8:30 | 9:30 | 17:00 | 8:30 | 9:30 | 17:00 | 8:30 | 9:30 | 17:00 | 8:30
CA | 40001013 | 6012 | From T32 to BFSS | 6012_Blackwater - Bedford Weir 66 kV | Voltage at Constrained Conductor | 69.0419 | 69.1818 | 69.0446 | 69.0257 | 69.1661 | 69.0284 | 69.0097 | 69.151 | 69.0125 | 68.9965 | 69.1386 | 68.9993 | 68.9851 | 69.0864 | 68.988
CA | 40001019 | 6058 | From BFSS to BGSS | 6058_Bedford Weir - Bingegang 66 kV | % of Rated A | 11.6471 | 10.9181 | 12.2642 | 11.5577 | 10.8343 | 12.1701 | 11.79 | 11.0519 | 12.4148 | 11.7405 | 11.0054 | 12.3627 | 11.7089 | 10.9818 | 12.3293
CA | 40001019 | 6058 | From BFSS to BGSS | 6058_Bedford Weir - Bingegang 66 kV | Limiting Line Name | TR_LINE 22154_1 | TR_LINE 22154_1 | TR_LINE 22154_1 | TR_LINE 22154_1 | TR_LINE 22154_1 | TR_LINE 22154_1 | TR_LINE 22154_1 | TR_LINE 22154_1 | TR_LINE 22154_1 | TR_LINE 22154_1 | TR_LINE 22154_1 | TR_LINE 22154_1 | TR_LINE 22154_1 | TR_LINE 22154_1 | TR_LINE 22154_1
CA | 40001019 | 6058 | From BFSS to BGSS | 6058_Bedford Weir - Bingegang 66 kV | Loading (A) | 32.3788 | 32.3176 | 32.3776 | 32.1304 | 32.0695 | 32.1292 | 32.7763 | 32.7137 | 32.7751 | 32.6387 | 32.576 | 32.6375 | 32.5507 | 32.5061 | 32.5494
CA | 40001019 | 6058 | From BFSS to BGSS | 6058_Bedford Weir - Bingegang 66 kV | Loading (MVA) | 3.854 | 3.8546 | 3.854 | 3.8243 | 3.8249 | 3.8243 | 3.9005 | 3.9012 | 3.9006 | 3.8841 | 3.8847 | 3.8841 | 3.8736 | 3.874 | 3.8736
CA | 40001019 | 6058 | From BFSS to BGSS | 6058_Bedford Weir - Bingegang 66 kV | Loading (MW) | 3.7753 | 3.7752 | 3.7753 | 3.7449 | 3.7448 | 3.7449 | 3.8231 | 3.823 | 3.8231 | 3.8063 | 3.8062 | 3.8063 | 3.7955 | 3.7954 | 3.7955
CA | 40001019 | 6058 | From BFSS to BGSS | 6058_Bedford Weir - Bingegang 66 kV | Power Factor | 0.9796 | 0.97942 | 0.9796 | 0.97924 | 0.97906 | 0.97924 | 0.98016 | 0.97998 | 0.98015 | 0.97997 | 0.97979 | 0.97996 | 0.97985 | 0.97972 | 0.97984
CA | 40001019 | 6058 | From BFSS to BGSS | 6058_Bedford Weir - Bingegang 66 kV | Rating (A) | 278 | 296 | 264 | 278 | 296 | 264 | 278 | 296 | 264 | 278 | 296 | 264 | 278 | 296 | 264
CA | 40001019 | 6058 | From BFSS to BGSS | 6058_Bedford Weir - Bingegang 66 kV | Time | 9:30 | 17:00 | 8:30 | 9:30 | 17:00 | 8:30 | 9:30 | 17:00 | 8:30 | 9:30 | 17:00 | 8:30 | 9:30 | 17:00 | 8:30
CA | 40001019 | 6058 | From BFSS to BGSS | 6058_Bedford Weir - Bingegang 66 kV | Voltage at Constrained Conductor | 68.7205 | 68.8616 | 68.7233 | 68.7191 | 68.8607 | 68.7219 | 68.7075 | 68.8499 | 68.7103 | 68.7066 | 68.8498 | 68.7094 | 68.7055 | 68.8075 | 68.7083
CA | 40001027 | 6085 | From TMSS to TISS | 6085_Tieri Tee - Tieri 66 kV | % of Rated A | 2.5939 | 2.3406 | 2.5671 | 2.5555 | 2.3064 | 2.5296 | 2.5275 | 2.2805 | 2.5012 | 2.472 | 2.252 | 2.4699 | 2.4506 | 2.2318 | 2.4477
CA | 40001027 | 6085 | From TMSS to TISS | 6085_Tieri Tee - Tieri 66 kV | Limiting Line Name | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1
CA | 40001027 | 6085 | From TMSS to TISS | 6085_Tieri Tee - Tieri 66 kV | Loading (A) | 6.3031 | 6.3664 | 6.3664 | 6.2098 | 6.2735 | 6.2735 | 6.1419 | 6.2029 | 6.2029 | 6.0071 | 6.1253 | 6.1253 | 5.9551 | 6.0704 | 6.0704
CA | 40001027 | 6085 | From TMSS to TISS | 6085_Tieri Tee - Tieri 66 kV | Loading (MVA) | 0.76209 | 0.7617 | 0.7617 | 0.75108 | 0.75068 | 0.75068 | 0.74284 | 0.74244 | 0.74244 | 0.73418 | 0.73337 | 0.73337 | 0.72779 | 0.72699 | 0.72699
CA | 40001027 | 6085 | From TMSS to TISS | 6085_Tieri Tee - Tieri 66 kV | Loading (MW) | 0.75285 | 0.75285 | 0.75285 | 0.74167 | 0.74168 | 0.74168 | 0.73331 | 0.73331 | 0.73331 | 0.72409 | 0.7241 | 0.7241 | 0.7176 | 0.71761 | 0.71761
CA | 40001027 | 6085 | From TMSS to TISS | 6085_Tieri Tee - Tieri 66 kV | Power Factor | 0.98788 | 0.98838 | 0.98838 | 0.98747 | 0.98801 | 0.98801 | 0.98717 | 0.9877 | 0.9877 | 0.98626 | 0.98736 | 0.98736 | 0.986 | 0.9871 | 0.9871
CA | 40001027 | 6085 | From TMSS to TISS | 6085_Tieri Tee - Tieri 66 kV | Rating (A) | 243 | 272 | 248 | 243 | 272 | 248 | 243 | 272 | 248 | 243 | 272 | 248 | 243 | 272 | 248
CA | 40001027 | 6085 | From TMSS to TISS | 6085_Tieri Tee - Tieri 66 kV | Time | 16:00 | 20:00 | 22:00 | 16:30 | 20:00 | 22:00 | 16:30 | 20:00 | 22:00 | 9:30 | 20:00 | 22:00 | 9:30 | 20:00 | 22:00
CA | 40001027 | 6085 | From TMSS to TISS | 6085_Tieri Tee - Tieri 66 kV | Voltage at Constrained Conductor | 69.8054 | 69.0767 | 69.0767 | 69.8316 | 69.0851 | 69.0851 | 69.828 | 69.1052 | 69.1052 | 70.5632 | 69.1251 | 69.1251 | 70.56 | 69.1434 | 69.1434
CA | 40001028 | 6086 | From TMSS to MDSS | 6086_Tieri Tee - Middlemount 66 kV | % of Rated A | 79.9222 | 66.5578 | 78.9564 | 81.453 | 67.9338 | 79.807 | 83.7548 | 70.005 | 82.0623 | 86.3004 | 72.2949 | 84.5562 | 88.0676 | 73.9532 | 86.2876
CA | 40001028 | 6086 | From TMSS to MDSS | 6086_Tieri Tee - Middlemount 66 kV | Limiting Line Name | TR_LINE 17095_3 | TR_LINE 17095_3 | TR_LINE 17095_3 | TR_LINE 17095_3 | TR_LINE 17095_3 | TR_LINE 17095_3 | TR_LINE 17095_3 | TR_LINE 17095_3 | TR_LINE 17095_3 | TR_LINE 17095_3 | TR_LINE 17095_3 | TR_LINE 17095_3 | TR_LINE 17095_3 | TR_LINE 17095_3 | TR_LINE 17095_3
CA | 40001028 | 6086 | From TMSS to MDSS | 6086_Tieri Tee - Middlemount 66 kV | Loading (A) | 194.0935 | 180.9074 | 195.6998 | 197.815 | 184.6525 | 197.8057 | 203.4112 | 190.2894 | 203.4014 | 209.6 | 196.5216 | 209.5895 | 213.8964 | 201.0351 | 213.8853
CA | 40001028 | 6086 | From TMSS to MDSS | 6086_Tieri Tee - Middlemount 66 kV | Loading (MVA) | 25.2299 | 23.2468 | 25.1726 | 25.7358 | 23.7503 | 25.7361 | 26.5027 | 24.5135 | 26.503 | 27.3478 | 25.3544 | 27.3481 | 27.9385 | 25.936 | 27.9388
CA | 40001028 | 6086 | From TMSS to MDSS | 6086_Tieri Tee - Middlemount 66 kV | Loading (MW) | 24.5329 | 22.4467 | 24.5283 | 25.0479 | 22.9617 | 25.0479 | 25.8283 | 23.7424 | 25.8283 | 26.6903 | 24.6046 | 26.6903 | 27.2928 | 25.2068 | 27.2928
CA | 40001028 | 6086 | From TMSS to MDSS | 6086_Tieri Tee - Middlemount 66 kV | Power Factor | 0.97238 | 0.96558 | 0.97441 | 0.97327 | 0.9668 | 0.97326 | 0.97455 | 0.96854 | 0.97454 | 0.97596 | 0.97042 | 0.97595 | 0.97689 | 0.97188 | 0.97688
CA | 40001028 | 6086 | From TMSS to MDSS | 6086_Tieri Tee - Middlemount 66 kV | Rating (A) | 243 | 272 | 248 | 243 | 272 | 248 | 243 | 272 | 248 | 243 | 272 | 248 | 243 | 272 | 248
CA | 40001028 | 6086 | From TMSS to MDSS | 6086_Tieri Tee - Middlemount 66 kV | Time | 9:30 | 17:00 | 7:30 | 9:30 | 17:00 | 8:30 | 9:30 | 17:00 | 8:30 | 9:30 | 17:00 | 8:30 | 9:30 | 17:00 | 8:30
CA | 40001028 | 6086 | From TMSS to MDSS | 6086_Tieri Tee - Middlemount 66 kV | Voltage at Constrained Conductor | 75.0487 | 74.1903 | 74.2638 | 75.1134 | 74.2598 | 75.1179 | 75.2236 | 74.3754 | 75.2282 | 75.3304 | 74.4874 | 75.3351 | 75.4116 | 74.4854 | 75.4164
CA | 40001036 | 6019 | From GFSS to T19 | 6019_Gladstone South - Friend St 66 kV | % of Rated A | 26.5412 | 24.1504 | 29.0524 | 24.6489 | 22.6884 | 27.2994 | 22.6739 | 21.1935 | 25.5097 | 20.7092 | 19.7163 | 23.7358 | 18.9065 | 18.3592 | 22.1067
CA | 40001036 | 6019 | From GFSS to T19 | 6019_Gladstone South - Friend St 66 kV | Limiting Line Name | TR_LINE 22252_1 | TR_LINE 21764_1 | TR_LINE 21764_1 | TR_LINE 22252_1 | TR_LINE 21764_1 | TR_LINE 21764_1 | TR_LINE 22252_1 | TR_LINE 21764_1 | TR_LINE 21764_1 | TR_LINE 22252_1 | TR_LINE 21764_1 | TR_LINE 21764_1 | TR_LINE 22252_1 | TR_LINE 21764_1 | TR_LINE 21764_1
CA | 40001036 | 6019 | From GFSS to T19 | 6019_Gladstone South - Friend St 66 kV | Loading (A) | 65.026 | 82.5921 | 82.7972 | 60.3898 | 77.5921 | 77.8008 | 55.5509 | 72.4795 | 72.7002 | 50.7375 | 67.4298 | 67.647 | 46.3209 | 62.7884 | 63.0041
CA | 40001036 | 6019 | From GFSS to T19 | 6019_Gladstone South - Friend St 66 kV | Loading (MVA) | 7.793 | 9.8653 | 9.8963 | 7.239 | 9.2707 | 9.3049 | 6.6598 | 8.673 | 8.6998 | 6.0845 | 8.0701 | 8.0964 | 5.5547 | 7.5151 | 7.5412
CA | 40001036 | 6019 | From GFSS to T19 | 6019_Gladstone South - Friend St 66 kV | Loading (MW) | 7.7307 | 8.991 | 9.0166 | 7.1479 | 8.4097 | 8.4365 | 6.5354 | 7.8009 | 7.8275 | 5.921 | 7.1872 | 7.2136 | 5.3467 | 6.6145 | 6.6409
CA | 40001036 | 6019 | From GFSS to T19 | 6019_Gladstone South - Friend St 66 kV | Power Factor | 0.99201 | 0.91138 | 0.9111 | 0.98741 | 0.90712 | 0.90667 | 0.98133 | 0.89945 | 0.89974 | 0.97313 | 0.8906 | 0.89097 | 0.96254 | 0.88017 | 0.88062
CA | 40001036 | 6019 | From GFSS to T19 | 6019_Gladstone South - Friend St 66 kV | Rating (A) | 245 | 342 | 285 | 245 | 342 | 285 | 245 | 342 | 285 | 245 | 342 | 285 | 245 | 342 | 285
CA | 40001036 | 6019 | From GFSS to T19 | 6019_Gladstone South - Friend St 66 kV | Time | 15:30 | 17:30 | 4:00 | 15:30 | 17:30 | 4:00 | 15:30 | 19:00 | 4:00 | 15:30 | 19:00 | 4:00 | 15:30 | 19:00 | 4:00
CA | 40001036 | 6019 | From GFSS to T19 | 6019_Gladstone South - Friend St 66 kV | Voltage at Constrained Conductor | 69.1922 | 68.9621 | 69.0078 | 69.2075 | 68.982 | 69.0504 | 69.2159 | 69.0865 | 69.0894 | 69.2364 | 69.0979 | 69.1007 | 69.2351 | 69.1022 | 69.105
CA | 40001047 | 6020 | GLSO - BORT 6020 | 6020_Gladstone South - BORE 66 kV | % of Rated A | 7.6856 | 5.4937 | 6.7632 | 10.0285 | 7.172 | 8.7742 | 12.2419 | 8.7577 | 10.676 | 14.3528 | 10.2719 | 12.4937 | 16.2836 | 11.6535 | 14.1555
CA | 40001047 | 6020 | GLSO - BORT 6020 | 6020_Gladstone South - BORE 66 kV | Limiting Line Name | TR_LINE 215689_1 | TR_LINE 215689_1 | TR_LINE 215689_1 | TR_LINE 215689_1 | TR_LINE 215689_1 | TR_LINE 215689_1 | TR_LINE 215689_1 | TR_LINE 215689_1 | TR_LINE 215689_1 | TR_LINE 215689_1 | TR_LINE 215689_1 | TR_LINE 215689_1 | TR_LINE 215689_1 | TR_LINE 215689_1 | TR_LINE 215689_1
CA | 40001047 | 6020 | GLSO - BORT 6020 | 6020_Gladstone South - BORE 66 kV | Loading (A) | 16.2165 | 16.2064 | 16.5698 | 21.1602 | 21.1575 | 21.4969 | 25.8304 | 25.8352 | 26.1562 | 30.2845 | 30.3022 | 30.6096 | 34.3584 | 34.3778 | 34.681
CA | 40001047 | 6020 | GLSO - BORT 6020 | 6020_Gladstone South - BORE 66 kV | Loading (MVA) | 1.9451 | 1.9395 | 1.9843 | 2.539 | 2.533 | 2.5762 | 3.1002 | 3.0939 | 3.1366 | 3.6363 | 3.6297 | 3.6717 | 4.1259 | 4.1184 | 4.1606
CA | 40001047 | 6020 | GLSO - BORT 6020 | 6020_Gladstone South - BORE 66 kV | Loading (MW) | 1.7698 | 1.7629 | 1.8016 | 2.4268 | 2.4199 | 2.4582 | 3.0228 | 3.0159 | 3.0544 | 3.5811 | 3.5741 | 3.6126 | 4.0853 | 4.0778 | 4.1168
CA | 40001047 | 6020 | GLSO - BORT 6020 | 6020_Gladstone South - BORE 66 kV | Power Factor | 0.90989 | 0.90892 | 0.90793 | 0.95581 | 0.95534 | 0.95419 | 0.97505 | 0.97479 | 0.97379 | 0.98481 | 0.98467 | 0.9839 | 0.99017 | 0.99014 | 0.98948
CA | 40001047 | 6020 | GLSO - BORT 6020 | 6020_Gladstone South - BORE 66 kV | Rating (A) | 211 | 295 | 245 | 211 | 295 | 245 | 211 | 295 | 245 | 211 | 295 | 245 | 211 | 295 | 245
CA | 40001047 | 6020 | GLSO - BORT 6020 | 6020_Gladstone South - BORE 66 kV | Time | 15:30 | 17:30 | 4:00 | 15:30 | 17:30 | 4:00 | 15:30 | 17:30 | 4:00 | 15:30 | 17:30 | 4:00 | 15:30 | 17:30 | 4:00
CA | 40001047 | 6020 | GLSO - BORT 6020 | 6020_Gladstone South - BORE 66 kV | Voltage at Constrained Conductor | 69.2499 | 69.0942 | 69.1416 | 69.2759 | 69.121 | 69.1909 | 69.294 | 69.1416 | 69.2357 | 69.3235 | 69.158 | 69.2544 | 69.3303 | 69.1649 | 69.2631
CA | 40001055 | 6079 | From T72 to LRSS | 6079_Barcaldine - Longreach 66 kV | % of Rated A | 95.9956 | 80.7065 | 91.793 | 99.4019 | 84.1306 | 95.2053 | 102.3037 | 87.0469 | 98.1119 | 104.8556 | 89.6111 | 100.6676 | 106.8938 | 91.6587 | 102.7088
CA | 40001055 | 6079 | From T72 to LRSS | 6079_Barcaldine - Longreach 66 kV | Limiting Line Name | TR_CABLE 562_1 | TR_CABLE 562_1 | TR_CABLE 562_1 | TR_CABLE 562_1 | TR_CABLE 562_1 | TR_CABLE 562_1 | TR_CABLE 562_1 | TR_CABLE 562_1 | TR_CABLE 562_1 | TR_CABLE 562_1 | TR_CABLE 562_1 | TR_CABLE 562_1 | TR_CABLE 562_1 | TR_CABLE 562_1 | TR_CABLE 562_1
CA | 40001055 | 6079 | From T72 to LRSS | 6079_Barcaldine - Longreach 66 kV | Loading (A) | 95.9956 | 80.7065 | 91.793 | 99.4019 | 84.1306 | 95.2054 | 102.3037 | 87.0469 | 98.1119 | 104.8556 | 89.6111 | 100.6676 | 106.8938 | 91.6587 | 102.7088
CA | 40001055 | 6079 | From T72 to LRSS | 6079_Barcaldine - Longreach 66 kV | Loading (MVA) | 10.904 | 9.2425 | 10.4591 | 11.2803 | 9.6267 | 10.8382 | 11.6001 | 9.9533 | 11.1603 | 11.8808 | 10.24 | 11.4431 | 12.1046 | 10.4686 | 11.6686
CA | 40001055 | 6079 | From T72 to LRSS | 6079_Barcaldine - Longreach 66 kV | Loading (MW) | 10.7432 | 9.0826 | 10.2837 | 11.1028 | 9.4482 | 10.6449 | 11.4082 | 9.7587 | 10.9517 | 11.6761 | 10.031 | 11.2208 | 11.8896 | 10.248 | 11.4352
CA | 40001055 | 6079 | From T72 to LRSS | 6079_Barcaldine - Longreach 66 kV | Power Factor | 0.98525 | 0.98271 | 0.98323 | 0.98427 | 0.98146 | 0.98217 | 0.98346 | 0.98045 | 0.9813 | 0.98277 | 0.97959 | 0.98057 | 0.98224 | 0.97893 | 0.98
CA | 40001055 | 6079 | From T72 to LRSS | 6079_Barcaldine - Longreach 66 kV | Rating (A) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
CA | 40001055 | 6079 | From T72 to LRSS | 6079_Barcaldine - Longreach 66 kV | Time | 14:00 | 17:00 | 8:30 | 14:00 | 17:00 | 8:30 | 14:00 | 17:00 | 8:30 | 14:00 | 17:00 | 8:30 | 14:00 | 17:00 | 8:30
CA | 40001055 | 6079 | From T72 to LRSS | 6079_Barcaldine - Longreach 66 kV | Voltage at Constrained Conductor | 65.5803 | 66.1179 | 65.7846 | 65.5184 | 66.0637 | 65.7255 | 65.4648 | 66.0166 | 65.6743 | 65.4172 | 65.9746 | 65.6287 | 65.3788 | 65.9406 | 65.592
CA | 40001056 | 7154 | Barcaldine | 7154_Clermont - Barcaldine 132 kV | % of Rated A | 74.4873 | 62.9366 | 74.0441 | 75.4056 | 63.78 | 74.9843 | 76.1823 | 64.4932 | 75.7794 | 76.8513 | 65.1074 | 76.4642 | 77.3724 | 65.5854 | 76.9977
CA | 40001056 | 7154 | Barcaldine | 7154_Clermont - Barcaldine 132 kV | Limiting Line Name | TR_LINE 52321_1 | TR_LINE 52321_1 | TR_LINE 52321_1 | TR_LINE 52321_1 | TR_LINE 52321_1 | TR_LINE 52321_1 | TR_LINE 52321_1 | TR_LINE 52321_1 | TR_LINE 52321_1 | TR_LINE 52321_1 | TR_LINE 52321_1 | TR_LINE 52321_1 | TR_LINE 52321_1 | TR_LINE 52321_1 | TR_LINE 52321_1
CA | 40001056 | 7154 | Barcaldine | 7154_Clermont - Barcaldine 132 kV | Loading (A) | 268.1542 | 246.0821 | 259.8948 | 271.4603 | 249.3799 | 263.1948 | 274.2564 | 252.1684 | 265.9858 | 276.6646 | 254.5698 | 268.3894 | 278.5407 | 256.439 | 270.2619
CA | 40001056 | 7154 | Barcaldine | 7154_Clermont - Barcaldine 132 kV | Loading (MVA) | 61.476 | 56.6476 | 59.6756 | 62.2085 | 57.3886 | 60.4107 | 62.8268 | 58.014 | 61.0312 | 63.3582 | 58.5517 | 61.5645 | 63.7712 | 58.9693 | 61.9792
CA | 40001056 | 7154 | Barcaldine | 7154_Clermont - Barcaldine 132 kV | Loading (MW) | 57.1991 | 52.017 | 55.2753 | 57.9912 | 52.8166 | 56.0697 | 58.6596 | 53.4915 | 56.74 | 59.234 | 54.0714 | 57.316 | 59.6807 | 54.5226 | 57.764
CA | 40001056 | 7154 | Barcaldine | 7154_Clermont - Barcaldine 132 kV | Power Factor | 0.93043 | 0.91826 | 0.92626 | 0.93221 | 0.92033 | 0.92814 | 0.93367 | 0.92204 | 0.92969 | 0.93491 | 0.92348 | 0.93099 | 0.93586 | 0.92459 | 0.93199
CA | 40001056 | 7154 | Barcaldine | 7154_Clermont - Barcaldine 132 kV | Rating (A) | 360 | 391 | 351 | 360 | 391 | 351 | 360 | 391 | 351 | 360 | 391 | 351 | 360 | 391 | 351
CA | 40001056 | 7154 | Barcaldine | 7154_Clermont - Barcaldine 132 kV | Time | 13:30 | 17:00 | 8:30 | 13:30 | 17:00 | 8:30 | 13:30 | 17:00 | 8:30 | 13:30 | 17:00 | 8:30 | 13:30 | 17:00 | 8:30
CA | 40001056 | 7154 | Barcaldine | 7154_Clermont - Barcaldine 132 kV | Voltage at Constrained Conductor | 132.3611 | 132.9049 | 132.568 | 132.3071 | 132.8628 | 132.5184 | 132.2597 | 132.8256 | 132.4747 | 132.2173 | 132.792 | 132.4356 | 132.1829 | 132.7643 | 132.4037
CA | 40001070 | 6023 | From GFSS to CISS | 6023_Friend St-Clinton Industrial 66 kV | % of Rated A | 9.8275 | 17.9344 | 22.1349 | 10.316 | 18.3395 | 22.6482 | 11.1232 | 18.8807 | 23.3335 | 12.1832 | 19.5592 | 24.1739 | 13.2848 | 20.2698 | 25.0535
CA | 40001070 | 6023 | From GFSS to CISS | 6023_Friend St-Clinton Industrial 66 kV | Limiting Line Name | TR_LINE 22245_1 | TR_LINE 22245_1 | TR_LINE 22275_1 | TR_LINE 22245_1 | TR_LINE 22245_1 | TR_LINE 22275_1 | TR_LINE 22245_1 | TR_LINE 22245_1 | TR_LINE 22275_1 | TR_LINE 22245_1 | TR_LINE 22275_1 | TR_LINE 22275_1 | TR_LINE 22245_1 | TR_LINE 22275_1 | TR_LINE 22275_1
CA | 40001070 | 6023 | From GFSS to CISS | 6023_Friend St-Clinton Industrial 66 kV | Loading (A) | 43.3394 | 86.6232 | 86.1049 | 45.4938 | 88.5796 | 88.1015 | 49.0533 | 91.194 | 90.7672 | 53.7279 | 93.878 | 94.03 | 58.5858 | 97.2889 | 97.4521
CA | 40001070 | 6023 | From GFSS to CISS | 6023_Friend St-Clinton Industrial 66 kV | Loading (MVA) | 5.1744 | 10.2794 | 10.2719 | 5.4325 | 10.5129 | 10.5145 | 5.8577 | 10.8255 | 10.8377 | 6.418 | 11.213 | 11.2316 | 6.9973 | 11.6225 | 11.6424
CA | 40001070 | 6023 | From GFSS to CISS | 6023_Friend St-Clinton Industrial 66 kV | Loading (MW) | 0.88546 | 2.1252 | 2.1779 | 2.1256 | 3.3659 | 3.4199 | 3.2046 | 4.4469 | 4.5048 | 4.2464 | 5.5229 | 5.5493 | 5.1692 | 6.4495 | 6.4759
CA | 40001070 | 6023 | From GFSS to CISS | 6023_Friend St-Clinton Industrial 66 kV | Power Factor | 0.17112 | 0.20674 | 0.21202 | 0.39127 | 0.32017 | 0.32525 | 0.54707 | 0.41078 | 0.41566 | 0.66164 | 0.49255 | 0.49408 | 0.73875 | 0.55492 | 0.55623
CA | 40001070 | 6023 | From GFSS to CISS | 6023_Friend St-Clinton Industrial 66 kV | Rating (A) | 441 | 483 | 389 | 441 | 483 | 389 | 441 | 483 | 389 | 441 | 480 | 389 | 441 | 480 | 389
CA | 40001070 | 6023 | From GFSS to CISS | 6023_Friend St-Clinton Industrial 66 kV | Time | 16:30 | 18:30 | 5:30 | 16:30 | 18:30 | 5:30 | 16:30 | 19:00 | 4:00 | 16:30 | 19:00 | 4:00 | 16:30 | 19:00 | 4:00
CA | 40001070 | 6023 | From GFSS to CISS | 6023_Friend St-Clinton Industrial 66 kV | Voltage at Constrained Conductor | 68.932 | 68.5127 | 68.8752 | 68.9424 | 68.5217 | 68.9039 | 68.9445 | 68.5363 | 68.936 | 68.9666 | 68.9602 | 68.9626 | 68.9567 | 68.9722 | 68.9745
CA | 40001073 | 6001 | From T23 to PHSS | 6001_Glenmore - Parkhurst 66 kV | % of Rated A | 6.4111 | 6.147 | 6.9088 | 5.9685 | 5.7222 | 6.4317 | 5.5858 | 5.3553 | 6.0193 | 5.1969 | 4.9822 | 5.6 | 4.8041 | 4.6095 | 5.1804
CA | 40001073 | 6001 | From T23 to PHSS | 6001_Glenmore - Parkhurst 66 kV | Limiting Line Name | TR_LINE 22133_1 | TR_LINE 22133_1 | TR_LINE 22133_1 | TR_LINE 22133_1 | TR_LINE 22133_1 | TR_LINE 22133_1 | TR_LINE 22133_1 | TR_LINE 22133_1 | TR_LINE 22133_1 | TR_LINE 22133_1 | TR_LINE 22133_1 | TR_LINE 22133_1 | TR_LINE 22133_1 | TR_LINE 22133_1 | TR_LINE 22133_1
CA | 40001073 | 6001 | From T23 to PHSS | 6001_Glenmore - Parkhurst 66 kV | Loading (A) | 25.7085 | 25.6943 | 25.7008 | 23.9335 | 23.9189 | 23.926 | 22.3992 | 22.385 | 22.3917 | 20.8395 | 20.8257 | 20.832 | 19.2645 | 19.2677 | 19.2711
CA | 40001073 | 6001 | From T23 to PHSS | 6001_Glenmore - Parkhurst 66 kV | Loading (MVA) | 3.0829 | 3.0816 | 3.0819 | 2.8721 | 2.8708 | 2.8712 | 2.6895 | 2.6883 | 2.6886 | 2.5038 | 2.5026 | 2.5029 | 2.3154 | 2.3167 | 2.3181
CA | 40001073 | 6001 | From T23 to PHSS | 6001_Glenmore - Parkhurst 66 kV | Loading (MW) | 2.9069 | 2.9053 | 2.9059 | 2.6922 | 2.6906 | 2.6911 | 2.5066 | 2.505 | 2.5055 | 2.3201 | 2.3185 | 2.319 | 2.1269 | 2.1249 | 2.1264
CA | 40001073 | 6001 | From T23 to PHSS | 6001_Glenmore - Parkhurst 66 kV | Power Factor | 0.94294 | 0.94281 | 0.94287 | 0.93738 | 0.93722 | 0.9373 | 0.93199 | 0.93181 | 0.9319 | 0.92664 | 0.92644 | 0.92653 | 0.91861 | 0.91724 | 0.91733
CA | 40001073 | 6001 | From T23 to PHSS | 6001_Glenmore - Parkhurst 66 kV | Rating (A) | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372
CA | 40001073 | 6001 | From T23 to PHSS | 6001_Glenmore - Parkhurst 66 kV | Time | 14:00 | 17:00 | 8:30 | 14:00 | 17:00 | 8:30 | 14:00 | 17:00 | 8:30 | 14:00 | 17:00 | 8:30 | 14:00 | 17:30 | 3:30
CA | 40001073 | 6001 | From T23 to PHSS | 6001_Glenmore - Parkhurst 66 kV | Voltage at Constrained Conductor | 69.2335 | 69.2428 | 69.2335 | 69.2833 | 69.2957 | 69.2834 | 69.3239 | 69.3363 | 69.3239 | 69.366 | 69.3782 | 69.3661 | 69.3904 | 69.4182 | 69.4477
CA | 40001074 | 6003 | From RGBS to BERS | 6003_Glenmore - Berserker 66 kV | % of Rated A | 22.4504 | 21.545 | 24.209 | 20.898 | 20.059 | 22.5391 | 19.8591 | 19.0663 | 21.4239 | 19.1802 | 18.4144 | 20.6914 | 18.8901 | 18.139 | 20.3819
CA | 40001074 | 6003 | From RGBS to BERS | 6003_Glenmore - Berserker 66 kV | Limiting Line Name | TR_LINE 22137_1 | TR_LINE 22137_1 | TR_LINE 22137_1 | TR_LINE 22137_1 | TR_LINE 22137_1 | TR_LINE 22137_1 | TR_LINE 22137_1 | TR_LINE 22137_1 | TR_LINE 22137_1 | TR_LINE 22137_1 | TR_LINE 22137_1 | TR_LINE 22137_1 | TR_LINE 22137_1 | TR_LINE 22137_1 | TR_LINE 22137_1
CA | 40001074 | 6003 | From RGBS to BERS | 6003_Glenmore - Berserker 66 kV | Loading (A) | 90.0259 | 90.0582 | 90.0574 | 83.8008 | 83.8465 | 83.8453 | 79.635 | 79.6972 | 79.6969 | 76.9124 | 76.9724 | 76.9721 | 75.7493 | 75.8209 | 75.8206
CA | 40001074 | 6003 | From RGBS to BERS | 6003_Glenmore - Berserker 66 kV | Loading (MVA) | 10.7961 | 10.8089 | 10.809 | 10.0572 | 10.0709 | 10.071 | 9.5625 | 9.5786 | 9.5786 | 9.2414 | 9.2557 | 9.2557 | 9.1046 | 9.1201 | 9.1201
CA | 40001074 | 6003 | From RGBS to BERS | 6003_Glenmore - Berserker 66 kV | Loading (MW) | 6.0567 | 6.0565 | 6.0569 | 4.475 | 4.4748 | 4.4752 | 3.084 | 3.0837 | 3.0837 | 1.7746 | 1.7743 | 1.7743 | 0.57182 | 0.57207 | 0.57212
CA | 40001074 | 6003 | From RGBS to BERS | 6003_Glenmore - Berserker 66 kV | Power Factor | 0.56101 | 0.56033 | 0.56036 | 0.44496 | 0.44433 | 0.44437 | 0.32252 | 0.32194 | 0.32194 | 0.19203 | 0.19169 | 0.1917 | 0.062805 | 0.062726 | 0.062732
CA | 40001074 | 6003 | From RGBS to BERS | 6003_Glenmore - Berserker 66 kV | Rating (A) | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372
CA | 40001074 | 6003 | From RGBS to BERS | 6003_Glenmore - Berserker 66 kV | Time | 16:30 | 18:30 | 5:30 | 16:30 | 18:30 | 5:30 | 16:30 | 21:00 | 22:00 | 16:30 | 21:00 | 22:00 | 16:30 | 21:00 | 22:00
CA | 40001074 | 6003 | From RGBS to BERS | 6003_Glenmore - Berserker 66 kV | Voltage at Constrained Conductor | 69.2371 | 69.2943 | 69.2955 | 69.2897 | 69.3464 | 69.3476 | 69.3277 | 69.3901 | 69.3902 | 69.3716 | 69.4249 | 69.425 | 69.3943 | 69.4463 | 69.4464
CA | 40001075 | 6004 | From T23 to RSSS | 6004_Glenmore - Rockhampton South 66 kV | % of Rated A | 3.696 | 3.6197 | 4.0134 | 4.6427 | 4.5582 | 5.0414 | 5.8475 | 5.7506 | 6.3496 | 7.0294 | 6.919 | 7.633 | 7.7981 | 7.6783 | 8.4675
CA | 40001075 | 6004 | From T23 to RSSS | 6004_Glenmore - Rockhampton South 66 kV | Limiting Line Name | TR_LINE 139201_1 | TR_CABLE 301_1 | TR_LINE 139201_1 | TR_LINE 139201_1 | TR_CABLE 301_1 | TR_LINE 139201_1 | TR_LINE 139201_1 | TR_CABLE 301_1 | TR_LINE 139201_1 | TR_LINE 139201_1 | TR_CABLE 301_1 | TR_LINE 139201_1 | TR_LINE 139201_1 | TR_CABLE 301_1 | TR_LINE 139201_1
CA | 40001075 | 6004 | From T23 to RSSS | 6004_Glenmore - Rockhampton South 66 kV | Loading (A) | 13.5644 | 13.4653 | 13.5651 | 17.0388 | 16.9565 | 17.0398 | 21.4603 | 21.3921 | 21.4616 | 25.7981 | 25.7386 | 25.7995 | 28.6189 | 28.5634 | 28.6203
CA | 40001075 | 6004 | From T23 to RSSS | 6004_Glenmore - Rockhampton South 66 kV | Loading (MVA) | 1.6267 | 1.615 | 1.6268 | 2.0449 | 2.0353 | 2.0451 | 2.5772 | 2.5692 | 2.5775 | 3.1003 | 3.0932 | 3.1005 | 3.4406 | 3.4338 | 3.4408
CA | 40001075 | 6004 | From T23 to RSSS | 6004_Glenmore - Rockhampton South 66 kV | Loading (MW) | 1.4561 | 1.4561 | 1.4564 | 1.9035 | 1.9033 | 1.9038 | 2.4596 | 2.4592 | 2.46 | 2.9971 | 2.9965 | 2.9975 | 3.3412 | 3.3403 | 3.3416
CA | 40001075 | 6004 | From T23 to RSSS | 6004_Glenmore - Rockhampton South 66 kV | Power Factor | 0.89511 | 0.9016 | 0.89527 | 0.93085 | 0.93517 | 0.93094 | 0.95435 | 0.95718 | 0.95441 | 0.96674 | 0.96873 | 0.96678 | 0.97111 | 0.97278 | 0.97115
CA | 40001075 | 6004 | From T23 to RSSS | 6004_Glenmore - Rockhampton South 66 kV | Rating (A) | 367 | 372 | 338 | 367 | 372 | 338 | 367 | 372 | 338 | 367 | 372 | 338 | 367 | 372 | 338
CA | 40001075 | 6004 | From T23 to RSSS | 6004_Glenmore - Rockhampton South 66 kV | Time | 9:30 | 17:00 | 7:30 | 10:00 | 17:00 | 7:30 | 10:00 | 17:00 | 7:30 | 10:00 | 17:00 | 7:30 | 10:00 | 17:00 | 7:30
CA | 40001075 | 6004 | From T23 to RSSS | 6004_Glenmore - Rockhampton South 66 kV | Voltage at Constrained Conductor | 69.2372 | 69.2452 | 69.2386 | 69.2908 | 69.299 | 69.2922 | 69.3359 | 69.3408 | 69.3373 | 69.3825 | 69.3837 | 69.3839 | 69.4095 | 69.4068 | 69.411
CA | 40001076 | 6006 | From T23 to FVSS | 6006_Glenmore - Frenchville 66 kV | % of Rated A | 4.621 | 4.4305 | 4.9796 | 3.2612 | 3.1265 | 3.5141 | 2.1796 | 2.0899 | 2.349 | 1.6313 | 1.5678 | 1.7615 | 2.0233 | 1.9553 | 2.1964
CA | 40001076 | 6006 | From T23 to FVSS | 6006_Glenmore - Frenchville 66 kV | Limiting Line Name | TR_LINE 22134_1 | TR_LINE 22134_1 | TR_LINE 22134_1 | TR_LINE 22134_1 | TR_LINE 22134_1 | TR_LINE 22134_1 | TR_LINE 22134_1 | TR_LINE 22134_1 | TR_LINE 22134_1 | TR_LINE 22134_1 | TR_LINE 22134_1 | TR_LINE 22134_1 | TR_LINE 22134_1 | TR_LINE 22134_1 | TR_LINE 22134_1
CA | 40001076 | 6006 | From T23 to FVSS | 6006_Glenmore - Frenchville 66 kV | Loading (A) | 18.5301 | 18.5193 | 18.524 | 13.0776 | 13.0688 | 13.0724 | 8.7402 | 8.7359 | 8.7384 | 6.5415 | 6.5536 | 6.5526 | 8.1135 | 8.1731 | 8.1706
CA | 40001076 | 6006 | From T23 to FVSS | 6006_Glenmore - Frenchville 66 kV | Loading (MVA) | 2.2221 | 2.2211 | 2.2213 | 1.5693 | 1.5686 | 1.5687 | 1.0495 | 1.0491 | 1.0503 | 0.786 | 0.78805 | 0.78794 | 0.9752 | 0.9831 | 0.9828
CA | 40001076 | 6006 | From T23 to FVSS | 6006_Glenmore - Frenchville 66 kV | Loading (MW) | 2.0414 | 2.0401 | 2.0405 | 1.3179 | 1.3166 | 1.317 | 0.65023 | 0.6489 | 0.64993 | 0.0001073 | 0.003212 | 0.0028862 | 0.62127 | 0.62448 | 0.62416
CA | 40001076 | 6006 | From T23 to FVSS | 6006_Glenmore - Frenchville 66 kV | Power Factor | 0.91872 | 0.91853 | 0.91862 | 0.83979 | 0.83935 | 0.83955 | 0.61959 | 0.61851 | 0.61882 | 0.00013652 | 0.0040759 | 0.003663 | 0.63708 | 0.63522 | 0.63508
CA | 40001076 | 6006 | From T23 to FVSS | 6006_Glenmore - Frenchville 66 kV | Rating (A) | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372
CA | 40001076 | 6006 | From T23 to FVSS | 6006_Glenmore - Frenchville 66 kV | Time | 14:00 | 17:00 | 8:30 | 14:00 | 17:00 | 8:30 | 14:00 | 17:00 | 3:30 | 16:30 | 21:00 | 22:00 | 16:30 | 21:00 | 22:00
CA | 40001076 | 6006 | From T23 to FVSS | 6006_Glenmore - Frenchville 66 kV | Voltage at Constrained Conductor | 69.2335 | 69.2428 | 69.2335 | 69.2833 | 69.2957 | 69.2834 | 69.3239 | 69.3363 | 69.3916 | 69.3716 | 69.4249 | 69.425 | 69.3943 | 69.4463 | 69.4464
CA | 40001077 | 6044 | From RLSS to EQSS - YWSS | 6044_Raglan-East End Quarry/Yarwun 66 kV | % of Rated A | 1.51 | 1.1946 | 1.2547 | 1.5125 | 1.1965 | 1.2567 | 1.5147 | 1.1984 | 1.2587 | 1.5173 | 1.2002 | 1.2606 | 1.5194 | 1.2018 | 1.2623
CA | 40001077 | 6044 | From RLSS to EQSS - YWSS | 6044_Raglan-East End Quarry/Yarwun 66 kV | Limiting Line Name | TR_LINE 22122_1 | TR_LINE 22122_1 | TR_LINE 22122_1 | TR_LINE 22122_1 | TR_LINE 22122_1 | TR_LINE 22122_1 | TR_LINE 22122_1 | TR_LINE 22122_1 | TR_LINE 22122_1 | TR_LINE 22122_1 | TR_LINE 22122_1 | TR_LINE 22122_1 | TR_LINE 22122_1 | TR_LINE 22122_1 | TR_LINE 22122_1
CA | 40001077 | 6044 | From RLSS to EQSS - YWSS | 6044_Raglan-East End Quarry/Yarwun 66 kV | Loading (A) | 1.9932 | 1.9949 | 1.9949 | 1.9965 | 1.9981 | 1.9981 | 1.9994 | 2.0013 | 2.0013 | 2.0029 | 2.0044 | 2.0044 | 2.0055 | 2.007 | 2.0071
CA | 40001077 | 6044 | From RLSS to EQSS - YWSS | 6044_Raglan-East End Quarry/Yarwun 66 kV | Loading (MVA) | 0.23943 | 0.23983 | 0.23983 | 0.2402 | 0.24059 | 0.2406 | 0.24092 | 0.24136 | 0.24136 | 0.24174 | 0.24211 | 0.24212 | 0.24239 | 0.24276 | 0.24276
CA | 40001077 | 6044 | From RLSS to EQSS - YWSS | 6044_Raglan-East End Quarry/Yarwun 66 kV | Loading (MW) | 3.564e-05 | 3.5699e-05 | 3.57e-05 | 3.5755e-05 | 3.5814e-05 | 3.5815e-05 | 3.5862e-05 | 3.5927e-05 | 3.5928e-05 | 3.5984e-05 | 3.604e-05 | 3.6041e-05 | 3.6081e-05 | 3.6136e-05 | 3.6137e-05
CA | 40001077 | 6044 | From RLSS to EQSS - YWSS | 6044_Raglan-East End Quarry/Yarwun 66 kV | Power Factor | 0.00014886 | 0.00014886 | 0.00014886 | 0.00014886 | 0.00014886 | 0.00014886 | 0.00014886 | 0.00014886 | 0.00014886 | 0.00014886 | 0.00014886 | 0.00014886 | 0.00014886 | 0.00014886 | 0.00014886
CA | 40001077 | 6044 | From RLSS to EQSS - YWSS | 6044_Raglan-East End Quarry/Yarwun 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
CA | 40001077 | 6044 | From RLSS to EQSS - YWSS | 6044_Raglan-East End Quarry/Yarwun 66 kV | Time | 16:30 | 18:30 | 5:30 | 16:30 | 18:30 | 5:30 | 16:30 | 19:30 | 4:00 | 16:30 | 19:30 | 4:00 | 16:30 | 19:30 | 4:00
CA | 40001077 | 6044 | From RLSS to EQSS - YWSS | 6044_Raglan-East End Quarry/Yarwun 66 kV | Voltage at Constrained Conductor | 69.3512 | 69.4086 | 69.4097 | 69.4629 | 69.5198 | 69.5209 | 69.5669 | 69.6297 | 69.6309 | 69.6853 | 69.7388 | 69.7401 | 69.7791 | 69.8313 | 69.8326
CA | 40001079 | 6050 | From FVSS to PHSS | 6050_Parkhurst - Frenchville 66 kV | % of Rated A | 5.9896 | 5.743 | 6.4548 | 6.6709 | 6.3962 | 7.1892 | 7.3478 | 7.0453 | 7.9187 | 7.9881 | 7.6595 | 8.6089 | 8.5584 | 8.2068 | 9.2237
CA | 40001079 | 6050 | From FVSS to PHSS | 6050_Parkhurst - Frenchville 66 kV | Limiting Line Name | TR_LINE 22210_1 | TR_LINE 22210_1 | TR_LINE 22210_1 | TR_LINE 22210_1 | TR_LINE 22210_1 | TR_LINE 22210_1 | TR_LINE 22210_1 | TR_LINE 22210_1 | TR_LINE 22210_1 | TR_LINE 22210_1 | TR_LINE 22210_1 | TR_LINE 22210_1 | TR_LINE 22210_1 | TR_LINE 22210_1 | TR_LINE 22210_1
CA | 40001079 | 6050 | From FVSS to PHSS | 6050_Parkhurst - Frenchville 66 kV | Loading (A) | 24.0184 | 24.0057 | 24.0117 | 26.7505 | 26.7361 | 26.7437 | 29.4646 | 29.4495 | 29.4577 | 32.0322 | 32.0166 | 32.0252 | 34.3193 | 34.3042 | 34.3123
CA | 40001079 | 6050 | From FVSS to PHSS | 6050_Parkhurst - Frenchville 66 kV | Loading (MVA) | 2.8797 | 2.8786 | 2.8789 | 3.2102 | 3.2091 | 3.2094 | 3.5386 | 3.5374 | 3.5378 | 3.85 | 3.8488 | 3.8491 | 4.127 | 4.1257 | 4.1261
CA | 40001079 | 6050 | From FVSS to PHSS | 6050_Parkhurst - Frenchville 66 kV | Loading (MW) | 2.7666 | 2.7653 | 2.7657 | 3.1139 | 3.1125 | 3.113 | 3.4548 | 3.4535 | 3.4539 | 3.7769 | 3.7756 | 3.776 | 4.0609 | 4.0596 | 4.06
CA | 40001079 | 6050 | From FVSS to PHSS | 6050_Parkhurst - Frenchville 66 kV | Power Factor | 0.96072 | 0.96063 | 0.96067 | 0.96999 | 0.96992 | 0.96996 | 0.97632 | 0.97626 | 0.97629 | 0.98102 | 0.98098 | 0.981 | 0.984 | 0.98396 | 0.98398
CA | 40001079 | 6050 | From FVSS to PHSS | 6050_Parkhurst - Frenchville 66 kV | Rating (A) | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372
CA | 40001079 | 6050 | From FVSS to PHSS | 6050_Parkhurst - Frenchville 66 kV | Time | 14:00 | 17:00 | 8:30 | 14:00 | 17:00 | 8:30 | 14:00 | 17:00 | 8:30 | 14:00 | 17:00 | 8:30 | 14:00 | 17:00 | 8:30
CA | 40001079 | 6050 | From FVSS to PHSS | 6050_Parkhurst - Frenchville 66 kV | Voltage at Constrained Conductor | 69.2217 | 69.2311 | 69.2218 | 69.2852 | 69.2976 | 69.2852 | 69.338 | 69.3505 | 69.3381 | 69.3918 | 69.404 | 69.3919 | 69.4273 | 69.4376 | 69.4275
CA | 40001081 | 6024 | CALLIOPE | 6024_Awoonga - Calliope 66kV | % of Rated A | 4.6914 | 3.2642 | 3.3723 | 4.4181 | 3.0653 | 3.1751 | 4.1686 | 2.8962 | 2.9953 | 3.9369 | 2.7249 | 2.8278 | 3.727 | 2.5854 | 2.6764
CA | 40001081 | 6024 | CALLIOPE | 6024_Awoonga - Calliope 66kV | Limiting Line Name | TR_LINE 181307_1 | TR_LINE 181307_1 | TR_LINE 181307_1 | TR_LINE 181307_1 | TR_LINE 181307_1 | TR_LINE 181307_1 | TR_LINE 181307_1 | TR_LINE 181307_1 | TR_LINE 181307_1 | TR_LINE 181307_1 | TR_LINE 181307_1 | TR_LINE 181307_1 | TR_LINE 181307_1 | TR_LINE 181307_1 | TR_LINE 181307_1
CA | 40001081 | 6024 | CALLIOPE | 6024_Awoonga - Calliope 66kV | Loading (A) | 7.9285 | 7.834 | 7.8913 | 7.4666 | 7.3568 | 7.4297 | 7.0449 | 6.9508 | 7.0089 | 6.6534 | 6.5396 | 6.6172 | 6.2986 | 6.2049 | 6.2628
CA | 40001081 | 6024 | CALLIOPE | 6024_Awoonga - Calliope 66kV | Loading (MVA) | 0.95276 | 0.94179 | 0.9483 | 0.89779 | 0.88173 | 0.89337 | 0.84748 | 0.83655 | 0.84317 | 0.80087 | 0.78469 | 0.79653 | 0.75838 | 0.74741 | 0.75408
CA | 40001081 | 6024 | CALLIOPE | 6024_Awoonga - Calliope 66kV | Loading (MW) | 0.17814 | 0.17704 | 0.17333 | 0.15972 | 0.15995 | 0.15492 | 0.14233 | 0.14122 | 0.13753 | 0.12631 | 0.12652 | 0.12151 | 0.11213 | 0.11102 | 0.10733
CA | 40001081 | 6024 | CALLIOPE | 6024_Awoonga - Calliope 66kV | Power Factor | 0.18697 | 0.18798 | 0.18278 | 0.17791 | 0.18141 | 0.17341 | 0.16794 | 0.16881 | 0.16312 | 0.15772 | 0.16124 | 0.15255 | 0.14785 | 0.14854 | 0.14233
CA | 40001081 | 6024 | CALLIOPE | 6024_Awoonga - Calliope 66kV | Rating (A) | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234
CA | 40001081 | 6024 | CALLIOPE | 6024_Awoonga - Calliope 66kV | Time | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30
CA | 40001081 | 6024 | CALLIOPE | 6024_Awoonga - Calliope 66kV | Voltage at Constrained Conductor | 69.3791 | 69.4082 | 69.3806 | 69.4211 | 69.1964 | 69.4226 | 69.4536 | 69.4854 | 69.455 | 69.4963 | 69.2763 | 69.4978 | 69.5148 | 69.5447 | 69.5163
CA | 40001083 | 6090 | From EHBS to RLSS | 6090_Egan's Hill - Raglan 66 kV | % of Rated A | 5.5486 | 4.3863 | 4.607 | 4.7484 | 3.755 | 3.944 | 4.2737 | 3.3809 | 3.5511 | 4.3811 | 3.4652 | 3.6396 | 5.0609 | 4.0014 | 4.2028
CA | 40001083 | 6090 | From EHBS to RLSS | 6090_Egan's Hill - Raglan 66 kV | Limiting Line Name | TR_LINE 160589_1 | TR_LINE 160589_1 | TR_LINE 160589_1 | TR_LINE 160589_1 | TR_LINE 160589_1 | TR_LINE 160589_1 | TR_LINE 160589_1 | TR_LINE 160589_1 | TR_LINE 160589_1 | TR_LINE 160589_1 | TR_LINE 160589_1 | TR_LINE 160589_1 | TR_LINE 160589_1 | TR_LINE 160589_1 | TR_LINE 160589_1
CA | 40001083 | 6090 | From EHBS to RLSS | 6090_Egan's Hill - Raglan 66 kV | Loading (A) | 7.3241 | 7.325 | 7.3251 | 6.2679 | 6.2709 | 6.271 | 5.6413 | 5.6461 | 5.6462 | 5.7831 | 5.7869 | 5.787 | 6.6804 | 6.6824 | 6.6824
CA | 40001083 | 6090 | From EHBS to RLSS | 6090_Egan's Hill - Raglan 66 kV | Loading (MVA) | 0.88022 | 0.88106 | 0.88108 | 0.75392 | 0.7549 | 0.75492 | 0.67899 | 0.68019 | 0.68022 | 0.69661 | 0.69761 | 0.69763 | 0.80508 | 0.80593 | 0.80595
CA | 40001083 | 6090 | From EHBS to RLSS | 6090_Egan's Hill - Raglan 66 kV | Loading (MW) | 0.57639 | 0.57639 | 0.57639 | 0.34739 | 0.34739 | 0.34739 | 0.098365 | 0.098366 | 0.098366 | 0.17791 | 0.17791 | 0.17791 | 0.44126 | 0.44126 | 0.44126
CA | 40001083 | 6090 | From EHBS to RLSS | 6090_Egan's Hill - Raglan 66 kV | Power Factor | 0.65483 | 0.6542 | 0.65419 | 0.46078 | 0.46019 | 0.46017 | 0.14487 | 0.14462 | 0.14461 | 0.25539 | 0.25502 | 0.25501 | 0.5481 | 0.54752 | 0.5475
CA | 40001083 | 6090 | From EHBS to RLSS | 6090_Egan's Hill - Raglan 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
CA | 40001083 | 6090 | From EHBS to RLSS | 6090_Egan's Hill - Raglan 66 kV | Time | 16:30 | 18:30 | 5:30 | 16:30 | 18:30 | 5:30 | 16:30 | 19:30 | 4:00 | 16:30 | 19:30 | 4:00 | 16:30 | 19:30 | 4:00
CA | 40001083 | 6090 | From EHBS to RLSS | 6090_Egan's Hill - Raglan 66 kV | Voltage at Constrained Conductor | 69.3868 | 69.444 | 69.4451 | 69.4449 | 69.5017 | 69.5028 | 69.4911 | 69.5537 | 69.555 | 69.5456 | 69.5991 | 69.6003 | 69.5788 | 69.6311 | 69.6323
CA | 40001084 | 6091 | From EHBS to GASS / MASS&MLSS | 6091_Egan's Hill - Gavial 66 kV | % of Rated A | 6.7262 | 4.9878 | 5.1756 | 8.8243 | 6.5392 | 6.7853 | 12.8522 | 9.5219 | 9.881 | 17.3133 | 12.8264 | 13.3107 | 21.6237 | 16.0197 | 16.6246
CA | 40001084 | 6091 | From EHBS to GASS / MASS&MLSS | 6091_Egan's Hill - Gavial 66 kV | Limiting Line Name | TR_LINE 13465_1 | TR_LINE 13465_1 | TR_LINE 13465_1 | TR_LINE 13465_1 | TR_LINE 13465_1 | TR_LINE 13465_1 | TR_LINE 13465_1 | TR_LINE 13465_1 | TR_LINE 13465_1 | TR_LINE 13465_1 | TR_LINE 13465_1 | TR_LINE 13465_1 | TR_LINE 13465_1 | TR_LINE 13465_1 | TR_LINE 13465_1
CA | 40001084 | 6091 | From EHBS to GASS / MASS&MLSS | 6091_Egan's Hill - Gavial 66 kV | Loading (A) | 9.6184 | 9.6265 | 9.6266 | 12.6188 | 12.6206 | 12.6206 | 18.3787 | 18.3772 | 18.3786 | 24.7581 | 24.755 | 24.758 | 30.9218 | 30.9181 | 30.9217
CA | 40001084 | 6091 | From EHBS to GASS / MASS&MLSS | 6091_Egan's Hill - Gavial 66 kV | Loading (MVA) | 1.1552 | 1.1571 | 1.1571 | 1.5165 | 1.5179 | 1.518 | 2.2095 | 2.2097 | 2.2095 | 2.978 | 2.9781 | 2.978 | 3.7204 | 3.7205 | 3.7204
CA | 40001084 | 6091 | From EHBS to GASS / MASS&MLSS | 6091_Egan's Hill - Gavial 66 kV | Loading (MW) | 0.029353 | 0.029353 | 0.029353 | 0.99419 | 0.99419 | 0.99419 | 1.9009 | 1.9009 | 1.9009 | 2.7672 | 2.7672 | 2.7672 | 3.5634 | 3.5634 | 3.5634
CA | 40001084 | 6091 | From EHBS to GASS / MASS&MLSS | 6091_Egan's Hill - Gavial 66 kV | Power Factor | 0.02541 | 0.025368 | 0.025367 | 0.65559 | 0.65496 | 0.65495 | 0.86031 | 0.86022 | 0.8603 | 0.92921 | 0.92916 | 0.92921 | 0.95781 | 0.95779 | 0.95781
CA | 40001084 | 6091 | From EHBS to GASS / MASS&MLSS | 6091_Egan's Hill - Gavial 66 kV | Rating (A) | 143 | 193 | 186 | 143 | 193 | 186 | 143 | 193 | 186 | 143 | 193 | 186 | 143 | 193 | 186
CA | 40001084 | 6091 | From EHBS to GASS / MASS&MLSS | 6091_Egan's Hill - Gavial 66 kV | Time | 16:30 | 18:30 | 5:30 | 16:30 | 18:30 | 5:30 | 9:30 | 17:00 | 8:30 | 9:30 | 17:00 | 8:30 | 9:30 | 17:00 | 8:30
CA | 40001084 | 6091 | From EHBS to GASS / MASS&MLSS | 6091_Egan's Hill - Gavial 66 kV | Voltage at Constrained Conductor | 69.3402 | 69.3973 | 69.3984 | 69.3837 | 69.4404 | 69.4415 | 69.41 | 69.4227 | 69.4103 | 69.4454 | 69.4578 | 69.4458 | 69.464 | 69.4745 | 69.4644
CA | 40001085 | 6093 | GASS - MLSS | 6093_Gavial - Mt Morgan 66 kV | % of Rated A | 6.5535 | 5.1804 | 5.4411 | 6.554 | 5.1808 | 5.4415 | 6.5544 | 5.1812 | 5.4419 | 6.5549 | 5.1815 | 5.4422 | 6.5552 | 5.1817 | 5.4425
CA | 40001085 | 6093 | GASS - MLSS | 6093_Gavial - Mt Morgan 66 kV | Limiting Line Name | TR_LINE 19767_1 | TR_LINE 19767_1 | TR_LINE 19767_1 | TR_LINE 19767_1 | TR_LINE 19767_1 | TR_LINE 19767_1 | TR_LINE 19767_1 | TR_LINE 19767_1 | TR_LINE 19767_1 | TR_LINE 19767_1 | TR_LINE 19767_1 | TR_LINE 19767_1 | TR_LINE 19767_1 | TR_LINE 19767_1 | TR_LINE 19767_1
CA | 40001085 | 6093 | GASS - MLSS | 6093_Gavial - Mt Morgan 66 kV | Loading (A) | 8.6506 | 8.6513 | 8.6513 | 8.6513 | 8.652 | 8.652 | 8.6519 | 8.6526 | 8.6526 | 8.6525 | 8.6531 | 8.6532 | 8.6529 | 8.6535 | 8.6535
CA | 40001085 | 6093 | GASS - MLSS | 6093_Gavial - Mt Morgan 66 kV | Loading (MVA) | 1.0398 | 1.0407 | 1.0408 | 1.0408 | 1.0417 | 1.0417 | 1.0415 | 1.0426 | 1.0426 | 1.0424 | 1.0433 | 1.0433 | 1.0429 | 1.0437 | 1.0438
CA | 40001085 | 6093 | GASS - MLSS | 6093_Gavial - Mt Morgan 66 kV | Loading (MW) | 0.70172 | 0.70172 | 0.70172 | 0.70172 | 0.70172 | 0.70172 | 0.70172 | 0.70172 | 0.70172 | 0.70172 | 0.70172 | 0.70172 | 0.70172 | 0.70172 | 0.70172
CA | 40001085 | 6093 | GASS - MLSS | 6093_Gavial - Mt Morgan 66 kV | Power Factor | 0.67486 | 0.67425 | 0.67424 | 0.67422 | 0.67362 | 0.6736 | 0.67373 | 0.67307 | 0.67306 | 0.67319 | 0.67262 | 0.67261 | 0.67287 | 0.67232 | 0.67231
CA | 40001085 | 6093 | GASS - MLSS | 6093_Gavial - Mt Morgan 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
CA | 40001085 | 6093 | GASS - MLSS | 6093_Gavial - Mt Morgan 66 kV | Time | 16:30 | 18:30 | 5:30 | 16:30 | 18:30 | 5:30 | 16:30 | 19:30 | 4:00 | 16:30 | 19:30 | 4:00 | 16:30 | 19:30 | 4:00
CA | 40001085 | 6093 | GASS - MLSS | 6093_Gavial - Mt Morgan 66 kV | Voltage at Constrained Conductor | 69.3976 | 69.4548 | 69.4559 | 69.4578 | 69.5146 | 69.5157 | 69.5035 | 69.5662 | 69.5674 | 69.5549 | 69.6085 | 69.6097 | 69.5846 | 69.6369 | 69.6381
CA | 40001086 | 6094 | From GASS to MASS T | 6094_Malchi Tee - Malchi 66 kV | % of Rated A | 3.6611 | 2.5777 | 2.6441 | 8.3703 | 5.8931 | 6.0452 | 12.8142 | 9.0217 | 9.2546 | 17.0603 | 12.0111 | 12.3212 | 20.9677 | 14.7626 | 15.1433
CA | 40001086 | 6094 | From GASS to MASS T | 6094_Malchi Tee - Malchi 66 kV | Limiting Line Name | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1
CA | 40001086 | 6094 | From GASS to MASS T | 6094_Malchi Tee - Malchi 66 kV | Loading (A) | 6.1873 | 6.1865 | 6.1873 | 14.1459 | 14.1433 | 14.1458 | 21.6404 | 21.6364 | 21.6403 | 28.8273 | 28.8222 | 28.8272 | 35.4355 | 35.4302 | 35.4353
CA | 40001086 | 6094 | From GASS to MASS T | 6094_Malchi Tee - Malchi 66 kV | Loading (MVA) | 0.74361 | 0.74362 | 0.74361 | 1.7015 | 1.7015 | 1.7015 | 2.6085 | 2.6085 | 2.6085 | 3.4788 | 3.4788 | 3.4788 | 4.2799 | 4.2799 | 4.2799
CA | 40001086 | 6094 | From GASS to MASS T | 6094_Malchi Tee - Malchi 66 kV | Loading (MW) | 0.73229 | 0.73229 | 0.73229 | 1.6974 | 1.6974 | 1.6974 | 2.6084 | 2.6084 | 2.6084 | 3.4785 | 3.4785 | 3.4785 | 4.2793 | 4.2793 | 4.2793
CA | 40001086 | 6094 | From GASS to MASS T | 6094_Malchi Tee - Malchi 66 kV | Power Factor | 0.98478 | 0.98477 | 0.98478 | 0.99757 | 0.99757 | 0.99757 | 0.99995 | 0.99995 | 0.99995 | 0.99991 | 0.99991 | 0.99991 | 0.99986 | 0.99986 | 0.99986
CA | 40001086 | 6094 | From GASS to MASS T | 6094_Malchi Tee - Malchi 66 kV | Rating (A) | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234
CA | 40001086 | 6094 | From GASS to MASS T | 6094_Malchi Tee - Malchi 66 kV | Time | 9:30 | 17:00 | 8:30 | 9:30 | 17:00 | 8:30 | 9:30 | 17:00 | 8:30 | 9:30 | 17:00 | 8:30 | 9:30 | 17:00 | 8:30
CA | 40001086 | 6094 | From GASS to MASS T | 6094_Malchi Tee - Malchi 66 kV | Voltage at Constrained Conductor | 69.388 | 69.3976 | 69.3883 | 69.4458 | 69.4585 | 69.4462 | 69.5928 | 69.6055 | 69.5931 | 69.6735 | 69.6859 | 69.6738 | 69.7331 | 69.7435 | 69.7335
CA | 40001087 | 6095 | From EHBS to RSSS | 6095_Egan's Hill-Rockhampton South 66 kV | % of Rated A | 12.1326 | 12.0346 | 13.6775 | 11.1245 | 11.0342 | 12.5411 | 10.1599 | 10.0775 | 11.4536 | 9.2834 | 9.2082 | 10.4655 | 8.6818 | 8.6117 | 9.7874
CA | 40001087 | 6095 | From EHBS to RSSS | 6095_Egan's Hill-Rockhampton South 66 kV | Limiting Line Name | TR_LINE 20983_1 | TR_LINE 20983_1 | TR_LINE 20983_1 | TR_LINE 20983_1 | TR_LINE 20983_1 | TR_LINE 20983_1 | TR_LINE 20983_1 | TR_LINE 20983_1 | TR_LINE 20983_1 | TR_LINE 20983_1 | TR_LINE 20983_1 | TR_LINE 20983_1 | TR_LINE 20983_1 | TR_LINE 20983_1 | TR_LINE 20983_1
CA | 40001087 | 6095 | From EHBS to RSSS | 6095_Egan's Hill-Rockhampton South 66 kV | Loading (A) | 30.0889 | 30.0865 | 30.0905 | 27.5888 | 27.5856 | 27.5904 | 25.1965 | 25.1937 | 25.198 | 23.0228 | 23.0204 | 23.0242 | 21.531 | 21.5293 | 21.5323
CA | 40001087 | 6095 | From EHBS to RSSS | 6095_Egan's Hill-Rockhampton South 66 kV | Loading (MVA) | 3.6118 | 3.612 | 3.612 | 3.3138 | 3.3141 | 3.3141 | 3.0281 | 3.0284 | 3.0284 | 2.7685 | 2.7687 | 2.7687 | 2.5899 | 2.5901 | 2.5901
CA | 40001087 | 6095 | From EHBS to RSSS | 6095_Egan's Hill-Rockhampton South 66 kV | Loading (MW) | 3.5522 | 3.5525 | 3.5526 | 3.243 | 3.2433 | 3.2434 | 2.9443 | 2.9445 | 2.9446 | 2.6701 | 2.6703 | 2.6704 | 2.4764 | 2.4766 | 2.4767
CA | 40001087 | 6095 | From EHBS to RSSS | 6095_Egan's Hill-Rockhampton South 66 kV | Power Factor | 0.98351 | 0.98352 | 0.98354 | 0.97864 | 0.97865 | 0.97867 | 0.97231 | 0.97232 | 0.97235 | 0.96446 | 0.96448 | 0.96451 | 0.95616 | 0.95619 | 0.95622
CA | 40001087 | 6095 | From EHBS to RSSS | 6095_Egan's Hill-Rockhampton South 66 kV | Rating (A) | 248 | 250 | 220 | 248 | 250 | 220 | 248 | 250 | 220 | 248 | 250 | 220 | 248 | 250 | 220
CA | 40001087 | 6095 | From EHBS to RSSS | 6095_Egan's Hill-Rockhampton South 66 kV | Time | 10:00 | 17:00 | 7:30 | 10:00 | 17:00 | 7:30 | 10:00 | 17:00 | 7:30 | 10:00 | 17:00 | 7:30 | 10:00 | 17:00 | 7:30
CA | 40001087 | 6095 | From EHBS to RSSS | 6095_Egan's Hill-Rockhampton South 66 kV | Voltage at Constrained Conductor | 69.3029 | 69.3125 | 69.3043 | 69.3487 | 69.3613 | 69.3501 | 69.3864 | 69.3991 | 69.3878 | 69.4262 | 69.4386 | 69.4276 | 69.4482 | 69.4586 | 69.4496
CA | 40001089 | 6097 | From EHBS To CNSS | 6097_Egan's Hill - Canning 66 kV | % of Rated A | 15.8276 | 15.7388 | 17.8855 | 14.6834 | 14.6013 | 16.5935 | 13.6783 | 13.6027 | 15.4594 | 12.7256 | 12.6578 | 14.3863 | 11.8796 | 11.7906 | 13.4083
CA | 40001089 | 6097 | From EHBS To CNSS | 6097_Egan's Hill - Canning 66 kV | Limiting Line Name | TR_LINE 20992_1 | TR_LINE 20992_1 | TR_LINE 20992_1 | TR_LINE 20992_1 | TR_LINE 20992_1 | TR_LINE 20992_1 | TR_LINE 20992_1 | TR_LINE 20992_1 | TR_LINE 20992_1 | TR_LINE 20992_1 | TR_LINE 20992_1 | TR_LINE 20992_1 | TR_LINE 20992_1 | TR_LINE 20992_1 | TR_LINE 20992_1
CA | 40001089 | 6097 | From EHBS To CNSS | 6097_Egan's Hill - Canning 66 kV | Loading (A) | 39.2524 | 39.3469 | 39.348 | 36.4147 | 36.5032 | 36.5056 | 33.9221 | 34.0068 | 34.0106 | 31.5596 | 31.6444 | 31.6498 | 29.4615 | 29.4764 | 29.4982
CA | 40001089 | 6097 | From EHBS To CNSS | 6097_Egan's Hill - Canning 66 kV | Loading (MVA) | 4.7134 | 4.7275 | 4.7277 | 4.3758 | 4.3898 | 4.3901 | 4.0783 | 4.0922 | 4.0927 | 3.7966 | 3.8097 | 3.8104 | 3.5453 | 3.5474 | 3.5496
CA | 40001089 | 6097 | From EHBS To CNSS | 6097_Egan's Hill - Canning 66 kV | Loading (MW) | 4.286 | 4.3028 | 4.3014 | 3.8984 | 3.9153 | 3.9139 | 3.5475 | 3.5643 | 3.5629 | 3.2064 | 3.2232 | 3.2218 | 2.8918 | 2.8947 | 2.8979
CA | 40001089 | 6097 | From EHBS To CNSS | 6097_Egan's Hill - Canning 66 kV | Power Factor | 0.90931 | 0.91016 | 0.90982 | 0.89092 | 0.89191 | 0.89151 | 0.86983 | 0.87101 | 0.87055 | 0.84455 | 0.84606 | 0.84554 | 0.81568 | 0.81602 | 0.81641
CA | 40001089 | 6097 | From EHBS To CNSS | 6097_Egan's Hill - Canning 66 kV | Rating (A) | 248 | 250 | 220 | 248 | 250 | 220 | 248 | 250 | 220 | 248 | 250 | 220 | 248 | 250 | 220
CA | 40001089 | 6097 | From EHBS To CNSS | 6097_Egan's Hill - Canning 66 kV | Time | 16:30 | 21:00 | 0:00 | 16:30 | 21:00 | 0:00 | 16:30 | 21:00 | 0:00 | 16:30 | 21:00 | 0:00 | 16:30 | 17:00 | 7:30
CA | 40001089 | 6097 | From EHBS To CNSS | 6097_Egan's Hill - Canning 66 kV | Voltage at Constrained Conductor | 69.3278 | 69.3685 | 69.3692 | 69.377 | 69.4309 | 69.4316 | 69.4125 | 69.4747 | 69.4753 | 69.4546 | 69.5077 | 69.5083 | 69.4761 | 69.4824 | 69.4734
CA | 40001092 | 6029 | From LMSS to MVSS | 6029_Littlemore - Miriam Vale 66 kV | % of Rated A | 2.5139 | 1.9871 | 2.0871 | 3.1036 | 2.4551 | 2.5783 | 3.715 | 2.9392 | 3.0875 | 4.3216 | 3.4224 | 3.5948 | 4.8887 | 3.8703 | 4.0629
CA | 40001092 | 6029 | From LMSS to MVSS | 6029_Littlemore - Miriam Vale 66 kV | Limiting Line Name | TR_LINE 16162_1 | TR_LINE 16162_1 | TR_LINE 16162_1 | TR_LINE 16162_1 | TR_LINE 16162_1 | TR_LINE 16162_1 | TR_LINE 16162_1 | TR_LINE 16162_1 | TR_LINE 16162_1 | TR_LINE 16162_1 | TR_LINE 16162_1 | TR_LINE 16162_1 | TR_LINE 16162_1 | TR_LINE 16162_1 | TR_LINE 16162_1
CA | 40001092 | 6029 | From LMSS to MVSS | 6029_Littlemore - Miriam Vale 66 kV | Loading (A) | 3.3183 | 3.3185 | 3.3184 | 4.0968 | 4.1 | 4.0995 | 4.9038 | 4.9084 | 4.9092 | 5.7045 | 5.7154 | 5.7158 | 6.4531 | 6.4635 | 6.46
CA | 40001092 | 6029 | From LMSS to MVSS | 6029_Littlemore - Miriam Vale 66 kV | Loading (MVA) | 0.40369 | 0.4038 | 0.40375 | 0.49895 | 0.49773 | 0.49803 | 0.59789 | 0.59717 | 0.59706 | 0.69632 | 0.69545 | 0.69542 | 0.7883 | 0.78773 | 0.78792
CA | 40001092 | 6029 | From LMSS to MVSS | 6029_Littlemore - Miriam Vale 66 kV | Loading (MW) | 0.26314 | 0.26314 | 0.26314 | 0.39429 | 0.39429 | 0.39429 | 0.51416 | 0.51415 | 0.51415 | 0.62636 | 0.62636 | 0.62636 | 0.72778 | 0.72777 | 0.72777
CA | 40001092 | 6029 | From LMSS to MVSS | 6029_Littlemore - Miriam Vale 66 kV | Power Factor | 0.65183 | 0.65166 | 0.65174 | 0.79023 | 0.79217 | 0.7917 | 0.85996 | 0.86098 | 0.86113 | 0.89953 | 0.90065 | 0.90069 | 0.92322 | 0.92388 | 0.92366
CA | 40001092 | 6029 | From LMSS to MVSS | 6029_Littlemore - Miriam Vale 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
CA | 40001092 | 6029 | From LMSS to MVSS | 6029_Littlemore - Miriam Vale 66 kV | Time | 16:30 | 17:00 | 7:00 | 12:00 | 17:00 | 6:30 | 12:00 | 17:30 | 6:30 | 12:00 | 17:00 | 7:00 | 12:00 | 17:30 | 6:00
CA | 40001092 | 6029 | From LMSS to MVSS | 6029_Littlemore - Miriam Vale 66 kV | Voltage at Constrained Conductor | 70.2372 | 70.2531 | 70.2458 | 70.3159 | 70.0884 | 70.1391 | 70.3923 | 70.2414 | 70.2183 | 70.4749 | 70.2524 | 70.2438 | 70.5282 | 70.3644 | 70.4191
CA | 40001103 | 6031 | From CPSS to LMSS | 6031_Calliope - Littlemore 66 kV | % of Rated A | 13.3875 | 10.5841 | 11.1155 | 13.5824 | 10.7239 | 11.2775 | 13.8085 | 10.9169 | 11.4649 | 14.0601 | 11.1024 | 11.671 | 14.3078 | 11.3111 | 11.8792
CA | 40001103 | 6031 | From CPSS to LMSS | 6031_Calliope - Littlemore 66 kV | Limiting Line Name | TR_LINE 13872_1 | TR_LINE 13872_1 | TR_LINE 13872_1 | TR_LINE 13872_1 | TR_LINE 13872_1 | TR_LINE 13872_1 | TR_LINE 13872_1 | TR_LINE 13872_1 | TR_LINE 13872_1 | TR_LINE 13872_1 | TR_LINE 13872_1 | TR_LINE 13872_1 | TR_LINE 13872_1 | TR_LINE 13872_1 | TR_LINE 13872_1
CA | 40001103 | 6031 | From CPSS to LMSS | 6031_Calliope - Littlemore 66 kV | Loading (A) | 17.6716 | 17.6754 | 17.6736 | 17.9288 | 17.909 | 17.9312 | 18.2272 | 18.2313 | 18.2292 | 18.5593 | 18.541 | 18.5569 | 18.8863 | 18.8895 | 18.888
CA | 40001103 | 6031 | From CPSS to LMSS | 6031_Calliope - Littlemore 66 kV | Loading (MVA) | 2.1257 | 2.1267 | 2.1263 | 2.158 | 2.1529 | 2.1585 | 2.1948 | 2.1958 | 2.1953 | 2.2362 | 2.2312 | 2.2355 | 2.2759 | 2.2769 | 2.2764
CA | 40001103 | 6031 | From CPSS to LMSS | 6031_Calliope - Littlemore 66 kV | Loading (MW) | 0.32495 | 0.32495 | 0.32495 | 0.48121 | 0.48124 | 0.48121 | 0.62131 | 0.6213 | 0.6213 | 0.74944 | 0.74946 | 0.74944 | 0.86225 | 0.86224 | 0.86224
CA | 40001103 | 6031 | From CPSS to LMSS | 6031_Calliope - Littlemore 66 kV | Power Factor | 0.15286 | 0.15279 | 0.15283 | 0.22299 | 0.22353 | 0.22294 | 0.28309 | 0.28295 | 0.28302 | 0.33514 | 0.33591 | 0.33524 | 0.37885 | 0.3787 | 0.37877
CA | 40001103 | 6031 | From CPSS to LMSS | 6031_Calliope - Littlemore 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
CA | 40001103 | 6031 | From CPSS to LMSS | 6031_Calliope - Littlemore 66 kV | Time | 16:30 | 17:00 | 7:00 | 16:30 | 18:30 | 7:00 | 16:30 | 17:00 | 7:00 | 16:30 | 21:00 | 7:30 | 16:30 | 17:00 | 7:00
CA | 40001103 | 6031 | From CPSS to LMSS | 6031_Calliope - Littlemore 66 kV | Voltage at Constrained Conductor | 69.4507 | 69.4664 | 69.4592 | 69.4917 | 69.4062 | 69.5005 | 69.5191 | 69.5375 | 69.5278 | 69.5648 | 69.4762 | 69.5528 | 69.5751 | 69.5915 | 69.5837
CA | 40001125 | 6039 | From CISS to BCSS | 6039_Clinton Industrial - Beecher 66 kV | % of Rated A | 6.0971 | 5.5101 | 6.557 | 6.4242 | 5.8034 | 6.9003 | 6.4239 | 5.7964 | 6.8977 | 6.421 | 5.8017 | 6.9028 | 6.4229 | 5.7964 | 6.8918
CA | 40001125 | 6039 | From CISS to BCSS | 6039_Clinton Industrial - Beecher 66 kV | Limiting Line Name | TR_LINE 33766_1 | TR_LINE 16739_1 | TR_LINE 16739_1 | TR_LINE 33766_1 | TR_LINE 16739_1 | TR_LINE 16739_1 | TR_LINE 33766_1 | TR_LINE 16739_1 | TR_LINE 16739_1 | TR_LINE 33766_1 | TR_LINE 16739_1 | TR_LINE 16739_1 | TR_LINE 33766_1 | TR_LINE 16739_1 | TR_LINE 16739_1
CA | 40001125 | 6039 | From CISS to BCSS | 6039_Clinton Industrial - Beecher 66 kV | Loading (A) | 14.9378 | 15.208 | 15.2122 | 15.7393 | 16.0174 | 16.0087 | 15.7385 | 15.9981 | 16.0027 | 15.7314 | 16.0127 | 16.0145 | 15.7362 | 15.9982 | 15.9889
CA | 40001125 | 6039 | From CISS to BCSS | 6039_Clinton Industrial - Beecher 66 kV | Loading (MVA) | 1.7823 | 1.802 | 1.8018 | 1.8781 | 1.896 | 1.8963 | 1.8781 | 1.8959 | 1.8958 | 1.8777 | 1.8962 | 1.8961 | 1.8781 | 1.8959 | 1.8962
CA | 40001125 | 6039 | From CISS to BCSS | 6039_Clinton Industrial - Beecher 66 kV | Loading (MW) | 1.7159 | 1.7168 | 1.7168 | 1.8177 | 1.8187 | 1.8187 | 1.8177 | 1.8188 | 1.8188 | 1.8178 | 1.8187 | 1.8187 | 1.8177 | 1.8188 | 1.8187
CA | 40001125 | 6039 | From CISS to BCSS | 6039_Clinton Industrial - Beecher 66 kV | Power Factor | 0.96273 | 0.95272 | 0.9528 | 0.96786 | 0.9592 | 0.95905 | 0.96784 | 0.9593 | 0.95938 | 0.96811 | 0.95912 | 0.95915 | 0.96781 | 0.9593 | 0.95914
CA | 40001125 | 6039 | From CISS to BCSS | 6039_Clinton Industrial - Beecher 66 kV | Rating (A) | 245 | 276 | 232 | 245 | 276 | 232 | 245 | 276 | 232 | 245 | 276 | 232 | 245 | 276 | 232
CA | 40001125 | 6039 | From CISS to BCSS | 6039_Clinton Industrial - Beecher 66 kV | Time | 9:30 | 17:30 | 6:30 | 9:30 | 17:00 | 6:30 | 9:30 | 17:30 | 6:30 | 9:30 | 17:00 | 7:00 | 9:30 | 17:30 | 6:00
CA | 40001125 | 6039 | From CISS to BCSS | 6039_Clinton Industrial - Beecher 66 kV | Voltage at Constrained Conductor | 68.8872 | 68.4093 | 68.3845 | 68.8908 | 68.3431 | 68.3899 | 68.8949 | 68.4213 | 68.3965 | 68.9112 | 68.368 | 68.3585 | 68.9072 | 68.4208 | 68.4711
CA | 40001136 | 6041 | From YWSS to BCSS | 6041_Yarwun - Boat Creek 66 kV | % of Rated A | 11.2584 | 8.9521 | 9.4053 | 11.8697 | 9.448 | 9.9176 | 11.8691 | 9.4365 | 9.9144 | 11.8639 | 9.4451 | 9.9215 | 11.8673 | 9.4366 | 9.9052
CA | 40001136 | 6041 | From YWSS to BCSS | 6041_Yarwun - Boat Creek 66 kV | Limiting Line Name | TR_LINE 15181_1 | TR_LINE 15181_1 | TR_LINE 15181_1 | TR_LINE 15181_1 | TR_LINE 15181_1 | TR_LINE 15181_1 | TR_LINE 15181_1 | TR_LINE 15181_1 | TR_LINE 15181_1 | TR_LINE 15181_1 | TR_LINE 15181_1 | TR_LINE 15181_1 | TR_LINE 15181_1 | TR_LINE 15181_1 | TR_LINE 15181_1
CA | 40001136 | 6041 | From YWSS to BCSS | 6041_Yarwun - Boat Creek 66 kV | Loading (A) | 14.8611 | 14.9499 | 14.9545 | 15.6681 | 15.7782 | 15.7689 | 15.6673 | 15.759 | 15.764 | 15.6604 | 15.7733 | 15.7752 | 15.6649 | 15.7591 | 15.7492
CA | 40001136 | 6041 | From YWSS to BCSS | 6041_Yarwun - Boat Creek 66 kV | Loading (MVA) | 1.7727 | 1.7706 | 1.7705 | 1.8691 | 1.8668 | 1.867 | 1.8691 | 1.8667 | 1.8666 | 1.8687 | 1.8669 | 1.8669 | 1.8691 | 1.8667 | 1.8669
CA | 40001136 | 6041 | From YWSS to BCSS | 6041_Yarwun - Boat Creek 66 kV | Loading (MW) | 1.7153 | 1.7155 | 1.7155 | 1.817 | 1.8172 | 1.8172 | 1.817 | 1.8173 | 1.8173 | 1.8171 | 1.8172 | 1.8172 | 1.817 | 1.8173 | 1.8173
CA | 40001136 | 6041 | From YWSS to BCSS | 6041_Yarwun - Boat Creek 66 kV | Power Factor | 0.96757 | 0.96884 | 0.9689 | 0.97213 | 0.97343 | 0.97332 | 0.97212 | 0.97354 | 0.9736 | 0.97238 | 0.97337 | 0.97339 | 0.97209 | 0.97354 | 0.97343
CA | 40001136 | 6041 | From YWSS to BCSS | 6041_Yarwun - Boat Creek 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
CA | 40001136 | 6041 | From YWSS to BCSS | 6041_Yarwun - Boat Creek 66 kV | Time | 9:30 | 17:30 | 6:30 | 9:30 | 17:00 | 6:30 | 9:30 | 17:30 | 6:30 | 9:30 | 17:00 | 7:00 | 9:30 | 17:30 | 6:00
CA | 40001136 | 6041 | From YWSS to BCSS | 6041_Yarwun - Boat Creek 66 kV | Voltage at Constrained Conductor | 68.8705 | 68.3805 | 68.3557 | 68.8726 | 68.311 | 68.3579 | 68.8767 | 68.3892 | 68.3644 | 68.8929 | 68.3359 | 68.3264 | 68.889 | 68.3887 | 68.4391
CA | 40001150 | 6005 | From T23 to CNSS | 6005_Rockhampton Glenmore-Canning 66 kV | % of Rated A | 6.2886 | 6.0512 | 6.8025 | 5.9989 | 5.7648 | 6.48 | 5.9151 | 5.6764 | 6.3896 | 6.0787 | 5.8252 | 6.5636 | 6.4703 | 6.1957 | 6.9581
CA | 40001150 | 6005 | From T23 to CNSS | 6005_Rockhampton Glenmore-Canning 66 kV | Limiting Line Name | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1
CA | 40001150 | 6005 | From T23 to CNSS | 6005_Rockhampton Glenmore-Canning 66 kV | Loading (A) | 25.0915 | 25.1124 | 25.1692 | 23.9355 | 23.924 | 23.9762 | 23.6013 | 23.5573 | 23.6416 | 24.254 | 24.1745 | 24.2853 | 25.8165 | 25.7122 | 25.745
CA | 40001150 | 6005 | From T23 to CNSS | 6005_Rockhampton Glenmore-Canning 66 kV | Loading (MVA) | 3.009 | 3.014 | 3.0202 | 2.8723 | 2.8726 | 2.8798 | 2.8339 | 2.8303 | 2.8415 | 2.914 | 2.905 | 2.9203 | 3.1028 | 3.0907 | 3.0942
CA | 40001150 | 6005 | From T23 to CNSS | 6005_Rockhampton Glenmore-Canning 66 kV | Loading (MW) | 1.0403 | 1.0672 | 1.0793 | 0.47858 | 0.49907 | 0.4809 | 0.088495 | 0.068017 | 0.086178 | 0.68203 | 0.66367 | 0.67972 | 1.2738 | 1.2555 | 1.2612
CA | 40001150 | 6005 | From T23 to CNSS | 6005_Rockhampton Glenmore-Canning 66 kV | Power Factor | 0.34574 | 0.35407 | 0.35735 | 0.16662 | 0.17374 | 0.16699 | 0.031228 | 0.024032 | 0.030328 | 0.23405 | 0.22846 | 0.23276 | 0.41054 | 0.4062 | 0.40761
CA | 40001150 | 6005 | From T23 to CNSS | 6005_Rockhampton Glenmore-Canning 66 kV | Rating (A) | 399 | 415 | 370 | 399 | 415 | 370 | 399 | 415 | 370 | 399 | 415 | 370 | 399 | 415 | 370
CA | 40001150 | 6005 | From T23 to CNSS | 6005_Rockhampton Glenmore-Canning 66 kV | Time | 16:30 | 18:30 | 0:00 | 14:00 | 17:30 | 4:00 | 14:00 | 17:30 | 4:00 | 14:00 | 17:00 | 4:00 | 14:00 | 17:00 | 8:30
CA | 40001150 | 6005 | From T23 to CNSS | 6005_Rockhampton Glenmore-Canning 66 kV | Voltage at Constrained Conductor | 69.2371 | 69.2943 | 69.2787 | 69.2833 | 69.323 | 69.3455 | 69.3239 | 69.3651 | 69.3916 | 69.366 | 69.3782 | 69.4264 | 69.3904 | 69.4006 | 69.3905
CA | 40001151 | 6053 | PDBS to PHSS | 6053_Parkhurst - Pandoin 66 kV | % of Rated A | 15.345 | 13.5642 | 14.7073 | 13.1017 | 11.5825 | 12.5591 | 11.1783 | 9.8842 | 10.7182 | 9.5382 | 8.4351 | 9.1477 | 8.4066 | 7.4278 | 8.0542
CA | 40001151 | 6053 | PDBS to PHSS | 6053_Parkhurst - Pandoin 66 kV | Limiting Line Name | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1
CA | 40001151 | 6053 | PDBS to PHSS | 6053_Parkhurst - Pandoin 66 kV | Loading (A) | 80.2542 | 80.2998 | 80.3019 | 68.5219 | 68.5685 | 68.5729 | 58.4625 | 58.5142 | 58.5214 | 49.8848 | 49.9358 | 49.9463 | 43.9663 | 43.9725 | 43.9757
CA | 40001151 | 6053 | PDBS to PHSS | 6053_Parkhurst - Pandoin 66 kV | Loading (MVA) | 9.609 | 9.6202 | 9.6205 | 8.2088 | 8.2208 | 8.2214 | 7.0062 | 7.0187 | 7.0196 | 5.9809 | 5.9917 | 5.993 | 5.2723 | 5.2735 | 5.2736
CA | 40001151 | 6053 | PDBS to PHSS | 6053_Parkhurst - Pandoin 66 kV | Loading (MW) | 8.4913 | 8.5025 | 8.5016 | 6.8037 | 6.815 | 6.8141 | 5.2312 | 5.2425 | 5.2416 | 3.7021 | 3.7134 | 3.7125 | 2.3217 | 2.3237 | 2.3245
CA | 40001151 | 6053 | PDBS to PHSS | 6053_Parkhurst - Pandoin 66 kV | Power Factor | 0.88368 | 0.88382 | 0.8837 | 0.82884 | 0.82899 | 0.82882 | 0.74666 | 0.74694 | 0.74671 | 0.61899 | 0.61976 | 0.61947 | 0.44037 | 0.44063 | 0.44078
CA | 40001151 | 6053 | PDBS to PHSS | 6053_Parkhurst - Pandoin 66 kV | Rating (A) | 523 | 592 | 546 | 523 | 592 | 546 | 523 | 592 | 546 | 523 | 592 | 546 | 523 | 592 | 546
CA | 40001151 | 6053 | PDBS to PHSS | 6053_Parkhurst - Pandoin 66 kV | Time | 16:30 | 21:00 | 0:00 | 16:30 | 21:00 | 0:00 | 16:30 | 21:00 | 0:00 | 16:30 | 21:00 | 0:00 | 16:30 | 17:00 | 7:00
CA | 40001151 | 6053 | PDBS to PHSS | 6053_Parkhurst - Pandoin 66 kV | Voltage at Constrained Conductor | 69.1271 | 69.1683 | 69.1688 | 69.1652 | 69.2196 | 69.2201 | 69.1897 | 69.2524 | 69.2529 | 69.2213 | 69.2749 | 69.2753 | 69.2337 | 69.2401 | 69.2366
CA | 40001158 | 6066 | BOCOOLIMA TEE WOODERSON | 6066_Bocoolima Tee -Wooderson 66 kV | % of Rated A | 3.2379 | 2.2805 | 2.3388 | 3.2398 | 2.2786 | 2.3401 | 3.241 | 2.2828 | 2.341 | 3.2431 | 2.2808 | 2.3419 | 3.2436 | 2.2846 | 2.3429
CA | 40001158 | 6066 | BOCOOLIMA TEE WOODERSON | 6066_Bocoolima Tee -Wooderson 66 kV | Limiting Line Name | TR_LINE 22217_1 | TR_LINE 22217_1 | TR_LINE 22217_1 | TR_LINE 22217_1 | TR_LINE 22217_1 | TR_LINE 22217_1 | TR_LINE 22217_1 | TR_LINE 22217_1 | TR_LINE 22217_1 | TR_LINE 22217_1 | TR_LINE 22217_1 | TR_LINE 22217_1 | TR_LINE 22217_1 | TR_LINE 22217_1 | TR_LINE 22217_1
CA | 40001158 | 6066 | BOCOOLIMA TEE WOODERSON | 6066_Bocoolima Tee -Wooderson 66 kV | Loading (A) | 5.472 | 5.4732 | 5.4727 | 5.4752 | 5.4685 | 5.4759 | 5.4773 | 5.4788 | 5.478 | 5.4809 | 5.474 | 5.48 | 5.4817 | 5.483 | 5.4824
CA | 40001158 | 6066 | BOCOOLIMA TEE WOODERSON | 6066_Bocoolima Tee -Wooderson 66 kV | Loading (MVA) | 0.65823 | 0.65853 | 0.65839 | 0.659 | 0.65739 | 0.65917 | 0.65952 | 0.65987 | 0.65968 | 0.66038 | 0.65871 | 0.66015 | 0.66058 | 0.66089 | 0.66074
CA | 40001158 | 6066 | BOCOOLIMA TEE WOODERSON | 6066_Bocoolima Tee -Wooderson 66 kV | Loading (MW) | 0.04696 | 0.04696 | 0.04696 | 0.046961 | 0.04696 | 0.046961 | 0.046961 | 0.046961 | 0.046961 | 0.046961 | 0.04696 | 0.046961 | 0.046961 | 0.046962 | 0.046962
CA | 40001158 | 6066 | BOCOOLIMA TEE WOODERSON | 6066_Bocoolima Tee -Wooderson 66 kV | Power Factor | 0.071343 | 0.071311 | 0.071326 | 0.07126 | 0.071434 | 0.071242 | 0.071205 | 0.071168 | 0.071187 | 0.071112 | 0.071292 | 0.071137 | 0.071092 | 0.071059 | 0.071074
CA | 40001158 | 6066 | BOCOOLIMA TEE WOODERSON | 6066_Bocoolima Tee -Wooderson 66 kV | Rating (A) | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234
CA | 40001158 | 6066 | BOCOOLIMA TEE WOODERSON | 6066_Bocoolima Tee -Wooderson 66 kV | Time | 16:30 | 17:00 | 7:00 | 16:30 | 18:30 | 7:00 | 16:30 | 17:00 | 7:00 | 16:30 | 21:00 | 7:30 | 16:30 | 17:00 | 7:00
CA | 40001158 | 6066 | BOCOOLIMA TEE WOODERSON | 6066_Bocoolima Tee -Wooderson 66 kV | Voltage at Constrained Conductor | 69.4496 | 69.4653 | 69.4581 | 69.4905 | 69.405 | 69.4993 | 69.5179 | 69.5362 | 69.5266 | 69.5636 | 69.4749 | 69.5515 | 69.5738 | 69.5902 | 69.5824
CA | 40001159 | 6051 | From PHSS to KESS | 6051_Parkhurst - Keppel 66 kV | % of Rated A | 9.0045 | 7.5664 | 8.174 | 8.9912 | 7.5552 | 8.1623 | 10.7462 | 8.6437 | 9.3385 | 13.3068 | 10.2879 | 11.4673 | 16.1719 | 12.2047 | 13.9364
CA | 40001159 | 6051 | From PHSS to KESS | 6051_Parkhurst - Keppel 66 kV | Limiting Line Name | TR_LINE 19655_1 | TR_LINE 13436_1 | TR_LINE 13436_1 | TR_LINE 19655_1 | TR_LINE 13436_1 | TR_LINE 13436_1 | TR_LINE 19655_1 | TR_LINE 13436_1 | TR_LINE 13436_1 | TR_LINE 19655_1 | TR_LINE 13436_1 | TR_LINE 19655_1 | TR_LINE 19655_1 | TR_LINE 13436_1 | TR_LINE 19655_1
CA | 40001159 | 6051 | From PHSS to KESS | 6051_Parkhurst - Keppel 66 kV | Loading (A) | 19.0895 | 22.3965 | 22.3969 | 19.0614 | 22.3633 | 22.3647 | 22.782 | 25.5853 | 25.5875 | 28.2104 | 30.4521 | 28.2096 | 34.2844 | 36.1258 | 34.2836
CA | 40001159 | 6051 | From PHSS to KESS | 6051_Parkhurst - Keppel 66 kV | Loading (MVA) | 2.2995 | 2.6865 | 2.6865 | 2.3023 | 2.6847 | 2.6849 | 2.7578 | 3.0737 | 3.074 | 3.4222 | 3.659 | 3.4221 | 4.1666 | 4.3412 | 4.1665
CA | 40001159 | 6051 | From PHSS to KESS | 6051_Parkhurst - Keppel 66 kV | Loading (MW) | 0.5496 | 0.56001 | 0.5597 | 0.59055 | 0.58017 | 0.58048 | 1.6496 | 1.6354 | 1.6358 | 2.6611 | 2.6406 | 2.661 | 3.5826 | 3.553 | 3.5825
CA | 40001159 | 6051 | From PHSS to KESS | 6051_Parkhurst - Keppel 66 kV | Power Factor | 0.23901 | 0.20846 | 0.20833 | 0.25651 | 0.2161 | 0.2162 | 0.59816 | 0.53208 | 0.53213 | 0.7776 | 0.72166 | 0.77759 | 0.85983 | 0.81844 | 0.85982
CA | 40001159 | 6051 | From PHSS to KESS | 6051_Parkhurst - Keppel 66 kV | Rating (A) | 212 | 296 | 274 | 212 | 296 | 274 | 212 | 296 | 274 | 212 | 296 | 246 | 212 | 296 | 246
CA | 40001159 | 6051 | From PHSS to KESS | 6051_Parkhurst - Keppel 66 kV | Time | 16:30 | 18:30 | 5:30 | 16:30 | 18:30 | 5:30 | 14:00 | 19:00 | 4:00 | 14:00 | 17:30 | 8:30 | 14:00 | 17:00 | 8:30
CA | 40001159 | 6051 | From PHSS to KESS | 6051_Parkhurst - Keppel 66 kV | Voltage at Constrained Conductor | 69.5463 | 69.2533 | 69.2543 | 69.733 | 69.3113 | 69.3123 | 69.8887 | 69.3599 | 69.3612 | 70.0384 | 69.3721 | 70.0386 | 70.166 | 69.3796 | 70.1662
CA | 40001161 | 6082 | From KESS to YPSS | 6082_Farnborough Tee - Yeppoon 66 kV | % of Rated A | 8.3144 | 5.9594 | 7.1708 | 8.3028 | 5.9508 | 7.1609 | 10.1814 | 7.2933 | 8.7766 | 12.8675 | 9.2152 | 11.0887 | 15.8166 | 11.3269 | 13.6302
CA | 40001161 | 6082 | From KESS to YPSS | 6082_Farnborough Tee - Yeppoon 66 kV | Limiting Line Name | TR_LINE 19629_1 | TR_LINE 19629_1 | TR_LINE 19629_1 | TR_LINE 19629_1 | TR_LINE 19629_1 | TR_LINE 19629_1 | TR_LINE 19629_1 | TR_LINE 19629_1 | TR_LINE 19629_1 | TR_LINE 19629_1 | TR_LINE 19629_1 | TR_LINE 19629_1 | TR_LINE 19629_1 | TR_LINE 19629_1 | TR_LINE 19629_1
CA | 40001161 | 6082 | From KESS to YPSS | 6082_Farnborough Tee - Yeppoon 66 kV | Loading (A) | 17.6266 | 17.64 | 17.6401 | 17.6019 | 17.6143 | 17.6157 | 21.5845 | 21.5882 | 21.5905 | 27.2791 | 27.2769 | 27.2783 | 33.5312 | 33.5275 | 33.5303
CA | 40001161 | 6082 | From KESS to YPSS | 6082_Farnborough Tee - Yeppoon 66 kV | Loading (MVA) | 2.1241 | 2.1275 | 2.1276 | 2.1272 | 2.1304 | 2.1307 | 2.6147 | 2.6177 | 2.618 | 3.3121 | 3.3124 | 3.312 | 4.0791 | 4.0793 | 4.079
CA | 40001161 | 6082 | From KESS to YPSS | 6082_Farnborough Tee - Yeppoon 66 kV | Loading (MW) | 0.54882 | 0.54899 | 0.54868 | 0.59133 | 0.59116 | 0.59146 | 1.6507 | 1.6504 | 1.6508 | 2.6628 | 2.6627 | 2.6627 | 3.5851 | 3.585 | 3.585
CA | 40001161 | 6082 | From KESS to YPSS | 6082_Farnborough Tee - Yeppoon 66 kV | Power Factor | 0.25837 | 0.25804 | 0.25789 | 0.27798 | 0.27748 | 0.2776 | 0.63131 | 0.6305 | 0.63055 | 0.80398 | 0.80386 | 0.80397 | 0.8789 | 0.87883 | 0.8789
CA | 40001161 | 6082 | From KESS to YPSS | 6082_Farnborough Tee - Yeppoon 66 kV | Rating (A) | 212 | 296 | 246 | 212 | 296 | 246 | 212 | 296 | 246 | 212 | 296 | 246 | 212 | 296 | 246
CA | 40001161 | 6082 | From KESS to YPSS | 6082_Farnborough Tee - Yeppoon 66 kV | Time | 16:30 | 18:30 | 5:30 | 16:30 | 18:30 | 5:30 | 14:00 | 19:00 | 4:00 | 14:00 | 17:00 | 8:30 | 14:00 | 17:00 | 8:30
CA | 40001161 | 6082 | From KESS to YPSS | 6082_Farnborough Tee - Yeppoon 66 kV | Voltage at Constrained Conductor | 69.575 | 69.6328 | 69.6339 | 69.7732 | 69.8305 | 69.8316 | 69.9396 | 70.0064 | 70.0078 | 70.0988 | 70.111 | 70.0989 | 70.2354 | 70.2457 | 70.2355
CA | 40001163 | 6075 | KESS to FBSS | 6075_Keppel - Farnborough 66 kV | % of Rated A | 0.31782 | 0.28972 | 0.35678 | 0.31872 | 0.29054 | 0.3578 | 0.3195 | 0.29128 | 0.3587 | 0.32023 | 0.29191 | 0.35948 | 0.32085 | 0.29246 | 0.36016
CA | 40001163 | 6075 | KESS to FBSS | 6075_Keppel - Farnborough 66 kV | Limiting Line Name | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2
CA | 40001163 | 6075 | KESS to FBSS | 6075_Keppel - Farnborough 66 kV | Loading (A) | 1.2013 | 1.2023 | 1.2024 | 1.2048 | 1.2058 | 1.2058 | 1.2077 | 1.2088 | 1.2088 | 1.2105 | 1.2114 | 1.2114 | 1.2128 | 1.2137 | 1.2137
CA | 40001163 | 6075 | KESS to FBSS | 6075_Keppel - Farnborough 66 kV | Loading (MVA) | 0.14477 | 0.14501 | 0.14502 | 0.1456 | 0.14584 | 0.14584 | 0.14631 | 0.14657 | 0.14658 | 0.14698 | 0.14721 | 0.14721 | 0.14755 | 0.14777 | 0.14778
CA | 40001163 | 6075 | KESS to FBSS | 6075_Keppel - Farnborough 66 kV | Loading (MW) | 3.6075e-06 | 3.6135e-06 | 3.6136e-06 | 3.628e-06 | 3.6339e-06 | 3.6341e-06 | 3.6458e-06 | 3.6524e-06 | 3.6525e-06 | 3.6626e-06 | 3.6682e-06 | 3.6682e-06 | 3.6767e-06 | 3.6821e-06 | 3.6823e-06
CA | 40001163 | 6075 | KESS to FBSS | 6075_Keppel - Farnborough 66 kV | Power Factor | 2.4919e-05 | 2.4919e-05 | 2.4919e-05 | 2.4918e-05 | 2.4918e-05 | 2.4918e-05 | 2.4919e-05 | 2.4918e-05 | 2.4918e-05 | 2.4919e-05 | 2.4918e-05 | 2.4918e-05 | 2.4918e-05 | 2.4918e-05 | 2.4918e-05
CA | 40001163 | 6075 | KESS to FBSS | 6075_Keppel - Farnborough 66 kV | Rating (A) | 378 | 415 | 337 | 378 | 415 | 337 | 378 | 415 | 337 | 378 | 415 | 337 | 378 | 415 | 337
CA | 40001163 | 6075 | KESS to FBSS | 6075_Keppel - Farnborough 66 kV | Time | 16:30 | 18:30 | 5:30 | 16:30 | 18:30 | 5:30 | 16:30 | 19:30 | 4:00 | 16:30 | 19:30 | 4:00 | 16:30 | 19:30 | 4:00
CA | 40001163 | 6075 | KESS to FBSS | 6075_Keppel - Farnborough 66 kV | Voltage at Constrained Conductor | 69.575 | 69.6328 | 69.6339 | 69.7732 | 69.8305 | 69.8316 | 69.9434 | 70.0065 | 70.0078 | 70.1044 | 70.1582 | 70.1594 | 70.2393 | 70.292 | 70.2931
CA | 40001218 | 6032 | Boyne Residental Tee to Awoonga | 6032_Boyne Residential Tee-Awoonga 66 kV | % of Rated A | 3.901 | 2.7838 | 3.5024 | 4.1596 | 2.9676 | 3.719 | 4.4158 | 3.15 | 3.9368 | 4.6655 | 3.3282 | 4.1491 | 4.8975 | 3.4916 | 4.3462
CA | 40001218 | 6032 | Boyne Residental Tee to Awoonga | 6032_Boyne Residential Tee-Awoonga 66 kV | Limiting Line Name | TR_LINE 69280_1 | TR_LINE 69280_1 | TR_LINE 69280_1 | TR_LINE 69280_1 | TR_LINE 69280_1 | TR_LINE 69280_1 | TR_LINE 69280_1 | TR_LINE 69280_1 | TR_LINE 69280_1 | TR_LINE 69280_1 | TR_LINE 69280_1 | TR_LINE 69280_1 | TR_LINE 69280_1 | TR_LINE 69280_1 | TR_LINE 69280_1
CA | 40001218 | 6032 | Boyne Residental Tee to Awoonga | 6032_Boyne Residential Tee-Awoonga 66 kV | Loading (A) | 8.2312 | 8.2121 | 8.5808 | 8.7767 | 8.7544 | 9.1116 | 9.3174 | 9.2925 | 9.6452 | 9.8442 | 9.8181 | 10.1652 | 10.3337 | 10.3003 | 10.6483
CA | 40001218 | 6032 | Boyne Residental Tee to Awoonga | 6032_Boyne Residential Tee-Awoonga 66 kV | Loading (MVA) | 0.98836 | 0.98385 | 1.0288 | 1.0545 | 1.0495 | 1.0934 | 1.12 | 1.1145 | 1.1584 | 1.184 | 1.1781 | 1.2214 | 1.2432 | 1.2362 | 1.2798
CA | 40001218 | 6032 | Boyne Residental Tee to Awoonga | 6032_Boyne Residential Tee-Awoonga 66 kV | Loading (MW) | 0.87401 | 0.86707 | 0.90593 | 0.97215 | 0.96523 | 1.0037 | 1.0605 | 1.0536 | 1.0922 | 1.1414 | 1.1344 | 1.173 | 1.2127 | 1.2052 | 1.2444
CA | 40001218 | 6032 | Boyne Residental Tee to Awoonga | 6032_Boyne Residential Tee-Awoonga 66 kV | Power Factor | 0.88431 | 0.88131 | 0.8806 | 0.92192 | 0.91974 | 0.91793 | 0.94693 | 0.94534 | 0.94284 | 0.96399 | 0.96291 | 0.96033 | 0.9755 | 0.97489 | 0.97228
CA | 40001218 | 6032 | Boyne Residental Tee to Awoonga | 6032_Boyne Residential Tee-Awoonga 66 kV | Rating (A) | 211 | 295 | 245 | 211 | 295 | 245 | 211 | 295 | 245 | 211 | 295 | 245 | 211 | 295 | 245
CA | 40001218 | 6032 | Boyne Residental Tee to Awoonga | 6032_Boyne Residential Tee-Awoonga 66 kV | Time | 15:30 | 17:30 | 4:00 | 15:30 | 17:30 | 4:00 | 15:30 | 17:30 | 4:00 | 15:30 | 17:30 | 4:00 | 15:30 | 17:30 | 4:00
CA | 40001218 | 6032 | Boyne Residental Tee to Awoonga | 6032_Boyne Residential Tee-Awoonga 66 kV | Voltage at Constrained Conductor | 69.3248 | 69.1693 | 69.2185 | 69.3661 | 69.2113 | 69.283 | 69.3979 | 69.2456 | 69.3415 | 69.4401 | 69.2748 | 69.373 | 69.4583 | 69.293 | 69.3931
CA | 40001219 | 6034 | Boyne Residental Tee to Boyne Residental | 6034_Boyne Residential Tee - BORE 66 kV | % of Rated A | 4.6098 | 3.4177 | 4.1435 | 7.397 | 5.4904 | 6.6496 | 9.9446 | 7.3738 | 8.9393 | 12.3419 | 9.161 | 11.104 | 14.5209 | 10.7691 | 13.0415
CA | 40001219 | 6034 | Boyne Residental Tee to Boyne Residental | 6034_Boyne Residential Tee - BORE 66 kV | Limiting Line Name | TR_LINE 18809_1 | TR_LINE 18809_1 | TR_LINE 18809_1 | TR_LINE 18809_1 | TR_LINE 18809_1 | TR_LINE 18809_1 | TR_LINE 18809_1 | TR_LINE 18809_1 | TR_LINE 18809_1 | TR_LINE 18809_1 | TR_LINE 18809_1 | TR_LINE 18809_1 | TR_LINE 18809_1 | TR_LINE 18809_1 | TR_LINE 18809_1
CA | 40001219 | 6034 | Boyne Residental Tee to Boyne Residental | 6034_Boyne Residential Tee - BORE 66 kV | Loading (A) | 7.6061 | 7.6215 | 7.624 | 12.2051 | 12.2437 | 12.2354 | 16.4087 | 16.4435 | 16.4483 | 20.3642 | 20.4289 | 20.4314 | 23.958 | 24.0136 | 23.9949
CA | 40001219 | 6034 | Boyne Residental Tee to Boyne Residental | 6034_Boyne Residential Tee - BORE 66 kV | Loading (MVA) | 0.91326 | 0.91309 | 0.91309 | 1.4663 | 1.4662 | 1.4663 | 1.9723 | 1.9722 | 1.9721 | 2.4492 | 2.4492 | 2.4492 | 2.8824 | 2.8823 | 2.8823
CA | 40001219 | 6034 | Boyne Residental Tee to Boyne Residental | 6034_Boyne Residential Tee - BORE 66 kV | Loading (MW) | 0.89719 | 0.89718 | 0.89719 | 1.4571 | 1.4571 | 1.4571 | 1.966 | 1.966 | 1.966 | 2.4448 | 2.4448 | 2.4448 | 2.8794 | 2.8793 | 2.8793
CA | 40001219 | 6034 | Boyne Residental Tee to Boyne Residental | 6034_Boyne Residential Tee - BORE 66 kV | Power Factor | 0.9824 | 0.98257 | 0.98258 | 0.99369 | 0.99378 | 0.99374 | 0.99684 | 0.99687 | 0.99689 | 0.99821 | 0.99822 | 0.99822 | 0.99895 | 0.99896 | 0.99896
CA | 40001219 | 6034 | Boyne Residental Tee to Boyne Residental | 6034_Boyne Residential Tee - BORE 66 kV | Rating (A) | 165 | 223 | 184 | 165 | 223 | 184 | 165 | 223 | 184 | 165 | 223 | 184 | 165 | 223 | 184
CA | 40001219 | 6034 | Boyne Residental Tee to Boyne Residental | 6034_Boyne Residential Tee - BORE 66 kV | Time | 12:00 | 17:30 | 6:30 | 12:00 | 17:00 | 6:30 | 12:00 | 17:30 | 6:30 | 12:00 | 17:00 | 7:00 | 12:00 | 17:30 | 6:00
CA | 40001219 | 6034 | Boyne Residental Tee to Boyne Residental | 6034_Boyne Residential Tee - BORE 66 kV | Voltage at Constrained Conductor | 69.3221 | 69.1693 | 69.1467 | 69.3633 | 69.1379 | 69.1884 | 69.3952 | 69.2456 | 69.2229 | 69.4374 | 69.2167 | 69.2082 | 69.4609 | 69.2984 | 69.353
CA | 40001235 | 6102 | BOAT CREEK TO YARWUN | 6102_Boat Creek - Yarwun 66 kV | % of Rated A | 8.0387 | 7.3704 | 8.9857 | 9.1435 | 8.428 | 10.274 | 9.1511 | 8.3888 | 10.2291 | 9.2448 | 8.5002 | 10.3632 | 9.2465 | 8.5015 | 10.3592
CA | 40001235 | 6102 | BOAT CREEK TO YARWUN | 6102_Boat Creek - Yarwun 66 kV | Limiting Line Name | TR_LINE 16861_2 | TR_LINE 16861_2 | TR_LINE 16861_2 | TR_LINE 16861_2 | TR_LINE 16861_2 | TR_LINE 16861_2 | TR_LINE 16861_2 | TR_LINE 16861_2 | TR_LINE 16861_2 | TR_LINE 16861_2 | TR_LINE 16861_2 | TR_LINE 16861_2 | TR_LINE 16861_2 | TR_LINE 16861_2 | TR_LINE 16861_2
CA | 40001235 | 6102 | BOAT CREEK TO YARWUN | 6102_Boat Creek - Yarwun 66 kV | Loading (A) | 59.4739 | 59.4669 | 59.4731 | 67.647 | 67.9985 | 67.9984 | 67.7026 | 67.6826 | 67.7016 | 68.3958 | 68.5807 | 68.5888 | 68.4087 | 68.5912 | 68.5625
CA | 40001235 | 6102 | BOAT CREEK TO YARWUN | 6102_Boat Creek - Yarwun 66 kV | Loading (MVA) | 6.9277 | 6.9277 | 6.9277 | 7.9385 | 7.9391 | 7.9391 | 7.9386 | 7.9386 | 7.9386 | 8.0396 | 8.0399 | 8.04 | 8.0397 | 8.04 | 8.0399
CA | 40001235 | 6102 | BOAT CREEK TO YARWUN | 6102_Boat Creek - Yarwun 66 kV | Loading (MW) | 6.9224 | 6.9224 | 6.9224 | 7.9294 | 7.9297 | 7.9297 | 7.9295 | 7.9294 | 7.9295 | 8.0301 | 8.0303 | 8.0303 | 8.0301 | 8.0303 | 8.0303
CA | 40001235 | 6102 | BOAT CREEK TO YARWUN | 6102_Boat Creek - Yarwun 66 kV | Power Factor | 0.99923 | 0.99923 | 0.99923 | 0.99885 | 0.99882 | 0.99882 | 0.99884 | 0.99885 | 0.99884 | 0.99881 | 0.9988 | 0.9988 | 0.99881 | 0.9988 | 0.9988
CA | 40001235 | 6102 | BOAT CREEK TO YARWUN | 6102_Boat Creek - Yarwun 66 kV | Rating (A) | 740 | 807 | 662 | 740 | 807 | 662 | 740 | 807 | 662 | 740 | 807 | 662 | 740 | 807 | 662
CA | 40001235 | 6102 | BOAT CREEK TO YARWUN | 6102_Boat Creek - Yarwun 66 kV | Time | 9:30 | 17:00 | 8:30 | 9:30 | 19:00 | 5:00 | 9:30 | 17:00 | 8:30 | 9:30 | 17:30 | 6:30 | 9:30 | 17:30 | 6:00
CA | 40001235 | 6102 | BOAT CREEK TO YARWUN | 6102_Boat Creek - Yarwun 66 kV | Voltage at Constrained Conductor | 67.2516 | 67.2595 | 67.2525 | 67.7535 | 67.4082 | 67.4083 | 67.6987 | 67.7182 | 67.6997 | 67.8651 | 67.6847 | 67.6767 | 67.8525 | 67.6745 | 67.7025
CA | 40001238 | 6007 | From T26 to COSS | 6007_Biloela - Coominglah Tee 66 kV | % of Rated A | 14.6045 | 11.6448 | 12.2324 | 14.4667 | 11.3958 | 12.0102 | 14.4215 | 11.3507 | 11.9726 | 14.4851 | 11.3854 | 12.0257 | 14.4908 | 11.5122 | 12.0915
CA | 40001238 | 6007 | From T26 to COSS | 6007_Biloela - Coominglah Tee 66 kV | Limiting Line Name | TR_LINE 18121_1 | TR_LINE 18121_1 | TR_LINE 18121_1 | TR_LINE 18121_1 | TR_LINE 18121_1 | TR_LINE 18121_1 | TR_LINE 18121_1 | TR_LINE 18121_1 | TR_LINE 18121_1 | TR_LINE 18121_1 | TR_LINE 18121_1 | TR_LINE 18121_1 | TR_LINE 18121_1 | TR_LINE 18121_1 | TR_LINE 18121_1
CA | 40001238 | 6007 | From T26 to COSS | 6007_Biloela - Coominglah Tee 66 kV | Loading (A) | 19.2779 | 19.4468 | 19.4496 | 19.096 | 19.031 | 19.0962 | 19.0363 | 18.9556 | 19.0364 | 19.1204 | 19.0135 | 19.1209 | 19.1279 | 19.2254 | 19.2254
CA | 40001238 | 6007 | From T26 to COSS | 6007_Biloela - Coominglah Tee 66 kV | Loading (MVA) | 2.3209 | 2.3367 | 2.3373 | 2.2821 | 2.2917 | 2.2822 | 2.302 | 2.2825 | 2.302 | 2.3121 | 2.2861 | 2.3122 | 2.3128 | 2.3114 | 2.3114
CA | 40001238 | 6007 | From T26 to COSS | 6007_Biloela - Coominglah Tee 66 kV | Loading (MW) | 0.50957 | 0.51027 | 0.51028 | 0.28121 | 0.28082 | 0.28121 | 0.063037 | 0.062801 | 0.063038 | 0.151 | 0.15131 | 0.151 | 0.34664 | 0.34616 | 0.34616
CA | 40001238 | 6007 | From T26 to COSS | 6007_Biloela - Coominglah Tee 66 kV | Power Factor | 0.21956 | 0.21838 | 0.21832 | 0.12322 | 0.12254 | 0.12322 | 0.027384 | 0.027514 | 0.027383 | 0.065308 | 0.066186 | 0.065304 | 0.14988 | 0.14977 | 0.14977
CA | 40001238 | 6007 | From T26 to COSS | 6007_Biloela - Coominglah Tee 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
CA | 40001238 | 6007 | From T26 to COSS | 6007_Biloela - Coominglah Tee 66 kV | Time | 16:30 | 18:00 | 6:00 | 16:00 | 17:00 | 7:30 | 15:30 | 17:00 | 8:30 | 15:30 | 21:30 | 8:00 | 16:00 | 21:30 | 0:00
CA | 40001238 | 6007 | From T26 to COSS | 6007_Biloela - Coominglah Tee 66 kV | Voltage at Constrained Conductor | 69.5092 | 69.3721 | 69.3827 | 68.9985 | 69.5256 | 68.9991 | 69.8176 | 69.5216 | 69.8179 | 69.8143 | 69.4186 | 69.8164 | 69.8082 | 69.4116 | 69.4116
CA | 40001239 | 6008 | From T26 to WNSS | 6008_Biloela - Wowan 66 kV | % of Rated A | 13.4161 | 10.6203 | 11.1577 | 11.5054 | 9.0751 | 9.5515 | 9.696 | 7.6571 | 8.0495 | 8.1599 | 6.4428 | 6.7743 | 7.0938 | 5.5882 | 5.8893
CA | 40001239 | 6008 | From T26 to WNSS | 6008_Biloela - Wowan 66 kV | Limiting Line Name | TR_LINE 21790_1 | TR_LINE 21790_1 | TR_LINE 21790_1 | TR_LINE 21790_1 | TR_LINE 21790_1 | TR_LINE 21790_1 | TR_LINE 21790_1 | TR_LINE 21790_1 | TR_LINE 21790_1 | TR_LINE 21790_1 | TR_LINE 21790_1 | TR_LINE 21790_1 | TR_LINE 21790_1 | TR_LINE 21790_1 | TR_LINE 21790_1
CA | 40001239 | 6008 | From T26 to WNSS | 6008_Biloela - Wowan 66 kV | Loading (A) | 17.7093 | 17.7359 | 17.7408 | 15.1871 | 15.1553 | 15.1869 | 12.7987 | 12.7874 | 12.7988 | 10.771 | 10.7594 | 10.7711 | 9.3639 | 9.3323 | 9.3639
CA | 40001239 | 6008 | From T26 to WNSS | 6008_Biloela - Wowan 66 kV | Loading (MVA) | 2.1317 | 2.1297 | 2.1293 | 1.8148 | 1.8197 | 1.8149 | 1.5294 | 1.5353 | 1.5294 | 1.3025 | 1.2937 | 1.3025 | 1.1322 | 1.122 | 1.1322
CA | 40001239 | 6008 | From T26 to WNSS | 6008_Biloela - Wowan 66 kV | Loading (MW) | 1.9096 | 1.9097 | 1.9097 | 1.5459 | 1.5458 | 1.5459 | 1.1863 | 1.1862 | 1.1863 | 0.83412 | 0.83414 | 0.83412 | 0.51628 | 0.51627 | 0.51628
CA | 40001239 | 6008 | From T26 to WNSS | 6008_Biloela - Wowan 66 kV | Power Factor | 0.89584 | 0.8967 | 0.89689 | 0.85182 | 0.84947 | 0.85181 | 0.77566 | 0.77263 | 0.77568 | 0.64042 | 0.64478 | 0.6404 | 0.45599 | 0.46014 | 0.45599
CA | 40001239 | 6008 | From T26 to WNSS | 6008_Biloela - Wowan 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
CA | 40001239 | 6008 | From T26 to WNSS | 6008_Biloela - Wowan 66 kV | Time | 9:30 | 17:30 | 6:30 | 9:30 | 17:30 | 8:30 | 16:00 | 17:30 | 8:00 | 15:30 | 21:30 | 8:00 | 16:00 | 21:30 | 7:30
CA | 40001239 | 6008 | From T26 to WNSS | 6008_Biloela - Wowan 66 kV | Voltage at Constrained Conductor | 69.496 | 69.3277 | 69.295 | 68.992 | 69.3231 | 68.994 | 68.9915 | 69.3201 | 68.9891 | 69.8143 | 69.4187 | 69.8165 | 69.8085 | 69.4119 | 69.8091
CA | 40001243 | 6030 | From LMSS to MTSS | 6030_Littlemore - Monto 66 kV | % of Rated A | 5.3914 | 4.2624 | 4.4764 | 5.3985 | 4.2619 | 4.4824 | 5.4042 | 4.2727 | 4.4871 | 5.411 | 4.2716 | 4.4914 | 5.4147 | 4.2809 | 4.4958
CA | 40001243 | 6030 | From LMSS to MTSS | 6030_Littlemore - Monto 66 kV | Limiting Line Name | TR_LINE 19505_1 | TR_LINE 19505_1 | TR_LINE 19505_1 | TR_LINE 19505_1 | TR_LINE 19505_1 | TR_LINE 19505_1 | TR_LINE 19505_1 | TR_LINE 19505_1 | TR_LINE 19505_1 | TR_LINE 19505_1 | TR_LINE 19505_1 | TR_LINE 19505_1 | TR_LINE 19505_1 | TR_LINE 19505_1 | TR_LINE 19505_1
CA | 40001243 | 6030 | From LMSS to MTSS | 6030_Littlemore - Monto 66 kV | Loading (A) | 7.1166 | 7.1182 | 7.1175 | 7.1261 | 7.1174 | 7.127 | 7.1336 | 7.1355 | 7.1345 | 7.1426 | 7.1335 | 7.1413 | 7.1474 | 7.149 | 7.1482
CA | 40001243 | 6030 | From LMSS to MTSS | 6030_Littlemore - Monto 66 kV | Loading (MVA) | 0.8658 | 0.86619 | 0.86601 | 0.86811 | 0.86598 | 0.86833 | 0.86994 | 0.8704 | 0.87016 | 0.87213 | 0.86992 | 0.87183 | 0.8733 | 0.87371 | 0.87352
CA | 40001243 | 6030 | From LMSS to MTSS | 6030_Littlemore - Monto 66 kV | Loading (MW) | 0.0015832 | 0.001584 | 0.0015836 | 0.0015875 | 0.0015836 | 0.0015879 | 0.0015908 | 0.0015917 | 0.0015912 | 0.0015948 | 0.0015908 | 0.0015943 | 0.001597 | 0.0015977 | 0.0015974
CA | 40001243 | 6030 | From LMSS to MTSS | 6030_Littlemore - Monto 66 kV | Power Factor | 0.0018286 | 0.0018286 | 0.0018286 | 0.0018286 | 0.0018286 | 0.0018286 | 0.0018286 | 0.0018286 | 0.0018286 | 0.0018286 | 0.0018286 | 0.0018286 | 0.0018286 | 0.0018286 | 0.0018286
CA | 40001243 | 6030 | From LMSS to MTSS | 6030_Littlemore - Monto 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
CA | 40001243 | 6030 | From LMSS to MTSS | 6030_Littlemore - Monto 66 kV | Time | 16:30 | 17:00 | 7:00 | 16:30 | 18:30 | 7:00 | 16:30 | 17:00 | 7:00 | 16:30 | 21:00 | 7:30 | 16:30 | 17:00 | 7:00
CA | 40001243 | 6030 | From LMSS to MTSS | 6030_Littlemore - Monto 66 kV | Voltage at Constrained Conductor | 70.24 | 70.2559 | 70.2486 | 70.3336 | 70.2474 | 70.3424 | 70.4078 | 70.4263 | 70.4166 | 70.4962 | 70.407 | 70.484 | 70.5436 | 70.5602 | 70.5523
CA | 40001244 | 6045 | From MTSS to COSS | 6045_Coominglah Tee - Monto 66 kV | % of Rated A | 10.7688 | 8.6179 | 9.0528 | 10.6478 | 8.3547 | 8.8398 | 10.5919 | 8.3099 | 8.7946 | 10.6341 | 8.3589 | 8.8285 | 10.6992 | 8.5041 | 8.932
CA | 40001244 | 6045 | From MTSS to COSS | 6045_Coominglah Tee - Monto 66 kV | Limiting Line Name | TR_LINE 75765_1 | TR_LINE 75765_1 | TR_LINE 75765_1 | TR_LINE 75765_1 | TR_LINE 75765_1 | TR_LINE 75765_1 | TR_LINE 75765_1 | TR_LINE 75765_1 | TR_LINE 75765_1 | TR_LINE 75765_1 | TR_LINE 75765_1 | TR_LINE 75765_1 | TR_LINE 75765_1 | TR_LINE 75765_1 | TR_LINE 75765_1
CA | 40001244 | 6045 | From MTSS to COSS | 6045_Coominglah Tee - Monto 66 kV | Loading (A) | 14.2148 | 14.3919 | 14.3939 | 14.0551 | 13.9523 | 14.0552 | 13.9813 | 13.8775 | 13.9834 | 14.037 | 13.9594 | 14.0374 | 14.1229 | 14.2019 | 14.2019
CA | 40001244 | 6045 | From MTSS to COSS | 6045_Coominglah Tee - Monto 66 kV | Loading (MVA) | 1.7219 | 1.7401 | 1.7406 | 1.692 | 1.6923 | 1.6921 | 1.6849 | 1.6849 | 1.6854 | 1.7131 | 1.694 | 1.7132 | 1.7048 | 1.7248 | 1.7248
CA | 40001244 | 6045 | From MTSS to COSS | 6045_Coominglah Tee - Monto 66 kV | Loading (MW) | 0.42035 | 0.42065 | 0.42066 | 0.21749 | 0.21729 | 0.21749 | 0.023169 | 0.022969 | 0.023172 | 0.16953 | 0.16964 | 0.16953 | 0.34618 | 0.34607 | 0.34607
CA | 40001244 | 6045 | From MTSS to COSS | 6045_Coominglah Tee - Monto 66 kV | Power Factor | 0.24412 | 0.24174 | 0.24167 | 0.12854 | 0.1284 | 0.12854 | 0.013751 | 0.013632 | 0.013748 | 0.09896 | 0.10014 | 0.098954 | 0.20306 | 0.20064 | 0.20064
CA | 40001244 | 6045 | From MTSS to COSS | 6045_Coominglah Tee - Monto 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
CA | 40001244 | 6045 | From MTSS to COSS | 6045_Coominglah Tee - Monto 66 kV | Time | 16:30 | 18:00 | 6:00 | 16:00 | 17:00 | 7:30 | 16:30 | 17:00 | 7:00 | 15:30 | 21:30 | 8:00 | 16:30 | 21:30 | 0:00
CA | 40001244 | 6045 | From MTSS to COSS | 6045_Coominglah Tee - Monto 66 kV | Voltage at Constrained Conductor | 69.9372 | 69.806 | 69.8166 | 69.5042 | 70.0291 | 69.5048 | 69.5782 | 70.0965 | 69.5887 | 70.4614 | 70.0627 | 70.4635 | 69.6926 | 70.1192 | 70.1192
CA | 40216264 | 6080 | BBBS TO BKSS | 6080_Barcaldine - Blackall 66 kV | % of Rated A | 3.4247 | 3.416 | 3.9314 | 3.349 | 3.3443 | 3.8489 | 3.316 | 3.314 | 3.814 | 3.3092 | 3.3089 | 3.8082 | 3.3159 | 3.3167 | 3.8172
CA | 40216264 | 6080 | BBBS TO BKSS | 6080_Barcaldine - Blackall 66 kV | Limiting Line Name | TR_LINE 22558_1 | TR_LINE 22558_1 | TR_LINE 22558_1 | TR_LINE 22558_1 | TR_LINE 22558_1 | TR_LINE 22558_1 | TR_LINE 22558_1 | TR_LINE 22558_1 | TR_LINE 22558_1 | TR_LINE 22558_1 | TR_LINE 22558_1 | TR_LINE 22558_1 | TR_LINE 22558_1 | TR_LINE 22558_1 | TR_LINE 22558_1
CA | 40216264 | 6080 | BBBS TO BKSS | 6080_Barcaldine - Blackall 66 kV | Loading (A) | 13.2194 | 13.2881 | 13.2882 | 12.9273 | 13.0093 | 13.0093 | 12.7997 | 12.8914 | 12.8915 | 12.7734 | 12.8718 | 12.8718 | 12.7994 | 12.902 | 12.9021
CA | 40216264 | 6080 | BBBS TO BKSS | 6080_Barcaldine - Blackall 66 kV | Loading (MVA) | 1.529 | 1.5461 | 1.5461 | 1.4947 | 1.5142 | 1.5142 | 1.4795 | 1.5009 | 1.5009 | 1.4761 | 1.4989 | 1.4989 | 1.4788 | 1.5027 | 1.5027
CA | 40216264 | 6080 | BBBS TO BKSS | 6080_Barcaldine - Blackall 66 kV | Loading (MW) | 0.41299 | 0.41303 | 0.41303 | 0.24495 | 0.245 | 0.245 | 0.10686 | 0.10692 | 0.10692 | 0.0063328 | 0.0062654 | 0.0062654 | 0.089774 | 0.089705 | 0.089705
CA | 40216264 | 6080 | BBBS TO BKSS | 6080_Barcaldine - Blackall 66 kV | Power Factor | 0.27011 | 0.26714 | 0.26714 | 0.16388 | 0.1618 | 0.1618 | 0.072227 | 0.071241 | 0.07124 | 0.0042902 | 0.0041799 | 0.0041798 | 0.060708 | 0.059696 | 0.059695
CA | 40216264 | 6080 | BBBS TO BKSS | 6080_Barcaldine - Blackall 66 kV | Rating (A) | 386 | 389 | 338 | 386 | 389 | 338 | 386 | 389 | 338 | 386 | 389 | 338 | 386 | 389 | 338
CA | 40216264 | 6080 | BBBS TO BKSS | 6080_Barcaldine - Blackall 66 kV | Time | 16:30 | 21:30 | 5:00 | 16:30 | 21:30 | 5:00 | 16:30 | 21:30 | 5:00 | 16:30 | 21:30 | 5:00 | 16:30 | 21:00 | 5:00
CA | 40216264 | 6080 | BBBS TO BKSS | 6080_Barcaldine - Blackall 66 kV | Voltage at Constrained Conductor | 66.7762 | 67.176 | 67.1765 | 66.7555 | 67.1999 | 67.2003 | 66.7366 | 67.2184 | 67.2188 | 66.7191 | 67.2331 | 67.2334 | 66.7046 | 67.2439 | 67.2442
CA | 40218335 | 6046 | MMLS-MMSS-WOWA | 6046_Mt Morgan - Wowan 66 kV | % of Rated A | 5.8961 | 4.6603 | 4.8949 | 5.8955 | 4.6598 | 4.8944 | 5.895 | 4.6594 | 4.894 | 5.8945 | 4.659 | 4.8935 | 5.8942 | 4.6588 | 4.8933
CA | 40218335 | 6046 | MMLS-MMSS-WOWA | 6046_Mt Morgan - Wowan 66 kV | Limiting Line Name | TR_LINE 22233_1 | TR_LINE 22233_1 | TR_LINE 22233_1 | TR_LINE 22233_1 | TR_LINE 22233_1 | TR_LINE 22233_1 | TR_LINE 22233_1 | TR_LINE 22233_1 | TR_LINE 22233_1 | TR_LINE 22233_1 | TR_LINE 22233_1 | TR_LINE 22233_1 | TR_LINE 22233_1 | TR_LINE 22233_1 | TR_LINE 22233_1
CA | 40218335 | 6046 | MMLS-MMSS-WOWA | 6046_Mt Morgan - Wowan 66 kV | Loading (A) | 7.7828 | 7.7827 | 7.7828 | 7.782 | 7.7819 | 7.782 | 7.7814 | 7.7812 | 7.7814 | 7.7807 | 7.7806 | 7.7807 | 7.7803 | 7.7802 | 7.7803
CA | 40218335 | 6046 | MMLS-MMSS-WOWA | 6046_Mt Morgan - Wowan 66 kV | Loading (MVA) | 0.93538 | 0.9355 | 0.93539 | 0.93607 | 0.93622 | 0.93607 | 0.93664 | 0.93679 | 0.93665 | 0.93723 | 0.93738 | 0.93724 | 0.93761 | 0.93773 | 0.93761
CA | 40218335 | 6046 | MMLS-MMSS-WOWA | 6046_Mt Morgan - Wowan 66 kV | Loading (MW) | 0.7006 | 0.7006 | 0.7006 | 0.7006 | 0.7006 | 0.7006 | 0.7006 | 0.7006 | 0.7006 | 0.7006 | 0.70061 | 0.7006 | 0.70061 | 0.70061 | 0.70061
CA | 40218335 | 6046 | MMLS-MMSS-WOWA | 6046_Mt Morgan - Wowan 66 kV | Power Factor | 0.749 | 0.74891 | 0.749 | 0.74845 | 0.74833 | 0.74845 | 0.748 | 0.74787 | 0.74799 | 0.74752 | 0.74741 | 0.74752 | 0.74723 | 0.74713 | 0.74722
CA | 40218335 | 6046 | MMLS-MMSS-WOWA | 6046_Mt Morgan - Wowan 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
CA | 40218335 | 6046 | MMLS-MMSS-WOWA | 6046_Mt Morgan - Wowan 66 kV | Time | 9:30 | 17:00 | 8:30 | 9:30 | 17:00 | 8:30 | 9:30 | 17:00 | 8:30 | 9:30 | 17:00 | 8:30 | 9:30 | 17:00 | 8:30
CA | 40218335 | 6046 | MMLS-MMSS-WOWA | 6046_Mt Morgan - Wowan 66 kV | Voltage at Constrained Conductor | 69.3893 | 69.399 | 69.3897 | 69.447 | 69.4597 | 69.4473 | 69.4953 | 69.5081 | 69.4957 | 69.5451 | 69.5575 | 69.5455 | 69.5765 | 69.587 | 69.5769
CA | 82575918 | 6109 | 6109 CLINTON INDUSTRIAL 66KV FEEDER | 6109_Gladstone North - Clinton 66 kV | % of Rated A | 26.2414 | 21.0853 | 24.9213 | 23.2624 | 19.6242 | 23.1991 | 20.7788 | 18.5135 | 21.8892 | 18.8729 | 17.744 | 20.9809 | 17.6801 | 17.3417 | 20.5069
CA | 82575918 | 6109 | 6109 CLINTON INDUSTRIAL 66KV FEEDER | 6109_Gladstone North - Clinton 66 kV | Limiting Line Name | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 60722_1
CA | 82575918 | 6109 | 6109 CLINTON INDUSTRIAL 66KV FEEDER | 6109_Gladstone North - Clinton 66 kV | Loading (A) | 95.2562 | 114.9147 | 114.8873 | 84.4424 | 106.9518 | 106.948 | 75.427 | 100.8986 | 100.9093 | 68.5086 | 96.705 | 96.7219 | 64.1787 | 94.512 | 94.537
CA | 82575918 | 6109 | 6109 CLINTON INDUSTRIAL 66KV FEEDER | 6109_Gladstone North - Clinton 66 kV | Loading (MVA) | 11.362 | 13.6134 | 13.6029 | 10.0728 | 12.6707 | 12.6676 | 8.9969 | 11.9553 | 11.9566 | 8.1737 | 11.4585 | 11.4605 | 7.6555 | 11.1975 | 11.2006
CA | 82575918 | 6109 | 6109 CLINTON INDUSTRIAL 66KV FEEDER | 6109_Gladstone North - Clinton 66 kV | Loading (MW) | 8.2654 | 7.3371 | 7.3368 | 6.4602 | 5.5316 | 5.5303 | 4.7125 | 3.7853 | 3.7806 | 3.0263 | 2.0991 | 2.0944 | 1.4874 | 0.55934 | 0.53685
CA | 82575918 | 6109 | 6109 CLINTON INDUSTRIAL 66KV FEEDER | 6109_Gladstone North - Clinton 66 kV | Power Factor | 0.72746 | 0.53896 | 0.53936 | 0.64135 | 0.43656 | 0.43657 | 0.52379 | 0.31662 | 0.31619 | 0.37025 | 0.18319 | 0.18275 | 0.19429 | 0.049953 | 0.04793
CA | 82575918 | 6109 | 6109 CLINTON INDUSTRIAL 66KV FEEDER | 6109_Gladstone North - Clinton 66 kV | Rating (A) | 363 | 545 | 461 | 363 | 545 | 461 | 363 | 545 | 461 | 363 | 545 | 461 | 363 | 545 | 461
CA | 82575918 | 6109 | 6109 CLINTON INDUSTRIAL 66KV FEEDER | 6109_Gladstone North - Clinton 66 kV | Time | 16:30 | 18:30 | 0:00 | 16:30 | 18:30 | 0:00 | 16:30 | 21:00 | 0:00 | 16:30 | 21:00 | 0:00 | 16:30 | 21:00 | 4:00
CA | 82575918 | 6109 | 6109 CLINTON INDUSTRIAL 66KV FEEDER | 6109_Gladstone North - Clinton 66 kV | Voltage at Constrained Conductor | 68.8652 | 68.3961 | 68.3593 | 68.87 | 68.3993 | 68.3848 | 68.8665 | 68.409 | 68.4094 | 68.8833 | 68.4095 | 68.4099 | 68.8688 | 68.4025 | 68.4033
CA | 82588694 | 7290 | Boat Creek - Yarwun 132 kV | 7290_Boat Creek - Yarwun 132 kV | % of Rated A | 11.2442 | 10.1575 | 11.9142 | 11.6397 | 10.5118 | 12.3332 | 11.7193 | 10.5852 | 12.4176 | 11.8127 | 10.6973 | 12.5474 | 11.8147 | 10.6987 | 12.5432
CA | 82588694 | 7290 | Boat Creek - Yarwun 132 kV | 7290_Boat Creek - Yarwun 132 kV | Limiting Line Name | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1
CA | 82588694 | 7290 | Boat Creek - Yarwun 132 kV | 7290_Boat Creek - Yarwun 132 kV | Loading (A) | 99.9587 | 99.9476 | 99.9574 | 103.4769 | 103.4362 | 103.4756 | 104.1812 | 104.1544 | 104.1799 | 105.0153 | 105.2578 | 105.2688 | 105.0323 | 105.272 | 105.2337
CA | 82588694 | 7290 | Boat Creek - Yarwun 132 kV | 7290_Boat Creek - Yarwun 132 kV | Loading (MVA) | 23.9083 | 23.9086 | 23.9083 | 24.6474 | 24.6495 | 24.6474 | 24.7947 | 24.796 | 24.7948 | 25.0592 | 25.0461 | 25.0455 | 25.0582 | 25.0454 | 25.0475
CA | 82588694 | 7290 | Boat Creek - Yarwun 132 kV | 7290_Boat Creek - Yarwun 132 kV | Loading (MW) | 23.8864 | 23.8864 | 23.8864 | 24.59 | 24.59 | 24.59 | 24.7415 | 24.7415 | 24.7415 | 24.9918 | 24.9927 | 24.9928 | 24.9919 | 24.9928 | 24.9928
CA | 82588694 | 7290 | Boat Creek - Yarwun 132 kV | 7290_Boat Creek - Yarwun 132 kV | Power Factor | 0.99908 | 0.99907 | 0.99908 | 0.99767 | 0.99758 | 0.99767 | 0.99786 | 0.9978 | 0.99785 | 0.99731 | 0.99787 | 0.99789 | 0.99735 | 0.9979 | 0.99782
CA | 82588694 | 7290 | Boat Creek - Yarwun 132 kV | 7290_Boat Creek - Yarwun 132 kV | Rating (A) | 889 | 984 | 839 | 889 | 984 | 839 | 889 | 984 | 839 | 889 | 984 | 839 | 889 | 984 | 839
CA | 82588694 | 7290 | Boat Creek - Yarwun 132 kV | 7290_Boat Creek - Yarwun 132 kV | Time | 9:30 | 17:00 | 8:30 | 9:30 | 17:00 | 8:30 | 9:30 | 17:00 | 8:30 | 9:30 | 17:30 | 6:30 | 9:30 | 17:30 | 6:00
CA | 82588694 | 7290 | Boat Creek - Yarwun 132 kV | 7290_Boat Creek - Yarwun 132 kV | Voltage at Constrained Conductor | 138.0915 | 138.1089 | 138.0935 | 137.5202 | 137.5863 | 137.5223 | 137.4069 | 137.4497 | 137.4091 | 137.7697 | 137.3803 | 137.363 | 137.7421 | 137.3581 | 137.4194
CA | 82588698 | 7291 | Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | % of Rated A | 11.2993 | 10.2073 | 11.9726 | 11.6956 | 10.5623 | 12.3925 | 11.7756 | 10.636 | 12.4772 | 11.8695 | 10.7487 | 12.6076 | 11.8714 | 10.7501 | 12.6034
CA | 82588698 | 7291 | Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | Limiting Line Name | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1
CA | 82588698 | 7291 | Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | Loading (A) | 100.4493 | 100.4381 | 100.448 | 103.9741 | 103.9332 | 103.9728 | 104.6827 | 104.6557 | 104.6813 | 105.5199 | 105.7644 | 105.7755 | 105.537 | 105.7787 | 105.7402
CA | 82588698 | 7291 | Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | Loading (MVA) | 24.0257 | 24.0261 | 24.0258 | 24.7661 | 24.7683 | 24.7662 | 24.9141 | 24.9155 | 24.9142 | 25.1799 | 25.1667 | 25.1662 | 25.1789 | 25.166 | 25.1681
CA | 82588698 | 7291 | Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | Loading (MW) | 24.0033 | 24.0033 | 24.0033 | 24.7081 | 24.708 | 24.7081 | 24.8601 | 24.8601 | 24.8601 | 25.1118 | 25.1126 | 25.1126 | 25.1118 | 25.1126 | 25.1126
CA | 82588698 | 7291 | Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | Power Factor | 0.99907 | 0.99905 | 0.99907 | 0.99766 | 0.99757 | 0.99765 | 0.99783 | 0.99778 | 0.99783 | 0.99729 | 0.99785 | 0.99787 | 0.99733 | 0.99788 | 0.9978
CA | 82588698 | 7291 | Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | Rating (A) | 889 | 984 | 839 | 889 | 984 | 839 | 889 | 984 | 839 | 889 | 984 | 839 | 889 | 984 | 839
CA | 82588698 | 7291 | Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | Time | 9:30 | 17:00 | 8:30 | 9:30 | 17:00 | 8:30 | 9:30 | 17:00 | 8:30 | 9:30 | 17:30 | 6:30 | 9:30 | 17:30 | 6:00
CA | 82588698 | 7291 | Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | Voltage at Constrained Conductor | 138.0921 | 138.1094 | 138.0941 | 137.5218 | 137.588 | 137.5239 | 137.4075 | 137.4503 | 137.4097 | 137.7714 | 137.3809 | 137.3636 | 137.7438 | 137.3586 | 137.42
CA | 82860724 | 6022 | GSBS TO CALLIOPE | 6022_Gladstone South - Calliope 66 kV | % of Rated A | 3.3563 | 3.1471 | 3.5344 | 3.9108 | 3.6688 | 4.1128 | 4.4914 | 4.2149 | 4.7176 | 5.0768 | 4.7657 | 5.3268 | 5.6297 | 5.2847 | 5.9019
CA | 82860724 | 6022 | GSBS TO CALLIOPE | 6022_Gladstone South - Calliope 66 kV | Limiting Line Name | TR_LINE 72653_1 | TR_LINE 72653_1 | TR_LINE 72653_1 | TR_LINE 72653_1 | TR_LINE 72653_1 | TR_LINE 72653_1 | TR_LINE 72653_1 | TR_LINE 72653_1 | TR_LINE 72653_1 | TR_LINE 72653_1 | TR_LINE 72653_1 | TR_LINE 72653_1 | TR_LINE 72653_1 | TR_LINE 72653_1 | TR_LINE 72653_1
CA | 82860724 | 6022 | GSBS TO CALLIOPE | 6022_Gladstone South - Calliope 66 kV | Loading (A) | 20.9095 | 20.8967 | 21.1708 | 24.3642 | 24.3611 | 24.6359 | 27.9817 | 27.9869 | 28.2583 | 31.6285 | 31.6442 | 31.9074 | 35.0731 | 35.0903 | 35.3524
CA | 82860724 | 6022 | GSBS TO CALLIOPE | 6022_Gladstone South - Calliope 66 kV | Loading (MVA) | 2.5109 | 2.51 | 2.538 | 2.9267 | 2.9196 | 2.9555 | 3.362 | 3.3552 | 3.3924 | 3.8018 | 3.7946 | 3.8315 | 4.2163 | 4.2083 | 4.2458
CA | 82860724 | 6022 | GSBS TO CALLIOPE | 6022_Gladstone South - Calliope 66 kV | Loading (MW) | 1.301 | 1.2971 | 1.3264 | 1.9342 | 1.9307 | 1.9573 | 2.5092 | 2.5045 | 2.531 | 3.0455 | 3.0408 | 3.0673 | 3.5294 | 3.5244 | 3.5511
CA | 82860724 | 6022 | GSBS TO CALLIOPE | 6022_Gladstone South - Calliope 66 kV | Power Factor | 0.51815 | 0.5168 | 0.52262 | 0.6609 | 0.66128 | 0.66225 | 0.74635 | 0.74645 | 0.74608 | 0.80106 | 0.80135 | 0.80054 | 0.83708 | 0.8375 | 0.8364
CA | 82860724 | 6022 | GSBS TO CALLIOPE | 6022_Gladstone South - Calliope 66 kV | Rating (A) | 623 | 664 | 599 | 623 | 664 | 599 | 623 | 664 | 599 | 623 | 664 | 599 | 623 | 664 | 599
CA | 82860724 | 6022 | GSBS TO CALLIOPE | 6022_Gladstone South - Calliope 66 kV | Time | 16:30 | 17:00 | 4:00 | 16:00 | 17:30 | 4:00 | 15:30 | 17:30 | 4:00 | 15:30 | 17:30 | 4:00 | 15:30 | 17:30 | 4:00
CA | 82860724 | 6022 | GSBS TO CALLIOPE | 6022_Gladstone South - Calliope 66 kV | Voltage at Constrained Conductor | 69.3314 | 69.3471 | 69.2133 | 69.3522 | 69.1938 | 69.2639 | 69.3679 | 69.2154 | 69.3097 | 69.3983 | 69.2326 | 69.3293 | 69.4058 | 69.2403 | 69.3388
CA | 82999218 | 6103 | FISHERMANS LANDING | 6103_Fisherman Landing-Boat Creek 66 kV | % of Rated A | 83.7402 | 76.3664 | 85.2616 | 83.7278 | 76.7587 | 85.6904 | 84.4105 | 76.9643 | 85.9439 | 84.8144 | 77.5632 | 86.5989 | 84.8304 | 77.575 | 86.5657
CA | 82999218 | 6103 | FISHERMANS LANDING | 6103_Fisherman Landing-Boat Creek 66 kV | Limiting Line Name | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1
CA | 82999218 | 6103 | FISHERMANS LANDING | 6103_Fisherman Landing-Boat Creek 66 kV | Loading (A) | 234.4725 | 234.4448 | 234.4693 | 234.4379 | 235.6491 | 235.6486 | 236.3493 | 236.2804 | 236.3458 | 237.4804 | 238.1189 | 238.1471 | 237.5251 | 238.1551 | 238.0558
CA | 82999218 | 6103 | FISHERMANS LANDING | 6103_Fisherman Landing-Boat Creek 66 kV | Loading (MVA) | 27.2031 | 27.2031 | 27.2031 | 27.4031 | 27.4032 | 27.4032 | 27.6032 | 27.6032 | 27.6032 | 27.8032 | 27.8032 | 27.8032 | 27.8032 | 27.8032 | 27.8032
CA | 82999218 | 6103 | FISHERMANS LANDING | 6103_Fisherman Landing-Boat Creek 66 kV | Loading (MW) | 27.2031 | 27.2031 | 27.2031 | 27.4031 | 27.4032 | 27.4032 | 27.6032 | 27.6032 | 27.6032 | 27.8032 | 27.8032 | 27.8032 | 27.8032 | 27.8032 | 27.8032
CA | 82999218 | 6103 | FISHERMANS LANDING | 6103_Fisherman Landing-Boat Creek 66 kV | Power Factor | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
CA | 82999218 | 6103 | FISHERMANS LANDING | 6103_Fisherman Landing-Boat Creek 66 kV | Rating (A) | 280 | 307 | 275 | 280 | 307 | 275 | 280 | 307 | 275 | 280 | 307 | 275 | 280 | 307 | 275
CA | 82999218 | 6103 | FISHERMANS LANDING | 6103_Fisherman Landing-Boat Creek 66 kV | Time | 9:30 | 17:00 | 8:30 | 9:30 | 19:00 | 5:00 | 9:30 | 17:00 | 8:30 | 9:30 | 17:30 | 6:30 | 9:30 | 17:30 | 6:00
CA | 82999218 | 6103 | FISHERMANS LANDING | 6103_Fisherman Landing-Boat Creek 66 kV | Voltage at Constrained Conductor | 66.9832 | 66.9911 | 66.9842 | 67.4857 | 67.1389 | 67.139 | 67.4286 | 67.4482 | 67.4296 | 67.5937 | 67.4125 | 67.4045 | 67.581 | 67.4023 | 67.4304
CA | 83009518 | 6112 | 66KV 6112 AGNES WATER FDR | 6112_Agnes Water 66 kV | % of Rated A | 2.2668 | 1.3405 | 1.3377 | 2.6975 | 1.5919 | 1.5886 | 3.4705 | 2.0467 | 2.0425 | 4.3964 | 2.5972 | 2.5919 | 5.3397 | 3.1568 | 3.1502
CA | 83009518 | 6112 | 66KV 6112 AGNES WATER FDR | 6112_Agnes Water 66 kV | Limiting Line Name | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1
CA | 83009518 | 6112 | 66KV 6112 AGNES WATER FDR | 6112_Agnes Water 66 kV | Loading (A) | 6.4376 | 6.4613 | 6.4613 | 7.661 | 7.6731 | 7.6731 | 9.8563 | 9.8653 | 9.8653 | 12.4857 | 12.5187 | 12.5187 | 15.1647 | 15.2157 | 15.2157
CA | 83009518 | 6112 | 66KV 6112 AGNES WATER FDR | 6112_Agnes Water 66 kV | Loading (MVA) | 0.75232 | 0.75795 | 0.75795 | 0.89563 | 0.90062 | 0.90062 | 1.1492 | 1.1443 | 1.1443 | 1.4558 | 1.4519 | 1.4519 | 1.7682 | 1.7651 | 1.7651
CA | 83009518 | 6112 | 66KV 6112 AGNES WATER FDR | 6112_Agnes Water 66 kV | Loading (MW) | 0.090667 | 0.090666 | 0.090666 | 0.4962 | 0.4962 | 0.4962 | 0.88151 | 0.8815 | 0.8815 | 1.2592 | 1.2592 | 1.2592 | 1.614 | 1.614 | 1.614
CA | 83009518 | 6112 | 66KV 6112 AGNES WATER FDR | 6112_Agnes Water 66 kV | Power Factor | 0.12052 | 0.11962 | 0.11962 | 0.55403 | 0.55096 | 0.55096 | 0.76706 | 0.77031 | 0.77031 | 0.86494 | 0.86727 | 0.86727 | 0.91281 | 0.91436 | 0.91436
CA | 83009518 | 6112 | 66KV 6112 AGNES WATER FDR | 6112_Agnes Water 66 kV | Rating (A) | 284 | 482 | 483 | 284 | 482 | 483 | 284 | 482 | 483 | 284 | 482 | 483 | 284 | 482 | 483
CA | 83009518 | 6112 | 66KV 6112 AGNES WATER FDR | 6112_Agnes Water 66 kV | Time | 16:30 | 18:30 | 4:30 | 16:30 | 18:30 | 4:30 | 9:00 | 18:30 | 5:00 | 9:00 | 19:00 | 0:00 | 9:00 | 19:00 | 0:00
CA | 83009518 | 6112 | 66KV 6112 AGNES WATER FDR | 6112_Agnes Water 66 kV | Voltage at Constrained Conductor | 67.4713 | 67.727 | 67.7271 | 67.4965 | 67.7657 | 67.7658 | 67.3168 | 66.971 | 66.9711 | 67.3196 | 66.9617 | 66.9617 | 67.3175 | 66.9775 | 66.9775
CA | 83878739 | 6298 | TANB to YPSS | 6298_Tanby - Yeppoon 66 kV | % of Rated A | 3.9461 | 3.5937 | 4.4259 | 3.6069 | 3.2848 | 4.0456 | 3.3283 | 3.0311 | 3.733 | 3.0499 | 2.7776 | 3.4208 | 2.862 | 2.607 | 3.2104
CA | 83878739 | 6298 | TANB to YPSS | 6298_Tanby - Yeppoon 66 kV | Limiting Line Name | TR_LINE 112499_1 | TR_LINE 112499_1 | TR_LINE 112499_1 | TR_LINE 112499_1 | TR_LINE 112499_1 | TR_LINE 112499_1 | TR_LINE 112499_1 | TR_LINE 112499_1 | TR_LINE 112499_1 | TR_LINE 112499_1 | TR_LINE 112499_1 | TR_LINE 112499_1 | TR_LINE 112499_1 | TR_LINE 112499_1 | TR_LINE 112499_1
CA | 83878739 | 6298 | TANB to YPSS | 6298_Tanby - Yeppoon 66 kV | Loading (A) | 14.9162 | 14.9138 | 14.9154 | 13.6343 | 13.6319 | 13.6335 | 12.5811 | 12.5791 | 12.5803 | 11.5288 | 11.5271 | 11.5281 | 10.8183 | 10.8191 | 10.819
CA | 83878739 | 6298 | TANB to YPSS | 6298_Tanby - Yeppoon 66 kV | Loading (MVA) | 1.7986 | 1.7985 | 1.7985 | 1.6489 | 1.6489 | 1.6488 | 1.5255 | 1.5256 | 1.5255 | 1.4013 | 1.4014 | 1.4013 | 1.3177 | 1.3184 | 1.3187
CA | 83878739 | 6298 | TANB to YPSS | 6298_Tanby - Yeppoon 66 kV | Loading (MW) | 1.6288 | 1.6287 | 1.6287 | 1.443 | 1.4428 | 1.4429 | 1.2802 | 1.28 | 1.2801 | 1.128 | 1.1279 | 1.1279 | 1.0007 | 1.0005 | 1.0006
CA | 83878739 | 6298 | TANB to YPSS | 6298_Tanby - Yeppoon 66 kV | Power Factor | 0.90562 | 0.90556 | 0.90561 | 0.87512 | 0.87502 | 0.8751 | 0.83917 | 0.83905 | 0.83914 | 0.80494 | 0.80481 | 0.80491 | 0.75941 | 0.75886 | 0.75879
CA | 83878739 | 6298 | TANB to YPSS | 6298_Tanby - Yeppoon 66 kV | Rating (A) | 378 | 415 | 337 | 378 | 415 | 337 | 378 | 415 | 337 | 378 | 415 | 337 | 378 | 415 | 337
CA | 83878739 | 6298 | TANB to YPSS | 6298_Tanby - Yeppoon 66 kV | Time | 14:00 | 17:00 | 8:30 | 14:00 | 17:00 | 8:30 | 14:00 | 17:00 | 8:30 | 14:00 | 17:00 | 8:30 | 14:00 | 17:30 | 6:00
CA | 83878739 | 6298 | TANB to YPSS | 6298_Tanby - Yeppoon 66 kV | Voltage at Constrained Conductor | 69.6155 | 69.625 | 69.6155 | 69.8236 | 69.8361 | 69.8237 | 70.0081 | 70.0207 | 70.0082 | 70.1782 | 70.1904 | 70.1783 | 70.3249 | 70.3531 | 70.3701
CA | 83966216 | 6310 | LAKES CREEK | 6310_Lakes Creek - Berserker 66 kV | % of Rated A | 5.8376 | 5.8421 | 6.0181 | 6.4009 | 6.4048 | 6.567 | 7.1412 | 7.1439 | 7.2899 | 7.978 | 7.9792 | 8.1092 | 8.8753 | 8.8757 | 8.9927
CA | 83966216 | 6310 | LAKES CREEK | 6310_Lakes Creek - Berserker 66 kV | Limiting Line Name | TR_CABLE 51_1 | TR_CABLE 51_1 | TR_LINE 20950_1 | TR_CABLE 51_1 | TR_CABLE 51_1 | TR_LINE 20950_1 | TR_CABLE 51_1 | TR_CABLE 51_1 | TR_LINE 20950_1 | TR_CABLE 51_1 | TR_CABLE 51_1 | TR_LINE 20950_1 | TR_CABLE 51_1 | TR_CABLE 51_1 | TR_LINE 20950_1
CA | 83966216 | 6310 | LAKES CREEK | 6310_Lakes Creek - Berserker 66 kV | Loading (A) | 21.7157 | 21.7327 | 22.3874 | 23.8115 | 23.826 | 24.4292 | 26.5652 | 26.5754 | 27.1185 | 29.678 | 29.6825 | 30.1663 | 33.0162 | 33.0178 | 33.4529
CA | 83966216 | 6310 | LAKES CREEK | 6310_Lakes Creek - Berserker 66 kV | Loading (MVA) | 2.6123 | 2.6166 | 2.6907 | 2.868 | 2.872 | 2.9398 | 3.2027 | 3.2069 | 3.2664 | 3.5817 | 3.585 | 3.6361 | 3.9873 | 3.9904 | 4.0312
CA | 83966216 | 6310 | LAKES CREEK | 6310_Lakes Creek - Berserker 66 kV | Loading (MW) | 0.83237 | 0.83261 | 0.83072 | 1.4258 | 1.4262 | 1.4237 | 2.0106 | 2.011 | 2.008 | 2.587 | 2.5874 | 2.5836 | 3.1292 | 3.129 | 3.1248
CA | 83966216 | 6310 | LAKES CREEK | 6310_Lakes Creek - Berserker 66 kV | Power Factor | 0.31863 | 0.31821 | 0.30874 | 0.49713 | 0.49659 | 0.48429 | 0.62779 | 0.62711 | 0.61474 | 0.72229 | 0.72174 | 0.71054 | 0.7848 | 0.78413 | 0.77516
CA | 83966216 | 6310 | LAKES CREEK | 6310_Lakes Creek - Berserker 66 kV | Rating (A) | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372
CA | 83966216 | 6310 | LAKES CREEK | 6310_Lakes Creek - Berserker 66 kV | Time | 16:30 | 18:30 | 22:00 | 16:30 | 21:00 | 22:00 | 16:30 | 21:00 | 22:00 | 16:30 | 21:00 | 22:00 | 16:30 | 21:00 | 7:30
CA | 83966216 | 6310 | LAKES CREEK | 6310_Lakes Creek - Berserker 66 kV | Voltage at Constrained Conductor | 69.4539 | 69.5114 | 69.3909 | 69.539 | 69.5934 | 69.4771 | 69.6062 | 69.6689 | 69.5409 | 69.6769 | 69.7304 | 69.5916 | 69.7248 | 69.7771 | 69.5728
CA | 84873218 | 7450 | ROLLESTON | 7450_Memooloo - Rolleston 132 kV | % of Rated A | 9.8491 | 9.4471 | 10.6497 | 9.8292 | 9.428 | 10.6282 | 9.8239 | 9.4229 | 10.6224 | 9.8305 | 9.4292 | 10.6296 | 9.7912 | 9.3915 | 10.5871
CA | 84873218 | 7450 | ROLLESTON | 7450_Memooloo - Rolleston 132 kV | Limiting Line Name | TR_LINE 200880_1 | TR_LINE 200880_1 | TR_LINE 200880_1 | TR_LINE 200880_1 | TR_LINE 200880_1 | TR_LINE 200880_1 | TR_LINE 200880_1 | TR_LINE 200880_1 | TR_LINE 200880_1 | TR_LINE 200880_1 | TR_LINE 200880_1 | TR_LINE 200880_1 | TR_LINE 200880_1 | TR_LINE 200880_1 | TR_LINE 200880_1
CA | 84873218 | 7450 | ROLLESTON | 7450_Memooloo - Rolleston 132 kV | Loading (A) | 69.4362 | 69.4362 | 69.4362 | 69.296 | 69.296 | 69.296 | 69.2582 | 69.2582 | 69.2582 | 69.3048 | 69.3048 | 69.3048 | 69.0279 | 69.0279 | 69.0279
CA | 84873218 | 7450 | ROLLESTON | 7450_Memooloo - Rolleston 132 kV | Loading (MVA) | 16.6268 | 16.6268 | 16.6268 | 16.5928 | 16.5928 | 16.5928 | 16.5839 | 16.5839 | 16.5839 | 16.5943 | 16.5943 | 16.5943 | 16.5286 | 16.5286 | 16.5286
CA | 84873218 | 7450 | ROLLESTON | 7450_Memooloo - Rolleston 132 kV | Loading (MW) | 16.5183 | 16.5183 | 16.5183 | 16.4838 | 16.4838 | 16.4838 | 16.4747 | 16.4747 | 16.4747 | 16.4852 | 16.4852 | 16.4852 | 16.4186 | 16.4186 | 16.4186
CA | 84873218 | 7450 | ROLLESTON | 7450_Memooloo - Rolleston 132 kV | Power Factor | 0.99348 | 0.99348 | 0.99348 | 0.99343 | 0.99343 | 0.99343 | 0.99342 | 0.99342 | 0.99342 | 0.99343 | 0.99343 | 0.99343 | 0.99334 | 0.99334 | 0.99334
CA | 84873218 | 7450 | ROLLESTON | 7450_Memooloo - Rolleston 132 kV | Rating (A) | 705 | 735 | 652 | 705 | 735 | 652 | 705 | 735 | 652 | 705 | 735 | 652 | 705 | 735 | 652
CA | 84873218 | 7450 | ROLLESTON | 7450_Memooloo - Rolleston 132 kV | Time | 16:00 | 18:30 | 0:30 | 15:30 | 17:30 | 6:00 | 9:00 | 18:30 | 22:00 | 11:30 | 17:30 | 6:30 | 10:30 | 17:00 | 0:00
CA | 84873218 | 7450 | ROLLESTON | 7450_Memooloo - Rolleston 132 kV | Voltage at Constrained Conductor | 138.2487 | 138.2487 | 138.2487 | 138.2458 | 138.2458 | 138.2458 | 138.2467 | 138.2467 | 138.2467 | 138.2404 | 138.2404 | 138.2404 | 138.2454 | 138.2454 | 138.2454
FN | 10020664 | 7200 | 7200 - CRAIGLIE NO 2 | 7200_Craiglie No 2 132 kV | % of Rated A | 9.3791 | 12.3741 | 13.795 | 9.8658 | 12.3093 | 13.7236 | 10.2024 | 12.2745 | 13.6848 | 10.5637 | 12.2677 | 13.677 | 10.9103 | 12.2816 | 13.6924
FN | 10020664 | 7200 | 7200 - CRAIGLIE NO 2 | 7200_Craiglie No 2 132 kV | Limiting Line Name | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1
FN | 10020664 | 7200 | 7200 - CRAIGLIE NO 2 | 7200_Craiglie No 2 132 kV | Loading (A) | 42.3934 | 58.9008 | 58.9045 | 44.5933 | 58.5921 | 58.5997 | 46.1149 | 58.4267 | 58.434 | 47.7481 | 58.3941 | 58.4008 | 49.3146 | 58.4603 | 58.4666
FN | 10020664 | 7200 | 7200 - CRAIGLIE NO 2 | 7200_Craiglie No 2 132 kV | Loading (MVA) | 10.5446 | 14.7332 | 14.7367 | 11.1101 | 14.6931 | 14.6969 | 11.4988 | 14.6712 | 14.6749 | 11.9127 | 14.6778 | 14.6812 | 12.3079 | 14.7052 | 14.7084
FN | 10020664 | 7200 | 7200 - CRAIGLIE NO 2 | 7200_Craiglie No 2 132 kV | Loading (MW) | 6.0846 | 2.645 | 2.6449 | 7.6329 | 1.7577 | 1.7577 | 8.4071 | 0.96172 | 0.96169 | 9.1245 | 0.22522 | 0.22518 | 9.7493 | 0.4156 | 0.41563
FN | 10020664 | 7200 | 7200 - CRAIGLIE NO 2 | 7200_Craiglie No 2 132 kV | Power Factor | 0.57704 | 0.17952 | 0.17948 | 0.68703 | 0.11963 | 0.11959 | 0.73113 | 0.065552 | 0.065533 | 0.76595 | 0.015344 | 0.015338 | 0.79212 | 0.028262 | 0.028258
FN | 10020664 | 7200 | 7200 - CRAIGLIE NO 2 | 7200_Craiglie No 2 132 kV | Rating (A) | 452 | 476 | 427 | 452 | 476 | 427 | 452 | 476 | 427 | 452 | 476 | 427 | 452 | 476 | 427
FN | 10020664 | 7200 | 7200 - CRAIGLIE NO 2 | 7200_Craiglie No 2 132 kV | Time | 10:00 | 21:00 | 4:00 | 12:00 | 19:00 | 4:00 | 12:00 | 19:00 | 4:00 | 12:00 | 19:00 | 4:00 | 12:00 | 19:00 | 4:00
FN | 10020664 | 7200 | 7200 - CRAIGLIE NO 2 | 7200_Craiglie No 2 132 kV | Voltage at Constrained Conductor | 143.6051 | 144.4162 | 144.4412 | 143.8424 | 144.7817 | 144.8009 | 143.9624 | 144.9749 | 144.9932 | 144.0434 | 145.1217 | 145.1384 | 144.0951 | 145.2279 | 145.2434
FN | 10020665 | 7201 | 7201 - CRAIGLIE NO 1 | 7201_Craiglie No 1 132 kV | % of Rated A | 5.1492 | 5.2909 | 5.8988 | 5.0389 | 5.1958 | 5.7927 | 4.9732 | 5.1286 | 5.7178 | 4.9596 | 5.0859 | 5.6702 | 4.9797 | 5.0652 | 5.6471
FN | 10020665 | 7201 | 7201 - CRAIGLIE NO 1 | 7201_Craiglie No 1 132 kV | Limiting Line Name | TR_LINE 3957_2 | TR_LINE 3957_2 | TR_LINE 3957_2 | TR_LINE 3957_2 | TR_LINE 3957_2 | TR_LINE 3957_2 | TR_LINE 3957_2 | TR_LINE 3957_2 | TR_LINE 3957_2 | TR_LINE 3957_2 | TR_LINE 3957_2 | TR_LINE 3957_2 | TR_LINE 3957_2 | TR_LINE 3957_2 | TR_LINE 3957_2
FN | 10020665 | 7201 | 7201 - CRAIGLIE NO 1 | 7201_Craiglie No 1 132 kV | Loading (A) | 23.2745 | 25.1848 | 25.1877 | 22.776 | 24.732 | 24.7349 | 22.4786 | 24.4121 | 24.415 | 22.4176 | 24.2088 | 24.2115 | 22.5085 | 24.1104 | 24.113
FN | 10020665 | 7201 | 7201 - CRAIGLIE NO 1 | 7201_Craiglie No 1 132 kV | Loading (MVA) | 5.7911 | 6.2998 | 6.3015 | 5.6773 | 6.202 | 6.2036 | 5.6083 | 6.13 | 6.1315 | 5.593 | 6.0851 | 6.0865 | 5.6177 | 6.0648 | 6.0661
FN | 10020665 | 7201 | 7201 - CRAIGLIE NO 1 | 7201_Craiglie No 1 132 kV | Loading (MW) | 1.6572 | 2.2126 | 2.2127 | 1.1665 | 1.7334 | 1.7334 | 0.71954 | 1.2937 | 1.2938 | 0.1889 | 0.8796 | 0.87966 | 0.5582 | 0.51406 | 0.51412
FN | 10020665 | 7201 | 7201 - CRAIGLIE NO 1 | 7201_Craiglie No 1 132 kV | Power Factor | 0.28617 | 0.35121 | 0.35114 | 0.20546 | 0.27948 | 0.27943 | 0.1283 | 0.21105 | 0.21101 | 0.033774 | 0.14455 | 0.14453 | 0.099365 | 0.084761 | 0.084753
FN | 10020665 | 7201 | 7201 - CRAIGLIE NO 1 | 7201_Craiglie No 1 132 kV | Rating (A) | 452 | 476 | 427 | 452 | 476 | 427 | 452 | 476 | 427 | 452 | 476 | 427 | 452 | 476 | 427
FN | 10020665 | 7201 | 7201 - CRAIGLIE NO 1 | 7201_Craiglie No 1 132 kV | Time | 16:30 | 19:00 | 4:00 | 16:30 | 19:00 | 4:00 | 16:30 | 19:00 | 4:00 | 12:00 | 19:00 | 4:00 | 12:00 | 19:00 | 4:00
FN | 10020665 | 7201 | 7201 - CRAIGLIE NO 1 | 7201_Craiglie No 1 132 kV | Voltage at Constrained Conductor | 143.654 | 144.4207 | 144.4412 | 143.9152 | 144.7817 | 144.8009 | 144.0461 | 144.9749 | 144.9932 | 144.0434 | 145.1217 | 145.1384 | 144.0951 | 145.2279 | 145.2434
FN | 10020666 | 7216 | 4GEO (GEORGETOWN) | 7216_4GEO (Georgetown) 132 kV | % of Rated A | 8.3521 | 8.5092 | 8.559 | 8.8248 | 8.6273 | 8.6778 | 9.3069 | 8.9152 | 8.9674 | 9.7842 | 8.4403 | 8.4897 | 10.2093 | 8.6167 | 8.6671
FN | 10020666 | 7216 | 4GEO (GEORGETOWN) | 7216_4GEO (Georgetown) 132 kV | Limiting Line Name | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1
FN | 10020666 | 7216 | 4GEO (GEORGETOWN) | 7216_4GEO (Georgetown) 132 kV | Loading (A) | 24.8893 | 29.2716 | 29.2717 | 26.2979 | 29.678 | 29.6781 | 27.7345 | 30.6684 | 30.6685 | 29.1571 | 29.0346 | 29.0347 | 30.4237 | 29.6414 | 29.6415
FN | 10020666 | 7216 | 4GEO (GEORGETOWN) | 7216_4GEO (Georgetown) 132 kV | Loading (MVA) | 5.9507 | 7.648 | 7.648 | 6.2891 | 7.7623 | 7.7623 | 6.6341 | 8.0352 | 8.0352 | 6.9757 | 7.6747 | 7.6747 | 7.28 | 7.8404 | 7.8404
FN | 10020666 | 7216 | 4GEO (GEORGETOWN) | 7216_4GEO (Georgetown) 132 kV | Loading (MW) | 2.1538 | 1.8549 | 1.8549 | 2.6932 | 1.2858 | 1.2858 | 3.1968 | 0.75571 | 0.75571 | 3.6634 | 0.26116 | 0.26116 | 4.0599 | 0.1564 | 0.1564
FN | 10020666 | 7216 | 4GEO (GEORGETOWN) | 7216_4GEO (Georgetown) 132 kV | Power Factor | 0.36194 | 0.24254 | 0.24254 | 0.42824 | 0.16565 | 0.16565 | 0.48187 | 0.094051 | 0.094051 | 0.52517 | 0.034029 | 0.034028 | 0.55769 | 0.019948 | 0.019948
FN | 10020666 | 7216 | 4GEO (GEORGETOWN) | 7216_4GEO (Georgetown) 132 kV | Rating (A) | 298 | 344 | 342 | 298 | 344 | 342 | 298 | 344 | 342 | 298 | 344 | 342 | 298 | 344 | 342
FN | 10020666 | 7216 | 4GEO (GEORGETOWN) | 7216_4GEO (Georgetown) 132 kV | Time | 12:30 | 19:00 | 4:00 | 12:30 | 19:00 | 4:00 | 12:30 | 19:00 | 1:30 | 12:30 | 19:00 | 4:00 | 12:30 | 19:00 | 4:00
FN | 10020666 | 7216 | 4GEO (GEORGETOWN) | 7216_4GEO (Georgetown) 132 kV | Voltage at Constrained Conductor | 138.0376 | 150.8476 | 150.8477 | 138.0715 | 151.0062 | 151.0063 | 138.102 | 151.2668 | 151.2668 | 138.1292 | 152.6103 | 152.6103 | 138.1517 | 152.7132 | 152.7132
FN | 10020667 | 3AT2 | ATHERTON NO 2 | 3AT2_Atherton No 2 66 kV | % of Rated A | 4.5786 | 4.4539 | 4.8407 | 6.1525 | 5.9943 | 6.4725 | 7.7485 | 7.5561 | 8.1447 | 9.3344 | 9.1074 | 9.8094 | 10.8246 | 10.5654 | 11.3743
FN | 10020667 | 3AT2 | ATHERTON NO 2 | 3AT2_Atherton No 2 66 kV | Limiting Line Name | TR_LINE 4672_1 | TR_CABLE 14_1 | TR_LINE 4672_1 | TR_LINE 4672_1 | TR_CABLE 14_1 | TR_LINE 4672_1 | TR_LINE 4672_1 | TR_CABLE 14_1 | TR_LINE 4672_1 | TR_LINE 4672_1 | TR_CABLE 14_1 | TR_LINE 4672_1 | TR_LINE 4672_1 | TR_CABLE 14_1 | TR_LINE 4672_1
FN | 10020667 | 3AT2 | ATHERTON NO 2 | 3AT2_Atherton No 2 66 kV | Loading (A) | 25.0905 | 24.9421 | 25.2201 | 33.7156 | 33.568 | 33.7217 | 42.4618 | 42.3141 | 42.4338 | 51.1523 | 51.0012 | 51.1069 | 59.3187 | 59.1663 | 59.2599
FN | 10020667 | 3AT2 | ATHERTON NO 2 | 3AT2_Atherton No 2 66 kV | Loading (MVA) | 3.0477 | 3.0313 | 3.0816 | 4.1026 | 4.0877 | 4.1311 | 5.1714 | 5.1579 | 5.173 | 6.2332 | 6.2209 | 6.2345 | 7.2305 | 7.2191 | 7.2314
FN | 10020667 | 3AT2 | ATHERTON NO 2 | 3AT2_Atherton No 2 66 kV | Loading (MW) | 2.5093 | 2.4984 | 2.5121 | 3.7239 | 3.7127 | 3.7266 | 4.881 | 4.8701 | 4.8792 | 6.0051 | 5.9947 | 6.0035 | 7.0459 | 7.0358 | 7.0443
FN | 10020667 | 3AT2 | ATHERTON NO 2 | 3AT2_Atherton No 2 66 kV | Power Factor | 0.82334 | 0.82419 | 0.81519 | 0.9077 | 0.90827 | 0.90208 | 0.94384 | 0.9442 | 0.94321 | 0.96341 | 0.96364 | 0.96294 | 0.97447 | 0.97462 | 0.97412
FN | 10020667 | 3AT2 | ATHERTON NO 2 | 3AT2_Atherton No 2 66 kV | Rating (A) | 548 | 560 | 521 | 548 | 560 | 521 | 548 | 560 | 521 | 548 | 560 | 521 | 548 | 560 | 521
FN | 10020667 | 3AT2 | ATHERTON NO 2 | 3AT2_Atherton No 2 66 kV | Time | 14:30 | 17:00 | 4:00 | 14:00 | 17:00 | 4:00 | 14:00 | 17:00 | 5:30 | 14:00 | 17:00 | 5:30 | 14:00 | 17:00 | 5:30
FN | 10020667 | 3AT2 | ATHERTON NO 2 | 3AT2_Atherton No 2 66 kV | Voltage at Constrained Conductor | 70.1297 | 70.1683 | 70.5451 | 70.2529 | 70.3061 | 70.7283 | 70.3153 | 70.3769 | 70.383 | 70.3534 | 70.4228 | 70.4305 | 70.3748 | 70.4444 | 70.4535
FN | 10020668 | 4KID | ROSS - KIDSTON | 4KID_Ross - Kidston 132 kV | % of Rated A | 61.5029 | 46.221 | 59.0113 | 62.0181 | 46.7198 | 59.5704 | 62.4985 | 47.1846 | 60.0913 | 62.9439 | 47.6152 | 60.574 | 63.3215 | 47.98 | 60.983
FN | 10020668 | 4KID | ROSS - KIDSTON | 4KID_Ross - Kidston 132 kV | Limiting Line Name | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1
FN | 10020668 | 4KID | ROSS - KIDSTON | 4KID_Ross - Kidston 132 kV | Loading (A) | 218.3354 | 177.951 | 204.7692 | 220.1643 | 179.8712 | 206.7093 | 221.8697 | 181.6606 | 208.5169 | 223.4507 | 183.3184 | 210.1918 | 224.7914 | 184.723 | 211.611
FN | 10020668 | 4KID | ROSS - KIDSTON | 4KID_Ross - Kidston 132 kV | Loading (MVA) | 52.4141 | 42.7201 | 49.1577 | 52.8531 | 43.1811 | 49.6234 | 53.2624 | 43.6106 | 50.0573 | 53.6419 | 44.0086 | 50.4593 | 53.9637 | 44.3457 | 50.8
FN | 10020668 | 4KID | ROSS - KIDSTON | 4KID_Ross - Kidston 132 kV | Loading (MW) | 47.3571 | 35.3857 | 43.3559 | 47.8952 | 35.9596 | 43.93 | 48.3962 | 36.4935 | 44.4641 | 48.8604 | 36.988 | 44.9587 | 49.2538 | 37.4067 | 45.3775
FN | 10020668 | 4KID | ROSS - KIDSTON | 4KID_Ross - Kidston 132 kV | Power Factor | 0.90352 | 0.82831 | 0.88198 | 0.9062 | 0.83276 | 0.88527 | 0.90864 | 0.8368 | 0.88826 | 0.91086 | 0.84047 | 0.89099 | 0.91272 | 0.84352 | 0.89326
FN | 10020668 | 4KID | ROSS - KIDSTON | 4KID_Ross - Kidston 132 kV | Rating (A) | 355 | 385 | 347 | 355 | 385 | 347 | 355 | 385 | 347 | 355 | 385 | 347 | 355 | 385 | 347
FN | 10020668 | 4KID | ROSS - KIDSTON | 4KID_Ross - Kidston 132 kV | Time | 12:30 | 17:00 | 8:30 | 12:30 | 17:00 | 8:30 | 12:30 | 17:00 | 8:30 | 12:30 | 17:00 | 8:30 | 12:30 | 17:00 | 8:30
FN | 10020668 | 4KID | ROSS - KIDSTON | 4KID_Ross - Kidston 132 kV | Voltage at Constrained Conductor | 138.6 | 138.6026 | 138.601 | 138.5999 | 138.6025 | 138.6008 | 138.5997 | 138.6024 | 138.6007 | 138.5996 | 138.6023 | 138.6006 | 138.5995 | 138.6022 | 138.6005
FN | 10020672 | 3CRO | CROYDON | 3CRO_Croydon 66 kV | % of Rated A | 5.2684 | 4.9439 | 5.101 | 5.6669 | 4.4504 | 4.5918 | 6.2701 | 4.0534 | 4.1822 | 6.9001 | 3.753 | 3.8723 | 7.4258 | 3.5612 | 3.6744
FN | 10020672 | 3CRO | CROYDON | 3CRO_Croydon 66 kV | Limiting Line Name | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1
FN | 10020672 | 3CRO | CROYDON | 3CRO_Croydon 66 kV | Loading (A) | 24.0768 | 24.0768 | 24.0768 | 25.8978 | 21.6735 | 21.6735 | 28.6543 | 19.7399 | 19.7399 | 31.5335 | 18.2771 | 18.2771 | 33.9357 | 17.3431 | 17.3431
FN | 10020672 | 3CRO | CROYDON | 3CRO_Croydon 66 kV | Loading (MVA) | 2.8728 | 2.8728 | 2.8728 | 3.0878 | 2.5863 | 2.5863 | 3.4627 | 2.3557 | 2.3557 | 3.8104 | 2.1813 | 2.1813 | 4.1004 | 2.0699 | 2.0699
FN | 10020672 | 3CRO | CROYDON | 3CRO_Croydon 66 kV | Loading (MW) | 1.4822 | 1.4822 | 1.4822 | 2.8983 | 1.0694 | 1.0694 | 3.2957 | 0.68984 | 0.68984 | 3.6269 | 0.34227 | 0.34227 | 3.9027 | 0.053483 | 0.053483
FN | 10020672 | 3CRO | CROYDON | 3CRO_Croydon 66 kV | Power Factor | 0.51594 | 0.51594 | 0.51594 | 0.93864 | 0.41348 | 0.41348 | 0.95177 | 0.29283 | 0.29283 | 0.95182 | 0.15691 | 0.15691 | 0.95179 | 0.025838 | 0.025838
FN | 10020672 | 3CRO | CROYDON | 3CRO_Croydon 66 kV | Rating (A) | 457 | 487 | 472 | 457 | 487 | 472 | 457 | 487 | 472 | 457 | 487 | 472 | 457 | 487 | 472
FN | 10020672 | 3CRO | CROYDON | 3CRO_Croydon 66 kV | Time | 16:30 | 18:00 | 6:30 | 12:30 | 18:00 | 6:30 | 12:30 | 17:30 | 6:30 | 12:30 | 18:00 | 6:30 | 12:30 | 18:00 | 6:30
FN | 10020672 | 3CRO | CROYDON | 3CRO_Croydon 66 kV | Voltage at Constrained Conductor | 68.8886 | 68.8886 | 68.8886 | 68.8371 | 68.8954 | 68.8954 | 69.769 | 68.9006 | 68.9006 | 69.7657 | 68.9044 | 68.9044 | 69.7605 | 68.907 | 68.907
FN | 10020676 | 3NOR | NORMANTON | 3NOR_Normanton 66 kV | % of Rated A | 7.4899 | 4.5635 | 4.7086 | 8.0616 | 4.5355 | 4.6797 | 8.6037 | 4.6196 | 4.7664 | 9.1153 | 4.6087 | 4.7552 | 9.5525 | 4.7526 | 4.9036
FN | 10020676 | 3NOR | NORMANTON | 3NOR_Normanton 66 kV | Limiting Line Name | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1
FN | 10020676 | 3NOR | NORMANTON | 3NOR_Normanton 66 kV | Loading (A) | 34.2288 | 22.2244 | 22.2245 | 36.8417 | 22.0881 | 22.0881 | 39.3188 | 22.4975 | 22.4975 | 41.6571 | 22.4445 | 22.4446 | 43.6548 | 23.145 | 23.1451
FN | 10020676 | 3NOR | NORMANTON | 3NOR_Normanton 66 kV | Loading (MVA) | 4.0882 | 2.6436 | 2.6436 | 4.4018 | 2.6292 | 2.6292 | 4.6991 | 2.6799 | 2.6799 | 4.9799 | 2.6739 | 2.6739 | 5.2197 | 2.7586 | 2.7586
FN | 10020676 | 3NOR | NORMANTON | 3NOR_Normanton 66 kV | Loading (MW) | 2.7681 | 1.2838 | 1.2838 | 3.124 | 0.9264 | 0.9264 | 3.4562 | 0.5928 | 0.5928 | 3.7665 | 0.28088 | 0.28088 | 4.0297 | 0.016573 | 0.016573
FN | 10020676 | 3NOR | NORMANTON | 3NOR_Normanton 66 kV | Power Factor | 0.6771 | 0.48563 | 0.48563 | 0.7097 | 0.35235 | 0.35235 | 0.73549 | 0.22121 | 0.22121 | 0.75635 | 0.10504 | 0.10504 | 0.77202 | 0.0060078 | 0.0060078
FN | 10020676 | 3NOR | NORMANTON | 3NOR_Normanton 66 kV | Rating (A) | 457 | 487 | 472 | 457 | 487 | 472 | 457 | 487 | 472 | 457 | 487 | 472 | 457 | 487 | 472
FN | 10020676 | 3NOR | NORMANTON | 3NOR_Normanton 66 kV | Time | 12:30 | 19:00 | 4:00 | 12:30 | 19:00 | 4:00 | 12:30 | 19:00 | 1:30 | 12:30 | 19:00 | 4:00 | 12:30 | 19:00 | 4:00
FN | 10020676 | 3NOR | NORMANTON | 3NOR_Normanton 66 kV | Voltage at Constrained Conductor | 68.9576 | 68.6749 | 68.6749 | 68.9811 | 68.7231 | 68.7231 | 69.0015 | 68.7728 | 68.7728 | 69.019 | 68.7827 | 68.7827 | 69.0328 | 68.8137 | 68.8137
FN | 10020678 | 3AT1 | ATHERTON NO 1 | 3AT1_Atherton No 1 66 kV | % of Rated A | 4.5763 | 4.4517 | 4.8382 | 6.151 | 5.9929 | 6.4709 | 7.7476 | 7.5552 | 8.1437 | 9.3339 | 9.1069 | 9.8089 | 10.8244 | 10.5653 | 11.3741
FN | 10020678 | 3AT1 | ATHERTON NO 1 | 3AT1_Atherton No 1 66 kV | Limiting Line Name | TR_LINE 4407_1 | TR_CABLE 15_1 | TR_LINE 4407_1 | TR_LINE 4407_1 | TR_CABLE 15_1 | TR_LINE 4407_1 | TR_LINE 4407_1 | TR_CABLE 15_1 | TR_LINE 4407_1 | TR_LINE 4407_1 | TR_CABLE 15_1 | TR_LINE 4407_1 | TR_LINE 4407_1 | TR_CABLE 15_1 | TR_LINE 4407_1
FN | 10020678 | 3AT1 | ATHERTON NO 1 | 3AT1_Atherton No 1 66 kV | Loading (A) | 25.078 | 24.9296 | 25.2071 | 33.7076 | 33.5601 | 33.7134 | 42.4568 | 42.3092 | 42.4289 | 51.1497 | 50.9986 | 51.1042 | 59.3179 | 59.1655 | 59.2591
FN | 10020678 | 3AT1 | ATHERTON NO 1 | 3AT1_Atherton No 1 66 kV | Loading (MVA) | 3.0462 | 3.0298 | 3.08 | 4.1016 | 4.0867 | 4.1301 | 5.1708 | 5.1573 | 5.1724 | 6.2329 | 6.2206 | 6.2342 | 7.2304 | 7.219 | 7.2313
FN | 10020678 | 3AT1 | ATHERTON NO 1 | 3AT1_Atherton No 1 66 kV | Loading (MW) | 2.5095 | 2.4987 | 2.5123 | 3.7242 | 3.7131 | 3.7269 | 4.8814 | 4.8706 | 4.8796 | 6.0057 | 5.9952 | 6.004 | 7.0465 | 7.0364 | 7.0449
FN | 10020678 | 3AT1 | ATHERTON NO 1 | 3AT1_Atherton No 1 66 kV | Power Factor | 0.82383 | 0.82469 | 0.81568 | 0.908 | 0.90857 | 0.90239 | 0.94403 | 0.94439 | 0.9434 | 0.96354 | 0.96377 | 0.96308 | 0.97456 | 0.97471 | 0.97421
FN | 10020678 | 3AT1 | ATHERTON NO 1 | 3AT1_Atherton No 1 66 kV | Rating (A) | 548 | 560 | 521 | 548 | 560 | 521 | 548 | 560 | 521 | 548 | 560 | 521 | 548 | 560 | 521
FN | 10020678 | 3AT1 | ATHERTON NO 1 | 3AT1_Atherton No 1 66 kV | Time | 14:30 | 17:00 | 4:00 | 14:00 | 17:00 | 4:00 | 14:00 | 17:00 | 5:30 | 14:00 | 17:00 | 5:30 | 14:00 | 17:00 | 5:30
FN | 10020678 | 3AT1 | ATHERTON NO 1 | 3AT1_Atherton No 1 66 kV | Voltage at Constrained Conductor | 70.1297 | 70.1683 | 70.5451 | 70.2529 | 70.3061 | 70.7283 | 70.3153 | 70.3769 | 70.383 | 70.3534 | 70.4228 | 70.4305 | 70.3748 | 70.4444 | 70.4535
FN | 10020733 | 3EVE | EVELYN | 3EVE_Evelyn 66 kV | % of Rated A | 55.7074 | 39.0485 | 40.0394 | 56.6967 | 39.7368 | 40.764 | 57.7708 | 40.486 | 41.5375 | 58.8169 | 41.2158 | 42.2854 | 59.7881 | 41.8971 | 42.9865
FN | 10020733 | 3EVE | EVELYN | 3EVE_Evelyn 66 kV | Limiting Line Name | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1
FN | 10020733 | 3EVE | EVELYN | 3EVE_Evelyn 66 kV | Loading (A) | 94.1456 | 94.1069 | 94.0926 | 95.8175 | 95.7658 | 95.7953 | 97.6327 | 97.5714 | 97.6132 | 99.4005 | 99.33 | 99.3708 | 101.0419 | 100.9721 | 101.0183
FN | 10020733 | 3EVE | EVELYN | 3EVE_Evelyn 66 kV | Loading (MVA) | 11.6592 | 11.6593 | 11.6594 | 11.9265 | 11.9267 | 11.9266 | 12.1773 | 12.1775 | 12.1774 | 12.4179 | 12.4181 | 12.418 | 12.6392 | 12.6393 | 12.6392
FN | 10020733 | 3EVE | EVELYN | 3EVE_Evelyn 66 kV | Loading (MW) | 11.6331 | 11.6332 | 11.6333 | 11.8999 | 11.9001 | 11.9 | 12.1495 | 12.1498 | 12.1496 | 12.3889 | 12.3892 | 12.389 | 12.6088 | 12.6091 | 12.6089
FN | 10020733 | 3EVE | EVELYN | 3EVE_Evelyn 66 kV | Power Factor | 0.99775 | 0.99776 | 0.99777 | 0.99776 | 0.99777 | 0.99777 | 0.99772 | 0.99773 | 0.99772 | 0.99766 | 0.99767 | 0.99766 | 0.9976 | 0.99761 | 0.9976
FN | 10020733 | 3EVE | EVELYN | 3EVE_Evelyn 66 kV | Rating (A) | 169 | 241 | 235 | 169 | 241 | 235 | 169 | 241 | 235 | 169 | 241 | 235 | 169 | 241 | 235
FN | 10020733 | 3EVE | EVELYN | 3EVE_Evelyn 66 kV | Time | 12:00 | 18:30 | 6:00 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30
FN | 10020733 | 3EVE | EVELYN | 3EVE_Evelyn 66 kV | Voltage at Constrained Conductor | 71.5006 | 71.5306 | 71.5417 | 71.8636 | 71.9032 | 71.8806 | 72.0106 | 72.0567 | 72.0253 | 72.1273 | 72.1795 | 72.1493 | 72.2199 | 72.2707 | 72.2371
FN | 10020762 | 3MTG | MT GARNET | 3MTG_Mt Garnet 66 kV | % of Rated A | 6.0337 | 4.7902 | 5.1916 | 5.8474 | 4.727 | 5.1232 | 5.7095 | 4.6803 | 5.0726 | 5.6067 | 4.6466 | 5.036 | 5.5383 | 4.6253 | 5.0129
FN | 10020762 | 3MTG | MT GARNET | 3MTG_Mt Garnet 66 kV | Limiting Line Name | TR_LINE 169447_1 | TR_LINE 12086527_1 | TR_LINE 12086527_1 | TR_LINE 169447_1 | TR_LINE 12086527_1 | TR_LINE 12086527_1 | TR_LINE 169447_1 | TR_LINE 12086527_1 | TR_LINE 12086527_1 | TR_LINE 169447_1 | TR_LINE 12086527_1 | TR_LINE 12086527_1 | TR_LINE 169447_1 | TR_LINE 12086527_1 | TR_LINE 12086527_1
FN | 10020762 | 3MTG | MT GARNET | 3MTG_Mt Garnet 66 kV | Loading (A) | 10.1969 | 14.2747 | 14.277 | 9.8822 | 14.0866 | 14.0889 | 9.6491 | 13.9473 | 13.9496 | 9.4753 | 13.8468 | 13.849 | 9.3597 | 13.7833 | 13.7854
FN | 10020762 | 3MTG | MT GARNET | 3MTG_Mt Garnet 66 kV | Loading (MVA) | 1.2461 | 1.7498 | 1.7505 | 1.2113 | 1.7329 | 1.7335 | 1.185 | 1.7196 | 1.7202 | 1.1655 | 1.7103 | 1.7109 | 1.1525 | 1.7048 | 1.7054
FN | 10020762 | 3MTG | MT GARNET | 3MTG_Mt Garnet 66 kV | Loading (MW) | 0.66921 | 0.67333 | 0.67333 | 0.5885 | 0.59247 | 0.59247 | 0.52226 | 0.52612 | 0.52613 | 0.46747 | 0.47125 | 0.47125 | 0.42741 | 0.43114 | 0.43114
FN | 10020762 | 3MTG | MT GARNET | 3MTG_Mt Garnet 66 kV | Power Factor | 0.53704 | 0.3848 | 0.38465 | 0.48585 | 0.3419 | 0.34177 | 0.44071 | 0.30596 | 0.30585 | 0.40109 | 0.27555 | 0.27545 | 0.37085 | 0.2529 | 0.25281
FN | 10020762 | 3MTG | MT GARNET | 3MTG_Mt Garnet 66 kV | Rating (A) | 169 | 298 | 275 | 169 | 298 | 275 | 169 | 298 | 275 | 169 | 298 | 275 | 169 | 298 | 275
FN | 10020762 | 3MTG | MT GARNET | 3MTG_Mt Garnet 66 kV | Time | 16:30 | 19:00 | 4:00 | 16:30 | 19:00 | 4:00 | 16:30 | 19:00 | 4:00 | 16:30 | 19:00 | 4:00 | 16:30 | 19:00 | 4:00
FN | 10020762 | 3MTG | MT GARNET | 3MTG_Mt Garnet 66 kV | Voltage at Constrained Conductor | 70.5556 | 70.7728 | 70.7886 | 70.7674 | 71.0229 | 71.0378 | 70.907 | 71.1815 | 71.1958 | 71.0154 | 71.3101 | 71.3235 | 71.0921 | 71.4109 | 71.4236
FN | 10020819 | 7206 | 7206 CAIRNS CITY | 7206 Woree-Cairns Terminal-Cairns City | % of Rated A | 0.99403 | 0.99417 | 0.99456 | 0.99077 | 0.99094 | 0.99131 | 0.99202 | 0.99222 | 0.9926 | 0.99314 | 0.99336 | 0.99369 | 0.99394 | 0.99418 | 0.9945
FN | 10020819 | 7206 | 7206 CAIRNS CITY | 7206 Woree-Cairns Terminal-Cairns City | Limiting Line Name | TR_CABLE 11_1 | TR_CABLE 11_1 | TR_CABLE 11_1 | TR_CABLE 11_1 | TR_CABLE 11_1 | TR_CABLE 11_1 | TR_CABLE 11_1 | TR_CABLE 11_1 | TR_CABLE 11_1 | TR_CABLE 11_1 | TR_CABLE 11_1 | TR_CABLE 11_1 | TR_CABLE 11_1 | TR_CABLE 11_1 | TR_CABLE 11_1
FN | 10020819 | 7206 | 7206 CAIRNS CITY | 7206 Woree-Cairns Terminal-Cairns City | Loading (A) | 4.7614 | 4.7621 | 4.764 | 4.7458 | 4.7466 | 4.7484 | 4.7518 | 4.7527 | 4.7546 | 4.7571 | 4.7582 | 4.7598 | 4.761 | 4.7621 | 4.7636
FN | 10020819 | 7206 | 7206 CAIRNS CITY | 7206 Woree-Cairns Terminal-Cairns City | Loading (MVA) | 1.154 | 1.1543 | 1.1552 | 1.1464 | 1.1468 | 1.1477 | 1.1493 | 1.1498 | 1.1507 | 1.1519 | 1.1524 | 1.1532 | 1.1538 | 1.1543 | 1.1551
FN | 10020819 | 7206 | 7206 CAIRNS CITY | 7206 Woree-Cairns Terminal-Cairns City | Loading (MW) | 0.018217 | 0.018222 | 0.018236 | 0.018098 | 0.018104 | 0.018118 | 0.018144 | 0.018151 | 0.018165 | 0.018184 | 0.018192 | 0.018204 | 0.018214 | 0.018222 | 0.018234
FN | 10020819 | 7206 | 7206 CAIRNS CITY | 7206 Woree-Cairns Terminal-Cairns City | Power Factor | 0.015786 | 0.015786 | 0.015786 | 0.015786 | 0.015786 | 0.015786 | 0.015786 | 0.015786 | 0.015786 | 0.015786 | 0.015786 | 0.015786 | 0.015786 | 0.015786 | 0.015786
FN | 10020819 | 7206 | 7206 CAIRNS CITY | 7206 Woree-Cairns Terminal-Cairns City | Rating (A) | 479 | 479 | 479 | 479 | 479 | 479 | 479 | 479 | 479 | 479 | 479 | 479 | 479 | 479 | 479
FN | 10020819 | 7206 | 7206 CAIRNS CITY | 7206 Woree-Cairns Terminal-Cairns City | Time | 16:30 | 19:00 | 4:00 | 16:30 | 19:00 | 4:00 | 16:30 | 19:00 | 4:00 | 16:30 | 19:00 | 4:00 | 16:30 | 19:00 | 4:00
FN | 10020819 | 7206 | 7206 CAIRNS CITY | 7206 Woree-Cairns Terminal-Cairns City | Voltage at Constrained Conductor | 139.9277 | 139.9476 | 140.0024 | 139.4688 | 139.4931 | 139.5451 | 139.6451 | 139.6727 | 139.7268 | 139.8016 | 139.8325 | 139.8795 | 139.9144 | 139.9481 | 139.993
FN | 10020851 | 3MO2 | MOSSMAN NO 2 | 3MO2_Mossman No 2 66 kV | % of Rated A | 5.1635 | 3.7102 | 3.8754 | 5.1772 | 3.7051 | 3.9937 | 6.1427 | 4.6751 | 5.3233 | 8.3959 | 6.6201 | 7.3484 | 10.963 | 8.6418 | 9.452
FN | 10020851 | 3MO2 | MOSSMAN NO 2 | 3MO2_Mossman No 2 66 kV | Limiting Line Name | TR_LINE 2062_3 | TR_LINE 2062_3 | TR_LINE 2062_3 | TR_LINE 2062_3 | TR_LINE 2062_3 | TR_LINE 2062_3 | TR_LINE 2062_3 | TR_LINE 167072_1 | TR_LINE 167072_1 | TR_LINE 167072_1 | TR_LINE 167072_1 | TR_LINE 167072_1 | TR_LINE 167072_1 | TR_LINE 167072_1 | TR_LINE 167072_1
FN | 10020851 | 3MO2 | MOSSMAN NO 2 | 3MO2_Mossman No 2 66 kV | Loading (A) | 8.7264 | 8.8673 | 9.0297 | 8.7495 | 8.8553 | 9.3053 | 10.3812 | 7.8075 | 8.4641 | 11.0826 | 11.0556 | 11.684 | 14.4712 | 14.4318 | 15.0286
FN | 10020851 | 3MO2 | MOSSMAN NO 2 | 3MO2_Mossman No 2 66 kV | Loading (MVA) | 1.0603 | 1.0833 | 1.1033 | 1.0652 | 1.0846 | 1.1399 | 1.2648 | 0.95465 | 1.0418 | 1.3563 | 1.3537 | 1.4406 | 1.7727 | 1.7689 | 1.8428
FN | 10020851 | 3MO2 | MOSSMAN NO 2 | 3MO2_Mossman No 2 66 kV | Loading (MW) | 0.25065 | 0.26241 | 0.17948 | 0.24097 | 0.22925 | 0.31175 | 0.72873 | 0.72542 | 0.79851 | 1.2144 | 1.2073 | 1.2802 | 1.6716 | 1.6645 | 1.7306
FN | 10020851 | 3MO2 | MOSSMAN NO 2 | 3MO2_Mossman No 2 66 kV | Power Factor | 0.23639 | 0.24224 | 0.16267 | 0.22622 | 0.21136 | 0.27348 | 0.57617 | 0.75989 | 0.76646 | 0.89538 | 0.89187 | 0.88865 | 0.94298 | 0.94101 | 0.93916
FN | 10020851 | 3MO2 | MOSSMAN NO 2 | 3MO2_Mossman No 2 66 kV | Rating (A) | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
FN | 10020851 | 3MO2 | MOSSMAN NO 2 | 3MO2_Mossman No 2 66 kV | Time | 16:30 | 19:00 | 4:00 | 16:30 | 19:00 | 4:00 | 16:00 | 17:30 | 4:00 | 15:30 | 17:30 | 4:00 | 15:30 | 17:30 | 5:30
FN | 10020851 | 3MO2 | MOSSMAN NO 2 | 3MO2_Mossman No 2 66 kV | Voltage at Constrained Conductor | 70.153 | 70.5323 | 70.5451 | 70.2873 | 70.7164 | 70.7283 | 70.3413 | 70.5945 | 71.0646 | 70.6574 | 70.6942 | 71.1872 | 70.7236 | 70.7657 | 70.793
FN | 10020852 | 3MO1 | MOSSMAN NO 1 | 3MO1_Mossman No 1 66 kV | % of Rated A | 23.903 | 18.9875 | 19.9462 | 23.445 | 18.6447 | 19.5861 | 24.1652 | 19.2111 | 20.1806 | 25.7208 | 20.4242 | 21.4539 | 27.6755 | 21.9463 | 23.0519
FN | 10020852 | 3MO1 | MOSSMAN NO 1 | 3MO1_Mossman No 1 66 kV | Limiting Line Name | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1
FN | 10020852 | 3MO1 | MOSSMAN NO 1 | 3MO1_Mossman No 1 66 kV | Loading (A) | 31.5519 | 31.7091 | 31.7144 | 30.9474 | 31.1367 | 31.1419 | 31.898 | 32.0826 | 32.0872 | 33.9515 | 34.1084 | 34.1118 | 36.5316 | 36.6503 | 36.6526
FN | 10020852 | 3MO1 | MOSSMAN NO 1 | 3MO1_Mossman No 1 66 kV | Loading (MVA) | 3.8417 | 3.8818 | 3.8831 | 3.7773 | 3.8236 | 3.8249 | 3.8989 | 3.947 | 3.9482 | 4.1542 | 4.2022 | 4.2032 | 4.4727 | 4.5201 | 4.521
FN | 10020852 | 3MO1 | MOSSMAN NO 1 | 3MO1_Mossman No 1 66 kV | Loading (MW) | 0.74632 | 0.74582 | 0.7458 | 0.17964 | 0.1802 | 0.18022 | 1.02 | 1.0206 | 1.0206 | 1.7979 | 1.7985 | 1.7986 | 2.4811 | 2.4818 | 2.4818
FN | 10020852 | 3MO1 | MOSSMAN NO 1 | 3MO1_Mossman No 1 66 kV | Power Factor | 0.19426 | 0.19213 | 0.19206 | 0.047557 | 0.047129 | 0.047118 | 0.26161 | 0.25857 | 0.2585 | 0.43279 | 0.428 | 0.4279 | 0.55472 | 0.54907 | 0.54896
FN | 10020852 | 3MO1 | MOSSMAN NO 1 | 3MO1_Mossman No 1 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
FN | 10020852 | 3MO1 | MOSSMAN NO 1 | 3MO1_Mossman No 1 66 kV | Time | 16:30 | 19:00 | 4:00 | 16:30 | 19:00 | 4:00 | 16:30 | 19:00 | 4:00 | 16:30 | 19:00 | 4:00 | 16:30 | 19:00 | 4:00
FN | 10020852 | 3MO1 | MOSSMAN NO 1 | 3MO1_Mossman No 1 66 kV | Voltage at Constrained Conductor | 70.2978 | 70.6782 | 70.691 | 70.4684 | 70.8984 | 70.9104 | 70.5688 | 71.0286 | 71.0401 | 70.6421 | 71.1296 | 71.1402 | 70.6877 | 71.2048 | 71.2147
FN | 10020859 | 3DIM | DIMBULAH | 3DIM_Dimbulah 66 kV | % of Rated A | 61.5836 | 49.8821 | 53.0293 | 61.2889 | 49.637 | 52.7953 | 60.8803 | 49.301 | 52.4438 | 60.8198 | 49.2472 | 52.3871 | 60.8695 | 49.2981 | 52.4442
FN | 10020859 | 3DIM | DIMBULAH | 3DIM_Dimbulah 66 kV | Limiting Line Name | TR_LINE 173520_1 | TR_LINE 173520_1 | TR_LINE 173520_1 | TR_LINE 173520_1 | TR_LINE 173520_1 | TR_LINE 173520_1 | TR_LINE 173520_1 | TR_LINE 173520_1 | TR_LINE 173520_1 | TR_LINE 173520_1 | TR_LINE 173520_1 | TR_LINE 173520_1 | TR_LINE 173520_1 | TR_LINE 173520_1 | TR_LINE 173520_1
FN | 10020859 | 3DIM | DIMBULAH | 3DIM_Dimbulah 66 kV | Loading (A) | 134.2522 | 134.1829 | 134.164 | 133.6098 | 133.5235 | 133.5722 | 132.7191 | 132.6196 | 132.6828 | 132.5871 | 132.4751 | 132.5393 | 132.6956 | 132.6119 | 132.6838
FN | 10020859 | 3DIM | DIMBULAH | 3DIM_Dimbulah 66 kV | Loading (MVA) | 16.2588 | 16.258 | 16.2578 | 16.2512 | 16.2502 | 16.2508 | 16.1635 | 16.1624 | 16.1631 | 16.162 | 16.1606 | 16.1614 | 16.1883 | 16.1873 | 16.1881
FN | 10020859 | 3DIM | DIMBULAH | 3DIM_Dimbulah 66 kV | Loading (MW) | 13.9036 | 13.9037 | 13.9037 | 13.9043 | 13.9044 | 13.9043 | 13.8045 | 13.8046 | 13.8046 | 13.8047 | 13.8048 | 13.8047 | 13.8032 | 13.8033 | 13.8032
FN | 10020859 | 3DIM | DIMBULAH | 3DIM_Dimbulah 66 kV | Power Factor | 0.85514 | 0.85519 | 0.8552 | 0.85558 | 0.85564 | 0.85561 | 0.85405 | 0.85412 | 0.85408 | 0.85414 | 0.85422 | 0.85418 | 0.85267 | 0.85273 | 0.85268
FN | 10020859 | 3DIM | DIMBULAH | 3DIM_Dimbulah 66 kV | Rating (A) | 218 | 269 | 253 | 218 | 269 | 253 | 218 | 269 | 253 | 218 | 269 | 253 | 218 | 269 | 253
FN | 10020859 | 3DIM | DIMBULAH | 3DIM_Dimbulah 66 kV | Time | 12:00 | 18:30 | 6:00 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 15:00 | 17:00 | 8:30
FN | 10020859 | 3DIM | DIMBULAH | 3DIM_Dimbulah 66 kV | Voltage at Constrained Conductor | 69.921 | 69.9535 | 69.9624 | 70.2244 | 70.2653 | 70.2422 | 70.3141 | 70.3617 | 70.3314 | 70.3772 | 70.431 | 70.4001 | 70.4342 | 70.4742 | 70.4399
FN | 10129304 | 3RA1 | RAVENSHOE NO 1 | 3RA1_Ravenshoe No 1 66 kV | % of Rated A | 56.6069 | 39.679 | 40.6859 | 57.2266 | 40.1081 | 41.1449 | 57.983 | 40.6347 | 41.6901 | 58.7522 | 41.1704 | 42.2389 | 59.4997 | 41.695 | 42.7792
FN | 10129304 | 3RA1 | RAVENSHOE NO 1 | 3RA1_Ravenshoe No 1 66 kV | Limiting Line Name | TR_LINE 4408_1 | TR_LINE 4408_1 | TR_LINE 4408_1 | TR_LINE 4408_1 | TR_LINE 4408_1 | TR_LINE 4408_1 | TR_LINE 4408_1 | TR_LINE 4408_1 | TR_LINE 4408_1 | TR_LINE 4408_1 | TR_LINE 4408_1 | TR_LINE 4408_1 | TR_LINE 4408_1 | TR_LINE 4408_1 | TR_LINE 4408_1
FN | 10129304 | 3RA1 | RAVENSHOE NO 1 | 3RA1_Ravenshoe No 1 66 kV | Loading (A) | 95.6657 | 95.6264 | 95.6118 | 96.7129 | 96.6606 | 96.6905 | 97.9913 | 97.9296 | 97.9716 | 99.2912 | 99.2207 | 99.2615 | 100.5545 | 100.485 | 100.531
FN | 10129304 | 3RA1 | RAVENSHOE NO 1 | 3RA1_Ravenshoe No 1 66 kV | Loading (MVA) | 11.9339 | 11.934 | 11.934 | 12.1263 | 12.1263 | 12.1263 | 12.3126 | 12.3126 | 12.3126 | 12.497 | 12.4971 | 12.4971 | 12.6732 | 12.6732 | 12.6732
FN | 10129304 | 3RA1 | RAVENSHOE NO 1 | 3RA1_Ravenshoe No 1 66 kV | Loading (MW) | 11.905 | 11.9052 | 11.9052 | 12.0968 | 12.0969 | 12.0968 | 12.2819 | 12.2821 | 12.282 | 12.4652 | 12.4654 | 12.4653 | 12.6402 | 12.6403 | 12.6402
FN | 10129304 | 3RA1 | RAVENSHOE NO 1 | 3RA1_Ravenshoe No 1 66 kV | Power Factor | 0.99758 | 0.99758 | 0.99759 | 0.99757 | 0.99757 | 0.99757 | 0.99751 | 0.99752 | 0.99752 | 0.99745 | 0.99747 | 0.99746 | 0.99739 | 0.9974 | 0.9974
FN | 10129304 | 3RA1 | RAVENSHOE NO 1 | 3RA1_Ravenshoe No 1 66 kV | Rating (A) | 169 | 241 | 235 | 169 | 241 | 235 | 169 | 241 | 235 | 169 | 241 | 235 | 169 | 241 | 235
FN | 10129304 | 3RA1 | RAVENSHOE NO 1 | 3RA1_Ravenshoe No 1 66 kV | Time | 12:00 | 18:30 | 6:00 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30
FN | 10129304 | 3RA1 | RAVENSHOE NO 1 | 3RA1_Ravenshoe No 1 66 kV | Voltage at Constrained Conductor | 72.0223 | 72.0521 | 72.0632 | 72.3908 | 72.4302 | 72.4077 | 72.5439 | 72.5898 | 72.5585 | 72.6667 | 72.7187 | 72.6887 | 72.7652 | 72.8158 | 72.7823
FN | 10131933 | 3MA2 | 3MA2 | 3MA2_Mareeba No 2 66 kV | % of Rated A | 19.364 | 13.6468 | 13.9976 | 19.0885 | 13.4668 | 13.8129 | 19.7646 | 13.9383 | 14.2961 | 21.1118 | 14.8705 | 15.2517 | 22.774 | 16.0194 | 16.4293
FN | 10131933 | 3MA2 | 3MA2 | 3MA2_Mareeba No 2 66 kV | Limiting Line Name | TR_LINE 5351_1 | TR_LINE 5351_1 | TR_LINE 5351_1 | TR_LINE 5351_1 | TR_LINE 5351_1 | TR_LINE 5351_1 | TR_LINE 5351_1 | TR_LINE 5351_1 | TR_LINE 5351_1 | TR_LINE 5351_1 | TR_LINE 5351_1 | TR_LINE 5351_1 | TR_LINE 5351_1 | TR_LINE 5351_1 | TR_LINE 5351_1
FN | 10131933 | 3MA2 | 3MA2 | 3MA2_Mareeba No 2 66 kV | Loading (A) | 32.7252 | 32.8887 | 32.8942 | 32.2596 | 32.455 | 32.4604 | 33.4022 | 33.5912 | 33.5959 | 35.6789 | 35.838 | 35.8415 | 38.4881 | 38.6067 | 38.609
FN | 10131933 | 3MA2 | 3MA2 | 3MA2_Mareeba No 2 66 kV | Loading (MVA) | 3.9764 | 4.0179 | 4.0193 | 3.9273 | 3.9752 | 3.9766 | 4.0703 | 4.1201 | 4.1213 | 4.3504 | 4.4001 | 4.4011 | 4.6942 | 4.7432 | 4.7442
FN | 10131933 | 3MA2 | 3MA2 | 3MA2_Mareeba No 2 66 kV | Loading (MW) | 0.85375 | 0.85439 | 0.85441 | 0.10862 | 0.10789 | 0.10787 | 0.98425 | 0.98348 | 0.98346 | 1.7967 | 1.7959 | 1.7959 | 2.5124 | 2.5116 | 2.5116
FN | 10131933 | 3MA2 | 3MA2 | 3MA2_Mareeba No 2 66 kV | Power Factor | 0.2147 | 0.21265 | 0.21258 | 0.027659 | 0.027141 | 0.027127 | 0.24181 | 0.2387 | 0.23863 | 0.413 | 0.40816 | 0.40806 | 0.53522 | 0.52951 | 0.5294
FN | 10131933 | 3MA2 | 3MA2 | 3MA2_Mareeba No 2 66 kV | Rating (A) | 169 | 241 | 235 | 169 | 241 | 235 | 169 | 241 | 235 | 169 | 241 | 235 | 169 | 241 | 235
FN | 10131933 | 3MA2 | 3MA2 | 3MA2_Mareeba No 2 66 kV | Time | 16:30 | 19:00 | 4:00 | 16:30 | 19:00 | 4:00 | 16:30 | 19:00 | 4:00 | 16:30 | 19:00 | 4:00 | 16:30 | 19:00 | 4:00
FN | 10131933 | 3MA2 | 3MA2 | 3MA2_Mareeba No 2 66 kV | Voltage at Constrained Conductor | 70.153 | 70.5323 | 70.5451 | 70.2873 | 70.7164 | 70.7283 | 70.3549 | 70.8139 | 70.8254 | 70.3979 | 70.8848 | 70.8953 | 70.4169 | 70.9334 | 70.9433
FN | 10132678 | 4LAK | 7285 LAKELAND 132kV | 7285_4LAK (Lakeland) 132kV | % of Rated A | 9.5667 | 7.4688 | 8.4648 | 9.406 | 7.4722 | 8.4696 | 9.8055 | 7.4805 | 8.479 | 10.1565 | 7.4952 | 8.4955 | 10.4496 | 7.5129 | 8.5156
FN | 10132678 | 4LAK | 7285 LAKELAND 132kV | 7285_4LAK (Lakeland) 132kV | Limiting Line Name | TR_LINE 37762_1 | TR_LINE 37686_1 | TR_LINE 37686_1 | TR_LINE 37762_1 | TR_LINE 37686_1 | TR_LINE 37686_1 | TR_LINE 37762_1 | TR_LINE 37686_1 | TR_LINE 37686_1 | TR_LINE 37762_1 | TR_LINE 37686_1 | TR_LINE 37686_1 | TR_LINE 37762_1 | TR_LINE 37686_1 | TR_LINE 37686_1
FN | 10132678 | 4LAK | 7285 LAKELAND 132kV | 7285_4LAK (Lakeland) 132kV | Loading (A) | 44.7722 | 40.6304 | 40.6308 | 44.0201 | 40.6486 | 40.6539 | 45.8899 | 40.6939 | 40.6991 | 47.5326 | 40.7736 | 40.7783 | 48.9041 | 40.8704 | 40.8748
FN | 10132678 | 4LAK | 7285 LAKELAND 132kV | 7285_4LAK (Lakeland) 132kV | Loading (MVA) | 11.2409 | 10.2881 | 10.2899 | 11.1481 | 10.3233 | 10.326 | 11.6287 | 10.3526 | 10.3552 | 12.0508 | 10.387 | 10.3894 | 12.403 | 10.4224 | 10.4247
FN | 10132678 | 4LAK | 7285 LAKELAND 132kV | 7285_4LAK (Lakeland) 132kV | Loading (MW) | 9.4403 | 1.0419 | 1.0419 | 9.9348 | 0.55943 | 0.55944 | 10.3543 | 0.13693 | 0.13694 | 10.7348 | 0.24584 | 0.24583 | 11.0604 | 0.57302 | 0.57302
FN | 10132678 | 4LAK | 7285 LAKELAND 132kV | 7285_4LAK (Lakeland) 132kV | Power Factor | 0.83982 | 0.10127 | 0.10125 | 0.89117 | 0.054191 | 0.054178 | 0.8904 | 0.013226 | 0.013224 | 0.89079 | 0.023668 | 0.023661 | 0.89175 | 0.05498 | 0.054967
FN | 10132678 | 4LAK | 7285 LAKELAND 132kV | 7285_4LAK (Lakeland) 132kV | Rating (A) | 468 | 544 | 480 | 468 | 544 | 480 | 468 | 544 | 480 | 468 | 544 | 480 | 468 | 544 | 480
FN | 10132678 | 4LAK | 7285 LAKELAND 132kV | 7285_4LAK (Lakeland) 132kV | Time | 12:00 | 21:00 | 4:00 | 12:00 | 19:00 | 4:00 | 12:00 | 19:00 | 4:00 | 12:00 | 19:00 | 4:00 | 12:00 | 19:00 | 4:00
FN | 10132678 | 4LAK | 7285 LAKELAND 132kV | 7285_4LAK (Lakeland) 132kV | Voltage at Constrained Conductor | 144.9546 | 146.1915 | 146.2166 | 146.214 | 146.6263 | 146.6457 | 146.3036 | 146.8788 | 146.8974 | 146.3737 | 147.0793 | 147.0962 | 146.4266 | 147.2312 | 147.2469
FN | 80076156 | 3HLA | 3HLA | 3HLA_Helenvale 66 kV | % of Rated A | 3.5459 | 3.3772 | 3.4819 | 3.2203 | 3.0883 | 3.1844 | 3.0327 | 2.926 | 3.0171 | 2.9433 | 2.8516 | 2.9404 | 2.9197 | 2.8345 | 2.9227
FN | 80076156 | 3HLA | 3HLA | 3HLA_Helenvale 66 kV | Limiting Line Name | TR_LINE 39200_1 | TR_LINE 39200_1 | TR_LINE 39200_1 | TR_LINE 39200_1 | TR_LINE 39200_1 | TR_LINE 39200_1 | TR_LINE 39200_1 | TR_LINE 39200_1 | TR_LINE 39200_1 | TR_LINE 39200_1 | TR_LINE 39200_1 | TR_LINE 39200_1 | TR_LINE 39200_1 | TR_LINE 39200_1 | TR_LINE 39200_1
FN | 80076156 | 3HLA | 3HLA | 3HLA_Helenvale 66 kV | Loading (A) | 13.4035 | 13.4751 | 13.475 | 12.1726 | 12.3225 | 12.3236 | 11.4635 | 11.6749 | 11.6761 | 11.1258 | 11.3779 | 11.3792 | 11.0366 | 11.3098 | 11.311
FN | 80076156 | 3HLA | 3HLA | 3HLA_Helenvale 66 kV | Loading (MVA) | 1.5809 | 1.6162 | 1.6162 | 1.4333 | 1.483 | 1.4834 | 1.3498 | 1.408 | 1.4084 | 1.31 | 1.3745 | 1.3748 | 1.2995 | 1.3681 | 1.3684
FN | 80076156 | 3HLA | 3HLA | 3HLA_Helenvale 66 kV | Loading (MW) | 0.91401 | 0.91408 | 0.91408 | 0.62026 | 0.62041 | 0.62041 | 0.37696 | 0.37716 | 0.37716 | 0.17487 | 0.17511 | 0.17511 | 0.022277 | 0.022535 | 0.022536
FN | 80076156 | 3HLA | 3HLA | 3HLA_Helenvale 66 kV | Power Factor | 0.57816 | 0.56556 | 0.56556 | 0.43275 | 0.41834 | 0.41825 | 0.27927 | 0.26787 | 0.26781 | 0.13349 | 0.1274 | 0.12737 | 0.017142 | 0.016472 | 0.016469
FN | 80076156 | 3HLA | 3HLA | 3HLA_Helenvale 66 kV | Rating (A) | 378 | 399 | 387 | 378 | 399 | 387 | 378 | 399 | 387 | 378 | 399 | 387 | 378 | 399 | 387
FN | 80076156 | 3HLA | 3HLA | 3HLA_Helenvale 66 kV | Time | 9:30 | 21:00 | 22:00 | 16:30 | 19:00 | 4:00 | 16:30 | 19:00 | 4:00 | 16:30 | 19:00 | 4:00 | 16:30 | 19:00 | 4:00
FN | 80076156 | 3HLA | 3HLA | 3HLA_Helenvale 66 kV | Voltage at Constrained Conductor | 68.0965 | 69.2488 | 69.2486 | 67.9814 | 69.4849 | 69.4941 | 67.9815 | 69.6303 | 69.6391 | 67.9816 | 69.7477 | 69.7557 | 67.9817 | 69.8383 | 69.8458
FN | 83003861 | 3CHI | CHILLAGOE FDR | 3CHI_Chillagoe 66 kV | % of Rated A | 7.7332 | 7.3162 | 8.1298 | 7.7863 | 7.3657 | 8.188 | 7.7147 | 7.2975 | 8.1128 | 7.7936 | 7.3716 | 8.1953 | 7.7328 | 7.3146 | 8.1322
FN | 83003861 | 3CHI | CHILLAGOE FDR | 3CHI_Chillagoe 66 kV | Limiting Line Name | TR_LINE 104006_1 | TR_LINE 104006_1 | TR_LINE 104006_1 | TR_LINE 104006_1 | TR_LINE 104006_1 | TR_LINE 104006_1 | TR_LINE 104006_1 | TR_LINE 104006_1 | TR_LINE 104006_1 | TR_LINE 104006_1 | TR_LINE 104006_1 | TR_LINE 104006_1 | TR_LINE 104006_1 | TR_LINE 104006_1 | TR_LINE 104006_1
FN | 83003861 | 3CHI | CHILLAGOE FDR | 3CHI_Chillagoe 66 kV | Loading (A) | 42.3778 | 42.3611 | 42.3565 | 42.6687 | 42.6476 | 42.6595 | 42.2767 | 42.2527 | 42.2679 | 42.709 | 42.6815 | 42.6973 | 42.3758 | 42.3517 | 42.369
FN | 83003861 | 3CHI | CHILLAGOE FDR | 3CHI_Chillagoe 66 kV | Loading (MVA) | 5.108 | 5.1084 | 5.1085 | 5.1703 | 5.1708 | 5.1705 | 5.1349 | 5.1355 | 5.1351 | 5.1964 | 5.1971 | 5.1967 | 5.1642 | 5.1648 | 5.1644
FN | 83003861 | 3CHI | CHILLAGOE FDR | 3CHI_Chillagoe 66 kV | Loading (MW) | 4.9134 | 4.9133 | 4.9133 | 4.9743 | 4.9742 | 4.9743 | 4.9341 | 4.934 | 4.934 | 4.998 | 4.9979 | 4.9979 | 4.962 | 4.9619 | 4.962
FN | 83003861 | 3CHI | CHILLAGOE FDR | 3CHI_Chillagoe 66 kV | Power Factor | 0.9619 | 0.96181 | 0.96178 | 0.96209 | 0.96198 | 0.96204 | 0.96089 | 0.96075 | 0.96084 | 0.96182 | 0.96167 | 0.96175 | 0.96084 | 0.9607 | 0.9608
FN | 83003861 | 3CHI | CHILLAGOE FDR | 3CHI_Chillagoe 66 kV | Rating (A) | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521
FN | 83003861 | 3CHI | CHILLAGOE FDR | 3CHI_Chillagoe 66 kV | Time | 12:00 | 18:30 | 6:00 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30
FN | 83003861 | 3CHI | CHILLAGOE FDR | 3CHI_Chillagoe 66 kV | Voltage at Constrained Conductor | 69.5907 | 69.6238 | 69.6328 | 69.9596 | 70.0012 | 69.9777 | 70.1247 | 70.173 | 70.1423 | 70.246 | 70.3004 | 70.2692 | 70.3599 | 70.4084 | 70.3737
FN | 83842085 | FDR 7333 | 132KV CANO 7333 FDR | 7333_Cairns North 132 kV | % of Rated A | 19.3375 | 18.4059 | 20.5175 | 18.9735 | 18.0602 | 20.1322 | 18.7739 | 17.8707 | 19.9216 | 18.6598 | 17.7625 | 19.8002 | 18.6321 | 17.7365 | 19.7709
FN | 83842085 | FDR 7333 | 132KV CANO 7333 FDR | 7333_Cairns North 132 kV | Limiting Line Name | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2
FN | 83842085 | FDR 7333 | 132KV CANO 7333 FDR | 7333_Cairns North 132 kV | Loading (A) | 91.4663 | 91.4774 | 91.5079 | 89.7448 | 89.759 | 89.7894 | 88.8006 | 88.8174 | 88.8501 | 88.2608 | 88.2798 | 88.3089 | 88.1296 | 88.1506 | 88.1784
FN | 83842085 | FDR 7333 | 132KV CANO 7333 FDR | 7333_Cairns North 132 kV | Loading (MVA) | 22.137 | 22.1427 | 22.1586 | 21.6382 | 21.6453 | 21.6606 | 21.4258 | 21.434 | 21.4501 | 21.3076 | 21.3168 | 21.3308 | 21.2837 | 21.2938 | 21.3073
FN | 83842085 | FDR 7333 | 132KV CANO 7333 FDR | 7333_Cairns North 132 kV | Loading (MW) | 6.2494 | 6.2494 | 6.2497 | 4.6368 | 4.6369 | 4.6371 | 3.0388 | 3.0389 | 3.0391 | 1.434 | 1.4341 | 1.4343 | 0.089878 | 0.089745 | 0.089568
FN | 83842085 | FDR 7333 | 132KV CANO 7333 FDR | 7333_Cairns North 132 kV | Power Factor | 0.2823 | 0.28223 | 0.28204 | 0.21429 | 0.21422 | 0.21408 | 0.14183 | 0.14178 | 0.14168 | 0.067298 | 0.067274 | 0.067239 | 0.0042228 | 0.0042146 | 0.0042036
FN | 83842085 | FDR 7333 | 132KV CANO 7333 FDR | 7333_Cairns North 132 kV | Rating (A) | 473 | 497 | 446 | 473 | 497 | 446 | 473 | 497 | 446 | 473 | 497 | 446 | 473 | 497 | 446
FN | 83842085 | FDR 7333 | 132KV CANO 7333 FDR | 7333_Cairns North 132 kV | Time | 16:30 | 19:00 | 4:00 | 16:30 | 19:00 | 4:00 | 16:30 | 19:00 | 4:00 | 16:30 | 19:00 | 4:00 | 16:30 | 19:00 | 4:00
FN | 83842085 | FDR 7333 | 132KV CANO 7333 FDR | 7333_Cairns North 132 kV | Voltage at Constrained Conductor | 139.7321 | 139.7515 | 139.8051 | 139.2038 | 139.2276 | 139.2785 | 139.3031 | 139.3302 | 139.3832 | 139.3815 | 139.4118 | 139.4579 | 139.4328 | 139.4659 | 139.51
FN | 83842089 | 7332 | Cairns North 132 kV | 7332_Cairns North 132 kV | % of Rated A | 19.7987 | 18.8449 | 21.0067 | 19.409 | 18.4747 | 20.5942 | 19.1918 | 18.2685 | 20.365 | 19.0672 | 18.1503 | 20.2325 | 19.0362 | 18.1212 | 20.1998
FN | 83842089 | 7332 | Cairns North 132 kV | 7332_Cairns North 132 kV | Limiting Line Name | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2
FN | 83842089 | 7332 | Cairns North 132 kV | 7332_Cairns North 132 kV | Loading (A) | 93.6478 | 93.659 | 93.69 | 91.8048 | 91.8192 | 91.8502 | 90.7774 | 90.7945 | 90.8279 | 90.1877 | 90.2071 | 90.2368 | 90.0411 | 90.0625 | 90.091
FN | 83842089 | 7332 | Cairns North 132 kV | 7332_Cairns North 132 kV | Loading (MVA) | 22.6649 | 22.6708 | 22.687 | 22.1349 | 22.1421 | 22.1577 | 21.9028 | 21.9112 | 21.9276 | 21.7727 | 21.7822 | 21.7965 | 21.7454 | 21.7557 | 21.7694
FN | 83842089 | 7332 | Cairns North 132 kV | 7332_Cairns North 132 kV | Loading (MW) | 6.5395 | 6.5396 | 6.5398 | 4.8476 | 4.8477 | 4.8479 | 3.1709 | 3.171 | 3.1713 | 1.4871 | 1.4872 | 1.4874 | 0.11174 | 0.11161 | 0.11144
FN | 83842089 | 7332 | Cairns North 132 kV | 7332_Cairns North 132 kV | Power Factor | 0.28853 | 0.28846 | 0.28826 | 0.219 | 0.21894 | 0.21879 | 0.14477 | 0.14472 | 0.14462 | 0.068301 | 0.068276 | 0.06824 | 0.0051387 | 0.0051303 | 0.005119
FN | 83842089 | 7332 | Cairns North 132 kV | 7332_Cairns North 132 kV | Rating (A) | 473 | 497 | 446 | 473 | 497 | 446 | 473 | 497 | 446 | 473 | 497 | 446 | 473 | 497 | 446
FN | 83842089 | 7332 | Cairns North 132 kV | 7332_Cairns North 132 kV | Time | 16:30 | 19:00 | 4:00 | 16:30 | 19:00 | 4:00 | 16:30 | 19:00 | 4:00 | 16:30 | 19:00 | 4:00 | 16:30 | 19:00 | 4:00
FN | 83842089 | 7332 | Cairns North 132 kV | 7332_Cairns North 132 kV | Voltage at Constrained Conductor | 139.7321 | 139.7515 | 139.8051 | 139.2038 | 139.2276 | 139.2785 | 139.3031 | 139.3302 | 139.3832 | 139.3815 | 139.4118 | 139.4579 | 139.4328 | 139.4659 | 139.51
FN | 84463555 | 3COO | COOKTOWN FEEDER | 3COO_Cooktown 66 kV | % of Rated A | 2.9839 | 2.9838 | 2.9839 | 2.0012 | 2.0012 | 2.0012 | 1.2286 | 1.2096 | 1.3373 | 1.049 | 1.0315 | 1.1571 | 1.0162 | 1.0036 | 1.1257
FN | 84463555 | 3COO | COOKTOWN FEEDER | 3COO_Cooktown 66 kV | Limiting Line Name | TR_CABLE 12_1 | TR_CABLE 12_1 | TR_CABLE 12_1 | TR_CABLE 12_1 | TR_CABLE 12_1 | TR_CABLE 12_1 | TR_LINE 138000_1 | TR_CABLE 12_1 | TR_LINE 138000_1 | TR_LINE 138000_1 | TR_LINE 138000_1 | TR_LINE 138000_1 | TR_LINE 138000_1 | TR_LINE 138000_1 | TR_LINE 138000_1
FN | 84463555 | 3COO | COOKTOWN FEEDER | 3COO_Cooktown 66 kV | Loading (A) | 7.4001 | 7.3999 | 7.4 | 4.963 | 4.9629 | 4.9629 | 4.9021 | 2.9998 | 4.948 | 4.1853 | 4.2807 | 4.2811 | 4.0548 | 4.1648 | 4.1652
FN | 84463555 | 3COO | COOKTOWN FEEDER | 3COO_Cooktown 66 kV | Loading (MVA) | 0.87271 | 0.87271 | 0.87271 | 0.58594 | 0.58594 | 0.58594 | 0.57914 | 0.35449 | 0.59883 | 0.4947 | 0.51912 | 0.51923 | 0.47944 | 0.50589 | 0.50599
FN | 84463555 | 3COO | COOKTOWN FEEDER | 3COO_Cooktown 66 kV | Loading (MW) | 0.863 | 0.863 | 0.863 | 0.57083 | 0.57083 | 0.57083 | 0.32863 | 0.32837 | 0.32876 | 0.1268 | 0.12694 | 0.12694 | 0.025736 | 0.02558 | 0.02558
FN | 84463555 | 3COO | COOKTOWN FEEDER | 3COO_Cooktown 66 kV | Power Factor | 0.98888 | 0.98888 | 0.98888 | 0.97422 | 0.97422 | 0.97422 | 0.56744 | 0.92631 | 0.54901 | 0.25631 | 0.24453 | 0.24448 | 0.053679 | 0.050565 | 0.050553
FN | 84463555 | 3COO | COOKTOWN FEEDER | 3COO_Cooktown 66 kV | Rating (A) | 248 | 248 | 248 | 248 | 248 | 248 | 399 | 248 | 370 | 399 | 415 | 370 | 399 | 415 | 370
FN | 84463555 | 3COO | COOKTOWN FEEDER | 3COO_Cooktown 66 kV | Time | 10:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 16:30 | 17:00 | 4:00 | 16:30 | 19:00 | 4:00 | 16:30 | 19:00 | 4:00
FN | 84463555 | 3COO | COOKTOWN FEEDER | 3COO_Cooktown 66 kV | Voltage at Constrained Conductor | 68.0881 | 68.0896 | 68.0885 | 68.1628 | 68.1646 | 68.1635 | 68.2092 | 68.2262 | 69.8741 | 68.2417 | 70.0149 | 70.0229 | 68.2661 | 70.1296 | 70.1371
MK | 20010276 | ME-PR-1 | Merinda-Proserpine No.1 | ME-PR-1_Merinda - Proserpine No 1 66 kV | % of Rated A | 11.0129 | 7.2775 | 7.803 | 11.6486 | 7.6424 | 8.2444 | 12.4044 | 8.1118 | 8.7771 | 13.3279 | 8.7093 | 9.5577 | 14.2166 | 9.3021 | 10.4864
MK | 20010276 | ME-PR-1 | Merinda-Proserpine No.1 | ME-PR-1_Merinda - Proserpine No 1 66 kV | Limiting Line Name | TR_LINE 175214_1 | TR_LINE 175214_1 | TR_LINE 175214_1 | TR_LINE 175214_1 | TR_LINE 175214_1 | TR_LINE 175214_1 | TR_LINE 175214_1 | TR_LINE 175214_1 | TR_LINE 175214_1 | TR_LINE 175214_1 | TR_LINE 175214_1 | TR_LINE 112170_1 | TR_LINE 175214_1 | TR_LINE 175214_1 | TR_LINE 112170_1
MK | 20010276 | ME-PR-1 | Merinda-Proserpine No.1 | ME-PR-1_Merinda - Proserpine No 1 66 kV | Loading (A) | 21.2548 | 19.9404 | 20.8341 | 22.4818 | 20.9401 | 22.0126 | 23.9405 | 22.2264 | 23.4349 | 25.7229 | 23.8636 | 20.8358 | 27.4381 | 25.4878 | 22.8604
MK | 20010276 | ME-PR-1 | Merinda-Proserpine No.1 | ME-PR-1_Merinda - Proserpine No 1 66 kV | Loading (MVA) | 2.5424 | 2.3831 | 2.4917 | 2.6942 | 2.5074 | 2.6377 | 2.8738 | 2.6658 | 2.8128 | 3.0928 | 2.8669 | 2.5111 | 3.3037 | 3.0664 | 2.7567
MK | 20010276 | ME-PR-1 | Merinda-Proserpine No.1 | ME-PR-1_Merinda - Proserpine No 1 66 kV | Loading (MW) | 1.2408 | 0.94789 | 1.1676 | 1.565 | 1.2719 | 1.4917 | 1.8756 | 1.5822 | 1.8021 | 2.2058 | 1.912 | 2.1099 | 2.4959 | 2.2026 | 2.3962
MK | 20010276 | ME-PR-1 | Merinda-Proserpine No.1 | ME-PR-1_Merinda - Proserpine No 1 66 kV | Power Factor | 0.48805 | 0.39775 | 0.46857 | 0.58089 | 0.50728 | 0.56554 | 0.65266 | 0.59352 | 0.64067 | 0.71322 | 0.66692 | 0.84024 | 0.75549 | 0.71829 | 0.86923
MK | 20010276 | ME-PR-1 | Merinda-Proserpine No.1 | ME-PR-1_Merinda - Proserpine No 1 66 kV | Rating (A) | 193 | 274 | 267 | 193 | 274 | 267 | 193 | 274 | 267 | 193 | 274 | 218 | 193 | 274 | 218
MK | 20010276 | ME-PR-1 | Merinda-Proserpine No.1 | ME-PR-1_Merinda - Proserpine No 1 66 kV | Time | 11:00 | 17:00 | 8:30 | 11:00 | 17:00 | 8:30 | 11:00 | 17:00 | 8:30 | 11:00 | 17:00 | 8:30 | 11:00 | 17:00 | 8:30
MK | 20010276 | ME-PR-1 | Merinda-Proserpine No.1 | ME-PR-1_Merinda - Proserpine No 1 66 kV | Voltage at Constrained Conductor | 69.0586 | 69.0011 | 69.0506 | 69.1885 | 69.1317 | 69.1808 | 69.3041 | 69.2478 | 69.2964 | 69.4171 | 69.3615 | 69.5816 | 69.5159 | 69.4609 | 69.6211
MK | 20011116 | NL-WR-1 | Newlands-Wirralie | NL-WR-1_Newlands-Wirralie 1 66 kV | % of Rated A | 5.1821 | 4.7524 | 5.2661 | 5.1775 | 4.7481 | 5.2614 | 5.1822 | 4.7525 | 5.2662 | 5.1914 | 4.7609 | 5.2756 | 5.1992 | 4.768 | 5.2835
MK | 20011116 | NL-WR-1 | Newlands-Wirralie | NL-WR-1_Newlands-Wirralie 1 66 kV | Limiting Line Name | TR_LINE 180753_1 | TR_LINE 180753_1 | TR_LINE 180753_1 | TR_LINE 180753_1 | TR_LINE 180753_1 | TR_LINE 180753_1 | TR_LINE 180753_1 | TR_LINE 180753_1 | TR_LINE 180753_1 | TR_LINE 180753_1 | TR_LINE 180753_1 | TR_LINE 180753_1 | TR_LINE 180753_1 | TR_LINE 180753_1 | TR_LINE 180753_1
MK | 20011116 | NL-WR-1 | Newlands-Wirralie | NL-WR-1_Newlands-Wirralie 1 66 kV | Loading (A) | 9.7424 | 9.7424 | 9.7424 | 9.7336 | 9.7336 | 9.7336 | 9.7426 | 9.7426 | 9.7426 | 9.7598 | 9.7598 | 9.7598 | 9.7744 | 9.7744 | 9.7744
MK | 20011116 | NL-WR-1 | Newlands-Wirralie | NL-WR-1_Newlands-Wirralie 1 66 kV | Loading (MVA) | 1.1595 | 1.1595 | 1.1595 | 1.1585 | 1.1585 | 1.1585 | 1.1597 | 1.1597 | 1.1597 | 1.162 | 1.162 | 1.162 | 1.164 | 1.164 | 1.164
MK | 20011116 | NL-WR-1 | Newlands-Wirralie | NL-WR-1_Newlands-Wirralie 1 66 kV | Loading (MW) | 0.070813 | 0.070813 | 0.070813 | 0.014133 | 0.014133 | 0.014133 | 0.038823 | 0.038823 | 0.038823 | 0.077823 | 0.077823 | 0.077823 | 0.10018 | 0.10018 | 0.10018
MK | 20011116 | NL-WR-1 | Newlands-Wirralie | NL-WR-1_Newlands-Wirralie 1 66 kV | Power Factor | 0.061074 | 0.061074 | 0.061074 | 0.0122 | 0.0122 | 0.0122 | 0.033477 | 0.033477 | 0.033477 | 0.066972 | 0.066972 | 0.066972 | 0.086065 | 0.086065 | 0.086065
MK | 20011116 | NL-WR-1 | Newlands-Wirralie | NL-WR-1_Newlands-Wirralie 1 66 kV | Rating (A) | 188 | 205 | 185 | 188 | 205 | 185 | 188 | 205 | 185 | 188 | 205 | 185 | 188 | 205 | 185
MK | 20011116 | NL-WR-1 | Newlands-Wirralie | NL-WR-1_Newlands-Wirralie 1 66 kV | Time | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30
MK | 20011116 | NL-WR-1 | Newlands-Wirralie | NL-WR-1_Newlands-Wirralie 1 66 kV | Voltage at Constrained Conductor | 68.7116 | 68.7116 | 68.7116 | 68.7141 | 68.7141 | 68.7141 | 68.7253 | 68.7253 | 68.7253 | 68.7403 | 68.7403 | 68.7403 | 68.7555 | 68.7555 | 68.7555
MK | 30053760 | 118 | CANNONVALE NO 2 | 118_Cannonvale No 2 66 kV | % of Rated A | 47.6777 | 47.6405 | 47.6725 | 47.1859 | 47.1476 | 47.1805 | 47.7346 | 47.6976 | 47.7295 | 49.3183 | 49.2851 | 49.3137 | 51.6822 | 51.6541 | 51.6784
MK | 30053760 | 118 | CANNONVALE NO 2 | 118_Cannonvale No 2 66 kV | Limiting Line Name | TR_CABLE 7280_1 | TR_CABLE 7280_1 | TR_CABLE 7280_1 | TR_CABLE 7280_1 | TR_CABLE 7280_1 | TR_CABLE 7280_1 | TR_CABLE 7280_1 | TR_CABLE 7280_1 | TR_CABLE 7280_1 | TR_CABLE 7280_1 | TR_CABLE 7280_1 | TR_CABLE 7280_1 | TR_CABLE 7280_1 | TR_CABLE 7280_1 | TR_CABLE 7280_1
MK | 30053760 | 118 | CANNONVALE NO 2 | 118_Cannonvale No 2 66 kV | Loading (A) | 92.018 | 91.9462 | 92.008 | 91.0687 | 90.9948 | 91.0585 | 92.1277 | 92.0564 | 92.1179 | 95.1844 | 95.1202 | 95.1755 | 99.7467 | 99.6924 | 99.7392
MK | 30053760 | 118 | CANNONVALE NO 2 | 118_Cannonvale No 2 66 kV | Loading (MVA) | 11.0065 | 10.9888 | 11.004 | 10.9134 | 10.8957 | 10.911 | 11.0588 | 11.0414 | 11.0564 | 11.4443 | 11.4276 | 11.442 | 12.01 | 11.9941 | 12.0078
MK | 30053760 | 118 | CANNONVALE NO 2 | 118_Cannonvale No 2 66 kV | Loading (MW) | 2.2213 | 2.221 | 2.2213 | 0.48371 | 0.48341 | 0.48367 | 1.268 | 1.2682 | 1.268 | 3.0418 | 3.0421 | 3.0418 | 4.7256 | 4.7259 | 4.7257
MK | 30053760 | 118 | CANNONVALE NO 2 | 118_Cannonvale No 2 66 kV | Power Factor | 0.20182 | 0.20212 | 0.20186 | 0.044322 | 0.044367 | 0.044328 | 0.11466 | 0.11486 | 0.11469 | 0.26579 | 0.2662 | 0.26585 | 0.39348 | 0.39402 | 0.39355
MK | 30053760 | 118 | CANNONVALE NO 2 | 118_Cannonvale No 2 66 kV | Rating (A) | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193
MK | 30053760 | 118 | CANNONVALE NO 2 | 118_Cannonvale No 2 66 kV | Time | 11:00 | 21:00 | 8:30 | 11:00 | 21:00 | 8:30 | 11:00 | 21:00 | 8:30 | 11:00 | 21:00 | 8:30 | 11:00 | 21:00 | 8:30
MK | 30053760 | 118 | CANNONVALE NO 2 | 118_Cannonvale No 2 66 kV | Voltage at Constrained Conductor | 69.058 | 69.001 | 69.05 | 69.188 | 69.1318 | 69.1802 | 69.3037 | 69.2481 | 69.296 | 69.4167 | 69.3619 | 69.4092 | 69.5156 | 69.4614 | 69.5082
MK | 30053761 | 119 | CANNONVALE NO 1 | 119_Cannonvale No 1 66 kV | % of Rated A | 35.8663 | 25.6206 | 26.3322 | 33.7163 | 24.0847 | 24.7537 | 31.9939 | 22.8543 | 23.4891 | 29.7716 | 21.2668 | 21.8575 | 27.6285 | 19.7358 | 20.2841
MK | 30053761 | 119 | CANNONVALE NO 1 | 119_Cannonvale No 1 66 kV | Limiting Line Name | TR_LINE 13015_1 | TR_LINE 13015_1 | TR_LINE 13015_1 | TR_LINE 13015_1 | TR_LINE 13015_1 | TR_LINE 13015_1 | TR_LINE 13015_1 | TR_LINE 13015_1 | TR_LINE 13015_1 | TR_LINE 13015_1 | TR_LINE 13015_1 | TR_LINE 13015_1 | TR_LINE 13015_1 | TR_LINE 13015_1 | TR_LINE 13015_1
MK | 30053761 | 119 | CANNONVALE NO 1 | 119_Cannonvale No 1 66 kV | Loading (A) | 66.3527 | 66.3573 | 66.3573 | 62.3751 | 62.3793 | 62.3793 | 59.1887 | 59.1926 | 59.1926 | 55.0775 | 55.0809 | 55.0809 | 51.1128 | 51.1158 | 51.116
MK | 30053761 | 119 | CANNONVALE NO 1 | 119_Cannonvale No 1 66 kV | Loading (MVA) | 7.9204 | 7.9203 | 7.9203 | 7.4608 | 7.4607 | 7.4607 | 7.0923 | 7.0922 | 7.0922 | 6.6114 | 6.6113 | 6.6113 | 6.1451 | 6.145 | 6.145
MK | 30053761 | 119 | CANNONVALE NO 1 | 119_Cannonvale No 1 66 kV | Loading (MW) | 7.7388 | 7.7388 | 7.7388 | 7.2604 | 7.2604 | 7.2604 | 6.8796 | 6.8796 | 6.8796 | 6.3764 | 6.3764 | 6.3764 | 5.8894 | 5.8895 | 5.8895
MK | 30053761 | 119 | CANNONVALE NO 1 | 119_Cannonvale No 1 66 kV | Power Factor | 0.97707 | 0.97708 | 0.97708 | 0.97314 | 0.97316 | 0.97316 | 0.97001 | 0.97003 | 0.97003 | 0.96445 | 0.96446 | 0.96446 | 0.9584 | 0.95842 | 0.95842
MK | 30053761 | 119 | CANNONVALE NO 1 | 119_Cannonvale No 1 66 kV | Rating (A) | 185 | 259 | 252 | 185 | 259 | 252 | 185 | 259 | 252 | 185 | 259 | 252 | 185 | 259 | 252
MK | 30053761 | 119 | CANNONVALE NO 1 | 119_Cannonvale No 1 66 kV | Time | 16:30 | 17:00 | 7:30 | 16:30 | 17:00 | 7:30 | 16:30 | 17:00 | 7:30 | 16:30 | 17:00 | 7:30 | 16:30 | 17:00 | 7:30
MK | 30053761 | 119 | CANNONVALE NO 1 | 119_Cannonvale No 1 66 kV | Voltage at Constrained Conductor | 68.9173 | 68.9119 | 68.9119 | 69.0578 | 69.0524 | 69.0524 | 69.1811 | 69.1758 | 69.1757 | 69.3043 | 69.299 | 69.299 | 69.4123 | 69.4071 | 69.4069
MK | 30053762 | 120 | Proserpine-Calen | 120_Prosperpine - Calen 66 kV | % of Rated A | 9.0821 | 6.7718 | 7.0518 | 10.989 | 8.1953 | 8.5327 | 13.0911 | 9.7632 | 10.1652 | 15.2244 | 11.3542 | 11.8218 | 17.2127 | 12.8372 | 13.3658
MK | 30053762 | 120 | Proserpine-Calen | 120_Prosperpine - Calen 66 kV | Limiting Line Name | TR_LINE 89457_1 | TR_LINE 89457_1 | TR_LINE 89457_1 | TR_LINE 89457_1 | TR_LINE 89457_1 | TR_LINE 89457_1 | TR_LINE 89457_1 | TR_LINE 89457_1 | TR_LINE 89457_1 | TR_LINE 89457_1 | TR_LINE 89457_1 | TR_LINE 89457_1 | TR_LINE 89457_1 | TR_LINE 89457_1 | TR_LINE 89457_1
MK | 30053762 | 120 | Proserpine-Calen | 120_Prosperpine - Calen 66 kV | Loading (A) | 11.9884 | 11.9861 | 11.9881 | 14.5055 | 14.5057 | 14.5057 | 17.2803 | 17.2808 | 17.2808 | 20.0962 | 20.097 | 20.097 | 22.7207 | 22.7218 | 22.7218
MK | 30053762 | 120 | Proserpine-Calen | 120_Prosperpine - Calen 66 kV | Loading (MVA) | 1.434 | 1.4325 | 1.4338 | 1.737 | 1.7369 | 1.7369 | 2.0728 | 2.0727 | 2.0727 | 2.4145 | 2.4144 | 2.4144 | 2.7337 | 2.7336 | 2.7336
MK | 30053762 | 120 | Proserpine-Calen | 120_Prosperpine - Calen 66 kV | Loading (MW) | 0.88973 | 0.88973 | 0.88973 | 1.3232 | 1.3232 | 1.3232 | 1.7405 | 1.7405 | 1.7405 | 2.1367 | 2.1367 | 2.1367 | 2.493 | 2.493 | 2.493
MK | 30053762 | 120 | Proserpine-Calen | 120_Prosperpine - Calen 66 kV | Power Factor | 0.62048 | 0.62111 | 0.62056 | 0.76175 | 0.7618 | 0.7618 | 0.83971 | 0.83975 | 0.83975 | 0.88496 | 0.88499 | 0.88499 | 0.91193 | 0.91195 | 0.91195
MK | 30053762 | 120 | Proserpine-Calen | 120_Prosperpine - Calen 66 kV | Rating (A) | 132 | 177 | 170 | 132 | 177 | 170 | 132 | 177 | 170 | 132 | 177 | 170 | 132 | 177 | 170
MK | 30053762 | 120 | Proserpine-Calen | 120_Prosperpine - Calen 66 kV | Time | 11:00 | 21:00 | 8:30 | 16:30 | 17:00 | 7:30 | 16:30 | 17:00 | 7:30 | 16:30 | 17:00 | 7:30 | 16:30 | 17:00 | 7:30
MK | 30053762 | 120 | Proserpine-Calen | 120_Prosperpine - Calen 66 kV | Voltage at Constrained Conductor | 69.058 | 69.001 | 69.05 | 69.1365 | 69.1312 | 69.1311 | 69.2526 | 69.2473 | 69.2473 | 69.3663 | 69.361 | 69.361 | 69.4657 | 69.4605 | 69.4603
MK | 30053795 | 3045 | SARINA 1 | 3045_Sarina No 1 33 kV | % of Rated A | 25.846 | 23.3503 | 25.0403 | 26.2994 | 23.7596 | 25.4881 | 26.9297 | 24.3288 | 26.1113 | 27.6989 | 25.0234 | 26.8721 | 28.5173 | 25.7624 | 27.6814
MK | 30053795 | 3045 | SARINA 1 | 3045_Sarina No 1 33 kV | Limiting Line Name | TR_LINE 12173_1 | TR_LINE 12173_1 | TR_LINE 11547_1 | TR_LINE 12173_1 | TR_LINE 12173_1 | TR_LINE 11547_1 | TR_LINE 12173_1 | TR_LINE 12173_1 | TR_LINE 11547_1 | TR_LINE 12173_1 | TR_LINE 12173_1 | TR_LINE 11547_1 | TR_LINE 12173_1 | TR_LINE 12173_1 | TR_LINE 11547_1
MK | 30053795 | 3045 | SARINA 1 | 3045_Sarina No 1 33 kV | Loading (A) | 77.2723 | 77.282 | 76.3592 | 78.6279 | 78.637 | 77.7251 | 80.5126 | 80.5211 | 79.6262 | 82.8128 | 82.8204 | 81.9469 | 85.2601 | 85.2669 | 84.4158
MK | 30053795 | 3045 | SARINA 1 | 3045_Sarina No 1 33 kV | Loading (MVA) | 4.7896 | 4.7908 | 4.8202 | 4.884 | 4.8852 | 4.9224 | 5.0115 | 5.0126 | 5.0588 | 5.1647 | 5.1658 | 5.2219 | 5.3265 | 5.3276 | 5.3935
MK | 30053795 | 3045 | SARINA 1 | 3045_Sarina No 1 33 kV | Loading (MW) | 0.53116 | 0.53114 | 0.59054 | 0.97218 | 0.97217 | 1.0337 | 1.4121 | 1.4121 | 1.4766 | 1.8393 | 1.8393 | 1.9075 | 2.2262 | 2.2262 | 2.2986
MK | 30053795 | 3045 | SARINA 1 | 3045_Sarina No 1 33 kV | Power Factor | 0.1109 | 0.11087 | 0.12251 | 0.19905 | 0.199 | 0.20999 | 0.28177 | 0.2817 | 0.29188 | 0.35612 | 0.35604 | 0.3653 | 0.41795 | 0.41786 | 0.42618
MK | 30053795 | 3045 | SARINA 1 | 3045_Sarina No 1 33 kV | Rating (A) | 299 | 331 | 305 | 299 | 331 | 305 | 299 | 331 | 305 | 299 | 331 | 305 | 299 | 331 | 305
MK | 30053795 | 3045 | SARINA 1 | 3045_Sarina No 1 33 kV | Time | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00
MK | 30053795 | 3045 | SARINA 1 | 3045_Sarina No 1 33 kV | Voltage at Constrained Conductor | 35.786 | 35.7907 | 36.4454 | 35.8627 | 35.8673 | 36.5645 | 35.9368 | 35.9413 | 36.6803 | 36.0069 | 36.0114 | 36.7904 | 36.0691 | 36.0735 | 36.8884
MK | 30053796 | 3046 | ROSELLA | 3046_Rosella 33 kV | % of Rated A | 2.422 | 2.4218 | 2.4219 | 1.9419 | 1.9417 | 1.9418 | 1.5169 | 1.5168 | 1.5168 | 1.1447 | 1.1446 | 1.1447 | 0.84841 | 0.84837 | 0.8484
MK | 30053796 | 3046 | ROSELLA | 3046_Rosella 33 kV | Limiting Line Name | TR_CABLE 6962_1 | TR_CABLE 6962_1 | TR_CABLE 6962_1 | TR_CABLE 6962_1 | TR_CABLE 6962_1 | TR_CABLE 6962_1 | TR_CABLE 6962_1 | TR_CABLE 6962_1 | TR_CABLE 6962_1 | TR_CABLE 6962_1 | TR_CABLE 6962_1 | TR_CABLE 6962_1 | TR_CABLE 6962_1 | TR_CABLE 6962_1 | TR_CABLE 6962_1
MK | 30053796 | 3046 | ROSELLA | 3046_Rosella 33 kV | Loading (A) | 9.9059 | 9.9052 | 9.9056 | 7.9422 | 7.9416 | 7.942 | 6.2041 | 6.2037 | 6.2039 | 4.6818 | 4.6816 | 4.6817 | 3.47 | 3.4698 | 3.4699
MK | 30053796 | 3046 | ROSELLA | 3046_Rosella 33 kV | Loading (MVA) | 0.5963 | 0.5963 | 0.5963 | 0.47811 | 0.47811 | 0.47811 | 0.37349 | 0.37349 | 0.37349 | 0.28186 | 0.28186 | 0.28186 | 0.2089 | 0.20891 | 0.2089
MK | 30053796 | 3046 | ROSELLA | 3046_Rosella 33 kV | Loading (MW) | 0.59214 | 0.59214 | 0.59214 | 0.47259 | 0.47259 | 0.47259 | 0.36609 | 0.36609 | 0.36609 | 0.27169 | 0.27169 | 0.27169 | 0.19473 | 0.19473 | 0.19473
MK | 30053796 | 3046 | ROSELLA | 3046_Rosella 33 kV | Power Factor | 0.99303 | 0.99302 | 0.99303 | 0.98845 | 0.98844 | 0.98845 | 0.98018 | 0.98018 | 0.98018 | 0.96393 | 0.96392 | 0.96393 | 0.93216 | 0.93214 | 0.93215
MK | 30053796 | 3046 | ROSELLA | 3046_Rosella 33 kV | Rating (A) | 409 | 409 | 409 | 409 | 409 | 409 | 409 | 409 | 409 | 409 | 409 | 409 | 409 | 409 | 409
MK | 30053796 | 3046 | ROSELLA | 3046_Rosella 33 kV | Time | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30
MK | 30053796 | 3046 | ROSELLA | 3046_Rosella 33 kV | Voltage at Constrained Conductor | 34.7545 | 34.7569 | 34.7554 | 34.756 | 34.7584 | 34.7569 | 34.757 | 34.7594 | 34.7579 | 34.7576 | 34.76 | 34.7585 | 34.7578 | 34.7601 | 34.7587
MK | 30053797 | 3047 | SARINA 2 | 3047_Sarina No 2 33 kV | % of Rated A | 1.8489 | 1.7496 | 1.8013 | 2.1556 | 2.3145 | 2.4765 | 3.9382 | 3.9372 | 4.0922 | 5.8913 | 5.6975 | 5.8373 | 7.7225 | 7.3512 | 7.478
MK | 30053797 | 3047 | SARINA 2 | 3047_Sarina No 2 33 kV | Limiting Line Name | TR_LINE 11717_1 | TR_LINE 11717_1 | TR_LINE 11717_1 | TR_LINE 11717_1 | TR_LINE 11717_1 | TR_LINE 11717_1 | TR_LINE 11717_1 | TR_LINE 11717_1 | TR_LINE 11717_1 | TR_LINE 11717_1 | TR_LINE 11717_1 | TR_LINE 11717_1 | TR_LINE 11717_1 | TR_LINE 11717_1 | TR_LINE 11717_1
MK | 30053797 | 3047 | SARINA 2 | 3047_Sarina No 2 33 kV | Loading (A) | 7.0259 | 7.3135 | 7.5654 | 8.1912 | 9.6745 | 10.4014 | 14.9652 | 16.4574 | 17.1872 | 22.3868 | 23.8154 | 24.5166 | 29.3415 | 30.7239 | 31.4033
MK | 30053797 | 3047 | SARINA 2 | 3047_Sarina No 2 33 kV | Loading (MVA) | 0.42321 | 0.44091 | 0.45619 | 0.49425 | 0.58401 | 0.62802 | 0.90407 | 0.99464 | 1.039 | 1.3539 | 1.4409 | 1.4837 | 1.7766 | 1.8611 | 1.9026
MK | 30053797 | 3047 | SARINA 2 | 3047_Sarina No 2 33 kV | Loading (MW) | 0.27184 | 0.12225 | 0.084287 | 0.33147 | 0.40867 | 0.44648 | 0.83099 | 0.9079 | 0.94557 | 1.31 | 1.3867 | 1.4242 | 1.7467 | 1.8231 | 1.8605
MK | 30053797 | 3047 | SARINA 2 | 3047_Sarina No 2 33 kV | Power Factor | 0.64234 | 0.27727 | 0.18476 | 0.67066 | 0.69976 | 0.71093 | 0.91917 | 0.91279 | 0.9101 | 0.96759 | 0.96235 | 0.95994 | 0.98317 | 0.9796 | 0.97788
MK | 30053797 | 3047 | SARINA 2 | 3047_Sarina No 2 33 kV | Rating (A) | 380 | 418 | 420 | 380 | 418 | 420 | 380 | 418 | 420 | 380 | 418 | 420 | 380 | 418 | 420
MK | 30053797 | 3047 | SARINA 2 | 3047_Sarina No 2 33 kV | Time | 12:00 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00
MK | 30053797 | 3047 | SARINA 2 | 3047_Sarina No 2 33 kV | Voltage at Constrained Conductor | 34.7767 | 34.8068 | 34.8143 | 34.8369 | 34.8522 | 34.8596 | 34.8784 | 34.8936 | 34.901 | 34.9171 | 34.9322 | 34.9395 | 34.9571 | 34.9724 | 34.9798
MK | 30053798 | 231 | Carmila | 231_Carmila 33 kV | % of Rated A | 5.7021 | 3.0155 | 3.7368 | 5.7451 | 4.6001 | 4.9095 | 8.2532 | 6.6052 | 7.0515 | 10.7383 | 8.5927 | 9.1743 | 13.0481 | 10.4405 | 11.1474
MK | 30053798 | 231 | Carmila | 231_Carmila 33 kV | Limiting Line Name | TR_LINE 211924_1 | TR_LINE 211924_1 | TR_LINE 211924_1 | TR_LINE 11490_1 | TR_LINE 11490_1 | TR_LINE 11490_1 | TR_LINE 11490_1 | TR_LINE 11490_1 | TR_LINE 11490_1 | TR_LINE 11490_1 | TR_LINE 11490_1 | TR_LINE 11490_1 | TR_LINE 11490_1 | TR_LINE 11490_1 | TR_LINE 11490_1
MK | 30053798 | 231 | Carmila | 231_Carmila 33 kV | Loading (A) | 11.005 | 8.2626 | 9.9772 | 3.7343 | 3.7261 | 3.7312 | 5.3646 | 5.3502 | 5.3592 | 6.9799 | 6.9601 | 6.9725 | 8.4812 | 8.4568 | 8.4721
MK | 30053798 | 231 | Carmila | 231_Carmila 33 kV | Loading (MVA) | 0.65783 | 0.49583 | 0.59727 | 0.22458 | 0.22483 | 0.22467 | 0.32377 | 0.32396 | 0.32384 | 0.42265 | 0.42282 | 0.42271 | 0.51506 | 0.51523 | 0.51512
MK | 30053798 | 231 | Carmila | 231_Carmila 33 kV | Loading (MW) | 0.54401 | 0.40791 | 0.4932 | 0.20697 | 0.20698 | 0.20697 | 0.31248 | 0.31251 | 0.31249 | 0.41478 | 0.41483 | 0.4148 | 0.50932 | 0.50938 | 0.50934
MK | 30053798 | 231 | Carmila | 231_Carmila 33 kV | Power Factor | 0.82698 | 0.82267 | 0.82575 | 0.92157 | 0.92061 | 0.92121 | 0.96513 | 0.96465 | 0.96495 | 0.98139 | 0.9811 | 0.98128 | 0.98884 | 0.98865 | 0.98877
MK | 30053798 | 231 | Carmila | 231_Carmila 33 kV | Rating (A) | 193 | 274 | 267 | 65 | 81 | 76 | 65 | 81 | 76 | 65 | 81 | 76 | 65 | 81 | 76
MK | 30053798 | 231 | Carmila | 231_Carmila 33 kV | Time | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30
MK | 30053798 | 231 | Carmila | 231_Carmila 33 kV | Voltage at Constrained Conductor | 34.5113 | 34.6467 | 34.5621 | 34.7214 | 34.8366 | 34.7646 | 34.8449 | 34.9593 | 34.8878 | 34.96 | 35.0736 | 35.0026 | 35.0621 | 35.1752 | 35.1045
MK | 30053799 | 232 | Newlands-Glenden | 232_Newlands-Glenden 66 kV | % of Rated A | 3.9773 | 2.8835 | 2.9575 | 2.78 | 2.0155 | 2.0671 | 2.2547 | 1.6347 | 1.6766 | 4.9794 | 3.6101 | 3.7026 | 8.0715 | 5.8518 | 6.0019
MK | 30053799 | 232 | Newlands-Glenden | 232_Newlands-Glenden 66 kV | Limiting Line Name | TR_LINE 10181_1 | TR_LINE 10181_1 | TR_LINE 10181_1 | TR_LINE 10181_1 | TR_LINE 10181_1 | TR_LINE 10181_1 | TR_LINE 10181_1 | TR_LINE 10181_1 | TR_LINE 10181_1 | TR_LINE 10181_1 | TR_LINE 10181_1 | TR_LINE 10181_1 | TR_LINE 10181_1 | TR_LINE 10181_1 | TR_LINE 10181_1
MK | 30053799 | 232 | Newlands-Glenden | 232_Newlands-Glenden 66 kV | Loading (A) | 4.6136 | 4.6136 | 4.6136 | 3.2247 | 3.2247 | 3.2247 | 2.6154 | 2.6154 | 2.6154 | 5.7761 | 5.7761 | 5.7761 | 9.3629 | 9.3629 | 9.3629
MK | 30053799 | 232 | Newlands-Glenden | 232_Newlands-Glenden 66 kV | Loading (MVA) | 0.54908 | 0.54908 | 0.54908 | 0.3838 | 0.3838 | 0.3838 | 0.31133 | 0.31133 | 0.31133 | 0.68771 | 0.68771 | 0.68771 | 1.115 | 1.115 | 1.115
MK | 30053799 | 232 | Newlands-Glenden | 232_Newlands-Glenden 66 kV | Loading (MW) | 0.46913 | 0.46913 | 0.46913 | 0.25447 | 0.25447 | 0.25447 | 0.11771 | 0.11771 | 0.11771 | 0.62626 | 0.62626 | 0.62626 | 1.0805 | 1.0805 | 1.0805
MK | 30053799 | 232 | Newlands-Glenden | 232_Newlands-Glenden 66 kV | Power Factor | 0.85439 | 0.85439 | 0.85439 | 0.66303 | 0.66303 | 0.66303 | 0.37808 | 0.37808 | 0.37808 | 0.91065 | 0.91065 | 0.91065 | 0.96903 | 0.96903 | 0.96903
MK | 30053799 | 232 | Newlands-Glenden | 232_Newlands-Glenden 66 kV | Rating (A) | 116 | 160 | 156 | 116 | 160 | 156 | 116 | 160 | 156 | 116 | 160 | 156 | 116 | 160 | 156
MK | 30053799 | 232 | Newlands-Glenden | 232_Newlands-Glenden 66 kV | Time | 16:30 | 21:00 | 4:00 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00
MK | 30053799 | 232 | Newlands-Glenden | 232_Newlands-Glenden 66 kV | Voltage at Constrained Conductor | 68.7116 | 68.7116 | 68.7116 | 68.7141 | 68.7141 | 68.7141 | 68.7253 | 68.7253 | 68.7253 | 68.7403 | 68.7403 | 68.7403 | 68.7555 | 68.7555 | 68.7555
MK | 30053850 | 340 | MK3-1 Farleigh | 340_MK3-1 Farleigh 33 kV | % of Rated A | 2.3046 | 1.733 | 1.7564 | 2.3136 | 1.7397 | 1.7632 | 2.321 | 1.7453 | 1.7689 | 2.3003 | 1.7297 | 1.753 | 2.3053 | 1.7334 | 1.7569
MK | 30053850 | 340 | MK3-1 Farleigh | 340_MK3-1 Farleigh 33 kV | Limiting Line Name | TR_LINE 11332_1 | TR_LINE 11330_1 | TR_LINE 11330_1 | TR_LINE 11332_1 | TR_LINE 11330_1 | TR_LINE 11330_1 | TR_LINE 11332_1 | TR_LINE 11330_1 | TR_LINE 11330_1 | TR_LINE 11332_1 | TR_LINE 11330_1 | TR_LINE 11330_1 | TR_LINE 11332_1 | TR_LINE 11330_1 | TR_LINE 11330_1
MK | 30053850 | 340 | MK3-1 Farleigh | 340_MK3-1 Farleigh 33 kV | Loading (A) | 3.964 | 3.8992 | 3.8992 | 3.9793 | 3.9143 | 3.9143 | 3.9922 | 3.9269 | 3.9269 | 3.9564 | 3.8918 | 3.8918 | 3.9651 | 3.9002 | 3.9002
MK | 30053850 | 340 | MK3-1 Farleigh | 340_MK3-1 Farleigh 33 kV | Loading (MVA) | 0.24115 | 0.23723 | 0.23723 | 0.24303 | 0.23907 | 0.23907 | 0.24459 | 0.24061 | 0.24062 | 0.24024 | 0.23633 | 0.23633 | 0.24129 | 0.23736 | 0.23736
MK | 30053850 | 340 | MK3-1 Farleigh | 340_MK3-1 Farleigh 33 kV | Loading (MW) | 0.0044308 | 0.0044095 | 0.0044095 | 0.0044653 | 0.0044439 | 0.0044439 | 0.0044941 | 0.0044725 | 0.0044725 | 0.004414 | 0.0043928 | 0.0043928 | 0.0044333 | 0.004412 | 0.004412
MK | 30053850 | 340 | MK3-1 Farleigh | 340_MK3-1 Farleigh 33 kV | Power Factor | 0.018374 | 0.018588 | 0.018588 | 0.018374 | 0.018588 | 0.018588 | 0.018374 | 0.018588 | 0.018588 | 0.018374 | 0.018588 | 0.018588 | 0.018374 | 0.018588 | 0.018588
MK | 30053850 | 340 | MK3-1 Farleigh | 340_MK3-1 Farleigh 33 kV | Rating (A) | 172 | 225 | 222 | 172 | 225 | 222 | 172 | 225 | 222 | 172 | 225 | 222 | 172 | 225 | 222
MK | 30053850 | 340 | MK3-1 Farleigh | 340_MK3-1 Farleigh 33 kV | Time | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30
MK | 30053850 | 340 | MK3-1 Farleigh | 340_MK3-1 Farleigh 33 kV | Voltage at Constrained Conductor | 35.1236 | 35.1263 | 35.1263 | 35.26 | 35.2627 | 35.2627 | 35.3735 | 35.3763 | 35.3763 | 35.057 | 35.0596 | 35.0597 | 35.1334 | 35.1361 | 35.1361
MK | 30053851 | 341 | TENNYSON ST 2 | 341_Tennyson St No 2 33 kV | % of Rated A | 22.8215 | 22.8215 | 22.8215 | 18.5838 | 18.5839 | 18.5839 | 15.4201 | 15.4201 | 15.4201 | 13.2949 | 13.2949 | 13.2949 | 12.1265 | 12.1265 | 12.1265
MK | 30053851 | 341 | TENNYSON ST 2 | 341_Tennyson St No 2 33 kV | Limiting Line Name | TR_CABLE 253_1 | TR_CABLE 253_1 | TR_CABLE 253_1 | TR_CABLE 253_1 | TR_CABLE 253_1 | TR_CABLE 253_1 | TR_CABLE 253_1 | TR_CABLE 253_1 | TR_CABLE 253_1 | TR_CABLE 253_1 | TR_CABLE 253_1 | TR_CABLE 253_1 | TR_CABLE 253_1 | TR_CABLE 253_1 | TR_CABLE 253_1
MK | 30053851 | 341 | TENNYSON ST 2 | 341_Tennyson St No 2 33 kV | Loading (A) | 79.8752 | 79.8752 | 79.8752 | 65.0435 | 65.0435 | 65.0435 | 53.9702 | 53.9702 | 53.9702 | 46.5322 | 46.5322 | 46.5322 | 42.4429 | 42.4428 | 42.4429
MK | 30053851 | 341 | TENNYSON ST 2 | 341_Tennyson St No 2 33 kV | Loading (MVA) | 4.7564 | 4.7564 | 4.7564 | 3.8799 | 3.8799 | 3.8799 | 3.2234 | 3.2234 | 3.2234 | 2.7478 | 2.7478 | 2.7478 | 2.5077 | 2.5077 | 2.5077
MK | 30053851 | 341 | TENNYSON ST 2 | 341_Tennyson St No 2 33 kV | Loading (MW) | 4.0895 | 4.0895 | 4.0895 | 3.0263 | 3.0263 | 3.0263 | 2.1321 | 2.1321 | 2.1321 | 1.4324 | 1.4324 | 1.4324 | 0.92421 | 0.92421 | 0.92421
MK | 30053851 | 341 | TENNYSON ST 2 | 341_Tennyson St No 2 33 kV | Power Factor | 0.85979 | 0.85979 | 0.85979 | 0.77999 | 0.77999 | 0.77999 | 0.66144 | 0.66144 | 0.66144 | 0.52129 | 0.52129 | 0.52129 | 0.36855 | 0.36855 | 0.36855
MK | 30053851 | 341 | TENNYSON ST 2 | 341_Tennyson St No 2 33 kV | Rating (A) | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350
MK | 30053851 | 341 | TENNYSON ST 2 | 341_Tennyson St No 2 33 kV | Time | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30
MK | 30053851 | 341 | TENNYSON ST 2 | 341_Tennyson St No 2 33 kV | Voltage at Constrained Conductor | 34.3798 | 34.3798 | 34.3798 | 34.4396 | 34.4396 | 34.4396 | 34.4831 | 34.483 | 34.4831 | 34.0929 | 34.0929 | 34.0929 | 34.1121 | 34.112 | 34.1121
MK | 30053852 | 342 | SOUTH MACKAY | 342_South Mackay 33 kV | % of Rated A | 56.1859 | 38.7568 | 38.6779 | 55.0633 | 37.9824 | 37.9051 | 56.2506 | 38.8014 | 38.7224 | 57.9089 | 39.9453 | 39.864 | 60.4535 | 41.7005 | 41.6156
MK | 30053852 | 342 | SOUTH MACKAY | 342_South Mackay 33 kV | Limiting Line Name | TR_LINE 12122806_1 | TR_LINE 12122806_1 | TR_LINE 12122806_1 | TR_LINE 12122806_1 | TR_LINE 12122806_1 | TR_LINE 12122806_1 | TR_LINE 12122806_1 | TR_LINE 12122806_1 | TR_LINE 12122806_1 | TR_LINE 12122806_1 | TR_LINE 12122806_1 | TR_LINE 12122806_1 | TR_LINE 12122806_1 | TR_LINE 12122806_1 | TR_LINE 12122806_1
MK | 30053852 | 342 | SOUTH MACKAY | 342_South Mackay 33 kV | Loading (A) | 189.9028 | 189.9028 | 189.9028 | 186.108 | 186.108 | 186.108 | 190.1211 | 190.121 | 190.1211 | 195.7267 | 195.7266 | 195.7267 | 204.3276 | 204.3275 | 204.3275
MK | 30053852 | 342 | SOUTH MACKAY | 342_South Mackay 33 kV | Loading (MVA) | 11.3112 | 11.3112 | 11.3112 | 11.1048 | 11.1048 | 11.1048 | 11.3588 | 11.3588 | 11.3588 | 11.5616 | 11.5616 | 11.5616 | 12.0766 | 12.0766 | 12.0766
MK | 30053852 | 342 | SOUTH MACKAY | 342_South Mackay 33 kV | Loading (MW) | 2.639 | 2.639 | 2.639 | 0.090907 | 0.090907 | 0.090907 | 2.2107 | 2.2107 | 2.2107 | 3.9406 | 3.9406 | 3.9406 | 5.3088 | 5.3088 | 5.3088
MK | 30053852 | 342 | SOUTH MACKAY | 342_South Mackay 33 kV | Power Factor | 0.23331 | 0.23331 | 0.23331 | 0.0081863 | 0.0081863 | 0.0081863 | 0.19462 | 0.19462 | 0.19462 | 0.34083 | 0.34083 | 0.34083 | 0.43959 | 0.43959 | 0.43959
MK | 30053852 | 342 | SOUTH MACKAY | 342_South Mackay 33 kV | Rating (A) | 338 | 490 | 491 | 338 | 490 | 491 | 338 | 490 | 491 | 338 | 490 | 491 | 338 | 490 | 491
MK | 30053852 | 342 | SOUTH MACKAY | 342_South Mackay 33 kV | Time | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30
MK | 30053852 | 342 | SOUTH MACKAY | 342_South Mackay 33 kV | Voltage at Constrained Conductor | 34.3888 | 34.3888 | 34.3888 | 34.4497 | 34.4497 | 34.4497 | 34.4939 | 34.4939 | 34.4939 | 34.1043 | 34.1042 | 34.1043 | 34.1239 | 34.1238 | 34.1238
MK | 30053853 | 343 | PLEYSTOWE | 343_Pleystowe 33 kV | % of Rated A | 13.6865 | 13.6828 | 13.6828 | 16.2623 | 16.2591 | 16.2591 | 18.8299 | 18.8272 | 18.8273 | 21.5464 | 21.5441 | 21.5441 | 23.8446 | 23.8426 | 23.8426
MK | 30053853 | 343 | PLEYSTOWE | 343_Pleystowe 33 kV | Limiting Line Name | TR_LINE 114413_2 | TR_CABLE 18_1 | TR_CABLE 18_1 | TR_LINE 114413_2 | TR_CABLE 18_1 | TR_CABLE 18_1 | TR_LINE 114413_2 | TR_CABLE 18_1 | TR_CABLE 18_1 | TR_LINE 114413_2 | TR_CABLE 18_1 | TR_CABLE 18_1 | TR_LINE 114413_2 | TR_CABLE 18_1 | TR_CABLE 18_1
MK | 30053853 | 343 | PLEYSTOWE | 343_Pleystowe 33 kV | Loading (A) | 30.1104 | 30.1021 | 30.1021 | 35.777 | 35.7701 | 35.7701 | 41.4232 | 41.4199 | 41.42 | 47.3998 | 47.3971 | 47.3971 | 52.4561 | 52.4537 | 52.4537
MK | 30053853 | 343 | PLEYSTOWE | 343_Pleystowe 33 kV | Loading (MVA) | 1.793 | 1.7928 | 1.7928 | 2.1341 | 2.1341 | 2.1341 | 2.4743 | 2.4743 | 2.4743 | 2.7992 | 2.7994 | 2.7994 | 3.0996 | 3.0998 | 3.0998
MK | 30053853 | 343 | PLEYSTOWE | 343_Pleystowe 33 kV | Loading (MW) | 1.3962 | 1.3964 | 1.3964 | 1.8222 | 1.8224 | 1.8224 | 2.2192 | 2.2194 | 2.2194 | 2.5885 | 2.5887 | 2.5887 | 2.9178 | 2.9181 | 2.9181
MK | 30053853 | 343 | PLEYSTOWE | 343_Pleystowe 33 kV | Power Factor | 0.77871 | 0.7789 | 0.7789 | 0.85382 | 0.85395 | 0.85395 | 0.89692 | 0.89697 | 0.89697 | 0.92473 | 0.92476 | 0.92476 | 0.94136 | 0.94138 | 0.94138
MK | 30053853 | 343 | PLEYSTOWE | 343_Pleystowe 33 kV | Rating (A) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
MK | 30053853 | 343 | PLEYSTOWE | 343_Pleystowe 33 kV | Time | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00
MK | 30053853 | 343 | PLEYSTOWE | 343_Pleystowe 33 kV | Voltage at Constrained Conductor | 34.3798 | 34.3845 | 34.3845 | 34.4396 | 34.4449 | 34.4449 | 34.4858 | 34.4889 | 34.4889 | 34.096 | 34.0994 | 34.0994 | 34.1153 | 34.119 | 34.119
MK | 30053854 | 344 | WEST MACKAY 2 | 344_West Mackay 2 33 kV | % of Rated A | 6.9687 | 6.9687 | 6.9687 | 5.7476 | 5.7476 | 5.7476 | 4.6005 | 4.6005 | 4.6005 | 3.5129 | 3.5129 | 3.5129 | 2.4437 | 2.4437 | 2.4437
MK | 30053854 | 344 | WEST MACKAY 2 | 344_West Mackay 2 33 kV | Limiting Line Name | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1
MK | 30053854 | 344 | WEST MACKAY 2 | 344_West Mackay 2 33 kV | Loading (A) | 43.5545 | 43.5545 | 43.5545 | 35.9222 | 35.9223 | 35.9223 | 28.7531 | 28.7531 | 28.7531 | 21.9554 | 21.9555 | 21.9555 | 15.2731 | 15.2731 | 15.2731
MK | 30053854 | 344 | WEST MACKAY 2 | 344_West Mackay 2 33 kV | Loading (MVA) | 2.5936 | 2.5936 | 2.5936 | 2.1428 | 2.1428 | 2.1428 | 1.7173 | 1.7173 | 1.7173 | 1.2965 | 1.2965 | 1.2965 | 0.90239 | 0.90239 | 0.90239
MK | 30053854 | 344 | WEST MACKAY 2 | 344_West Mackay 2 33 kV | Loading (MW) | 2.5936 | 2.5936 | 2.5936 | 2.1428 | 2.1428 | 2.1428 | 1.7171 | 1.7171 | 1.7171 | 1.2961 | 1.2961 | 1.2961 | 0.90163 | 0.90163 | 0.90163
MK | 30053854 | 344 | WEST MACKAY 2 | 344_West Mackay 2 33 kV | Power Factor | 1 | 1 | 1 | 0.99998 | 0.99998 | 0.99998 | 0.9999 | 0.9999 | 0.9999 | 0.99971 | 0.99971 | 0.99971 | 0.99916 | 0.99916 | 0.99916
MK | 30053854 | 344 | WEST MACKAY 2 | 344_West Mackay 2 33 kV | Rating (A) | 625 | 625 | 625 | 625 | 625 | 625 | 625 | 625 | 625 | 625 | 625 | 625 | 625 | 625 | 625
MK | 30053854 | 344 | WEST MACKAY 2 | 344_West Mackay 2 33 kV | Time | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00
MK | 30053854 | 344 | WEST MACKAY 2 | 344_West Mackay 2 33 kV | Voltage at Constrained Conductor | 34.3798 | 34.3798 | 34.3798 | 34.4396 | 34.4396 | 34.4396 | 34.483 | 34.483 | 34.483 | 34.0929 | 34.0929 | 34.0929 | 34.112 | 34.112 | 34.112
MK | 30053855 | 3053 | MT BASSETT | 3053_Mt Bassett 33 kV | % of Rated A | 5.8207 | 4.2088 | 4.2349 | 3.8014 | 2.7487 | 2.7657 | 2.2552 | 1.6307 | 1.6408 | 1.1531 | 0.94176 | 0.94176 | 0.78495 | 0.78495 | 0.78495
MK | 30053855 | 3053 | MT BASSETT | 3053_Mt Bassett 33 kV | Limiting Line Name | TR_LINE 11627_1 | TR_LINE 11627_1 | TR_LINE 11627_1 | TR_LINE 11627_1 | TR_LINE 11627_1 | TR_LINE 11627_1 | TR_LINE 11627_1 | TR_LINE 11627_1 | TR_LINE 11627_1 | TR_LINE 11627_1 | TR_CABLE 318_1 | TR_CABLE 318_1 | TR_CABLE 318_1 | TR_CABLE 318_1 | TR_CABLE 318_1
MK | 30053855 | 3053 | MT BASSETT | 3053_Mt Bassett 33 kV | Loading (A) | 13.6787 | 13.6787 | 13.6787 | 8.9333 | 8.9333 | 8.9333 | 5.2998 | 5.2998 | 5.2998 | 2.7097 | 3.6634 | 3.6634 | 3.0535 | 3.0534 | 3.0534
MK | 30053855 | 3053 | MT BASSETT | 3053_Mt Bassett 33 kV | Loading (MVA) | 0.81402 | 0.81402 | 0.81402 | 0.53272 | 0.53272 | 0.53272 | 0.31652 | 0.31652 | 0.31652 | 0.16003 | 0.21635 | 0.21635 | 0.18043 | 0.18043 | 0.18043
MK | 30053855 | 3053 | MT BASSETT | 3053_Mt Bassett 33 kV | Loading (MW) | 0.8137 | 0.8137 | 0.8137 | 0.53022 | 0.53022 | 0.53022 | 0.30786 | 0.30786 | 0.30786 | 0.1343 | 0.13565 | 0.13565 | 0.014033 | 0.014033 | 0.014033
MK | 30053855 | 3053 | MT BASSETT | 3053_Mt Bassett 33 kV | Power Factor | 0.99961 | 0.99961 | 0.99961 | 0.9953 | 0.9953 | 0.9953 | 0.97263 | 0.97263 | 0.97263 | 0.83918 | 0.62701 | 0.62701 | 0.077773 | 0.077773 | 0.077773
MK | 30053855 | 3053 | MT BASSETT | 3053_Mt Bassett 33 kV | Rating (A) | 235 | 325 | 323 | 235 | 325 | 323 | 235 | 325 | 323 | 235 | 389 | 389 | 389 | 389 | 389
MK | 30053855 | 3053 | MT BASSETT | 3053_Mt Bassett 33 kV | Time | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30
MK | 30053855 | 3053 | MT BASSETT | 3053_Mt Bassett 33 kV | Voltage at Constrained Conductor | 34.3583 | 34.3583 | 34.3583 | 34.4293 | 34.4292 | 34.4292 | 34.4814 | 34.4814 | 34.4813 | 34.0978 | 34.0958 | 34.0958 | 34.1164 | 34.1164 | 34.1164
MK | 30053856 | 346 | RITCHIES RD | 346_Ritchies Rd 33 kV | % of Rated A | 10.1699 | 7.3598 | 7.3841 | 12.1006 | 8.757 | 8.7859 | 14.0229 | 10.1482 | 10.1817 | 16.0553 | 11.619 | 11.6573 | 17.7737 | 12.8626 | 12.905
MK | 30053856 | 346 | RITCHIES RD | 346_Ritchies Rd 33 kV | Limiting Line Name | TR_LINE 11501_1 | TR_LINE 11501_1 | TR_LINE 11501_1 | TR_LINE 11501_1 | TR_LINE 11501_1 | TR_LINE 11501_1 | TR_LINE 11501_1 | TR_LINE 11501_1 | TR_LINE 11501_1 | TR_LINE 11501_1 | TR_LINE 11501_1 | TR_LINE 11501_1 | TR_LINE 11501_1 | TR_LINE 11501_1 | TR_LINE 11501_1
MK | 30053856 | 346 | RITCHIES RD | 346_Ritchies Rd 33 kV | Loading (A) | 22.3738 | 22.3738 | 22.3738 | 26.6213 | 26.6213 | 26.6213 | 30.8504 | 30.8505 | 30.8505 | 35.319 | 35.319 | 35.319 | 39.0998 | 39.0999 | 39.0999
MK | 30053856 | 346 | RITCHIES RD | 346_Ritchies Rd 33 kV | Loading (MVA) | 1.3323 | 1.3323 | 1.3323 | 1.588 | 1.588 | 1.588 | 1.8426 | 1.8426 | 1.8426 | 2.0858 | 2.0858 | 2.0858 | 2.3104 | 2.3104 | 2.3104
MK | 30053856 | 346 | RITCHIES RD | 346_Ritchies Rd 33 kV | Loading (MW) | 1.0445 | 1.0445 | 1.0445 | 1.3623 | 1.3623 | 1.3623 | 1.6585 | 1.6585 | 1.6585 | 1.9342 | 1.9342 | 1.9342 | 2.1799 | 2.1799 | 2.1799
MK | 30053856 | 346 | RITCHIES RD | 346_Ritchies Rd 33 kV | Power Factor | 0.78397 | 0.78397 | 0.78397 | 0.85791 | 0.85791 | 0.85791 | 0.9001 | 0.9001 | 0.9001 | 0.92731 | 0.92731 | 0.92731 | 0.94352 | 0.94352 | 0.94352
MK | 30053856 | 346 | RITCHIES RD | 346_Ritchies Rd 33 kV | Rating (A) | 220 | 304 | 303 | 220 | 304 | 303 | 220 | 304 | 303 | 220 | 304 | 303 | 220 | 304 | 303
MK | 30053856 | 346 | RITCHIES RD | 346_Ritchies Rd 33 kV | Time | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00
MK | 30053856 | 346 | RITCHIES RD | 346_Ritchies Rd 33 kV | Voltage at Constrained Conductor | 34.3798 | 34.3798 | 34.3798 | 34.4396 | 34.4396 | 34.4396 | 34.483 | 34.483 | 34.483 | 34.0957 | 34.0957 | 34.0957 | 34.115 | 34.115 | 34.115
MK | 30053857 | 347 | MT BASSETT | 347_Mt Bassett 33 kV | % of Rated A | 5.4457 | 5.4457 | 5.4457 | 2.8893 | 2.8893 | 2.8893 | 1.085 | 1.085 | 1.085 | 0.91511 | 0.91511 | 0.91511 | 1.8161 | 1.8161 | 1.8161
MK | 30053857 | 347 | MT BASSETT | 347_Mt Bassett 33 kV | Limiting Line Name | TR_CABLE 22_1 | TR_CABLE 22_1 | TR_CABLE 22_1 | TR_CABLE 22_1 | TR_CABLE 22_1 | TR_CABLE 22_1 | TR_CABLE 22_1 | TR_CABLE 22_1 | TR_CABLE 22_1 | TR_CABLE 22_1 | TR_CABLE 22_1 | TR_CABLE 22_1 | TR_CABLE 4883_1 | TR_CABLE 4883_1 | TR_CABLE 4883_1
MK | 30053857 | 347 | MT BASSETT | 347_Mt Bassett 33 kV | Loading (A) | 13.8866 | 13.8866 | 13.8866 | 7.3678 | 7.3678 | 7.3678 | 2.7668 | 2.7668 | 2.7668 | 2.3335 | 2.3335 | 2.3335 | 4.631 | 4.631 | 4.631
MK | 30053857 | 347 | MT BASSETT | 347_Mt Bassett 33 kV | Loading (MVA) | 0.82655 | 0.82655 | 0.82655 | 0.4394 | 0.4394 | 0.4394 | 0.16524 | 0.16524 | 0.16524 | 0.13781 | 0.13781 | 0.13781 | 0.27369 | 0.27369 | 0.27369
MK | 30053857 | 347 | MT BASSETT | 347_Mt Bassett 33 kV | Loading (MW) | 0.81343 | 0.81343 | 0.81343 | 0.42074 | 0.42074 | 0.42074 | 0.12464 | 0.12464 | 0.12464 | 0.10281 | 0.10281 | 0.10281 | 0.26369 | 0.26369 | 0.26369
MK | 30053857 | 347 | MT BASSETT | 347_Mt Bassett 33 kV | Power Factor | 0.98413 | 0.98413 | 0.98413 | 0.95754 | 0.95754 | 0.95754 | 0.75428 | 0.75428 | 0.75428 | 0.74601 | 0.74601 | 0.74601 | 0.96347 | 0.96347 | 0.96347
MK | 30053857 | 347 | MT BASSETT | 347_Mt Bassett 33 kV | Rating (A) | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255
MK | 30053857 | 347 | MT BASSETT | 347_Mt Bassett 33 kV | Time | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00
MK | 30053857 | 347 | MT BASSETT | 347_Mt Bassett 33 kV | Voltage at Constrained Conductor | 34.3645 | 34.3645 | 34.3645 | 34.4321 | 34.4321 | 34.4321 | 34.4821 | 34.4821 | 34.482 | 34.0967 | 34.0967 | 34.0967 | 34.1209 | 34.1208 | 34.1208
MK | 30053858 | 348 | Farleigh | 348_Farleigh 33 kV | % of Rated A | 19.3003 | 14.401 | 14.5127 | 20.5697 | 15.3481 | 15.4671 | 21.8104 | 16.2739 | 16.4001 | 23.2313 | 17.3341 | 17.4685 | 24.3348 | 18.1575 | 18.2983
MK | 30053858 | 348 | Farleigh | 348_Farleigh 33 kV | Limiting Line Name | TR_LINE 13162_1 | TR_LINE 13162_1 | TR_LINE 13162_1 | TR_LINE 13162_1 | TR_LINE 13162_1 | TR_LINE 13162_1 | TR_LINE 13162_1 | TR_LINE 13162_1 | TR_LINE 13162_1 | TR_LINE 13162_1 | TR_LINE 13162_1 | TR_LINE 13162_1 | TR_LINE 13162_1 | TR_LINE 13162_1 | TR_LINE 13162_1
MK | 30053858 | 348 | Farleigh | 348_Farleigh 33 kV | Loading (A) | 37.4427 | 37.4427 | 37.4427 | 39.9051 | 39.9052 | 39.9052 | 42.3067 | 42.3067 | 42.3067 | 45.0635 | 45.0635 | 45.0636 | 47.2046 | 47.2047 | 47.2047
MK | 30053858 | 348 | Farleigh | 348_Farleigh 33 kV | Loading (MVA) | 2.256 | 2.256 | 2.256 | 2.4123 | 2.4123 | 2.4123 | 2.5646 | 2.5646 | 2.5646 | 2.7053 | 2.7053 | 2.7053 | 2.8388 | 2.8388 | 2.8388
MK | 30053858 | 348 | Farleigh | 348_Farleigh 33 kV | Loading (MW) | 1.4711 | 1.4711 | 1.4711 | 1.7098 | 1.7098 | 1.7098 | 1.9275 | 1.9275 | 1.9275 | 2.1261 | 2.1261 | 2.1261 | 2.3009 | 2.3009 | 2.3009
MK | 30053858 | 348 | Farleigh | 348_Farleigh 33 kV | Power Factor | 0.65208 | 0.65208 | 0.65208 | 0.70881 | 0.70881 | 0.70881 | 0.75157 | 0.75157 | 0.75157 | 0.7859 | 0.7859 | 0.7859 | 0.81052 | 0.81052 | 0.81052
MK | 30053858 | 348 | Farleigh | 348_Farleigh 33 kV | Rating (A) | 194 | 260 | 258 | 194 | 260 | 258 | 194 | 260 | 258 | 194 | 260 | 258 | 194 | 260 | 258
MK | 30053858 | 348 | Farleigh | 348_Farleigh 33 kV | Time | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00
MK | 30053858 | 348 | Farleigh | 348_Farleigh 33 kV | Voltage at Constrained Conductor | 34.7873 | 34.7872 | 34.7872 | 34.9008 | 34.9008 | 34.9008 | 34.9992 | 34.9992 | 34.9991 | 34.6603 | 34.6603 | 34.6603 | 34.7205 | 34.7204 | 34.7204
MK | 30053859 | 349 | Pioneer Valley-Pinnacle(Marian) | 349_Pioneer Valley - Pinnacle 66 kV | % of Rated A | 7.5011 | 5.3041 | 5.4407 | 8.2954 | 6.0032 | 6.0231 | 10.5249 | 7.6167 | 7.6418 | 12.823 | 9.2798 | 9.3104 | 14.8827 | 10.7704 | 10.806
MK | 30053859 | 349 | Pioneer Valley-Pinnacle(Marian) | 349_Pioneer Valley - Pinnacle 66 kV | Limiting Line Name | TR_LINE 10204_1 | TR_LINE 10204_1 | TR_LINE 10204_1 | TR_LINE 9735_1 | TR_LINE 9735_1 | TR_LINE 9735_1 | TR_LINE 9735_1 | TR_LINE 9735_1 | TR_LINE 9735_1 | TR_LINE 9735_1 | TR_LINE 9735_1 | TR_LINE 9735_1 | TR_LINE 9735_1 | TR_LINE 9735_1 | TR_LINE 9735_1
MK | 30053859 | 349 | Pioneer Valley-Pinnacle(Marian) | 349_Pioneer Valley - Pinnacle 66 kV | Loading (A) | 12.6769 | 12.6769 | 12.6769 | 18.2499 | 18.2499 | 18.2499 | 23.1547 | 23.1547 | 23.1547 | 28.2105 | 28.2105 | 28.2105 | 32.742 | 32.742 | 32.742
MK | 30053859 | 349 | Pioneer Valley-Pinnacle(Marian) | 349_Pioneer Valley - Pinnacle 66 kV | Loading (MVA) | 1.5309 | 1.5309 | 1.5309 | 2.2024 | 2.2024 | 2.2024 | 2.7959 | 2.7959 | 2.7959 | 3.4066 | 3.4066 | 3.4066 | 3.9534 | 3.9534 | 3.9534
MK | 30053859 | 349 | Pioneer Valley-Pinnacle(Marian) | 349_Pioneer Valley - Pinnacle 66 kV | Loading (MW) | 0.43501 | 0.43501 | 0.43501 | 1.4633 | 1.4633 | 1.4633 | 2.2723 | 2.2723 | 2.2723 | 3.0042 | 3.0042 | 3.0042 | 3.6234 | 3.6234 | 3.6234
MK | 30053859 | 349 | Pioneer Valley-Pinnacle(Marian) | 349_Pioneer Valley - Pinnacle 66 kV | Power Factor | 0.28415 | 0.28415 | 0.28415 | 0.66441 | 0.66441 | 0.66441 | 0.81272 | 0.81273 | 0.81273 | 0.88189 | 0.88189 | 0.88189 | 0.91651 | 0.91651 | 0.91651
MK | 30053859 | 349 | Pioneer Valley-Pinnacle(Marian) | 349_Pioneer Valley - Pinnacle 66 kV | Rating (A) | 169 | 239 | 233 | 220 | 304 | 303 | 220 | 304 | 303 | 220 | 304 | 303 | 220 | 304 | 303
MK | 30053859 | 349 | Pioneer Valley-Pinnacle(Marian) | 349_Pioneer Valley - Pinnacle 66 kV | Time | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00
MK | 30053859 | 349 | Pioneer Valley-Pinnacle(Marian) | 349_Pioneer Valley - Pinnacle 66 kV | Voltage at Constrained Conductor | 69.7234 | 69.7234 | 69.7234 | 69.6756 | 69.6756 | 69.6756 | 69.7137 | 69.7137 | 69.7137 | 69.7178 | 69.7178 | 69.7177 | 69.7124 | 69.7123 | 69.7123
MK | 30053869 | 360 | Pinnacle-Crediton/Eungella Dam | 360_Pinnacle-Crediton/Eungella Dam 66 kV | % of Rated A | 9.7497 | 7.5376 | 7.9378 | 9.5129 | 7.3545 | 7.745 | 9.3039 | 7.1929 | 7.5749 | 9.1296 | 7.0582 | 7.433 | 8.9978 | 6.9562 | 7.3256
MK | 30053869 | 360 | Pinnacle-Crediton/Eungella Dam | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Limiting Line Name | TR_LINE 10229_1 | TR_LINE 10229_1 | TR_LINE 10229_1 | TR_LINE 10229_1 | TR_LINE 10229_1 | TR_LINE 10229_1 | TR_LINE 10229_1 | TR_LINE 10229_1 | TR_LINE 10229_1 | TR_LINE 10229_1 | TR_LINE 10229_1 | TR_LINE 10229_1 | TR_LINE 10229_1 | TR_LINE 10229_1 | TR_LINE 10229_1
MK | 30053869 | 360 | Pinnacle-Crediton/Eungella Dam | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Loading (A) | 8.9697 | 8.9697 | 8.9697 | 8.7519 | 8.7519 | 8.7519 | 8.5596 | 8.5596 | 8.5596 | 8.3993 | 8.3993 | 8.3993 | 8.2779 | 8.2779 | 8.2779
MK | 30053869 | 360 | Pinnacle-Crediton/Eungella Dam | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Loading (MVA) | 1.0853 | 1.0853 | 1.0853 | 1.0609 | 1.0609 | 1.0609 | 1.039 | 1.039 | 1.039 | 1.0203 | 1.0203 | 1.0203 | 1.0061 | 1.0061 | 1.0061
MK | 30053869 | 360 | Pinnacle-Crediton/Eungella Dam | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Loading (MW) | 0.90543 | 0.90543 | 0.90543 | 0.87424 | 0.87424 | 0.87424 | 0.84624 | 0.84624 | 0.84624 | 0.82251 | 0.82251 | 0.82251 | 0.80438 | 0.80438 | 0.80438
MK | 30053869 | 360 | Pinnacle-Crediton/Eungella Dam | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Power Factor | 0.83425 | 0.83425 | 0.83425 | 0.82409 | 0.82409 | 0.82409 | 0.81451 | 0.81451 | 0.81451 | 0.80615 | 0.80615 | 0.80615 | 0.79952 | 0.79952 | 0.79952
MK | 30053869 | 360 | Pinnacle-Crediton/Eungella Dam | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Rating (A) | 92 | 119 | 113 | 92 | 119 | 113 | 92 | 119 | 113 | 92 | 119 | 113 | 92 | 119 | 113
MK | 30053869 | 360 | Pinnacle-Crediton/Eungella Dam | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Time | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00
MK | 30053869 | 360 | Pinnacle-Crediton/Eungella Dam | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Voltage at Constrained Conductor | 69.8582 | 69.8582 | 69.8582 | 69.983 | 69.983 | 69.983 | 70.0784 | 70.0783 | 70.0783 | 70.1332 | 70.1331 | 70.1331 | 70.1695 | 70.1695 | 70.1694
MK | 30053873 | 364 | WEST MACKAY 1 | 364_West Mackay No 1 33 kV | % of Rated A | 15.0168 | 10.5958 | 10.6216 | 12.3835 | 8.7378 | 8.7591 | 9.9099 | 6.9924 | 7.0094 | 7.5642 | 5.3373 | 5.3503 | 5.2574 | 3.7096 | 3.7186
MK | 30053873 | 364 | WEST MACKAY 1 | 364_West Mackay No 1 33 kV | Limiting Line Name | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1
MK | 30053873 | 364 | WEST MACKAY 1 | 364_West Mackay No 1 33 kV | Loading (A) | 43.5487 | 43.5487 | 43.5487 | 35.9121 | 35.9121 | 35.9121 | 28.7387 | 28.7387 | 28.7387 | 21.9361 | 21.9361 | 21.9361 | 15.2464 | 15.2464 | 15.2464
MK | 30053873 | 364 | WEST MACKAY 1 | 364_West Mackay No 1 33 kV | Loading (MVA) | 2.593 | 2.593 | 2.593 | 2.142 | 2.142 | 2.142 | 1.7163 | 1.7163 | 1.7163 | 1.2953 | 1.2953 | 1.2953 | 0.90078 | 0.90078 | 0.90078
MK | 30053873 | 364 | WEST MACKAY 1 | 364_West Mackay No 1 33 kV | Loading (MW) | 2.5926 | 2.5926 | 2.5926 | 2.1418 | 2.1418 | 2.1418 | 1.7162 | 1.7162 | 1.7162 | 1.2952 | 1.2952 | 1.2952 | 0.90077 | 0.90077 | 0.90077
MK | 30053873 | 364 | WEST MACKAY 1 | 364_West Mackay No 1 33 kV | Power Factor | 0.99986 | 0.99986 | 0.99986 | 0.99991 | 0.99991 | 0.99991 | 0.99994 | 0.99994 | 0.99994 | 0.99996 | 0.99996 | 0.99996 | 0.99998 | 0.99998 | 0.99998
MK | 30053873 | 364 | WEST MACKAY 1 | 364_West Mackay No 1 33 kV | Rating (A) | 290 | 411 | 410 | 290 | 411 | 410 | 290 | 411 | 410 | 290 | 411 | 410 | 290 | 411 | 410
MK | 30053873 | 364 | WEST MACKAY 1 | 364_West Mackay No 1 33 kV | Time | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00
MK | 30053873 | 364 | WEST MACKAY 1 | 364_West Mackay No 1 33 kV | Voltage at Constrained Conductor | 34.3765 | 34.3765 | 34.3765 | 34.4369 | 34.4369 | 34.4369 | 34.4809 | 34.4809 | 34.4809 | 34.0913 | 34.0913 | 34.0912 | 34.1109 | 34.1109 | 34.1109
MK | 30053874 | 365 | MACKAY CITY 1 | 365_Tennyson St No 1 33 kV | % of Rated A | 2.9082 | 2.9082 | 2.9082 | 2.3455 | 2.3455 | 2.3455 | 1.9263 | 1.9263 | 1.9263 | 1.6485 | 1.6485 | 1.6485 | 1.4988 | 1.4988 | 1.4988
MK | 30053874 | 365 | MACKAY CITY 1 | 365_Tennyson St No 1 33 kV | Limiting Line Name | TR_CABLE 7286_1 | TR_CABLE 7286_1 | TR_CABLE 7286_1 | TR_CABLE 7286_1 | TR_CABLE 7286_1 | TR_CABLE 7286_1 | TR_CABLE 7286_1 | TR_CABLE 7286_1 | TR_CABLE 7286_1 | TR_CABLE 7286_1 | TR_CABLE 7286_1 | TR_CABLE 7286_1 | TR_CABLE 7286_1 | TR_CABLE 7286_1 | TR_CABLE 7286_1
MK | 30053874 | 365 | MACKAY CITY 1 | 365_Tennyson St No 1 33 kV | Loading (A) | 19.3398 | 19.3398 | 19.3398 | 15.5979 | 15.5979 | 15.5979 | 12.8098 | 12.8098 | 12.8098 | 10.9625 | 10.9625 | 10.9625 | 9.9668 | 9.9668 | 9.9668
MK | 30053874 | 365 | MACKAY CITY 1 | 365_Tennyson St No 1 33 kV | Loading (MVA) | 1.1516 | 1.1516 | 1.1516 | 0.93043 | 0.93043 | 0.93043 | 0.76508 | 0.76508 | 0.76508 | 0.64734 | 0.64734 | 0.64734 | 0.58888 | 0.58888 | 0.58888
MK | 30053874 | 365 | MACKAY CITY 1 | 365_Tennyson St No 1 33 kV | Loading (MW) | 1.151 | 1.151 | 1.151 | 0.91601 | 0.91601 | 0.91601 | 0.71724 | 0.71724 | 0.71724 | 0.55502 | 0.55502 | 0.55502 | 0.44115 | 0.44115 | 0.44115
MK | 30053874 | 365 | MACKAY CITY 1 | 365_Tennyson St No 1 33 kV | Power Factor | 0.99946 | 0.99946 | 0.99946 | 0.9845 | 0.9845 | 0.9845 | 0.93746 | 0.93746 | 0.93746 | 0.85738 | 0.85738 | 0.85738 | 0.74913 | 0.74913 | 0.74913
MK | 30053874 | 365 | MACKAY CITY 1 | 365_Tennyson St No 1 33 kV | Rating (A) | 665 | 665 | 665 | 665 | 665 | 665 | 665 | 665 | 665 | 665 | 665 | 665 | 665 | 665 | 665
MK | 30053874 | 365 | MACKAY CITY 1 | 365_Tennyson St No 1 33 kV | Time | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30
MK | 30053874 | 365 | MACKAY CITY 1 | 365_Tennyson St No 1 33 kV | Voltage at Constrained Conductor | 34.3798 | 34.3798 | 34.3798 | 34.4396 | 34.4396 | 34.4396 | 34.4831 | 34.483 | 34.4831 | 34.0929 | 34.0929 | 34.0929 | 34.1121 | 34.112 | 34.1121
MK | 30053876 | 367 | Pioneer Valley-Greenmount | 367_Pioneer Valley - Greenmount 66 kV | % of Rated A | 0.064875 | 0.046844 | 0.046979 | 0.064933 | 0.046886 | 0.04702 | 0.064968 | 0.046911 | 0.047046 | 0.064972 | 0.046914 | 0.047049 | 0.064967 | 0.04691 | 0.047045
MK | 30053876 | 367 | Pioneer Valley-Greenmount | 367_Pioneer Valley - Greenmount 66 kV | Limiting Line Name | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1
MK | 30053876 | 367 | Pioneer Valley-Greenmount | 367_Pioneer Valley - Greenmount 66 kV | Loading (A) | 0.16349 | 0.16349 | 0.16349 | 0.16363 | 0.16363 | 0.16363 | 0.16372 | 0.16372 | 0.16372 | 0.16373 | 0.16373 | 0.16373 | 0.16372 | 0.16372 | 0.16372
MK | 30053876 | 367 | Pioneer Valley-Greenmount | 367_Pioneer Valley - Greenmount 66 kV | Loading (MVA) | 0.019712 | 0.019712 | 0.019712 | 0.019747 | 0.019747 | 0.019747 | 0.019769 | 0.019769 | 0.019769 | 0.019771 | 0.019771 | 0.019771 | 0.019768 | 0.019768 | 0.019768
MK | 30053876 | 367 | Pioneer Valley-Greenmount | 367_Pioneer Valley - Greenmount 66 kV | Loading (MW) | 8.0229e-08 | 8.0243e-08 | 8.0274e-08 | 8.0345e-08 | 8.043e-08 | 8.0424e-08 | 8.0503e-08 | 8.0459e-08 | 8.0446e-08 | 8.0455e-08 | 8.0487e-08 | 8.0489e-08 | 8.0452e-08 | 8.0471e-08 | 8.0451e-08
MK | 30053876 | 367 | Pioneer Valley-Greenmount | 367_Pioneer Valley - Greenmount 66 kV | Power Factor | 4.07e-06 | 4.0707e-06 | 4.0723e-06 | 4.0687e-06 | 4.073e-06 | 4.0727e-06 | 4.0722e-06 | 4.0701e-06 | 4.0694e-06 | 4.0694e-06 | 4.071e-06 | 4.0711e-06 | 4.0699e-06 | 4.0708e-06 | 4.0698e-06
MK | 30053876 | 367 | Pioneer Valley-Greenmount | 367_Pioneer Valley - Greenmount 66 kV | Rating (A) | 252 | 349 | 348 | 252 | 349 | 348 | 252 | 349 | 348 | 252 | 349 | 348 | 252 | 349 | 348
MK | 30053876 | 367 | Pioneer Valley-Greenmount | 367_Pioneer Valley - Greenmount 66 kV | Time | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30
MK | 30053876 | 367 | Pioneer Valley-Greenmount | 367_Pioneer Valley - Greenmount 66 kV | Voltage at Constrained Conductor | 69.6134 | 69.6134 | 69.6134 | 69.675 | 69.6749 | 69.675 | 69.713 | 69.7129 | 69.713 | 69.717 | 69.7169 | 69.717 | 69.7115 | 69.7114 | 69.7115
MK | 30053881 | 372 | Pioneer Valley-MCKINLEY CREEK | 372_Pioneer Valley-McKinley Creek 33 kV | % of Rated A | 2.548 | 1.7873 | 1.8402 | 3.3884 | 2.3767 | 2.4472 | 4.1679 | 2.9235 | 3.0102 | 4.9058 | 3.4411 | 3.5431 | 5.5778 | 3.9125 | 4.0284
MK | 30053881 | 372 | Pioneer Valley-MCKINLEY CREEK | 372_Pioneer Valley-McKinley Creek 33 kV | Limiting Line Name | TR_LINE 9963_1 | TR_LINE 9963_1 | TR_LINE 9963_1 | TR_LINE 9963_1 | TR_LINE 9963_1 | TR_LINE 9963_1 | TR_LINE 9963_1 | TR_LINE 9963_1 | TR_LINE 9963_1 | TR_LINE 9963_1 | TR_LINE 9963_1 | TR_LINE 9963_1 | TR_LINE 9963_1 | TR_LINE 9963_1 | TR_LINE 9963_1
MK | 30053881 | 372 | Pioneer Valley-MCKINLEY CREEK | 372_Pioneer Valley-McKinley Creek 33 kV | Loading (A) | 4.9686 | 4.9686 | 4.9686 | 6.6073 | 6.6073 | 6.6073 | 8.1275 | 8.1275 | 8.1275 | 9.5663 | 9.5663 | 9.5663 | 10.8768 | 10.8768 | 10.8768
MK | 30053881 | 372 | Pioneer Valley-MCKINLEY CREEK | 372_Pioneer Valley-McKinley Creek 33 kV | Loading (MVA) | 0.59936 | 0.59936 | 0.59936 | 0.79781 | 0.79781 | 0.79781 | 0.98198 | 0.98198 | 0.98198 | 1.156 | 1.156 | 1.156 | 1.3143 | 1.3143 | 1.3143
MK | 30053881 | 372 | Pioneer Valley-MCKINLEY CREEK | 372_Pioneer Valley-McKinley Creek 33 kV | Loading (MW) | 0.58416 | 0.58416 | 0.58416 | 0.78681 | 0.78681 | 0.78681 | 0.97341 | 0.97341 | 0.97341 | 1.149 | 1.149 | 1.149 | 1.3086 | 1.3086 | 1.3086
MK | 30053881 | 372 | Pioneer Valley-MCKINLEY CREEK | 372_Pioneer Valley-McKinley Creek 33 kV | Power Factor | 0.97465 | 0.97465 | 0.97465 | 0.98621 | 0.98621 | 0.98621 | 0.99127 | 0.99127 | 0.99127 | 0.994 | 0.994 | 0.994 | 0.9956 | 0.9956 | 0.9956
MK | 30053881 | 372 | Pioneer Valley-MCKINLEY CREEK | 372_Pioneer Valley-McKinley Creek 33 kV | Rating (A) | 195 | 278 | 270 | 195 | 278 | 270 | 195 | 278 | 270 | 195 | 278 | 270 | 195 | 278 | 270
MK | 30053881 | 372 | Pioneer Valley-MCKINLEY CREEK | 372_Pioneer Valley-McKinley Creek 33 kV | Time | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00
MK | 30053881 | 372 | Pioneer Valley-MCKINLEY CREEK | 372_Pioneer Valley-McKinley Creek 33 kV | Voltage at Constrained Conductor | 69.6449 | 69.6449 | 69.6449 | 69.7131 | 69.7131 | 69.713 | 69.7572 | 69.7571 | 69.7571 | 69.7669 | 69.7668 | 69.7668 | 69.7665 | 69.7664 | 69.7664
MK | 80001012 | PROS-KECR-1 | Proserpine No.1 66kV Feeder | PROS-KECR-1_Proserpine No 1 66 kV | % of Rated A | 2.5618 | 1.9215 | 2.0066 | 4.1735 | 3.1304 | 3.2689 | 5.6856 | 4.2645 | 4.4532 | 7.1061 | 5.33 | 5.5658 | 8.3737 | 6.2807 | 6.5587
MK | 80001012 | PROS-KECR-1 | Proserpine No.1 66kV Feeder | PROS-KECR-1_Proserpine No 1 66 kV | Limiting Line Name | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1
MK | 80001012 | PROS-KECR-1 | Proserpine No.1 66kV Feeder | PROS-KECR-1_Proserpine No 1 66 kV | Loading (A) | 4.5345 | 4.5348 | 4.5348 | 7.3871 | 7.3877 | 7.3877 | 10.0635 | 10.0642 | 10.0642 | 12.5778 | 12.5788 | 12.5788 | 14.8214 | 14.8225 | 14.8226
MK | 80001012 | PROS-KECR-1 | Proserpine No.1 66kV Feeder | PROS-KECR-1_Proserpine No 1 66 kV | Loading (MVA) | 0.54197 | 0.54197 | 0.54197 | 0.8846 | 0.8846 | 0.8846 | 1.2071 | 1.2071 | 1.2071 | 1.5112 | 1.5112 | 1.5112 | 1.7833 | 1.7833 | 1.7833
MK | 80001012 | PROS-KECR-1 | Proserpine No.1 66kV Feeder | PROS-KECR-1_Proserpine No 1 66 kV | Loading (MW) | 0.54196 | 0.54196 | 0.54196 | 0.88457 | 0.88457 | 0.88457 | 1.2071 | 1.2071 | 1.2071 | 1.5111 | 1.5111 | 1.5111 | 1.7831 | 1.7831 | 1.7831
MK | 80001012 | PROS-KECR-1 | Proserpine No.1 66kV Feeder | PROS-KECR-1_Proserpine No 1 66 kV | Power Factor | 0.99999 | 0.99999 | 0.99999 | 0.99997 | 0.99997 | 0.99997 | 0.99994 | 0.99994 | 0.99994 | 0.99991 | 0.99991 | 0.99991 | 0.99987 | 0.99987 | 0.99987
MK | 80001012 | PROS-KECR-1 | Proserpine No.1 66kV Feeder | PROS-KECR-1_Proserpine No 1 66 kV | Rating (A) | 177 | 236 | 226 | 177 | 236 | 226 | 177 | 236 | 226 | 177 | 236 | 226 | 177 | 236 | 226
MK | 80001012 | PROS-KECR-1 | Proserpine No.1 66kV Feeder | PROS-KECR-1_Proserpine No 1 66 kV | Time | 16:30 | 17:00 | 7:30 | 16:30 | 17:00 | 7:30 | 16:30 | 17:00 | 7:30 | 16:30 | 17:00 | 7:30 | 16:30 | 17:00 | 7:30
MK | 80001012 | PROS-KECR-1 | Proserpine No.1 66kV Feeder | PROS-KECR-1_Proserpine No 1 66 kV | Voltage at Constrained Conductor | 69.0061 | 69.0008 | 69.0008 | 69.1371 | 69.1318 | 69.1318 | 69.2535 | 69.2482 | 69.2482 | 69.3674 | 69.3621 | 69.3621 | 69.467 | 69.4618 | 69.4616
MK | 80075847 | PROS-KECR-2 | Proserpine No.2 66kV Feeder | PROS-KECR-2_Proserpine No 2 66 kV | % of Rated A | 5.1223 | 3.8421 | 4.0121 | 8.3435 | 6.2581 | 6.535 | 11.3646 | 8.5241 | 8.9012 | 14.2017 | 10.6521 | 11.1234 | 16.7327 | 12.5505 | 13.1059
MK | 80075847 | PROS-KECR-2 | Proserpine No.2 66kV Feeder | PROS-KECR-2_Proserpine No 2 66 kV | Limiting Line Name | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1
MK | 80075847 | PROS-KECR-2 | Proserpine No.2 66kV Feeder | PROS-KECR-2_Proserpine No 2 66 kV | Loading (A) | 9.0665 | 9.0672 | 9.0673 | 14.7679 | 14.7691 | 14.7691 | 20.1153 | 20.1168 | 20.1168 | 25.137 | 25.1389 | 25.1389 | 29.6169 | 29.6191 | 29.6192
MK | 80075847 | PROS-KECR-2 | Proserpine No.2 66kV Feeder | PROS-KECR-2_Proserpine No 2 66 kV | Loading (MVA) | 1.0837 | 1.0837 | 1.0837 | 1.7685 | 1.7685 | 1.7685 | 2.4129 | 2.4129 | 2.4129 | 3.0202 | 3.0202 | 3.0202 | 3.5636 | 3.5636 | 3.5636
MK | 80075847 | PROS-KECR-2 | Proserpine No.2 66kV Feeder | PROS-KECR-2_Proserpine No 2 66 kV | Loading (MW) | 1.0836 | 1.0836 | 1.0836 | 1.7684 | 1.7684 | 1.7684 | 2.4127 | 2.4127 | 2.4127 | 3.0199 | 3.0199 | 3.0199 | 3.5631 | 3.5631 | 3.5631
MK | 80075847 | PROS-KECR-2 | Proserpine No.2 66kV Feeder | PROS-KECR-2_Proserpine No 2 66 kV | Power Factor | 0.99999 | 0.99999 | 0.99999 | 0.99997 | 0.99997 | 0.99997 | 0.99994 | 0.99994 | 0.99994 | 0.99991 | 0.99991 | 0.99991 | 0.99987 | 0.99987 | 0.99987
MK | 80075847 | PROS-KECR-2 | Proserpine No.2 66kV Feeder | PROS-KECR-2_Proserpine No 2 66 kV | Rating (A) | 177 | 236 | 226 | 177 | 236 | 226 | 177 | 236 | 226 | 177 | 236 | 226 | 177 | 236 | 226
MK | 80075847 | PROS-KECR-2 | Proserpine No.2 66kV Feeder | PROS-KECR-2_Proserpine No 2 66 kV | Time | 16:30 | 17:00 | 7:30 | 16:30 | 17:00 | 7:30 | 16:30 | 17:00 | 7:30 | 16:30 | 17:00 | 7:30 | 16:30 | 17:00 | 7:30
MK | 80075847 | PROS-KECR-2 | Proserpine No.2 66kV Feeder | PROS-KECR-2_Proserpine No 2 66 kV | Voltage at Constrained Conductor | 69.0065 | 69.0011 | 69.0011 | 69.1376 | 69.1323 | 69.1323 | 69.2542 | 69.2489 | 69.2489 | 69.3682 | 69.363 | 69.3629 | 69.468 | 69.4628 | 69.4626
MK | 82846747 | 351 | ALLIGATOR CREEK 33kV FDR | 351_Alligator Creek 33 kV | % of Rated A | 4.1916 | 4.1883 | 4.1883 | 3.3365 | 3.3318 | 3.3318 | 2.5814 | 2.575 | 2.575 | 1.9401 | 1.9313 | 1.9313 | 1.3956 | 1.3831 | 1.3831
MK | 82846747 | 351 | ALLIGATOR CREEK 33kV FDR | 351_Alligator Creek 33 kV | Limiting Line Name | TR_LINE 93922_3 | TR_CABLE 7120_1 | TR_CABLE 7120_1 | TR_LINE 93922_3 | TR_CABLE 7120_1 | TR_CABLE 7120_1 | TR_LINE 93922_3 | TR_CABLE 7120_1 | TR_CABLE 7120_1 | TR_LINE 93922_3 | TR_CABLE 7120_1 | TR_CABLE 7120_1 | TR_LINE 93922_3 | TR_CABLE 7120_1 | TR_CABLE 7120_1
MK | 82846747 | 351 | ALLIGATOR CREEK 33kV FDR | 351_Alligator Creek 33 kV | Loading (A) | 9.8082 | 9.8005 | 9.8005 | 7.8073 | 7.7965 | 7.7965 | 6.0406 | 6.0255 | 6.0255 | 4.5397 | 4.5193 | 4.5193 | 3.2658 | 3.2365 | 3.2365
MK | 82846747 | 351 | ALLIGATOR CREEK 33kV FDR | 351_Alligator Creek 33 kV | Loading (MVA) | 0.59161 | 0.59093 | 0.59093 | 0.47255 | 0.47176 | 0.47176 | 0.36654 | 0.36555 | 0.36555 | 0.27265 | 0.27138 | 0.27138 | 0.1964 | 0.19462 | 0.19462
MK | 82846747 | 351 | ALLIGATOR CREEK 33kV FDR | 351_Alligator Creek 33 kV | Loading (MW) | 0.59112 | 0.59089 | 0.59089 | 0.47183 | 0.47168 | 0.47168 | 0.36551 | 0.36542 | 0.36542 | 0.27123 | 0.27118 | 0.27118 | 0.19434 | 0.19432 | 0.19432
MK | 82846747 | 351 | ALLIGATOR CREEK 33kV FDR | 351_Alligator Creek 33 kV | Power Factor | 0.99917 | 0.99993 | 0.99993 | 0.99847 | 0.99983 | 0.99983 | 0.99718 | 0.99964 | 0.99964 | 0.9948 | 0.99927 | 0.99927 | 0.98952 | 0.99845 | 0.99845
MK | 82846747 | 351 | ALLIGATOR CREEK 33kV FDR | 351_Alligator Creek 33 kV | Rating (A) | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234
MK | 82846747 | 351 | ALLIGATOR CREEK 33kV FDR | 351_Alligator Creek 33 kV | Time | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00
MK | 82846747 | 351 | ALLIGATOR CREEK 33kV FDR | 351_Alligator Creek 33 kV | Voltage at Constrained Conductor | 34.8246 | 34.8119 | 34.8119 | 34.945 | 34.9351 | 34.9351 | 35.0338 | 35.0263 | 35.0263 | 34.6742 | 34.6688 | 34.6688 | 34.7212 | 34.7176 | 34.7176
MK | 82913608 | PV 6/5 | PV 6/5 GLENELLA NO 1 | PV 6/5_Glenella No 1 66 kV | % of Rated A | 48.4831 | 43.2178 | 44.0707 | 48.3572 | 43.1055 | 43.9563 | 48.2534 | 43.013 | 43.862 | 48.1787 | 42.9465 | 43.7941 | 48.1715 | 42.94 | 43.7875
MK | 82913608 | PV 6/5 | PV 6/5 GLENELLA NO 1 | PV 6/5_Glenella No 1 66 kV | Limiting Line Name | TR_LINE 143921_1 | TR_LINE 143921_1 | TR_LINE 143921_1 | TR_LINE 143921_1 | TR_LINE 143921_1 | TR_LINE 143921_1 | TR_LINE 143921_1 | TR_LINE 143921_1 | TR_LINE 143921_1 | TR_LINE 143921_1 | TR_LINE 143921_1 | TR_LINE 143921_1 | TR_LINE 143921_1 | TR_LINE 143921_1 | TR_LINE 143921_1
MK | 82913608 | PV 6/5 | PV 6/5 GLENELLA NO 1 | PV 6/5_Glenella No 1 66 kV | Loading (A) | 401.9185 | 401.9185 | 401.9186 | 400.8747 | 400.8749 | 400.8749 | 400.0141 | 400.0144 | 400.0146 | 399.3951 | 399.3955 | 399.3957 | 399.335 | 399.3355 | 399.3358
MK | 82913608 | PV 6/5 | PV 6/5 GLENELLA NO 1 | PV 6/5_Glenella No 1 66 kV | Loading (MVA) | 46.9983 | 46.9983 | 46.9983 | 46.9445 | 46.9445 | 46.9445 | 46.8912 | 46.8912 | 46.8912 | 46.8384 | 46.8384 | 46.8384 | 46.8383 | 46.8383 | 46.8383
MK | 82913608 | PV 6/5 | PV 6/5 GLENELLA NO 1 | PV 6/5_Glenella No 1 66 kV | Loading (MW) | 27.1872 | 27.1872 | 27.1872 | 27.0871 | 27.0871 | 27.0871 | 26.9869 | 26.9869 | 26.9869 | 26.8868 | 26.8868 | 26.8868 | 26.8868 | 26.8868 | 26.8868
MK | 82913608 | PV 6/5 | PV 6/5 GLENELLA NO 1 | PV 6/5_Glenella No 1 66 kV | Power Factor | 0.57847 | 0.57847 | 0.57847 | 0.577 | 0.577 | 0.577 | 0.57552 | 0.57552 | 0.57552 | 0.57403 | 0.57403 | 0.57403 | 0.57403 | 0.57403 | 0.57403
MK | 82913608 | PV 6/5 | PV 6/5 GLENELLA NO 1 | PV 6/5_Glenella No 1 66 kV | Rating (A) | 829 | 930 | 912 | 829 | 930 | 912 | 829 | 930 | 912 | 829 | 930 | 912 | 829 | 930 | 912
MK | 82913608 | PV 6/5 | PV 6/5 GLENELLA NO 1 | PV 6/5_Glenella No 1 66 kV | Time | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00
MK | 82913608 | PV 6/5 | PV 6/5 GLENELLA NO 1 | PV 6/5_Glenella No 1 66 kV | Voltage at Constrained Conductor | 67.5124 | 67.5124 | 67.5124 | 67.6108 | 67.6107 | 67.6107 | 67.6792 | 67.6792 | 67.6792 | 67.7078 | 67.7077 | 67.7077 | 67.7179 | 67.7178 | 67.7177
MK | 82913611 | PV 6/4 | PV 6/4 GLENELLA NO 2 | PV 6/4_Glenella No 2 66 kV | % of Rated A | 19.3412 | 17.2324 | 17.5612 | 20.7426 | 18.4811 | 18.8337 | 22.1637 | 19.7472 | 20.124 | 23.6076 | 21.0337 | 21.435 | 25.0645 | 22.3317 | 22.7578
MK | 82913611 | PV 6/4 | PV 6/4 GLENELLA NO 2 | PV 6/4_Glenella No 2 66 kV | Limiting Line Name | TR_LINE 105543_1 | TR_LINE 105543_1 | TR_LINE 105543_1 | TR_LINE 105543_1 | TR_LINE 105543_1 | TR_LINE 105543_1 | TR_LINE 105543_1 | TR_LINE 105543_1 | TR_LINE 105543_1 | TR_LINE 105543_1 | TR_LINE 105543_1 | TR_LINE 105543_1 | TR_LINE 105543_1 | TR_LINE 105543_1 | TR_LINE 105543_1
MK | 82913611 | PV 6/4 | PV 6/4 GLENELLA NO 2 | PV 6/4_Glenella No 2 66 kV | Loading (A) | 156.4643 | 156.4644 | 156.4644 | 167.8026 | 167.8027 | 167.8027 | 179.2995 | 179.2996 | 179.2997 | 190.9808 | 190.9811 | 190.9812 | 202.7669 | 202.7672 | 202.7674
MK | 82913611 | PV 6/4 | PV 6/4 GLENELLA NO 2 | PV 6/4_Glenella No 2 66 kV | Loading (MVA) | 18.6073 | 18.6073 | 18.6073 | 19.9856 | 19.9856 | 19.9856 | 21.3775 | 21.3775 | 21.3775 | 22.7813 | 22.7813 | 22.7813 | 24.1916 | 24.1916 | 24.1916
MK | 82913611 | PV 6/4 | PV 6/4 GLENELLA NO 2 | PV 6/4_Glenella No 2 66 kV | Loading (MW) | 13.64 | 13.64 | 13.64 | 15.434 | 15.434 | 15.434 | 17.1443 | 17.1443 | 17.1443 | 18.7948 | 18.7948 | 18.7948 | 20.3645 | 20.3645 | 20.3645
MK | 82913611 | PV 6/4 | PV 6/4 GLENELLA NO 2 | PV 6/4_Glenella No 2 66 kV | Power Factor | 0.73305 | 0.73305 | 0.73305 | 0.77225 | 0.77225 | 0.77225 | 0.80198 | 0.80198 | 0.80198 | 0.82501 | 0.82501 | 0.82501 | 0.8418 | 0.8418 | 0.8418
MK | 82913611 | PV 6/4 | PV 6/4 GLENELLA NO 2 | PV 6/4_Glenella No 2 66 kV | Rating (A) | 809 | 908 | 891 | 809 | 908 | 891 | 809 | 908 | 891 | 809 | 908 | 891 | 809 | 908 | 891
MK | 82913611 | PV 6/4 | PV 6/4 GLENELLA NO 2 | PV 6/4_Glenella No 2 66 kV | Time | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00
MK | 82913611 | PV 6/4 | PV 6/4 GLENELLA NO 2 | PV 6/4_Glenella No 2 66 kV | Voltage at Constrained Conductor | 68.6605 | 68.6605 | 68.6605 | 68.7634 | 68.7634 | 68.7634 | 68.8364 | 68.8363 | 68.8363 | 68.8695 | 68.8695 | 68.8694 | 68.8821 | 68.8821 | 68.882
MK | 83058752 | 395 | MACT-ALST | 395_Tennyson Street-Alfred Street 33 kV | % of Rated A | 5.8857 | 5.8857 | 5.8857 | 4.5044 | 4.5044 | 4.5044 | 4.7081 | 4.7081 | 4.7081 | 5.6499 | 5.6499 | 5.6499 | 6.6485 | 6.6485 | 6.6485
MK | 83058752 | 395 | MACT-ALST | 395_Tennyson Street-Alfred Street 33 kV | Limiting Line Name | TR_CABLE 2960_1 | TR_CABLE 2960_1 | TR_CABLE 2960_1 | TR_CABLE 2960_1 | TR_CABLE 2960_1 | TR_CABLE 2960_1 | TR_CABLE 2960_1 | TR_CABLE 2960_1 | TR_CABLE 2960_1 | TR_CABLE 2960_1 | TR_CABLE 2960_1 | TR_CABLE 2960_1 | TR_CABLE 2960_1 | TR_CABLE 2960_1 | TR_CABLE 2960_1
MK | 83058752 | 395 | MACT-ALST | 395_Tennyson Street-Alfred Street 33 kV | Loading (A) | 39.5518 | 39.5518 | 39.5518 | 30.2698 | 30.2697 | 30.2697 | 31.6387 | 31.6387 | 31.6387 | 37.9676 | 37.9675 | 37.9676 | 44.6779 | 44.6778 | 44.6778
MK | 83058752 | 395 | MACT-ALST | 395_Tennyson Street-Alfred Street 33 kV | Loading (MVA) | 2.3542 | 2.3542 | 2.3542 | 1.8052 | 1.8052 | 1.8052 | 1.8896 | 1.8896 | 1.8896 | 2.2423 | 2.2423 | 2.2423 | 2.6403 | 2.6403 | 2.6403
MK | 83058752 | 395 | MACT-ALST | 395_Tennyson Street-Alfred Street 33 kV | Loading (MW) | 1.668 | 1.668 | 1.668 | 0.48175 | 0.48175 | 0.48175 | 0.52503 | 0.52503 | 0.52503 | 1.2943 | 1.2943 | 1.2943 | 1.8512 | 1.8512 | 1.8512
MK | 83058752 | 395 | MACT-ALST | 395_Tennyson Street-Alfred Street 33 kV | Power Factor | 0.70854 | 0.70854 | 0.70854 | 0.26686 | 0.26686 | 0.26686 | 0.27785 | 0.27785 | 0.27785 | 0.57724 | 0.57724 | 0.57724 | 0.70113 | 0.70113 | 0.70113
MK | 83058752 | 395 | MACT-ALST | 395_Tennyson Street-Alfred Street 33 kV | Rating (A) | 672 | 672 | 672 | 672 | 672 | 672 | 672 | 672 | 672 | 672 | 672 | 672 | 672 | 672 | 672
MK | 83058752 | 395 | MACT-ALST | 395_Tennyson Street-Alfred Street 33 kV | Time | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30
MK | 83058752 | 395 | MACT-ALST | 395_Tennyson Street-Alfred Street 33 kV | Voltage at Constrained Conductor | 34.3645 | 34.3645 | 34.3645 | 34.4321 | 34.4321 | 34.4321 | 34.4821 | 34.4821 | 34.4821 | 34.0967 | 34.0967 | 34.0967 | 34.1195 | 34.1195 | 34.1195
MK | 84186116 | 423 | NORTH MACKAY NO 2 | 423_North Mackay No 2 33 kV | % of Rated A | 12.4835 | 12.4835 | 12.4835 | 13.4539 | 13.4539 | 13.4539 | 14.6589 | 14.6589 | 14.6589 | 16.0326 | 16.0326 | 16.0326 | 17.4926 | 17.4926 | 17.4926
MK | 84186116 | 423 | NORTH MACKAY NO 2 | 423_North Mackay No 2 33 kV | Limiting Line Name | TR_CABLE 6563_1 | TR_CABLE 6563_1 | TR_CABLE 6563_1 | TR_CABLE 6563_1 | TR_CABLE 6563_1 | TR_CABLE 6563_1 | TR_CABLE 6563_1 | TR_CABLE 6563_1 | TR_CABLE 6563_1 | TR_CABLE 6563_1 | TR_CABLE 6563_1 | TR_CABLE 6563_1 | TR_CABLE 6563_1 | TR_CABLE 6563_1 | TR_CABLE 6563_1
MK | 84186116 | 423 | NORTH MACKAY NO 2 | 423_North Mackay No 2 33 kV | Loading (A) | 76.3989 | 76.3989 | 76.3989 | 82.3378 | 82.3377 | 82.3377 | 89.7123 | 89.7123 | 89.7123 | 98.1197 | 98.1197 | 98.1197 | 107.0549 | 107.0549 | 107.0549
MK | 84186116 | 423 | NORTH MACKAY NO 2 | 423_North Mackay No 2 33 kV | Loading (MVA) | 4.5981 | 4.5981 | 4.5981 | 4.9636 | 4.9636 | 4.9636 | 5.4145 | 5.4145 | 5.4145 | 5.9252 | 5.9252 | 5.9252 | 6.3857 | 6.3857 | 6.3857
MK | 84186116 | 423 | NORTH MACKAY NO 2 | 423_North Mackay No 2 33 kV | Loading (MW) | 1.5895 | 1.5895 | 1.5895 | 2.4562 | 2.4562 | 2.4562 | 3.2882 | 3.2882 | 3.2882 | 4.0988 | 4.0988 | 4.0988 | 4.8637 | 4.8637 | 4.8637
MK | 84186116 | 423 | NORTH MACKAY NO 2 | 423_North Mackay No 2 33 kV | Power Factor | 0.34568 | 0.34568 | 0.34568 | 0.49484 | 0.49484 | 0.49484 | 0.6073 | 0.6073 | 0.6073 | 0.69175 | 0.69175 | 0.69175 | 0.76165 | 0.76165 | 0.76165
MK | 84186116 | 423 | NORTH MACKAY NO 2 | 423_North Mackay No 2 33 kV | Rating (A) | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612
MK | 84186116 | 423 | NORTH MACKAY NO 2 | 423_North Mackay No 2 33 kV | Time | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 16:30 | 21:00 | 4:00
MK | 84186116 | 423 | NORTH MACKAY NO 2 | 423_North Mackay No 2 33 kV | Voltage at Constrained Conductor | 34.7478 | 34.7478 | 34.7478 | 34.8046 | 34.8046 | 34.8046 | 34.8452 | 34.8452 | 34.8452 | 34.8649 | 34.8649 | 34.8649 | 34.4385 | 34.4385 | 34.4385
MK | 84186121 | 422 | NORTH MACKAY NO 1 | 422_North Mackay No 1 33 kV | % of Rated A | 15.4461 | 15.4461 | 15.4461 | 19.0792 | 17.207 | 17.6137 | 23.6179 | 21.3004 | 21.8038 | 28.3124 | 25.5343 | 26.1378 | 32.8422 | 29.6196 | 30.3196
MK | 84186121 | 422 | NORTH MACKAY NO 1 | 422_North Mackay No 1 33 kV | Limiting Line Name | TR_CABLE 21_1 | TR_CABLE 21_1 | TR_CABLE 21_1 | TR_LINE 97201_1 | TR_LINE 97201_1 | TR_LINE 97201_1 | TR_LINE 97201_1 | TR_LINE 97201_1 | TR_LINE 97201_1 | TR_LINE 97201_1 | TR_LINE 97201_1 | TR_LINE 97201_1 | TR_LINE 97201_1 | TR_LINE 97201_1 | TR_LINE 97201_1
MK | 84186121 | 422 | NORTH MACKAY NO 1 | 422_North Mackay No 1 33 kV | Loading (A) | 76.4583 | 76.4583 | 76.4583 | 119.2421 | 119.2421 | 119.2421 | 147.6097 | 147.6097 | 147.6098 | 176.9511 | 176.9512 | 176.9512 | 205.262 | 205.2622 | 205.2623
MK | 84186121 | 422 | NORTH MACKAY NO 1 | 422_North Mackay No 1 33 kV | Loading (MVA) | 4.6036 | 4.6036 | 4.6036 | 7.1924 | 7.1924 | 7.1924 | 8.9143 | 8.9143 | 8.9143 | 10.6923 | 10.6923 | 10.6923 | 12.4054 | 12.4053 | 12.4053
MK | 84186121 | 422 | NORTH MACKAY NO 1 | 422_North Mackay No 1 33 kV | Loading (MW) | 1.5893 | 1.5893 | 1.5893 | 5.7757 | 5.7757 | 5.7757 | 7.851 | 7.851 | 7.851 | 9.8614 | 9.8614 | 9.8614 | 11.7337 | 11.7337 | 11.7337
MK | 84186121 | 422 | NORTH MACKAY NO 1 | 422_North Mackay No 1 33 kV | Power Factor | 0.34524 | 0.34524 | 0.34524 | 0.80303 | 0.80303 | 0.80303 | 0.88071 | 0.88071 | 0.88071 | 0.92229 | 0.92229 | 0.92229 | 0.94586 | 0.94586 | 0.94586
MK | 84186121 | 422 | NORTH MACKAY NO 1 | 422_North Mackay No 1 33 kV | Rating (A) | 495 | 495 | 495 | 625 | 693 | 677 | 625 | 693 | 677 | 625 | 693 | 677 | 625 | 693 | 677
MK | 84186121 | 422 | NORTH MACKAY NO 1 | 422_North Mackay No 1 33 kV | Time | 12:00 | 17:00 | 8:30 | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00
MK | 84186121 | 422 | NORTH MACKAY NO 1 | 422_North Mackay No 1 33 kV | Voltage at Constrained Conductor | 34.7629 | 34.7629 | 34.7629 | 34.8242 | 34.8242 | 34.8242 | 34.8669 | 34.8669 | 34.8669 | 34.8866 | 34.8865 | 34.8865 | 34.8931 | 34.8931 | 34.8931
MK | 84211409 | 426 | MT ROOPER | 426_Mt Rooper 66 kV | % of Rated A | 24.6036 | 21.8794 | 21.8794 | 24.4367 | 21.7309 | 21.731 | 24.6403 | 21.912 | 21.912 | 24.4858 | 21.7746 | 21.7746 | 24.3485 | 21.6525 | 21.6526
MK | 84211409 | 426 | MT ROOPER | 426_Mt Rooper 66 kV | Limiting Line Name | TR_LINE 97526_1 | TR_CABLE 2481_1 | TR_CABLE 2481_1 | TR_LINE 97526_1 | TR_CABLE 2481_1 | TR_CABLE 2481_1 | TR_LINE 97526_1 | TR_CABLE 2481_1 | TR_CABLE 2481_1 | TR_LINE 97526_1 | TR_CABLE 2481_1 | TR_CABLE 2481_1 | TR_LINE 97526_1 | TR_CABLE 2481_1 | TR_CABLE 2481_1
MK | 84211409 | 426 | MT ROOPER | 426_Mt Rooper 66 kV | Loading (A) | 61.263 | 61.2624 | 61.2624 | 60.8475 | 60.8466 | 60.8467 | 61.3542 | 61.3536 | 61.3536 | 60.9697 | 60.9688 | 60.9689 | 60.6278 | 60.627 | 60.6272
MK | 84211409 | 426 | MT ROOPER | 426_Mt Rooper 66 kV | Loading (MVA) | 7.2604 | 7.2573 | 7.2573 | 7.2311 | 7.228 | 7.228 | 7.3083 | 7.3051 | 7.3051 | 7.2807 | 7.2776 | 7.2776 | 7.256 | 7.2529 | 7.2529
MK | 84211409 | 426 | MT ROOPER | 426_Mt Rooper 66 kV | Loading (MW) | 7.2524 | 7.2497 | 7.2497 | 7.2228 | 7.2201 | 7.2201 | 7.3005 | 7.2978 | 7.2978 | 7.2726 | 7.27 | 7.27 | 7.2482 | 7.2456 | 7.2456
MK | 84211409 | 426 | MT ROOPER | 426_Mt Rooper 66 kV | Power Factor | 0.99889 | 0.99896 | 0.99896 | 0.99884 | 0.99891 | 0.99891 | 0.99894 | 0.999 | 0.999 | 0.99889 | 0.99896 | 0.99896 | 0.99893 | 0.99899 | 0.99899
MK | 84211409 | 426 | MT ROOPER | 426_Mt Rooper 66 kV | Rating (A) | 249 | 280 | 280 | 249 | 280 | 280 | 249 | 280 | 280 | 249 | 280 | 280 | 249 | 280 | 280
MK | 84211409 | 426 | MT ROOPER | 426_Mt Rooper 66 kV | Time | 16:30 | 17:00 | 7:30 | 16:30 | 17:00 | 7:30 | 16:30 | 17:00 | 7:30 | 16:30 | 17:00 | 7:30 | 16:30 | 17:00 | 7:30
MK | 84211409 | 426 | MT ROOPER | 426_Mt Rooper 66 kV | Voltage at Constrained Conductor | 68.423 | 68.3944 | 68.3944 | 68.6122 | 68.5839 | 68.5839 | 68.7715 | 68.743 | 68.7429 | 68.9443 | 68.916 | 68.9159 | 69.0978 | 69.0696 | 69.0694
MK | 84216180 | 387 | ALFRED ST 1 | 387_Mackay-Alfred Street 1 33 kV | % of Rated A | 29.1319 | 29.1319 | 29.1319 | 26.1447 | 26.1447 | 26.1447 | 23.883 | 23.883 | 23.883 | 22.1676 | 22.1675 | 22.1676 | 21.104 | 21.104 | 21.104
MK | 84216180 | 387 | ALFRED ST 1 | 387_Mackay-Alfred Street 1 33 kV | Limiting Line Name | TR_CABLE 2967_1 | TR_CABLE 2967_1 | TR_CABLE 2967_1 | TR_CABLE 2967_1 | TR_CABLE 2967_1 | TR_CABLE 2967_1 | TR_CABLE 2967_1 | TR_CABLE 2967_1 | TR_CABLE 2967_1 | TR_CABLE 2967_1 | TR_CABLE 2967_1 | TR_CABLE 2967_1 | TR_CABLE 2967_1 | TR_CABLE 2967_1 | TR_CABLE 2967_1
MK | 84216180 | 387 | ALFRED ST 1 | 387_Mackay-Alfred Street 1 33 kV | Loading (A) | 125.5584 | 125.5584 | 125.5584 | 112.6836 | 112.6836 | 112.6836 | 102.9356 | 102.9356 | 102.9356 | 95.5422 | 95.5421 | 95.5421 | 90.9581 | 90.9581 | 90.9581
MK | 84216180 | 387 | ALFRED ST 1 | 387_Mackay-Alfred Street 1 33 kV | Loading (MVA) | 7.4767 | 7.4767 | 7.4767 | 6.7217 | 6.7217 | 6.7217 | 6.148 | 6.148 | 6.148 | 5.6418 | 5.6418 | 5.6418 | 5.3742 | 5.3741 | 5.3742
MK | 84216180 | 387 | ALFRED ST 1 | 387_Mackay-Alfred Street 1 33 kV | Loading (MW) | 5.7133 | 5.7133 | 5.7133 | 4.6694 | 4.6694 | 4.6694 | 3.7971 | 3.7971 | 3.7971 | 3.1049 | 3.1049 | 3.1049 | 2.5998 | 2.5998 | 2.5998
MK | 84216180 | 387 | ALFRED ST 1 | 387_Mackay-Alfred Street 1 33 kV | Power Factor | 0.76414 | 0.76414 | 0.76414 | 0.69467 | 0.69467 | 0.69467 | 0.61761 | 0.61761 | 0.61761 | 0.55034 | 0.55034 | 0.55034 | 0.48376 | 0.48376 | 0.48376
MK | 84216180 | 387 | ALFRED ST 1 | 387_Mackay-Alfred Street 1 33 kV | Rating (A) | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431
MK | 84216180 | 387 | ALFRED ST 1 | 387_Mackay-Alfred Street 1 33 kV | Time | 16:30 | 21:00 | 4:00 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30
MK | 84216180 | 387 | ALFRED ST 1 | 387_Mackay-Alfred Street 1 33 kV | Voltage at Constrained Conductor | 34.3798 | 34.3798 | 34.3798 | 34.4396 | 34.4396 | 34.4396 | 34.4831 | 34.483 | 34.4831 | 34.0929 | 34.0929 | 34.0929 | 34.1121 | 34.112 | 34.1121
MK | 84293483 | 6328 | BROADLEA-MOORVALE | 6328_Broadlea - Moorvale 66 kV | % of Rated A | 3.0528 | 3.0293 | 3.4864 | 3.0465 | 3.023 | 3.4791 | 3.0441 | 3.0206 | 3.4764 | 3.0403 | 3.0169 | 3.4721 | 3.0401 | 3.0166 | 3.4718
MK | 84293483 | 6328 | BROADLEA-MOORVALE | 6328_Broadlea - Moorvale 66 kV | Limiting Line Name | TR_LINE 174096_1 | TR_LINE 174096_1 | TR_LINE 174096_1 | TR_LINE 174096_1 | TR_LINE 174096_1 | TR_LINE 174096_1 | TR_LINE 174096_1 | TR_LINE 174096_1 | TR_LINE 174096_1 | TR_LINE 174096_1 | TR_LINE 174096_1 | TR_LINE 174096_1 | TR_LINE 174096_1 | TR_LINE 174096_1 | TR_LINE 174096_1
MK | 84293483 | 6328 | BROADLEA-MOORVALE | 6328_Broadlea - Moorvale 66 kV | Loading (A) | 11.784 | 11.784 | 11.784 | 11.7593 | 11.7593 | 11.7593 | 11.7503 | 11.7503 | 11.7503 | 11.7357 | 11.7357 | 11.7357 | 11.7347 | 11.7347 | 11.7347
MK | 84293483 | 6328 | BROADLEA-MOORVALE | 6328_Broadlea - Moorvale 66 kV | Loading (MVA) | 1.4189 | 1.4189 | 1.4189 | 1.4158 | 1.4158 | 1.4158 | 1.4145 | 1.4145 | 1.4145 | 1.4126 | 1.4126 | 1.4126 | 1.4125 | 1.4125 | 1.4125
MK | 84293483 | 6328 | BROADLEA-MOORVALE | 6328_Broadlea - Moorvale 66 kV | Loading (MW) | 1.4186 | 1.4186 | 1.4186 | 1.4155 | 1.4155 | 1.4155 | 1.4142 | 1.4142 | 1.4142 | 1.4123 | 1.4123 | 1.4123 | 1.4122 | 1.4122 | 1.4122
MK | 84293483 | 6328 | BROADLEA-MOORVALE | 6328_Broadlea - Moorvale 66 kV | Power Factor | 0.99978 | 0.99978 | 0.99978 | 0.99978 | 0.99978 | 0.99978 | 0.99978 | 0.99978 | 0.99978 | 0.99978 | 0.99978 | 0.99978 | 0.99978 | 0.99978 | 0.99978
MK | 84293483 | 6328 | BROADLEA-MOORVALE | 6328_Broadlea - Moorvale 66 kV | Rating (A) | 386 | 389 | 338 | 386 | 389 | 338 | 386 | 389 | 338 | 386 | 389 | 338 | 386 | 389 | 338
MK | 84293483 | 6328 | BROADLEA-MOORVALE | 6328_Broadlea - Moorvale 66 kV | Time | 14:30 | 19:00 | 6:00 | 15:30 | 20:30 | 0:00 | 16:30 | 21:00 | 23:30 | 11:00 | 20:30 | 3:30 | 16:30 | 17:00 | 2:30
MK | 84293483 | 6328 | BROADLEA-MOORVALE | 6328_Broadlea - Moorvale 66 kV | Voltage at Constrained Conductor | 69.5174 | 69.5174 | 69.5174 | 69.5104 | 69.5104 | 69.5104 | 69.5011 | 69.5011 | 69.5011 | 69.494 | 69.494 | 69.494 | 69.494 | 69.494 | 69.494
MK | 84293489 | 6330 | BROADLEA-MILLENNIUM | 6330 Broadlea - Millennium 66 kV | % of Rated A | 37.6339 | 36.0978 | 40.6931 | 37.9922 | 36.4415 | 41.0805 | 38.2338 | 36.6732 | 41.3417 | 38.5923 | 37.0171 | 41.7294 | 38.5923 | 37.0171 | 41.7294
MK | 84293489 | 6330 | BROADLEA-MILLENNIUM | 6330 Broadlea - Millennium 66 kV | Limiting Line Name | TR_LINE 63688_1 | TR_LINE 63688_1 | TR_LINE 63688_1 | TR_LINE 63688_1 | TR_LINE 63688_1 | TR_LINE 63688_1 | TR_LINE 63688_1 | TR_LINE 63688_1 | TR_LINE 63688_1 | TR_LINE 63688_1 | TR_LINE 63688_1 | TR_LINE 63688_1 | TR_LINE 63688_1 | TR_LINE 63688_1 | TR_LINE 63688_1
MK | 84293489 | 6330 | BROADLEA-MILLENNIUM | 6330 Broadlea - Millennium 66 kV | Loading (A) | 265.3188 | 265.3188 | 265.3188 | 267.8449 | 267.8449 | 267.8449 | 269.5479 | 269.5479 | 269.5479 | 272.0754 | 272.0754 | 272.0754 | 272.0754 | 272.0754 | 272.0754
MK | 84293489 | 6330 | BROADLEA-MILLENNIUM | 6330 Broadlea - Millennium 66 kV | Loading (MVA) | 31.9472 | 31.9472 | 31.9472 | 32.2481 | 32.2481 | 32.2481 | 32.4487 | 32.4487 | 32.4487 | 32.7496 | 32.7496 | 32.7496 | 32.7496 | 32.7496 | 32.7496
MK | 84293489 | 6330 | BROADLEA-MILLENNIUM | 6330 Broadlea - Millennium 66 kV | Loading (MW) | 31.9471 | 31.9471 | 31.9471 | 32.2479 | 32.2479 | 32.2479 | 32.4486 | 32.4486 | 32.4486 | 32.7494 | 32.7494 | 32.7494 | 32.7494 | 32.7494 | 32.7494
MK | 84293489 | 6330 | BROADLEA-MILLENNIUM | 6330 Broadlea - Millennium 66 kV | Power Factor | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
MK | 84293489 | 6330 | BROADLEA-MILLENNIUM | 6330 Broadlea - Millennium 66 kV | Rating (A) | 705 | 735 | 652 | 705 | 735 | 652 | 705 | 735 | 652 | 705 | 735 | 652 | 705 | 735 | 652
MK | 84293489 | 6330 | BROADLEA-MILLENNIUM | 6330 Broadlea - Millennium 66 kV | Time | 10:00 | 20:00 | 7:00 | 10:00 | 18:30 | 22:30 | 9:00 | 17:00 | 8:00 | 16:30 | 21:00 | 22:00 | 9:00 | 18:00 | 4:00
MK | 84293489 | 6330 | BROADLEA-MILLENNIUM | 6330 Broadlea - Millennium 66 kV | Voltage at Constrained Conductor | 69.5192 | 69.5192 | 69.5192 | 69.512 | 69.512 | 69.512 | 69.5026 | 69.5026 | 69.5026 | 69.4953 | 69.4953 | 69.4953 | 69.4953 | 69.4953 | 69.4953
MK | 84544397 | 7366 | 132KV MORA - BROD | 7366_Moranbah - Broadlea 132 kV | % of Rated A | 30.4291 | 29.1871 | 32.9026 | 30.67 | 29.4181 | 33.1631 | 30.9174 | 29.6555 | 33.4306 | 31.1591 | 29.8873 | 33.692 | 31.1591 | 29.8873 | 33.6919
MK | 84544397 | 7366 | 132KV MORA - BROD | 7366_Moranbah - Broadlea 132 kV | Limiting Line Name | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1
MK | 84544397 | 7366 | 132KV MORA - BROD | 7366_Moranbah - Broadlea 132 kV | Loading (A) | 214.5245 | 214.5245 | 214.5245 | 216.2225 | 216.2225 | 216.2225 | 217.967 | 217.967 | 217.967 | 219.6712 | 219.6712 | 219.6712 | 219.6707 | 219.6707 | 219.6707
MK | 84544397 | 7366 | 132KV MORA - BROD | 7366_Moranbah - Broadlea 132 kV | Loading (MVA) | 51.089 | 51.089 | 51.089 | 51.4891 | 51.4891 | 51.4891 | 51.8993 | 51.8993 | 51.8993 | 52.3006 | 52.3006 | 52.3006 | 52.3005 | 52.3005 | 52.3005
MK | 84544397 | 7366 | 132KV MORA - BROD | 7366_Moranbah - Broadlea 132 kV | Loading (MW) | 51.0683 | 51.0683 | 51.0683 | 51.4677 | 51.4677 | 51.4677 | 51.8764 | 51.8764 | 51.8764 | 52.277 | 52.277 | 52.277 | 52.2769 | 52.2769 | 52.2769
MK | 84544397 | 7366 | 132KV MORA - BROD | 7366_Moranbah - Broadlea 132 kV | Power Factor | 0.9996 | 0.9996 | 0.9996 | 0.99958 | 0.99958 | 0.99958 | 0.99956 | 0.99956 | 0.99956 | 0.99955 | 0.99955 | 0.99955 | 0.99955 | 0.99955 | 0.99955
MK | 84544397 | 7366 | 132KV MORA - BROD | 7366_Moranbah - Broadlea 132 kV | Rating (A) | 705 | 735 | 652 | 705 | 735 | 652 | 705 | 735 | 652 | 705 | 735 | 652 | 705 | 735 | 652
MK | 84544397 | 7366 | 132KV MORA - BROD | 7366_Moranbah - Broadlea 132 kV | Time | 14:30 | 21:00 | 6:00 | 9:30 | 20:00 | 7:00 | 13:00 | 21:00 | 8:00 | 16:00 | 19:30 | 1:00 | 12:00 | 18:00 | 1:30
MK | 84544397 | 7366 | 132KV MORA - BROD | 7366_Moranbah - Broadlea 132 kV | Voltage at Constrained Conductor | 137.4959 | 137.4959 | 137.4959 | 137.4844 | 137.4844 | 137.4844 | 137.4706 | 137.4706 | 137.4706 | 137.459 | 137.459 | 137.459 | 137.459 | 137.459 | 137.459
MK | 84750025 | 430 | ALFRED ST 2 | 430_Mackay-Alfred Street 2 33 kV | % of Rated A | 21.1022 | 21.1022 | 21.1022 | 18.9443 | 18.9443 | 18.9443 | 17.3109 | 17.3109 | 17.3109 | 16.0715 | 16.0715 | 16.0715 | 15.3037 | 15.3037 | 15.3037
MK | 84750025 | 430 | ALFRED ST 2 | 430_Mackay-Alfred Street 2 33 kV | Limiting Line Name | TR_CABLE 8887_1 | TR_CABLE 8887_1 | TR_CABLE 8887_1 | TR_CABLE 8887_1 | TR_CABLE 8887_1 | TR_CABLE 8887_1 | TR_CABLE 8887_1 | TR_CABLE 8887_1 | TR_CABLE 8887_1 | TR_CABLE 8887_1 | TR_CABLE 8887_1 | TR_CABLE 8887_1 | TR_CABLE 8887_1 | TR_CABLE 8887_1 | TR_CABLE 8887_1
MK | 84750025 | 430 | ALFRED ST 2 | 430_Mackay-Alfred Street 2 33 kV | Loading (A) | 122.1815 | 122.1815 | 122.1815 | 109.6874 | 109.6874 | 109.6874 | 100.2301 | 100.2301 | 100.2301 | 93.054 | 93.054 | 93.054 | 88.6086 | 88.6085 | 88.6085
MK | 84750025 | 430 | ALFRED ST 2 | 430_Mackay-Alfred Street 2 33 kV | Loading (MVA) | 7.2756 | 7.2756 | 7.2756 | 6.543 | 6.543 | 6.543 | 5.9864 | 5.9864 | 5.9864 | 5.4949 | 5.4949 | 5.4949 | 5.2353 | 5.2353 | 5.2353
MK | 84750025 | 430 | ALFRED ST 2 | 430_Mackay-Alfred Street 2 33 kV | Loading (MW) | 5.5527 | 5.5527 | 5.5527 | 4.5382 | 4.5382 | 4.5382 | 3.6904 | 3.6904 | 3.6904 | 3.0178 | 3.0178 | 3.0178 | 2.5269 | 2.5269 | 2.5269
MK | 84750025 | 430 | ALFRED ST 2 | 430_Mackay-Alfred Street 2 33 kV | Power Factor | 0.76319 | 0.76319 | 0.76319 | 0.6936 | 0.6936 | 0.6936 | 0.61647 | 0.61647 | 0.61647 | 0.5492 | 0.5492 | 0.5492 | 0.48266 | 0.48267 | 0.48267
MK | 84750025 | 430 | ALFRED ST 2 | 430_Mackay-Alfred Street 2 33 kV | Rating (A) | 579 | 579 | 579 | 579 | 579 | 579 | 579 | 579 | 579 | 579 | 579 | 579 | 579 | 579 | 579
MK | 84750025 | 430 | ALFRED ST 2 | 430_Mackay-Alfred Street 2 33 kV | Time | 16:30 | 21:00 | 4:00 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30
MK | 84750025 | 430 | ALFRED ST 2 | 430_Mackay-Alfred Street 2 33 kV | Voltage at Constrained Conductor | 34.3798 | 34.3798 | 34.3798 | 34.4396 | 34.4396 | 34.4396 | 34.4831 | 34.483 | 34.4831 | 34.0929 | 34.0929 | 34.0929 | 34.1121 | 34.112 | 34.1121
NQ | 10132026 | 7182 | ROSS - MILLCHESTER | 7182 Ross - Milchester | % of Rated A | 53.2212 | 45.2704 | 50.414 | 54.0797 | 46.0139 | 51.2324 | 56.4592 | 46.655 | 53.4895 | 57.1177 | 47.2378 | 54.1135 | 57.3375 | 47.7107 | 54.1731
NQ | 10132026 | 7182 | ROSS - MILLCHESTER | 7182 Ross - Milchester | Limiting Line Name | TR_LINE 221851_1 | TR_LINE 221851_1 | TR_LINE 221851_1 | TR_LINE 221851_1 | TR_LINE 221851_1 | TR_LINE 221851_1 | TR_LINE 221851_1 | TR_LINE 221851_1 | TR_LINE 221851_1 | TR_LINE 221851_1 | TR_LINE 221851_1 | TR_LINE 221851_1 | TR_LINE 221851_1 | TR_LINE 221851_1 | TR_LINE 221851_1
NQ | 10132026 | 7182 | ROSS - MILLCHESTER | 7182 Ross - Milchester | Loading (A) | 166.0501 | 162.068 | 165.8622 | 168.7286 | 164.7297 | 168.5547 | 176.1527 | 167.0248 | 175.9806 | 178.2072 | 169.1114 | 178.0334 | 178.8931 | 170.8044 | 178.2296
NQ | 10132026 | 7182 | ROSS - MILLCHESTER | 7182 Ross - Milchester | Loading (MVA) | 37.9626 | 37.0957 | 37.9199 | 38.5635 | 37.6943 | 38.5238 | 40.086 | 38.2112 | 40.0469 | 40.549 | 38.6846 | 40.5095 | 40.7155 | 39.0704 | 40.5669
NQ | 10132026 | 7182 | ROSS - MILLCHESTER | 7182 Ross - Milchester | Loading (MW) | 16.0519 | 15.4538 | 15.9995 | 16.6983 | 16.1051 | 16.6466 | 16.7523 | 16.6759 | 16.7005 | 17.3099 | 17.2368 | 17.2582 | 17.6411 | 17.7131 | 17.4726
NQ | 10132026 | 7182 | ROSS - MILLCHESTER | 7182 Ross - Milchester | Power Factor | 0.42284 | 0.41659 | 0.42193 | 0.43301 | 0.42725 | 0.43211 | 0.41791 | 0.43641 | 0.41702 | 0.42689 | 0.44557 | 0.42603 | 0.43328 | 0.45336 | 0.43071
NQ | 10132026 | 7182 | ROSS - MILLCHESTER | 7182 Ross - Milchester | Rating (A) | 312 | 358 | 329 | 312 | 358 | 329 | 312 | 358 | 329 | 312 | 358 | 329 | 312 | 358 | 329
NQ | 10132026 | 7182 | ROSS - MILLCHESTER | 7182 Ross - Milchester | Time | 11:00 | 17:00 | 8:30 | 11:00 | 17:00 | 8:30 | 11:00 | 17:00 | 8:30 | 11:00 | 17:00 | 8:30 | 16:00 | 17:00 | 7:00
NQ | 10132026 | 7182 | ROSS - MILLCHESTER | 7182 Ross - Milchester | Voltage at Constrained Conductor | 131.9945 | 132.1494 | 131.9956 | 131.9554 | 132.1123 | 131.9555 | 131.3841 | 132.0837 | 131.3842 | 131.3693 | 132.0699 | 131.3695 | 131.403 | 132.0652 | 131.4109
NQ | 20001222 | AV-CB-1 | Aitkenvale-Cranbrook | AV-CB-1_Aitkenvale-Cranbrook 66 kV | % of Rated A | 10.4437 | 8.9184 | 9.5858 | 10.4172 | 8.8958 | 9.5615 | 10.3646 | 8.8507 | 9.512 | 10.2891 | 8.7863 | 9.4382 | 10.2321 | 8.7428 | 9.3936
NQ | 20001222 | AV-CB-1 | Aitkenvale-Cranbrook | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Limiting Line Name | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1
NQ | 20001222 | AV-CB-1 | Aitkenvale-Cranbrook | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Loading (A) | 34.7775 | 34.7818 | 34.7964 | 34.6892 | 34.6935 | 34.7083 | 34.514 | 34.5178 | 34.5286 | 34.2628 | 34.2664 | 34.2608 | 34.0729 | 34.0971 | 34.0989
NQ | 20001222 | AV-CB-1 | Aitkenvale-Cranbrook | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Loading (MVA) | 4.1894 | 4.19 | 4.1916 | 4.1804 | 4.181 | 4.1827 | 4.1606 | 4.1612 | 4.1623 | 4.1314 | 4.1319 | 4.1311 | 4.1094 | 4.1123 | 4.1127
NQ | 20001222 | AV-CB-1 | Aitkenvale-Cranbrook | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Loading (MW) | 2.6832 | 2.684 | 2.6851 | 2.5784 | 2.5792 | 2.5803 | 2.4622 | 2.463 | 2.4638 | 2.3338 | 2.3347 | 2.3342 | 2.2253 | 2.2277 | 2.2313
NQ | 20001222 | AV-CB-1 | Aitkenvale-Cranbrook | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Power Factor | 0.64046 | 0.64056 | 0.64058 | 0.61678 | 0.61689 | 0.61691 | 0.59179 | 0.5919 | 0.59193 | 0.56491 | 0.56504 | 0.56503 | 0.54152 | 0.54171 | 0.54253
NQ | 20001222 | AV-CB-1 | Aitkenvale-Cranbrook | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Rating (A) | 333 | 390 | 363 | 333 | 390 | 363 | 333 | 390 | 363 | 333 | 390 | 363 | 333 | 390 | 363
NQ | 20001222 | AV-CB-1 | Aitkenvale-Cranbrook | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Time | 16:30 | 17:00 | 7:30 | 16:30 | 17:00 | 7:30 | 16:30 | 17:00 | 7:00 | 16:30 | 17:00 | 7:30 | 16:30 | 17:00 | 7:30
NQ | 20001222 | AV-CB-1 | Aitkenvale-Cranbrook | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Voltage at Constrained Conductor | 69.5496 | 69.5512 | 69.5487 | 69.577 | 69.5786 | 69.576 | 69.5986 | 69.6001 | 69.5983 | 69.6162 | 69.6178 | 69.6163 | 69.6312 | 69.6317 | 69.6352
NQ | 20001857 | AY-HH-1 | AYR-HOMEHILL/JARVISFIELD | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | % of Rated A | 51.9135 | 45.4041 | 49.2581 | 52.9364 | 46.2987 | 50.2287 | 53.8521 | 47.0994 | 51.0911 | 54.9315 | 48.0433 | 52.1141 | 55.934 | 48.9266 | 53.0725
NQ | 20001857 | AY-HH-1 | AYR-HOMEHILL/JARVISFIELD | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Limiting Line Name | TR_LINE 33601_1 | TR_LINE 33601_1 | TR_LINE 33601_1 | TR_LINE 33601_1 | TR_LINE 33601_1 | TR_LINE 33601_1 | TR_LINE 33601_1 | TR_LINE 33601_1 | TR_LINE 33601_1 | TR_LINE 159617_1 | TR_LINE 159617_1 | TR_LINE 159617_1 | TR_LINE 31671_1 | TR_LINE 31671_1 | TR_LINE 31671_1
NQ | 20001857 | AY-HH-1 | AYR-HOMEHILL/JARVISFIELD | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Loading (A) | 133.935 | 133.9402 | 133.9801 | 136.5748 | 136.5801 | 136.6209 | 138.9381 | 138.9429 | 138.9676 | 141.723 | 141.7276 | 141.7501 | 144.3096 | 144.3335 | 144.3573
NQ | 20001857 | AY-HH-1 | AYR-HOMEHILL/JARVISFIELD | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Loading (MVA) | 16.4809 | 16.4825 | 16.4853 | 16.8231 | 16.8248 | 16.8275 | 17.1311 | 17.1328 | 17.1341 | 17.5792 | 17.5809 | 17.5837 | 17.9177 | 17.9193 | 17.9221
NQ | 20001857 | AY-HH-1 | AYR-HOMEHILL/JARVISFIELD | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Loading (MW) | 16.4804 | 16.4821 | 16.4848 | 16.823 | 16.8246 | 16.8273 | 17.1311 | 17.1328 | 17.1341 | 17.5792 | 17.5808 | 17.5837 | 17.9177 | 17.9193 | 17.9221
NQ | 20001857 | AY-HH-1 | AYR-HOMEHILL/JARVISFIELD | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Power Factor | 0.99997 | 0.99997 | 0.99997 | 0.99999 | 0.99999 | 0.99999 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
NQ | 20001857 | AY-HH-1 | AYR-HOMEHILL/JARVISFIELD | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Rating (A) | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272
NQ | 20001857 | AY-HH-1 | AYR-HOMEHILL/JARVISFIELD | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Time | 16:30 | 17:00 | 7:30 | 16:30 | 17:00 | 7:30 | 16:30 | 17:00 | 7:00 | 16:30 | 17:00 | 7:30 | 16:30 | 17:00 | 7:30
NQ | 20001857 | AY-HH-1 | AYR-HOMEHILL/JARVISFIELD | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Voltage at Constrained Conductor | 71.0436 | 71.0481 | 71.0387 | 71.1173 | 71.1217 | 71.1118 | 71.1874 | 71.1919 | 71.1849 | 71.614 | 71.6185 | 71.6188 | 71.6846 | 71.6791 | 71.6786
NQ | 20003134 | BO-DG-1 | Bohle-Dan Gleeson | BO-DG-1_Bohle-Dan Gleeson 66 kV | % of Rated A | 77.5784 | 77.5348 | 77.5675 | 81.048 | 81.0041 | 81.0371 | 84.2572 | 84.2116 | 84.2462 | 87.1904 | 87.1444 | 87.1793 | 89.6349 | 89.6 | 89.6227
NQ | 20003134 | BO-DG-1 | Bohle-Dan Gleeson | BO-DG-1_Bohle-Dan Gleeson 66 kV | Limiting Line Name | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1
NQ | 20003134 | BO-DG-1 | Bohle-Dan Gleeson | BO-DG-1_Bohle-Dan Gleeson 66 kV | Loading (A) | 346.7756 | 346.5807 | 346.7269 | 362.2846 | 362.0882 | 362.2357 | 376.6298 | 376.4257 | 376.5806 | 389.7409 | 389.5354 | 389.6915 | 400.6678 | 400.5121 | 400.6133
NQ | 20003134 | BO-DG-1 | Bohle-Dan Gleeson | BO-DG-1_Bohle-Dan Gleeson 66 kV | Loading (MVA) | 41.7116 | 41.6916 | 41.7063 | 43.5906 | 43.5706 | 43.5852 | 45.3277 | 45.3062 | 45.3223 | 46.9135 | 46.8919 | 46.9081 | 48.2353 | 48.2189 | 48.2319
NQ | 20003134 | BO-DG-1 | Bohle-Dan Gleeson | BO-DG-1_Bohle-Dan Gleeson 66 kV | Loading (MW) | 41.4817 | 41.4628 | 41.4766 | 43.3593 | 43.3404 | 43.3542 | 45.092 | 45.0717 | 45.0869 | 46.6713 | 46.651 | 46.6662 | 47.9861 | 47.9706 | 47.9827
NQ | 20003134 | BO-DG-1 | Bohle-Dan Gleeson | BO-DG-1_Bohle-Dan Gleeson 66 kV | Power Factor | 0.99449 | 0.99451 | 0.99449 | 0.99469 | 0.99472 | 0.9947 | 0.9948 | 0.99482 | 0.9948 | 0.99484 | 0.99486 | 0.99484 | 0.99483 | 0.99485 | 0.99483
NQ | 20003134 | BO-DG-1 | Bohle-Dan Gleeson | BO-DG-1_Bohle-Dan Gleeson 66 kV | Rating (A) | 447 | 447 | 447 | 447 | 447 | 447 | 447 | 447 | 447 | 447 | 447 | 447 | 447 | 447 | 447
NQ | 20003134 | BO-DG-1 | Bohle-Dan Gleeson | BO-DG-1_Bohle-Dan Gleeson 66 kV | Time | 11:00 | 17:00 | 8:30 | 11:00 | 17:00 | 8:30 | 11:00 | 17:00 | 8:30 | 11:00 | 17:00 | 8:30 | 16:00 | 17:00 | 8:30
NQ | 20003134 | BO-DG-1 | Bohle-Dan Gleeson | BO-DG-1_Bohle-Dan Gleeson 66 kV | Voltage at Constrained Conductor | 69.4461 | 69.4519 | 69.4469 | 69.4676 | 69.4734 | 69.4685 | 69.4846 | 69.4893 | 69.4854 | 69.4962 | 69.5009 | 69.497 | 69.5057 | 69.509 | 69.5101
NQ | 20003135 | 6127 | BOHLE-BLACK RIVER 1 | 6127_Bohle-Black River 1 66 kV | % of Rated A | 52.9244 | 49.2702 | 54.34 | 54.1732 | 50.4327 | 55.6222 | 55.3546 | 51.5333 | 56.8352 | 56.4748 | 52.5762 | 57.9854 | 57.4852 | 53.518 | 59.0212
NQ | 20003135 | 6127 | BOHLE-BLACK RIVER 1 | 6127_Bohle-Black River 1 66 kV | Limiting Line Name | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1
NQ | 20003135 | 6127 | BOHLE-BLACK RIVER 1 | 6127_Bohle-Black River 1 66 kV | Loading (A) | 385.8192 | 385.7855 | 385.8142 | 394.9223 | 394.8878 | 394.9173 | 403.535 | 403.506 | 403.5298 | 411.7014 | 411.6717 | 411.6961 | 419.0669 | 419.0458 | 419.0503
NQ | 20003135 | 6127 | BOHLE-BLACK RIVER 1 | 6127_Bohle-Black River 1 66 kV | Loading (MVA) | 46.7675 | 46.7674 | 46.7675 | 47.9069 | 47.9068 | 47.9069 | 48.9826 | 48.9825 | 48.9825 | 49.999 | 49.9989 | 49.999 | 50.9143 | 50.9142 | 50.9142
NQ | 20003135 | 6127 | BOHLE-BLACK RIVER 1 | 6127_Bohle-Black River 1 66 kV | Loading (MW) | 46.1665 | 46.1665 | 46.1665 | 47.3146 | 47.3147 | 47.3147 | 48.396 | 48.3961 | 48.3961 | 49.4158 | 49.4158 | 49.4158 | 50.3324 | 50.3324 | 50.3324
NQ | 20003135 | 6127 | BOHLE-BLACK RIVER 1 | 6127_Bohle-Black River 1 66 kV | Power Factor | 0.98715 | 0.98715 | 0.98715 | 0.98764 | 0.98764 | 0.98764 | 0.98803 | 0.98803 | 0.98803 | 0.98834 | 0.98834 | 0.98834 | 0.98857 | 0.98857 | 0.98857
NQ | 20003135 | 6127 | BOHLE-BLACK RIVER 1 | 6127_Bohle-Black River 1 66 kV | Rating (A) | 729 | 783 | 710 | 729 | 783 | 710 | 729 | 783 | 710 | 729 | 783 | 710 | 729 | 783 | 710
NQ | 20003135 | 6127 | BOHLE-BLACK RIVER 1 | 6127_Bohle-Black River 1 66 kV | Time | 11:00 | 17:00 | 8:30 | 11:00 | 17:00 | 8:30 | 11:00 | 17:00 | 8:30 | 11:00 | 17:00 | 8:30 | 16:00 | 17:00 | 7:00
NQ | 20003135 | 6127 | BOHLE-BLACK RIVER 1 | 6127_Bohle-Black River 1 66 kV | Voltage at Constrained Conductor | 69.9842 | 69.9901 | 69.9851 | 70.0367 | 70.0427 | 70.0376 | 70.0809 | 70.0858 | 70.0818 | 70.1162 | 70.1211 | 70.1171 | 70.1448 | 70.1483 | 70.1475
NQ | 20003596 | CH-CC-1 | CHUMVALE-CLONCURRY | CH-CC-1_Chumvale-Cloncurry 66 kV | % of Rated A | 3.9331 | 3.5225 | 3.7273 | 2.9078 | 2.6042 | 2.7556 | 1.9939 | 1.7858 | 1.8896 | 1.7306 | 1.5499 | 1.64 | 1.7865 | 1.5339 | 1.6069
NQ | 20003596 | CH-CC-1 | CHUMVALE-CLONCURRY | CH-CC-1_Chumvale-Cloncurry 66 kV | Limiting Line Name | TR_LINE 34857_1 | TR_LINE 34857_1 | TR_LINE 34857_1 | TR_LINE 34857_1 | TR_LINE 34857_1 | TR_LINE 34857_1 | TR_LINE 172154_1 | TR_LINE 172154_1 | TR_LINE 172154_1 | TR_LINE 172154_1 | TR_LINE 172154_1 | TR_LINE 172154_1 | TR_LINE 34531_1 | TR_LINE 34531_1 | TR_LINE 34531_1
NQ | 20003596 | CH-CC-1 | CHUMVALE-CLONCURRY | CH-CC-1_Chumvale-Cloncurry 66 kV | Loading (A) | 6.4109 | 6.4109 | 6.4109 | 4.7397 | 4.7397 | 4.7397 | 3.2501 | 3.2501 | 3.2501 | 2.8209 | 2.8209 | 2.8209 | 3.0371 | 3.0371 | 3.0371
NQ | 20003596 | CH-CC-1 | CHUMVALE-CLONCURRY | CH-CC-1_Chumvale-Cloncurry 66 kV | Loading (MVA) | 1.0293 | 1.0293 | 1.0293 | 0.76132 | 0.76132 | 0.76132 | 0.52215 | 0.52215 | 0.52215 | 0.45338 | 0.45338 | 0.45338 | 0.4881 | 0.4881 | 0.4881
NQ | 20003596 | CH-CC-1 | CHUMVALE-CLONCURRY | CH-CC-1_Chumvale-Cloncurry 66 kV | Loading (MW) | 0.98677 | 0.98677 | 0.98677 | 0.70198 | 0.70198 | 0.70198 | 0.52214 | 0.52214 | 0.52214 | 0.45337 | 0.45337 | 0.45337 | 0.48048 | 0.48048 | 0.48048
NQ | 20003596 | CH-CC-1 | CHUMVALE-CLONCURRY | CH-CC-1_Chumvale-Cloncurry 66 kV | Power Factor | 0.9587 | 0.9587 | 0.9587 | 0.92206 | 0.92206 | 0.92206 | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 0.9844 | 0.9844 | 0.9844
NQ | 20003596 | CH-CC-1 | CHUMVALE-CLONCURRY | CH-CC-1_Chumvale-Cloncurry 66 kV | Rating (A) | 163 | 182 | 172 | 163 | 182 | 172 | 163 | 182 | 172 | 163 | 182 | 172 | 170 | 198 | 189
NQ | 20003596 | CH-CC-1 | CHUMVALE-CLONCURRY | CH-CC-1_Chumvale-Cloncurry 66 kV | Time | 9:00 | 17:00 | 0:00 | 9:00 | 17:00 | 0:00 | 9:00 | 17:00 | 0:00 | 9:00 | 17:00 | 0:00 | 9:00 | 17:00 | 0:00
NQ | 20003596 | CH-CC-1 | CHUMVALE-CLONCURRY | CH-CC-1_Chumvale-Cloncurry 66 kV | Voltage at Constrained Conductor | 92.6944 | 92.6944 | 92.6944 | 92.7373 | 92.7373 | 92.7373 | 92.755 | 92.755 | 92.755 | 92.7926 | 92.7926 | 92.7926 | 92.7871 | 92.7871 | 92.7871
NQ | 20003732 | CHTO | CLARESOUTH-CHARTERSTOWERS | CHTO_Clare South - Charters Towers 66 kV | % of Rated A | 72.222 | 64.3617 | 70.4428 | 73.1858 | 65.2199 | 71.3966 | 73.6716 | 65.6728 | 71.8648 | 74.1394 | 66.1088 | 72.2089 | 74.0708 | 66.125 | 72.2594
NQ | 20003732 | CHTO | CLARESOUTH-CHARTERSTOWERS | CHTO_Clare South - Charters Towers 66 kV | Limiting Line Name | TR_LINE 33612_1 | TR_LINE 33612_1 | TR_LINE 33612_1 | TR_LINE 33612_1 | TR_LINE 33612_1 | TR_LINE 33612_1 | TR_LINE 33612_1 | TR_LINE 33612_1 | TR_LINE 33612_1 | TR_LINE 33612_1 | TR_LINE 33612_1 | TR_LINE 33612_1 | TR_LINE 33612_1 | TR_LINE 33612_1 | TR_LINE 33612_1
NQ | 20003732 | CHTO | CLARESOUTH-CHARTERSTOWERS | CHTO_Clare South - Charters Towers 66 kV | Loading (A) | 143.7211 | 143.5259 | 143.7025 | 145.639 | 145.4397 | 145.6483 | 146.6058 | 146.4495 | 146.6035 | 147.5367 | 147.422 | 147.3053 | 147.4001 | 147.4581 | 147.4084
NQ | 20003732 | CHTO | CLARESOUTH-CHARTERSTOWERS | CHTO_Clare South - Charters Towers 66 kV | Loading (MVA) | 16.2681 | 16.2678 | 16.2661 | 16.468 | 16.4678 | 16.468 | 16.5699 | 16.5697 | 16.5699 | 16.6699 | 16.6698 | 16.6697 | 16.6718 | 16.6698 | 16.6718
NQ | 20003732 | CHTO | CLARESOUTH-CHARTERSTOWERS | CHTO_Clare South - Charters Towers 66 kV | Loading (MW) | 16.2531 | 16.253 | 16.2519 | 16.4533 | 16.4531 | 16.4533 | 16.5545 | 16.5544 | 16.5545 | 16.6546 | 16.6545 | 16.6545 | 16.6557 | 16.6546 | 16.6558
NQ | 20003732 | CHTO | CLARESOUTH-CHARTERSTOWERS | CHTO_Clare South - Charters Towers 66 kV | Power Factor | 0.99908 | 0.99909 | 0.99913 | 0.9991 | 0.99911 | 0.9991 | 0.99907 | 0.99908 | 0.99907 | 0.99908 | 0.99908 | 0.99909 | 0.99904 | 0.99908 | 0.99904
NQ | 20003732 | CHTO | CLARESOUTH-CHARTERSTOWERS | CHTO_Clare South - Charters Towers 66 kV | Rating (A) | 199 | 223 | 204 | 199 | 223 | 204 | 199 | 223 | 204 | 199 | 223 | 204 | 199 | 223 | 204
NQ | 20003732 | CHTO | CLARESOUTH-CHARTERSTOWERS | CHTO_Clare South - Charters Towers 66 kV | Time | 9:00 | 17:00 | 7:30 | 9:00 | 17:00 | 7:30 | 16:00 | 17:00 | 7:00 | 16:30 | 17:00 | 7:30 | 9:00 | 17:00 | 7:30
NQ | 20003732 | CHTO | CLARESOUTH-CHARTERSTOWERS | CHTO_Clare South - Charters Towers 66 kV | Voltage at Constrained Conductor | 65.3513 | 65.4393 | 65.3519 | 65.2835 | 65.372 | 65.2793 | 65.254 | 65.3229 | 65.255 | 65.2339 | 65.2841 | 65.3353 | 65.3018 | 65.2683 | 65.2981
NQ | 20003733 | EAAY | CLARESOUTH-EASTAYR | EAAY_Clare South - East Ayr 66 kV | % of Rated A | 48.2276 | 32.1441 | 32.6645 | 51.1246 | 34.0753 | 34.6272 | 53.8981 | 35.9268 | 36.5073 | 56.541 | 37.6896 | 38.2955 | 58.7401 | 39.1564 | 39.7863
NQ | 20003733 | EAAY | CLARESOUTH-EASTAYR | EAAY_Clare South - East Ayr 66 kV | Limiting Line Name | TR_LINE 183529_1 | TR_LINE 183529_1 | TR_LINE 183529_1 | TR_LINE 183529_1 | TR_LINE 183529_1 | TR_LINE 183529_1 | TR_LINE 183529_1 | TR_LINE 183529_1 | TR_LINE 183529_1 | TR_LINE 183529_1 | TR_LINE 183529_1 | TR_LINE 183529_1 | TR_LINE 183529_1 | TR_LINE 183529_1 | TR_LINE 183529_1
NQ | 20003733 | EAAY | CLARESOUTH-EASTAYR | EAAY_Clare South - East Ayr 66 kV | Loading (A) | 101.2671 | 101.243 | 101.2491 | 107.3514 | 107.3269 | 107.334 | 113.1762 | 113.1595 | 113.1628 | 118.7267 | 118.713 | 118.7068 | 123.3452 | 123.3337 | 123.3283
NQ | 20003733 | EAAY | CLARESOUTH-EASTAYR | EAAY_Clare South - East Ayr 66 kV | Loading (MVA) | 12.4766 | 12.4745 | 12.4742 | 13.2382 | 13.2361 | 13.2358 | 13.9685 | 13.9672 | 13.9663 | 14.665 | 14.6643 | 14.6643 | 15.2473 | 15.2449 | 15.2449
NQ | 20003733 | EAAY | CLARESOUTH-EASTAYR | EAAY_Clare South - East Ayr 66 kV | Loading (MW) | 12.0303 | 12.0281 | 12.028 | 12.8122 | 12.81 | 12.8099 | 13.5607 | 13.5593 | 13.5586 | 14.2735 | 14.2727 | 14.2726 | 14.8684 | 14.8661 | 14.8661
NQ | 20003733 | EAAY | CLARESOUTH-EASTAYR | EAAY_Clare South - East Ayr 66 kV | Power Factor | 0.96423 | 0.96422 | 0.96423 | 0.96782 | 0.96781 | 0.96782 | 0.9708 | 0.9708 | 0.97081 | 0.97331 | 0.9733 | 0.97329 | 0.97515 | 0.97516 | 0.97515
NQ | 20003733 | EAAY | CLARESOUTH-EASTAYR | EAAY_Clare South - East Ayr 66 kV | Rating (A) | 210 | 315 | 310 | 210 | 315 | 310 | 210 | 315 | 310 | 210 | 315 | 310 | 210 | 315 | 310
NQ | 20003733 | EAAY | CLARESOUTH-EASTAYR | EAAY_Clare South - East Ayr 66 kV | Time | 14:00 | 17:00 | 8:30 | 14:00 | 17:00 | 8:30 | 16:00 | 17:00 | 7:00 | 16:30 | 17:00 | 8:30 | 14:00 | 17:00 | 8:30
NQ | 20003733 | EAAY | CLARESOUTH-EASTAYR | EAAY_Clare South - East Ayr 66 kV | Voltage at Constrained Conductor | 71.1326 | 71.1374 | 71.1315 | 71.197 | 71.2018 | 71.1955 | 71.2582 | 71.2621 | 71.2552 | 71.3138 | 71.3184 | 71.3222 | 71.3689 | 71.3644 | 71.3674
NQ | 20003734 | CLSO-HOHI-1 | CLARESOUTH-HOMEHILL NO.01 | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | % of Rated A | 26.8229 | 23.0434 | 24.8222 | 28.8151 | 24.7556 | 26.6668 | 30.7579 | 26.4283 | 28.4659 | 32.5613 | 27.9784 | 30.1353 | 34.0294 | 29.2402 | 31.4946
NQ | 20003734 | CLSO-HOHI-1 | CLARESOUTH-HOMEHILL NO.01 | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Limiting Line Name | TR_LINE 102266_1 | TR_LINE 102266_1 | TR_LINE 102266_1 | TR_LINE 102266_1 | TR_LINE 102266_1 | TR_LINE 102266_1 | TR_LINE 102266_1 | TR_LINE 102266_1 | TR_LINE 102266_1 | TR_LINE 102266_1 | TR_LINE 102266_1 | TR_LINE 102266_1 | TR_LINE 102266_1 | TR_LINE 102266_1 | TR_LINE 102266_1
NQ | 20003734 | CLSO-HOHI-1 | CLARESOUTH-HOMEHILL NO.01 | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Loading (A) | 83.6823 | 83.6426 | 83.6459 | 89.8984 | 89.8583 | 89.8626 | 95.9606 | 95.9305 | 95.9258 | 101.5875 | 101.5578 | 101.5521 | 106.1682 | 106.1382 | 106.1331
NQ | 20003734 | CLSO-HOHI-1 | CLARESOUTH-HOMEHILL NO.01 | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Loading (MVA) | 10.0434 | 10.0394 | 10.0389 | 10.7878 | 10.7838 | 10.7833 | 11.5152 | 11.5107 | 11.5091 | 12.1886 | 12.1842 | 12.1842 | 12.7365 | 12.7321 | 12.7321
NQ | 20003734 | CLSO-HOHI-1 | CLARESOUTH-HOMEHILL NO.01 | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Loading (MW) | 9.6804 | 9.6763 | 9.6761 | 10.4644 | 10.4603 | 10.4601 | 11.2259 | 11.2217 | 11.2202 | 11.9289 | 11.9247 | 11.9246 | 12.4993 | 12.4951 | 12.495
NQ | 20003734 | CLSO-HOHI-1 | CLARESOUTH-HOMEHILL NO.01 | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Power Factor | 0.96386 | 0.96383 | 0.96386 | 0.97002 | 0.97 | 0.97002 | 0.97488 | 0.97489 | 0.97491 | 0.97869 | 0.9787 | 0.9787 | 0.98137 | 0.98138 | 0.98138
NQ | 20003734 | CLSO-HOHI-1 | CLARESOUTH-HOMEHILL NO.01 | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Rating (A) | 312 | 363 | 337 | 312 | 363 | 337 | 312 | 363 | 337 | 312 | 363 | 337 | 312 | 363 | 337
NQ | 20003734 | CLSO-HOHI-1 | CLARESOUTH-HOMEHILL NO.01 | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Time | 14:00 | 17:00 | 8:30 | 14:00 | 17:00 | 8:30 | 14:00 | 17:00 | 7:00 | 14:00 | 17:00 | 8:30 | 14:00 | 17:00 | 8:30
NQ | 20003734 | CLSO-HOHI-1 | CLARESOUTH-HOMEHILL NO.01 | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Voltage at Constrained Conductor | 69.2925 | 69.2976 | 69.2918 | 69.2819 | 69.287 | 69.2808 | 69.2815 | 69.2766 | 69.2697 | 69.2714 | 69.2665 | 69.2703 | 69.2621 | 69.2579 | 69.261
NQ | 20003735 | CLSO-HOHI-2 | CLARESOUTH-HOMEHILL NO.02 | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | % of Rated A | 47.2947 | 33.4266 | 34.2888 | 50.8619 | 35.9489 | 36.8765 | 54.3373 | 38.4106 | 39.3978 | 57.5613 | 40.6905 | 41.7359 | 60.1846 | 42.5453 | 43.6388
NQ | 20003735 | CLSO-HOHI-2 | CLARESOUTH-HOMEHILL NO.02 | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Limiting Line Name | TR_LINE 147761_2 | TR_LINE 147761_2 | TR_LINE 147761_2 | TR_LINE 147761_2 | TR_LINE 147761_2 | TR_LINE 147761_2 | TR_LINE 147761_2 | TR_LINE 147761_2 | TR_LINE 147761_2 | TR_LINE 147761_2 | TR_LINE 147761_2 | TR_LINE 147761_2 | TR_LINE 147761_2 | TR_LINE 147761_2 | TR_LINE 147761_2
NQ | 20003735 | CLSO-HOHI-2 | CLARESOUTH-HOMEHILL NO.02 | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Loading (A) | 79.9214 | 79.883 | 79.8864 | 85.9507 | 85.9119 | 85.9163 | 91.8247 | 91.7959 | 91.7916 | 97.2737 | 97.2454 | 97.2398 | 101.7076 | 101.6788 | 101.6738
NQ | 20003735 | CLSO-HOHI-2 | CLARESOUTH-HOMEHILL NO.02 | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Loading (MVA) | 9.7279 | 9.7239 | 9.7235 | 10.4677 | 10.4637 | 10.4633 | 11.1907 | 11.1864 | 11.1847 | 11.8605 | 11.8562 | 11.8561 | 12.4057 | 12.4014 | 12.4013
NQ | 20003735 | CLSO-HOHI-2 | CLARESOUTH-HOMEHILL NO.02 | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Loading (MW) | 9.5364 | 9.5323 | 9.5321 | 10.3028 | 10.2987 | 10.2985 | 11.0482 | 11.044 | 11.0425 | 11.7369 | 11.7327 | 11.7326 | 12.2961 | 12.2919 | 12.2918
NQ | 20003735 | CLSO-HOHI-2 | CLARESOUTH-HOMEHILL NO.02 | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Power Factor | 0.98031 | 0.9803 | 0.98032 | 0.98424 | 0.98423 | 0.98425 | 0.98726 | 0.98727 | 0.98728 | 0.98958 | 0.98958 | 0.98958 | 0.99117 | 0.99118 | 0.99117
NQ | 20003735 | CLSO-HOHI-2 | CLARESOUTH-HOMEHILL NO.02 | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Rating (A) | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233
NQ | 20003735 | CLSO-HOHI-2 | CLARESOUTH-HOMEHILL NO.02 | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Time | 14:00 | 17:00 | 8:30 | 14:00 | 17:00 | 8:30 | 14:00 | 17:00 | 7:00 | 14:00 | 17:00 | 8:30 | 14:00 | 17:00 | 8:30
NQ | 20003735 | CLSO-HOHI-2 | CLARESOUTH-HOMEHILL NO.02 | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Voltage at Constrained Conductor | 70.274 | 70.2787 | 70.2728 | 70.3139 | 70.3186 | 70.3123 | 70.362 | 70.3567 | 70.3497 | 70.3959 | 70.3906 | 70.3944 | 70.4217 | 70.4171 | 70.4202
NQ | 20003736 | CS-ML-1 | CLARESOUTH-MILLAROO | CS-ML-1_Clare South - Millaroo 66 kV | % of Rated A | 2.6613 | 2.383 | 2.6105 | 3.0147 | 2.6977 | 2.9553 | 3.2284 | 2.888 | 3.1637 | 3.3575 | 3.0032 | 3.29 | 3.4234 | 3.0623 | 3.3546
NQ | 20003736 | CS-ML-1 | CLARESOUTH-MILLAROO | CS-ML-1_Clare South - Millaroo 66 kV | Limiting Line Name | TR_LINE 102260_1 | TR_LINE 102260_1 | TR_LINE 102260_1 | TR_LINE 102260_1 | TR_LINE 102260_1 | TR_LINE 102260_1 | TR_LINE 102260_1 | TR_LINE 102260_1 | TR_LINE 102260_1 | TR_LINE 102260_1 | TR_LINE 102260_1 | TR_LINE 102260_1 | TR_LINE 102260_1 | TR_LINE 102260_1 | TR_LINE 102260_1
NQ | 20003736 | CS-ML-1 | CLARESOUTH-MILLAROO | CS-ML-1_Clare South - Millaroo 66 kV | Loading (A) | 5.1895 | 5.195 | 5.195 | 5.8787 | 5.881 | 5.881 | 6.2953 | 6.2958 | 6.2958 | 6.5471 | 6.5471 | 6.5471 | 6.6757 | 6.6757 | 6.6757
NQ | 20003736 | CS-ML-1 | CLARESOUTH-MILLAROO | CS-ML-1_Clare South - Millaroo 66 kV | Loading (MVA) | 0.62273 | 0.62463 | 0.62463 | 0.70533 | 0.707 | 0.70701 | 0.75529 | 0.75676 | 0.75676 | 0.78526 | 0.78531 | 0.78532 | 0.80068 | 0.80064 | 0.80064
NQ | 20003736 | CS-ML-1 | CLARESOUTH-MILLAROO | CS-ML-1_Clare South - Millaroo 66 kV | Loading (MW) | 0.30549 | 0.30549 | 0.30549 | 0.45146 | 0.45146 | 0.45146 | 0.52647 | 0.52647 | 0.52647 | 0.5691 | 0.5691 | 0.5691 | 0.59027 | 0.59027 | 0.59027
NQ | 20003736 | CS-ML-1 | CLARESOUTH-MILLAROO | CS-ML-1_Clare South - Millaroo 66 kV | Power Factor | 0.49057 | 0.48908 | 0.48907 | 0.64007 | 0.63856 | 0.63855 | 0.69705 | 0.69569 | 0.69569 | 0.72473 | 0.72468 | 0.72468 | 0.73721 | 0.73725 | 0.73725
NQ | 20003736 | CS-ML-1 | CLARESOUTH-MILLAROO | CS-ML-1_Clare South - Millaroo 66 kV | Rating (A) | 195 | 218 | 199 | 195 | 218 | 199 | 195 | 218 | 199 | 195 | 218 | 199 | 195 | 218 | 199
NQ | 20003736 | CS-ML-1 | CLARESOUTH-MILLAROO | CS-ML-1_Clare South - Millaroo 66 kV | Time | 16:00 | 20:00 | 4:00 | 16:00 | 20:00 | 4:00 | 14:30 | 20:00 | 4:00 | 16:30 | 17:00 | 7:30 | 9:00 | 17:00 | 7:30
NQ | 20003736 | CS-ML-1 | CLARESOUTH-MILLAROO | CS-ML-1_Clare South - Millaroo 66 kV | Voltage at Constrained Conductor | 69.281 | 69.4192 | 69.4194 | 69.2699 | 69.4084 | 69.4086 | 69.2678 | 69.3979 | 69.3981 | 69.2475 | 69.2523 | 69.2529 | 69.2472 | 69.2432 | 69.2431
NQ | 20003737 | MOPA | CLARESOUTH-MONAPARK | MOPA_Clare South - Mona Park 66 kV | % of Rated A | 54.7468 | 36.4903 | 37.0812 | 58.194 | 38.7883 | 39.4166 | 61.5266 | 41.0124 | 41.6755 | 64.6421 | 43.0901 | 43.7829 | 67.1332 | 44.7525 | 45.4724
NQ | 20003737 | MOPA | CLARESOUTH-MONAPARK | MOPA_Clare South - Mona Park 66 kV | Limiting Line Name | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1
NQ | 20003737 | MOPA | CLARESOUTH-MONAPARK | MOPA_Clare South - Mona Park 66 kV | Loading (A) | 114.967 | 114.9432 | 114.9504 | 122.2061 | 122.1819 | 122.1903 | 129.2047 | 129.1879 | 129.1931 | 135.7473 | 135.7329 | 135.7259 | 140.9787 | 140.9693 | 140.9634
NQ | 20003737 | MOPA | CLARESOUTH-MONAPARK | MOPA_Clare South - Mona Park 66 kV | Loading (MVA) | 13.7962 | 13.7944 | 13.7941 | 14.6626 | 14.6607 | 14.6604 | 15.5001 | 15.499 | 15.4981 | 16.2823 | 16.2817 | 16.2818 | 16.9098 | 16.9077 | 16.9077
NQ | 20003737 | MOPA | CLARESOUTH-MONAPARK | MOPA_Clare South - Mona Park 66 kV | Loading (MW) | 13.5234 | 13.5214 | 13.5213 | 14.4171 | 14.4152 | 14.415 | 15.2791 | 15.2779 | 15.2771 | 16.0828 | 16.0821 | 16.0821 | 16.7265 | 16.7245 | 16.7244
NQ | 20003737 | MOPA | CLARESOUTH-MONAPARK | MOPA_Clare South - Mona Park 66 kV | Power Factor | 0.98022 | 0.98021 | 0.98023 | 0.98326 | 0.98325 | 0.98326 | 0.98574 | 0.98574 | 0.98574 | 0.98775 | 0.98774 | 0.98774 | 0.98916 | 0.98916 | 0.98916
NQ | 20003737 | MOPA | CLARESOUTH-MONAPARK | MOPA_Clare South - Mona Park 66 kV | Rating (A) | 210 | 315 | 310 | 210 | 315 | 310 | 210 | 315 | 310 | 210 | 315 | 310 | 210 | 315 | 310
NQ | 20003737 | MOPA | CLARESOUTH-MONAPARK | MOPA_Clare South - Mona Park 66 kV | Time | 14:00 | 17:00 | 8:30 | 14:00 | 17:00 | 8:30 | 16:00 | 17:00 | 7:00 | 16:30 | 17:00 | 8:30 | 14:00 | 17:00 | 8:30
NQ | 20003737 | MOPA | CLARESOUTH-MONAPARK | MOPA_Clare South - Mona Park 66 kV | Voltage at Constrained Conductor | 69.2829 | 69.288 | 69.2822 | 69.2718 | 69.277 | 69.2707 | 69.262 | 69.2661 | 69.2593 | 69.2508 | 69.2556 | 69.2594 | 69.2508 | 69.2467 | 69.2497
NQ | 20004005 | CR-HU-1 | CAPERIVER-HUGHENDEN NO.01 | CR-HU-1_Cape River-Hughenden No 1 66 kV | % of Rated A | 104.1872 | 68.4814 | 71.2875 | 105.1526 | 69.1323 | 71.9479 | 105.999 | 69.6575 | 72.527 | 106.6194 | 70.0765 | 72.9515 | 106.5488 | 70.3722 | 72.9048
NQ | 20004005 | CR-HU-1 | CAPERIVER-HUGHENDEN NO.01 | CR-HU-1_Cape River-Hughenden No 1 66 kV | Limiting Line Name | TR_LINE 32874_1 | TR_LINE 32874_1 | TR_LINE 32874_1 | TR_LINE 32874_1 | TR_LINE 32874_1 | TR_LINE 32874_1 | TR_LINE 32874_1 | TR_LINE 32874_1 | TR_LINE 32874_1 | TR_LINE 32874_1 | TR_LINE 32874_1 | TR_LINE 32874_1 | TR_LINE 32874_1 | TR_LINE 32874_1 | TR_LINE 32874_1
NQ | 20004005 | CR-HU-1 | CAPERIVER-HUGHENDEN NO.01 | CR-HU-1_Cape River-Hughenden No 1 66 kV | Loading (A) | 148.9877 | 145.1805 | 148.9909 | 150.3683 | 146.5606 | 150.3711 | 151.5786 | 147.674 | 151.5814 | 152.4658 | 148.5621 | 152.4686 | 152.3649 | 149.1891 | 152.3709
NQ | 20004005 | CR-HU-1 | CAPERIVER-HUGHENDEN NO.01 | CR-HU-1_Cape River-Hughenden No 1 66 kV | Loading (MVA) | 17.337 | 16.8932 | 17.3375 | 17.5007 | 17.0569 | 17.5011 | 17.6482 | 17.1889 | 17.6487 | 17.7534 | 17.2943 | 17.7538 | 17.7464 | 17.3686 | 17.7475
NQ | 20004005 | CR-HU-1 | CAPERIVER-HUGHENDEN NO.01 | CR-HU-1_Cape River-Hughenden No 1 66 kV | Loading (MW) | 15.5579 | 15.0783 | 15.5576 | 15.7374 | 15.2577 | 15.7371 | 15.8717 | 15.4023 | 15.8714 | 15.9867 | 15.5173 | 15.9864 | 15.9023 | 15.5983 | 15.9017
NQ | 20004005 | CR-HU-1 | CAPERIVER-HUGHENDEN NO.01 | CR-HU-1_Cape River-Hughenden No 1 66 kV | Power Factor | 0.89738 | 0.89256 | 0.89734 | 0.89924 | 0.89452 | 0.8992 | 0.89934 | 0.89606 | 0.8993 | 0.90049 | 0.89725 | 0.90045 | 0.89609 | 0.89807 | 0.896
NQ | 20004005 | CR-HU-1 | CAPERIVER-HUGHENDEN NO.01 | CR-HU-1_Cape River-Hughenden No 1 66 kV | Rating (A) | 143 | 212 | 209 | 143 | 212 | 209 | 143 | 212 | 209 | 143 | 212 | 209 | 143 | 212 | 209
NQ | 20004005 | CR-HU-1 | CAPERIVER-HUGHENDEN NO.01 | CR-HU-1_Cape River-Hughenden No 1 66 kV | Time | 9:00 | 17:00 | 7:30 | 9:00 | 17:00 | 7:30 | 9:00 | 17:00 | 7:30 | 9:00 | 17:00 | 7:30 | 9:00 | 17:00 | 7:30
NQ | 20004005 | CR-HU-1 | CAPERIVER-HUGHENDEN NO.01 | CR-HU-1_Cape River-Hughenden No 1 66 kV | Voltage at Constrained Conductor | 67.1837 | 67.1806 | 67.1842 | 67.1952 | 67.1929 | 67.1956 | 67.2206 | 67.2024 | 67.2211 | 67.2276 | 67.2099 | 67.2281 | 67.2458 | 67.2152 | 67.2471
NQ | 20004647 | CT-CR-1 | CHARTERSTOWERS-CAPERIVER | CT-CR-1_Charters Towers-CARI No 1 66 kV | % of Rated A | 150.8661 | 136.7065 | 154.2559 | 151.8143 | 137.5817 | 155.2226 | 153.0394 | 138.2976 | 156.475 | 153.6741 | 138.8862 | 157.1238 | 153.6005 | 139.3133 | 156.9357
NQ | 20004647 | CT-CR-1 | CHARTERSTOWERS-CAPERIVER | CT-CR-1_Charters Towers-CARI No 1 66 kV | Limiting Line Name | TR_LINE 64803_1 | TR_LINE 64803_1 | TR_LINE 64803_1 | TR_LINE 64803_1 | TR_LINE 64803_1 | TR_LINE 64803_1 | TR_LINE 64803_1 | TR_LINE 64803_1 | TR_LINE 64803_1 | TR_LINE 64803_1 | TR_LINE 64803_1 | TR_LINE 64803_1 | TR_LINE 64803_1 | TR_LINE 64803_1 | TR_LINE 64803_1
NQ | 20004647 | CT-CR-1 | CHARTERSTOWERS-CAPERIVER | CT-CR-1_Charters Towers-CARI No 1 66 kV | Loading (A) | 277.5937 | 273.413 | 277.6606 | 279.3383 | 275.1635 | 279.4007 | 281.5926 | 276.5952 | 281.6551 | 282.7603 | 277.7724 | 282.8228 | 282.6248 | 278.6267 | 282.4842
NQ | 20004647 | CT-CR-1 | CHARTERSTOWERS-CAPERIVER | CT-CR-1_Charters Towers-CARI No 1 66 kV | Loading (MVA) | 30.6558 | 30.2594 | 30.6646 | 30.8247 | 30.4303 | 30.8328 | 31.1002 | 30.5699 | 31.1083 | 31.214 | 30.6856 | 31.2222 | 31.2054 | 30.7699 | 31.1939
NQ | 20004647 | CT-CR-1 | CHARTERSTOWERS-CAPERIVER | CT-CR-1_Charters Towers-CARI No 1 66 kV | Loading (MW) | 24.1458 | 23.6918 | 24.1494 | 24.3344 | 23.8817 | 24.3381 | 24.4474 | 24.0367 | 24.451 | 24.5722 | 24.1622 | 24.5758 | 24.5545 | 24.2521 | 24.5368
NQ | 20004647 | CT-CR-1 | CHARTERSTOWERS-CAPERIVER | CT-CR-1_Charters Towers-CARI No 1 66 kV | Power Factor | 0.78764 | 0.78296 | 0.78753 | 0.78944 | 0.7848 | 0.78936 | 0.78608 | 0.78629 | 0.786 | 0.78722 | 0.78741 | 0.78713 | 0.78687 | 0.78818 | 0.78659
NQ | 20004647 | CT-CR-1 | CHARTERSTOWERS-CAPERIVER | CT-CR-1_Charters Towers-CARI No 1 66 kV | Rating (A) | 184 | 200 | 180 | 184 | 200 | 180 | 184 | 200 | 180 | 184 | 200 | 180 | 184 | 200 | 180
NQ | 20004647 | CT-CR-1 | CHARTERSTOWERS-CAPERIVER | CT-CR-1_Charters Towers-CARI No 1 66 kV | Time | 9:00 | 17:00 | 7:30 | 9:00 | 17:00 | 7:30 | 9:00 | 17:00 | 7:30 | 9:00 | 17:00 | 7:30 | 16:00 | 17:00 | 7:00
NQ | 20004647 | CT-CR-1 | CHARTERSTOWERS-CAPERIVER | CT-CR-1_Charters Towers-CARI No 1 66 kV | Voltage at Constrained Conductor | 63.7592 | 63.897 | 63.762 | 63.71 | 63.8491 | 63.7125 | 63.7649 | 63.8101 | 63.7674 | 63.7339 | 63.78 | 63.7365 | 63.7468 | 63.7592 | 63.7552
NQ | 20004649 | CT-MR-1 | MILLCHESTER-CHARTERSTOWERS | CT-MR-1_Millchester-CHTO No 1 66 kV | % of Rated A | 41.5363 | 37.0812 | 40.6109 | 41.5021 | 37.0327 | 40.5856 | 43.7315 | 37.0497 | 42.7701 | 43.7422 | 37.0751 | 42.7784 | 43.7368 | 37.0962 | 42.7005
NQ | 20004649 | CT-MR-1 | MILLCHESTER-CHARTERSTOWERS | CT-MR-1_Millchester-CHTO No 1 66 kV | Limiting Line Name | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1
NQ | 20004649 | CT-MR-1 | MILLCHESTER-CHARTERSTOWERS | CT-MR-1_Millchester-CHTO No 1 66 kV | Loading (A) | 115.4608 | 115.3124 | 115.3249 | 115.3657 | 115.1616 | 115.2532 | 121.5635 | 115.2145 | 121.4572 | 121.5934 | 115.2936 | 121.4806 | 121.5783 | 115.3591 | 121.2593
NQ | 20004649 | CT-MR-1 | MILLCHESTER-CHARTERSTOWERS | CT-MR-1_Millchester-CHTO No 1 66 kV | Loading (MVA) | 13.1116 | 13.1355 | 13.0969 | 13.0865 | 13.1042 | 13.0741 | 13.8467 | 13.0988 | 13.8351 | 13.8412 | 13.0995 | 13.8288 | 13.8444 | 13.1016 | 13.8114
NQ | 20004649 | CT-MR-1 | MILLCHESTER-CHARTERSTOWERS | CT-MR-1_Millchester-CHTO No 1 66 kV | Loading (MW) | 0.40029 | 0.6805 | 0.45201 | 0.045002 | 0.32489 | 0.096031 | 0.18546 | 0.0036957 | 0.23665 | 0.052315 | 0.23487 | 0.0011766 | 0.18331 | 0.43756 | 0.030198
NQ | 20004649 | CT-MR-1 | MILLCHESTER-CHARTERSTOWERS | CT-MR-1_Millchester-CHTO No 1 66 kV | Power Factor | 0.030529 | 0.051806 | 0.034512 | 0.0034388 | 0.024793 | 0.0073451 | 0.013394 | 0.00028214 | 0.017105 | 0.0037797 | 0.01793 | 8.5081e-05 | 0.013241 | 0.033397 | 0.0021864
NQ | 20004649 | CT-MR-1 | MILLCHESTER-CHARTERSTOWERS | CT-MR-1_Millchester-CHTO No 1 66 kV | Rating (A) | 278 | 311 | 284 | 278 | 311 | 284 | 278 | 311 | 284 | 278 | 311 | 284 | 278 | 311 | 284
NQ | 20004649 | CT-MR-1 | MILLCHESTER-CHARTERSTOWERS | CT-MR-1_Millchester-CHTO No 1 66 kV | Time | 11:00 | 17:00 | 8:30 | 11:00 | 17:00 | 8:30 | 11:00 | 17:00 | 8:30 | 11:00 | 17:00 | 8:30 | 16:00 | 17:00 | 7:00
NQ | 20004649 | CT-MR-1 | MILLCHESTER-CHARTERSTOWERS | CT-MR-1_Millchester-CHTO No 1 66 kV | Voltage at Constrained Conductor | 65.5634 | 65.7672 | 65.567 | 65.4914 | 65.6966 | 65.4936 | 65.7631 | 65.6393 | 65.7654 | 65.7207 | 65.5979 | 65.723 | 65.7442 | 65.5711 | 65.76
NQ | 20005445 | DR-CC-1 | DUCHESSRD-CLONCURRY | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | % of Rated A | 20.5157 | 12.5206 | 12.0766 | 20.5277 | 12.5279 | 12.0837 | 20.536 | 12.533 | 12.0886 | 20.5432 | 12.5374 | 12.0928 | 20.5395 | 12.5352 | 12.0906
NQ | 20005445 | DR-CC-1 | DUCHESSRD-CLONCURRY | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Limiting Line Name | TR_LINE 234732_1 | TR_LINE 234732_1 | TR_LINE 234732_1 | TR_LINE 234732_1 | TR_LINE 234732_1 | TR_LINE 234732_1 | TR_LINE 234732_1 | TR_LINE 234732_1 | TR_LINE 234732_1 | TR_LINE 234732_1 | TR_LINE 234732_1 | TR_LINE 234732_1 | TR_LINE 234732_1 | TR_LINE 234732_1 | TR_LINE 234732_1
NQ | 20005445 | DR-CC-1 | DUCHESSRD-CLONCURRY | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Loading (A) | 17.0281 | 17.0281 | 17.0281 | 17.038 | 17.038 | 17.038 | 17.0449 | 17.0449 | 17.0449 | 17.0509 | 17.0509 | 17.0509 | 17.0478 | 17.0478 | 17.0478
NQ | 20005445 | DR-CC-1 | DUCHESSRD-CLONCURRY | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Loading (MVA) | 2.8064 | 2.8064 | 2.8064 | 2.8097 | 2.8097 | 2.8097 | 2.812 | 2.812 | 2.812 | 2.814 | 2.814 | 2.814 | 2.813 | 2.813 | 2.813
NQ | 20005445 | DR-CC-1 | DUCHESSRD-CLONCURRY | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Loading (MW) | 0.11598 | 0.11598 | 0.11598 | 0.116 | 0.116 | 0.116 | 0.11601 | 0.11601 | 0.11601 | 0.11602 | 0.11602 | 0.11602 | 0.11601 | 0.11601 | 0.11601
NQ | 20005445 | DR-CC-1 | DUCHESSRD-CLONCURRY | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Power Factor | 0.041325 | 0.041325 | 0.041325 | 0.041284 | 0.041284 | 0.041284 | 0.041255 | 0.041255 | 0.041255 | 0.04123 | 0.04123 | 0.04123 | 0.041243 | 0.041243 | 0.041243
NQ | 20005445 | DR-CC-1 | DUCHESSRD-CLONCURRY | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Rating (A) | 83 | 136 | 141 | 83 | 136 | 141 | 83 | 136 | 141 | 83 | 136 | 141 | 83 | 136 | 141
NQ | 20005445 | DR-CC-1 | DUCHESSRD-CLONCURRY | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Time | 9:00 | 17:00 | 0:00 | 9:00 | 17:00 | 0:00 | 9:00 | 17:00 | 0:00 | 9:00 | 17:00 | 0:00 | 9:00 | 17:00 | 0:00
NQ | 20005445 | DR-CC-1 | DUCHESSRD-CLONCURRY | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Voltage at Constrained Conductor | 95.1547 | 95.1547 | 95.1547 | 95.2101 | 95.2101 | 95.2101 | 95.2488 | 95.2488 | 95.2488 | 95.2821 | 95.2821 | 95.2821 | 95.2651 | 95.2651 | 95.2651
NQ | 20006056 | GA-BO-1 | GARBUTT-BOHLE | GA-BO-1_Garbutt-Bohle No 1 66 kV | % of Rated A | 74.2441 | 70.2888 | 78.0737 | 77.1581 | 73.0476 | 81.1379 | 79.8241 | 75.5715 | 83.94 | 82.2132 | 77.8333 | 86.4496 | 84.2058 | 79.7234 | 88.5474
NQ | 20006056 | GA-BO-1 | GARBUTT-BOHLE | GA-BO-1_Garbutt-Bohle No 1 66 kV | Limiting Line Name | TR_LINE 32140_1 | TR_LINE 32140_1 | TR_LINE 32140_1 | TR_LINE 32140_1 | TR_LINE 32140_1 | TR_LINE 32140_1 | TR_LINE 32140_1 | TR_LINE 32140_1 | TR_LINE 32140_1 | TR_LINE 32140_1 | TR_LINE 32140_1 | TR_LINE 32140_1 | TR_LINE 32140_1 | TR_LINE 32140_1 | TR_LINE 32140_1
NQ | 20006056 | GA-BO-1 | GARBUTT-BOHLE | GA-BO-1_Garbutt-Bohle No 1 66 kV | Loading (A) | 409.0847 | 409.0808 | 409.1059 | 425.1409 | 425.137 | 425.1628 | 439.8309 | 439.8262 | 439.8453 | 452.9949 | 452.99 | 452.9957 | 463.9739 | 463.9904 | 463.9885
NQ | 20006056 | GA-BO-1 | GARBUTT-BOHLE | GA-BO-1_Garbutt-Bohle No 1 66 kV | Loading (MVA) | 49.5047 | 49.5053 | 49.5066 | 51.4805 | 51.4812 | 51.4824 | 53.2868 | 53.2874 | 53.2883 | 54.9045 | 54.9051 | 54.9047 | 56.2538 | 56.2562 | 56.2554
NQ | 20006056 | GA-BO-1 | GARBUTT-BOHLE | GA-BO-1_Garbutt-Bohle No 1 66 kV | Loading (MW) | 48.3691 | 48.3699 | 48.3708 | 50.3573 | 50.358 | 50.3589 | 52.169 | 52.1697 | 52.1704 | 53.7862 | 53.7869 | 53.7865 | 55.1304 | 55.1325 | 55.1318
NQ | 20006056 | GA-BO-1 | GARBUTT-BOHLE | GA-BO-1_Garbutt-Bohle No 1 66 kV | Power Factor | 0.97706 | 0.97706 | 0.97706 | 0.97818 | 0.97818 | 0.97818 | 0.97902 | 0.97903 | 0.97902 | 0.97963 | 0.97963 | 0.97963 | 0.98003 | 0.98003 | 0.98003
NQ | 20006056 | GA-BO-1 | GARBUTT-BOHLE | GA-BO-1_Garbutt-Bohle No 1 66 kV | Rating (A) | 551 | 582 | 524 | 551 | 582 | 524 | 551 | 582 | 524 | 551 | 582 | 524 | 551 | 582 | 524
NQ | 20006056 | GA-BO-1 | GARBUTT-BOHLE | GA-BO-1_Garbutt-Bohle No 1 66 kV | Time | 16:30 | 17:00 | 7:30 | 16:30 | 17:00 | 7:30 | 16:30 | 17:00 | 7:00 | 16:30 | 17:00 | 7:30 | 16:30 | 17:00 | 7:00
NQ | 20006056 | GA-BO-1 | GARBUTT-BOHLE | GA-BO-1_Garbutt-Bohle No 1 66 kV | Voltage at Constrained Conductor | 69.8671 | 69.8686 | 69.8661 | 69.9116 | 69.9131 | 69.9106 | 69.9476 | 69.9492 | 69.9473 | 69.9768 | 69.9784 | 69.9769 | 69.9999 | 70.0004 | 69.9997
NQ | 20006058 | GA-HP-1 | GARBUTT-HERMITPARK | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | % of Rated A | 36.4694 | 35.1872 | 39.5294 | 35.8362 | 34.579 | 38.847 | 35.2348 | 34.0009 | 38.1985 | 34.5928 | 33.3845 | 37.4026 | 33.8364 | 32.7511 | 36.6924
NQ | 20006058 | GA-HP-1 | GARBUTT-HERMITPARK | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Limiting Line Name | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1
NQ | 20006058 | GA-HP-1 | GARBUTT-HERMITPARK | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Loading (A) | 125.8117 | 126.3146 | 126.4871 | 123.6273 | 124.1316 | 124.3036 | 121.553 | 122.0567 | 122.2285 | 119.3383 | 119.8441 | 119.682 | 116.7289 | 117.5704 | 117.4098
NQ | 20006058 | GA-HP-1 | GARBUTT-HERMITPARK | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Loading (MVA) | 15.1474 | 15.2121 | 15.2336 | 14.8893 | 14.9541 | 14.9756 | 14.6432 | 14.7079 | 14.7293 | 14.3793 | 14.4442 | 14.4257 | 14.0674 | 14.1725 | 14.1541
NQ | 20006058 | GA-HP-1 | GARBUTT-HERMITPARK | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Loading (MW) | 14.8681 | 14.9645 | 14.9918 | 14.6342 | 14.7295 | 14.7565 | 14.4101 | 14.5041 | 14.5308 | 14.1662 | 14.2594 | 14.2486 | 13.8737 | 14.0036 | 13.9927
NQ | 20006058 | GA-HP-1 | GARBUTT-HERMITPARK | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Power Factor | 0.98156 | 0.98372 | 0.98413 | 0.98287 | 0.98498 | 0.98537 | 0.98408 | 0.98614 | 0.98652 | 0.98518 | 0.9872 | 0.98772 | 0.98623 | 0.98808 | 0.9886
NQ | 20006058 | GA-HP-1 | GARBUTT-HERMITPARK | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Rating (A) | 345 | 359 | 320 | 345 | 359 | 320 | 345 | 359 | 320 | 345 | 359 | 320 | 345 | 359 | 320
NQ | 20006058 | GA-HP-1 | GARBUTT-HERMITPARK | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Time | 16:30 | 18:00 | 6:00 | 16:30 | 18:00 | 6:00 | 16:30 | 18:00 | 6:00 | 16:30 | 18:00 | 6:00 | 16:30 | 18:00 | 6:00
NQ | 20006058 | GA-HP-1 | GARBUTT-HERMITPARK | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Voltage at Constrained Conductor | 69.5114 | 69.5305 | 69.5338 | 69.5343 | 69.5534 | 69.5568 | 69.5519 | 69.571 | 69.5744 | 69.566 | 69.5853 | 69.5903 | 69.5783 | 69.5964 | 69.6014
NQ | 20006059 | GA-NS-1 | GARBUTT-NEILSMITH | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | % of Rated A | 16.7196 | 11.8218 | 12.1269 | 15.7653 | 11.147 | 11.4348 | 14.9528 | 10.5727 | 10.8455 | 14.1665 | 10.0167 | 10.2751 | 13.5019 | 9.547 | 9.7929
NQ | 20006059 | GA-NS-1 | GARBUTT-NEILSMITH | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Limiting Line Name | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1
NQ | 20006059 | GA-NS-1 | GARBUTT-NEILSMITH | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Loading (A) | 28.2561 | 28.254 | 28.2558 | 26.6433 | 26.6414 | 26.6431 | 25.2702 | 25.2687 | 25.2699 | 23.9413 | 23.9399 | 23.9411 | 22.8183 | 22.8173 | 22.8175
NQ | 20006059 | GA-NS-1 | GARBUTT-NEILSMITH | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Loading (MVA) | 3.4047 | 3.4048 | 3.4047 | 3.2114 | 3.2115 | 3.2114 | 3.0467 | 3.0467 | 3.0467 | 2.887 | 2.8871 | 2.887 | 2.752 | 2.7521 | 2.7521
NQ | 20006059 | GA-NS-1 | GARBUTT-NEILSMITH | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Loading (MW) | 3.3067 | 3.3067 | 3.3067 | 3.1053 | 3.1053 | 3.1053 | 2.933 | 2.933 | 2.933 | 2.7652 | 2.7652 | 2.7652 | 2.6226 | 2.6226 | 2.6226
NQ | 20006059 | GA-NS-1 | GARBUTT-NEILSMITH | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Power Factor | 0.9712 | 0.97119 | 0.9712 | 0.96697 | 0.96696 | 0.96697 | 0.96269 | 0.96268 | 0.96269 | 0.9578 | 0.95779 | 0.9578 | 0.95296 | 0.95295 | 0.95296
NQ | 20006059 | GA-NS-1 | GARBUTT-NEILSMITH | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Rating (A) | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233
NQ | 20006059 | GA-NS-1 | GARBUTT-NEILSMITH | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Time | 11:00 | 17:00 | 8:30 | 11:00 | 17:00 | 8:30 | 11:00 | 17:00 | 8:30 | 11:00 | 17:00 | 8:30 | 16:00 | 17:00 | 7:00
NQ | 20006059 | GA-NS-1 | GARBUTT-NEILSMITH | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Voltage at Constrained Conductor | 69.5681 | 69.5741 | 69.569 | 69.59 | 69.596 | 69.5909 | 69.6077 | 69.6127 | 69.6086 | 69.6209 | 69.6259 | 69.6218 | 69.6323 | 69.6359 | 69.6351
NQ | 20006060 | GA-TP-1 | GARBUTT-TOWNSVILLEPORT | GA-TP-1_Garbutt-Townsville Port 1 66 kV | % of Rated A | 50.8418 | 44.6351 | 48.448 | 54.0871 | 47.4712 | 51.5234 | 56.9344 | 49.9591 | 54.2211 | 59.4302 | 52.1404 | 56.5342 | 61.4928 | 53.9926 | 58.5428
NQ | 20006060 | GA-TP-1 | GARBUTT-TOWNSVILLEPORT | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Limiting Line Name | TR_LINE 35540_1 | TR_LINE 35540_1 | TR_LINE 35540_1 | TR_LINE 35540_1 | TR_LINE 35540_1 | TR_LINE 35540_1 | TR_LINE 35540_1 | TR_LINE 35540_1 | TR_LINE 35540_1 | TR_LINE 35540_1 | TR_LINE 35540_1 | TR_LINE 35540_1 | TR_LINE 35540_1 | TR_LINE 35540_1 | TR_LINE 35540_1
NQ | 20006060 | GA-TP-1 | GARBUTT-TOWNSVILLEPORT | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Loading (A) | 131.1719 | 131.6735 | 131.7785 | 139.5446 | 140.0399 | 140.1435 | 146.8907 | 147.3792 | 147.4815 | 153.33 | 153.8142 | 153.7731 | 158.6513 | 159.2782 | 159.2364
NQ | 20006060 | GA-TP-1 | GARBUTT-TOWNSVILLEPORT | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Loading (MVA) | 15.8071 | 15.8718 | 15.8852 | 16.8211 | 16.8853 | 16.8986 | 17.7106 | 17.7743 | 17.7875 | 18.4903 | 18.5537 | 18.5499 | 19.1348 | 19.2153 | 19.2116
NQ | 20006060 | GA-TP-1 | GARBUTT-TOWNSVILLEPORT | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Loading (MW) | 15.6917 | 15.7548 | 15.7679 | 16.6992 | 16.7619 | 16.7749 | 17.5811 | 17.6433 | 17.6562 | 18.3525 | 18.4144 | 18.41 | 18.9886 | 19.068 | 19.0636
NQ | 20006060 | GA-TP-1 | GARBUTT-TOWNSVILLEPORT | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Power Factor | 0.9927 | 0.99263 | 0.99262 | 0.99275 | 0.99269 | 0.99268 | 0.99269 | 0.99263 | 0.99262 | 0.99255 | 0.9925 | 0.99246 | 0.99236 | 0.99233 | 0.9923
NQ | 20006060 | GA-TP-1 | GARBUTT-TOWNSVILLEPORT | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Rating (A) | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272
NQ | 20006060 | GA-TP-1 | GARBUTT-TOWNSVILLEPORT | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Time | 16:30 | 18:00 | 6:00 | 16:30 | 18:00 | 6:00 | 16:30 | 18:00 | 6:00 | 16:30 | 18:00 | 6:00 | 16:30 | 18:00 | 6:00
NQ | 20006060 | GA-TP-1 | GARBUTT-TOWNSVILLEPORT | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Voltage at Constrained Conductor | 69.5747 | 69.5932 | 69.5965 | 69.5955 | 69.6141 | 69.6174 | 69.6112 | 69.6298 | 69.6332 | 69.6235 | 69.6422 | 69.6469 | 69.6338 | 69.6515 | 69.6562
NQ | 20007825 | HU-WI-1 | HUGHENDEN-WINTON | HU-WI-1 Hughenden-Winton No 1 66 kV | % of Rated A | 9.9998 | 9.0029 | 9.9241 | 9.9349 | 8.9445 | 9.8597 | 9.8942 | 8.9058 | 9.8193 | 9.8716 | 8.8855 | 9.7969 | 9.8668 | 8.8794 | 9.7922
NQ | 20007825 | HU-WI-1 | HUGHENDEN-WINTON | HU-WI-1 Hughenden-Winton No 1 66 kV | Limiting Line Name | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2
NQ | 20007825 | HU-WI-1 | HUGHENDEN-WINTON | HU-WI-1 Hughenden-Winton No 1 66 kV | Loading (A) | 26.1994 | 26.1983 | 26.1996 | 26.0295 | 26.0286 | 26.0297 | 25.9228 | 25.9158 | 25.923 | 25.8636 | 25.8568 | 25.8638 | 25.851 | 25.839 | 25.8514
NQ | 20007825 | HU-WI-1 | HUGHENDEN-WINTON | HU-WI-1 Hughenden-Winton No 1 66 kV | Loading (MVA) | 3.0487 | 3.0484 | 3.0488 | 3.0295 | 3.0293 | 3.0295 | 3.0182 | 3.0165 | 3.0182 | 3.0116 | 3.01 | 3.0116 | 3.011 | 3.0082 | 3.0111
NQ | 20007825 | HU-WI-1 | HUGHENDEN-WINTON | HU-WI-1 Hughenden-Winton No 1 66 kV | Loading (MW) | 0.62554 | 0.62554 | 0.62554 | 0.46966 | 0.46965 | 0.46966 | 0.32725 | 0.32723 | 0.32725 | 0.20139 | 0.20137 | 0.20139 | 0.10459 | 0.10455 | 0.10459
NQ | 20007825 | HU-WI-1 | HUGHENDEN-WINTON | HU-WI-1 Hughenden-Winton No 1 66 kV | Power Factor | 0.20518 | 0.2052 | 0.20518 | 0.15503 | 0.15504 | 0.15503 | 0.10843 | 0.10848 | 0.10842 | 0.066873 | 0.066901 | 0.066872 | 0.034736 | 0.034756 | 0.034736
NQ | 20007825 | HU-WI-1 | HUGHENDEN-WINTON | HU-WI-1 Hughenden-Winton No 1 66 kV | Rating (A) | 262 | 291 | 264 | 262 | 291 | 264 | 262 | 291 | 264 | 262 | 291 | 264 | 262 | 291 | 264
NQ | 20007825 | HU-WI-1 | HUGHENDEN-WINTON | HU-WI-1 Hughenden-Winton No 1 66 kV | Time | 9:00 | 17:00 | 7:30 | 9:00 | 17:00 | 7:30 | 9:00 | 17:00 | 7:30 | 16:00 | 17:00 | 7:30 | 15:30 | 17:00 | 7:30
NQ | 20007825 | HU-WI-1 | HUGHENDEN-WINTON | HU-WI-1 Hughenden-Winton No 1 66 kV | Voltage at Constrained Conductor | 67.1837 | 67.1806 | 67.1842 | 67.1952 | 67.1929 | 67.1956 | 67.2206 | 67.2024 | 67.2211 | 67.2277 | 67.2099 | 67.2281 | 67.2462 | 67.2152 | 67.2471
NQ | 20007826 | HU-RI-1 | HUGHENDEN-RICHMOND | HU-RI-1_Hughenden-Richmond No 1 66 kV | % of Rated A | 10.8875 | 8.755 | 9.573 | 10.8374 | 8.7174 | 9.5317 | 10.8253 | 8.7067 | 9.5223 | 10.8273 | 8.7086 | 9.5243 | 10.8367 | 8.7144 | 9.5326
NQ | 20007826 | HU-RI-1 | HUGHENDEN-RICHMOND | HU-RI-1_Hughenden-Richmond No 1 66 kV | Limiting Line Name | TR_LINE 163222_1 | TR_LINE 163213_1 | TR_LINE 163213_1 | TR_LINE 163222_1 | TR_LINE 163213_1 | TR_LINE 163213_1 | TR_LINE 163222_1 | TR_LINE 163213_1 | TR_LINE 163213_1 | TR_LINE 163222_1 | TR_LINE 163213_1 | TR_LINE 163213_1 | TR_LINE 163222_1 | TR_LINE 163213_1 | TR_LINE 163213_1
NQ | 20007826 | HU-RI-1 | HUGHENDEN-RICHMOND | HU-RI-1_Hughenden-Richmond No 1 66 kV | Loading (A) | 31.0294 | 31.7806 | 31.7822 | 30.8864 | 31.6441 | 31.6454 | 30.8521 | 31.6052 | 31.614 | 30.8578 | 31.6121 | 31.6207 | 30.8847 | 31.6332 | 31.6482
NQ | 20007826 | HU-RI-1 | HUGHENDEN-RICHMOND | HU-RI-1_Hughenden-Richmond No 1 66 kV | Loading (MVA) | 3.6176 | 3.698 | 3.6984 | 3.6018 | 3.6828 | 3.6831 | 3.5994 | 3.6788 | 3.6808 | 3.6005 | 3.68 | 3.682 | 3.6048 | 3.6827 | 3.6862
NQ | 20007826 | HU-RI-1 | HUGHENDEN-RICHMOND | HU-RI-1_Hughenden-Richmond No 1 66 kV | Loading (MW) | 0.58136 | 0.58504 | 0.58505 | 0.36069 | 0.36434 | 0.36435 | 0.19438 | 0.198 | 0.19803 | 0.071484 | 0.075108 | 0.075138 | 0.0095105 | 0.0059014 | 0.0058493
NQ | 20007826 | HU-RI-1 | HUGHENDEN-RICHMOND | HU-RI-1_Hughenden-Richmond No 1 66 kV | Power Factor | 0.1607 | 0.15821 | 0.15819 | 0.10014 | 0.098931 | 0.098925 | 0.054004 | 0.053823 | 0.053801 | 0.019854 | 0.02041 | 0.020407 | 0.0026383 | 0.0016025 | 0.0015868
NQ | 20007826 | HU-RI-1 | HUGHENDEN-RICHMOND | HU-RI-1_Hughenden-Richmond No 1 66 kV | Rating (A) | 285 | 363 | 332 | 285 | 363 | 332 | 285 | 363 | 332 | 285 | 363 | 332 | 285 | 363 | 332
NQ | 20007826 | HU-RI-1 | HUGHENDEN-RICHMOND | HU-RI-1_Hughenden-Richmond No 1 66 kV | Time | 9:00 | 17:00 | 7:30 | 9:00 | 17:00 | 7:30 | 9:00 | 17:00 | 7:30 | 16:00 | 17:00 | 7:30 | 15:30 | 17:00 | 7:30
NQ | 20007826 | HU-RI-1 | HUGHENDEN-RICHMOND | HU-RI-1_Hughenden-Richmond No 1 66 kV | Voltage at Constrained Conductor | 67.3118 | 67.1806 | 67.1842 | 67.3279 | 67.1929 | 67.1956 | 67.3568 | 67.2024 | 67.2211 | 67.3663 | 67.2099 | 67.2281 | 67.3865 | 67.2152 | 67.2471
NQ | 20008181 | IN-LA-1 | INGHAM-LANNERCOST | IN-LA-1_Ingham-Lannercost No 1 66 kV | % of Rated A | 1.5633 | 1.3812 | 1.5131 | 1.4272 | 1.2768 | 1.3987 | 1.3519 | 1.2095 | 1.325 | 1.309 | 1.1712 | 1.283 | 1.2913 | 1.1553 | 1.2656
NQ | 20008181 | IN-LA-1 | INGHAM-LANNERCOST | IN-LA-1_Ingham-Lannercost No 1 66 kV | Limiting Line Name | TR_LINE 32824_1 | TR_LINE 31685_1 | TR_LINE 31685_1 | TR_LINE 31685_1 | TR_LINE 31685_1 | TR_LINE 31685_1 | TR_LINE 31685_1 | TR_LINE 31685_1 | TR_LINE 31685_1 | TR_LINE 31685_1 | TR_LINE 31685_1 | TR_LINE 31685_1 | TR_LINE 31685_1 | TR_LINE 31685_1 | TR_LINE 31685_1
NQ | 20008181 | IN-LA-1 | INGHAM-LANNERCOST | IN-LA-1_Ingham-Lannercost No 1 66 kV | Loading (A) | 2.0948 | 3.0111 | 3.0111 | 2.783 | 2.7834 | 2.7834 | 2.6363 | 2.6368 | 2.6368 | 2.5526 | 2.5532 | 2.5532 | 2.518 | 2.5185 | 2.5185
NQ | 20008181 | IN-LA-1 | INGHAM-LANNERCOST | IN-LA-1_Ingham-Lannercost No 1 66 kV | Loading (MVA) | 0.25042 | 0.36006 | 0.36006 | 0.33272 | 0.33285 | 0.33285 | 0.3152 | 0.31533 | 0.31533 | 0.3052 | 0.30534 | 0.30534 | 0.30107 | 0.3012 | 0.3012
NQ | 20008181 | IN-LA-1 | INGHAM-LANNERCOST | IN-LA-1_Ingham-Lannercost No 1 66 kV | Loading (MW) | 0.19918 | 0.19928 | 0.19928 | 0.14375 | 0.14375 | 0.14375 | 0.09582 | 0.09582 | 0.09582 | 0.053932 | 0.053932 | 0.053932 | 0.018905 | 0.018905 | 0.018905
NQ | 20008181 | IN-LA-1 | INGHAM-LANNERCOST | IN-LA-1_Ingham-Lannercost No 1 66 kV | Power Factor | 0.79539 | 0.55346 | 0.55346 | 0.43205 | 0.43189 | 0.43189 | 0.304 | 0.30387 | 0.30387 | 0.17671 | 0.17663 | 0.17663 | 0.062792 | 0.062763 | 0.062763
NQ | 20008181 | IN-LA-1 | INGHAM-LANNERCOST | IN-LA-1_Ingham-Lannercost No 1 66 kV | Rating (A) | 134 | 218 | 199 | 195 | 218 | 199 | 195 | 218 | 199 | 195 | 218 | 199 | 195 | 218 | 199
NQ | 20008181 | IN-LA-1 | INGHAM-LANNERCOST | IN-LA-1_Ingham-Lannercost No 1 66 kV | Time | 11:00 | 21:00 | 22:00 | 16:30 | 21:00 | 22:00 | 16:30 | 21:00 | 22:00 | 16:30 | 21:00 | 22:00 | 16:30 | 21:00 | 22:00
NQ | 20008181 | IN-LA-1 | INGHAM-LANNERCOST | IN-LA-1_Ingham-Lannercost No 1 66 kV | Voltage at Constrained Conductor | 69.0207 | 69.0384 | 69.0384 | 69.0258 | 69.0415 | 69.0415 | 69.0294 | 69.0451 | 69.0451 | 69.0303 | 69.046 | 69.046 | 69.0319 | 69.0478 | 69.0478
NQ | 20008182 | IN-VC-1 | INGHAM-VICTORIA | IN-VC-1_Ingham-Victoria No 1 66 kV | % of Rated A | 11.2433 | 10.0327 | 10.9676 | 11.3205 | 10.1016 | 11.0429 | 11.7653 | 10.4985 | 11.4768 | 11.7678 | 10.5007 | 11.4792 | 12.1403 | 10.8333 | 11.8425
NQ | 20008182 | IN-VC-1 | INGHAM-VICTORIA | IN-VC-1_Ingham-Victoria No 1 66 kV | Limiting Line Name | TR_LINE 31692_2 | TR_LINE 31692_2 | TR_LINE 31692_2 | TR_LINE 31692_2 | TR_LINE 31692_2 | TR_LINE 31692_2 | TR_LINE 31692_2 | TR_LINE 31692_2 | TR_LINE 31692_2 | TR_LINE 31692_2 | TR_LINE 31692_2 | TR_LINE 31692_2 | TR_LINE 31692_2 | TR_LINE 31692_2 | TR_LINE 31692_2
NQ | 20008182 | IN-VC-1 | INGHAM-VICTORIA | IN-VC-1_Ingham-Victoria No 1 66 kV | Loading (A) | 22.3741 | 22.3729 | 22.3739 | 22.5277 | 22.5265 | 22.5274 | 23.4128 | 23.4115 | 23.4126 | 23.4178 | 23.4164 | 23.4175 | 24.1592 | 24.1581 | 24.1586
NQ | 20008182 | IN-VC-1 | INGHAM-VICTORIA | IN-VC-1_Ingham-Victoria No 1 66 kV | Loading (MVA) | 2.6747 | 2.6747 | 2.6747 | 2.6932 | 2.6932 | 2.6932 | 2.7992 | 2.7992 | 2.7992 | 2.7998 | 2.7998 | 2.7998 | 2.8886 | 2.8886 | 2.8886
NQ | 20008182 | IN-VC-1 | INGHAM-VICTORIA | IN-VC-1_Ingham-Victoria No 1 66 kV | Loading (MW) | 2.6741 | 2.6741 | 2.6741 | 2.6926 | 2.6926 | 2.6926 | 2.7987 | 2.7987 | 2.7987 | 2.7993 | 2.7993 | 2.7993 | 2.8881 | 2.8881 | 2.8881
NQ | 20008182 | IN-VC-1 | INGHAM-VICTORIA | IN-VC-1_Ingham-Victoria No 1 66 kV | Power Factor | 0.99975 | 0.99975 | 0.99975 | 0.99978 | 0.99978 | 0.99978 | 0.99982 | 0.99982 | 0.99982 | 0.99983 | 0.99983 | 0.99983 | 0.99986 | 0.99986 | 0.99986
NQ | 20008182 | IN-VC-1 | INGHAM-VICTORIA | IN-VC-1_Ingham-Victoria No 1 66 kV | Rating (A) | 199 | 223 | 204 | 199 | 223 | 204 | 199 | 223 | 204 | 199 | 223 | 204 | 199 | 223 | 204
NQ | 20008182 | IN-VC-1 | INGHAM-VICTORIA | IN-VC-1_Ingham-Victoria No 1 66 kV | Time | 11:00 | 17:00 | 8:30 | 11:00 | 17:00 | 8:30 | 11:00 | 17:00 | 8:30 | 11:00 | 17:00 | 8:30 | 16:00 | 17:00 | 8:30
NQ | 20008182 | IN-VC-1 | INGHAM-VICTORIA | IN-VC-1_Ingham-Victoria No 1 66 kV | Voltage at Constrained Conductor | 69.0201 | 69.0239 | 69.021 | 69.0231 | 69.0269 | 69.0239 | 69.0265 | 69.0305 | 69.0273 | 69.0273 | 69.0313 | 69.0281 | 69.0301 | 69.0332 | 69.0318
NQ | 20008540 | JA-EA-1 | JARVISFIELD-EASTAYR | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | % of Rated A | 6.828 | 4.8197 | 4.9434 | 6.4945 | 4.5852 | 4.7029 | 6.0375 | 4.264 | 4.3734 | 5.6169 | 3.9683 | 4.0701 | 5.2842 | 3.7344 | 3.8303
NQ | 20008540 | JA-EA-1 | JARVISFIELD-EASTAYR | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Limiting Line Name | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1
NQ | 20008540 | JA-EA-1 | JARVISFIELD-EASTAYR | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Loading (A) | 11.5394 | 11.5673 | 11.5675 | 10.9756 | 11.0045 | 11.0047 | 10.2034 | 10.2335 | 10.2338 | 9.4925 | 9.5238 | 9.5241 | 8.9303 | 8.9627 | 8.9629
NQ | 20008540 | JA-EA-1 | JARVISFIELD-EASTAYR | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Loading (MVA) | 1.4292 | 1.4354 | 1.4355 | 1.3609 | 1.3671 | 1.3672 | 1.2665 | 1.2727 | 1.2728 | 1.1795 | 1.1857 | 1.1857 | 1.1107 | 1.1167 | 1.1167
NQ | 20008540 | JA-EA-1 | JARVISFIELD-EASTAYR | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Loading (MW) | 1.2162 | 1.2214 | 1.2214 | 1.1505 | 1.1556 | 1.1557 | 1.052 | 1.0571 | 1.0572 | 0.96097 | 0.96615 | 0.96618 | 0.8897 | 0.89483 | 0.89486
NQ | 20008540 | JA-EA-1 | JARVISFIELD-EASTAYR | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Power Factor | 0.85097 | 0.85088 | 0.85088 | 0.84534 | 0.84528 | 0.84529 | 0.83058 | 0.8306 | 0.83061 | 0.81475 | 0.81487 | 0.81487 | 0.80104 | 0.80131 | 0.80131
NQ | 20008540 | JA-EA-1 | JARVISFIELD-EASTAYR | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Rating (A) | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234
NQ | 20008540 | JA-EA-1 | JARVISFIELD-EASTAYR | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Time | 16:30 | 21:00 | 22:00 | 16:30 | 21:00 | 22:00 | 16:30 | 21:00 | 22:00 | 16:30 | 21:00 | 22:00 | 16:30 | 21:00 | 22:00
NQ | 20008540 | JA-EA-1 | JARVISFIELD-EASTAYR | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Voltage at Constrained Conductor | 71.5084 | 71.6461 | 71.6461 | 71.5898 | 71.7276 | 71.7276 | 71.6659 | 71.8043 | 71.8043 | 71.7373 | 71.8762 | 71.8762 | 71.8059 | 71.9352 | 71.9352
NQ | 20010431 | MICB - DURO 1 | MICA CK B - DUCHESS ROAD NO.01 | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | % of Rated A | 1.7272 | 1.3508 | 1.4564 | 1.2858 | 1.0056 | 1.0966 | 0.93668 | 0.73255 | 0.81653 | 0.70602 | 0.57094 | 0.63644 | 0.66995 | 0.54622 | 0.60888
NQ | 20010431 | MICB - DURO 1 | MICA CK B - DUCHESS ROAD NO.01 | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Limiting Line Name | TR_LINE 174405_1 | TR_LINE 174405_1 | TR_LINE 210015_1 | TR_LINE 174405_1 | TR_LINE 174405_1 | TR_LINE 210015_1 | TR_LINE 174405_1 | TR_LINE 174405_1 | TR_LINE 210015_1 | TR_LINE 174405_1 | TR_LINE 210015_1 | TR_LINE 210015_1 | TR_LINE 174405_1 | TR_LINE 210015_1 | TR_LINE 210015_1
NQ | 20010431 | MICB - DURO 1 | MICA CK B - DUCHESS ROAD NO.01 | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Loading (A) | 6.6323 | 6.6323 | 6.7285 | 4.9374 | 4.9374 | 5.0664 | 3.5968 | 3.5968 | 3.7724 | 2.7111 | 2.9403 | 2.9403 | 2.5726 | 2.813 | 2.813
NQ | 20010431 | MICB - DURO 1 | MICA CK B - DUCHESS ROAD NO.01 | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Loading (MVA) | 2.1274 | 2.1274 | 2.1582 | 1.5846 | 1.5846 | 1.626 | 1.1548 | 1.1548 | 1.2111 | 0.87069 | 0.94429 | 0.94429 | 0.82603 | 0.90322 | 0.90322
NQ | 20010431 | MICB - DURO 1 | MICA CK B - DUCHESS ROAD NO.01 | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Loading (MW) | 1.9683 | 1.9683 | 1.9683 | 1.3616 | 1.3616 | 1.3616 | 0.8207 | 0.8207 | 0.8207 | 0.31021 | 0.31022 | 0.31022 | 0.1444 | 0.1444 | 0.1444
NQ | 20010431 | MICB - DURO 1 | MICA CK B - DUCHESS ROAD NO.01 | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Power Factor | 0.9252 | 0.9252 | 0.91198 | 0.85931 | 0.85931 | 0.83744 | 0.7107 | 0.7107 | 0.67764 | 0.35628 | 0.32852 | 0.32852 | 0.17482 | 0.15987 | 0.15987
NQ | 20010431 | MICB - DURO 1 | MICA CK B - DUCHESS ROAD NO.01 | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Rating (A) | 384 | 491 | 462 | 384 | 491 | 462 | 384 | 491 | 462 | 384 | 515 | 462 | 384 | 515 | 462
NQ | 20010431 | MICB - DURO 1 | MICA CK B - DUCHESS ROAD NO.01 | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Time | 9:00 | 17:00 | 0:00 | 9:00 | 17:00 | 0:00 | 9:00 | 17:00 | 0:00 | 9:00 | 17:00 | 0:00 | 9:00 | 17:00 | 0:00
NQ | 20010431 | MICB - DURO 1 | MICA CK B - DUCHESS ROAD NO.01 | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Voltage at Constrained Conductor | 185.192 | 185.192 | 185.1922 | 185.2919 | 185.2919 | 185.2916 | 185.3601 | 185.3601 | 185.3593 | 185.4184 | 185.4171 | 185.4171 | 185.3794 | 185.3777 | 185.3777
NQ | 20010432 | MICB - DURO 2 | MICA CREEKB-DUCHESSRD NO.02 | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | % of Rated A | 4.2881 | 3.4678 | 3.5607 | 3.9641 | 3.2057 | 3.2916 | 3.755 | 3.0366 | 3.118 | 3.6389 | 2.9427 | 3.0216 | 3.6066 | 2.9166 | 2.9948
NQ | 20010432 | MICB - DURO 2 | MICA CREEKB-DUCHESSRD NO.02 | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Limiting Line Name | TR_LINE 174422_1 | TR_LINE 174422_1 | TR_LINE 174422_1 | TR_LINE 174422_1 | TR_LINE 174422_1 | TR_LINE 174422_1 | TR_LINE 174422_1 | TR_LINE 174422_1 | TR_LINE 174422_1 | TR_LINE 174422_1 | TR_LINE 174422_1 | TR_LINE 174422_1 | TR_LINE 174422_1 | TR_LINE 174422_1 | TR_LINE 174422_1
NQ | 20010432 | MICB - DURO 2 | MICA CREEKB-DUCHESSRD NO.02 | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Loading (A) | 11.9639 | 11.9639 | 11.9639 | 11.0598 | 11.0598 | 11.0598 | 10.4763 | 10.4763 | 10.4763 | 10.1524 | 10.1524 | 10.1524 | 10.0624 | 10.0624 | 10.0624
NQ | 20010432 | MICB - DURO 2 | MICA CREEKB-DUCHESSRD NO.02 | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Loading (MVA) | 3.8376 | 3.8376 | 3.8376 | 3.5496 | 3.5496 | 3.5496 | 3.3635 | 3.3635 | 3.3635 | 3.2606 | 3.2606 | 3.2606 | 3.231 | 3.231 | 3.231
NQ | 20010432 | MICB - DURO 2 | MICA CREEKB-DUCHESSRD NO.02 | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Loading (MW) | 2.0898 | 2.0898 | 2.0898 | 1.4831 | 1.4831 | 1.4831 | 0.94221 | 0.94221 | 0.94221 | 0.43174 | 0.43174 | 0.43174 | 0.022895 | 0.022895 | 0.022895
NQ | 20010432 | MICB - DURO 2 | MICA CREEKB-DUCHESSRD NO.02 | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Power Factor | 0.54454 | 0.54454 | 0.54454 | 0.41784 | 0.41784 | 0.41784 | 0.28013 | 0.28013 | 0.28013 | 0.13241 | 0.13241 | 0.13241 | 0.0070861 | 0.0070861 | 0.0070861
NQ | 20010432 | MICB - DURO 2 | MICA CREEKB-DUCHESSRD NO.02 | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Rating (A) | 279 | 345 | 336 | 279 | 345 | 336 | 279 | 345 | 336 | 279 | 345 | 336 | 279 | 345 | 336
NQ | 20010432 | MICB - DURO 2 | MICA CREEKB-DUCHESSRD NO.02 | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Time | 9:00 | 17:00 | 0:00 | 9:00 | 17:00 | 0:00 | 9:00 | 17:00 | 0:00 | 9:00 | 17:00 | 0:00 | 9:00 | 17:00 | 0:00
NQ | 20010432 | MICB - DURO 2 | MICA CREEKB-DUCHESSRD NO.02 | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Voltage at Constrained Conductor | 185.1959 | 185.1959 | 185.1959 | 185.2958 | 185.2958 | 185.2958 | 185.3639 | 185.3639 | 185.3639 | 185.4221 | 185.4221 | 185.4221 | 185.3831 | 185.3831 | 185.3831
NQ | 20010433 | CHUM | MICC - CHUM 220KV FDR 7018 | 7018_Mica Creek C - Chumvale 220 kV | % of Rated A | 20.4972 | 18.8442 | 20.0976 | 20.5547 | 18.8971 | 20.154 | 20.5848 | 18.9247 | 20.1835 | 20.6154 | 18.9529 | 20.2135 | 20.5781 | 18.9186 | 20.1769
NQ | 20010433 | CHUM | MICC - CHUM 220KV FDR 7018 | 7018_Mica Creek C - Chumvale 220 kV | Limiting Line Name | TR_LINE 3024_1 | TR_LINE 3024_1 | TR_LINE 3024_1 | TR_LINE 3024_1 | TR_LINE 3024_1 | TR_LINE 3024_1 | TR_LINE 3024_1 | TR_LINE 3024_1 | TR_LINE 3024_1 | TR_LINE 3024_1 | TR_LINE 3024_1 | TR_LINE 3024_1 | TR_LINE 3024_1 | TR_LINE 3024_1 | TR_LINE 3024_1
NQ | 20010433 | CHUM | MICC - CHUM 220KV FDR 7018 | 7018_Mica Creek C - Chumvale 220 kV | Loading (A) | 175.2515 | 175.2515 | 175.2515 | 175.7427 | 175.7427 | 175.7427 | 176 | 176 | 176 | 176.2621 | 176.2621 | 176.2621 | 175.9428 | 175.9428 | 175.9428
NQ | 20010433 | CHUM | MICC - CHUM 220KV FDR 7018 | 7018_Mica Creek C - Chumvale 220 kV | Loading (MVA) | 97.0034 | 97.0034 | 97.0034 | 97.3234 | 97.3234 | 97.3234 | 97.4985 | 97.4985 | 97.4985 | 97.6715 | 97.6715 | 97.6715 | 97.4743 | 97.4743 | 97.4743
NQ | 20010433 | CHUM | MICC - CHUM 220KV FDR 7018 | 7018_Mica Creek C - Chumvale 220 kV | Loading (MW) | 74.9198 | 74.9198 | 74.9198 | 75.3408 | 75.3408 | 75.3408 | 75.5702 | 75.5702 | 75.5702 | 75.8034 | 75.8034 | 75.8034 | 75.5604 | 75.5604 | 75.5604
NQ | 20010433 | CHUM | MICC - CHUM 220KV FDR 7018 | 7018_Mica Creek C - Chumvale 220 kV | Power Factor | 0.77234 | 0.77234 | 0.77234 | 0.77413 | 0.77413 | 0.77413 | 0.77509 | 0.77509 | 0.77509 | 0.77611 | 0.77611 | 0.77611 | 0.77518 | 0.77518 | 0.77518
NQ | 20010433 | CHUM | MICC - CHUM 220KV FDR 7018 | 7018_Mica Creek C - Chumvale 220 kV | Rating (A) | 855 | 930 | 872 | 855 | 930 | 872 | 855 | 930 | 872 | 855 | 930 | 872 | 855 | 930 | 872
NQ | 20010433 | CHUM | MICC - CHUM 220KV FDR 7018 | 7018_Mica Creek C - Chumvale 220 kV | Time | 9:00 | 17:00 | 0:00 | 9:00 | 17:00 | 0:00 | 9:00 | 17:00 | 0:00 | 9:00 | 17:00 | 0:00 | 9:00 | 17:00 | 0:00
NQ | 20010433 | CHUM | MICC - CHUM 220KV FDR 7018 | 7018_Mica Creek C - Chumvale 220 kV | Voltage at Constrained Conductor | 319.5691 | 319.5691 | 319.5691 | 319.727 | 319.727 | 319.727 | 319.8339 | 319.8339 | 319.8339 | 319.925 | 319.925 | 319.925 | 319.8588 | 319.8588 | 319.8588
NQ | 20010916 | MP-AY-1 | MONAPARK-AYR | MP-AY-1 Mona Park - Ayr No 1 66 kV | % of Rated A | 56.2156 | 38.0426 | 38.7033 | 58.476 | 39.5725 | 40.26 | 60.6352 | 41.0366 | 41.7482 | 62.7503 | 42.4692 | 43.2017 | 64.5573 | 43.6936 | 44.4476
NQ | 20010916 | MP-AY-1 | MONAPARK-AYR | MP-AY-1 Mona Park - Ayr No 1 66 kV | Limiting Line Name | TR_LINE 32534_1 | TR_LINE 32534_1 | TR_LINE 32534_1 | TR_LINE 32534_1 | TR_LINE 32534_1 | TR_LINE 32534_1 | TR_LINE 32534_1 | TR_LINE 32534_1 | TR_LINE 32534_1 | TR_LINE 32534_1 | TR_LINE 32534_1 | TR_LINE 32534_1 | TR_LINE 32534_1 | TR_LINE 32534_1 | TR_LINE 32534_1
NQ | 20010916 | MP-AY-1 | MONAPARK-AYR | MP-AY-1 Mona Park - Ayr No 1 66 kV | Loading (A) | 111.8683 | 111.8444 | 111.8517 | 116.3665 | 116.3424 | 116.3506 | 120.6633 | 120.6469 | 120.6515 | 124.8724 | 124.8586 | 124.852 | 128.4684 | 128.4585 | 128.4529
NQ | 20010916 | MP-AY-1 | MONAPARK-AYR | MP-AY-1 Mona Park - Ayr No 1 66 kV | Loading (MVA) | 13.6599 | 13.658 | 13.6577 | 14.2176 | 14.2156 | 14.2154 | 14.7509 | 14.7497 | 14.7488 | 15.273 | 15.2724 | 15.2724 | 15.7211 | 15.7189 | 15.7189
NQ | 20010916 | MP-AY-1 | MONAPARK-AYR | MP-AY-1 Mona Park - Ayr No 1 66 kV | Loading (MW) | 13.4244 | 13.4224 | 13.4222 | 13.9939 | 13.9919 | 13.9918 | 14.5384 | 14.5372 | 14.5364 | 15.0712 | 15.0705 | 15.0704 | 15.5279 | 15.5259 | 15.5258
NQ | 20010916 | MP-AY-1 | MONAPARK-AYR | MP-AY-1 Mona Park - Ayr No 1 66 kV | Power Factor | 0.98276 | 0.98275 | 0.98276 | 0.98427 | 0.98426 | 0.98427 | 0.98559 | 0.98559 | 0.9856 | 0.98678 | 0.98678 | 0.98678 | 0.98771 | 0.98772 | 0.98772
NQ | 20010916 | MP-AY-1 | MONAPARK-AYR | MP-AY-1 Mona Park - Ayr No 1 66 kV | Rating (A) | 199 | 294 | 289 | 199 | 294 | 289 | 199 | 294 | 289 | 199 | 294 | 289 | 199 | 294 | 289
NQ | 20010916 | MP-AY-1 | MONAPARK-AYR | MP-AY-1 Mona Park - Ayr No 1 66 kV | Time | 14:00 | 17:00 | 8:30 | 14:00 | 17:00 | 8:30 | 16:00 | 17:00 | 7:00 | 16:30 | 17:00 | 8:30 | 14:00 | 17:00 | 8:30
NQ | 20010916 | MP-AY-1 | MONAPARK-AYR | MP-AY-1 Mona Park - Ayr No 1 66 kV | Voltage at Constrained Conductor | 70.4987 | 70.5036 | 70.4978 | 70.5402 | 70.5451 | 70.5389 | 70.5802 | 70.5841 | 70.5773 | 70.6153 | 70.62 | 70.6237 | 70.6522 | 70.6479 | 70.6509
NQ | 20010918 | MR-LE-1 | MILLCHESTER-MOUNTLEYSHON | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | % of Rated A | 45.9295 | 42.0474 | 46.6966 | 46.5294 | 42.5864 | 47.2815 | 47.0801 | 43.1206 | 47.8433 | 47.0737 | 43.1495 | 47.6432 | 47.1006 | 43.1686 | 47.8616
NQ | 20010918 | MR-LE-1 | MILLCHESTER-MOUNTLEYSHON | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Limiting Line Name | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 49923_1
NQ | 20010918 | MR-LE-1 | MILLCHESTER-MOUNTLEYSHON | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Loading (A) | 86.1076 | 85.9514 | 86.1485 | 87.2302 | 87.0512 | 87.2258 | 88.2612 | 88.1414 | 88.2538 | 88.2491 | 88.2003 | 87.8856 | 88.2925 | 88.2394 | 88.2873
NQ | 20010918 | MR-LE-1 | MILLCHESTER-MOUNTLEYSHON | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Loading (MVA) | 9.678 | 9.6789 | 9.6785 | 9.7891 | 9.7897 | 9.789 | 9.8993 | 9.9006 | 9.9019 | 9.8991 | 9.9013 | 9.8979 | 9.9023 | 9.9017 | 9.9022
NQ | 20010918 | MR-LE-1 | MILLCHESTER-MOUNTLEYSHON | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Loading (MW) | 9.6561 | 9.656 | 9.6565 | 9.7655 | 9.7651 | 9.7654 | 9.8742 | 9.8744 | 9.8753 | 9.8741 | 9.8749 | 9.8722 | 9.8756 | 9.8752 | 9.8756
NQ | 20010918 | MR-LE-1 | MILLCHESTER-MOUNTLEYSHON | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Power Factor | 0.99774 | 0.99763 | 0.99773 | 0.99759 | 0.99749 | 0.99759 | 0.99746 | 0.99734 | 0.99732 | 0.99747 | 0.99733 | 0.9974 | 0.99731 | 0.99732 | 0.99731
NQ | 20010918 | MR-LE-1 | MILLCHESTER-MOUNTLEYSHON | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Rating (A) | 188 | 205 | 185 | 188 | 205 | 185 | 188 | 205 | 185 | 188 | 205 | 185 | 188 | 205 | 185
NQ | 20010918 | MR-LE-1 | MILLCHESTER-MOUNTLEYSHON | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Time | 11:00 | 18:00 | 6:30 | 11:00 | 18:00 | 8:30 | 16:00 | 18:00 | 6:00 | 16:30 | 18:00 | 6:30 | 11:00 | 18:00 | 8:30
NQ | 20010918 | MR-LE-1 | MILLCHESTER-MOUNTLEYSHON | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Voltage at Constrained Conductor | 64.8911 | 65.0145 | 64.8631 | 64.7908 | 64.9283 | 64.7938 | 64.755 | 64.852 | 64.7774 | 64.763 | 64.8128 | 65.0224 | 64.7517 | 64.7869 | 64.7551
NQ | 20012877 | ST-GI-1 | Stuart-Giru | ST-GI-1_Stuart-Giru 66 kV | % of Rated A | 2.4994 | 2.2899 | 2.5522 | 2.4399 | 2.2355 | 2.4917 | 2.3995 | 2.1987 | 2.4506 | 2.3722 | 2.1737 | 2.4228 | 2.3552 | 2.1581 | 2.4054
NQ | 20012877 | ST-GI-1 | Stuart-Giru | ST-GI-1_Stuart-Giru 66 kV | Limiting Line Name | TR_LINE 162083_1 | TR_LINE 162083_1 | TR_LINE 162083_1 | TR_LINE 162083_1 | TR_LINE 162083_1 | TR_LINE 162083_1 | TR_LINE 162083_1 | TR_LINE 162083_1 | TR_LINE 162083_1 | TR_LINE 162083_1 | TR_LINE 162083_1 | TR_LINE 162083_1 | TR_LINE 162083_1 | TR_LINE 162083_1 | TR_LINE 162083_1
NQ | 20012877 | ST-GI-1 | Stuart-Giru | ST-GI-1_Stuart-Giru 66 kV | Loading (A) | 2.4494 | 2.4501 | 2.4501 | 2.3911 | 2.392 | 2.392 | 2.3515 | 2.3526 | 2.3526 | 2.3247 | 2.3259 | 2.3259 | 2.3081 | 2.3092 | 2.3092
NQ | 20012877 | ST-GI-1 | Stuart-Giru | ST-GI-1_Stuart-Giru 66 kV | Loading (MVA) | 0.29205 | 0.29252 | 0.29252 | 0.28508 | 0.28556 | 0.28556 | 0.28035 | 0.28083 | 0.28083 | 0.27713 | 0.27762 | 0.27762 | 0.27513 | 0.27561 | 0.27561
NQ | 20012877 | ST-GI-1 | Stuart-Giru | ST-GI-1_Stuart-Giru 66 kV | Loading (MW) | 0.17935 | 0.17935 | 0.17935 | 0.16767 | 0.16767 | 0.16767 | 0.15944 | 0.15944 | 0.15944 | 0.15371 | 0.15371 | 0.15371 | 0.15007 | 0.15007 | 0.15007
NQ | 20012877 | ST-GI-1 | Stuart-Giru | ST-GI-1_Stuart-Giru 66 kV | Power Factor | 0.61412 | 0.61313 | 0.61313 | 0.58816 | 0.58716 | 0.58716 | 0.56872 | 0.56774 | 0.56774 | 0.55463 | 0.55366 | 0.55366 | 0.54544 | 0.5445 | 0.5445
NQ | 20012877 | ST-GI-1 | Stuart-Giru | ST-GI-1_Stuart-Giru 66 kV | Rating (A) | 98 | 107 | 96 | 98 | 107 | 96 | 98 | 107 | 96 | 98 | 107 | 96 | 98 | 107 | 96
NQ | 20012877 | ST-GI-1 | Stuart-Giru | ST-GI-1_Stuart-Giru 66 kV | Time | 16:30 | 21:00 | 22:00 | 16:30 | 21:00 | 22:00 | 15:30 | 21:00 | 22:00 | 16:00 | 21:00 | 22:00 | 15:30 | 21:00 | 22:00
NQ | 20012877 | ST-GI-1 | Stuart-Giru | ST-GI-1_Stuart-Giru 66 kV | Voltage at Constrained Conductor | 68.8385 | 68.9286 | 68.9286 | 68.8348 | 68.9251 | 68.9251 | 68.8312 | 68.92 | 68.92 | 68.8261 | 68.9139 | 68.9139 | 68.8216 | 68.9076 | 68.9076
NQ | 20012878 | HP-OO | HERMIT PARK - OONOONBA | HP-OO_Hermit park - Oonoonba 66 kV | % of Rated A | 22.3393 | 21.8687 | 24.8582 | 23.4666 | 22.9761 | 26.1164 | 24.4914 | 23.9814 | 27.2584 | 25.4271 | 24.8994 | 28.1925 | 26.1264 | 25.6813 | 29.0813
NQ | 20012878 | HP-OO | HERMIT PARK - OONOONBA | HP-OO_Hermit park - Oonoonba 66 kV | Limiting Line Name | TR_LINE 106404_1 | TR_LINE 106404_1 | TR_LINE 106404_1 | TR_LINE 106404_1 | TR_LINE 106404_1 | TR_LINE 106404_1 | TR_LINE 106404_1 | TR_LINE 106404_1 | TR_LINE 106404_1 | TR_LINE 106404_1 | TR_LINE 106404_1 | TR_LINE 106404_1 | TR_LINE 106404_1 | TR_LINE 106404_1 | TR_LINE 106404_1
NQ | 20012878 | HP-OO | HERMIT PARK - OONOONBA | HP-OO_Hermit park - Oonoonba 66 kV | Loading (A) | 77.0609 | 77.406 | 77.5486 | 80.9509 | 81.3272 | 81.4751 | 84.4872 | 84.8867 | 85.0389 | 87.7161 | 88.1371 | 87.9538 | 90.1294 | 90.9056 | 90.7275
NQ | 20012878 | HP-OO | HERMIT PARK - OONOONBA | HP-OO_Hermit park - Oonoonba 66 kV | Loading (MVA) | 9.2302 | 9.2747 | 9.2923 | 9.6988 | 9.7472 | 9.7655 | 10.1246 | 10.176 | 10.1948 | 10.5134 | 10.5675 | 10.5466 | 10.8046 | 10.901 | 10.8808
NQ | 20012878 | HP-OO | HERMIT PARK - OONOONBA | HP-OO_Hermit park - Oonoonba 66 kV | Loading (MW) | 8.8011 | 8.8971 | 8.9243 | 9.3268 | 9.4217 | 9.4486 | 9.8004 | 9.894 | 9.9206 | 10.2299 | 10.3226 | 10.3121 | 10.5569 | 10.686 | 10.6753
NQ | 20012878 | HP-OO | HERMIT PARK - OONOONBA | HP-OO_Hermit park - Oonoonba 66 kV | Power Factor | 0.95351 | 0.9593 | 0.9604 | 0.96165 | 0.96661 | 0.96755 | 0.96798 | 0.97229 | 0.9731 | 0.97304 | 0.97683 | 0.97776 | 0.97707 | 0.98028 | 0.98112
NQ | 20012878 | HP-OO | HERMIT PARK - OONOONBA | HP-OO_Hermit park - Oonoonba 66 kV | Rating (A) | 345 | 354 | 312 | 345 | 354 | 312 | 345 | 354 | 312 | 345 | 354 | 312 | 345 | 354 | 312
NQ | 20012878 | HP-OO | HERMIT PARK - OONOONBA | HP-OO_Hermit park - Oonoonba 66 kV | Time | 16:30 | 18:00 | 6:00 | 16:30 | 18:00 | 6:00 | 16:30 | 18:00 | 6:00 | 16:30 | 18:00 | 6:00 | 16:30 | 18:00 | 6:00
NQ | 20012878 | HP-OO | HERMIT PARK - OONOONBA | HP-OO_Hermit park - Oonoonba 66 kV | Voltage at Constrained Conductor | 69.1536 | 69.1771 | 69.181 | 69.1728 | 69.1964 | 69.2004 | 69.1875 | 69.2112 | 69.2152 | 69.1996 | 69.2234 | 69.2307 | 69.2123 | 69.2333 | 69.2406
NQ | 20012879 | ST-RM-1 | Stuart-Rasmussen | ST-RM-1_Stuart-Rasmussen 66 kV | % of Rated A | 9.6951 | 9.2463 | 10.2916 | 10.5916 | 10.0967 | 11.2364 | 11.394 | 10.8574 | 12.0815 | 12.1239 | 11.5493 | 12.8178 | 12.7391 | 12.1619 | 13.4985
NQ | 20012879 | ST-RM-1 | Stuart-Rasmussen | ST-RM-1_Stuart-Rasmussen 66 kV | Limiting Line Name | TR_LINE 32428_1 | TR_LINE 32428_1 | TR_LINE 32428_1 | TR_LINE 32428_1 | TR_LINE 32428_1 | TR_LINE 32428_1 | TR_LINE 32428_1 | TR_LINE 32428_1 | TR_LINE 32428_1 | TR_LINE 32428_1 | TR_LINE 32428_1 | TR_LINE 32428_1 | TR_LINE 32428_1 | TR_LINE 32428_1 | TR_LINE 32428_1
NQ | 20012879 | ST-RM-1 | Stuart-Rasmussen | ST-RM-1_Stuart-Rasmussen 66 kV | Loading (A) | 53.4201 | 53.8135 | 53.9282 | 58.3597 | 58.7628 | 58.8789 | 62.7812 | 62.8681 | 62.9894 | 66.488 | 66.9244 | 66.8794 | 69.9059 | 70.5139 | 70.4703
NQ | 20012879 | ST-RM-1 | Stuart-Rasmussen | ST-RM-1_Stuart-Rasmussen 66 kV | Loading (MVA) | 6.3675 | 6.417 | 6.4311 | 6.9557 | 7.0067 | 7.021 | 7.482 | 7.5345 | 7.5494 | 7.9663 | 8.0213 | 8.0168 | 8.3767 | 8.4521 | 8.4477
NQ | 20012879 | ST-RM-1 | Stuart-Rasmussen | ST-RM-1_Stuart-Rasmussen 66 kV | Loading (MW) | 6.2123 | 6.2794 | 6.2966 | 6.8215 | 6.888 | 6.905 | 7.3648 | 7.4585 | 7.4755 | 7.8886 | 7.9544 | 7.9532 | 8.3088 | 8.3927 | 8.3915
NQ | 20012879 | ST-RM-1 | Stuart-Rasmussen | ST-RM-1_Stuart-Rasmussen 66 kV | Power Factor | 0.97563 | 0.97857 | 0.97909 | 0.9807 | 0.98307 | 0.98349 | 0.98434 | 0.98992 | 0.99021 | 0.99025 | 0.99166 | 0.99207 | 0.9919 | 0.99297 | 0.99334
NQ | 20012879 | ST-RM-1 | Stuart-Rasmussen | ST-RM-1_Stuart-Rasmussen 66 kV | Rating (A) | 551 | 582 | 524 | 551 | 582 | 524 | 551 | 582 | 524 | 551 | 582 | 524 | 551 | 582 | 524
NQ | 20012879 | ST-RM-1 | Stuart-Rasmussen | ST-RM-1_Stuart-Rasmussen 66 kV | Time | 16:30 | 18:00 | 6:00 | 16:30 | 18:00 | 6:00 | 16:30 | 18:00 | 6:00 | 16:30 | 18:00 | 6:00 | 16:30 | 18:00 | 6:00
NQ | 20012879 | ST-RM-1 | Stuart-Rasmussen | ST-RM-1_Stuart-Rasmussen 66 kV | Voltage at Constrained Conductor | 68.8179 | 68.8461 | 68.8506 | 68.8128 | 68.841 | 68.8456 | 68.8063 | 69.1928 | 69.1968 | 69.1753 | 69.1991 | 69.2064 | 69.1826 | 69.2035 | 69.2108
NQ | 20012880 | ST-RP-1 | Stuart-RossPlains | ST-RP-1_Stuart-Ross Plains 66 kV | % of Rated A | 9.9432 | 9.319 | 10.2866 | 11.0775 | 10.3807 | 11.4567 | 12.0884 | 11.3251 | 12.4974 | 13.0032 | 12.1793 | 13.3904 | 13.7592 | 12.9289 | 14.2166
NQ | 20012880 | ST-RP-1 | Stuart-RossPlains | ST-RP-1_Stuart-Ross Plains 66 kV | Limiting Line Name | TR_LINE 32425_1 | TR_LINE 32425_1 | TR_LINE 32425_1 | TR_LINE 32425_1 | TR_LINE 32425_1 | TR_LINE 32425_1 | TR_LINE 32425_1 | TR_LINE 32425_1 | TR_LINE 32425_1 | TR_LINE 32425_1 | TR_LINE 32425_1 | TR_LINE 32425_1 | TR_LINE 32425_1 | TR_LINE 32425_1 | TR_LINE 32425_1
NQ | 20012880 | ST-RP-1 | Stuart-RossPlains | ST-RP-1_Stuart-Ross Plains 66 kV | Loading (A) | 67.514 | 68.0291 | 68.1999 | 75.2165 | 75.779 | 75.9579 | 82.0802 | 82.6734 | 82.8579 | 88.2894 | 88.9071 | 88.7767 | 93.4229 | 94.3788 | 94.2541
NQ | 20012880 | ST-RP-1 | Stuart-RossPlains | ST-RP-1_Stuart-Ross Plains 66 kV | Loading (MVA) | 8.0474 | 8.1121 | 8.133 | 8.9648 | 9.0356 | 9.0575 | 9.782 | 9.8568 | 9.8794 | 10.5211 | 10.5992 | 10.5851 | 11.1325 | 11.2504 | 11.2371
NQ | 20012880 | ST-RP-1 | Stuart-RossPlains | ST-RP-1_Stuart-Ross Plains 66 kV | Loading (MW) | 7.4519 | 7.5746 | 7.6059 | 8.4435 | 8.565 | 8.596 | 9.3177 | 9.4379 | 9.4687 | 10.1027 | 10.2221 | 10.2205 | 10.7552 | 10.9068 | 10.905
NQ | 20012880 | ST-RP-1 | Stuart-RossPlains | ST-RP-1_Stuart-Ross Plains 66 kV | Power Factor | 0.926 | 0.93374 | 0.93518 | 0.94185 | 0.94792 | 0.94904 | 0.95253 | 0.95751 | 0.95843 | 0.96023 | 0.96443 | 0.96555 | 0.96611 | 0.96946 | 0.97045
NQ | 20012880 | ST-RP-1 | Stuart-RossPlains | ST-RP-1_Stuart-Ross Plains 66 kV | Rating (A) | 679 | 730 | 663 | 679 | 730 | 663 | 679 | 730 | 663 | 679 | 730 | 663 | 679 | 730 | 663
NQ | 20012880 | ST-RP-1 | Stuart-RossPlains | ST-RP-1_Stuart-Ross Plains 66 kV | Time | 16:30 | 18:00 | 6:00 | 16:30 | 18:00 | 6:00 | 16:30 | 18:00 | 6:00 | 16:30 | 18:00 | 6:00 | 16:30 | 18:00 | 6:00
NQ | 20012880 | ST-RP-1 | Stuart-RossPlains | ST-RP-1_Stuart-Ross Plains 66 kV | Voltage at Constrained Conductor | 68.8179 | 68.8461 | 68.8506 | 68.8128 | 68.841 | 68.8456 | 68.8063 | 68.8347 | 68.8394 | 68.8009 | 68.8295 | 68.8393 | 68.7986 | 68.8227 | 68.8326
NQ | 20012881 | ST-TOPO-1 | Stuart-TOPO | ST-TOPO-1_Stuart-Townsville Port 66 kV | % of Rated A | 14.0329 | 11.4965 | 12.9025 | 14.1022 | 11.5489 | 12.9587 | 14.1562 | 11.6098 | 12.9868 | 14.2322 | 11.6926 | 13.0269 | 14.3073 | 11.7775 | 13.1221
NQ | 20012881 | ST-TOPO-1 | Stuart-TOPO | ST-TOPO-1_Stuart-Townsville Port 66 kV | Limiting Line Name | TR_LINE 31745_2 | TR_LINE 31664_1 | TR_LINE 31664_1 | TR_LINE 31745_2 | TR_LINE 31664_1 | TR_LINE 31664_1 | TR_LINE 31745_2 | TR_LINE 31664_1 | TR_LINE 31664_1 | TR_LINE 31745_2 | TR_LINE 31664_1 | TR_LINE 31664_1 | TR_LINE 31745_2 | TR_LINE 31664_1 | TR_LINE 31664_1
NQ | 20012881 | ST-TOPO-1 | Stuart-TOPO | ST-TOPO-1_Stuart-Townsville Port 66 kV | Loading (A) | 35.2226 | 36.0989 | 36.3852 | 35.3966 | 36.2636 | 36.5435 | 35.5321 | 36.4549 | 36.6227 | 35.7229 | 36.7146 | 36.7359 | 35.9114 | 36.9815 | 37.0044
NQ | 20012881 | ST-TOPO-1 | Stuart-TOPO | ST-TOPO-1_Stuart-Townsville Port 66 kV | Loading (MVA) | 4.2208 | 4.3053 | 4.3391 | 4.2416 | 4.3246 | 4.3577 | 4.2577 | 4.3471 | 4.3669 | 4.2805 | 4.3776 | 4.3801 | 4.3031 | 4.409 | 4.4119
NQ | 20012881 | ST-TOPO-1 | Stuart-TOPO | ST-TOPO-1_Stuart-Townsville Port 66 kV | Loading (MW) | 1.5296 | 1.5342 | 1.5248 | 1.6995 | 1.7039 | 1.6947 | 1.8616 | 1.8616 | 1.8682 | 2.0378 | 2.0232 | 1.9846 | 2.1453 | 2.1674 | 2.1401
NQ | 20012881 | ST-TOPO-1 | Stuart-TOPO | ST-TOPO-1_Stuart-Townsville Port 66 kV | Power Factor | 0.36238 | 0.35636 | 0.3514 | 0.40066 | 0.39399 | 0.38889 | 0.43723 | 0.42824 | 0.42781 | 0.47607 | 0.46216 | 0.45309 | 0.49854 | 0.49158 | 0.48508
NQ | 20012881 | ST-TOPO-1 | Stuart-TOPO | ST-TOPO-1_Stuart-Townsville Port 66 kV | Rating (A) | 251 | 314 | 282 | 251 | 314 | 282 | 251 | 314 | 282 | 251 | 314 | 282 | 251 | 314 | 282
NQ | 20012881 | ST-TOPO-1 | Stuart-TOPO | ST-TOPO-1_Stuart-Townsville Port 66 kV | Time | 11:00 | 17:00 | 8:30 | 11:00 | 17:00 | 8:30 | 16:00 | 17:00 | 7:00 | 16:30 | 17:00 | 8:30 | 11:00 | 17:00 | 8:30
NQ | 20012881 | ST-TOPO-1 | Stuart-TOPO | ST-TOPO-1_Stuart-Townsville Port 66 kV | Voltage at Constrained Conductor | 69.1857 | 68.8571 | 68.8517 | 69.1847 | 68.8524 | 68.847 | 69.1828 | 68.8465 | 68.8427 | 69.1804 | 68.8398 | 68.8387 | 69.1809 | 68.8333 | 68.8355
NQ | 20012883 | ST-WO-1 | STUA-WOSO | ST-WO-1_Stuart-Woodstock South 1 66 kV | % of Rated A | 41.3918 | 31.4974 | 34.3012 | 41.9873 | 31.9699 | 34.8004 | 42.1158 | 32.3562 | 34.7494 | 42.2266 | 32.7121 | 34.9979 | 42.2515 | 32.975 | 35.0199
NQ | 20012883 | ST-WO-1 | STUA-WOSO | ST-WO-1_Stuart-Woodstock South 1 66 kV | Limiting Line Name | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1
NQ | 20012883 | ST-WO-1 | STUA-WOSO | ST-WO-1_Stuart-Woodstock South 1 66 kV | Loading (A) | 54.6372 | 52.6006 | 54.5389 | 55.4232 | 53.3897 | 55.3327 | 55.5929 | 54.0348 | 55.2516 | 55.7392 | 54.6293 | 55.6466 | 55.7719 | 55.0683 | 55.6817
NQ | 20012883 | ST-WO-1 | STUA-WOSO | ST-WO-1_Stuart-Woodstock South 1 66 kV | Loading (MVA) | 6.4278 | 6.1942 | 6.4163 | 6.519 | 6.2861 | 6.5085 | 6.5394 | 6.361 | 6.4998 | 6.5636 | 6.4302 | 6.5528 | 6.5662 | 6.4814 | 6.5556
NQ | 20012883 | ST-WO-1 | STUA-WOSO | ST-WO-1_Stuart-Woodstock South 1 66 kV | Loading (MW) | 2.0765 | 2.0746 | 2.0714 | 2.1268 | 2.1262 | 2.1213 | 2.1712 | 2.1726 | 2.1561 | 2.4114 | 2.2235 | 2.4058 | 2.3853 | 2.2681 | 2.3801
NQ | 20012883 | ST-WO-1 | STUA-WOSO | ST-WO-1_Stuart-Woodstock South 1 66 kV | Power Factor | 0.32305 | 0.33493 | 0.32283 | 0.32625 | 0.33825 | 0.32592 | 0.33202 | 0.34155 | 0.33171 | 0.3674 | 0.34579 | 0.36714 | 0.36327 | 0.34994 | 0.36307
NQ | 20012883 | ST-WO-1 | STUA-WOSO | ST-WO-1_Stuart-Woodstock South 1 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
NQ | 20012883 | ST-WO-1 | STUA-WOSO | ST-WO-1_Stuart-Woodstock South 1 66 kV | Time | 11:00 | 17:00 | 8:30 | 11:00 | 17:00 | 8:30 | 16:00 | 17:00 | 7:00 | 11:00 | 17:00 | 8:30 | 11:00 | 17:00 | 8:30
NQ | 20012883 | ST-WO-1 | STUA-WOSO | ST-WO-1_Stuart-Woodstock South 1 66 kV | Voltage at Constrained Conductor | 67.9221 | 67.9886 | 67.9235 | 67.9097 | 67.9767 | 67.9107 | 67.9141 | 67.9662 | 67.9199 | 67.9863 | 67.958 | 67.9873 | 67.9728 | 67.9527 | 67.9739
NQ | 20012969 | TP-NS-1 | TP-NeilSmith | TP-NS-1_Townsville Port-NESM No 1 66 kV | % of Rated A | 11.0096 | 9.6284 | 10.443 | 10.3851 | 9.0823 | 9.8506 | 9.8531 | 8.617 | 9.3459 | 9.3374 | 8.1662 | 8.8568 | 8.9015 | 7.785 | 8.4433
NQ | 20012969 | TP-NS-1 | TP-NeilSmith | TP-NS-1_Townsville Port-NESM No 1 66 kV | Limiting Line Name | TR_LINE 56322_1 | TR_LINE 56322_1 | TR_LINE 56322_1 | TR_LINE 56322_1 | TR_LINE 56322_1 | TR_LINE 56322_1 | TR_LINE 56322_1 | TR_LINE 56322_1 | TR_LINE 56322_1 | TR_LINE 56322_1 | TR_LINE 56322_1 | TR_LINE 56322_1 | TR_LINE 56322_1 | TR_LINE 56322_1 | TR_LINE 56322_1
NQ | 20012969 | TP-NS-1 | TP-NeilSmith | TP-NS-1_Townsville Port-NESM No 1 66 kV | Loading (A) | 28.4048 | 28.4039 | 28.4049 | 26.7936 | 26.7928 | 26.7937 | 25.4209 | 25.4203 | 25.4209 | 24.0906 | 24.0902 | 24.0905 | 22.9659 | 22.9658 | 22.9659
NQ | 20012969 | TP-NS-1 | TP-NeilSmith | TP-NS-1_Townsville Port-NESM No 1 66 kV | Loading (MVA) | 3.4061 | 3.4061 | 3.4061 | 3.2129 | 3.2129 | 3.2129 | 3.0482 | 3.0482 | 3.0482 | 2.8886 | 2.8886 | 2.8886 | 2.7537 | 2.7537 | 2.7537
NQ | 20012969 | TP-NS-1 | TP-NeilSmith | TP-NS-1_Townsville Port-NESM No 1 66 kV | Loading (MW) | 3.3059 | 3.3059 | 3.3059 | 3.1048 | 3.1048 | 3.1048 | 2.9326 | 2.9326 | 2.9326 | 2.7649 | 2.7649 | 2.7649 | 2.6225 | 2.6225 | 2.6225
NQ | 20012969 | TP-NS-1 | TP-NeilSmith | TP-NS-1_Townsville Port-NESM No 1 66 kV | Power Factor | 0.97059 | 0.97059 | 0.97059 | 0.96636 | 0.96636 | 0.96636 | 0.96208 | 0.96208 | 0.96208 | 0.9572 | 0.95719 | 0.9572 | 0.95236 | 0.95236 | 0.95236
NQ | 20012969 | TP-NS-1 | TP-NeilSmith | TP-NS-1_Townsville Port-NESM No 1 66 kV | Rating (A) | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272
NQ | 20012969 | TP-NS-1 | TP-NeilSmith | TP-NS-1_Townsville Port-NESM No 1 66 kV | Time | 9:00 | 17:00 | 7:30 | 9:00 | 17:00 | 7:30 | 16:00 | 17:00 | 7:00 | 16:30 | 17:00 | 7:30 | 16:00 | 17:00 | 7:00
NQ | 20012969 | TP-NS-1 | TP-NeilSmith | TP-NS-1_Townsville Port-NESM No 1 66 kV | Voltage at Constrained Conductor | 69.2314 | 69.2341 | 69.2314 | 69.231 | 69.2336 | 69.2309 | 69.2294 | 69.2315 | 69.2295 | 69.2273 | 69.2288 | 69.2276 | 69.2253 | 69.2257 | 69.2253
NQ | 20013599 | DG-CB-1 | DANGLEESON-CRANBROOK | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | % of Rated A | 32.0403 | 20.8897 | 21.168 | 31.2216 | 20.3559 | 20.6271 | 30.5842 | 19.9401 | 20.2048 | 30.087 | 19.6158 | 19.8723 | 29.7569 | 19.4052 | 19.6584
NQ | 20013599 | DG-CB-1 | DANGLEESON-CRANBROOK | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Limiting Line Name | TR_LINE 31660_1 | TR_LINE 31660_1 | TR_LINE 31660_1 | TR_LINE 31660_1 | TR_LINE 31660_1 | TR_LINE 31660_1 | TR_LINE 31660_1 | TR_LINE 31660_1 | TR_LINE 31660_1 | TR_LINE 31660_1 | TR_LINE 31660_1 | TR_LINE 31660_1 | TR_LINE 31660_1 | TR_LINE 31660_1 | TR_LINE 31660_1
NQ | 20013599 | DG-CB-1 | DANGLEESON-CRANBROOK | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Loading (A) | 80.4212 | 80.4252 | 80.4382 | 78.3663 | 78.3701 | 78.3829 | 76.7662 | 76.7694 | 76.7783 | 75.5182 | 75.521 | 75.5148 | 74.6898 | 74.7098 | 74.702
NQ | 20013599 | DG-CB-1 | DANGLEESON-CRANBROOK | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Loading (MVA) | 9.6535 | 9.6542 | 9.6554 | 9.4088 | 9.4094 | 9.4106 | 9.2179 | 9.2185 | 9.2193 | 9.0688 | 9.0694 | 9.0684 | 8.97 | 8.9724 | 8.972
NQ | 20013599 | DG-CB-1 | DANGLEESON-CRANBROOK | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Loading (MW) | 4.569 | 4.5699 | 4.571 | 3.8355 | 3.8363 | 3.8374 | 3.1454 | 3.1462 | 3.147 | 2.4694 | 2.4703 | 2.4698 | 1.8594 | 1.8618 | 1.8654
NQ | 20013599 | DG-CB-1 | DANGLEESON-CRANBROOK | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Power Factor | 0.4733 | 0.47335 | 0.47341 | 0.40765 | 0.40771 | 0.40777 | 0.34123 | 0.34129 | 0.34135 | 0.2723 | 0.27237 | 0.27235 | 0.20729 | 0.2075 | 0.20791
NQ | 20013599 | DG-CB-1 | DANGLEESON-CRANBROOK | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Rating (A) | 251 | 385 | 380 | 251 | 385 | 380 | 251 | 385 | 380 | 251 | 385 | 380 | 251 | 385 | 380
NQ | 20013599 | DG-CB-1 | DANGLEESON-CRANBROOK | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Time | 16:30 | 17:00 | 7:30 | 16:30 | 17:00 | 7:30 | 16:30 | 17:00 | 7:00 | 16:30 | 17:00 | 7:30 | 16:30 | 17:00 | 7:30
NQ | 20013599 | DG-CB-1 | DANGLEESON-CRANBROOK | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Voltage at Constrained Conductor | 69.3034 | 69.3049 | 69.3024 | 69.3175 | 69.319 | 69.3165 | 69.3268 | 69.3284 | 69.3265 | 69.3328 | 69.3344 | 69.333 | 69.3376 | 69.338 | 69.3417
NQ | 20013608 | GI-AY-1 | GIRU-AYR | GI-AY-1_Giru - Ayr 1 66 kV | % of Rated A | 3.8005 | 3.4921 | 3.8676 | 4.6564 | 4.2737 | 4.7333 | 5.8801 | 5.3948 | 5.975 | 7.1732 | 6.581 | 7.2887 | 8.2896 | 7.6057 | 8.4236
NQ | 20013608 | GI-AY-1 | GIRU-AYR | GI-AY-1_Giru - Ayr 1 66 kV | Limiting Line Name | TR_LINE 170050_1 | TR_LINE 170050_1 | TR_LINE 170050_1 | TR_LINE 170050_1 | TR_LINE 170050_1 | TR_LINE 170050_1 | TR_LINE 170050_1 | TR_LINE 170050_1 | TR_LINE 170050_1 | TR_LINE 170050_1 | TR_LINE 170050_1 | TR_LINE 170050_1 | TR_LINE 170050_1 | TR_LINE 170050_1 | TR_LINE 170050_1
NQ | 20013608 | GI-AY-1 | GIRU-AYR | GI-AY-1_Giru - Ayr 1 66 kV | Loading (A) | 7.1829 | 7.1937 | 7.1938 | 8.8006 | 8.8039 | 8.8039 | 11.1134 | 11.1133 | 11.1135 | 13.5573 | 13.5569 | 13.5569 | 15.6673 | 15.6678 | 15.6679
NQ | 20013608 | GI-AY-1 | GIRU-AYR | GI-AY-1_Giru - Ayr 1 66 kV | Loading (MVA) | 0.89361 | 0.89665 | 0.89668 | 1.0961 | 1.0986 | 1.0986 | 1.3857 | 1.3857 | 1.3856 | 1.6921 | 1.6922 | 1.6922 | 1.9573 | 1.9573 | 1.9573
NQ | 20013608 | GI-AY-1 | GIRU-AYR | GI-AY-1_Giru - Ayr 1 66 kV | Loading (MW) | 0.28879 | 0.28876 | 0.28876 | 0.69741 | 0.69739 | 0.69739 | 1.1 | 1.1 | 1.1 | 1.4703 | 1.4703 | 1.4703 | 1.7717 | 1.7717 | 1.7717
NQ | 20013608 | GI-AY-1 | GIRU-AYR | GI-AY-1_Giru - Ayr 1 66 kV | Power Factor | 0.32318 | 0.32205 | 0.32204 | 0.63625 | 0.63479 | 0.63478 | 0.79382 | 0.79379 | 0.79384 | 0.86889 | 0.86886 | 0.86886 | 0.90515 | 0.90517 | 0.90517
NQ | 20013608 | GI-AY-1 | GIRU-AYR | GI-AY-1_Giru - Ayr 1 66 kV | Rating (A) | 189 | 206 | 186 | 189 | 206 | 186 | 189 | 206 | 186 | 189 | 206 | 186 | 189 | 206 | 186
NQ | 20013608 | GI-AY-1 | GIRU-AYR | GI-AY-1_Giru - Ayr 1 66 kV | Time | 16:00 | 20:00 | 4:00 | 16:00 | 20:00 | 4:00 | 16:30 | 17:00 | 7:00 | 16:30 | 17:00 | 7:30 | 9:00 | 17:00 | 7:30
NQ | 20013608 | GI-AY-1 | GIRU-AYR | GI-AY-1_Giru - Ayr 1 66 kV | Voltage at Constrained Conductor | 71.8269 | 71.9634 | 71.9646 | 71.9098 | 72.0464 | 72.0476 | 71.987 | 71.9916 | 71.9847 | 72.0608 | 72.0654 | 72.0657 | 72.1296 | 72.1255 | 72.1251
NQ | 20013609 | IN-GR | INGHAM-BLACKRIVER/GREENVALE | IN-GR_Ingham-Black River/Greenvale 66 kV | % of Rated A | 23.0546 | 18.2888 | 19.4039 | 23.0343 | 18.2727 | 19.3869 | 23.0213 | 18.2623 | 19.3759 | 23.0113 | 18.2544 | 19.3675 | 23.0051 | 18.2496 | 19.3624
NQ | 20013609 | IN-GR | INGHAM-BLACKRIVER/GREENVALE | IN-GR_Ingham-Black River/Greenvale 66 kV | Limiting Line Name | TR_LINE 217286_1 | TR_LINE 217286_1 | TR_LINE 217286_1 | TR_LINE 217286_1 | TR_LINE 217286_1 | TR_LINE 217286_1 | TR_LINE 217286_1 | TR_LINE 217286_1 | TR_LINE 217286_1 | TR_LINE 217286_1 | TR_LINE 217286_1 | TR_LINE 217286_1 | TR_LINE 217286_1 | TR_LINE 217286_1 | TR_LINE 217286_1
NQ | 20013609 | IN-GR | INGHAM-BLACKRIVER/GREENVALE | IN-GR_Ingham-Black River/Greenvale 66 kV | Loading (A) | 15.9077 | 15.9112 | 15.9112 | 15.8937 | 15.8972 | 15.8972 | 15.8847 | 15.8882 | 15.8882 | 15.8778 | 15.8813 | 15.8813 | 15.8735 | 15.8771 | 15.8771
NQ | 20013609 | IN-GR | INGHAM-BLACKRIVER/GREENVALE | IN-GR_Ingham-Black River/Greenvale 66 kV | Loading (MVA) | 1.9072 | 1.908 | 1.908 | 1.9058 | 1.9066 | 1.9066 | 1.9049 | 1.9058 | 1.9058 | 1.9042 | 1.9051 | 1.9051 | 1.9039 | 1.9048 | 1.9048
NQ | 20013609 | IN-GR | INGHAM-BLACKRIVER/GREENVALE | IN-GR_Ingham-Black River/Greenvale 66 kV | Loading (MW) | 0.26823 | 0.26823 | 0.26823 | 0.24202 | 0.24203 | 0.24203 | 0.22009 | 0.22009 | 0.22009 | 0.20204 | 0.20204 | 0.20204 | 0.18868 | 0.18869 | 0.18869
NQ | 20013609 | IN-GR | INGHAM-BLACKRIVER/GREENVALE | IN-GR_Ingham-Black River/Greenvale 66 kV | Power Factor | 0.14064 | 0.14058 | 0.14058 | 0.127 | 0.12694 | 0.12694 | 0.11554 | 0.11548 | 0.11548 | 0.1061 | 0.10605 | 0.10605 | 0.099103 | 0.09906 | 0.09906
NQ | 20013609 | IN-GR | INGHAM-BLACKRIVER/GREENVALE | IN-GR_Ingham-Black River/Greenvale 66 kV | Rating (A) | 69 | 87 | 82 | 69 | 87 | 82 | 69 | 87 | 82 | 69 | 87 | 82 | 69 | 87 | 82
NQ | 20013609 | IN-GR | INGHAM-BLACKRIVER/GREENVALE | IN-GR_Ingham-Black River/Greenvale 66 kV | Time | 16:30 | 21:00 | 22:00 | 16:30 | 21:00 | 22:00 | 16:30 | 21:00 | 22:00 | 16:30 | 21:00 | 22:00 | 16:30 | 21:00 | 22:00
NQ | 20013609 | IN-GR | INGHAM-BLACKRIVER/GREENVALE | IN-GR_Ingham-Black River/Greenvale 66 kV | Voltage at Constrained Conductor | 69.219 | 69.2346 | 69.2346 | 69.2282 | 69.244 | 69.244 | 69.2371 | 69.2529 | 69.2529 | 69.2426 | 69.2584 | 69.2584 | 69.2479 | 69.2639 | 69.2639
NQ | 20013610 | MR-CR-1 | MILLCHESTER-CAPERIVER | MR-CR-1_Millchester-Cape River 1 66 kV | % of Rated A | 249.082 | 166.0496 | 170.8312 | 250.705 | 167.1516 | 171.9427 | 252.8326 | 168.0605 | 173.402 | 253.9201 | 168.8031 | 174.1479 | 253.8343 | 169.3464 | 173.9723
NQ | 20013610 | MR-CR-1 | MILLCHESTER-CAPERIVER | MR-CR-1_Millchester-Cape River 1 66 kV | Limiting Line Name | TR_LINE 198899_1 | TR_LINE 198899_1 | TR_LINE 198899_1 | TR_LINE 198899_1 | TR_LINE 198899_1 | TR_LINE 198899_1 | TR_LINE 198899_1 | TR_LINE 198899_1 | TR_LINE 198899_1 | TR_LINE 198899_1 | TR_LINE 198899_1 | TR_LINE 198899_1 | TR_LINE 198899_1 | TR_LINE 198899_1 | TR_LINE 198899_1
NQ | 20013610 | MR-CR-1 | MILLCHESTER-CAPERIVER | MR-CR-1_Millchester-Cape River 1 66 kV | Loading (A) | 386.0771 | 380.2537 | 386.0786 | 388.5927 | 382.7771 | 388.5905 | 391.8905 | 384.8586 | 391.8886 | 393.5761 | 386.5592 | 393.5742 | 393.4431 | 387.8032 | 393.1774
NQ | 20013610 | MR-CR-1 | MILLCHESTER-CAPERIVER | MR-CR-1_Millchester-Cape River 1 66 kV | Loading (MVA) | 42.8843 | 42.3124 | 42.8851 | 43.1371 | 42.5678 | 43.1373 | 43.5339 | 42.7785 | 43.5341 | 43.7042 | 42.9514 | 43.7044 | 43.6972 | 43.0786 | 43.6725
NQ | 20013610 | MR-CR-1 | MILLCHESTER-CAPERIVER | MR-CR-1_Millchester-Cape River 1 66 kV | Loading (MW) | 39.6234 | 38.9563 | 39.6223 | 39.9159 | 39.2514 | 39.9148 | 40.1868 | 39.4945 | 40.1856 | 40.382 | 39.6914 | 40.3809 | 40.3681 | 39.8349 | 40.3352
NQ | 20013610 | MR-CR-1 | MILLCHESTER-CAPERIVER | MR-CR-1_Millchester-Cape River 1 66 kV | Power Factor | 0.92396 | 0.92068 | 0.92392 | 0.92533 | 0.92209 | 0.9253 | 0.92312 | 0.92323 | 0.92308 | 0.92398 | 0.9241 | 0.92395 | 0.92381 | 0.9247 | 0.92358
NQ | 20013610 | MR-CR-1 | MILLCHESTER-CAPERIVER | MR-CR-1_Millchester-Cape River 1 66 kV | Rating (A) | 155 | 229 | 226 | 155 | 229 | 226 | 155 | 229 | 226 | 155 | 229 | 226 | 155 | 229 | 226
NQ | 20013610 | MR-CR-1 | MILLCHESTER-CAPERIVER | MR-CR-1_Millchester-Cape River 1 66 kV | Time | 11:00 | 17:00 | 8:30 | 11:00 | 17:00 | 8:30 | 11:00 | 17:00 | 8:30 | 11:00 | 17:00 | 8:30 | 16:00 | 17:00 | 7:00
NQ | 20013610 | MR-CR-1 | MILLCHESTER-CAPERIVER | MR-CR-1_Millchester-Cape River 1 66 kV | Voltage at Constrained Conductor | 64.1304 | 64.2442 | 64.1313 | 64.0909 | 64.2059 | 64.0915 | 64.136 | 64.1746 | 64.1366 | 64.1113 | 64.1506 | 64.1119 | 64.1226 | 64.1341 | 64.1297
NQ | 20013612 | WO-CT-1 | Woodstock-Charters Towers | WO-CT-1_Woodstock-CHTO No 1 66 kV | % of Rated A | 36.0168 | 33.0353 | 38.3169 | 36.3451 | 33.3445 | 38.6713 | 36.3434 | 33.595 | 38.5213 | 36.3064 | 33.8258 | 38.6291 | 36.2614 | 33.9878 | 38.5826
NQ | 20013612 | WO-CT-1 | Woodstock-Charters Towers | WO-CT-1_Woodstock-CHTO No 1 66 kV | Limiting Line Name | TR_LINE 31878_1 | TR_LINE 31878_1 | TR_LINE 31878_1 | TR_LINE 31878_1 | TR_LINE 31878_1 | TR_LINE 31878_1 | TR_LINE 31878_1 | TR_LINE 31878_1 | TR_LINE 31878_1 | TR_LINE 31878_1 | TR_LINE 31878_1 | TR_LINE 31878_1 | TR_LINE 31878_1 | TR_LINE 31878_1 | TR_LINE 31878_1
NQ | 20013612 | WO-CT-1 | Woodstock-Charters Towers | WO-CT-1_Woodstock-CHTO No 1 66 kV | Loading (A) | 64.4701 | 62.4366 | 64.3724 | 65.0577 | 63.0211 | 64.9678 | 65.0547 | 63.4945 | 64.7158 | 64.9884 | 63.9308 | 64.8969 | 64.908 | 64.237 | 64.8187
NQ | 20013612 | WO-CT-1 | Woodstock-Charters Towers | WO-CT-1_Woodstock-CHTO No 1 66 kV | Loading (MVA) | 7.3203 | 7.1115 | 7.3096 | 7.3789 | 7.1703 | 7.369 | 7.3773 | 7.2179 | 7.3406 | 7.3969 | 7.2629 | 7.3867 | 7.3797 | 7.2947 | 7.3698
NQ | 20013612 | WO-CT-1 | Woodstock-Charters Towers | WO-CT-1_Woodstock-CHTO No 1 66 kV | Loading (MW) | 2.8766 | 2.8428 | 2.8699 | 2.8642 | 2.8313 | 2.8572 | 2.8459 | 2.8223 | 2.8253 | 3.0307 | 2.8256 | 3.0236 | 2.958 | 2.83 | 2.9514
NQ | 20013612 | WO-CT-1 | Woodstock-Charters Towers | WO-CT-1_Woodstock-CHTO No 1 66 kV | Power Factor | 0.39295 | 0.39974 | 0.39262 | 0.38816 | 0.39486 | 0.38773 | 0.38576 | 0.39102 | 0.38488 | 0.40972 | 0.38904 | 0.40932 | 0.40083 | 0.38795 | 0.40047
NQ | 20013612 | WO-CT-1 | Woodstock-Charters Towers | WO-CT-1_Woodstock-CHTO No 1 66 kV | Rating (A) | 179 | 189 | 168 | 179 | 189 | 168 | 179 | 189 | 168 | 179 | 189 | 168 | 179 | 189 | 168
NQ | 20013612 | WO-CT-1 | Woodstock-Charters Towers | WO-CT-1_Woodstock-CHTO No 1 66 kV | Time | 11:00 | 17:00 | 8:30 | 11:00 | 17:00 | 8:30 | 16:00 | 17:00 | 7:00 | 11:00 | 17:00 | 8:30 | 11:00 | 17:00 | 8:30
NQ | 20013612 | WO-CT-1 | Woodstock-Charters Towers | WO-CT-1_Woodstock-CHTO No 1 66 kV | Voltage at Constrained Conductor | 65.5559 | 65.7596 | 65.5594 | 65.484 | 65.6891 | 65.4862 | 65.4724 | 65.6319 | 65.488 | 65.713 | 65.5906 | 65.7152 | 65.6416 | 65.5639 | 65.6443
NQ | 20013617 | PR-BN-1 | Proserpine-Bowen No.1 | PR-BN-1_Proserpine - Bowen No 1 66 kV | % of Rated A | 2.7776 | 2.4251 | 2.6267 | 2.7812 | 2.4282 | 2.6301 | 2.7843 | 2.431 | 2.6331 | 2.7872 | 2.4335 | 2.6358 | 2.7898 | 2.4358 | 2.6383
NQ | 20013617 | PR-BN-1 | Proserpine-Bowen No.1 | PR-BN-1_Proserpine - Bowen No 1 66 kV | Limiting Line Name | TR_LINE 175048_1 | TR_LINE 175048_1 | TR_LINE 175048_1 | TR_LINE 175048_1 | TR_LINE 175048_1 | TR_LINE 175048_1 | TR_LINE 175048_1 | TR_LINE 175048_1 | TR_LINE 175048_1 | TR_LINE 175048_1 | TR_LINE 175048_1 | TR_LINE 175048_1 | TR_LINE 175048_1 | TR_LINE 175048_1 | TR_LINE 175048_1
NQ | 20013617 | PR-BN-1 | Proserpine-Bowen No.1 | PR-BN-1_Proserpine - Bowen No 1 66 kV | Loading (A) | 8.2216 | 8.221 | 8.2216 | 8.2322 | 8.2317 | 8.2323 | 8.2416 | 8.2411 | 8.2416 | 8.2501 | 8.2497 | 8.2501 | 8.2578 | 8.2574 | 8.2579
NQ | 20013617 | PR-BN-1 | Proserpine-Bowen No.1 | PR-BN-1_Proserpine - Bowen No 1 66 kV | Loading (MVA) | 0.99424 | 0.9941 | 0.99424 | 0.99682 | 0.99669 | 0.99683 | 0.99909 | 0.99897 | 0.99909 | 1.0012 | 1.001 | 1.0012 | 1.003 | 1.0029 | 1.003
NQ | 20013617 | PR-BN-1 | Proserpine-Bowen No.1 | PR-BN-1_Proserpine - Bowen No 1 66 kV | Loading (MW) | 0.0011736 | 0.0011735 | 0.0011736 | 0.0011767 | 0.0011765 | 0.0011767 | 0.0011794 | 0.0011792 | 0.0011794 | 0.0011818 | 0.0011817 | 0.0011818 | 0.001184 | 0.0011839 | 0.001184
NQ | 20013617 | PR-BN-1 | Proserpine-Bowen No.1 | PR-BN-1_Proserpine - Bowen No 1 66 kV | Power Factor | 0.0011804 | 0.0011804 | 0.0011804 | 0.0011804 | 0.0011804 | 0.0011804 | 0.0011804 | 0.0011804 | 0.0011804 | 0.0011804 | 0.0011804 | 0.0011804 | 0.0011804 | 0.0011804 | 0.0011804
NQ | 20013617 | PR-BN-1 | Proserpine-Bowen No.1 | PR-BN-1_Proserpine - Bowen No 1 66 kV | Rating (A) | 296 | 339 | 313 | 296 | 339 | 313 | 296 | 339 | 313 | 296 | 339 | 313 | 296 | 339 | 313
NQ | 20013617 | PR-BN-1 | Proserpine-Bowen No.1 | PR-BN-1_Proserpine - Bowen No 1 66 kV | Time | 16:00 | 21:00 | 8:00 | 16:00 | 21:00 | 8:00 | 16:00 | 21:00 | 8:00 | 16:00 | 21:00 | 8:00 | 16:00 | 21:00 | 8:00
NQ | 20013617 | PR-BN-1 | Proserpine-Bowen No.1 | PR-BN-1_Proserpine - Bowen No 1 66 kV | Voltage at Constrained Conductor | 69.8193 | 69.8145 | 69.8194 | 69.9099 | 69.9055 | 69.9102 | 69.9893 | 69.9852 | 69.9895 | 70.0616 | 70.0579 | 70.062 | 70.1274 | 70.1239 | 70.1276
NQ | 20013621 | MF-TP-2 | Max Fulton-TPSS No.02 | MF-TP-2_Max Fulton-TOPO No 2 66 kV | % of Rated A | 15.6436 | 13.6886 | 14.846 | 15.3817 | 13.4599 | 14.5981 | 15.1554 | 13.2624 | 14.3838 | 14.9488 | 13.082 | 14.1882 | 14.7835 | 12.9372 | 14.0312
NQ | 20013621 | MF-TP-2 | Max Fulton-TPSS No.02 | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Limiting Line Name | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1
NQ | 20013621 | MF-TP-2 | Max Fulton-TPSS No.02 | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Loading (A) | 40.3606 | 40.3813 | 40.3813 | 39.6847 | 39.7067 | 39.7067 | 39.1009 | 39.124 | 39.124 | 38.568 | 38.592 | 38.592 | 38.1413 | 38.1649 | 38.1649
NQ | 20013621 | MF-TP-2 | Max Fulton-TPSS No.02 | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Loading (MVA) | 4.8412 | 4.8473 | 4.8473 | 4.7601 | 4.7663 | 4.7663 | 4.69 | 4.6962 | 4.6962 | 4.626 | 4.6322 | 4.6322 | 4.5748 | 4.5807 | 4.5807
NQ | 20013621 | MF-TP-2 | Max Fulton-TPSS No.02 | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Loading (MW) | 1.9385 | 1.9385 | 1.9385 | 1.7135 | 1.7135 | 1.7135 | 1.4959 | 1.496 | 1.496 | 1.2686 | 1.2686 | 1.2686 | 1.0539 | 1.054 | 1.054
NQ | 20013621 | MF-TP-2 | Max Fulton-TPSS No.02 | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Power Factor | 0.40042 | 0.39992 | 0.39992 | 0.35997 | 0.35951 | 0.35951 | 0.31896 | 0.31855 | 0.31855 | 0.27423 | 0.27387 | 0.27387 | 0.23038 | 0.23009 | 0.23009
NQ | 20013621 | MF-TP-2 | Max Fulton-TPSS No.02 | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Rating (A) | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272
NQ | 20013621 | MF-TP-2 | Max Fulton-TPSS No.02 | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Time | 16:30 | 21:00 | 22:00 | 16:30 | 21:00 | 22:00 | 15:30 | 21:00 | 22:00 | 16:00 | 21:00 | 22:00 | 15:30 | 21:00 | 22:00
NQ | 20013621 | MF-TP-2 | Max Fulton-TPSS No.02 | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Voltage at Constrained Conductor | 69.2532 | 69.304 | 69.304 | 69.2528 | 69.3037 | 69.3037 | 69.2511 | 69.3017 | 69.3017 | 69.2491 | 69.2993 | 69.2993 | 69.2491 | 69.2965 | 69.2965
NQ | 20013622 | ST-TS-1 | TownsvilleSouth-Stuart No.1 (607) | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | % of Rated A | 5.9598 | 5.6711 | 6.2024 | 7.3872 | 6.8705 | 7.5141 | 8.704 | 8.009 | 8.7813 | 9.9448 | 9.1381 | 10.0297 | 11.0948 | 10.1517 | 11.1415
NQ | 20013622 | ST-TS-1 | TownsvilleSouth-Stuart No.1 (607) | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Limiting Line Name | TR_LINE 157896_1 | TR_LINE 157896_1 | TR_LINE 157896_1 | TR_LINE 157896_1 | TR_LINE 157896_1 | TR_LINE 157896_1 | TR_LINE 157896_1 | TR_LINE 157896_1 | TR_LINE 157896_1 | TR_LINE 157896_1 | TR_LINE 157896_1 | TR_LINE 157896_1 | TR_LINE 157896_1 | TR_LINE 157896_1 | TR_LINE 157896_1
NQ | 20013622 | ST-TS-1 | TownsvilleSouth-Stuart No.1 (607) | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Loading (A) | 54.8896 | 56.9377 | 56.9377 | 68.0361 | 68.9795 | 68.9795 | 80.1634 | 80.4104 | 80.6124 | 91.5918 | 91.746 | 92.0728 | 102.1806 | 101.9209 | 102.2766
NQ | 20013622 | ST-TS-1 | TownsvilleSouth-Stuart No.1 (607) | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Loading (MVA) | 6.5406 | 6.793 | 6.793 | 8.1065 | 8.229 | 8.229 | 9.5504 | 9.5917 | 9.6042 | 10.9108 | 10.9296 | 10.9686 | 12.172 | 12.1408 | 12.1835
NQ | 20013622 | ST-TS-1 | TownsvilleSouth-Stuart No.1 (607) | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Loading (MW) | 5.8964 | 5.5689 | 5.5689 | 7.6506 | 7.3294 | 7.3294 | 9.2098 | 8.894 | 9.2585 | 10.6489 | 10.6608 | 10.6983 | 11.9538 | 11.9268 | 11.9683
NQ | 20013622 | ST-TS-1 | TownsvilleSouth-Stuart No.1 (607) | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Power Factor | 0.90151 | 0.8198 | 0.8198 | 0.94376 | 0.89067 | 0.89067 | 0.96433 | 0.92726 | 0.96401 | 0.976 | 0.97541 | 0.97535 | 0.98207 | 0.98238 | 0.98233
NQ | 20013622 | ST-TS-1 | TownsvilleSouth-Stuart No.1 (607) | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Rating (A) | 921 | 1003.9999 | 918 | 921 | 1003.9999 | 918 | 921 | 1003.9999 | 918 | 921 | 1003.9999 | 918 | 921 | 1003.9999 | 918
NQ | 20013622 | ST-TS-1 | TownsvilleSouth-Stuart No.1 (607) | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Time | 16:30 | 21:00 | 22:00 | 16:30 | 21:00 | 22:00 | 16:30 | 21:00 | 7:30 | 16:30 | 17:00 | 7:00 | 16:30 | 17:00 | 7:30
NQ | 20013622 | ST-TS-1 | TownsvilleSouth-Stuart No.1 (607) | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Voltage at Constrained Conductor | 68.797 | 68.8816 | 68.8816 | 68.791 | 68.8758 | 68.8758 | 68.7838 | 68.869 | 68.7858 | 68.7761 | 68.7789 | 68.7795 | 68.7752 | 68.7736 | 68.776
NQ | 20013640 | AY-EA-1 | AYR-EASTAYR | AY-EA-1_Ayr - East Ayr No 1 66 kV | % of Rated A | 45.6857 | 39.9717 | 43.1861 | 45.892 | 40.1522 | 43.3813 | 46.1448 | 40.3739 | 43.6194 | 46.4633 | 40.6526 | 43.916 | 46.6934 | 40.8585 | 44.1389
NQ | 20013640 | AY-EA-1 | AYR-EASTAYR | AY-EA-1_Ayr - East Ayr No 1 66 kV | Limiting Line Name | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1
NQ | 20013640 | AY-EA-1 | AYR-EASTAYR | AY-EA-1_Ayr - East Ayr No 1 66 kV | Loading (A) | 118.326 | 118.3163 | 118.3299 | 118.8602 | 118.8504 | 118.8647 | 119.515 | 119.5067 | 119.5172 | 120.34 | 120.3317 | 120.3298 | 120.936 | 120.9413 | 120.9406
NQ | 20013640 | AY-EA-1 | AYR-EASTAYR | AY-EA-1_Ayr - East Ayr No 1 66 kV | Loading (MVA) | 14.7204 | 14.7202 | 14.72 | 14.8039 | 14.8037 | 14.8035 | 14.9017 | 14.9016 | 14.9015 | 15.0199 | 15.0198 | 15.0197 | 15.1088 | 15.1085 | 15.1083
NQ | 20013640 | AY-EA-1 | AYR-EASTAYR | AY-EA-1_Ayr - East Ayr No 1 66 kV | Loading (MW) | 14.6697 | 14.6694 | 14.6692 | 14.7532 | 14.7529 | 14.7527 | 14.851 | 14.8509 | 14.8508 | 14.9693 | 14.9692 | 14.969 | 15.058 | 15.0577 | 15.0575
NQ | 20013640 | AY-EA-1 | AYR-EASTAYR | AY-EA-1_Ayr - East Ayr No 1 66 kV | Power Factor | 0.99655 | 0.99655 | 0.99655 | 0.99657 | 0.99657 | 0.99657 | 0.9966 | 0.9966 | 0.9966 | 0.99663 | 0.99663 | 0.99663 | 0.99664 | 0.99664 | 0.99664
NQ | 20013640 | AY-EA-1 | AYR-EASTAYR | AY-EA-1_Ayr - East Ayr No 1 66 kV | Rating (A) | 259 | 296 | 274 | 259 | 296 | 274 | 259 | 296 | 274 | 259 | 296 | 274 | 259 | 296 | 274
NQ | 20013640 | AY-EA-1 | AYR-EASTAYR | AY-EA-1_Ayr - East Ayr No 1 66 kV | Time | 14:00 | 17:00 | 7:30 | 14:00 | 17:00 | 7:30 | 16:30 | 17:00 | 7:00 | 16:30 | 17:00 | 7:30 | 14:00 | 17:00 | 7:30
NQ | 20013640 | AY-EA-1 | AYR-EASTAYR | AY-EA-1_Ayr - East Ayr No 1 66 kV | Voltage at Constrained Conductor | 71.8257 | 71.8304 | 71.8212 | 71.9084 | 71.9131 | 71.9035 | 71.9867 | 71.9912 | 71.9844 | 72.0604 | 72.065 | 72.0653 | 72.1295 | 72.125 | 72.1246
NQ | 20013643 | ME-BN-1 | Merinda-Bowen | ME-BN-1_Merinda - Bowen No 1 66 kV | % of Rated A | 30.686 | 27.4466 | 30.0693 | 30.5887 | 27.3597 | 29.974 | 30.7445 | 27.4992 | 30.1266 | 31.0953 | 27.8132 | 30.4704 | 31.5683 | 28.2365 | 30.9339
NQ | 20013643 | ME-BN-1 | Merinda-Bowen | ME-BN-1_Merinda - Bowen No 1 66 kV | Limiting Line Name | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1
NQ | 20013643 | ME-BN-1 | Merinda-Bowen | ME-BN-1_Merinda - Bowen No 1 66 kV | Loading (A) | 59.8377 | 59.8336 | 59.8378 | 59.648 | 59.6442 | 59.6482 | 59.9518 | 59.9483 | 59.952 | 60.6358 | 60.6327 | 60.6361 | 61.5583 | 61.5556 | 61.5585
NQ | 20013643 | ME-BN-1 | Merinda-Bowen | ME-BN-1_Merinda - Bowen No 1 66 kV | Loading (MVA) | 7.1988 | 7.1978 | 7.1988 | 7.1808 | 7.1799 | 7.1808 | 7.2215 | 7.2207 | 7.2215 | 7.3076 | 7.3069 | 7.3077 | 7.4224 | 7.4217 | 7.4224
NQ | 20013643 | ME-BN-1 | Merinda-Bowen | ME-BN-1_Merinda - Bowen No 1 66 kV | Loading (MW) | 0.7602 | 0.76019 | 0.7602 | 0.044272 | 0.044266 | 0.044272 | 0.60348 | 0.60349 | 0.60348 | 1.2079 | 1.2079 | 1.2079 | 1.7447 | 1.7447 | 1.7447
NQ | 20013643 | ME-BN-1 | Merinda-Bowen | ME-BN-1_Merinda - Bowen No 1 66 kV | Power Factor | 0.1056 | 0.10561 | 0.1056 | 0.0061654 | 0.0061652 | 0.0061654 | 0.083567 | 0.083578 | 0.083567 | 0.1653 | 0.16531 | 0.16529 | 0.23506 | 0.23508 | 0.23506
NQ | 20013643 | ME-BN-1 | Merinda-Bowen | ME-BN-1_Merinda - Bowen No 1 66 kV | Rating (A) | 195 | 218 | 199 | 195 | 218 | 199 | 195 | 218 | 199 | 195 | 218 | 199 | 195 | 218 | 199
NQ | 20013643 | ME-BN-1 | Merinda-Bowen | ME-BN-1_Merinda - Bowen No 1 66 kV | Time | 16:00 | 21:00 | 8:00 | 16:00 | 21:00 | 8:00 | 16:00 | 21:00 | 8:00 | 16:00 | 21:00 | 8:00 | 16:00 | 21:00 | 8:00
NQ | 20013643 | ME-BN-1 | Merinda-Bowen | ME-BN-1_Merinda - Bowen No 1 66 kV | Voltage at Constrained Conductor | 69.4581 | 69.4533 | 69.4583 | 69.5049 | 69.5005 | 69.5051 | 69.5448 | 69.5407 | 69.545 | 69.5805 | 69.5768 | 69.5809 | 69.6139 | 69.6104 | 69.6142
NQ | 20013651 | AV-GA-1 | GARBUTT-AITKENVALE | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | % of Rated A | 2.7635 | 2.4522 | 2.6705 | 1.2409 | 1.099 | 1.1965 | 0.57421 | 0.51954 | 0.56557 | 1.7371 | 1.5498 | 1.6866 | 2.8976 | 2.5866 | 2.8223
NQ | 20013651 | AV-GA-1 | GARBUTT-AITKENVALE | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Limiting Line Name | TR_LINE 34618_1 | TR_LINE 34618_1 | TR_LINE 34618_1 | TR_LINE 34618_1 | TR_LINE 34618_1 | TR_LINE 34618_1 | TR_LINE 34618_1 | TR_LINE 34618_1 | TR_LINE 34618_1 | TR_LINE 34618_1 | TR_LINE 34618_1 | TR_LINE 34618_1 | TR_LINE 34618_1 | TR_LINE 34618_1 | TR_LINE 34618_1
NQ | 20013651 | AV-GA-1 | GARBUTT-AITKENVALE | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Loading (A) | 12.7123 | 12.6535 | 12.6583 | 5.7082 | 5.6709 | 5.6715 | 2.6414 | 2.6808 | 2.6808 | 7.9905 | 7.9971 | 7.9945 | 13.3288 | 13.3468 | 13.3775
NQ | 20013651 | AV-GA-1 | GARBUTT-AITKENVALE | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Loading (MVA) | 1.5319 | 1.526 | 1.5255 | 0.6881 | 0.68413 | 0.68421 | 0.3185 | 0.32349 | 0.32349 | 0.96367 | 0.96449 | 0.96416 | 1.6077 | 1.6099 | 1.6137
NQ | 20013651 | AV-GA-1 | GARBUTT-AITKENVALE | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Loading (MW) | 1.4905 | 1.483 | 1.4845 | 0.61743 | 0.60996 | 0.61002 | 0.20268 | 0.1887 | 0.1887 | 0.94248 | 0.9433 | 0.94286 | 1.5997 | 1.602 | 1.6056
NQ | 20013651 | AV-GA-1 | GARBUTT-AITKENVALE | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Power Factor | 0.97292 | 0.97179 | 0.97317 | 0.8973 | 0.89157 | 0.89157 | 0.63638 | 0.58334 | 0.58334 | 0.978 | 0.97803 | 0.9779 | 0.99498 | 0.99511 | 0.995
NQ | 20013651 | AV-GA-1 | GARBUTT-AITKENVALE | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Rating (A) | 460 | 516 | 474 | 460 | 516 | 474 | 460 | 516 | 474 | 460 | 516 | 474 | 460 | 516 | 474
NQ | 20013651 | AV-GA-1 | GARBUTT-AITKENVALE | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Time | 11:00 | 20:00 | 8:30 | 11:00 | 20:00 | 4:00 | 16:30 | 21:00 | 22:00 | 16:30 | 17:00 | 7:30 | 16:30 | 17:00 | 7:30
NQ | 20013651 | AV-GA-1 | GARBUTT-AITKENVALE | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Voltage at Constrained Conductor | 69.5757 | 69.63 | 69.5766 | 69.5969 | 69.6513 | 69.6513 | 69.6173 | 69.6674 | 69.6674 | 69.6299 | 69.6314 | 69.63 | 69.6404 | 69.6409 | 69.6442
NQ | 20013655 | DG-RM-1 | DANGLEESON-RASMUSSEN | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | % of Rated A | 14.5697 | 9.8577 | 9.9874 | 13.3381 | 9.0683 | 9.1876 | 12.1816 | 8.3302 | 8.4398 | 11.0689 | 7.6232 | 7.7235 | 10.0053 | 6.9711 | 7.0629
NQ | 20013655 | DG-RM-1 | DANGLEESON-RASMUSSEN | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Limiting Line Name | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1
NQ | 20013655 | DG-RM-1 | DANGLEESON-RASMUSSEN | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Loading (A) | 36.57 | 37.952 | 37.952 | 33.4786 | 34.913 | 34.913 | 30.5758 | 32.0711 | 32.0712 | 27.783 | 29.3491 | 29.3492 | 25.1132 | 26.8389 | 26.8389
NQ | 20013655 | DG-RM-1 | DANGLEESON-RASMUSSEN | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Loading (MVA) | 4.3895 | 4.5587 | 4.5587 | 4.0192 | 4.1945 | 4.1945 | 3.6712 | 3.8536 | 3.8536 | 3.3362 | 3.5268 | 3.5268 | 3.0158 | 3.2253 | 3.2253
NQ | 20013655 | DG-RM-1 | DANGLEESON-RASMUSSEN | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Loading (MW) | 4.1225 | 4.2081 | 4.2081 | 3.7218 | 3.806 | 3.806 | 3.339 | 3.4219 | 3.4219 | 2.963 | 3.0449 | 3.0449 | 2.5862 | 2.686 | 2.686
NQ | 20013655 | DG-RM-1 | DANGLEESON-RASMUSSEN | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Power Factor | 0.93917 | 0.9231 | 0.9231 | 0.92601 | 0.90739 | 0.90739 | 0.90951 | 0.88799 | 0.88799 | 0.88815 | 0.86335 | 0.86335 | 0.85755 | 0.83278 | 0.83278
NQ | 20013655 | DG-RM-1 | DANGLEESON-RASMUSSEN | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Rating (A) | 251 | 385 | 380 | 251 | 385 | 380 | 251 | 385 | 380 | 251 | 385 | 380 | 251 | 385 | 380
NQ | 20013655 | DG-RM-1 | DANGLEESON-RASMUSSEN | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Time | 16:30 | 21:00 | 22:00 | 16:30 | 21:00 | 22:00 | 16:30 | 21:00 | 22:00 | 16:30 | 21:00 | 22:00 | 16:30 | 21:00 | 22:00
NQ | 20013655 | DG-RM-1 | DANGLEESON-RASMUSSEN | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Voltage at Constrained Conductor | 69.2989 | 69.3495 | 69.3495 | 69.3128 | 69.3635 | 69.3635 | 69.322 | 69.3728 | 69.3728 | 69.3279 | 69.3788 | 69.3788 | 69.3326 | 69.3825 | 69.3825
NQ | 20013660 | MF-TP-1 | Max Fulton-TPSS No.01 | MF-TP-1_Max Fulton-TOPO No 1 66 kV | % of Rated A | 6.2842 | 5.4958 | 5.9607 | 5.5639 | 4.8659 | 5.2776 | 4.8693 | 4.2585 | 4.6187 | 4.1463 | 3.6261 | 3.9328 | 3.4678 | 3.0329 | 3.2893
NQ | 20013660 | MF-TP-1 | Max Fulton-TPSS No.01 | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Limiting Line Name | TR_LINE 121605_1 | TR_LINE 121605_1 | TR_LINE 121605_1 | TR_LINE 121605_1 | TR_LINE 121605_1 | TR_LINE 121605_1 | TR_LINE 121605_1 | TR_LINE 121605_1 | TR_LINE 121605_1 | TR_LINE 121605_1 | TR_LINE 121605_1 | TR_LINE 121605_1 | TR_LINE 121605_1 | TR_LINE 121605_1 | TR_LINE 121605_1
NQ | 20013660 | MF-TP-1 | Max Fulton-TPSS No.01 | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Loading (A) | 16.2131 | 16.2125 | 16.2131 | 14.3549 | 14.3544 | 14.355 | 12.5628 | 12.5624 | 12.5628 | 10.6973 | 10.6971 | 10.6973 | 8.947 | 8.9469 | 8.947
NQ | 20013660 | MF-TP-1 | Max Fulton-TPSS No.01 | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Loading (MVA) | 1.9441 | 1.9441 | 1.9441 | 1.7213 | 1.7213 | 1.7213 | 1.5064 | 1.5064 | 1.5064 | 1.2827 | 1.2827 | 1.2827 | 1.0728 | 1.0728 | 1.0728
NQ | 20013660 | MF-TP-1 | Max Fulton-TPSS No.01 | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Loading (MW) | 1.9318 | 1.9318 | 1.9318 | 1.7068 | 1.7068 | 1.7068 | 1.4892 | 1.4892 | 1.4892 | 1.2618 | 1.2618 | 1.2618 | 1.0472 | 1.0472 | 1.0472
NQ | 20013660 | MF-TP-1 | Max Fulton-TPSS No.01 | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Power Factor | 0.99365 | 0.99365 | 0.99365 | 0.99156 | 0.99156 | 0.99156 | 0.9886 | 0.98859 | 0.98859 | 0.98377 | 0.98377 | 0.98377 | 0.97617 | 0.97617 | 0.97617
NQ | 20013660 | MF-TP-1 | Max Fulton-TPSS No.01 | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Rating (A) | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272
NQ | 20013660 | MF-TP-1 | Max Fulton-TPSS No.01 | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Time | 9:00 | 17:00 | 7:30 | 9:00 | 17:00 | 7:30 | 16:00 | 17:00 | 7:00 | 16:30 | 17:00 | 7:30 | 16:00 | 17:00 | 7:00
NQ | 20013660 | MF-TP-1 | Max Fulton-TPSS No.01 | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Voltage at Constrained Conductor | 69.2311 | 69.2338 | 69.2311 | 69.2307 | 69.2333 | 69.2306 | 69.2291 | 69.2312 | 69.2292 | 69.2271 | 69.2285 | 69.2274 | 69.2251 | 69.2255 | 69.2252
NQ | 20013662 | ST-TS-2 | TownsvilleSouth-Stuart No.2 (608) | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | % of Rated A | 6.0566 | 5.7632 | 6.3031 | 7.5072 | 6.982 | 7.6361 | 8.8453 | 8.1391 | 8.9239 | 10.1063 | 9.2865 | 10.1926 | 11.275 | 10.3166 | 11.3224
NQ | 20013662 | ST-TS-2 | TownsvilleSouth-Stuart No.2 (608) | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Limiting Line Name | TR_LINE 157898_1 | TR_LINE 157898_1 | TR_LINE 157898_1 | TR_LINE 157898_1 | TR_LINE 157898_1 | TR_LINE 157898_1 | TR_LINE 157898_1 | TR_LINE 157898_1 | TR_LINE 157898_1 | TR_LINE 157898_1 | TR_LINE 157898_1 | TR_LINE 157898_1 | TR_LINE 157898_1 | TR_LINE 157898_1 | TR_LINE 157898_1
NQ | 20013662 | ST-TS-2 | TownsvilleSouth-Stuart No.2 (608) | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Loading (A) | 55.781 | 57.8624 | 57.8624 | 69.141 | 70.0997 | 70.0997 | 81.4653 | 81.7162 | 81.9215 | 93.0793 | 93.236 | 93.5681 | 103.8399 | 103.576 | 103.9375
NQ | 20013662 | ST-TS-2 | TownsvilleSouth-Stuart No.2 (608) | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Loading (MVA) | 6.6468 | 6.9033 | 6.9033 | 8.238 | 8.3626 | 8.3626 | 9.7054 | 9.7474 | 9.7601 | 11.0878 | 11.1069 | 11.1466 | 12.3695 | 12.3378 | 12.3813
NQ | 20013662 | ST-TS-2 | TownsvilleSouth-Stuart No.2 (608) | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Loading (MW) | 5.9677 | 5.6258 | 5.6258 | 7.7515 | 7.416 | 7.416 | 9.3373 | 9.0072 | 9.3866 | 10.801 | 10.8128 | 10.8508 | 12.1277 | 12.1005 | 12.1425
NQ | 20013662 | ST-TS-2 | TownsvilleSouth-Stuart No.2 (608) | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Power Factor | 0.89783 | 0.81495 | 0.81495 | 0.94094 | 0.88681 | 0.88681 | 0.96207 | 0.92407 | 0.96174 | 0.97413 | 0.97352 | 0.97346 | 0.98045 | 0.98077 | 0.98072
NQ | 20013662 | ST-TS-2 | TownsvilleSouth-Stuart No.2 (608) | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Rating (A) | 921 | 1003.9999 | 918 | 921 | 1003.9999 | 918 | 921 | 1003.9999 | 918 | 921 | 1003.9999 | 918 | 921 | 1003.9999 | 918
NQ | 20013662 | ST-TS-2 | TownsvilleSouth-Stuart No.2 (608) | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Time | 16:30 | 21:00 | 22:00 | 16:30 | 21:00 | 22:00 | 16:30 | 21:00 | 7:30 | 16:30 | 17:00 | 7:00 | 16:30 | 17:00 | 7:30
NQ | 20013662 | ST-TS-2 | TownsvilleSouth-Stuart No.2 (608) | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Voltage at Constrained Conductor | 68.7964 | 68.881 | 68.881 | 68.7903 | 68.8751 | 68.8751 | 68.7831 | 68.8681 | 68.785 | 68.7753 | 68.778 | 68.7787 | 68.7744 | 68.7728 | 68.7752
NQ | 25267806 | DG-PA-1 | DANGLEESON-PETERARLETT | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | % of Rated A | 22.0293 | 21.0944 | 23.4293 | 22.2115 | 21.2643 | 23.618 | 22.3477 | 21.3915 | 23.7593 | 22.4355 | 21.4735 | 23.8503 | 22.4362 | 21.5208 | 23.9029
NQ | 25267806 | DG-PA-1 | DANGLEESON-PETERARLETT | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Limiting Line Name | TR_LINE 172527_2 | TR_LINE 172527_2 | TR_LINE 172527_2 | TR_LINE 172527_2 | TR_LINE 172527_2 | TR_LINE 172527_2 | TR_LINE 172527_2 | TR_LINE 172527_2 | TR_LINE 172527_2 | TR_LINE 172527_2 | TR_LINE 172527_2 | TR_LINE 172527_2 | TR_LINE 172527_2 | TR_LINE 172527_2 | TR_LINE 172527_2
NQ | 25267806 | DG-PA-1 | DANGLEESON-PETERARLETT | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Loading (A) | 121.3814 | 122.7697 | 122.7697 | 122.3854 | 123.7584 | 123.7584 | 123.136 | 124.4985 | 124.4985 | 123.6197 | 124.9757 | 124.9758 | 123.6232 | 125.2513 | 125.2513
NQ | 25267806 | DG-PA-1 | DANGLEESON-PETERARLETT | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Loading (MVA) | 14.5533 | 14.7323 | 14.7323 | 14.6766 | 14.854 | 14.854 | 14.7687 | 14.9449 | 14.9449 | 14.8281 | 15.0036 | 15.0036 | 14.8298 | 15.0377 | 15.0377
NQ | 25267806 | DG-PA-1 | DANGLEESON-PETERARLETT | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Loading (MW) | 14.5457 | 14.7042 | 14.7042 | 14.6677 | 14.8236 | 14.8236 | 14.7582 | 14.9117 | 14.9117 | 14.8159 | 14.9674 | 14.9674 | 14.8147 | 14.9983 | 14.9983
NQ | 25267806 | DG-PA-1 | DANGLEESON-PETERARLETT | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Power Factor | 0.99948 | 0.9981 | 0.9981 | 0.99939 | 0.99795 | 0.99795 | 0.99929 | 0.99778 | 0.99778 | 0.99918 | 0.99759 | 0.99759 | 0.99898 | 0.99738 | 0.99738
NQ | 25267806 | DG-PA-1 | DANGLEESON-PETERARLETT | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Rating (A) | 551 | 582 | 524 | 551 | 582 | 524 | 551 | 582 | 524 | 551 | 582 | 524 | 551 | 582 | 524
NQ | 25267806 | DG-PA-1 | DANGLEESON-PETERARLETT | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Time | 16:30 | 21:00 | 22:00 | 16:30 | 21:00 | 22:00 | 16:30 | 21:00 | 22:00 | 16:30 | 21:00 | 22:00 | 16:30 | 21:00 | 22:00
NQ | 25267806 | DG-PA-1 | DANGLEESON-PETERARLETT | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Voltage at Constrained Conductor | 69.2226 | 69.2817 | 69.2817 | 69.2367 | 69.2959 | 69.2959 | 69.2462 | 69.3056 | 69.3056 | 69.2527 | 69.3122 | 69.3122 | 69.2588 | 69.3166 | 69.3166
NQ | 25267807 | PA-RP-1 | PETERARLETT-ROSSPLAINS | PA-RP-1_Peter Arlett-Ross Plains 66 kV | % of Rated A | 29.9726 | 26.7268 | 28.9868 | 31.8951 | 28.3956 | 30.7967 | 33.5974 | 29.875 | 32.4012 | 35.1151 | 31.1951 | 33.8329 | 36.3192 | 32.3356 | 35.0698
NQ | 25267807 | PA-RP-1 | PETERARLETT-ROSSPLAINS | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Limiting Line Name | TR_LINE 32958_1 | TR_LINE 32958_1 | TR_LINE 32958_1 | TR_LINE 32958_1 | TR_LINE 32958_1 | TR_LINE 32958_1 | TR_LINE 32958_1 | TR_LINE 32958_1 | TR_LINE 32958_1 | TR_LINE 32958_1 | TR_LINE 32958_1 | TR_LINE 32958_1 | TR_LINE 32958_1 | TR_LINE 32958_1 | TR_LINE 32958_1
NQ | 25267807 | PA-RP-1 | PETERARLETT-ROSSPLAINS | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Loading (A) | 77.3294 | 78.8439 | 78.844 | 82.2894 | 83.7669 | 83.767 | 86.6814 | 88.1312 | 88.1312 | 90.5969 | 92.0255 | 92.0255 | 93.7035 | 95.3899 | 95.3899
NQ | 25267807 | PA-RP-1 | PETERARLETT-ROSSPLAINS | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Loading (MVA) | 9.259 | 9.4495 | 9.4495 | 9.8545 | 10.0412 | 10.0412 | 10.3816 | 10.5655 | 10.5655 | 10.8513 | 11.0332 | 11.0332 | 11.2243 | 11.4371 | 11.4371
NQ | 25267807 | PA-RP-1 | PETERARLETT-ROSSPLAINS | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Loading (MW) | 9.2465 | 9.4045 | 9.4045 | 9.8418 | 9.9972 | 9.9972 | 10.3683 | 10.5213 | 10.5213 | 10.8371 | 10.9881 | 10.9881 | 11.2077 | 11.3907 | 11.3907
NQ | 25267807 | PA-RP-1 | PETERARLETT-ROSSPLAINS | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Power Factor | 0.99865 | 0.99524 | 0.99524 | 0.99871 | 0.99562 | 0.99562 | 0.99872 | 0.99582 | 0.99582 | 0.99869 | 0.99591 | 0.99591 | 0.99852 | 0.99594 | 0.99594
NQ | 25267807 | PA-RP-1 | PETERARLETT-ROSSPLAINS | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Rating (A) | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272
NQ | 25267807 | PA-RP-1 | PETERARLETT-ROSSPLAINS | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Time | 16:30 | 21:00 | 22:00 | 16:30 | 21:00 | 22:00 | 16:30 | 21:00 | 22:00 | 16:30 | 21:00 | 22:00 | 16:30 | 21:00 | 22:00
NQ | 25267807 | PA-RP-1 | PETERARLETT-ROSSPLAINS | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Voltage at Constrained Conductor | 69.1287 | 69.1956 | 69.1956 | 69.1402 | 69.2072 | 69.2072 | 69.1477 | 69.2149 | 69.2149 | 69.1526 | 69.22 | 69.22 | 69.1583 | 69.2233 | 69.2233
NQ | 25273587 | RI-JC-1 | Richmond-Julia Creek No.1 66kV feeder | RI-JC-1_Richmond-Julia Creek No 1 66 kV | % of Rated A | 5.0301 | 4.6021 | 4.2517 | 5.0239 | 4.5965 | 4.2464 | 5.0328 | 4.6035 | 4.254 | 5.0447 | 4.6144 | 4.264 | 5.0558 | 4.6237 | 4.2734
NQ | 25273587 | RI-JC-1 | Richmond-Julia Creek No.1 66kV feeder | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Limiting Line Name | TR_LINE 32331_1 | TR_LINE 32331_1 | TR_LINE 32331_1 | TR_LINE 32331_1 | TR_LINE 32331_1 | TR_LINE 32331_1 | TR_LINE 32331_1 | TR_LINE 32331_1 | TR_LINE 32331_1 | TR_LINE 32331_1 | TR_LINE 32331_1 | TR_LINE 32331_1 | TR_LINE 32331_1 | TR_LINE 32331_1 | TR_LINE 32331_1
NQ | 25273587 | RI-JC-1 | Richmond-Julia Creek No.1 66kV feeder | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Loading (A) | 17.8569 | 17.8561 | 17.8571 | 17.8349 | 17.8343 | 17.8351 | 17.8665 | 17.8617 | 17.8667 | 17.9086 | 17.9039 | 17.9087 | 17.9481 | 17.94 | 17.9484
NQ | 25273587 | RI-JC-1 | Richmond-Julia Creek No.1 66kV feeder | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Loading (MVA) | 2.1334 | 2.1332 | 2.1334 | 2.1335 | 2.1334 | 2.1336 | 2.14 | 2.1388 | 2.14 | 2.1465 | 2.1454 | 2.1466 | 2.1527 | 2.1508 | 2.1528
NQ | 25273587 | RI-JC-1 | Richmond-Julia Creek No.1 66kV feeder | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Loading (MW) | 0.2036 | 0.2036 | 0.2036 | 0.066308 | 0.066307 | 0.066308 | 0.036102 | 0.036109 | 0.036101 | 0.10837 | 0.10838 | 0.10837 | 0.15342 | 0.15343 | 0.15342
NQ | 25273587 | RI-JC-1 | Richmond-Julia Creek No.1 66kV feeder | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Power Factor | 0.095434 | 0.095442 | 0.095432 | 0.031079 | 0.03108 | 0.031079 | 0.01687 | 0.016883 | 0.01687 | 0.050487 | 0.050517 | 0.050487 | 0.071265 | 0.071336 | 0.071263
NQ | 25273587 | RI-JC-1 | Richmond-Julia Creek No.1 66kV feeder | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Rating (A) | 355 | 388 | 420 | 355 | 388 | 420 | 355 | 388 | 420 | 355 | 388 | 420 | 355 | 388 | 420
NQ | 25273587 | RI-JC-1 | Richmond-Julia Creek No.1 66kV feeder | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Time | 9:00 | 17:00 | 7:30 | 9:00 | 17:00 | 7:30 | 9:00 | 17:00 | 7:30 | 16:00 | 17:00 | 7:30 | 15:30 | 17:00 | 7:30
NQ | 25273587 | RI-JC-1 | Richmond-Julia Creek No.1 66kV feeder | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Voltage at Constrained Conductor | 68.9765 | 68.9734 | 68.977 | 69.067 | 69.0647 | 69.0675 | 69.1517 | 69.1329 | 69.1522 | 69.2018 | 69.1835 | 69.2023 | 69.249 | 69.2171 | 69.25
NQ | 25275522 | 6266 | BOHLE-BLACK RIVER 2 | 6266_Bohle-Black River No 2 66 kV | % of Rated A | 53.5116 | 49.8168 | 54.9429 | 54.7742 | 50.9922 | 56.2392 | 55.9687 | 52.105 | 57.4657 | 57.1013 | 53.1595 | 58.6286 | 58.1229 | 54.1117 | 59.6759
NQ | 25275522 | 6266 | BOHLE-BLACK RIVER 2 | 6266_Bohle-Black River No 2 66 kV | Limiting Line Name | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1
NQ | 25275522 | 6266 | BOHLE-BLACK RIVER 2 | 6266_Bohle-Black River No 2 66 kV | Loading (A) | 390.0996 | 390.0655 | 390.0945 | 399.3036 | 399.2686 | 399.2985 | 408.0116 | 407.9824 | 408.0064 | 416.2686 | 416.2385 | 416.2632 | 423.7157 | 423.6943 | 423.6989
NQ | 25275522 | 6266 | BOHLE-BLACK RIVER 2 | 6266_Bohle-Black River No 2 66 kV | Loading (MVA) | 47.286 | 47.2859 | 47.286 | 48.4381 | 48.438 | 48.4381 | 49.5257 | 49.5256 | 49.5256 | 50.5534 | 50.5533 | 50.5534 | 51.4788 | 51.4788 | 51.4788
NQ | 25275522 | 6266 | BOHLE-BLACK RIVER 2 | 6266_Bohle-Black River No 2 66 kV | Loading (MW) | 46.6411 | 46.6411 | 46.6411 | 47.8019 | 47.8019 | 47.8019 | 48.8951 | 48.8952 | 48.8951 | 49.9259 | 49.926 | 49.9259 | 50.8524 | 50.8525 | 50.8525
NQ | 25275522 | 6266 | BOHLE-BLACK RIVER 2 | 6266_Bohle-Black River No 2 66 kV | Power Factor | 0.98636 | 0.98636 | 0.98636 | 0.98687 | 0.98687 | 0.98687 | 0.98727 | 0.98727 | 0.98727 | 0.98759 | 0.98759 | 0.98759 | 0.98783 | 0.98783 | 0.98783
NQ | 25275522 | 6266 | BOHLE-BLACK RIVER 2 | 6266_Bohle-Black River No 2 66 kV | Rating (A) | 729 | 783 | 710 | 729 | 783 | 710 | 729 | 783 | 710 | 729 | 783 | 710 | 729 | 783 | 710
NQ | 25275522 | 6266 | BOHLE-BLACK RIVER 2 | 6266_Bohle-Black River No 2 66 kV | Time | 11:00 | 17:00 | 8:30 | 11:00 | 17:00 | 8:30 | 11:00 | 17:00 | 8:30 | 11:00 | 17:00 | 8:30 | 16:00 | 17:00 | 7:00
NQ | 25275522 | 6266 | BOHLE-BLACK RIVER 2 | 6266_Bohle-Black River No 2 66 kV | Voltage at Constrained Conductor | 69.9837 | 69.9896 | 69.9846 | 70.0363 | 70.0423 | 70.0372 | 70.0805 | 70.0854 | 70.0814 | 70.1158 | 70.1207 | 70.1167 | 70.1445 | 70.1479 | 70.1472
NQ | 25275871 | KA-AY-01 | AYR-KALAMIA | KA-AY-01_Ayr - Kalamia No 1 66 kV | % of Rated A | 11.1413 | 9.9415 | 10.8688 | 11.3464 | 10.1245 | 11.0689 | 11.533 | 10.2911 | 11.2507 | 11.7065 | 10.446 | 11.4188 | 11.8568 | 10.5813 | 11.5669
NQ | 25275871 | KA-AY-01 | AYR-KALAMIA | KA-AY-01_Ayr - Kalamia No 1 66 kV | Limiting Line Name | TR_LINE 31747_1 | TR_LINE 31747_1 | TR_LINE 31747_1 | TR_LINE 31747_1 | TR_LINE 31747_1 | TR_LINE 31747_1 | TR_LINE 31747_1 | TR_LINE 31747_1 | TR_LINE 31747_1 | TR_LINE 31747_1 | TR_LINE 31747_1 | TR_LINE 31747_1 | TR_LINE 31747_1 | TR_LINE 31747_1 | TR_LINE 31747_1
NQ | 25275871 | KA-AY-01 | AYR-KALAMIA | KA-AY-01_Ayr - Kalamia No 1 66 kV | Loading (A) | 22.1711 | 22.1696 | 22.1724 | 22.579 | 22.5774 | 22.5804 | 22.9503 | 22.9489 | 22.9511 | 23.2957 | 23.2942 | 23.2941 | 23.5947 | 23.596 | 23.5962
NQ | 25275871 | KA-AY-01 | AYR-KALAMIA | KA-AY-01_Ayr - Kalamia No 1 66 kV | Loading (MVA) | 2.7582 | 2.7582 | 2.7582 | 2.8122 | 2.8122 | 2.8122 | 2.8616 | 2.8616 | 2.8616 | 2.9076 | 2.9076 | 2.9076 | 2.9478 | 2.9478 | 2.9478
NQ | 25275871 | KA-AY-01 | AYR-KALAMIA | KA-AY-01_Ayr - Kalamia No 1 66 kV | Loading (MW) | 2.7549 | 2.7549 | 2.7549 | 2.8091 | 2.8091 | 2.8091 | 2.8586 | 2.8586 | 2.8586 | 2.9048 | 2.9048 | 2.9048 | 2.945 | 2.945 | 2.945
NQ | 25275871 | KA-AY-01 | AYR-KALAMIA | KA-AY-01_Ayr - Kalamia No 1 66 kV | Power Factor | 0.9988 | 0.9988 | 0.9988 | 0.9989 | 0.99889 | 0.9989 | 0.99897 | 0.99897 | 0.99897 | 0.99903 | 0.99903 | 0.99903 | 0.99908 | 0.99908 | 0.99908
NQ | 25275871 | KA-AY-01 | AYR-KALAMIA | KA-AY-01_Ayr - Kalamia No 1 66 kV | Rating (A) | 199 | 223 | 204 | 199 | 223 | 204 | 199 | 223 | 204 | 199 | 223 | 204 | 199 | 223 | 204
NQ | 25275871 | KA-AY-01 | AYR-KALAMIA | KA-AY-01_Ayr - Kalamia No 1 66 kV | Time | 9:00 | 17:00 | 7:30 | 9:00 | 17:00 | 7:30 | 16:30 | 17:00 | 7:00 | 16:30 | 17:00 | 7:30 | 9:00 | 17:00 | 7:30
NQ | 25275871 | KA-AY-01 | AYR-KALAMIA | KA-AY-01_Ayr - Kalamia No 1 66 kV | Voltage at Constrained Conductor | 71.8253 | 71.8304 | 71.8212 | 71.9089 | 71.914 | 71.9044 | 71.9876 | 71.9922 | 71.9853 | 72.0613 | 72.0659 | 72.0662 | 72.1301 | 72.126 | 72.1256
NQ | 25279916 | BC-IN-1 | Black River - Ingham | BC-IN-1_Black River - Ingham No 1 66 kV | % of Rated A | 6.3168 | 5.2508 | 5.8157 | 7.9801 | 6.8176 | 7.5511 | 9.5164 | 8.4867 | 9.3997 | 11.1463 | 10.2258 | 11.326 | 12.8977 | 11.8328 | 13.1053
NQ | 25279916 | BC-IN-1 | Black River - Ingham | BC-IN-1_Black River - Ingham No 1 66 kV | Limiting Line Name | TR_LINE 32944_1 | TR_LINE 32345_1 | TR_LINE 32345_1 | TR_LINE 32944_1 | TR_LINE 32345_1 | TR_LINE 32345_1 | TR_LINE 32944_1 | TR_LINE 214252_1 | TR_LINE 214252_1 | TR_LINE 214252_1 | TR_LINE 214252_1 | TR_LINE 214252_1 | TR_LINE 214252_1 | TR_LINE 214252_1 | TR_LINE 214252_1
NQ | 25279916 | BC-IN-1 | Black River - Ingham | BC-IN-1_Black River - Ingham No 1 66 kV | Loading (A) | 8.7171 | 10.8166 | 10.8172 | 11.0125 | 14.0442 | 14.0451 | 13.1326 | 17.4825 | 17.4834 | 21.0666 | 21.0652 | 21.0663 | 24.3767 | 24.3755 | 24.3758
NQ | 25279916 | BC-IN-1 | Black River - Ingham | BC-IN-1_Black River - Ingham No 1 66 kV | Loading (MVA) | 1.0587 | 1.3124 | 1.3124 | 1.3391 | 1.7058 | 1.7058 | 1.5988 | 2.1233 | 2.1233 | 2.5599 | 2.56 | 2.5599 | 2.9636 | 2.9636 | 2.9636
NQ | 25279916 | BC-IN-1 | Black River - Ingham | BC-IN-1_Black River - Ingham No 1 66 kV | Loading (MW) | 1.0586 | 1.2513 | 1.2513 | 1.339 | 1.6616 | 1.6616 | 1.5984 | 2.0757 | 2.0757 | 2.5232 | 2.5232 | 2.5232 | 2.9343 | 2.9343 | 2.9343
NQ | 25279916 | BC-IN-1 | Black River - Ingham | BC-IN-1_Black River - Ingham No 1 66 kV | Power Factor | 0.99991 | 0.95338 | 0.9534 | 0.99985 | 0.97406 | 0.97407 | 0.99979 | 0.97757 | 0.97757 | 0.98565 | 0.98565 | 0.98565 | 0.99011 | 0.9901 | 0.9901
NQ | 25279916 | BC-IN-1 | Black River - Ingham | BC-IN-1_Black River - Ingham No 1 66 kV | Rating (A) | 138 | 206 | 186 | 138 | 206 | 186 | 138 | 206 | 186 | 189 | 206 | 186 | 189 | 206 | 186
NQ | 25279916 | BC-IN-1 | Black River - Ingham | BC-IN-1_Black River - Ingham No 1 66 kV | Time | 11:00 | 17:00 | 8:30 | 11:00 | 17:00 | 8:30 | 11:00 | 17:00 | 8:30 | 11:00 | 17:00 | 8:30 | 16:00 | 17:00 | 7:00
NQ | 25279916 | BC-IN-1 | Black River - Ingham | BC-IN-1_Black River - Ingham No 1 66 kV | Voltage at Constrained Conductor | 70.1168 | 70.0532 | 70.0481 | 70.2075 | 70.1264 | 70.1213 | 70.2869 | 70.1212 | 70.1172 | 70.1577 | 70.1627 | 70.1586 | 70.192 | 70.1954 | 70.1947
NQ | 82912295 | BEGA 2 | GARBUTT-BELGIANGARDENS NO.02 | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | % of Rated A | 3.0197 | 3.0215 | 3.0215 | 2.9563 | 2.9582 | 2.9582 | 2.9162 | 2.9182 | 2.9182 | 2.8928 | 2.8949 | 2.8949 | 2.8833 | 2.8853 | 2.8853
NQ | 82912295 | BEGA 2 | GARBUTT-BELGIANGARDENS NO.02 | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | Limiting Line Name | TR_CABLE 16086_1 | TR_CABLE 16086_1 | TR_CABLE 16086_1 | TR_CABLE 16086_1 | TR_CABLE 16086_1 | TR_CABLE 16086_1 | TR_CABLE 16086_1 | TR_CABLE 16086_1 | TR_CABLE 16086_1 | TR_CABLE 16086_1 | TR_CABLE 16086_1 | TR_CABLE 16086_1 | TR_CABLE 16086_1 | TR_CABLE 16086_1 | TR_CABLE 16086_1
NQ | 82912295 | BEGA 2 | GARBUTT-BELGIANGARDENS NO.02 | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | Loading (A) | 23.9762 | 23.9905 | 23.9905 | 23.4728 | 23.4881 | 23.4881 | 23.1546 | 23.1706 | 23.1706 | 22.9688 | 22.9852 | 22.9852 | 22.8934 | 22.9094 | 22.9094
NQ | 82912295 | BEGA 2 | GARBUTT-BELGIANGARDENS NO.02 | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | Loading (MVA) | 2.8895 | 2.8933 | 2.8933 | 2.8297 | 2.8336 | 2.8336 | 2.792 | 2.7959 | 2.7959 | 2.7701 | 2.7741 | 2.7741 | 2.7614 | 2.7653 | 2.7653
NQ | 82912295 | BEGA 2 | GARBUTT-BELGIANGARDENS NO.02 | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | Loading (MW) | 0.8827 | 0.88278 | 0.88278 | 0.64537 | 0.64545 | 0.64545 | 0.43661 | 0.43669 | 0.43669 | 0.24416 | 0.24424 | 0.24424 | 0.076287 | 0.076365 | 0.076365
NQ | 82912295 | BEGA 2 | GARBUTT-BELGIANGARDENS NO.02 | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | Power Factor | 0.30548 | 0.30511 | 0.30511 | 0.22807 | 0.22778 | 0.22778 | 0.15638 | 0.15619 | 0.15619 | 0.088143 | 0.088045 | 0.088045 | 0.027626 | 0.027615 | 0.027615
NQ | 82912295 | BEGA 2 | GARBUTT-BELGIANGARDENS NO.02 | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | Rating (A) | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794
NQ | 82912295 | BEGA 2 | GARBUTT-BELGIANGARDENS NO.02 | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | Time | 16:30 | 21:00 | 22:00 | 16:30 | 21:00 | 22:00 | 16:30 | 21:00 | 22:00 | 16:30 | 21:00 | 22:00 | 9:00 | 21:00 | 22:00
NQ | 82912295 | BEGA 2 | GARBUTT-BELGIANGARDENS NO.02 | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | Voltage at Constrained Conductor | 69.5801 | 69.63 | 69.63 | 69.6014 | 69.6513 | 69.6513 | 69.6173 | 69.6674 | 69.6674 | 69.6299 | 69.6801 | 69.6801 | 69.6408 | 69.6896 | 69.6896
NQ | 82912298 | BEGA 1 | GARBUTT-BELGIANGARDENS NO.01 | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | % of Rated A | 3.0371 | 3.0389 | 3.0389 | 2.9741 | 2.976 | 2.976 | 2.9343 | 2.9363 | 2.9363 | 2.9111 | 2.9132 | 2.9132 | 2.9017 | 2.9037 | 2.9037
NQ | 82912298 | BEGA 1 | GARBUTT-BELGIANGARDENS NO.01 | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | Limiting Line Name | TR_CABLE 4808_1 | TR_CABLE 4808_1 | TR_CABLE 4808_1 | TR_CABLE 4808_1 | TR_CABLE 4808_1 | TR_CABLE 4808_1 | TR_CABLE 4808_1 | TR_CABLE 4808_1 | TR_CABLE 4808_1 | TR_CABLE 4808_1 | TR_CABLE 4808_1 | TR_CABLE 4808_1 | TR_CABLE 4808_1 | TR_CABLE 4808_1 | TR_CABLE 4808_1
NQ | 82912298 | BEGA 1 | GARBUTT-BELGIANGARDENS NO.01 | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | Loading (A) | 24.1142 | 24.1286 | 24.1286 | 23.6142 | 23.6296 | 23.6296 | 23.2983 | 23.3143 | 23.3143 | 23.114 | 23.1305 | 23.1305 | 23.0396 | 23.0557 | 23.0557
NQ | 82912298 | BEGA 1 | GARBUTT-BELGIANGARDENS NO.01 | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | Loading (MVA) | 2.9062 | 2.91 | 2.91 | 2.8468 | 2.8507 | 2.8507 | 2.8093 | 2.8133 | 2.8133 | 2.7876 | 2.7916 | 2.7916 | 2.7791 | 2.783 | 2.783
NQ | 82912298 | BEGA 1 | GARBUTT-BELGIANGARDENS NO.01 | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | Loading (MW) | 0.88332 | 0.8834 | 0.8834 | 0.64588 | 0.64596 | 0.64596 | 0.43703 | 0.43711 | 0.43711 | 0.24449 | 0.24457 | 0.24457 | 0.076534 | 0.076611 | 0.076611
NQ | 82912298 | BEGA 1 | GARBUTT-BELGIANGARDENS NO.01 | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | Power Factor | 0.30395 | 0.30358 | 0.30358 | 0.22688 | 0.2266 | 0.2266 | 0.15556 | 0.15537 | 0.15537 | 0.087706 | 0.087609 | 0.087609 | 0.027539 | 0.027529 | 0.027529
NQ | 82912298 | BEGA 1 | GARBUTT-BELGIANGARDENS NO.01 | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | Rating (A) | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794
NQ | 82912298 | BEGA 1 | GARBUTT-BELGIANGARDENS NO.01 | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | Time | 16:30 | 21:00 | 22:00 | 16:30 | 21:00 | 22:00 | 16:30 | 21:00 | 22:00 | 16:30 | 21:00 | 22:00 | 9:00 | 21:00 | 22:00
NQ | 82912298 | BEGA 1 | GARBUTT-BELGIANGARDENS NO.01 | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | Voltage at Constrained Conductor | 69.5801 | 69.63 | 69.63 | 69.6014 | 69.6513 | 69.6513 | 69.6173 | 69.6674 | 69.6674 | 69.6299 | 69.6801 | 69.6801 | 69.6408 | 69.6896 | 69.6896
NQ | 83878913 | 6299 | TOPO FDR | 6299_Townsville Port 66 kV | % of Rated A | 3.186 | 2.8961 | 3.1509 | 4.4561 | 4.0472 | 4.405 | 5.5932 | 5.0777 | 5.5332 | 6.656 | 6.0408 | 6.5823 | 7.6022 | 6.8905 | 7.5176
NQ | 83878913 | 6299 | TOPO FDR | 6299_Townsville Port 66 kV | Limiting Line Name | TR_LINE 96488_1 | TR_LINE 96488_1 | TR_LINE 96488_1 | TR_LINE 96488_1 | TR_LINE 96488_1 | TR_LINE 96488_1 | TR_LINE 96488_1 | TR_LINE 96488_1 | TR_LINE 96488_1 | TR_LINE 96488_1 | TR_LINE 96488_1 | TR_LINE 96488_1 | TR_LINE 96488_1 | TR_LINE 96488_1 | TR_LINE 96488_1
NQ | 83878913 | 6299 | TOPO FDR | 6299_Townsville Port 66 kV | Loading (A) | 34.7906 | 34.898 | 34.8805 | 48.6607 | 48.7682 | 48.7638 | 61.0773 | 61.1857 | 61.2523 | 72.6831 | 72.7922 | 72.8663 | 83.0161 | 83.0308 | 83.2198
NQ | 83878913 | 6299 | TOPO FDR | 6299_Townsville Port 66 kV | Loading (MVA) | 4.172 | 4.185 | 4.1828 | 5.8352 | 5.8482 | 5.8481 | 7.3239 | 7.337 | 7.3449 | 8.7152 | 8.7284 | 8.7373 | 9.9539 | 9.9557 | 9.9787
NQ | 83878913 | 6299 | TOPO FDR | 6299_Townsville Port 66 kV | Loading (MW) | 4.1599 | 4.1737 | 4.1702 | 5.8224 | 5.8361 | 5.8385 | 7.3093 | 7.3232 | 7.3306 | 8.6988 | 8.7128 | 8.7215 | 9.9366 | 9.9381 | 9.9616
NQ | 83878913 | 6299 | TOPO FDR | 6299_Townsville Port 66 kV | Power Factor | 0.9971 | 0.99731 | 0.997 | 0.9978 | 0.99793 | 0.99836 | 0.99801 | 0.99812 | 0.99805 | 0.99812 | 0.9982 | 0.9982 | 0.99826 | 0.99823 | 0.99829
NQ | 83878913 | 6299 | TOPO FDR | 6299_Townsville Port 66 kV | Rating (A) | 1092 | 1205 | 1107 | 1092 | 1205 | 1107 | 1092 | 1205 | 1107 | 1092 | 1205 | 1107 | 1092 | 1205 | 1107
NQ | 83878913 | 6299 | TOPO FDR | 6299_Townsville Port 66 kV | Time | 16:30 | 17:00 | 7:00 | 16:30 | 17:00 | 6:30 | 16:30 | 17:00 | 7:30 | 16:30 | 17:00 | 7:00 | 16:30 | 17:00 | 7:30
NQ | 83878913 | 6299 | TOPO FDR | 6299_Townsville Port 66 kV | Voltage at Constrained Conductor | 69.2344 | 69.2358 | 69.2339 | 69.2335 | 69.235 | 69.2398 | 69.231 | 69.2325 | 69.2314 | 69.228 | 69.2295 | 69.2291 | 69.2263 | 69.2261 | 69.2285
NQ | 83969140 | 6312 | MERINDA-HOMEHILL | 6312_Merinda - Home Hill 66 kV | % of Rated A | 5.7141 | 5.1414 | 5.6321 | 5.9438 | 5.2241 | 5.7227 | 5.924 | 5.1632 | 5.6559 | 5.9054 | 5.105 | 5.5922 | 5.8901 | 5.0546 | 5.537
NQ | 83969140 | 6312 | MERINDA-HOMEHILL | 6312_Merinda - Home Hill 66 kV | Limiting Line Name | TR_LINE 32515_1 | TR_LINE 32515_1 | TR_LINE 32515_1 | TR_LINE 180012_1 | TR_LINE 32515_1 | TR_LINE 32515_1 | TR_LINE 180012_1 | TR_LINE 32515_1 | TR_LINE 32515_1 | TR_LINE 180012_1 | TR_LINE 32515_1 | TR_LINE 32515_1 | TR_LINE 180012_1 | TR_LINE 32515_1 | TR_LINE 32515_1
NQ | 83969140 | 6312 | MERINDA-HOMEHILL | 6312_Merinda - Home Hill 66 kV | Loading (A) | 14.7424 | 14.7559 | 14.7561 | 10.4017 | 14.9933 | 14.9935 | 10.367 | 14.8183 | 14.8185 | 10.3345 | 14.6513 | 14.6515 | 10.3076 | 14.5067 | 14.5069
NQ | 83969140 | 6312 | MERINDA-HOMEHILL | 6312_Merinda - Home Hill 66 kV | Loading (MVA) | 1.81 | 1.8152 | 1.8153 | 1.2809 | 1.8463 | 1.8463 | 1.278 | 1.8265 | 1.8266 | 1.2753 | 1.8075 | 1.8075 | 1.2731 | 1.7909 | 1.7909
NQ | 83969140 | 6312 | MERINDA-HOMEHILL | 6312_Merinda - Home Hill 66 kV | Loading (MW) | 0.94777 | 0.94777 | 0.94777 | 0.94919 | 1.0027 | 1.0027 | 0.94349 | 0.95966 | 0.95966 | 0.93811 | 0.91723 | 0.91723 | 0.93366 | 0.8794 | 0.8794
NQ | 83969140 | 6312 | MERINDA-HOMEHILL | 6312_Merinda - Home Hill 66 kV | Power Factor | 0.52362 | 0.52213 | 0.52211 | 0.74102 | 0.54312 | 0.5431 | 0.73823 | 0.52541 | 0.52539 | 0.73561 | 0.50747 | 0.50745 | 0.73335 | 0.49105 | 0.49103
NQ | 83969140 | 6312 | MERINDA-HOMEHILL | 6312_Merinda - Home Hill 66 kV | Rating (A) | 258 | 287 | 262 | 175 | 287 | 262 | 175 | 287 | 262 | 175 | 287 | 262 | 175 | 287 | 262
NQ | 83969140 | 6312 | MERINDA-HOMEHILL | 6312_Merinda - Home Hill 66 kV | Time | 16:00 | 20:00 | 4:00 | 9:00 | 20:00 | 4:00 | 16:30 | 20:00 | 4:00 | 16:30 | 20:00 | 4:00 | 9:00 | 20:00 | 4:00
NQ | 83969140 | 6312 | MERINDA-HOMEHILL | 6312_Merinda - Home Hill 66 kV | Voltage at Constrained Conductor | 70.886 | 71.0234 | 71.0253 | 71.0981 | 71.0948 | 71.0966 | 71.1759 | 71.1634 | 71.1652 | 71.2461 | 71.2251 | 71.2269 | 71.3112 | 71.274 | 71.2757
NQ | 84212381 | 6321 | 66kV LUCINDA FDR | 6321_Lucinda 66 kV | % of Rated A | 5.342 | 4.7668 | 5.211 | 5.713 | 5.0978 | 5.5729 | 6.0998 | 5.443 | 5.9502 | 6.5111 | 5.81 | 6.3514 | 6.8758 | 6.1356 | 6.7071
NQ | 84212381 | 6321 | 66kV LUCINDA FDR | 6321_Lucinda 66 kV | Limiting Line Name | TR_LINE 123204_1 | TR_LINE 123204_1 | TR_LINE 123204_1 | TR_LINE 123204_1 | TR_LINE 123204_1 | TR_LINE 123204_1 | TR_LINE 135526_1 | TR_LINE 135526_1 | TR_LINE 135526_1 | TR_LINE 135526_1 | TR_LINE 135526_1 | TR_LINE 135526_1 | TR_LINE 135526_1 | TR_LINE 135526_1 | TR_LINE 135526_1
NQ | 84212381 | 6321 | 66kV LUCINDA FDR | 6321_Lucinda 66 kV | Loading (A) | 10.6305 | 10.6299 | 10.6304 | 11.3688 | 11.3682 | 11.3686 | 12.1386 | 12.138 | 12.1385 | 12.9571 | 12.9564 | 12.957 | 13.6829 | 13.6823 | 13.6826
NQ | 84212381 | 6321 | 66kV LUCINDA FDR | 6321_Lucinda 66 kV | Loading (MVA) | 1.2751 | 1.2751 | 1.2751 | 1.3639 | 1.3639 | 1.3639 | 1.4541 | 1.4541 | 1.4541 | 1.5522 | 1.5522 | 1.5522 | 1.6393 | 1.6393 | 1.6393
NQ | 84212381 | 6321 | 66kV LUCINDA FDR | 6321_Lucinda 66 kV | Loading (MW) | 1.2751 | 1.2751 | 1.2751 | 1.3638 | 1.3638 | 1.3638 | 1.4214 | 1.4214 | 1.4214 | 1.522 | 1.522 | 1.522 | 1.6112 | 1.6112 | 1.6112
NQ | 84212381 | 6321 | 66kV LUCINDA FDR | 6321_Lucinda 66 kV | Power Factor | 0.99996 | 0.99996 | 0.99996 | 0.99995 | 0.99995 | 0.99995 | 0.97748 | 0.97748 | 0.97748 | 0.98058 | 0.98058 | 0.98058 | 0.98287 | 0.98287 | 0.98287
NQ | 84212381 | 6321 | 66kV LUCINDA FDR | 6321_Lucinda 66 kV | Rating (A) | 199 | 223 | 204 | 199 | 223 | 204 | 199 | 223 | 204 | 199 | 223 | 204 | 199 | 223 | 204
NQ | 84212381 | 6321 | 66kV LUCINDA FDR | 6321_Lucinda 66 kV | Time | 11:00 | 17:00 | 8:30 | 11:00 | 17:00 | 8:30 | 11:00 | 17:00 | 8:30 | 11:00 | 17:00 | 8:30 | 16:00 | 17:00 | 8:30
NQ | 84212381 | 6321 | 66kV LUCINDA FDR | 6321_Lucinda 66 kV | Voltage at Constrained Conductor | 69.2527 | 69.2564 | 69.2535 | 69.2647 | 69.2685 | 69.2655 | 69.1615 | 69.1655 | 69.1623 | 69.1623 | 69.1663 | 69.1631 | 69.1692 | 69.1723 | 69.1709
NQ | 84253050 | 6325 | OONOONBA-STUART | 6325_Oonoonba-Stuart 66 kV | % of Rated A | 21.3107 | 20.9446 | 23.7765 | 24.0364 | 23.6338 | 26.828 | 26.5022 | 26.0613 | 29.5816 | 28.8211 | 28.3422 | 32.0526 | 30.7868 | 30.376 | 34.3596
NQ | 84253050 | 6325 | OONOONBA-STUART | 6325_Oonoonba-Stuart 66 kV | Limiting Line Name | TR_LINE 31738_1 | TR_LINE 31738_1 | TR_LINE 31738_1 | TR_LINE 31738_1 | TR_LINE 31738_1 | TR_LINE 31738_1 | TR_LINE 31738_1 | TR_LINE 31738_1 | TR_LINE 31738_1 | TR_LINE 31738_1 | TR_LINE 31738_1 | TR_LINE 31738_1 | TR_LINE 31738_1 | TR_LINE 31738_1 | TR_LINE 31738_1
NQ | 84253050 | 6325 | OONOONBA-STUART | 6325_Oonoonba-Stuart 66 kV | Loading (A) | 69.2574 | 69.5337 | 69.6628 | 78.1163 | 78.4622 | 78.6041 | 86.1303 | 86.5217 | 86.6724 | 93.667 | 94.0946 | 93.9126 | 100.0558 | 100.8471 | 100.6725
NQ | 84253050 | 6325 | OONOONBA-STUART | 6325_Oonoonba-Stuart 66 kV | Loading (MVA) | 8.2556 | 8.2919 | 8.3079 | 9.3109 | 9.356 | 9.3736 | 10.2652 | 10.3161 | 10.3348 | 11.1623 | 11.218 | 11.1979 | 11.9233 | 12.0218 | 12.0027
NQ | 84253050 | 6325 | OONOONBA-STUART | 6325_Oonoonba-Stuart 66 kV | Loading (MW) | 7.755 | 7.8508 | 7.8779 | 8.9104 | 9.005 | 9.0317 | 9.9378 | 10.031 | 10.0574 | 10.8918 | 10.9841 | 10.9737 | 11.6984 | 11.8267 | 11.8162
NQ | 84253050 | 6325 | OONOONBA-STUART | 6325_Oonoonba-Stuart 66 kV | Power Factor | 0.93936 | 0.94681 | 0.94824 | 0.95698 | 0.96248 | 0.96353 | 0.9681 | 0.97236 | 0.97316 | 0.97577 | 0.97915 | 0.97998 | 0.98114 | 0.98377 | 0.98446
NQ | 84253050 | 6325 | OONOONBA-STUART | 6325_Oonoonba-Stuart 66 kV | Rating (A) | 325 | 332 | 293 | 325 | 332 | 293 | 325 | 332 | 293 | 325 | 332 | 293 | 325 | 332 | 293
NQ | 84253050 | 6325 | OONOONBA-STUART | 6325_Oonoonba-Stuart 66 kV | Time | 16:30 | 18:00 | 6:00 | 16:30 | 18:00 | 6:00 | 16:30 | 18:00 | 6:00 | 16:30 | 18:00 | 6:00 | 16:30 | 18:00 | 6:00
NQ | 84253050 | 6325 | OONOONBA-STUART | 6325_Oonoonba-Stuart 66 kV | Voltage at Constrained Conductor | 68.8212 | 68.8493 | 68.8539 | 68.8163 | 68.8445 | 68.8491 | 68.8101 | 68.8385 | 68.8431 | 68.8031 | 68.8317 | 68.8415 | 68.801 | 68.8251 | 68.8349
NQ | 84431571 | MICC-MICB 1 | MICA CREEK 'C' TO MICA CREEK 'B' 1 | MICC-MICB No 1 132 kV | % of Rated A | 55.2487 | 40.111 | 40.0553 | 55.4037 | 40.2236 | 40.1677 | 55.5085 | 40.2997 | 40.2437 | 55.5967 | 40.3637 | 40.3076 | 55.5507 | 40.3303 | 40.2743
NQ | 84431571 | MICC-MICB 1 | MICA CREEK 'C' TO MICA CREEK 'B' 1 | MICC-MICB No 1 132 kV | Limiting Line Name | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1
NQ | 84431571 | MICC-MICB 1 | MICA CREEK 'C' TO MICA CREEK 'B' 1 | MICC-MICB No 1 132 kV | Loading (A) | 288.3983 | 288.3983 | 288.3983 | 289.2076 | 289.2076 | 289.2076 | 289.7546 | 289.7546 | 289.7546 | 290.2148 | 290.2148 | 290.2148 | 289.9748 | 289.9748 | 289.9748
NQ | 84431571 | MICC-MICB 1 | MICA CREEK 'C' TO MICA CREEK 'B' 1 | MICC-MICB No 1 132 kV | Loading (MVA) | 92.5073 | 92.5073 | 92.5073 | 92.8167 | 92.8167 | 92.8167 | 93.0262 | 93.0262 | 93.0262 | 93.203 | 93.203 | 93.203 | 93.1062 | 93.1062 | 93.1062
NQ | 84431571 | MICC-MICB 1 | MICA CREEK 'C' TO MICA CREEK 'B' 1 | MICC-MICB No 1 132 kV | Loading (MW) | 63.6196 | 63.6196 | 63.6196 | 64.0829 | 64.0829 | 64.0829 | 64.4 | 64.4 | 64.4 | 64.6684 | 64.6684 | 64.6684 | 64.5469 | 64.5469 | 64.5469
NQ | 84431571 | MICC-MICB 1 | MICA CREEK 'C' TO MICA CREEK 'B' 1 | MICC-MICB No 1 132 kV | Power Factor | 0.68773 | 0.68773 | 0.68773 | 0.69042 | 0.69042 | 0.69042 | 0.69228 | 0.69228 | 0.69228 | 0.69384 | 0.69384 | 0.69384 | 0.69326 | 0.69326 | 0.69326
NQ | 84431571 | MICC-MICB 1 | MICA CREEK 'C' TO MICA CREEK 'B' 1 | MICC-MICB No 1 132 kV | Rating (A) | 522 | 719 | 720 | 522 | 719 | 720 | 522 | 719 | 720 | 522 | 719 | 720 | 522 | 719 | 720
NQ | 84431571 | MICC-MICB 1 | MICA CREEK 'C' TO MICA CREEK 'B' 1 | MICC-MICB No 1 132 kV | Time | 9:00 | 17:00 | 0:00 | 9:00 | 17:00 | 0:00 | 9:00 | 17:00 | 0:00 | 9:00 | 17:00 | 0:00 | 9:00 | 17:00 | 0:00
NQ | 84431571 | MICC-MICB 1 | MICA CREEK 'C' TO MICA CREEK 'B' 1 | MICC-MICB No 1 132 kV | Voltage at Constrained Conductor | 185.1922 | 185.1922 | 185.1922 | 185.2916 | 185.2916 | 185.2916 | 185.3593 | 185.3593 | 185.3593 | 185.4171 | 185.4171 | 185.4171 | 185.3777 | 185.3777 | 185.3777
NQ | 84431576 | MICC-MICB 2 | MICA CREEK 'C' TO MICA CREEK 'B' 2 | MICC-MICB No 2 132 kV | % of Rated A | 55.4407 | 40.2504 | 40.1945 | 55.5963 | 40.3634 | 40.3073 | 55.7015 | 40.4397 | 40.3836 | 55.7899 | 40.504 | 40.4477 | 55.7438 | 40.4705 | 40.4143
NQ | 84431576 | MICC-MICB 2 | MICA CREEK 'C' TO MICA CREEK 'B' 2 | MICC-MICB No 2 132 kV | Limiting Line Name | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1
NQ | 84431576 | MICC-MICB 2 | MICA CREEK 'C' TO MICA CREEK 'B' 2 | MICC-MICB No 2 132 kV | Loading (A) | 289.4006 | 289.4006 | 289.4006 | 290.2127 | 290.2127 | 290.2127 | 290.7617 | 290.7617 | 290.7617 | 291.2235 | 291.2235 | 291.2235 | 290.9827 | 290.9827 | 290.9827
NQ | 84431576 | MICC-MICB 2 | MICA CREEK 'C' TO MICA CREEK 'B' 2 | MICC-MICB No 2 132 kV | Loading (MVA) | 92.8288 | 92.8288 | 92.8288 | 93.1392 | 93.1392 | 93.1392 | 93.3495 | 93.3495 | 93.3495 | 93.527 | 93.527 | 93.527 | 93.4298 | 93.4298 | 93.4298
NQ | 84431576 | MICC-MICB 2 | MICA CREEK 'C' TO MICA CREEK 'B' 2 | MICC-MICB No 2 132 kV | Loading (MW) | 63.8407 | 63.8407 | 63.8407 | 64.3056 | 64.3056 | 64.3056 | 64.6238 | 64.6238 | 64.6238 | 64.8931 | 64.8931 | 64.8931 | 64.7712 | 64.7712 | 64.7712
NQ | 84431576 | MICC-MICB 2 | MICA CREEK 'C' TO MICA CREEK 'B' 2 | MICC-MICB No 2 132 kV | Power Factor | 0.68773 | 0.68773 | 0.68773 | 0.69042 | 0.69042 | 0.69042 | 0.69228 | 0.69228 | 0.69228 | 0.69384 | 0.69384 | 0.69384 | 0.69326 | 0.69326 | 0.69326
NQ | 84431576 | MICC-MICB 2 | MICA CREEK 'C' TO MICA CREEK 'B' 2 | MICC-MICB No 2 132 kV | Rating (A) | 522 | 719 | 720 | 522 | 719 | 720 | 522 | 719 | 720 | 522 | 719 | 720 | 522 | 719 | 720
NQ | 84431576 | MICC-MICB 2 | MICA CREEK 'C' TO MICA CREEK 'B' 2 | MICC-MICB No 2 132 kV | Time | 9:00 | 17:00 | 0:00 | 9:00 | 17:00 | 0:00 | 9:00 | 17:00 | 0:00 | 9:00 | 17:00 | 0:00 | 9:00 | 17:00 | 0:00
NQ | 84431576 | MICC-MICB 2 | MICA CREEK 'C' TO MICA CREEK 'B' 2 | MICC-MICB No 2 132 kV | Voltage at Constrained Conductor | 185.1922 | 185.1922 | 185.1922 | 185.2916 | 185.2916 | 185.2916 | 185.3593 | 185.3593 | 185.3593 | 185.4171 | 185.4171 | 185.4171 | 185.3777 | 185.3777 | 185.3777
NQ | 111543431 | 6382 | JACR - HUGH FDR 6382 | 6382 JACR-HUGH 132kV | % of Rated A | 37.0468 | 57.7235 | 57.7235 | 37.5961 | 55.7343 | 55.7343 | 38.2115 | 54.1486 | 54.1486 | 38.6911 | 52.8983 | 52.8983 | 38.7358 | 52.0235 | 52.0235
NQ | 111543431 | 6382 | JACR - HUGH FDR 6382 | 6382 JACR-HUGH 132kV | Limiting Line Name | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line
NQ | 111543431 | 6382 | JACR - HUGH FDR 6382 | 6382 JACR-HUGH 132kV | Loading (A) | 52.6065 | 81.0664 | 81.0664 | 53.3865 | 78.1949 | 78.1949 | 54.2603 | 75.9031 | 75.9031 | 54.9414 | 74.0937 | 74.0937 | 55.0049 | 72.8265 | 72.8265
NQ | 111543431 | 6382 | JACR - HUGH FDR 6382 | 6382 JACR-HUGH 132kV | Loading (MVA) | 6.1216 | 9.5438 | 9.5438 | 6.2134 | 9.2045 | 9.2045 | 6.3175 | 8.9337 | 8.9337 | 6.3975 | 8.72 | 8.72 | 6.4066 | 8.5704 | 8.5704
NQ | 111543431 | 6382 | JACR - HUGH FDR 6382 | 6382 JACR-HUGH 132kV | Loading (MW) | 0.51719 | 9.0615 | 9.0615 | 0.87522 | 8.6897 | 8.6897 | 1.1731 | 8.3906 | 8.3906 | 1.4029 | 8.1522 | 8.1522 | 1.7296 | 7.9841 | 7.9841
NQ | 111543431 | 6382 | JACR - HUGH FDR 6382 | 6382 JACR-HUGH 132kV | Power Factor | 0.084486 | 0.94947 | 0.94947 | 0.14086 | 0.94408 | 0.94408 | 0.18569 | 0.93921 | 0.93921 | 0.21929 | 0.93489 | 0.93489 | 0.26997 | 0.93159 | 0.93159
NQ | 111543431 | 6382 | JACR - HUGH FDR 6382 | 6382 JACR-HUGH 132kV | Rating (A) | 142 | 142 | 142 | 142 | 142 | 142 | 142 | 142 | 142 | 142 | 142 | 142 | 142 | 142 | 142
NQ | 111543431 | 6382 | JACR - HUGH FDR 6382 | 6382 JACR-HUGH 132kV | Time | 9:00 | 20:00 | 3:30 | 9:00 | 20:00 | 3:30 | 9:00 | 20:00 | 3:30 | 9:00 | 20:00 | 3:30 | 9:00 | 20:00 | 3:30
NQ | 111543431 | 6382 | JACR - HUGH FDR 6382 | 6382 JACR-HUGH 132kV | Voltage at Constrained Conductor | 67.1837 | 67.9706 | 67.9706 | 67.1952 | 67.9613 | 67.9613 | 67.2206 | 67.9532 | 67.9532 | 67.2276 | 67.9477 | 67.9477 | 67.2458 | 67.9441 | 67.9441
NQ | 111675890 | 7460 | CPRE-JACR FDR | 6383 CARI-CPRE 66kV | % of Rated A | 165.754 | 142.7371 | 157.2079 | 166.4952 | 143.3848 | 157.9085 | 167.6976 | 143.9064 | 159.0492 | 168.1762 | 144.3288 | 159.5031 | 168.0561 | 144.63 | 159.3017
NQ | 111675890 | 7460 | CPRE-JACR FDR | 6383 CARI-CPRE 66kV | Limiting Line Name | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1
NQ | 111675890 | 7460 | CPRE-JACR FDR | 6383 CARI-CPRE 66kV | Loading (A) | 517.1526 | 510.999 | 517.2139 | 519.4651 | 513.3176 | 519.519 | 523.2165 | 515.1848 | 523.2718 | 524.7097 | 516.6972 | 524.7651 | 524.3351 | 517.7753 | 524.1026
NQ | 111675890 | 7460 | CPRE-JACR FDR | 6383 CARI-CPRE 66kV | Loading (MVA) | 57.4446 | 56.8614 | 57.4537 | 57.6661 | 57.0854 | 57.6741 | 58.1232 | 57.2653 | 58.1314 | 58.2667 | 57.412 | 58.2749 | 58.2353 | 57.517 | 58.2158
NQ | 111675890 | 7460 | CPRE-JACR FDR | 6383 CARI-CPRE 66kV | Loading (MW) | 51.805 | 50.9995 | 51.8052 | 52.1026 | 51.2993 | 52.1028 | 52.3486 | 51.5404 | 52.3488 | 52.5388 | 51.732 | 52.539 | 52.4832 | 51.8669 | 52.4472
NQ | 111675890 | 7460 | CPRE-JACR FDR | 6383 CARI-CPRE 66kV | Power Factor | 0.90182 | 0.89691 | 0.90169 | 0.90352 | 0.89864 | 0.9034 | 0.90065 | 0.90003 | 0.90053 | 0.90169 | 0.90107 | 0.90157 | 0.90123 | 0.90177 | 0.90091
NQ | 111675890 | 7460 | CPRE-JACR FDR | 6383 CARI-CPRE 66kV | Rating (A) | 312 | 358 | 329 | 312 | 358 | 329 | 312 | 358 | 329 | 312 | 358 | 329 | 312 | 358 | 329
NQ | 111675890 | 7460 | CPRE-JACR FDR | 6383 CARI-CPRE 66kV | Time | 9:00 | 17:00 | 7:30 | 9:00 | 17:00 | 7:30 | 9:00 | 17:00 | 7:30 | 9:00 | 17:00 | 7:30 | 16:00 | 17:00 | 7:00
NQ | 111675890 | 7460 | CPRE-JACR FDR | 6383 CARI-CPRE 66kV | Voltage at Constrained Conductor | 64.1313 | 64.2446 | 64.1338 | 64.092 | 64.2064 | 64.0942 | 64.1369 | 64.1753 | 64.1391 | 64.1122 | 64.1514 | 64.1144 | 64.1234 | 64.1349 | 64.1305
NQ | 111675890 | 7460 | CPRE-JACR FDR | 7460 CPRE-JACR 132kV | % of Rated A | 147.4465 | 90.3306 | 91.758 | 148.2826 | 90.8509 | 92.2781 | 149.0432 | 91.2705 | 92.7515 | 149.5805 | 91.6053 | 93.0858 | 150.2135 | 91.8418 | 93.4827
NQ | 111675890 | 7460 | CPRE-JACR FDR | 7460 CPRE-JACR 132kV | Limiting Line Name | TR_LINE 51339257_1 | TR_LINE 51339257_1 | TR_LINE 51339257_1 | TR_LINE 51339257_1 | TR_LINE 51339257_1 | TR_LINE 51339257_1 | TR_LINE 51339257_1 | TR_LINE 51339257_1 | TR_LINE 51339257_1 | TR_LINE 51339257_1 | TR_LINE 51339257_1 | TR_LINE 51339257_1 | TR_LINE 51339257_1 | TR_LINE 51339257_1 | TR_LINE 51339257_1
NQ | 111675890 | 7460 | CPRE-JACR FDR | 7460 CPRE-JACR 132kV | Loading (A) | 255.0824 | 251.1192 | 255.0873 | 256.5288 | 252.5655 | 256.5331 | 257.8447 | 253.7319 | 257.8491 | 258.7743 | 254.6628 | 258.7786 | 259.8693 | 255.3203 | 259.8819
NQ | 111675890 | 7460 | CPRE-JACR FDR | 7460 CPRE-JACR 132kV | Loading (MVA) | 60.2065 | 59.3181 | 60.2083 | 60.5333 | 59.6461 | 60.5349 | 60.8527 | 59.9102 | 60.8543 | 61.0626 | 60.1212 | 61.0642 | 61.2857 | 60.2702 | 61.2905
NQ | 111675890 | 7460 | CPRE-JACR FDR | 7460 CPRE-JACR 132kV | Loading (MW) | 56.6862 | 55.7227 | 56.6865 | 57.0421 | 56.0798 | 57.0424 | 57.3376 | 56.3674 | 57.3379 | 57.5656 | 56.5962 | 57.5658 | 57.8918 | 56.7575 | 57.8924
NQ | 111675890 | 7460 | CPRE-JACR FDR | 7460 CPRE-JACR 132kV | Power Factor | 0.94153 | 0.93939 | 0.94151 | 0.94233 | 0.94021 | 0.94231 | 0.94224 | 0.94086 | 0.94222 | 0.94273 | 0.94137 | 0.94271 | 0.94462 | 0.94172 | 0.94456
NQ | 111675890 | 7460 | CPRE-JACR FDR | 7460 CPRE-JACR 132kV | Rating (A) | 173 | 278 | 278 | 173 | 278 | 278 | 173 | 278 | 278 | 173 | 278 | 278 | 173 | 278 | 278
NQ | 111675890 | 7460 | CPRE-JACR FDR | 7460 CPRE-JACR 132kV | Time | 9:00 | 17:00 | 7:30 | 9:00 | 17:00 | 7:30 | 9:00 | 17:00 | 7:30 | 9:00 | 17:00 | 7:30 | 9:00 | 17:00 | 7:30
NQ | 111675890 | 7460 | CPRE-JACR FDR | 7460 CPRE-JACR 132kV | Voltage at Constrained Conductor | 136.2706 | 136.3788 | 136.2721 | 136.2379 | 136.3476 | 136.2392 | 136.2576 | 136.3218 | 136.259 | 136.2365 | 136.3017 | 136.2379 | 136.158 | 136.2876 | 136.1621
SW | 60026645 | F008D | CENTRAL DALBY 2 | F008D_Central Dalby 2 33 kV | % of Rated A | 2.7444 | 2.5879 | 2.797 | 0.75517 | 0.78656 | 0.89715 | 1.6235 | 1.802 | 2.1964 | 3.266 | 3.4433 | 3.9177 | 4.6829 | 4.8643 | 5.4076
SW | 60026645 | F008D | CENTRAL DALBY 2 | F008D_Central Dalby 2 33 kV | Limiting Line Name | TR_CABLE 5204_1 | TR_CABLE 5204_1 | TR_LINE 92498_1 | TR_CABLE 5204_1 | TR_CABLE 5204_1 | TR_CABLE 5204_1 | TR_CABLE 5204_1 | TR_CABLE 5204_1 | TR_CABLE 5204_1 | TR_CABLE 5204_1 | TR_CABLE 5204_1 | TR_LINE 92498_1 | TR_CABLE 5204_1 | TR_CABLE 5204_1 | TR_LINE 92498_1
SW | 60026645 | F008D | CENTRAL DALBY 2 | F008D_Central Dalby 2 33 kV | Loading (A) | 13.722 | 12.9393 | 13.4258 | 3.7758 | 3.9328 | 4.4857 | 8.1176 | 9.0102 | 10.9822 | 16.33 | 17.2167 | 18.8051 | 23.4145 | 24.3214 | 25.9566
SW | 60026645 | F008D | CENTRAL DALBY 2 | F008D_Central Dalby 2 33 kV | Loading (MVA) | 0.80817 | 0.75796 | 0.7796 | 0.21942 | 0.2316 | 0.26068 | 0.47544 | 0.52364 | 0.63907 | 0.95735 | 1.0017 | 1.0956 | 1.3737 | 1.4163 | 1.5135
SW | 60026645 | F008D | CENTRAL DALBY 2 | F008D_Central Dalby 2 33 kV | Loading (MW) | 0.80062 | 0.74211 | 0.77926 | 0.17916 | 0.084841 | 0.018289 | 0.43605 | 0.47437 | 0.57699 | 0.93674 | 0.975 | 1.0795 | 1.359 | 1.3973 | 1.5017
SW | 60026645 | F008D | CENTRAL DALBY 2 | F008D_Central Dalby 2 33 kV | Power Factor | 0.99065 | 0.9791 | 0.99957 | 0.81651 | 0.36633 | 0.070159 | 0.91716 | 0.90591 | 0.90286 | 0.97847 | 0.97335 | 0.98531 | 0.98933 | 0.98656 | 0.99216
SW | 60026645 | F008D | CENTRAL DALBY 2 | F008D_Central Dalby 2 33 kV | Rating (A) | 500 | 500 | 480 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 480 | 500 | 500 | 480
SW | 60026645 | F008D | CENTRAL DALBY 2 | F008D_Central Dalby 2 33 kV | Time | 12:00 | 17:00 | 8:30 | 12:00 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00
SW | 60026645 | F008D | CENTRAL DALBY 2 | F008D_Central Dalby 2 33 kV | Voltage at Constrained Conductor | 34.0038 | 33.8198 | 33.5251 | 33.5514 | 33.9991 | 33.5513 | 33.8146 | 33.5533 | 33.5966 | 33.8475 | 33.5913 | 33.6355 | 33.8727 | 33.6208 | 33.6653
SW | 60026646 | F019D | WEST DALBY NO 1 | F019D_West Dalby No 1 33 kV | % of Rated A | 3.9613 | 3.3627 | 3.9856 | 1.5044 | 1.0816 | 1.4192 | 1.0855 | 1.2218 | 1.9882 | 3.0919 | 3.0558 | 3.9921 | 4.7717 | 4.6018 | 5.6956
SW | 60026646 | F019D | WEST DALBY NO 1 | F019D_West Dalby No 1 33 kV | Limiting Line Name | TR_LINE 58890_1 | TR_LINE 81367_1 | TR_LINE 58890_1 | TR_LINE 58890_1 | TR_LINE 81367_1 | TR_LINE 58890_1 | TR_LINE 81367_1 | TR_LINE 81367_1 | TR_LINE 81367_1 | TR_LINE 81367_1 | TR_LINE 81367_1 | TR_LINE 81367_1 | TR_LINE 81367_1 | TR_LINE 81367_1 | TR_LINE 81367_1
SW | 60026646 | F019D | WEST DALBY NO 1 | F019D_West Dalby No 1 33 kV | Loading (A) | 14.8549 | 13.7535 | 14.667 | 5.6416 | 4.4237 | 5.2228 | 4.0705 | 4.9974 | 7.3165 | 11.5945 | 12.4983 | 14.6908 | 17.8939 | 18.8213 | 20.96
SW | 60026646 | F019D | WEST DALBY NO 1 | F019D_West Dalby No 1 33 kV | Loading (MVA) | 0.87446 | 0.80564 | 0.85128 | 0.32778 | 0.25951 | 0.30365 | 0.2384 | 0.29043 | 0.42576 | 0.67974 | 0.72718 | 0.85585 | 1.0499 | 1.096 | 1.2222
SW | 60026646 | F019D | WEST DALBY NO 1 | F019D_West Dalby No 1 33 kV | Loading (MW) | 0.87315 | 0.80539 | 0.85062 | 0.32514 | 0.25745 | 0.30298 | 0.23617 | 0.28057 | 0.40139 | 0.67896 | 0.72331 | 0.84404 | 1.0495 | 1.0938 | 1.2144
SW | 60026646 | F019D | WEST DALBY NO 1 | F019D_West Dalby No 1 33 kV | Power Factor | 0.9985 | 0.9997 | 0.99922 | 0.99194 | 0.99207 | 0.9978 | 0.99061 | 0.96604 | 0.94276 | 0.99884 | 0.99467 | 0.9862 | 0.99963 | 0.99796 | 0.99367
SW | 60026646 | F019D | WEST DALBY NO 1 | F019D_West Dalby No 1 33 kV | Rating (A) | 375 | 409 | 368 | 375 | 409 | 368 | 375 | 409 | 368 | 375 | 409 | 368 | 375 | 409 | 368
SW | 60026646 | F019D | WEST DALBY NO 1 | F019D_West Dalby No 1 33 kV | Time | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00
SW | 60026646 | F019D | WEST DALBY NO 1 | F019D_West Dalby No 1 33 kV | Voltage at Constrained Conductor | 33.9869 | 33.8193 | 33.5096 | 33.5443 | 33.8691 | 33.5667 | 33.8148 | 33.5535 | 33.5969 | 33.848 | 33.5919 | 33.6349 | 33.8737 | 33.6216 | 33.6646
SW | 60026664 | F039D | WEST DALBY NO 2 | F039D_West Dalby No 2 33 kV | % of Rated A | 7.2492 | 6.5597 | 7.1066 | 5.5135 | 4.7062 | 5.252 | 3.8106 | 2.9838 | 3.5401 | 2.3853 | 1.5106 | 2.0937 | 1.4337 | 0.57084 | 1.6594
SW | 60026664 | F039D | WEST DALBY NO 2 | F039D_West Dalby No 2 33 kV | Limiting Line Name | TR_CABLE 139_1 | TR_CABLE 4400_1 | TR_CABLE 139_1 | TR_CABLE 139_1 | TR_CABLE 4400_1 | TR_CABLE 139_1 | TR_CABLE 139_1 | TR_CABLE 139_1 | TR_CABLE 139_1 | TR_CABLE 139_1 | TR_CABLE 139_1 | TR_CABLE 139_1 | TR_CABLE 139_1 | TR_CABLE 139_1 | TR_CABLE 4400_1
SW | 60026664 | F039D | WEST DALBY NO 2 | F039D_West Dalby No 2 33 kV | Loading (A) | 20.5878 | 18.6295 | 20.1828 | 15.6583 | 13.3655 | 14.9156 | 10.822 | 8.4741 | 10.0539 | 6.7742 | 4.2901 | 5.9461 | 4.0718 | 1.6212 | 4.7127
SW | 60026664 | F039D | WEST DALBY NO 2 | F039D_West Dalby No 2 33 kV | Loading (MVA) | 1.2113 | 1.0908 | 1.1708 | 0.90954 | 0.7841 | 0.86701 | 0.62967 | 0.49787 | 0.58539 | 0.3947 | 0.25242 | 0.34671 | 0.2375 | 0.095496 | 0.27519
SW | 60026664 | F039D | WEST DALBY NO 2 | F039D_West Dalby No 2 33 kV | Loading (MW) | 1.2054 | 1.0899 | 1.1669 | 0.89911 | 0.78342 | 0.86053 | 0.61153 | 0.49412 | 0.57298 | 0.3587 | 0.24126 | 0.32013 | 0.15869 | 0.041257 | 0.23491
SW | 60026664 | F039D | WEST DALBY NO 2 | F039D_West Dalby No 2 33 kV | Power Factor | 0.9951 | 0.99918 | 0.99667 | 0.98854 | 0.99913 | 0.99253 | 0.97119 | 0.99246 | 0.97881 | 0.90879 | 0.9558 | 0.92332 | 0.66817 | 0.43202 | 0.85365
SW | 60026664 | F039D | WEST DALBY NO 2 | F039D_West Dalby No 2 33 kV | Rating (A) | 284 | 284 | 284 | 284 | 284 | 284 | 284 | 284 | 284 | 284 | 284 | 284 | 284 | 284 | 284
SW | 60026664 | F039D | WEST DALBY NO 2 | F039D_West Dalby No 2 33 kV | Time | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 4:00
SW | 60026664 | F039D | WEST DALBY NO 2 | F039D_West Dalby No 2 33 kV | Voltage at Constrained Conductor | 33.9688 | 33.804 | 33.4923 | 33.5362 | 33.8707 | 33.5599 | 33.5927 | 33.9205 | 33.6162 | 33.6394 | 33.97 | 33.665 | 33.676 | 34.0088 | 33.7133
SW | 60026667 | F060T | TARA | F060T_Tara 33 kV | % of Rated A | 9.3098 | 7.2865 | 7.7162 | 8.8965 | 6.9006 | 7.4525 | 8.7707 | 6.8134 | 7.4622 | 8.804 | 6.8242 | 7.5412 | 8.9505 | 6.8652 | 7.6262
SW | 60026667 | F060T | TARA | F060T_Tara 33 kV | Limiting Line Name | TR_LINE 23982_1 | TR_LINE 23982_1 | TR_LINE 23982_1 | TR_LINE 104801_2 | TR_LINE 104801_2 | TR_LINE 104801_2 | TR_LINE 104801_2 | TR_LINE 104801_2 | TR_LINE 104801_2 | TR_LINE 63522_1 | TR_LINE 104801_2 | TR_LINE 104801_2 | TR_LINE 63522_1 | TR_LINE 104801_2 | TR_LINE 24595_1
SW | 60026667 | F060T | TARA | F060T_Tara 33 kV | Loading (A) | 8.6582 | 8.8896 | 9.028 | 8.2738 | 8.4187 | 8.7195 | 8.1567 | 8.3123 | 8.7308 | 8.1877 | 8.3255 | 8.8232 | 8.3239 | 8.3756 | 8.9227
SW | 60026667 | F060T | TARA | F060T_Tara 33 kV | Loading (MVA) | 0.49754 | 0.50577 | 0.51398 | 0.47638 | 0.48004 | 0.49814 | 0.47038 | 0.47479 | 0.49967 | 0.47336 | 0.47624 | 0.50569 | 0.48182 | 0.47963 | 0.51197
SW | 60026667 | F060T | TARA | F060T_Tara 33 kV | Loading (MW) | 0.21364 | 0.22582 | 0.21712 | 0.098902 | 0.094982 | 0.044185 | 0.035776 | 0.031843 | 0.01883 | 0.098956 | 0.01394 | 0.064525 | 0.12914 | 0.044099 | 0.096104
SW | 60026667 | F060T | TARA | F060T_Tara 33 kV | Power Factor | 0.4294 | 0.4465 | 0.42242 | 0.20761 | 0.19786 | 0.088699 | 0.076057 | 0.067067 | 0.037684 | 0.20905 | 0.029271 | 0.1276 | 0.26803 | 0.091945 | 0.18771
SW | 60026667 | F060T | TARA | F060T_Tara 33 kV | Rating (A) | 93 | 122 | 117 | 93 | 122 | 117 | 93 | 122 | 117 | 93 | 122 | 117 | 93 | 122 | 117
SW | 60026667 | F060T | TARA | F060T_Tara 33 kV | Time | 16:00 | 21:00 | 0:00 | 16:00 | 21:00 | 4:00 | 16:00 | 21:00 | 4:00 | 15:30 | 21:00 | 4:00 | 15:30 | 21:00 | 4:00
SW | 60026667 | F060T | TARA | F060T_Tara 33 kV | Voltage at Constrained Conductor | 33.1772 | 32.848 | 32.87 | 33.2424 | 32.9207 | 32.984 | 33.2946 | 32.9778 | 33.0423 | 33.3784 | 33.0256 | 33.0897 | 33.4195 | 33.062 | 33.1279
SW | 60026669 | F067C | KOGAN | F067C_Kogan 33 kV | % of Rated A | 43.5617 | 31.4499 | 34.0402 | 44.3926 | 31.968 | 34.614 | 44.2644 | 31.9494 | 34.6355 | 44.2335 | 31.9262 | 34.5647 | 44.3048 | 31.8996 | 34.5503
SW | 60026669 | F067C | KOGAN | F067C_Kogan 33 kV | Limiting Line Name | TR_LINE 28354_1 | TR_LINE 28354_1 | TR_LINE 28354_1 | TR_LINE 27340_1 | TR_LINE 28354_1 | TR_LINE 28354_1 | TR_LINE 28354_1 | TR_LINE 28354_1 | TR_LINE 27340_1 | TR_LINE 28354_1 | TR_LINE 28354_1 | TR_LINE 28354_1 | TR_LINE 27340_1 | TR_LINE 28354_1 | TR_LINE 28354_1
SW | 60026669 | F067C | KOGAN | F067C_Kogan 33 kV | Loading (A) | 40.5108 | 38.3677 | 39.8256 | 41.2448 | 38.9997 | 40.4969 | 41.1643 | 38.977 | 40.4859 | 41.1356 | 38.9487 | 40.4392 | 41.1631 | 38.9163 | 40.4224
SW | 60026669 | F067C | KOGAN | F067C_Kogan 33 kV | Loading (MVA) | 2.3279 | 2.2078 | 2.2898 | 2.3205 | 2.2092 | 2.2913 | 2.3294 | 2.2094 | 2.2809 | 2.3292 | 2.2093 | 2.291 | 2.3204 | 2.2089 | 2.2913
SW | 60026669 | F067C | KOGAN | F067C_Kogan 33 kV | Loading (MW) | 2.3066 | 2.1963 | 2.2723 | 2.2893 | 2.1977 | 2.2738 | 2.308 | 2.1977 | 2.2543 | 2.3079 | 2.1976 | 2.2736 | 2.2893 | 2.1975 | 2.2736
SW | 60026669 | F067C | KOGAN | F067C_Kogan 33 kV | Power Factor | 0.99082 | 0.99479 | 0.99236 | 0.98656 | 0.9948 | 0.99236 | 0.99084 | 0.99469 | 0.98836 | 0.99086 | 0.99471 | 0.9924 | 0.9866 | 0.99485 | 0.99227
SW | 60026669 | F067C | KOGAN | F067C_Kogan 33 kV | Rating (A) | 93 | 122 | 117 | 93 | 122 | 117 | 93 | 122 | 117 | 93 | 122 | 117 | 93 | 122 | 117
SW | 60026669 | F067C | KOGAN | F067C_Kogan 33 kV | Time | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30
SW | 60026669 | F067C | KOGAN | F067C_Kogan 33 kV | Voltage at Constrained Conductor | 33.1771 | 33.2231 | 33.1948 | 32.4829 | 32.7052 | 32.6664 | 32.6704 | 32.7269 | 32.5263 | 32.6913 | 32.7489 | 32.7091 | 32.5451 | 32.77 | 32.7269
SW | 60026670 | F069C | BRIGALOW | F069C_Brigalow 33 kV | % of Rated A | 5.5115 | 5.3871 | 5.5892 | 5.8429 | 5.6666 | 6.0059 | 7.1077 | 6.1718 | 6.5302 | 8.278 | 6.7139 | 7.0767 | 9.2632 | 7.3076 | 7.7391
SW | 60026670 | F069C | BRIGALOW | F069C_Brigalow 33 kV | Limiting Line Name | TR_LINE 77928_1 | TR_LINE 77928_1 | TR_LINE 77928_1 | TR_LINE 77928_1 | TR_LINE 77928_1 | TR_LINE 77928_1 | TR_LINE 28423_1 | TR_LINE 77928_1 | TR_LINE 77928_1 | TR_LINE 28423_1 | TR_LINE 77928_1 | TR_LINE 77928_1 | TR_LINE 28423_1 | TR_LINE 28423_1 | TR_LINE 28423_1
SW | 60026670 | F069C | BRIGALOW | F069C_Brigalow 33 kV | Loading (A) | 4.8501 | 4.7406 | 4.9185 | 5.1418 | 4.9866 | 5.2852 | 4.3357 | 5.4312 | 5.7466 | 5.0496 | 5.9082 | 6.2275 | 5.6506 | 5.6269 | 5.6496
SW | 60026670 | F069C | BRIGALOW | F069C_Brigalow 33 kV | Loading (MVA) | 0.28308 | 0.27664 | 0.28647 | 0.29554 | 0.28666 | 0.30812 | 0.2503 | 0.3125 | 0.33532 | 0.2919 | 0.34023 | 0.3637 | 0.32701 | 0.32567 | 0.32702
SW | 60026670 | F069C | BRIGALOW | F069C_Brigalow 33 kV | Loading (MW) | 0.061556 | 0.048018 | 0.06623 | 0.1257 | 0.11219 | 0.13035 | 0.21403 | 0.16723 | 0.18539 | 0.2616 | 0.21459 | 0.23275 | 0.3004 | 0.29911 | 0.30034
SW | 60026670 | F069C | BRIGALOW | F069C_Brigalow 33 kV | Power Factor | 0.21745 | 0.17357 | 0.2312 | 0.42534 | 0.39136 | 0.42304 | 0.85512 | 0.53516 | 0.55286 | 0.89619 | 0.63073 | 0.63995 | 0.91863 | 0.91844 | 0.9184
SW | 60026670 | F069C | BRIGALOW | F069C_Brigalow 33 kV | Rating (A) | 88 | 88 | 88 | 88 | 88 | 88 | 61 | 88 | 88 | 61 | 88 | 88 | 61 | 77 | 73
SW | 60026670 | F069C | BRIGALOW | F069C_Brigalow 33 kV | Time | 11:00 | 17:00 | 4:00 | 11:00 | 17:00 | 4:00 | 9:00 | 17:00 | 4:00 | 9:00 | 17:00 | 4:00 | 9:00 | 17:00 | 4:00
SW | 60026670 | F069C | BRIGALOW | F069C_Brigalow 33 kV | Voltage at Constrained Conductor | 33.6975 | 33.692 | 33.6263 | 33.1851 | 33.1893 | 33.6586 | 33.3303 | 33.219 | 33.6894 | 33.3747 | 33.2471 | 33.718 | 33.4123 | 33.4156 | 33.4199
SW | 60026673 | F073C | FAIRYMEADOW | F073C_Fairymeadow 33 kV | % of Rated A | 98.0136 | 74.0329 | 110.3782 | 98.3568 | 75.4555 | 112.4838 | 98.283 | 75.392 | 112.4014 | 98.2096 | 75.3305 | 112.3163 | 98.1452 | 75.2739 | 112.2381
SW | 60026673 | F073C | FAIRYMEADOW | F073C_Fairymeadow 33 kV | Limiting Line Name | TR_LINE 12072719_1 | TR_LINE 12072719_1 | TR_LINE 12072719_1 | TR_LINE 12072719_1 | TR_LINE 12072719_1 | TR_LINE 12072719_1 | TR_LINE 12072719_1 | TR_LINE 12072719_1 | TR_LINE 12072719_1 | TR_LINE 12072719_1 | TR_LINE 12072719_1 | TR_LINE 12072719_1 | TR_LINE 12072719_1 | TR_LINE 12072719_1 | TR_LINE 12072719_1
SW | 60026673 | F073C | FAIRYMEADOW | F073C_Fairymeadow 33 kV | Loading (A) | 327.3634 | 249.4885 | 322.3024 | 328.5095 | 254.2827 | 328.4508 | 328.2633 | 254.0685 | 328.2099 | 328.0181 | 253.8612 | 327.9614 | 327.8028 | 253.6705 | 327.7331
SW | 60026673 | F073C | FAIRYMEADOW | F073C_Fairymeadow 33 kV | Loading (MVA) | 18.4767 | 14.1161 | 18.5102 | 18.5564 | 14.1499 | 18.5513 | 18.5554 | 14.1484 | 18.5503 | 18.5537 | 14.1468 | 18.5486 | 18.5522 | 14.1454 | 18.547
SW | 60026673 | F073C | FAIRYMEADOW | F073C_Fairymeadow 33 kV | Loading (MW) | 13.9522 | 8.3406 | 14.043 | 14.0432 | 8.3365 | 14.0362 | 14.0435 | 8.3366 | 14.0365 | 14.0438 | 8.3368 | 14.0368 | 14.044 | 8.337 | 14.037
SW | 60026673 | F073C | FAIRYMEADOW | F073C_Fairymeadow 33 kV | Power Factor | 0.75512 | 0.59086 | 0.75866 | 0.75678 | 0.58915 | 0.75661 | 0.75685 | 0.58923 | 0.75667 | 0.75693 | 0.58931 | 0.75676 | 0.757 | 0.58938 | 0.75684
SW | 60026673 | F073C | FAIRYMEADOW | F073C_Fairymeadow 33 kV | Rating (A) | 334 | 337 | 292 | 334 | 337 | 292 | 334 | 337 | 292 | 334 | 337 | 292 | 334 | 337 | 292
SW | 60026673 | F073C | FAIRYMEADOW | F073C_Fairymeadow 33 kV | Time | 15:00 | 17:00 | 7:30 | 9:00 | 17:00 | 7:30 | 9:00 | 17:00 | 7:30 | 9:00 | 17:00 | 7:30 | 9:00 | 17:00 | 7:30
SW | 60026673 | F073C | FAIRYMEADOW | F073C_Fairymeadow 33 kV | Voltage at Constrained Conductor | 32.5861 | 32.6665 | 33.1579 | 32.6126 | 32.1275 | 32.6095 | 32.6352 | 32.151 | 32.6316 | 32.6566 | 32.1738 | 32.6533 | 32.6754 | 32.1947 | 32.6733
SW | 60026674 | F075S | ST GEORGE TOWN | F075S_St George Town 33 kV | % of Rated A | 4.4257 | 4.4598 | 4.4439 | 2.7187 | 2.7712 | 2.7496 | 1.2947 | 1.3624 | 1.3439 | 0.59553 | 0.58251 | 0.64362 | 1.5563 | 1.5418 | 1.558
SW | 60026674 | F075S | ST GEORGE TOWN | F075S_St George Town 33 kV | Limiting Line Name | TR_CABLE 16563_1 | TR_CABLE 16563_1 | TR_CABLE 16563_1 | TR_CABLE 16563_1 | TR_CABLE 16563_1 | TR_CABLE 16563_1 | TR_CABLE 16563_1 | TR_CABLE 16563_1 | TR_CABLE 16563_1 | TR_CABLE 16563_1 | TR_CABLE 16563_1 | TR_CABLE 16563_1 | TR_CABLE 10986_1 | TR_CABLE 10986_1 | TR_LINE 25573_1
SW | 60026674 | F075S | ST GEORGE TOWN | F075S_St George Town 33 kV | Loading (A) | 7.2581 | 7.3141 | 7.288 | 4.4586 | 4.5448 | 4.5093 | 2.1233 | 2.2344 | 2.204 | 0.97667 | 0.95531 | 1.0555 | 2.5523 | 2.5286 | 2.5552
SW | 60026674 | F075S | ST GEORGE TOWN | F075S_St George Town 33 kV | Loading (MVA) | 0.41361 | 0.4217 | 0.41563 | 0.254 | 0.26196 | 0.25987 | 0.1211 | 0.12873 | 0.12696 | 0.056328 | 0.055032 | 0.060648 | 0.14548 | 0.14561 | 0.14683
SW | 60026674 | F075S | ST GEORGE TOWN | F075S_St George Town 33 kV | Loading (MW) | 0.41053 | 0.41873 | 0.41264 | 0.24872 | 0.25693 | 0.25465 | 0.10971 | 0.11797 | 0.11568 | 0.0167 | 0.013386 | 0.021186 | 0.14209 | 0.14208 | 0.14206
SW | 60026674 | F075S | ST GEORGE TOWN | F075S_St George Town 33 kV | Power Factor | 0.99255 | 0.99296 | 0.99281 | 0.97923 | 0.98082 | 0.9799 | 0.90592 | 0.91641 | 0.91119 | 0.29647 | 0.24324 | 0.34933 | 0.97672 | 0.97577 | 0.9675
SW | 60026674 | F075S | ST GEORGE TOWN | F075S_St George Town 33 kV | Rating (A) | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164
SW | 60026674 | F075S | ST GEORGE TOWN | F075S_St George Town 33 kV | Time | 16:30 | 20:00 | 8:00 | 16:30 | 20:00 | 22:00 | 12:00 | 20:00 | 22:00 | 9:30 | 17:30 | 4:00 | 14:30 | 21:00 | 4:00
SW | 60026674 | F075S | ST GEORGE TOWN | F075S_St George Town 33 kV | Voltage at Constrained Conductor | 32.9005 | 33.2876 | 32.9257 | 32.8903 | 33.2775 | 33.2722 | 32.9289 | 33.2633 | 33.2582 | 33.298 | 33.2592 | 33.173 | 32.9089 | 33.2468 | 33.1776
SW | 60026675 | F077S | MAIN CAMP | F077S_Main Camp 33 kV | % of Rated A | 80.9166 | 59.9732 | 73.0086 | 80.95 | 59.0771 | 73.0381 | 80.9971 | 59.1093 | 73.0794 | 81.0391 | 59.1376 | 73.1164 | 81.0748 | 59.1617 | 72.0164
SW | 60026675 | F077S | MAIN CAMP | F077S_Main Camp 33 kV | Limiting Line Name | TR_CABLE 16560_1 | TR_CABLE 16560_1 | TR_CABLE 16560_1 | TR_CABLE 16560_1 | TR_CABLE 16560_1 | TR_CABLE 16560_1 | TR_CABLE 16560_1 | TR_CABLE 16560_1 | TR_CABLE 16560_1 | TR_CABLE 16560_1 | TR_CABLE 16560_1 | TR_CABLE 16560_1 | TR_CABLE 16560_1 | TR_CABLE 16560_1 | TR_CABLE 16560_1
SW | 60026675 | F077S | MAIN CAMP | F077S_Main Camp 33 kV | Loading (A) | 80.9166 | 59.9732 | 73.0086 | 80.95 | 59.0771 | 73.0381 | 80.9971 | 59.1093 | 73.0794 | 81.0392 | 59.1376 | 73.1164 | 81.0748 | 59.1617 | 72.0164
SW | 60026675 | F077S | MAIN CAMP | F077S_Main Camp 33 kV | Loading (MVA) | 4.6186 | 3.4172 | 4.1647 | 4.619 | 3.4072 | 4.1651 | 4.6196 | 3.4075 | 4.1655 | 4.6201 | 3.4079 | 4.166 | 4.6205 | 3.4081 | 4.1532
SW | 60026675 | F077S | MAIN CAMP | F077S_Main Camp 33 kV | Loading (MW) | 4.0934 | 3.1233 | 3.7305 | 4.0935 | 3.122 | 3.7306 | 4.0936 | 3.1221 | 3.7307 | 4.0937 | 3.1221 | 3.7307 | 4.0937 | 3.1222 | 3.7286
SW | 60026675 | F077S | MAIN CAMP | F077S_Main Camp 33 kV | Power Factor | 0.88628 | 0.91401 | 0.89575 | 0.88622 | 0.91631 | 0.89569 | 0.88614 | 0.91623 | 0.89561 | 0.88606 | 0.91615 | 0.89553 | 0.886 | 0.91609 | 0.89777
SW | 60026675 | F077S | MAIN CAMP | F077S_Main Camp 33 kV | Rating (A) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
SW | 60026675 | F077S | MAIN CAMP | F077S_Main Camp 33 kV | Time | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30
SW | 60026675 | F077S | MAIN CAMP | F077S_Main Camp 33 kV | Voltage at Constrained Conductor | 32.9543 | 32.8966 | 32.9344 | 32.9435 | 33.2977 | 32.9238 | 32.9284 | 33.2831 | 32.909 | 32.9149 | 33.2703 | 32.8957 | 32.9034 | 33.2593 | 33.2957
SW | 60026679 | F083C | CHINCHILLA | F083C_Chinchilla 33 kV | % of Rated A | 7.4078 | 7.3173 | 8.4906 | 3.1949 | 3.1731 | 3.6775 | 1.4461 | 1.4242 | 1.6418 | 5.5038 | 5.4378 | 6.2816 | 9.556 | 9.455 | 10.9228
SW | 60026679 | F083C | CHINCHILLA | F083C_Chinchilla 33 kV | Limiting Line Name | TR_LINE 27121_1 | TR_LINE 27121_1 | TR_LINE 27121_1 | TR_LINE 27121_1 | TR_LINE 27121_1 | TR_LINE 27121_1 | TR_LINE 27121_1 | TR_LINE 27121_1 | TR_LINE 27121_1 | TR_LINE 27121_1 | TR_LINE 27121_1 | TR_LINE 27121_1 | TR_LINE 27121_1 | TR_LINE 27121_1 | TR_LINE 27121_1
SW | 60026679 | F083C | CHINCHILLA | F083C_Chinchilla 33 kV | Loading (A) | 24.7419 | 24.6593 | 24.7924 | 10.6709 | 10.6933 | 10.7382 | 4.8301 | 4.7997 | 4.794 | 18.3828 | 18.3253 | 18.3423 | 31.9167 | 31.863 | 31.8942
SW | 60026679 | F083C | CHINCHILLA | F083C_Chinchilla 33 kV | Loading (MVA) | 1.419 | 1.4247 | 1.422 | 0.61241 | 0.61812 | 0.62465 | 0.2773 | 0.27545 | 0.27524 | 1.056 | 1.0524 | 1.0537 | 1.8346 | 1.831 | 1.8335
SW | 60026679 | F083C | CHINCHILLA | F083C_Chinchilla 33 kV | Loading (MW) | 1.4108 | 1.4165 | 1.4139 | 0.59118 | 0.59687 | 0.6035 | 0.22525 | 0.22165 | 0.22299 | 1.0443 | 1.0407 | 1.042 | 1.8287 | 1.8252 | 1.8276
SW | 60026679 | F083C | CHINCHILLA | F083C_Chinchilla 33 kV | Power Factor | 0.99425 | 0.99422 | 0.99427 | 0.96533 | 0.96563 | 0.96614 | 0.81231 | 0.8047 | 0.81019 | 0.98887 | 0.98891 | 0.98887 | 0.9968 | 0.99682 | 0.99677
SW | 60026679 | F083C | CHINCHILLA | F083C_Chinchilla 33 kV | Rating (A) | 334 | 337 | 292 | 334 | 337 | 292 | 334 | 337 | 292 | 334 | 337 | 292 | 334 | 337 | 292
SW | 60026679 | F083C | CHINCHILLA | F083C_Chinchilla 33 kV | Time | 16:30 | 19:30 | 7:00 | 16:30 | 19:30 | 0:00 | 14:00 | 17:30 | 8:30 | 14:00 | 17:30 | 8:30 | 14:00 | 17:30 | 3:30
SW | 60026679 | F083C | CHINCHILLA | F083C_Chinchilla 33 kV | Voltage at Constrained Conductor | 33.1116 | 33.3574 | 33.1145 | 33.1342 | 33.3732 | 33.5848 | 33.1457 | 33.1334 | 33.1472 | 33.1664 | 33.1551 | 33.1675 | 33.1867 | 33.1769 | 33.1908
SW | 60026682 | F095D | KAIMKILLENBUN | F095D_Kaimkillenbun 33 kV | % of Rated A | 4.6317 | 4.7071 | 4.7298 | 4.1761 | 4.2445 | 4.2861 | 4.5836 | 4.221 | 4.3261 | 5.6805 | 4.5608 | 4.7182 | 6.585 | 5.0753 | 5.2881
SW | 60026682 | F095D | KAIMKILLENBUN | F095D_Kaimkillenbun 33 kV | Limiting Line Name | TR_CABLE 5206_1 | TR_CABLE 5206_1 | TR_CABLE 5206_1 | TR_CABLE 5206_1 | TR_CABLE 5206_1 | TR_CABLE 5206_1 | TR_LINE 23047_1 | TR_CABLE 5206_1 | TR_CABLE 5206_1 | TR_LINE 23047_1 | TR_CABLE 5206_1 | TR_CABLE 5206_1 | TR_LINE 23047_1 | TR_LINE 23047_1 | TR_LINE 23047_1
SW | 60026682 | F095D | KAIMKILLENBUN | F095D_Kaimkillenbun 33 kV | Loading (A) | 4.6317 | 4.7071 | 4.7298 | 4.1761 | 4.2445 | 4.2861 | 4.2627 | 4.221 | 4.3261 | 5.2828 | 4.5608 | 4.7182 | 6.124 | 6.1411 | 6.1342
SW | 60026682 | F095D | KAIMKILLENBUN | F095D_Kaimkillenbun 33 kV | Loading (MVA) | 0.27286 | 0.27663 | 0.27823 | 0.2443 | 0.24995 | 0.25254 | 0.24856 | 0.24842 | 0.25174 | 0.30866 | 0.2687 | 0.27487 | 0.35838 | 0.35838 | 0.35838
SW | 60026682 | F095D | KAIMKILLENBUN | F095D_Kaimkillenbun 33 kV | Loading (MW) | 0.12069 | 0.12793 | 0.12214 | 0.031745 | 0.035316 | 0.033418 | 0.24853 | 0.044062 | 0.05598 | 0.30861 | 0.11375 | 0.12564 | 0.3583 | 0.35829 | 0.3583
SW | 60026682 | F095D | KAIMKILLENBUN | F095D_Kaimkillenbun 33 kV | Power Factor | 0.44233 | 0.46246 | 0.43899 | 0.12994 | 0.14129 | 0.13233 | 0.99988 | 0.17737 | 0.22238 | 0.99982 | 0.42333 | 0.45711 | 0.99976 | 0.99975 | 0.99976
SW | 60026682 | F095D | KAIMKILLENBUN | F095D_Kaimkillenbun 33 kV | Rating (A) | 100 | 100 | 100 | 100 | 100 | 100 | 93 | 100 | 100 | 93 | 100 | 100 | 93 | 121 | 116
SW | 60026682 | F095D | KAIMKILLENBUN | F095D_Kaimkillenbun 33 kV | Time | 9:00 | 19:00 | 0:00 | 16:30 | 21:00 | 0:00 | 12:00 | 17:30 | 4:00 | 12:00 | 17:30 | 4:00 | 12:00 | 17:30 | 6:30
SW | 60026682 | F095D | KAIMKILLENBUN | F095D_Kaimkillenbun 33 kV | Voltage at Constrained Conductor | 34.0122 | 33.9306 | 33.9625 | 33.7747 | 33.9991 | 34.0181 | 33.6658 | 33.9794 | 33.5966 | 33.7334 | 34.0138 | 33.6343 | 33.787 | 33.6931 | 33.7308
SW | 60026684 | F106R | ROMA EAST | F106R_Roma East 33 kV | % of Rated A | 7.2105 | 7.1675 | 8.399 | 3.2192 | 3.1685 | 3.7361 | 0.77859 | 0.7891 | 0.91864 | 4.4915 | 4.5083 | 5.2458 | 7.9434 | 7.97 | 9.2831
SW | 60026684 | F106R | ROMA EAST | F106R_Roma East 33 kV | Limiting Line Name | TR_LINE 44567_2 | TR_LINE 44567_2 | TR_LINE 44567_2 | TR_LINE 44567_2 | TR_LINE 44567_2 | TR_LINE 44567_2 | TR_LINE 44567_3 | TR_LINE 44567_3 | TR_LINE 44567_3 | TR_LINE 116092_1 | TR_LINE 116092_1 | TR_LINE 116092_1 | TR_LINE 116092_1 | TR_LINE 116092_1 | TR_LINE 116092_1
SW | 60026684 | F106R | ROMA EAST | F106R_Roma East 33 kV | Loading (A) | 18.4585 | 18.2768 | 18.3936 | 8.2412 | 8.0798 | 8.182 | 1.9932 | 2.0122 | 2.0118 | 11.4981 | 11.4961 | 11.4884 | 20.335 | 20.3235 | 20.3299
SW | 60026684 | F106R | ROMA EAST | F106R_Roma East 33 kV | Loading (MVA) | 1.0375 | 1.0294 | 1.0345 | 0.46393 | 0.45577 | 0.46087 | 0.11238 | 0.11238 | 0.11238 | 0.64262 | 0.64262 | 0.64262 | 1.1374 | 1.1374 | 1.1374
SW | 60026684 | F106R | ROMA EAST | F106R_Roma East 33 kV | Loading (MW) | 1.0372 | 1.0292 | 1.0342 | 0.46347 | 0.4555 | 0.46049 | 0.11238 | 0.11238 | 0.11238 | 0.64261 | 0.64261 | 0.64261 | 1.1374 | 1.1374 | 1.1374
SW | 60026684 | F106R | ROMA EAST | F106R_Roma East 33 kV | Power Factor | 0.9997 | 0.99981 | 0.99974 | 0.99901 | 0.99942 | 0.99917 | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 0.99997 | 0.99997 | 0.99997
SW | 60026684 | F106R | ROMA EAST | F106R_Roma East 33 kV | Rating (A) | 256 | 255 | 219 | 256 | 255 | 219 | 256 | 255 | 219 | 256 | 255 | 219 | 256 | 255 | 219
SW | 60026684 | F106R | ROMA EAST | F106R_Roma East 33 kV | Time | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:30 | 22:00 | 16:30 | 17:00 | 22:00 | 15:30 | 17:00 | 7:30
SW | 60026684 | F106R | ROMA EAST | F106R_Roma East 33 kV | Voltage at Constrained Conductor | 32.4508 | 32.5181 | 32.4703 | 32.5013 | 32.5675 | 32.5209 | 32.5509 | 32.2436 | 32.2497 | 32.2673 | 32.273 | 32.2948 | 32.294 | 32.3122 | 32.3021
SW | 60026689 | F127R | ROMA WEST | F127R_Roma West 33 kV | % of Rated A | 6.5146 | 4.8003 | 4.8685 | 3.6855 | 2.8184 | 2.8362 | 1.471 | 1.401 | 1.4019 | 0.98843 | 0.98606 | 0.99116 | 1.8422 | 1.5891 | 1.5916
SW | 60026689 | F127R | ROMA WEST | F127R_Roma West 33 kV | Limiting Line Name | TR_LINE 125471_1 | TR_CABLE 140_1 | TR_LINE 125471_1 | TR_LINE 125471_1 | TR_CABLE 140_1 | TR_CABLE 140_1 | TR_LINE 125471_1 | TR_CABLE 140_1 | TR_CABLE 140_1 | TR_CABLE 140_1 | TR_CABLE 140_1 | TR_CABLE 140_1 | TR_LINE 125471_2 | TR_CABLE 140_1 | TR_CABLE 140_1
SW | 60026689 | F127R | ROMA WEST | F127R_Roma West 33 kV | Loading (A) | 7.557 | 7.6804 | 7.5949 | 4.2751 | 4.5094 | 4.538 | 1.7064 | 2.2415 | 2.243 | 1.5815 | 1.5777 | 1.5859 | 2.1369 | 2.5426 | 2.5466
SW | 60026689 | F127R | ROMA WEST | F127R_Roma West 33 kV | Loading (MVA) | 0.42522 | 0.4331 | 0.42408 | 0.24079 | 0.25451 | 0.25351 | 0.096197 | 0.12517 | 0.12652 | 0.089368 | 0.088202 | 0.088899 | 0.11937 | 0.14223 | 0.14283
SW | 60026689 | F127R | ROMA WEST | F127R_Roma West 33 kV | Loading (MW) | 0.42458 | 0.42509 | 0.42343 | 0.2395 | 0.23997 | 0.2394 | 0.092719 | 0.093007 | 0.093565 | 0.025207 | 0.025906 | 0.02619 | 0.11701 | 0.1146 | 0.11488
SW | 60026689 | F127R | ROMA WEST | F127R_Roma West 33 kV | Power Factor | 0.99851 | 0.98151 | 0.99847 | 0.99463 | 0.94286 | 0.94437 | 0.96385 | 0.74304 | 0.7395 | 0.28206 | 0.29371 | 0.2946 | 0.98023 | 0.80575 | 0.80431
SW | 60026689 | F127R | ROMA WEST | F127R_Roma West 33 kV | Rating (A) | 116 | 160 | 156 | 116 | 160 | 160 | 116 | 160 | 160 | 160 | 160 | 160 | 116 | 160 | 160
SW | 60026689 | F127R | ROMA WEST | F127R_Roma West 33 kV | Time | 12:00 | 17:00 | 6:30 | 12:00 | 17:00 | 23:30 | 12:00 | 17:30 | 8:30 | 16:00 | 21:00 | 4:00 | 15:30 | 21:00 | 4:00
SW | 60026689 | F127R | ROMA WEST | F127R_Roma West 33 kV | Voltage at Constrained Conductor | 32.4865 | 32.5569 | 32.2377 | 32.5185 | 32.5858 | 32.2527 | 32.5481 | 32.2402 | 32.5673 | 32.6253 | 32.2771 | 32.3646 | 32.2509 | 32.2959 | 32.3825
SW | 60026700 | F2060 | SLADEVALE 1 | F2060_Sladevale 1 33kV | % of Rated A | 87.5199 | 80.8903 | 87.6304 | 88.4835 | 81.8543 | 88.5917 | 89.3438 | 82.7144 | 89.4505 | 90.1244 | 83.4936 | 90.2293 | 90.9328 | 84.1643 | 90.9004
SW | 60026700 | F2060 | SLADEVALE 1 | F2060_Sladevale 1 33kV | Limiting Line Name | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1
SW | 60026700 | F2060 | SLADEVALE 1 | F2060_Sladevale 1 33kV | Loading (A) | 555.7511 | 513.6534 | 556.4528 | 561.8701 | 519.7751 | 562.5573 | 567.3329 | 525.2365 | 568.0108 | 572.2902 | 530.1843 | 572.9563 | 577.4235 | 534.4431 | 577.2173
SW | 60026700 | F2060 | SLADEVALE 1 | F2060_Sladevale 1 33kV | Loading (MVA) | 33.0345 | 30.6582 | 33.1527 | 33.4027 | 31.0292 | 33.5208 | 33.7287 | 31.3589 | 33.8482 | 34.0234 | 31.6566 | 34.144 | 34.4304 | 31.9119 | 34.3978
SW | 60026700 | F2060 | SLADEVALE 1 | F2060_Sladevale 1 33kV | Loading (MW) | 32.6848 | 30.0941 | 32.6835 | 33.049 | 30.4583 | 33.0477 | 33.3748 | 30.7841 | 33.3736 | 33.6706 | 31.0799 | 33.6694 | 33.9241 | 31.335 | 33.9244
SW | 60026700 | F2060 | SLADEVALE 1 | F2060_Sladevale 1 33kV | Power Factor | 0.98941 | 0.9816 | 0.98585 | 0.98941 | 0.9816 | 0.98589 | 0.98951 | 0.98167 | 0.98598 | 0.98963 | 0.98178 | 0.9861 | 0.9853 | 0.98192 | 0.98624
SW | 60026700 | F2060 | SLADEVALE 1 | F2060_Sladevale 1 33kV | Rating (A) | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635
SW | 60026700 | F2060 | SLADEVALE 1 | F2060_Sladevale 1 33kV | Time | 11:00 | 17:00 | 7:30 | 11:00 | 17:00 | 7:30 | 11:00 | 17:00 | 7:30 | 11:00 | 17:00 | 7:30 | 9:00 | 17:00 | 7:30
SW | 60026700 | F2060 | SLADEVALE 1 | F2060_Sladevale 1 33kV | Voltage at Constrained Conductor | 34.3184 | 34.46 | 34.3977 | 34.3229 | 34.4663 | 34.4023 | 34.3243 | 34.4703 | 34.4048 | 34.3242 | 34.4728 | 34.4059 | 34.426 | 34.4739 | 34.4057
SW | 60026708 | F217R | ST GEORGE | F217R_St George 66 kV | % of Rated A | 22.7103 | 20.0666 | 24.7275 | 22.349 | 19.7167 | 24.3228 | 21.7938 | 19.1811 | 23.7012 | 21.2921 | 18.7 | 23.1394 | 20.8633 | 18.288 | 22.6531
SW | 60026708 | F217R | ST GEORGE | F217R_St George 66 kV | Limiting Line Name | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1
SW | 60026708 | F217R | ST GEORGE | F217R_St George 66 kV | Loading (A) | 101.5152 | 91.1022 | 97.9211 | 99.9001 | 89.514 | 96.3185 | 97.4185 | 87.0821 | 93.8568 | 95.1758 | 84.8982 | 91.6318 | 93.2588 | 83.0275 | 89.7064
SW | 60026708 | F217R | ST GEORGE | F217R_St George 66 kV | Loading (MVA) | 11.4636 | 10.2985 | 11.0608 | 11.2893 | 10.1259 | 10.8875 | 11.0161 | 9.8572 | 10.6161 | 10.7687 | 9.615 | 10.3703 | 10.5568 | 9.4074 | 10.1572
SW | 60026708 | F217R | ST GEORGE | F217R_St George 66 kV | Loading (MW) | 10.1038 | 8.9538 | 9.7033 | 9.9434 | 8.7964 | 9.5445 | 9.6825 | 8.5424 | 9.286 | 9.4463 | 8.3125 | 9.052 | 9.2444 | 8.1158 | 8.8492
SW | 60026708 | F217R | ST GEORGE | F217R_St George 66 kV | Power Factor | 0.88138 | 0.86943 | 0.87727 | 0.88078 | 0.86871 | 0.87664 | 0.87894 | 0.86661 | 0.87471 | 0.87721 | 0.86453 | 0.87288 | 0.87568 | 0.8627 | 0.87123
SW | 60026708 | F217R | ST GEORGE | F217R_St George 66 kV | Rating (A) | 447 | 454 | 396 | 447 | 454 | 396 | 447 | 454 | 396 | 447 | 454 | 396 | 447 | 454 | 396
SW | 60026708 | F217R | ST GEORGE | F217R_St George 66 kV | Time | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30
SW | 60026708 | F217R | ST GEORGE | F217R_St George 66 kV | Voltage at Constrained Conductor | 65.1974 | 65.2657 | 65.2152 | 65.2441 | 65.3105 | 65.2616 | 65.287 | 65.3529 | 65.3038 | 65.3243 | 65.3871 | 65.3406 | 65.3557 | 65.4164 | 65.3715
SW | 60026714 | F2325 | BROXBURN | F2325_Broxburn 33 kV | % of Rated A | 2.3606 | 2.5857 | 3.0084 | 0.57038 | 0.58699 | 0.67678 | 1.9381 | 2.0892 | 2.4268 | 3.6087 | 3.9279 | 4.5658 | 5.0724 | 5.5308 | 6.4297
SW | 60026714 | F2325 | BROXBURN | F2325_Broxburn 33 kV | Limiting Line Name | TR_LINE 60091_1 | TR_LINE 60091_1 | TR_LINE 60091_1 | TR_LINE 23767_1 | TR_LINE 23767_1 | TR_LINE 23767_1 | TR_LINE 23767_1 | TR_LINE 23767_1 | TR_LINE 23767_1 | TR_LINE 23767_1 | TR_LINE 23767_1 | TR_LINE 23767_1 | TR_LINE 23767_1 | TR_LINE 23767_1 | TR_LINE 23767_1
SW | 60026714 | F2325 | BROXBURN | F2325_Broxburn 33 kV | Loading (A) | 7.8845 | 8.7138 | 8.7845 | 2.2188 | 2.301 | 2.3011 | 7.539 | 8.1895 | 8.251 | 14.0379 | 15.3973 | 15.5236 | 19.7315 | 21.6802 | 21.8607
SW | 60026714 | F2325 | BROXBURN | F2325_Broxburn 33 kV | Loading (MVA) | 0.52771 | 0.52544 | 0.5253 | 0.14934 | 0.16064 | 0.16065 | 0.50492 | 0.49794 | 0.49744 | 0.94037 | 0.93635 | 0.93605 | 1.3219 | 1.3186 | 1.3183
SW | 60026714 | F2325 | BROXBURN | F2325_Broxburn 33 kV | Loading (MW) | 0.52085 | 0.52105 | 0.52107 | 0.0088507 | 0.0088903 | 0.0088903 | 0.48326 | 0.48325 | 0.48325 | 0.92953 | 0.92923 | 0.9292 | 1.3148 | 1.3142 | 1.3141
SW | 60026714 | F2325 | BROXBURN | F2325_Broxburn 33 kV | Power Factor | 0.987 | 0.99164 | 0.99194 | 0.059265 | 0.055341 | 0.055338 | 0.95709 | 0.9705 | 0.97147 | 0.98847 | 0.9924 | 0.99268 | 0.99463 | 0.99663 | 0.99677
SW | 60026714 | F2325 | BROXBURN | F2325_Broxburn 33 kV | Rating (A) | 334 | 337 | 292 | 389 | 392 | 340 | 389 | 392 | 340 | 389 | 392 | 340 | 389 | 392 | 340
SW | 60026714 | F2325 | BROXBURN | F2325_Broxburn 33 kV | Time | 16:30 | 17:30 | 6:30 | 15:30 | 21:00 | 4:00 | 16:30 | 17:30 | 6:30 | 16:30 | 17:30 | 6:30 | 16:30 | 17:30 | 6:30
SW | 60026714 | F2325 | BROXBURN | F2325_Broxburn 33 kV | Voltage at Constrained Conductor | 38.6421 | 34.814 | 34.525 | 38.8606 | 40.308 | 40.3093 | 38.6677 | 35.1042 | 34.8076 | 38.6755 | 35.1101 | 34.8134 | 38.6803 | 35.1147 | 34.8181
SW | 60026720 | F2450 | CARRINGTON ROAD | F2450_Carrington Road 33 kV | % of Rated A | 0.81947 | 0.82111 | 0.82141 | 2.3601 | 2.3629 | 2.3637 | 3.8405 | 3.8438 | 3.8451 | 5.2906 | 5.2932 | 5.295 | 6.6326 | 6.635 | 6.6372
SW | 60026720 | F2450 | CARRINGTON ROAD | F2450_Carrington Road 33 kV | Limiting Line Name | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1
SW | 60026720 | F2450 | CARRINGTON ROAD | F2450_Carrington Road 33 kV | Loading (A) | 2.7616 | 2.7672 | 2.7681 | 7.9534 | 7.9628 | 7.9655 | 12.9426 | 12.9537 | 12.9581 | 17.8293 | 17.8382 | 17.8442 | 22.352 | 22.36 | 22.3675
SW | 60026720 | F2450 | CARRINGTON ROAD | F2450_Carrington Road 33 kV | Loading (MVA) | 0.16187 | 0.16203 | 0.16204 | 0.46643 | 0.46659 | 0.46659 | 0.75927 | 0.75942 | 0.75942 | 1.0461 | 1.0461 | 1.0462 | 1.3116 | 1.3116 | 1.3116
SW | 60026720 | F2450 | CARRINGTON ROAD | F2450_Carrington Road 33 kV | Loading (MW) | 0.16181 | 0.16197 | 0.16198 | 0.46639 | 0.46655 | 0.46655 | 0.75921 | 0.75936 | 0.75936 | 1.0461 | 1.0461 | 1.0461 | 1.3115 | 1.3115 | 1.3115
SW | 60026720 | F2450 | CARRINGTON ROAD | F2450_Carrington Road 33 kV | Power Factor | 0.99962 | 0.99963 | 0.99963 | 0.99991 | 0.99991 | 0.99991 | 0.99993 | 0.99992 | 0.99992 | 0.99991 | 0.99991 | 0.99991 | 0.99989 | 0.99989 | 0.99989
SW | 60026720 | F2450 | CARRINGTON ROAD | F2450_Carrington Road 33 kV | Rating (A) | 337 | 337 | 337 | 337 | 337 | 337 | 337 | 337 | 337 | 337 | 337 | 337 | 337 | 337 | 337
SW | 60026720 | F2450 | CARRINGTON ROAD | F2450_Carrington Road 33 kV | Time | 16:30 | 18:00 | 6:00 | 16:30 | 18:00 | 6:00 | 16:30 | 18:00 | 6:00 | 16:30 | 18:00 | 6:00 | 16:30 | 18:00 | 6:00
SW | 60026720 | F2450 | CARRINGTON ROAD | F2450_Carrington Road 33 kV | Voltage at Constrained Conductor | 33.8419 | 33.8069 | 33.7956 | 33.8591 | 33.8304 | 33.8191 | 33.8699 | 33.8473 | 33.836 | 33.8764 | 33.8596 | 33.8483 | 33.8793 | 33.8672 | 33.856
SW | 60026721 | F2460 | CECIL PLAINS | F2460_Cecil Plains 33 kV | % of Rated A | 29.1757 | 20.4889 | 20.7852 | 29.1867 | 20.5175 | 20.8141 | 29.2048 | 20.5465 | 20.8435 | 29.2263 | 20.576 | 20.8735 | 29.3461 | 20.6038 | 20.9016
SW | 60026721 | F2460 | CECIL PLAINS | F2460_Cecil Plains 33 kV | Limiting Line Name | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1
SW | 60026721 | F2460 | CECIL PLAINS | F2460_Cecil Plains 33 kV | Loading (A) | 41.7213 | 43.2316 | 43.2332 | 41.737 | 43.2919 | 43.2932 | 41.7629 | 43.353 | 43.3545 | 41.7936 | 43.4154 | 43.4168 | 41.965 | 43.474 | 43.4753
SW | 60026721 | F2460 | CECIL PLAINS | F2460_Cecil Plains 33 kV | Loading (MVA) | 2.8693 | 3.0809 | 3.0811 | 2.8719 | 3.0899 | 3.0901 | 2.8751 | 3.0982 | 3.0984 | 2.8781 | 3.106 | 3.1063 | 2.9002 | 3.1129 | 3.1131
SW | 60026721 | F2460 | CECIL PLAINS | F2460_Cecil Plains 33 kV | Loading (MW) | 0.088393 | 0.089697 | 0.089698 | 0.034217 | 0.03556 | 0.035561 | 0.014691 | 0.013317 | 0.013315 | 0.060705 | 0.059301 | 0.0593 | 0.10177 | 0.10046 | 0.10046
SW | 60026721 | F2460 | CECIL PLAINS | F2460_Cecil Plains 33 kV | Power Factor | 0.030806 | 0.029114 | 0.029112 | 0.011914 | 0.011508 | 0.011508 | 0.00511 | 0.0042981 | 0.0042974 | 0.021092 | 0.019092 | 0.019091 | 0.03509 | 0.032272 | 0.032269
SW | 60026721 | F2460 | CECIL PLAINS | F2460_Cecil Plains 33 kV | Rating (A) | 143 | 211 | 208 | 143 | 211 | 208 | 143 | 211 | 208 | 143 | 211 | 208 | 143 | 211 | 208
SW | 60026721 | F2460 | CECIL PLAINS | F2460_Cecil Plains 33 kV | Time | 15:30 | 21:00 | 4:00 | 15:30 | 21:00 | 4:00 | 15:30 | 21:00 | 4:00 | 15:30 | 21:00 | 4:00 | 9:00 | 21:00 | 4:00
SW | 60026721 | F2460 | CECIL PLAINS | F2460_Cecil Plains 33 kV | Voltage at Constrained Conductor | 39.7064 | 41.1449 | 41.1465 | 39.7276 | 41.2076 | 41.2089 | 39.7462 | 41.2601 | 41.2615 | 39.7596 | 41.3051 | 41.3065 | 39.9008 | 41.3407 | 41.3421
SW | 60026723 | F2520 | CLIFTON | F2520_Clifton 33 kV | % of Rated A | 23.5713 | 23.5288 | 23.5269 | 24.1608 | 24.122 | 24.111 | 24.8431 | 24.8068 | 24.7965 | 26.8097 | 25.4848 | 25.5202 | 28.6185 | 26.0559 | 26.0864
SW | 60026723 | F2520 | CLIFTON | F2520_Clifton 33 kV | Limiting Line Name | TR_LINE 188412_1 | TR_LINE 188412_1 | TR_LINE 188412_1 | TR_LINE 188412_1 | TR_LINE 188412_1 | TR_LINE 188412_1 | TR_LINE 188412_1 | TR_LINE 188412_1 | TR_LINE 188412_1 | TR_LINE 23763_1 | TR_LINE 188412_1 | TR_LINE 188412_1 | TR_LINE 23763_1 | TR_LINE 188412_1 | TR_LINE 188412_1
SW | 60026723 | F2520 | CLIFTON | F2520_Clifton 33 kV | Loading (A) | 28.757 | 28.7051 | 28.7028 | 29.4761 | 29.4288 | 29.4155 | 30.3086 | 30.2643 | 30.2517 | 44.2359 | 31.0915 | 31.1347 | 47.2206 | 31.7882 | 31.8254
SW | 60026723 | F2520 | CLIFTON | F2520_Clifton 33 kV | Loading (MVA) | 1.8021 | 1.7955 | 1.7952 | 1.8525 | 1.8462 | 1.8444 | 1.9095 | 1.9032 | 1.9014 | 2.7483 | 1.9591 | 1.9657 | 2.9373 | 2.0061 | 2.0122
SW | 60026723 | F2520 | CLIFTON | F2520_Clifton 33 kV | Loading (MW) | 0.2184 | 0.21847 | 0.21847 | 0.43188 | 0.43194 | 0.43196 | 0.60434 | 0.60439 | 0.60441 | 2.7479 | 0.74427 | 0.74421 | 2.9368 | 0.84854 | 0.84849
SW | 60026723 | F2520 | CLIFTON | F2520_Clifton 33 kV | Power Factor | 0.1212 | 0.12168 | 0.1217 | 0.23313 | 0.23396 | 0.2342 | 0.31648 | 0.31756 | 0.31787 | 0.99985 | 0.3799 | 0.3786 | 0.99983 | 0.42297 | 0.42168
SW | 60026723 | F2520 | CLIFTON | F2520_Clifton 33 kV | Rating (A) | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 165 | 122 | 122 | 165 | 122 | 122
SW | 60026723 | F2520 | CLIFTON | F2520_Clifton 33 kV | Time | 12:00 | 17:00 | 7:00 | 11:00 | 17:00 | 7:00 | 15:30 | 17:00 | 7:00 | 16:00 | 17:00 | 8:30 | 16:00 | 17:00 | 8:30
SW | 60026723 | F2520 | CLIFTON | F2520_Clifton 33 kV | Voltage at Constrained Conductor | 36.1798 | 36.1123 | 36.1092 | 36.2859 | 36.22 | 36.2014 | 36.3749 | 36.3077 | 36.2886 | 35.8699 | 36.3801 | 36.4517 | 35.9137 | 36.4362 | 36.5031
SW | 60026737 | F2777 | EAST STANTHORPE | F2777_East Stanthorpe 33 kV | % of Rated A | 1.6147 | 1.2035 | 1.2451 | 1.6152 | 1.2042 | 1.2458 | 1.6155 | 1.2038 | 1.2455 | 1.6157 | 1.2043 | 1.246 | 1.616 | 1.2052 | 1.247
SW | 60026737 | F2777 | EAST STANTHORPE | F2777_East Stanthorpe 33 kV | Limiting Line Name | TR_LINE 140241_1 | TR_LINE 140241_1 | TR_LINE 140241_1 | TR_LINE 140241_1 | TR_LINE 140241_1 | TR_LINE 140241_1 | TR_LINE 140241_1 | TR_LINE 140241_1 | TR_LINE 140241_1 | TR_LINE 140241_1 | TR_LINE 140241_1 | TR_LINE 140241_1 | TR_LINE 140241_1 | TR_LINE 140241_1 | TR_LINE 140241_1
SW | 60026737 | F2777 | EAST STANTHORPE | F2777_East Stanthorpe 33 kV | Loading (A) | 2.4867 | 2.5033 | 2.5027 | 2.4874 | 2.5046 | 2.5041 | 2.4879 | 2.504 | 2.5035 | 2.4882 | 2.5049 | 2.5045 | 2.4887 | 2.5068 | 2.5065
SW | 60026737 | F2777 | EAST STANTHORPE | F2777_East Stanthorpe 33 kV | Loading (MVA) | 0.14818 | 0.15027 | 0.1502 | 0.14827 | 0.15044 | 0.15037 | 0.14832 | 0.15046 | 0.15041 | 0.14837 | 0.15057 | 0.15052 | 0.14842 | 0.1507 | 0.15066
SW | 60026737 | F2777 | EAST STANTHORPE | F2777_East Stanthorpe 33 kV | Loading (MW) | 7.036e-05 | 7.1251e-05 | 7.1218e-05 | 7.04e-05 | 7.1328e-05 | 7.1299e-05 | 7.0427e-05 | 7.124e-05 | 7.1215e-05 | 7.0447e-05 | 7.1291e-05 | 7.1269e-05 | 7.0471e-05 | 7.1452e-05 | 7.1433e-05
SW | 60026737 | F2777 | EAST STANTHORPE | F2777_East Stanthorpe 33 kV | Power Factor | 0.00047482 | 0.00047414 | 0.00047414 | 0.00047482 | 0.00047414 | 0.00047414 | 0.00047482 | 0.00047348 | 0.00047348 | 0.00047482 | 0.00047348 | 0.00047348 | 0.00047482 | 0.00047414 | 0.00047414
SW | 60026737 | F2777 | EAST STANTHORPE | F2777_East Stanthorpe 33 kV | Rating (A) | 154 | 208 | 201 | 154 | 208 | 201 | 154 | 208 | 201 | 154 | 208 | 201 | 154 | 208 | 201
SW | 60026737 | F2777 | EAST STANTHORPE | F2777_East Stanthorpe 33 kV | Time | 16:30 | 18:00 | 6:00 | 16:30 | 18:00 | 6:00 | 16:30 | 18:00 | 6:00 | 16:30 | 18:00 | 6:00 | 9:00 | 18:00 | 6:00
SW | 60026737 | F2777 | EAST STANTHORPE | F2777_East Stanthorpe 33 kV | Voltage at Constrained Conductor | 34.4043 | 34.6585 | 34.6504 | 34.4141 | 34.6771 | 34.67 | 34.4209 | 34.6921 | 34.6859 | 34.4256 | 34.7044 | 34.699 | 34.4315 | 34.7074 | 34.7027
SW | 60026738 | F2780 | WARWICK EAST 1 | F2780_East Warwick No 1 33 kV | % of Rated A | 8.6879 | 8.5375 | 9.7167 | 8.5225 | 8.3818 | 9.5395 | 8.5859 | 8.4441 | 9.6108 | 8.8214 | 8.6704 | 9.8688 | 9.1526 | 8.9687 | 10.2098
SW | 60026738 | F2780 | WARWICK EAST 1 | F2780_East Warwick No 1 33 kV | Limiting Line Name | TR_LINE 23896_1 | TR_LINE 23896_1 | TR_LINE 23896_1 | TR_LINE 23896_1 | TR_LINE 23896_1 | TR_LINE 23896_1 | TR_LINE 23896_1 | TR_LINE 23896_1 | TR_LINE 23896_1 | TR_LINE 23896_1 | TR_LINE 23896_1 | TR_LINE 23896_1 | TR_LINE 23896_1 | TR_LINE 23896_1 | TR_LINE 23896_1
SW | 60026738 | F2780 | WARWICK EAST 1 | F2780_East Warwick No 1 33 kV | Loading (A) | 46.0457 | 46.3587 | 46.3486 | 45.1692 | 45.513 | 45.5036 | 45.5055 | 45.8516 | 45.8436 | 46.7535 | 47.0805 | 47.0741 | 48.5089 | 48.7002 | 48.7008
SW | 60026738 | F2780 | WARWICK EAST 1 | F2780_East Warwick No 1 33 kV | Loading (MVA) | 2.7384 | 2.7773 | 2.7761 | 2.6866 | 2.7277 | 2.7266 | 2.7067 | 2.7488 | 2.7478 | 2.781 | 2.8231 | 2.8223 | 2.8856 | 2.9126 | 2.9127
SW | 60026738 | F2780 | WARWICK EAST 1 | F2780_East Warwick No 1 33 kV | Loading (MW) | 0.55743 | 0.55749 | 0.55749 | 0.087784 | 0.087843 | 0.087842 | 0.33472 | 0.33466 | 0.33466 | 0.72698 | 0.72692 | 0.72692 | 1.0661 | 1.066 | 1.066
SW | 60026738 | F2780 | WARWICK EAST 1 | F2780_East Warwick No 1 33 kV | Power Factor | 0.20356 | 0.20073 | 0.20082 | 0.032675 | 0.032204 | 0.032217 | 0.12366 | 0.12175 | 0.12179 | 0.26141 | 0.25749 | 0.25756 | 0.36945 | 0.36601 | 0.36599
SW | 60026738 | F2780 | WARWICK EAST 1 | F2780_East Warwick No 1 33 kV | Rating (A) | 530 | 543 | 477 | 530 | 543 | 477 | 530 | 543 | 477 | 530 | 543 | 477 | 530 | 543 | 477
SW | 60026738 | F2780 | WARWICK EAST 1 | F2780_East Warwick No 1 33 kV | Time | 16:30 | 18:00 | 6:00 | 16:30 | 18:00 | 6:00 | 16:30 | 18:00 | 6:00 | 16:30 | 18:00 | 6:00 | 9:00 | 18:30 | 5:30
SW | 60026738 | F2780 | WARWICK EAST 1 | F2780_East Warwick No 1 33 kV | Voltage at Constrained Conductor | 34.3353 | 34.5889 | 34.5808 | 34.3396 | 34.6021 | 34.5949 | 34.3415 | 34.6122 | 34.6059 | 34.3418 | 34.62 | 34.6146 | 34.3438 | 34.5293 | 34.53
SW | 60026739 | F2785 | WARWICK EAST 2 | F2785_East Warwick No 2 33 kV | % of Rated A | 8.6451 | 8.4955 | 9.6689 | 8.4805 | 8.3405 | 9.4926 | 8.5437 | 8.4026 | 9.5635 | 8.778 | 8.6278 | 9.8202 | 9.1076 | 8.9246 | 10.1595
SW | 60026739 | F2785 | WARWICK EAST 2 | F2785_East Warwick No 2 33 kV | Limiting Line Name | TR_LINE 23891_1 | TR_LINE 23891_1 | TR_LINE 23891_1 | TR_LINE 23891_1 | TR_LINE 23891_1 | TR_LINE 23891_1 | TR_LINE 23891_1 | TR_LINE 23891_1 | TR_LINE 23891_1 | TR_LINE 23891_1 | TR_LINE 23891_1 | TR_LINE 23891_1 | TR_LINE 23891_1 | TR_LINE 23891_1 | TR_LINE 23891_1
SW | 60026739 | F2785 | WARWICK EAST 2 | F2785_East Warwick No 2 33 kV | Loading (A) | 45.8191 | 46.1304 | 46.1205 | 44.9469 | 45.289 | 45.2797 | 45.2815 | 45.6259 | 45.618 | 46.5233 | 46.8488 | 46.8424 | 48.2701 | 48.4604 | 48.461
SW | 60026739 | F2785 | WARWICK EAST 2 | F2785_East Warwick No 2 33 kV | Loading (MVA) | 2.7249 | 2.7637 | 2.7624 | 2.6733 | 2.7143 | 2.7132 | 2.6934 | 2.7353 | 2.7343 | 2.7673 | 2.8092 | 2.8084 | 2.8714 | 2.8982 | 2.8983
SW | 60026739 | F2785 | WARWICK EAST 2 | F2785_East Warwick No 2 33 kV | Loading (MW) | 0.55581 | 0.55588 | 0.55588 | 0.088482 | 0.088558 | 0.088556 | 0.33193 | 0.33186 | 0.33186 | 0.72226 | 0.72218 | 0.72218 | 1.0597 | 1.0596 | 1.0596
SW | 60026739 | F2785 | WARWICK EAST 2 | F2785_East Warwick No 2 33 kV | Power Factor | 0.20398 | 0.20114 | 0.20123 | 0.033098 | 0.032627 | 0.032639 | 0.12324 | 0.12132 | 0.12137 | 0.261 | 0.25707 | 0.25715 | 0.36904 | 0.3656 | 0.36559
SW | 60026739 | F2785 | WARWICK EAST 2 | F2785_East Warwick No 2 33 kV | Rating (A) | 530 | 543 | 477 | 530 | 543 | 477 | 530 | 543 | 477 | 530 | 543 | 477 | 530 | 543 | 477
SW | 60026739 | F2785 | WARWICK EAST 2 | F2785_East Warwick No 2 33 kV | Time | 16:30 | 18:00 | 6:00 | 16:30 | 18:00 | 6:00 | 16:30 | 18:00 | 6:00 | 16:30 | 18:00 | 6:00 | 9:00 | 18:30 | 5:30
SW | 60026739 | F2785 | WARWICK EAST 2 | F2785_East Warwick No 2 33 kV | Voltage at Constrained Conductor | 34.3353 | 34.5889 | 34.5808 | 34.3396 | 34.6021 | 34.5949 | 34.3415 | 34.6122 | 34.6059 | 34.3418 | 34.62 | 34.6146 | 34.3438 | 34.5293 | 34.53
SW | 60026753 | F3040 | HAMPTON STREET | F3040 Hampton Street | % of Rated A | 0.30932 | 0.30873 | 0.3087 | 0.3093 | 0.30872 | 0.30856 | 0.30929 | 0.30869 | 0.30853 | 0.30919 | 0.30865 | 0.30928 | 0.30909 | 0.30859 | 0.30918
SW | 60026753 | F3040 | HAMPTON STREET | F3040 Hampton Street | Limiting Line Name | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1
SW | 60026753 | F3040 | HAMPTON STREET | F3040 Hampton Street | Loading (A) | 1.5466 | 1.5436 | 1.5435 | 1.5465 | 1.5436 | 1.5428 | 1.5464 | 1.5435 | 1.5426 | 1.546 | 1.5432 | 1.5464 | 1.5455 | 1.543 | 1.5459
SW | 60026753 | F3040 | HAMPTON STREET | F3040 Hampton Street | Loading (MVA) | 0.093702 | 0.093343 | 0.093327 | 0.093692 | 0.093341 | 0.093242 | 0.093681 | 0.093323 | 0.093221 | 0.093625 | 0.093295 | 0.093677 | 0.093565 | 0.09326 | 0.093618
SW | 60026753 | F3040 | HAMPTON STREET | F3040 Hampton Street | Loading (MW) | 0.0013205 | 0.0013155 | 0.0013153 | 0.0013204 | 0.0013154 | 0.0013141 | 0.0013202 | 0.0013152 | 0.0013138 | 0.0013195 | 0.0013148 | 0.0013202 | 0.0013186 | 0.0013143 | 0.0013193
SW | 60026753 | F3040 | HAMPTON STREET | F3040 Hampton Street | Power Factor | 0.014093 | 0.014093 | 0.014093 | 0.014093 | 0.014093 | 0.014093 | 0.014093 | 0.014093 | 0.014093 | 0.014093 | 0.014093 | 0.014093 | 0.014093 | 0.014093 | 0.014093
SW | 60026753 | F3040 | HAMPTON STREET | F3040 Hampton Street | Rating (A) | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500
SW | 60026753 | F3040 | HAMPTON STREET | F3040 Hampton Street | Time | 12:00 | 17:00 | 7:00 | 11:00 | 17:00 | 7:00 | 15:30 | 17:00 | 7:00 | 15:30 | 17:00 | 8:30 | 15:30 | 17:00 | 8:30
SW | 60026753 | F3040 | HAMPTON STREET | F3040 Hampton Street | Voltage at Constrained Conductor | 34.9791 | 34.9121 | 34.9091 | 34.9772 | 34.9116 | 34.8932 | 34.9753 | 34.9083 | 34.8893 | 34.9648 | 34.903 | 34.9745 | 34.9536 | 34.8965 | 34.9634
SW | 60026769 | F3255 | JENNINGS STREET | F3255_Jennings Street 33 kV | % of Rated A | 5.2322 | 5.2222 | 5.2291 | 3.4959 | 3.489 | 3.4945 | 1.8665 | 1.8665 | 1.8695 | 0.47394 | 0.47352 | 0.47401 | 1.3084 | 1.308 | 1.3084
SW | 60026769 | F3255 | JENNINGS STREET | F3255_Jennings Street 33 kV | Limiting Line Name | TR_LINE 120572_1 | TR_CABLE 7923_1 | TR_CABLE 7923_1 | TR_LINE 123294_1 | TR_CABLE 7923_1 | TR_CABLE 7923_1 | TR_CABLE 81_1 | TR_CABLE 81_1 | TR_CABLE 81_1 | TR_CABLE 81_1 | TR_CABLE 81_1 | TR_CABLE 81_1 | TR_CABLE 81_1 | TR_CABLE 81_1 | TR_CABLE 81_1
SW | 60026769 | F3255 | JENNINGS STREET | F3255_Jennings Street 33 kV | Loading (A) | 32.2827 | 32.2211 | 32.2636 | 21.5696 | 21.5273 | 21.5608 | 11.6658 | 11.6657 | 11.6843 | 2.9621 | 2.9595 | 2.9626 | 8.1774 | 8.1751 | 8.1774
SW | 60026769 | F3255 | JENNINGS STREET | F3255_Jennings Street 33 kV | Loading (MVA) | 1.93 | 1.9299 | 1.9299 | 1.2906 | 1.2898 | 1.2898 | 0.69929 | 0.69929 | 0.69917 | 0.17939 | 0.17891 | 0.17946 | 0.48991 | 0.48994 | 0.4899
SW | 60026769 | F3255 | JENNINGS STREET | F3255_Jennings Street 33 kV | Loading (MW) | 1.93 | 1.9299 | 1.9299 | 1.2903 | 1.2898 | 1.2898 | 0.68398 | 0.68398 | 0.68397 | 0.090855 | 0.090845 | 0.090856 | 0.46616 | 0.46615 | 0.46616
SW | 60026769 | F3255 | JENNINGS STREET | F3255_Jennings Street 33 kV | Power Factor | 1 | 1 | 1 | 0.99981 | 0.99993 | 0.99993 | 0.97811 | 0.97811 | 0.97827 | 0.50646 | 0.50776 | 0.50626 | 0.95152 | 0.95146 | 0.95152
SW | 60026769 | F3255 | JENNINGS STREET | F3255_Jennings Street 33 kV | Rating (A) | 617 | 617 | 617 | 617 | 617 | 617 | 625 | 625 | 625 | 625 | 625 | 625 | 625 | 625 | 625
SW | 60026769 | F3255 | JENNINGS STREET | F3255_Jennings Street 33 kV | Time | 10:30 | 18:30 | 8:30 | 15:30 | 17:30 | 8:30 | 16:00 | 17:30 | 8:30 | 15:30 | 17:00 | 8:30 | 16:00 | 17:30 | 8:00
SW | 60026769 | F3255 | JENNINGS STREET | F3255_Jennings Street 33 kV | Voltage at Constrained Conductor | 34.5158 | 34.5816 | 34.536 | 34.5442 | 34.593 | 34.5393 | 34.6087 | 34.6088 | 34.5477 | 34.9648 | 34.903 | 34.9745 | 34.5891 | 34.6008 | 34.5886
SW | 60026772 | F3315 | SLADEVALE 2 | F3315_Sladevale 2 33kV | % of Rated A | 85.9955 | 79.396 | 86.1212 | 86.3079 | 79.714 | 86.4338 | 86.5874 | 79.9981 | 86.7142 | 86.8438 | 80.2572 | 86.971 | 87.2333 | 80.4828 | 87.1951
SW | 60026772 | F3315 | SLADEVALE 2 | F3315_Sladevale 2 33kV | Limiting Line Name | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1
SW | 60026772 | F3315 | SLADEVALE 2 | F3315_Sladevale 2 33kV | Loading (A) | 546.0715 | 504.1643 | 546.8696 | 548.0549 | 506.1838 | 548.8547 | 549.8297 | 507.9878 | 550.6355 | 551.4583 | 509.6335 | 552.2656 | 553.9317 | 511.0659 | 553.6887
SW | 60026772 | F3315 | SLADEVALE 2 | F3315_Sladevale 2 33kV | Loading (MVA) | 32.4942 | 30.1192 | 32.6151 | 32.6154 | 30.2444 | 32.7368 | 32.7215 | 30.3549 | 32.8446 | 32.8177 | 30.4547 | 32.9422 | 33.0599 | 30.5408 | 33.0264
SW | 60026772 | F3315 | SLADEVALE 2 | F3315_Sladevale 2 33kV | Loading (MW) | 32.1137 | 29.5228 | 32.1123 | 32.2311 | 29.6402 | 32.2297 | 32.3374 | 29.7465 | 32.336 | 32.4355 | 29.8445 | 32.4341 | 32.52 | 29.9308 | 32.5204
SW | 60026772 | F3315 | SLADEVALE 2 | F3315_Sladevale 2 33kV | Power Factor | 0.98829 | 0.9802 | 0.98458 | 0.98822 | 0.98002 | 0.98451 | 0.98826 | 0.97996 | 0.98452 | 0.98836 | 0.97996 | 0.98458 | 0.98367 | 0.98003 | 0.98468
SW | 60026772 | F3315 | SLADEVALE 2 | F3315_Sladevale 2 33kV | Rating (A) | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635
SW | 60026772 | F3315 | SLADEVALE 2 | F3315_Sladevale 2 33kV | Time | 11:00 | 17:00 | 7:30 | 11:00 | 17:00 | 7:30 | 11:00 | 17:00 | 7:30 | 11:00 | 17:00 | 7:30 | 9:00 | 17:00 | 7:30
SW | 60026772 | F3315 | SLADEVALE 2 | F3315_Sladevale 2 33kV | Voltage at Constrained Conductor | 34.3554 | 34.4914 | 34.433 | 34.3588 | 34.4965 | 34.4364 | 34.3593 | 34.4996 | 34.4381 | 34.3585 | 34.5014 | 34.4384 | 34.4576 | 34.5019 | 34.4377
SW | 60026789 | F3530 | MILLMERRAN | F3530_Millmerran 33 kV | % of Rated A | 4.9159 | 3.5729 | 3.7023 | 1.4138 | 1.0258 | 1.0552 | 5.6476 | 4.1215 | 4.2718 | 10.176 | 7.4429 | 7.7176 | 14.0183 | 10.3748 | 10.6343
SW | 60026789 | F3530 | MILLMERRAN | F3530_Millmerran 33 kV | Limiting Line Name | TR_LINE 24237_1 | TR_LINE 24237_1 | TR_LINE 24237_1 | TR_LINE 24237_1 | TR_LINE 24237_1 | TR_LINE 24237_1 | TR_LINE 24237_1 | TR_LINE 24237_1 | TR_LINE 24237_1 | TR_LINE 24237_1 | TR_LINE 24237_1 | TR_LINE 24237_1 | TR_LINE 24237_1 | TR_LINE 24237_1 | TR_LINE 24237_1
SW | 60026789 | F3530 | MILLMERRAN | F3530_Millmerran 33 kV | Loading (A) | 6.2432 | 6.4312 | 6.4789 | 1.7955 | 1.8465 | 1.8466 | 7.1724 | 7.4187 | 7.4756 | 12.9236 | 13.3971 | 13.5058 | 17.803 | 18.6744 | 18.6098
SW | 60026789 | F3530 | MILLMERRAN | F3530_Millmerran 33 kV | Loading (MVA) | 0.3797 | 0.37807 | 0.3777 | 0.10998 | 0.11732 | 0.11733 | 0.43778 | 0.436 | 0.43565 | 0.78996 | 0.78868 | 0.7884 | 1.0895 | 1.0877 | 1.0878
SW | 60026789 | F3530 | MILLMERRAN | F3530_Millmerran 33 kV | Loading (MW) | 0.3667 | 0.36678 | 0.3668 | 0.038877 | 0.038876 | 0.038876 | 0.42645 | 0.42633 | 0.42631 | 0.78468 | 0.7843 | 0.78421 | 1.0865 | 1.0855 | 1.0856
SW | 60026789 | F3530 | MILLMERRAN | F3530_Millmerran 33 kV | Power Factor | 0.96577 | 0.97012 | 0.97113 | 0.35347 | 0.33136 | 0.33134 | 0.97412 | 0.97783 | 0.97857 | 0.99332 | 0.99445 | 0.99469 | 0.99726 | 0.99799 | 0.99794
SW | 60026789 | F3530 | MILLMERRAN | F3530_Millmerran 33 kV | Rating (A) | 127 | 180 | 175 | 127 | 180 | 175 | 127 | 180 | 175 | 127 | 180 | 175 | 127 | 180 | 175
SW | 60026789 | F3530 | MILLMERRAN | F3530_Millmerran 33 kV | Time | 16:30 | 17:30 | 6:30 | 15:30 | 21:00 | 4:00 | 16:30 | 17:30 | 6:30 | 16:30 | 17:30 | 6:30 | 16:30 | 17:30 | 6:30
SW | 60026789 | F3530 | MILLMERRAN | F3530_Millmerran 33 kV | Voltage at Constrained Conductor | 35.1137 | 33.9406 | 33.6578 | 35.3657 | 36.6829 | 36.6841 | 35.2395 | 33.9311 | 33.6454 | 35.2908 | 33.9881 | 33.7026 | 35.3317 | 33.6281 | 33.7487
SW | 60026795 | F3820 | BOUNDARY ROAD | F3820_Boundary Road 33 kV | % of Rated A | 6.2815 | 6.2866 | 6.2882 | 3.5758 | 3.5768 | 3.5772 | 2.071 | 2.0725 | 2.0725 | 3.2468 | 3.2472 | 3.2473 | 5.4771 | 5.4786 | 5.4799
SW | 60026795 | F3820 | BOUNDARY ROAD | F3820_Boundary Road 33 kV | Limiting Line Name | TR_CABLE 73_1 | TR_CABLE 73_1 | TR_CABLE 73_1 | TR_CABLE 73_1 | TR_CABLE 73_1 | TR_CABLE 73_1 | TR_CABLE 73_1 | TR_CABLE 73_1 | TR_CABLE 73_1 | TR_CABLE 73_1 | TR_CABLE 73_1 | TR_CABLE 73_1 | TR_CABLE 73_1 | TR_CABLE 73_1 | TR_CABLE 73_1
SW | 60026795 | F3820 | BOUNDARY ROAD | F3820_Boundary Road 33 kV | Loading (A) | 43.3423 | 43.3773 | 43.3886 | 24.6729 | 24.6798 | 24.6825 | 14.29 | 14.3 | 14.3005 | 22.4029 | 22.4054 | 22.406 | 37.7922 | 37.8021 | 37.8113
SW | 60026795 | F3820 | BOUNDARY ROAD | F3820_Boundary Road 33 kV | Loading (MVA) | 2.5399 | 2.5393 | 2.5391 | 1.446 | 1.4452 | 1.4449 | 0.84368 | 0.84487 | 0.84493 | 1.3126 | 1.3121 | 1.3117 | 2.2138 | 2.2135 | 2.2133
SW | 60026795 | F3820 | BOUNDARY ROAD | F3820_Boundary Road 33 kV | Loading (MW) | 2.4101 | 2.4101 | 2.4101 | 1.1898 | 1.1898 | 1.1898 | 0.070276 | 0.0703 | 0.070301 | 1.0219 | 1.0219 | 1.0219 | 2.0604 | 2.0604 | 2.0604
SW | 60026795 | F3820 | BOUNDARY ROAD | F3820_Boundary Road 33 kV | Power Factor | 0.9489 | 0.94911 | 0.94918 | 0.82284 | 0.82329 | 0.82347 | 0.083297 | 0.083207 | 0.083203 | 0.7785 | 0.77881 | 0.77906 | 0.93072 | 0.93082 | 0.9309
SW | 60026795 | F3820 | BOUNDARY ROAD | F3820_Boundary Road 33 kV | Rating (A) | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690
SW | 60026795 | F3820 | BOUNDARY ROAD | F3820_Boundary Road 33 kV | Time | 16:30 | 18:00 | 6:00 | 16:30 | 18:00 | 6:00 | 16:00 | 21:00 | 4:00 | 16:30 | 18:00 | 6:00 | 16:30 | 18:00 | 6:00
SW | 60026795 | F3820 | BOUNDARY ROAD | F3820_Boundary Road 33 kV | Voltage at Constrained Conductor | 33.8331 | 33.7982 | 33.7868 | 33.8366 | 33.8079 | 33.7966 | 34.0867 | 34.1109 | 34.1121 | 33.8282 | 33.8114 | 33.8 | 33.8195 | 33.8073 | 33.7961
SW | 60026796 | F3830 | NORWIN | F3830_Norwin 33 kV | % of Rated A | 3.8802 | 3.1059 | 3.2602 | 4.4803 | 3.5391 | 3.7149 | 5.1568 | 4.2606 | 4.341 | 5.8307 | 5.2124 | 5.2565 | 6.4134 | 5.988 | 6.0385
SW | 60026796 | F3830 | NORWIN | F3830_Norwin 33 kV | Limiting Line Name | TR_LINE 23942_1 | TR_LINE 23942_1 | TR_LINE 23942_1 | TR_LINE 23942_1 | TR_LINE 23942_1 | TR_LINE 23942_1 | TR_LINE 23942_1 | TR_CABLE 175_1 | TR_LINE 23942_1 | TR_LINE 23942_1 | TR_CABLE 175_1 | TR_CABLE 175_1 | TR_LINE 23942_1 | TR_CABLE 175_1 | TR_CABLE 175_1
SW | 60026796 | F3830 | NORWIN | F3830_Norwin 33 kV | Loading (A) | 4.501 | 4.5967 | 4.5969 | 5.1971 | 5.2379 | 5.2379 | 5.9818 | 4.9424 | 6.1209 | 6.7636 | 6.0464 | 6.0975 | 7.4395 | 6.9461 | 7.0047
SW | 60026796 | F3830 | NORWIN | F3830_Norwin 33 kV | Loading (MVA) | 0.30289 | 0.32053 | 0.32055 | 0.34981 | 0.36569 | 0.3657 | 0.40063 | 0.30194 | 0.36902 | 0.45308 | 0.36973 | 0.36973 | 0.49843 | 0.42505 | 0.42505
SW | 60026796 | F3830 | NORWIN | F3830_Norwin 33 kV | Loading (MW) | 0.1408 | 0.14078 | 0.14078 | 0.22483 | 0.22482 | 0.22482 | 0.30061 | 0.30194 | 0.3005 | 0.36798 | 0.36973 | 0.36973 | 0.4229 | 0.42505 | 0.42505
SW | 60026796 | F3830 | NORWIN | F3830_Norwin 33 kV | Power Factor | 0.46487 | 0.43922 | 0.43919 | 0.6427 | 0.61479 | 0.61477 | 0.75033 | 1 | 0.81431 | 0.81216 | 0.99999 | 0.99999 | 0.84846 | 0.99999 | 0.99999
SW | 60026796 | F3830 | NORWIN | F3830_Norwin 33 kV | Rating (A) | 116 | 148 | 141 | 116 | 148 | 141 | 116 | 116 | 141 | 116 | 116 | 116 | 116 | 116 | 116
SW | 60026796 | F3830 | NORWIN | F3830_Norwin 33 kV | Time | 15:30 | 21:00 | 4:00 | 15:30 | 21:00 | 4:00 | 16:30 | 17:30 | 6:30 | 16:30 | 17:30 | 6:30 | 16:30 | 17:30 | 6:30
SW | 60026796 | F3830 | NORWIN | F3830_Norwin 33 kV | Voltage at Constrained Conductor | 38.8516 | 40.2581 | 40.2597 | 38.8609 | 40.3083 | 40.3096 | 38.6681 | 35.2717 | 34.8079 | 38.6758 | 35.3043 | 35.0084 | 38.6807 | 35.3298 | 35.0342
SW | 60026800 | F3855 | O'MARAS ROAD | F3855 Omaras Road 33 kV | % of Rated A | 22.7892 | 22.813 | 22.8207 | 23.5247 | 23.5448 | 23.5527 | 23.5262 | 23.5421 | 23.55 | 23.5306 | 23.5424 | 23.5503 | 23.5367 | 23.5452 | 23.5531
SW | 60026800 | F3855 | O'MARAS ROAD | F3855 Omaras Road 33 kV | Limiting Line Name | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1
SW | 60026800 | F3855 | O'MARAS ROAD | F3855 Omaras Road 33 kV | Loading (A) | 53.0989 | 53.1543 | 53.1722 | 54.8125 | 54.8593 | 54.8778 | 54.816 | 54.853 | 54.8715 | 54.8262 | 54.8537 | 54.8723 | 54.8405 | 54.8603 | 54.8787
SW | 60026800 | F3855 | O'MARAS ROAD | F3855 Omaras Road 33 kV | Loading (MVA) | 3.1005 | 3.1005 | 3.1005 | 3.2005 | 3.2005 | 3.2005 | 3.2005 | 3.2005 | 3.2005 | 3.2005 | 3.2005 | 3.2005 | 3.2005 | 3.2005 | 3.2005
SW | 60026800 | F3855 | O'MARAS ROAD | F3855 Omaras Road 33 kV | Loading (MW) | 3.1004 | 3.1004 | 3.1004 | 3.2004 | 3.2004 | 3.2004 | 3.2004 | 3.2004 | 3.2004 | 3.2004 | 3.2004 | 3.2004 | 3.2004 | 3.2004 | 3.2004
SW | 60026800 | F3855 | O'MARAS ROAD | F3855 Omaras Road 33 kV | Power Factor | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998 | 0.99998
SW | 60026800 | F3855 | O'MARAS ROAD | F3855 Omaras Road 33 kV | Rating (A) | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233
SW | 60026800 | F3855 | O'MARAS ROAD | F3855 Omaras Road 33 kV | Time | 16:30 | 18:00 | 6:00 | 16:30 | 18:00 | 6:00 | 16:30 | 18:00 | 6:00 | 16:30 | 18:00 | 6:00 | 16:30 | 18:00 | 6:00
SW | 60026800 | F3855 | O'MARAS ROAD | F3855 Omaras Road 33 kV | Voltage at Constrained Conductor | 33.7116 | 33.6764 | 33.6651 | 33.711 | 33.6822 | 33.6708 | 33.7088 | 33.6861 | 33.6747 | 33.7026 | 33.6856 | 33.6743 | 33.6938 | 33.6816 | 33.6703
SW | 60026810 | F3970 | POZIERES | F3970_Pozieres 33 kV | % of Rated A | 1.3228 | 0.9198 | 0.95179 | 1.5808 | 1.1493 | 1.1895 | 3.2137 | 2.3009 | 2.3831 | 4.8702 | 3.4034 | 3.5273 | 6.2291 | 4.3191 | 4.4789
SW | 60026810 | F3970 | POZIERES | F3970_Pozieres 33 kV | Limiting Line Name | TR_LINE 23786_1 | TR_LINE 23974_1 | TR_LINE 23974_1 | TR_LINE 23786_1 | TR_LINE 23974_1 | TR_LINE 23974_1 | TR_LINE 221370_1 | TR_LINE 23974_1 | TR_LINE 23974_1 | TR_LINE 221370_1 | TR_LINE 23974_1 | TR_LINE 23974_1 | TR_LINE 221370_1 | TR_LINE 23974_1 | TR_LINE 23974_1
SW | 60026810 | F3970 | POZIERES | F3970_Pozieres 33 kV | Loading (A) | 2.1826 | 1.9132 | 1.9131 | 2.6082 | 2.3906 | 2.3908 | 4.5956 | 4.7858 | 4.79 | 6.9644 | 7.0791 | 7.0898 | 8.9077 | 8.9837 | 9.0025
SW | 60026810 | F3970 | POZIERES | F3970_Pozieres 33 kV | Loading (MVA) | 0.1422 | 0.12527 | 0.12523 | 0.1694 | 0.15542 | 0.15537 | 0.29931 | 0.31188 | 0.31182 | 0.45443 | 0.46231 | 0.46224 | 0.58214 | 0.58775 | 0.58768
SW | 60026810 | F3970 | POZIERES | F3970_Pozieres 33 kV | Loading (MW) | 0.078921 | 0.07872 | 0.07872 | 0.122 | 0.1222 | 0.1222 | 0.2971 | 0.29687 | 0.29687 | 0.45305 | 0.45254 | 0.45254 | 0.58113 | 0.58031 | 0.58031
SW | 60026810 | F3970 | POZIERES | F3970_Pozieres 33 kV | Power Factor | 0.55501 | 0.62839 | 0.62858 | 0.72017 | 0.78627 | 0.78651 | 0.9926 | 0.95186 | 0.95206 | 0.99697 | 0.97886 | 0.97901 | 0.99827 | 0.98734 | 0.98746
SW | 60026810 | F3970 | POZIERES | F3970_Pozieres 33 kV | Rating (A) | 165 | 208 | 201 | 165 | 208 | 201 | 143 | 208 | 201 | 143 | 208 | 201 | 143 | 208 | 201
SW | 60026810 | F3970 | POZIERES | F3970_Pozieres 33 kV | Time | 16:30 | 18:00 | 6:30 | 9:00 | 20:00 | 8:30 | 9:00 | 20:00 | 8:30 | 9:00 | 20:00 | 8:30 | 14:30 | 20:00 | 8:30
SW | 60026810 | F3970 | POZIERES | F3970_Pozieres 33 kV | Voltage at Constrained Conductor | 37.6145 | 37.8039 | 37.7945 | 37.4983 | 37.5353 | 37.5206 | 37.6024 | 37.625 | 37.5839 | 37.6719 | 37.7051 | 37.6424 | 37.7311 | 37.7728 | 37.6889
SW | 60026811 | F3980 | PURRAWUNDA | F3980_Purrawunda 33 kV | % of Rated A | 22.8153 | 22.8099 | 22.8194 | 22.8733 | 22.8791 | 22.8816 | 23.0364 | 23.0522 | 23.053 | 23.2733 | 23.2976 | 23.2983 | 23.5306 | 23.5618 | 23.5624
SW | 60026811 | F3980 | PURRAWUNDA | F3980_Purrawunda 33 kV | Limiting Line Name | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1
SW | 60026811 | F3980 | PURRAWUNDA | F3980_Purrawunda 33 kV | Loading (A) | 48.1402 | 48.1289 | 48.149 | 48.2627 | 48.275 | 48.2802 | 48.6068 | 48.6402 | 48.6418 | 49.1066 | 49.158 | 49.1595 | 49.6495 | 49.7153 | 49.7167
SW | 60026811 | F3980 | PURRAWUNDA | F3980_Purrawunda 33 kV | Loading (MVA) | 2.8425 | 2.8412 | 2.8435 | 2.8498 | 2.8513 | 2.8519 | 2.8697 | 2.8737 | 2.8739 | 2.8985 | 2.9048 | 2.905 | 2.9296 | 2.9379 | 2.9381
SW | 60026811 | F3980 | PURRAWUNDA | F3980_Purrawunda 33 kV | Loading (MW) | 0.10225 | 0.10223 | 0.10226 | 0.12134 | 0.12132 | 0.12131 | 0.32737 | 0.32731 | 0.32731 | 0.51401 | 0.51392 | 0.51392 | 0.66809 | 0.66797 | 0.66797
SW | 60026811 | F3980 | PURRAWUNDA | F3980_Purrawunda 33 kV | Power Factor | 0.03597 | 0.03598 | 0.035962 | 0.04258 | 0.04255 | 0.042538 | 0.11408 | 0.1139 | 0.11389 | 0.17734 | 0.17692 | 0.17691 | 0.22805 | 0.22737 | 0.22735
SW | 60026811 | F3980 | PURRAWUNDA | F3980_Purrawunda 33 kV | Rating (A) | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211
SW | 60026811 | F3980 | PURRAWUNDA | F3980_Purrawunda 33 kV | Time | 16:00 | 17:30 | 6:30 | 16:00 | 21:00 | 6:30 | 16:00 | 21:00 | 4:00 | 16:00 | 21:00 | 4:00 | 16:00 | 21:00 | 4:00
SW | 60026811 | F3980 | PURRAWUNDA | F3980_Purrawunda 33 kV | Voltage at Constrained Conductor | 34.0905 | 34.0824 | 34.0967 | 34.0913 | 34.1001 | 34.1038 | 34.0867 | 34.1109 | 34.1121 | 34.078 | 34.1164 | 34.1175 | 34.0669 | 34.1179 | 34.119
SW | 60026813 | F4005 | RACECOURSE | F4005_Racecourse 33 kV | % of Rated A | 6.7617 | 6.7687 | 6.7709 | 5.444 | 5.4486 | 5.4504 | 4.1505 | 4.1532 | 4.1546 | 2.8381 | 2.8395 | 2.8404 | 1.5635 | 1.564 | 1.5645
SW | 60026813 | F4005 | RACECOURSE | F4005_Racecourse 33 kV | Limiting Line Name | TR_CABLE 67_1 | TR_CABLE 67_1 | TR_CABLE 67_1 | TR_CABLE 67_1 | TR_CABLE 67_1 | TR_CABLE 67_1 | TR_CABLE 67_1 | TR_CABLE 67_1 | TR_CABLE 67_1 | TR_CABLE 67_1 | TR_CABLE 67_1 | TR_CABLE 67_1 | TR_CABLE 67_1 | TR_CABLE 67_1 | TR_CABLE 67_1
SW | 60026813 | F4005 | RACECOURSE | F4005_Racecourse 33 kV | Loading (A) | 47.7373 | 47.7868 | 47.8028 | 38.4346 | 38.4672 | 38.48 | 29.3023 | 29.3218 | 29.3316 | 20.0368 | 20.0466 | 20.0532 | 11.0382 | 11.0419 | 11.0454
SW | 60026813 | F4005 | RACECOURSE | F4005_Racecourse 33 kV | Loading (MVA) | 2.7974 | 2.7974 | 2.7974 | 2.2525 | 2.2525 | 2.2525 | 1.7172 | 1.7172 | 1.7172 | 1.174 | 1.174 | 1.174 | 0.64658 | 0.64657 | 0.64656
SW | 60026813 | F4005 | RACECOURSE | F4005_Racecourse 33 kV | Loading (MW) | 2.7971 | 2.7971 | 2.7971 | 2.2517 | 2.2517 | 2.2517 | 1.7156 | 1.7156 | 1.7156 | 1.1709 | 1.1709 | 1.1709 | 0.64011 | 0.64011 | 0.64011
SW | 60026813 | F4005 | RACECOURSE | F4005_Racecourse 33 kV | Power Factor | 0.99988 | 0.99989 | 0.99989 | 0.99963 | 0.99963 | 0.99964 | 0.99904 | 0.99904 | 0.99905 | 0.99735 | 0.99736 | 0.99736 | 0.98999 | 0.99 | 0.99002
SW | 60026813 | F4005 | RACECOURSE | F4005_Racecourse 33 kV | Rating (A) | 706 | 706 | 706 | 706 | 706 | 706 | 706 | 706 | 706 | 706 | 706 | 706 | 706 | 706 | 706
SW | 60026813 | F4005 | RACECOURSE | F4005_Racecourse 33 kV | Time | 16:30 | 18:00 | 6:00 | 16:30 | 18:00 | 6:00 | 16:30 | 18:00 | 6:00 | 16:30 | 18:00 | 6:00 | 16:30 | 18:00 | 6:00
SW | 60026813 | F4005 | RACECOURSE | F4005_Racecourse 33 kV | Voltage at Constrained Conductor | 33.8331 | 33.7982 | 33.7868 | 33.8366 | 33.8079 | 33.7966 | 33.8344 | 33.8118 | 33.8005 | 33.8282 | 33.8114 | 33.8 | 33.8195 | 33.8073 | 33.7961
SW | 60026814 | F4015 | RAMSAY STREET | F4015_Ramsay Street 33 kV | % of Rated A | 5.3026 | 5.2923 | 5.2993 | 3.5432 | 3.536 | 3.5415 | 1.8719 | 1.8699 | 1.8732 | 0.36028 | 0.36017 | 0.36029 | 1.2889 | 1.2856 | 1.286
SW | 60026814 | F4015 | RAMSAY STREET | F4015_Ramsay Street 33 kV | Limiting Line Name | TR_LINE 23917_1 | TR_CABLE 7922_1 | TR_CABLE 7922_1 | TR_LINE 23917_1 | TR_CABLE 7922_1 | TR_CABLE 7922_1 | TR_LINE 23917_1 | TR_CABLE 7922_1 | TR_CABLE 7922_1 | TR_CABLE 86_1 | TR_CABLE 86_1 | TR_CABLE 86_1 | TR_LINE 23917_1 | TR_CABLE 7922_1 | TR_CABLE 7922_1
SW | 60026814 | F4015 | RAMSAY STREET | F4015_Ramsay Street 33 kV | Loading (A) | 31.8156 | 31.7539 | 31.7958 | 21.2591 | 21.2157 | 21.2487 | 11.2316 | 11.2194 | 11.2391 | 2.2517 | 2.251 | 2.2518 | 7.7332 | 7.7133 | 7.716
SW | 60026814 | F4015 | RAMSAY STREET | F4015_Ramsay Street 33 kV | Loading (MVA) | 1.9034 | 1.9018 | 1.9018 | 1.2721 | 1.2711 | 1.2711 | 0.67326 | 0.67236 | 0.67235 | 0.13637 | 0.13608 | 0.13641 | 0.4633 | 0.46238 | 0.46238
SW | 60026814 | F4015 | RAMSAY STREET | F4015_Ramsay Street 33 kV | Loading (MW) | 1.9034 | 1.9018 | 1.9018 | 1.2717 | 1.2709 | 1.2709 | 0.67194 | 0.67174 | 0.67174 | 0.088572 | 0.088566 | 0.088573 | 0.46143 | 0.46152 | 0.46152
SW | 60026814 | F4015 | RAMSAY STREET | F4015_Ramsay Street 33 kV | Power Factor | 0.99998 | 1 | 1 | 0.99969 | 0.99988 | 0.99988 | 0.99804 | 0.99908 | 0.99909 | 0.64952 | 0.65082 | 0.64931 | 0.99595 | 0.99815 | 0.99816
SW | 60026814 | F4015 | RAMSAY STREET | F4015_Ramsay Street 33 kV | Rating (A) | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 625 | 625 | 625 | 600 | 600 | 600
SW | 60026814 | F4015 | RAMSAY STREET | F4015_Ramsay Street 33 kV | Time | 10:30 | 18:30 | 8:30 | 15:30 | 17:30 | 8:30 | 16:00 | 17:30 | 8:30 | 15:30 | 17:00 | 8:30 | 16:00 | 17:30 | 8:00
SW | 60026814 | F4015 | RAMSAY STREET | F4015_Ramsay Street 33 kV | Voltage at Constrained Conductor | 34.5409 | 34.5782 | 34.5326 | 34.5461 | 34.5907 | 34.537 | 34.6082 | 34.5994 | 34.5383 | 34.9648 | 34.903 | 34.9745 | 34.5895 | 34.6095 | 34.5973
SW | 60026827 | F4245 | STANTHORPE | F4245_Stanthorpe 33 kV | % of Rated A | 27.8343 | 27.972 | 28.0441 | 28.3916 | 28.5302 | 28.5971 | 29.3102 | 29.4426 | 29.5012 | 30.4991 | 30.6198 | 30.6748 | 31.8257 | 31.9162 | 31.9702
SW | 60026827 | F4245 | STANTHORPE | F4245_Stanthorpe 33 kV | Limiting Line Name | TR_CABLE 107_1 | TR_CABLE 107_1 | TR_LINE 23344_1 | TR_CABLE 107_1 | TR_CABLE 107_1 | TR_LINE 23344_1 | TR_CABLE 107_1 | TR_CABLE 107_1 | TR_LINE 23344_1 | TR_CABLE 107_1 | TR_CABLE 107_1 | TR_LINE 23344_1 | TR_CABLE 107_1 | TR_CABLE 107_1 | TR_LINE 23344_1
SW | 60026827 | F4245 | STANTHORPE | F4245_Stanthorpe 33 kV | Loading (A) | 81.2763 | 81.6782 | 81.8822 | 82.9036 | 83.3081 | 83.497 | 85.5858 | 85.9723 | 86.1371 | 89.0574 | 89.4099 | 89.5644 | 92.931 | 93.1953 | 93.3471
SW | 60026827 | F4245 | STANTHORPE | F4245_Stanthorpe 33 kV | Loading (MVA) | 5.3202 | 5.3731 | 5.3607 | 5.4398 | 5.4952 | 5.478 | 5.6275 | 5.6843 | 5.6606 | 5.8667 | 5.9241 | 5.8953 | 6.1365 | 6.1856 | 6.1526
SW | 60026827 | F4245 | STANTHORPE | F4245_Stanthorpe 33 kV | Loading (MW) | 0.36351 | 0.36351 | 0.34633 | 1.0946 | 1.0946 | 1.0768 | 1.7697 | 1.7697 | 1.7507 | 2.4077 | 2.4077 | 2.3872 | 2.9851 | 2.9851 | 2.9628
SW | 60026827 | F4245 | STANTHORPE | F4245_Stanthorpe 33 kV | Power Factor | 0.068327 | 0.067653 | 0.064605 | 0.20123 | 0.1992 | 0.19656 | 0.31448 | 0.31134 | 0.30928 | 0.41041 | 0.40643 | 0.40493 | 0.48645 | 0.48259 | 0.48154
SW | 60026827 | F4245 | STANTHORPE | F4245_Stanthorpe 33 kV | Rating (A) | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292
SW | 60026827 | F4245 | STANTHORPE | F4245_Stanthorpe 33 kV | Time | 16:30 | 18:00 | 6:30 | 16:30 | 18:00 | 6:30 | 16:30 | 18:00 | 6:30 | 16:30 | 18:00 | 6:30 | 9:00 | 18:00 | 6:30
SW | 60026827 | F4245 | STANTHORPE | F4245_Stanthorpe 33 kV | Voltage at Constrained Conductor | 37.792 | 37.9805 | 37.7982 | 37.8833 | 38.0835 | 37.878 | 37.9625 | 38.1733 | 37.9413 | 38.0333 | 38.254 | 38.0023 | 38.124 | 38.3201 | 38.0539
SW | 60026834 | F4470 | VACY STREET | F4470 Vacy Street | % of Rated A | 0.45441 | 0.45354 | 0.4535 | 0.45439 | 0.45353 | 0.45329 | 0.45436 | 0.45349 | 0.45324 | 0.45422 | 0.45342 | 0.45435 | 0.45408 | 0.45334 | 0.45421
SW | 60026834 | F4470 | VACY STREET | F4470 Vacy Street | Limiting Line Name | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2
SW | 60026834 | F4470 | VACY STREET | F4470 Vacy Street | Loading (A) | 2.272 | 2.2677 | 2.2675 | 2.2719 | 2.2677 | 2.2665 | 2.2718 | 2.2674 | 2.2662 | 2.2711 | 2.2671 | 2.2717 | 2.2704 | 2.2667 | 2.271
SW | 60026834 | F4470 | VACY STREET | F4470 Vacy Street | Loading (MVA) | 0.13765 | 0.13713 | 0.1371 | 0.13764 | 0.13712 | 0.13698 | 0.13762 | 0.1371 | 0.13695 | 0.13754 | 0.13706 | 0.13762 | 0.13745 | 0.137 | 0.13753
SW | 60026834 | F4470 | VACY STREET | F4470 Vacy Street | Loading (MW) | 0.0023929 | 0.0023837 | 0.0023833 | 0.0023926 | 0.0023836 | 0.0023811 | 0.0023923 | 0.0023832 | 0.0023806 | 0.0023909 | 0.0023825 | 0.0023922 | 0.0023894 | 0.0023816 | 0.0023907
SW | 60026834 | F4470 | VACY STREET | F4470 Vacy Street | Power Factor | 0.017383 | 0.017383 | 0.017383 | 0.017383 | 0.017383 | 0.017383 | 0.017383 | 0.017383 | 0.017383 | 0.017383 | 0.017383 | 0.017383 | 0.017383 | 0.017383 | 0.017383
SW | 60026834 | F4470 | VACY STREET | F4470 Vacy Street | Rating (A) | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500
SW | 60026834 | F4470 | VACY STREET | F4470 Vacy Street | Time | 12:00 | 17:00 | 7:00 | 11:00 | 17:00 | 7:00 | 15:30 | 17:00 | 7:00 | 15:30 | 17:00 | 8:30 | 15:30 | 17:00 | 8:30
SW | 60026834 | F4470 | VACY STREET | F4470 Vacy Street | Voltage at Constrained Conductor | 34.9791 | 34.9121 | 34.9091 | 34.9772 | 34.9116 | 34.8932 | 34.9753 | 34.9083 | 34.8893 | 34.9648 | 34.903 | 34.9745 | 34.9536 | 34.8965 | 34.9634
SW | 60026843 | F4605 | WEST WARWICK | F4605_West Warwick 33 kV | % of Rated A | 2.5836 | 2.5498 | 2.9551 | 4.4366 | 4.3774 | 5.0745 | 6.1427 | 6.0597 | 7.0258 | 7.7391 | 7.6336 | 8.8512 | 9.1759 | 9.0503 | 10.4947
SW | 60026843 | F4605 | WEST WARWICK | F4605_West Warwick 33 kV | Limiting Line Name | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1
SW | 60026843 | F4605 | WEST WARWICK | F4605_West Warwick 33 kV | Loading (A) | 10.0501 | 9.9954 | 10.0472 | 17.2585 | 17.1592 | 17.2534 | 23.8948 | 23.7538 | 23.8875 | 30.1047 | 29.9237 | 30.0938 | 35.6939 | 35.477 | 35.6819
SW | 60026843 | F4605 | WEST WARWICK | F4605_West Warwick 33 kV | Loading (MVA) | 0.59546 | 0.59564 | 0.59547 | 1.0226 | 1.0227 | 1.0226 | 1.4159 | 1.4159 | 1.4159 | 1.7837 | 1.7838 | 1.7837 | 2.1148 | 2.1149 | 2.1148
SW | 60026843 | F4605 | WEST WARWICK | F4605_West Warwick 33 kV | Loading (MW) | 0.58755 | 0.58754 | 0.58755 | 1.0185 | 1.0185 | 1.0185 | 1.4134 | 1.4134 | 1.4134 | 1.7821 | 1.7822 | 1.7821 | 2.1138 | 2.1138 | 2.1138
SW | 60026843 | F4605 | WEST WARWICK | F4605_West Warwick 33 kV | Power Factor | 0.98672 | 0.9864 | 0.9867 | 0.99599 | 0.99588 | 0.99598 | 0.99824 | 0.99818 | 0.99824 | 0.99912 | 0.99908 | 0.99912 | 0.99953 | 0.9995 | 0.99953
SW | 60026843 | F4605 | WEST WARWICK | F4605_West Warwick 33 kV | Rating (A) | 389 | 392 | 340 | 389 | 392 | 340 | 389 | 392 | 340 | 389 | 392 | 340 | 389 | 392 | 340
SW | 60026843 | F4605 | WEST WARWICK | F4605_West Warwick 33 kV | Time | 9:00 | 17:00 | 8:30 | 9:00 | 17:00 | 8:30 | 9:00 | 17:00 | 8:30 | 9:00 | 17:00 | 8:30 | 15:00 | 17:00 | 8:30
SW | 60026843 | F4605 | WEST WARWICK | F4605_West Warwick 33 kV | Voltage at Constrained Conductor | 34.2078 | 34.4055 | 34.218 | 34.2096 | 34.4113 | 34.22 | 34.21 | 34.4154 | 34.2207 | 34.2083 | 34.4171 | 34.2208 | 34.2065 | 34.4173 | 34.2181
SW | 60026846 | F4685 | WYALLA STREET | F4685_Wyalla Street 33 kV | % of Rated A | 6.104 | 6.1103 | 6.1124 | 4.9126 | 4.9168 | 4.9184 | 3.7425 | 3.7451 | 3.7463 | 2.5543 | 2.5555 | 2.5564 | 1.3962 | 1.3967 | 1.3972
SW | 60026846 | F4685 | WYALLA STREET | F4685_Wyalla Street 33 kV | Limiting Line Name | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1
SW | 60026846 | F4685 | WYALLA STREET | F4685_Wyalla Street 33 kV | Loading (A) | 42.1175 | 42.1613 | 42.1754 | 33.8969 | 33.9258 | 33.9372 | 25.8235 | 25.8409 | 25.8495 | 17.6243 | 17.6331 | 17.639 | 9.634 | 9.6374 | 9.6406
SW | 60026846 | F4685 | WYALLA STREET | F4685_Wyalla Street 33 kV | Loading (MVA) | 2.4657 | 2.4657 | 2.4657 | 1.9851 | 1.9851 | 1.9851 | 1.5125 | 1.5125 | 1.5125 | 1.0323 | 1.0323 | 1.0323 | 0.56422 | 0.56422 | 0.56422
SW | 60026846 | F4685 | WYALLA STREET | F4685_Wyalla Street 33 kV | Loading (MW) | 2.4656 | 2.4656 | 2.4656 | 1.985 | 1.985 | 1.985 | 1.5125 | 1.5125 | 1.5125 | 1.0322 | 1.0322 | 1.0322 | 0.56405 | 0.56405 | 0.56405
SW | 60026846 | F4685 | WYALLA STREET | F4685_Wyalla Street 33 kV | Power Factor | 0.99993 | 0.99993 | 0.99993 | 0.99998 | 0.99998 | 0.99998 | 1 | 1 | 1 | 0.99997 | 0.99997 | 0.99997 | 0.99969 | 0.99969 | 0.99969
SW | 60026846 | F4685 | WYALLA STREET | F4685_Wyalla Street 33 kV | Rating (A) | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690
SW | 60026846 | F4685 | WYALLA STREET | F4685_Wyalla Street 33 kV | Time | 16:30 | 18:00 | 6:00 | 16:30 | 18:00 | 6:00 | 16:30 | 18:00 | 6:00 | 16:30 | 18:00 | 6:00 | 16:30 | 18:00 | 6:00
SW | 60026846 | F4685 | WYALLA STREET | F4685_Wyalla Street 33 kV | Voltage at Constrained Conductor | 33.8005 | 33.7655 | 33.7542 | 33.8108 | 33.7821 | 33.7708 | 33.8152 | 33.7926 | 33.7813 | 33.8156 | 33.7987 | 33.7874 | 33.8131 | 33.8009 | 33.7897
SW | 60026848 | 790 | 790 WARWICK - STANTHORPE | 790_Warwick-Stanthorpe 110 kV | % of Rated A | 20.4805 | 15.157 | 17.1327 | 20.9834 | 15.3475 | 17.3455 | 21.8979 | 15.6769 | 17.7136 | 23.0944 | 16.3503 | 18.2008 | 24.4005 | 17.2543 | 18.738
SW | 60026848 | 790 | 790 WARWICK - STANTHORPE | 790_Warwick-Stanthorpe 110 kV | Limiting Line Name | TR_LINE 198182_1 | TR_LINE 178160_1 | TR_LINE 178160_1 | TR_LINE 198182_1 | TR_LINE 178160_1 | TR_LINE 178160_1 | TR_LINE 198182_1 | TR_LINE 178160_1 | TR_LINE 178160_1 | TR_LINE 198182_1 | TR_LINE 198182_1 | TR_LINE 178160_1 | TR_LINE 198182_1 | TR_LINE 198182_1 | TR_LINE 178160_1
SW | 60026848 | 790 | 790 WARWICK - STANTHORPE | 790_Warwick-Stanthorpe 110 kV | Loading (A) | 26.0103 | 38.0441 | 38.0347 | 26.649 | 38.5222 | 38.5069 | 27.8103 | 39.349 | 39.3243 | 29.3299 | 29.4306 | 40.4058 | 30.9886 | 31.0577 | 41.5983
SW | 60026848 | 790 | 790 WARWICK - STANTHORPE | 790_Warwick-Stanthorpe 110 kV | Loading (MVA) | 5.391 | 7.816 | 7.8122 | 5.534 | 7.9194 | 7.9129 | 5.7846 | 8.0935 | 8.0826 | 6.1095 | 6.1662 | 8.3073 | 6.4682 | 6.516 | 8.5542
SW | 60026848 | 790 | 790 WARWICK - STANTHORPE | 790_Warwick-Stanthorpe 110 kV | Loading (MW) | 0.2652 | 0.19042 | 0.19046 | 1.1964 | 1.1191 | 1.1192 | 2.0448 | 1.963 | 1.9631 | 2.8366 | 2.8364 | 2.7487 | 3.5395 | 3.5394 | 3.4447
SW | 60026848 | 790 | 790 WARWICK - STANTHORPE | 790_Warwick-Stanthorpe 110 kV | Power Factor | 0.049193 | 0.024362 | 0.02438 | 0.2162 | 0.14132 | 0.14144 | 0.35349 | 0.24254 | 0.24288 | 0.46429 | 0.46 | 0.33088 | 0.54722 | 0.54318 | 0.40269
SW | 60026848 | 790 | 790 WARWICK - STANTHORPE | 790_Warwick-Stanthorpe 110 kV | Rating (A) | 127 | 251 | 222 | 127 | 251 | 222 | 127 | 251 | 222 | 127 | 180 | 222 | 127 | 180 | 222
SW | 60026848 | 790 | 790 WARWICK - STANTHORPE | 790_Warwick-Stanthorpe 110 kV | Time | 16:30 | 18:00 | 6:30 | 16:30 | 18:00 | 6:30 | 16:30 | 18:00 | 6:30 | 16:30 | 18:00 | 6:30 | 9:00 | 18:00 | 6:30
SW | 60026848 | 790 | 790 WARWICK - STANTHORPE | 790_Warwick-Stanthorpe 110 kV | Voltage at Constrained Conductor | 119.6649 | 118.6147 | 118.5851 | 119.8935 | 118.6912 | 118.6418 | 120.0902 | 118.7527 | 118.6677 | 120.2645 | 120.9645 | 118.7009 | 120.5083 | 121.1303 | 118.725
SW | 60026891 | F074C | MILES - CONDAMINE | F074C_Miles-Condamine 33 kV | % of Rated A | 8.4742 | 4.9259 | 5.5526 | 8.0423 | 4.6468 | 5.2879 | 7.7264 | 4.4163 | 5.0437 | 7.4383 | 4.2334 | 4.9721 | 7.2303 | 4.1018 | 4.9672
SW | 60026891 | F074C | MILES - CONDAMINE | F074C_Miles-Condamine 33 kV | Limiting Line Name | TR_LINE 138809_5 | TR_LINE 138809_5 | TR_LINE 138809_5 | TR_LINE 138809_5 | TR_LINE 138809_5 | TR_LINE 138809_5 | TR_LINE 138809_5 | TR_LINE 138809_5 | TR_LINE 138809_5 | TR_LINE 138809_5 | TR_LINE 138809_5 | TR_LINE 22686_3 | TR_LINE 138809_5 | TR_LINE 138809_5 | TR_LINE 22686_3
SW | 60026891 | F074C | MILES - CONDAMINE | F074C_Miles-Condamine 33 kV | Loading (A) | 12.1181 | 10.4429 | 11.605 | 11.5005 | 9.8511 | 11.0517 | 11.0488 | 9.3627 | 10.5414 | 10.6368 | 8.9747 | 5.7676 | 10.3394 | 8.6958 | 5.762
SW | 60026891 | F074C | MILES - CONDAMINE | F074C_Miles-Condamine 33 kV | Loading (MVA) | 0.68941 | 0.59241 | 0.66091 | 0.65543 | 0.55981 | 0.62655 | 0.62663 | 0.53283 | 0.59849 | 0.60397 | 0.51132 | 0.32489 | 0.58762 | 0.49587 | 0.32489
SW | 60026891 | F074C | MILES - CONDAMINE | F074C_Miles-Condamine 33 kV | Loading (MW) | 0.68702 | 0.57463 | 0.65481 | 0.65268 | 0.54036 | 0.62054 | 0.62415 | 0.51181 | 0.59194 | 0.60125 | 0.48896 | 0.26988 | 0.58471 | 0.47245 | 0.26988
SW | 60026891 | F074C | MILES - CONDAMINE | F074C_Miles-Condamine 33 kV | Power Factor | 0.99654 | 0.96999 | 0.99077 | 0.99581 | 0.96526 | 0.99041 | 0.99603 | 0.96054 | 0.98906 | 0.99549 | 0.95626 | 0.83067 | 0.99506 | 0.95276 | 0.83067
SW | 60026891 | F074C | MILES - CONDAMINE | F074C_Miles-Condamine 33 kV | Rating (A) | 143 | 212 | 209 | 143 | 212 | 209 | 143 | 212 | 209 | 143 | 212 | 116 | 143 | 212 | 116
SW | 60026891 | F074C | MILES - CONDAMINE | F074C_Miles-Condamine 33 kV | Time | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30
SW | 60026891 | F074C | MILES - CONDAMINE | F074C_Miles-Condamine 33 kV | Voltage at Constrained Conductor | 32.8458 | 32.7523 | 32.8804 | 32.9038 | 32.809 | 32.7317 | 32.7446 | 32.857 | 32.7795 | 32.7828 | 32.8938 | 32.5225 | 32.8126 | 32.9233 | 32.5541
SW | 60026893 | F077C | WANDOAN | F077C_Wandoan 33 kV | % of Rated A | 14.2721 | 9.3476 | 11.2787 | 13.0022 | 9.3262 | 11.3237 | 12.4946 | 9.3077 | 11.2306 | 12.4731 | 9.3496 | 11.282 | 12.4557 | 9.3369 | 11.3366
SW | 60026893 | F077C | WANDOAN | F077C_Wandoan 33 kV | Limiting Line Name | TR_LINE 155280_1 | TR_CABLE 126_1 | TR_CABLE 126_1 | TR_LINE 155280_1 | TR_CABLE 126_1 | TR_CABLE 126_1 | TR_CABLE 126_1 | TR_CABLE 126_1 | TR_CABLE 126_1 | TR_CABLE 126_1 | TR_CABLE 126_1 | TR_CABLE 126_1 | TR_CABLE 126_1 | TR_CABLE 126_1 | TR_CABLE 126_1
SW | 60026893 | F077C | WANDOAN | F077C_Wandoan 33 kV | Loading (A) | 24.6907 | 9.3476 | 11.2787 | 22.4938 | 9.3262 | 11.3237 | 12.4946 | 9.3077 | 11.2306 | 12.4731 | 9.3496 | 11.282 | 12.4557 | 9.3369 | 11.3366
SW | 60026893 | F077C | WANDOAN | F077C_Wandoan 33 kV | Loading (MVA) | 1.4026 | 0.52986 | 0.64141 | 1.2809 | 0.52987 | 0.6414 | 0.70805 | 0.52989 | 0.64143 | 0.70805 | 0.52985 | 0.64141 | 0.70805 | 0.52986 | 0.6414
SW | 60026893 | F077C | WANDOAN | F077C_Wandoan 33 kV | Loading (MW) | 1.3855 | 0.43975 | 0.53276 | 1.2628 | 0.43975 | 0.53276 | 0.58817 | 0.43975 | 0.53276 | 0.58817 | 0.43975 | 0.53276 | 0.58817 | 0.43975 | 0.53276
SW | 60026893 | F077C | WANDOAN | F077C_Wandoan 33 kV | Power Factor | 0.98778 | 0.82993 | 0.83061 | 0.9859 | 0.82991 | 0.83062 | 0.83068 | 0.82989 | 0.83059 | 0.83068 | 0.82994 | 0.83061 | 0.83068 | 0.82992 | 0.83062
SW | 60026893 | F077C | WANDOAN | F077C_Wandoan 33 kV | Rating (A) | 173 | 100 | 100 | 173 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
SW | 60026893 | F077C | WANDOAN | F077C_Wandoan 33 kV | Time | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30
SW | 60026893 | F077C | WANDOAN | F077C_Wandoan 33 kV | Voltage at Constrained Conductor | 32.7985 | 32.7263 | 32.8335 | 32.876 | 32.8023 | 32.7026 | 32.7177 | 32.8686 | 32.9749 | 32.774 | 32.7192 | 32.824 | 32.8199 | 32.7644 | 32.6653
SW | 60026994 | F083S | Dirrabandi Town 33 kV | F083S_Dirrabandi Town 33 kV | % of Rated A | 12.8024 | 11.323 | 11.6109 | 12.8274 | 11.3415 | 11.625 | 12.8342 | 11.3434 | 11.6296 | 12.84 | 11.35 | 11.6304 | 12.8452 | 11.3536 | 11.637
SW | 60026994 | F083S | Dirrabandi Town 33 kV | F083S_Dirrabandi Town 33 kV | Limiting Line Name | TR_LINE 27419_1 | TR_LINE 44480_1 | TR_LINE 44480_1 | TR_LINE 27419_1 | TR_LINE 44480_1 | TR_LINE 44480_1 | TR_LINE 27419_1 | TR_LINE 44480_1 | TR_LINE 44480_1 | TR_LINE 27419_1 | TR_LINE 44480_1 | TR_LINE 44480_1 | TR_LINE 27419_1 | TR_LINE 44480_1 | TR_LINE 44480_1
SW | 60026994 | F083S | Dirrabandi Town 33 kV | F083S_Dirrabandi Town 33 kV | Loading (A) | 9.3457 | 10.3039 | 9.9854 | 9.364 | 10.3207 | 9.9975 | 9.369 | 10.3225 | 10.0015 | 9.3732 | 10.3285 | 10.0021 | 9.377 | 10.3318 | 10.0078
SW | 60026994 | F083S | Dirrabandi Town 33 kV | F083S_Dirrabandi Town 33 kV | Loading (MVA) | 0.51704 | 0.57987 | 0.56214 | 0.51707 | 0.57974 | 0.56176 | 0.51708 | 0.57957 | 0.56172 | 0.51708 | 0.57968 | 0.56153 | 0.51709 | 0.57965 | 0.56166
SW | 60026994 | F083S | Dirrabandi Town 33 kV | F083S_Dirrabandi Town 33 kV | Loading (MW) | 0.45777 | 0.5764 | 0.55727 | 0.45777 | 0.5764 | 0.55725 | 0.45776 | 0.57638 | 0.55725 | 0.45777 | 0.5764 | 0.55723 | 0.45777 | 0.5764 | 0.55725
SW | 60026994 | F083S | Dirrabandi Town 33 kV | F083S_Dirrabandi Town 33 kV | Power Factor | 0.88538 | 0.99402 | 0.99133 | 0.88531 | 0.99425 | 0.99197 | 0.8853 | 0.9945 | 0.99204 | 0.88528 | 0.99435 | 0.99234 | 0.88527 | 0.99439 | 0.99215
SW | 60026994 | F083S | Dirrabandi Town 33 kV | F083S_Dirrabandi Town 33 kV | Rating (A) | 73 | 91 | 86 | 73 | 91 | 86 | 73 | 91 | 86 | 73 | 91 | 86 | 73 | 91 | 86
SW | 60026994 | F083S | Dirrabandi Town 33 kV | F083S_Dirrabandi Town 33 kV | Time | 12:00 | 21:30 | 22:00 | 12:00 | 21:30 | 22:00 | 12:00 | 21:30 | 22:00 | 12:00 | 21:30 | 22:00 | 12:00 | 21:30 | 22:00
SW | 60026994 | F083S | Dirrabandi Town 33 kV | F083S_Dirrabandi Town 33 kV | Voltage at Constrained Conductor | 31.9408 | 32.4914 | 32.5028 | 31.8806 | 32.4311 | 32.4413 | 31.8641 | 32.4159 | 32.4262 | 31.8503 | 32.4032 | 32.4128 | 31.8378 | 32.3916 | 32.4022
SW | 60027002 | F097D | JANDOWAE | F097D_Jandowae 33 kV | % of Rated A | 5.7293 | 4.4925 | 5.4316 | 5.4238 | 4.1464 | 5.0465 | 5.2043 | 3.8645 | 4.7338 | 5.197 | 3.8425 | 4.7015 | 5.1913 | 3.838 | 4.6964
SW | 60027002 | F097D | JANDOWAE | F097D_Jandowae 33 kV | Limiting Line Name | TR_LINE 102880_1 | TR_LINE 25163_1 | TR_LINE 102880_1 | TR_LINE 102880_1 | TR_LINE 25163_1 | TR_LINE 102880_1 | TR_CABLE 130_1 | TR_LINE 25163_1 | TR_LINE 102880_1 | TR_CABLE 130_1 | TR_CABLE 130_1 | TR_CABLE 130_1 | TR_CABLE 130_1 | TR_CABLE 130_1 | TR_CABLE 130_1
SW | 60027002 | F097D | JANDOWAE | F097D_Jandowae 33 kV | Loading (A) | 13.9221 | 12.2195 | 13.4703 | 13.1799 | 11.2781 | 12.5153 | 8.3269 | 10.5115 | 11.7397 | 8.3152 | 6.1479 | 7.5225 | 8.306 | 6.1408 | 7.5142
SW | 60027002 | F097D | JANDOWAE | F097D_Jandowae 33 kV | Loading (MVA) | 0.81902 | 0.71519 | 0.78134 | 0.76549 | 0.66146 | 0.72741 | 0.48442 | 0.61757 | 0.68348 | 0.48442 | 0.36169 | 0.43858 | 0.48441 | 0.36169 | 0.43857
SW | 60027002 | F097D | JANDOWAE | F097D_Jandowae 33 kV | Loading (MW) | 0.81748 | 0.71494 | 0.78066 | 0.76347 | 0.66115 | 0.72679 | 0.40972 | 0.61721 | 0.68285 | 0.40972 | 0.30633 | 0.37112 | 0.40972 | 0.30633 | 0.37112
SW | 60027002 | F097D | JANDOWAE | F097D_Jandowae 33 kV | Power Factor | 0.99811 | 0.99966 | 0.99914 | 0.99736 | 0.99954 | 0.99914 | 0.84579 | 0.99942 | 0.99908 | 0.8458 | 0.84693 | 0.8462 | 0.84581 | 0.84694 | 0.84621
SW | 60027002 | F097D | JANDOWAE | F097D_Jandowae 33 kV | Rating (A) | 243 | 272 | 248 | 243 | 272 | 248 | 160 | 272 | 248 | 160 | 160 | 160 | 160 | 160 | 160
SW | 60027002 | F097D | JANDOWAE | F097D_Jandowae 33 kV | Time | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30
SW | 60027002 | F097D | JANDOWAE | F097D_Jandowae 33 kV | Voltage at Constrained Conductor | 33.9649 | 33.7914 | 33.4888 | 33.5324 | 33.8614 | 33.5565 | 33.5878 | 33.9204 | 33.613 | 33.6348 | 33.9666 | 33.6608 | 33.6715 | 34.0055 | 33.6976
SW | 60027003 | F099D | WARRA | F099D_Warra 33 kV | % of Rated A | 10.7708 | 9.4723 | 11.1757 | 10.7915 | 9.3369 | 11.0207 | 10.694 | 9.3849 | 10.9228 | 10.6193 | 9.31 | 10.8396 | 10.5669 | 9.2602 | 10.7849
SW | 60027003 | F099D | WARRA | F099D_Warra 33 kV | Limiting Line Name | TR_LINE 25305_1 | TR_LINE 25305_1 | TR_LINE 25305_1 | TR_LINE 25305_1 | TR_LINE 25305_1 | TR_LINE 25305_1 | TR_LINE 25305_1 | TR_LINE 25305_1 | TR_LINE 25305_1 | TR_LINE 25305_1 | TR_LINE 25305_1 | TR_LINE 25305_1 | TR_LINE 25305_1 | TR_LINE 25305_1 | TR_LINE 25305_1
SW | 60027003 | F099D | WARRA | F099D_Warra 33 kV | Loading (A) | 17.7718 | 16.7644 | 17.5434 | 17.8059 | 16.5247 | 17.3 | 17.6452 | 16.6097 | 17.1461 | 17.5218 | 16.477 | 17.0182 | 17.4354 | 16.3888 | 16.9323
SW | 60027003 | F099D | WARRA | F099D_Warra 33 kV | Loading (MVA) | 1.0452 | 0.98406 | 1.0175 | 1.0339 | 0.97216 | 1.0054 | 1.0263 | 0.96485 | 0.99815 | 1.0206 | 0.95869 | 0.99199 | 1.0166 | 0.95476 | 0.98806
SW | 60027003 | F099D | WARRA | F099D_Warra 33 kV | Loading (MW) | 1.0275 | 0.97862 | 1.0035 | 1.0153 | 0.96656 | 0.99143 | 1.0078 | 0.95889 | 0.98386 | 1.0016 | 0.95279 | 0.97762 | 0.99777 | 0.94892 | 0.97375
SW | 60027003 | F099D | WARRA | F099D_Warra 33 kV | Power Factor | 0.98297 | 0.99447 | 0.98622 | 0.98201 | 0.99424 | 0.98609 | 0.98193 | 0.99382 | 0.98569 | 0.98147 | 0.99385 | 0.98552 | 0.98145 | 0.99388 | 0.98551
SW | 60027003 | F099D | WARRA | F099D_Warra 33 kV | Rating (A) | 165 | 177 | 157 | 165 | 177 | 157 | 165 | 177 | 157 | 165 | 177 | 157 | 165 | 177 | 157
SW | 60027003 | F099D | WARRA | F099D_Warra 33 kV | Time | 12:00 | 18:30 | 8:30 | 12:00 | 18:30 | 8:30 | 12:00 | 18:30 | 8:30 | 12:00 | 18:30 | 8:30 | 12:00 | 18:30 | 8:30
SW | 60027003 | F099D | WARRA | F099D_Warra 33 kV | Voltage at Constrained Conductor | 33.9569 | 33.8901 | 33.4859 | 33.5243 | 33.966 | 33.5536 | 33.5809 | 33.5382 | 33.61 | 33.6277 | 33.5921 | 33.6538 | 33.6644 | 33.6345 | 33.6905
SW | 60300324 | F5530 | 728 MR - South Toowo | 728_Middle Ridge-South Toowoomba 110 kV | % of Rated A | 9.3753 | 9.0265 | 10.0583 | 9.0642 | 8.7299 | 9.7244 | 8.8216 | 8.4981 | 9.4655 | 8.6383 | 8.3243 | 9.3296 | 8.5167 | 8.2094 | 9.1986
SW | 60300324 | F5530 | 728 MR - South Toowo | 728_Middle Ridge-South Toowoomba 110 kV | Limiting Line Name | TR_LINE 12070761_1 | TR_LINE 12070761_1 | TR_LINE 12070761_1 | TR_LINE 12070761_1 | TR_LINE 12070761_1 | TR_LINE 12070761_1 | TR_LINE 12070761_1 | TR_LINE 12070761_1 | TR_LINE 12070761_1 | TR_LINE 12070761_1 | TR_LINE 12070761_1 | TR_LINE 12070761_1 | TR_LINE 12070761_1 | TR_LINE 12070761_1 | TR_LINE 12070761_1
SW | 60300324 | F5530 | 728 MR - South Toowo | 728_Middle Ridge-South Toowoomba 110 kV | Loading (A) | 96.4716 | 95.8616 | 95.856 | 93.2711 | 92.7119 | 92.6733 | 90.7747 | 90.2501 | 90.2067 | 88.8878 | 88.4039 | 88.9115 | 87.6373 | 87.1835 | 87.6622
SW | 60300324 | F5530 | 728 MR - South Toowo | 728_Middle Ridge-South Toowoomba 110 kV | Loading (MVA) | 19.1176 | 19.1979 | 19.1951 | 18.4791 | 18.5636 | 18.5461 | 17.981 | 18.0664 | 18.0478 | 17.5999 | 17.692 | 17.6094 | 17.3451 | 17.443 | 17.3549
SW | 60300324 | F5530 | 728 MR - South Toowo | 728_Middle Ridge-South Toowoomba 110 kV | Loading (MW) | 8.5758 | 8.5783 | 8.5782 | 6.901 | 6.9034 | 6.9033 | 5.314 | 5.3164 | 5.3163 | 3.7946 | 3.7972 | 3.7947 | 2.4221 | 2.4247 | 2.4222
SW | 60300324 | F5530 | 728 MR - South Toowo | 728_Middle Ridge-South Toowoomba 110 kV | Power Factor | 0.44858 | 0.44683 | 0.4469 | 0.37345 | 0.37188 | 0.37222 | 0.29553 | 0.29427 | 0.29457 | 0.2156 | 0.21462 | 0.21549 | 0.13964 | 0.13901 | 0.13957
SW | 60300324 | F5530 | 728 MR - South Toowo | 728_Middle Ridge-South Toowoomba 110 kV | Rating (A) | 1029 | 1062 | 953 | 1029 | 1062 | 953 | 1029 | 1062 | 953 | 1029 | 1062 | 953 | 1029 | 1062 | 953
SW | 60300324 | F5530 | 728 MR - South Toowo | 728_Middle Ridge-South Toowoomba 110 kV | Time | 12:00 | 17:00 | 7:00 | 11:00 | 17:00 | 7:00 | 15:30 | 17:00 | 7:00 | 15:30 | 17:00 | 8:30 | 15:30 | 17:00 | 8:30
SW | 60300324 | F5530 | 728 MR - South Toowo | 728_Middle Ridge-South Toowoomba 110 kV | Voltage at Constrained Conductor | 114.4126 | 115.624 | 115.6141 | 114.3864 | 115.6022 | 115.5411 | 114.3637 | 115.5746 | 115.5117 | 114.3158 | 115.5436 | 114.3475 | 114.2688 | 115.5117 | 114.3008
SW | 60300325 | F5555 | 734 MR - Yarranlea | F5555_734(Middle Ridge-Yarranlea) 110 kV | % of Rated A | 114.1003 | 53.0335 | 127.3329 | 115.2581 | 54.1815 | 128.68 | 116.3124 | 55.2196 | 129.905 | 117.2762 | 56.1655 | 131.0525 | 120.0494 | 56.9581 | 131.9938
SW | 60300325 | F5555 | 734 MR - Yarranlea | F5555_734(Middle Ridge-Yarranlea) 110 kV | Limiting Line Name | TR_LINE 25640_1 | TR_LINE 25640_1 | TR_LINE 25640_1 | TR_LINE 25640_1 | TR_LINE 25640_1 | TR_LINE 25640_1 | TR_LINE 25640_1 | TR_LINE 25640_1 | TR_LINE 25640_1 | TR_LINE 25640_1 | TR_LINE 25640_1 | TR_LINE 25640_1 | TR_LINE 25640_1 | TR_LINE 25640_1 | TR_LINE 25640_1
SW | 60300325 | F5555 | 734 MR - Yarranlea | F5555_734(Middle Ridge-Yarranlea) 110 kV | Loading (A) | 327.4679 | 151.6757 | 314.5123 | 330.7907 | 154.9592 | 317.8395 | 333.8165 | 157.928 | 320.8654 | 336.5826 | 160.6333 | 323.6996 | 344.5417 | 162.9001 | 326.0248
SW | 60300325 | F5555 | 734 MR - Yarranlea | F5555_734(Middle Ridge-Yarranlea) 110 kV | Loading (MVA) | 65.9812 | 30.1937 | 63.3358 | 66.6595 | 30.8562 | 64.0153 | 67.2753 | 31.4546 | 64.6312 | 67.8364 | 31.9993 | 65.2092 | 69.6859 | 32.455 | 65.6795
SW | 60300325 | F5555 | 734 MR - Yarranlea | F5555_734(Middle Ridge-Yarranlea) 110 kV | Loading (MW) | 57.5364 | 21.7306 | 55.0151 | 58.2354 | 22.4314 | 55.7144 | 58.8765 | 23.074 | 56.3558 | 59.4667 | 23.6656 | 56.9461 | 59.9465 | 24.1683 | 57.448
SW | 60300325 | F5555 | 734 MR - Yarranlea | F5555_734(Middle Ridge-Yarranlea) 110 kV | Power Factor | 0.87201 | 0.71971 | 0.86863 | 0.87362 | 0.72696 | 0.87033 | 0.87516 | 0.73357 | 0.87196 | 0.87662 | 0.73957 | 0.87328 | 0.86024 | 0.74467 | 0.87467
SW | 60300325 | F5555 | 734 MR - Yarranlea | F5555_734(Middle Ridge-Yarranlea) 110 kV | Rating (A) | 287 | 286 | 247 | 287 | 286 | 247 | 287 | 286 | 247 | 287 | 286 | 247 | 287 | 286 | 247
SW | 60300325 | F5555 | 734 MR - Yarranlea | F5555_734(Middle Ridge-Yarranlea) 110 kV | Time | 9:00 | 17:00 | 8:30 | 9:00 | 17:00 | 8:30 | 9:00 | 17:00 | 8:30 | 9:00 | 17:00 | 8:30 | 9:00 | 17:00 | 8:30
SW | 60300325 | F5555 | 734 MR - Yarranlea | F5555_734(Middle Ridge-Yarranlea) 110 kV | Voltage at Constrained Conductor | 116.3298 | 114.9315 | 116.2655 | 116.3451 | 114.9648 | 116.2827 | 116.3555 | 114.9912 | 116.2945 | 116.3618 | 115.0122 | 116.3071 | 116.773 | 115.0271 | 116.3103
SW | 60300326 | F5560 | 735 MR - Warwick | F5560_735(Middle Ridge-Warwick) 110 kV | % of Rated A | 55.2539 | 40.493 | 49.2531 | 57.6386 | 42.3915 | 51.3643 | 59.8015 | 44.1131 | 53.2778 | 61.8116 | 45.7124 | 55.0517 | 63.5758 | 47.1184 | 56.6136
SW | 60300326 | F5560 | 735 MR - Warwick | F5560_735(Middle Ridge-Warwick) 110 kV | Limiting Line Name | TR_LINE 94897_1 | TR_LINE 94897_1 | TR_LINE 25701_1 | TR_LINE 94897_1 | TR_LINE 94897_1 | TR_LINE 25701_1 | TR_LINE 94897_1 | TR_LINE 94897_1 | TR_LINE 25701_1 | TR_LINE 94897_1 | TR_LINE 94897_1 | TR_LINE 25701_1 | TR_LINE 94897_1 | TR_LINE 94897_1 | TR_LINE 25701_1
SW | 60300326 | F5560 | 735 MR - Warwick | F5560_735(Middle Ridge-Warwick) 110 kV | Loading (A) | 142.0024 | 129.5777 | 144.804 | 148.1313 | 135.653 | 151.0111 | 153.6899 | 141.1619 | 156.6367 | 158.8558 | 146.2796 | 161.852 | 163.3899 | 150.7789 | 166.444
SW | 60300326 | F5560 | 735 MR - Warwick | F5560_735(Middle Ridge-Warwick) 110 kV | Loading (MVA) | 28.155 | 25.9638 | 29.4659 | 29.3591 | 27.1761 | 30.7362 | 30.4485 | 28.273 | 31.8857 | 31.4586 | 29.2902 | 32.9521 | 32.3453 | 30.1828 | 33.8875
SW | 60300326 | F5560 | 735 MR - Warwick | F5560_735(Middle Ridge-Warwick) 110 kV | Loading (MW) | 27.4837 | 25.3224 | 28.6564 | 28.5929 | 26.4393 | 29.8697 | 29.5923 | 27.4458 | 30.9673 | 30.5153 | 28.3756 | 31.9827 | 31.3212 | 29.1888 | 32.8754
SW | 60300326 | F5560 | 735 MR - Warwick | F5560_735(Middle Ridge-Warwick) 110 kV | Power Factor | 0.97616 | 0.9753 | 0.97253 | 0.9739 | 0.97289 | 0.97181 | 0.97188 | 0.97074 | 0.9712 | 0.97002 | 0.96878 | 0.97058 | 0.96834 | 0.96707 | 0.97013
SW | 60300326 | F5560 | 735 MR - Warwick | F5560_735(Middle Ridge-Warwick) 110 kV | Rating (A) | 257 | 320 | 294 | 257 | 320 | 294 | 257 | 320 | 294 | 257 | 320 | 294 | 257 | 320 | 294
SW | 60300326 | F5560 | 735 MR - Warwick | F5560_735(Middle Ridge-Warwick) 110 kV | Time | 9:00 | 17:00 | 8:30 | 9:00 | 17:00 | 8:30 | 9:00 | 17:00 | 8:30 | 9:00 | 17:00 | 8:30 | 13:30 | 17:00 | 8:30
SW | 60300326 | F5560 | 735 MR - Warwick | F5560_735(Middle Ridge-Warwick) 110 kV | Voltage at Constrained Conductor | 114.472 | 115.6852 | 117.4841 | 114.4287 | 115.6636 | 117.5117 | 114.3825 | 115.6362 | 117.528 | 114.334 | 115.6053 | 117.5453 | 114.2945 | 115.5735 | 117.5469
SW | 60306799 | F3095 | Highfields | F3095_Highfields 33 kV | % of Rated A | 29.3736 | 20.9201 | 21.4616 | 27.9122 | 19.8702 | 20.3706 | 25.8366 | 18.3886 | 18.8491 | 23.4834 | 16.7109 | 17.1293 | 21.337 | 15.1813 | 15.5612
SW | 60306799 | F3095 | Highfields | F3095_Highfields 33 kV | Limiting Line Name | TR_LINE 194642_1 | TR_LINE 194642_1 | TR_LINE 194642_1 | TR_LINE 194642_1 | TR_LINE 194642_1 | TR_LINE 194642_1 | TR_LINE 194642_1 | TR_LINE 194642_1 | TR_LINE 194642_1 | TR_LINE 194642_1 | TR_LINE 194642_1 | TR_LINE 194642_1 | TR_LINE 194642_1 | TR_LINE 194642_1 | TR_LINE 194642_1
SW | 60306799 | F3095 | Highfields | F3095_Highfields 33 kV | Loading (A) | 49.6389 | 50.2059 | 50.2178 | 47.169 | 47.6859 | 47.6645 | 43.661 | 44.1299 | 44.1041 | 39.6839 | 40.1031 | 40.0796 | 36.0563 | 36.4319 | 36.41
SW | 60306799 | F3095 | Highfields | F3095_Highfields 33 kV | Loading (MVA) | 2.9151 | 2.9179 | 2.9172 | 2.7696 | 2.7717 | 2.7712 | 2.5634 | 2.5654 | 2.565 | 2.3298 | 2.3318 | 2.3314 | 2.1169 | 2.1187 | 2.1183
SW | 60306799 | F3095 | Highfields | F3095_Highfields 33 kV | Loading (MW) | 2.9085 | 2.9109 | 2.9101 | 2.7624 | 2.7642 | 2.7637 | 2.5556 | 2.5573 | 2.557 | 2.3219 | 2.3234 | 2.3231 | 2.1085 | 2.1099 | 2.1095
SW | 60306799 | F3095 | Highfields | F3095_Highfields 33 kV | Power Factor | 0.99773 | 0.99758 | 0.99758 | 0.9974 | 0.99728 | 0.99729 | 0.99698 | 0.99684 | 0.99686 | 0.99658 | 0.99641 | 0.99642 | 0.99604 | 0.99585 | 0.99587
SW | 60306799 | F3095 | Highfields | F3095_Highfields 33 kV | Rating (A) | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234
SW | 60306799 | F3095 | Highfields | F3095_Highfields 33 kV | Time | 9:00 | 18:30 | 5:30 | 9:00 | 17:30 | 5:30 | 9:00 | 17:30 | 6:30 | 9:00 | 17:30 | 6:30 | 14:30 | 17:30 | 6:30
SW | 60306799 | F3095 | Highfields | F3095_Highfields 33 kV | Voltage at Constrained Conductor | 33.9059 | 33.555 | 33.5385 | 33.8998 | 33.5583 | 33.5671 | 33.8967 | 33.5633 | 33.5778 | 33.8961 | 33.5702 | 33.5843 | 33.8962 | 33.5751 | 33.5891
SW | 60306800 | F3815 | North Street No 1 | F3815 North Street No 1 33 kV | % of Rated A | 1.3266 | 0.98993 | 1.0384 | 1.3262 | 0.99013 | 1.0381 | 1.3259 | 0.99024 | 1.0379 | 1.3255 | 0.99033 | 1.0414 | 1.3266 | 0.99035 | 1.0412
SW | 60306800 | F3815 | North Street No 1 | F3815 North Street No 1 33 kV | Limiting Line Name | TR_LINE 181524_1 | TR_LINE 181524_1 | TR_LINE 181524_1 | TR_LINE 181524_1 | TR_LINE 181524_1 | TR_LINE 181524_1 | TR_LINE 181524_1 | TR_LINE 181524_1 | TR_LINE 181524_1 | TR_LINE 181524_1 | TR_LINE 181524_1 | TR_LINE 181524_1 | TR_LINE 181524_1 | TR_LINE 181524_1 | TR_LINE 181524_1
SW | 60306800 | F3815 | North Street No 1 | F3815 North Street No 1 33 kV | Loading (A) | 2.348 | 2.3362 | 2.3468 | 2.3474 | 2.3367 | 2.3462 | 2.3468 | 2.337 | 2.3455 | 2.3462 | 2.3372 | 2.3537 | 2.3481 | 2.3372 | 2.3531
SW | 60306800 | F3815 | North Street No 1 | F3815 North Street No 1 33 kV | Loading (MVA) | 0.13956 | 0.13817 | 0.13942 | 0.1395 | 0.13822 | 0.13935 | 0.13942 | 0.13826 | 0.13927 | 0.13935 | 0.13828 | 0.14024 | 0.13958 | 0.13829 | 0.14017
SW | 60306800 | F3815 | North Street No 1 | F3815 North Street No 1 33 kV | Loading (MW) | 0.00044558 | 0.00044113 | 0.00044513 | 0.00044537 | 0.00044131 | 0.0004449 | 0.00044512 | 0.00044141 | 0.00044465 | 0.00044488 | 0.00044148 | 0.00044773 | 0.00044564 | 0.0004415 | 0.00044751
SW | 60306800 | F3815 | North Street No 1 | F3815 North Street No 1 33 kV | Power Factor | 0.0031927 | 0.0031927 | 0.0031927 | 0.0031927 | 0.0031927 | 0.0031927 | 0.0031927 | 0.0031927 | 0.0031927 | 0.0031927 | 0.0031927 | 0.0031927 | 0.0031927 | 0.0031927 | 0.0031927
SW | 60306800 | F3815 | North Street No 1 | F3815 North Street No 1 33 kV | Rating (A) | 177 | 236 | 226 | 177 | 236 | 226 | 177 | 236 | 226 | 177 | 236 | 226 | 177 | 236 | 226
SW | 60306800 | F3815 | North Street No 1 | F3815 North Street No 1 33 kV | Time | 16:30 | 21:00 | 7:30 | 16:30 | 21:00 | 7:30 | 16:30 | 21:00 | 7:30 | 16:30 | 21:00 | 7:00 | 9:00 | 21:00 | 7:00
SW | 60306800 | F3815 | North Street No 1 | F3815 North Street No 1 33 kV | Voltage at Constrained Conductor | 34.3174 | 34.1454 | 34.3 | 34.3091 | 34.1522 | 34.2912 | 34.2997 | 34.1561 | 34.2815 | 34.2905 | 34.1591 | 34.4001 | 34.3194 | 34.16 | 34.3915
SW | 60306801 | F3910 | Perseverence Creek 1 | F3910_Perseverence Creek 1 33 kV | % of Rated A | 47.0489 | 33.5178 | 34.3788 | 47.0306 | 33.4847 | 34.3244 | 48.0704 | 34.2158 | 35.0707 | 48.0235 | 34.1736 | 35.028 | 47.9826 | 34.1368 | 34.9904
SW | 60306801 | F3910 | Perseverence Creek 1 | F3910_Perseverence Creek 1 33 kV | Limiting Line Name | TR_LINE 183865_2 | TR_LINE 183865_2 | TR_LINE 183865_2 | TR_LINE 183865_2 | TR_LINE 183865_2 | TR_LINE 183865_2 | TR_LINE 183865_2 | TR_LINE 183865_2 | TR_LINE 183865_2 | TR_LINE 183865_2 | TR_LINE 183865_2 | TR_LINE 183865_2 | TR_LINE 183865_2 | TR_LINE 183865_2 | TR_LINE 183865_2
SW | 60306801 | F3910 | Perseverence Creek 1 | F3910_Perseverence Creek 1 33 kV | Loading (A) | 79.5098 | 80.4397 | 80.4435 | 79.4788 | 80.3603 | 80.3162 | 81.236 | 82.1148 | 82.0625 | 81.1567 | 82.0137 | 81.9625 | 81.0875 | 81.9254 | 81.8745
SW | 60306801 | F3910 | Perseverence Creek 1 | F3910_Perseverence Creek 1 33 kV | Loading (MVA) | 4.5362 | 4.5383 | 4.5362 | 4.536 | 4.5372 | 4.536 | 4.6383 | 4.6395 | 4.6387 | 4.6382 | 4.6394 | 4.6386 | 4.6384 | 4.6393 | 4.6385
SW | 60306801 | F3910 | Perseverence Creek 1 | F3910_Perseverence Creek 1 33 kV | Loading (MW) | 4.5326 | 4.5346 | 4.5325 | 4.5324 | 4.5336 | 4.5324 | 4.6343 | 4.6355 | 4.6347 | 4.6342 | 4.6354 | 4.6346 | 4.6344 | 4.6353 | 4.6345
SW | 60306801 | F3910 | Perseverence Creek 1 | F3910_Perseverence Creek 1 33 kV | Power Factor | 0.9992 | 0.99919 | 0.99919 | 0.9992 | 0.99919 | 0.9992 | 0.99914 | 0.99913 | 0.99914 | 0.99914 | 0.99914 | 0.99914 | 0.99915 | 0.99914 | 0.99915
SW | 60306801 | F3910 | Perseverence Creek 1 | F3910_Perseverence Creek 1 33 kV | Rating (A) | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234
SW | 60306801 | F3910 | Perseverence Creek 1 | F3910_Perseverence Creek 1 33 kV | Time | 10:00 | 18:30 | 5:30 | 9:00 | 17:30 | 5:30 | 9:00 | 17:30 | 6:30 | 9:00 | 17:30 | 6:30 | 14:30 | 17:30 | 6:30
SW | 60306801 | F3910 | Perseverence Creek 1 | F3910_Perseverence Creek 1 33 kV | Voltage at Constrained Conductor | 32.9391 | 32.573 | 32.5564 | 32.9506 | 32.5978 | 32.6071 | 32.9646 | 32.6204 | 32.6355 | 32.9963 | 32.6599 | 32.6746 | 33.0255 | 32.6944 | 32.7091
SW | 60306802 | F7233 | 7233 MR - Torrington | 7233_Middle Ridge-Torrington 110 kV | % of Rated A | 2.0816 | 1.878 | 2.1401 | 1.5848 | 1.4331 | 1.6293 | 2.4731 | 2.2297 | 2.5424 | 3.6983 | 3.3326 | 3.8005 | 4.8869 | 4.4025 | 5.0214
SW | 60306802 | F7233 | 7233 MR - Torrington | 7233_Middle Ridge-Torrington 110 kV | Limiting Line Name | TR_LINE 27024_1 | TR_LINE 27024_1 | TR_LINE 27024_1 | TR_LINE 27024_1 | TR_LINE 27024_1 | TR_LINE 27024_1 | TR_LINE 27024_1 | TR_LINE 27024_1 | TR_LINE 27024_1 | TR_LINE 27024_1 | TR_LINE 27024_1 | TR_LINE 27024_1 | TR_LINE 27024_1 | TR_LINE 27024_1 | TR_LINE 27024_1
SW | 60306802 | F7233 | 7233 MR - Torrington | 7233_Middle Ridge-Torrington 110 kV | Loading (A) | 18.2765 | 18.1036 | 18.2765 | 13.9145 | 13.8153 | 13.9146 | 21.7137 | 21.4945 | 21.7118 | 32.4714 | 32.1263 | 32.4559 | 42.9067 | 42.4405 | 42.8824
SW | 60306802 | F7233 | 7233 MR - Torrington | 7233_Middle Ridge-Torrington 110 kV | Loading (MVA) | 3.6273 | 3.6369 | 3.6274 | 2.7607 | 2.7758 | 2.7607 | 4.2959 | 4.2997 | 4.2984 | 6.4214 | 6.4247 | 6.4234 | 8.4819 | 8.4849 | 8.4833
SW | 60306802 | F7233 | 7233 MR - Torrington | 7233_Middle Ridge-Torrington 110 kV | Loading (MW) | 2.4213 | 2.4216 | 2.4213 | 0.66964 | 0.6694 | 0.66964 | 3.435 | 3.4349 | 3.435 | 5.934 | 5.934 | 5.9341 | 8.1636 | 8.1637 | 8.1637
SW | 60306802 | F7233 | 7233 MR - Torrington | 7233_Middle Ridge-Torrington 110 kV | Power Factor | 0.66752 | 0.66585 | 0.66749 | 0.24257 | 0.24115 | 0.24256 | 0.7996 | 0.79885 | 0.79914 | 0.9241 | 0.92362 | 0.92382 | 0.96248 | 0.96215 | 0.96233
SW | 60306802 | F7233 | 7233 MR - Torrington | 7233_Middle Ridge-Torrington 110 kV | Rating (A) | 878 | 964 | 854 | 878 | 964 | 854 | 878 | 964 | 854 | 878 | 964 | 854 | 878 | 964 | 854
SW | 60306802 | F7233 | 7233 MR - Torrington | 7233_Middle Ridge-Torrington 110 kV | Time | 16:00 | 21:00 | 8:00 | 16:00 | 21:00 | 8:00 | 9:00 | 17:00 | 8:30 | 9:00 | 17:00 | 8:30 | 14:30 | 17:00 | 8:30
SW | 60306802 | F7233 | 7233 MR - Torrington | 7233_Middle Ridge-Torrington 110 kV | Voltage at Constrained Conductor | 114.5871 | 115.9846 | 114.5886 | 114.5465 | 116.0034 | 114.5471 | 114.2247 | 115.4929 | 114.3007 | 114.1742 | 115.46 | 114.2634 | 114.1315 | 115.4265 | 114.2152
SW | 60306803 | F5535 | 730 MR - South Toowo | 730_Middle Ridge-South Toowoomba 110 kV | % of Rated A | 9.3757 | 9.0269 | 10.0588 | 9.0649 | 8.7306 | 9.7251 | 8.8225 | 8.4989 | 9.4664 | 8.6391 | 8.3251 | 9.3305 | 8.5175 | 8.2101 | 9.1994
SW | 60306803 | F5535 | 730 MR - South Toowo | 730_Middle Ridge-South Toowoomba 110 kV | Limiting Line Name | TR_LINE 12070768_1 | TR_LINE 12070768_1 | TR_LINE 12070768_1 | TR_LINE 12070768_1 | TR_LINE 12070768_1 | TR_LINE 12070768_1 | TR_LINE 12070768_1 | TR_LINE 12070768_1 | TR_LINE 12070768_1 | TR_LINE 12070768_1 | TR_LINE 12070768_1 | TR_LINE 12070768_1 | TR_LINE 12070768_1 | TR_LINE 12070768_1 | TR_LINE 12070768_1
SW | 60306803 | F5535 | 730 MR - South Toowo | 730_Middle Ridge-South Toowoomba 110 kV | Loading (A) | 96.4762 | 95.8661 | 95.8605 | 93.2782 | 92.7189 | 92.6804 | 90.7831 | 90.2584 | 90.215 | 88.8964 | 88.4123 | 88.92 | 87.645 | 87.1911 | 87.6699
SW | 60306803 | F5535 | 730 MR - South Toowo | 730_Middle Ridge-South Toowoomba 110 kV | Loading (MVA) | 19.1186 | 19.1988 | 19.1961 | 18.4806 | 18.565 | 18.5475 | 17.9827 | 18.0681 | 18.0496 | 17.6016 | 17.6938 | 17.6112 | 17.3467 | 17.4445 | 17.3565
SW | 60306803 | F5535 | 730 MR - South Toowo | 730_Middle Ridge-South Toowoomba 110 kV | Loading (MW) | 8.578 | 8.5804 | 8.5804 | 6.9046 | 6.9071 | 6.9069 | 5.319 | 5.3215 | 5.3214 | 3.801 | 3.8036 | 3.8011 | 2.4298 | 2.4324 | 2.4299
SW | 60306803 | F5535 | 730 MR - South Toowo | 730_Middle Ridge-South Toowoomba 110 kV | Power Factor | 0.44867 | 0.44692 | 0.44699 | 0.37361 | 0.37205 | 0.37239 | 0.29579 | 0.29453 | 0.29482 | 0.21595 | 0.21497 | 0.21583 | 0.14007 | 0.13944 | 0.14
SW | 60306803 | F5535 | 730 MR - South Toowo | 730_Middle Ridge-South Toowoomba 110 kV | Rating (A) | 1029 | 1062 | 953 | 1029 | 1062 | 953 | 1029 | 1062 | 953 | 1029 | 1062 | 953 | 1029 | 1062 | 953
SW | 60306803 | F5535 | 730 MR - South Toowo | 730_Middle Ridge-South Toowoomba 110 kV | Time | 12:00 | 17:00 | 7:00 | 11:00 | 17:00 | 7:00 | 15:30 | 17:00 | 7:00 | 15:30 | 17:00 | 8:30 | 15:30 | 17:00 | 8:30
SW | 60306803 | F5535 | 730 MR - South Toowo | 730_Middle Ridge-South Toowoomba 110 kV | Voltage at Constrained Conductor | 114.4128 | 115.6243 | 115.6143 | 114.3866 | 115.6024 | 115.5413 | 114.364 | 115.5749 | 115.512 | 114.3161 | 115.5439 | 114.3477 | 114.2691 | 115.512 | 114.3011
SW | 60306804 | F5550 | 733 MR - Yarranlea | F5550_733(Middle Ridge-Yarranlea) 110 kV | % of Rated A | 114.2115 | 53.0742 | 127.4565 | 115.3705 | 54.2236 | 128.805 | 116.4258 | 55.2629 | 130.0313 | 117.3907 | 56.2098 | 131.18 | 120.1662 | 57.0033 | 132.1224
SW | 60306804 | F5550 | 733 MR - Yarranlea | F5550_733(Middle Ridge-Yarranlea) 110 kV | Limiting Line Name | TR_LINE 224268_1 | TR_LINE 224268_1 | TR_LINE 224268_1 | TR_LINE 224268_1 | TR_LINE 224268_1 | TR_LINE 224268_1 | TR_LINE 224268_1 | TR_LINE 224268_1 | TR_LINE 224268_1 | TR_LINE 224268_1 | TR_LINE 224268_1 | TR_LINE 224268_1 | TR_LINE 224268_1 | TR_LINE 224268_1 | TR_LINE 224268_1
SW | 60306804 | F5550 | 733 MR - Yarranlea | F5550_733(Middle Ridge-Yarranlea) 110 kV | Loading (A) | 327.787 | 151.7924 | 314.8175 | 331.1132 | 155.0796 | 318.1483 | 334.1422 | 158.0518 | 321.1773 | 336.9112 | 160.7601 | 324.0146 | 344.877 | 163.0295 | 326.3422
SW | 60306804 | F5550 | 733 MR - Yarranlea | F5550_733(Middle Ridge-Yarranlea) 110 kV | Loading (MVA) | 66.0453 | 30.2169 | 63.3971 | 66.7243 | 30.8802 | 64.0773 | 67.3407 | 31.4793 | 64.6939 | 67.9024 | 32.0245 | 65.2725 | 69.7535 | 32.4808 | 65.7432
SW | 60306804 | F5550 | 733 MR - Yarranlea | F5550_733(Middle Ridge-Yarranlea) 110 kV | Loading (MW) | 57.682 | 21.808 | 55.1557 | 58.3821 | 22.5101 | 55.8561 | 59.0241 | 23.1539 | 56.4985 | 59.6152 | 23.7465 | 57.0897 | 60.103 | 24.25 | 57.5923
SW | 60306804 | F5550 | 733 MR - Yarranlea | F5550_733(Middle Ridge-Yarranlea) 110 kV | Power Factor | 0.87337 | 0.72172 | 0.87 | 0.87498 | 0.72895 | 0.8717 | 0.8765 | 0.73553 | 0.87332 | 0.87795 | 0.74151 | 0.87464 | 0.86165 | 0.74659 | 0.87602
SW | 60306804 | F5550 | 733 MR - Yarranlea | F5550_733(Middle Ridge-Yarranlea) 110 kV | Rating (A) | 287 | 286 | 247 | 287 | 286 | 247 | 287 | 286 | 247 | 287 | 286 | 247 | 287 | 286 | 247
SW | 60306804 | F5550 | 733 MR - Yarranlea | F5550_733(Middle Ridge-Yarranlea) 110 kV | Time | 9:00 | 17:00 | 8:30 | 9:00 | 17:00 | 8:30 | 9:00 | 17:00 | 8:30 | 9:00 | 17:00 | 8:30 | 9:00 | 17:00 | 8:30
SW | 60306804 | F5550 | 733 MR - Yarranlea | F5550_733(Middle Ridge-Yarranlea) 110 kV | Voltage at Constrained Conductor | 116.3294 | 114.9315 | 116.2652 | 116.3448 | 114.9648 | 116.2823 | 116.3552 | 114.9912 | 116.2941 | 116.3614 | 115.0122 | 116.3067 | 116.7726 | 115.0271 | 116.31
SW | 60306805 | F5565 | 736 MR - Warwick | F5565_736(Middle Ridge-Warwick) 110 kV | % of Rated A | 22.9351 | 20.5282 | 25.5333 | 23.9137 | 21.4784 | 26.6228 | 24.801 | 22.3399 | 27.6109 | 25.6256 | 23.1401 | 28.5267 | 26.3494 | 23.8436 | 29.334
SW | 60306805 | F5565 | 736 MR - Warwick | F5565_736(Middle Ridge-Warwick) 110 kV | Limiting Line Name | TR_LINE 141691_1 | TR_LINE 141691_1 | TR_LINE 141691_1 | TR_LINE 141691_1 | TR_LINE 141691_1 | TR_LINE 141691_1 | TR_LINE 141691_1 | TR_LINE 141691_1 | TR_LINE 141691_1 | TR_LINE 141691_1 | TR_LINE 141691_1 | TR_LINE 141691_1 | TR_LINE 141691_1 | TR_LINE 141691_1 | TR_LINE 141691_1
SW | 60306805 | F5565 | 736 MR - Warwick | F5565_736(Middle Ridge-Warwick) 110 kV | Loading (A) | 174.9528 | 159.8737 | 174.862 | 182.4224 | 167.2794 | 182.3283 | 189.196 | 173.9935 | 189.0993 | 195.4901 | 180.2299 | 195.3753 | 201.0145 | 185.7121 | 200.9076
SW | 60306805 | F5565 | 736 MR - Warwick | F5565_736(Middle Ridge-Warwick) 110 kV | Loading (MVA) | 34.7627 | 32.0958 | 34.766 | 36.2341 | 33.5772 | 36.2383 | 37.5652 | 34.9174 | 37.5701 | 38.7992 | 36.1599 | 38.8056 | 39.8825 | 37.2502 | 39.8888
SW | 60306805 | F5565 | 736 MR - Warwick | F5565_736(Middle Ridge-Warwick) 110 kV | Loading (MW) | 34.5144 | 31.8872 | 34.5262 | 36.0141 | 33.3946 | 36.0262 | 37.3692 | 34.7566 | 37.3815 | 38.6241 | 36.018 | 38.6386 | 39.7254 | 37.1238 | 39.7387
SW | 60306805 | F5565 | 736 MR - Warwick | F5565_736(Middle Ridge-Warwick) 110 kV | Power Factor | 0.99286 | 0.9935 | 0.9931 | 0.99393 | 0.99456 | 0.99415 | 0.99478 | 0.9954 | 0.99498 | 0.99549 | 0.99608 | 0.9957 | 0.99606 | 0.99661 | 0.99624
SW | 60306805 | F5565 | 736 MR - Warwick | F5565_736(Middle Ridge-Warwick) 110 kV | Rating (A) | 763 | 779 | 685 | 763 | 779 | 685 | 763 | 779 | 685 | 763 | 779 | 685 | 763 | 779 | 685
SW | 60306805 | F5565 | 736 MR - Warwick | F5565_736(Middle Ridge-Warwick) 110 kV | Time | 9:00 | 17:00 | 8:30 | 9:00 | 17:00 | 8:30 | 9:00 | 17:00 | 8:30 | 9:00 | 17:00 | 8:30 | 13:30 | 17:00 | 8:30
SW | 60306805 | F5565 | 736 MR - Warwick | F5565_736(Middle Ridge-Warwick) 110 kV | Voltage at Constrained Conductor | 114.718 | 115.9072 | 114.7886 | 114.6777 | 115.8886 | 114.7501 | 114.634 | 115.8638 | 114.7074 | 114.5876 | 115.8351 | 114.6738 | 114.5497 | 115.8051 | 114.6289
SW | 60306930 | F3867 | PAMPAS | F3867_Pampas 33 kV | % of Rated A | 3.5472 | 3.9322 | 4.045 | 0.70076 | 0.70946 | 0.80765 | 3.3656 | 3.6981 | 3.8043 | 6.4556 | 7.1011 | 7.3062 | 9.065 | 9.9694 | 10.2593
SW | 60306930 | F3867 | PAMPAS | F3867_Pampas 33 kV | Limiting Line Name | TR_CABLE 106_1 | TR_CABLE 106_1 | TR_LINE 23248_1 | TR_LINE 177041_1 | TR_LINE 177041_1 | TR_LINE 177041_1 | TR_CABLE 106_1 | TR_CABLE 106_1 | TR_LINE 23248_1 | TR_CABLE 106_1 | TR_CABLE 106_1 | TR_LINE 23248_1 | TR_CABLE 106_1 | TR_CABLE 106_1 | TR_LINE 23248_1
SW | 60306930 | F3867 | PAMPAS | F3867_Pampas 33 kV | Loading (A) | 10.6417 | 11.7965 | 11.8922 | 3.714 | 3.8524 | 3.8525 | 10.0969 | 11.0944 | 11.1846 | 19.3667 | 21.3034 | 21.4803 | 27.1949 | 29.9082 | 30.1622
SW | 60306930 | F3867 | PAMPAS | F3867_Pampas 33 kV | Loading (MVA) | 0.7119 | 0.71078 | 0.71058 | 0.24998 | 0.26896 | 0.26897 | 0.67783 | 0.67639 | 0.67614 | 1.302 | 1.3009 | 1.3007 | 1.8303 | 1.8288 | 1.8289
SW | 60306930 | F3867 | PAMPAS | F3867_Pampas 33 kV | Loading (MW) | 0.70415 | 0.7042 | 0.70422 | 0.0028831 | 0.0029011 | 0.0029012 | 0.66955 | 0.66946 | 0.66944 | 1.2985 | 1.2981 | 1.298 | 1.8285 | 1.8275 | 1.8276
SW | 60306930 | F3867 | PAMPAS | F3867_Pampas 33 kV | Power Factor | 0.98912 | 0.99074 | 0.99105 | 0.011533 | 0.010787 | 0.010786 | 0.98779 | 0.98975 | 0.99008 | 0.9973 | 0.99782 | 0.99791 | 0.999 | 0.9993 | 0.99928
SW | 60306930 | F3867 | PAMPAS | F3867_Pampas 33 kV | Rating (A) | 300 | 300 | 294 | 530 | 543 | 477 | 300 | 300 | 294 | 300 | 300 | 294 | 300 | 300 | 294
SW | 60306930 | F3867 | PAMPAS | F3867_Pampas 33 kV | Time | 16:30 | 17:30 | 6:30 | 15:30 | 21:00 | 4:00 | 16:30 | 17:30 | 6:30 | 16:30 | 17:30 | 6:30 | 16:30 | 17:30 | 6:30
SW | 60306930 | F3867 | PAMPAS | F3867_Pampas 33 kV | Voltage at Constrained Conductor | 38.623 | 34.7875 | 34.4977 | 38.8606 | 40.308 | 40.3093 | 38.7588 | 35.1993 | 34.9028 | 38.8144 | 35.2575 | 34.9613 | 38.8581 | 35.3031 | 35.0079
SW | 60320796 | F5540 | 7244 TANGKAM - DALBY | F5540_7244 Tangkam-Dalby 110 kV | % of Rated A | 8.5082 | 8.3896 | 9.5363 | 7.4119 | 7.4025 | 8.4693 | 6.7348 | 6.7467 | 7.8893 | 6.3897 | 6.4512 | 7.7096 | 6.3147 | 6.4043 | 7.7833
SW | 60320796 | F5540 | 7244 TANGKAM - DALBY | F5540_7244 Tangkam-Dalby 110 kV | Limiting Line Name | TR_LINE 24297_1 | TR_LINE 24297_1 | TR_LINE 24297_1 | TR_LINE 24297_1 | TR_LINE 24297_1 | TR_LINE 24297_1 | TR_LINE 24297_1 | TR_LINE 24297_1 | TR_LINE 24297_1 | TR_LINE 24297_1 | TR_LINE 24297_1 | TR_LINE 24297_1 | TR_LINE 24297_1 | TR_LINE 24297_1 | TR_LINE 24297_1
SW | 60320796 | F5540 | 7244 TANGKAM - DALBY | F5540_7244 Tangkam-Dalby 110 kV | Loading (A) | 22.4618 | 22.5681 | 22.4103 | 19.5674 | 19.9126 | 19.9028 | 17.7799 | 18.1487 | 18.5398 | 16.8687 | 17.3537 | 18.1176 | 16.6709 | 17.2276 | 18.2908
SW | 60320796 | F5540 | 7244 TANGKAM - DALBY | F5540_7244 Tangkam-Dalby 110 kV | Loading (MVA) | 4.4778 | 4.5514 | 4.4732 | 3.9232 | 4.0165 | 4.0149 | 3.5645 | 3.6612 | 3.7405 | 3.3814 | 3.501 | 3.6555 | 3.3413 | 3.4756 | 3.6905
SW | 60320796 | F5540 | 7244 TANGKAM - DALBY | F5540_7244 Tangkam-Dalby 110 kV | Loading (MW) | 3.1154 | 2.9691 | 3.0393 | 2.0072 | 2.0194 | 1.7798 | 1.1615 | 1.079 | 0.71821 | 0.41206 | 0.32988 | 0.029872 | 0.21218 | 0.29413 | 0.65303
SW | 60320796 | F5540 | 7244 TANGKAM - DALBY | F5540_7244 Tangkam-Dalby 110 kV | Power Factor | 0.69573 | 0.65235 | 0.67945 | 0.51163 | 0.50278 | 0.4433 | 0.32585 | 0.29472 | 0.19201 | 0.12186 | 0.094225 | 0.0081719 | 0.063502 | 0.084627 | 0.17695
SW | 60320796 | F5540 | 7244 TANGKAM - DALBY | F5540_7244 Tangkam-Dalby 110 kV | Rating (A) | 264 | 269 | 235 | 264 | 269 | 235 | 264 | 269 | 235 | 264 | 269 | 235 | 264 | 269 | 235
SW | 60320796 | F5540 | 7244 TANGKAM - DALBY | F5540_7244 Tangkam-Dalby 110 kV | Time | 12:00 | 19:00 | 8:00 | 16:30 | 19:00 | 0:00 | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00
SW | 60320796 | F5540 | 7244 TANGKAM - DALBY | F5540_7244 Tangkam-Dalby 110 kV | Voltage at Constrained Conductor | 115.0972 | 116.4378 | 115.2421 | 115.7574 | 116.4557 | 116.4656 | 115.7461 | 116.4702 | 116.4829 | 115.7322 | 116.4768 | 116.4892 | 115.7169 | 116.4791 | 116.4914
SW | 60320797 | F5545 | 7245 TANGKAM - DALBY | F5545_7245 Tangkam-Dalby 110 kV | % of Rated A | 18.1759 | 12.878 | 13.1573 | 15.7678 | 11.3239 | 11.6396 | 14.2919 | 10.2971 | 10.829 | 13.5535 | 9.845 | 10.5919 | 13.414 | 9.7888 | 10.7161
SW | 60320797 | F5545 | 7245 TANGKAM - DALBY | F5545_7245 Tangkam-Dalby 110 kV | Limiting Line Name | TR_LINE 140801_1 | TR_LINE 140801_1 | TR_LINE 140801_1 | TR_LINE 140801_1 | TR_LINE 140801_1 | TR_LINE 140801_1 | TR_LINE 140801_1 | TR_LINE 140801_1 | TR_LINE 140801_1 | TR_LINE 140801_1 | TR_LINE 140801_1 | TR_LINE 140801_1 | TR_LINE 140801_1 | TR_LINE 140801_1 | TR_LINE 140801_1
SW | 60320797 | F5545 | 7245 TANGKAM - DALBY | F5545_7245 Tangkam-Dalby 110 kV | Loading (A) | 23.0834 | 23.1804 | 23.0253 | 20.0252 | 20.383 | 20.3693 | 18.1507 | 18.5348 | 18.9507 | 17.2129 | 17.721 | 18.5359 | 17.0358 | 17.6198 | 18.7531
SW | 60320797 | F5545 | 7245 TANGKAM - DALBY | F5545_7245 Tangkam-Dalby 110 kV | Loading (MVA) | 4.6018 | 4.6749 | 4.596 | 4.015 | 4.1114 | 4.109 | 3.6388 | 3.7391 | 3.8234 | 3.4504 | 3.5751 | 3.7399 | 3.4144 | 3.5548 | 3.7838
SW | 60320797 | F5545 | 7245 TANGKAM - DALBY | F5545_7245 Tangkam-Dalby 110 kV | Loading (MW) | 3.2882 | 3.1391 | 3.2099 | 2.1319 | 2.1463 | 1.8982 | 1.2473 | 1.1632 | 0.78935 | 0.46325 | 0.37945 | 0.0066134 | 0.19007 | 0.27365 | 0.64561
SW | 60320797 | F5545 | 7245 TANGKAM - DALBY | F5545_7245 Tangkam-Dalby 110 kV | Power Factor | 0.71456 | 0.67148 | 0.69841 | 0.53099 | 0.52203 | 0.46197 | 0.34279 | 0.31111 | 0.20645 | 0.13426 | 0.10614 | 0.0017683 | 0.055665 | 0.076982 | 0.17063
SW | 60320797 | F5545 | 7245 TANGKAM - DALBY | F5545_7245 Tangkam-Dalby 110 kV | Rating (A) | 127 | 180 | 175 | 127 | 180 | 175 | 127 | 180 | 175 | 127 | 180 | 175 | 127 | 180 | 175
SW | 60320797 | F5545 | 7245 TANGKAM - DALBY | F5545_7245 Tangkam-Dalby 110 kV | Time | 12:00 | 19:00 | 8:00 | 16:30 | 19:00 | 0:00 | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00
SW | 60320797 | F5545 | 7245 TANGKAM - DALBY | F5545_7245 Tangkam-Dalby 110 kV | Voltage at Constrained Conductor | 115.0972 | 116.4378 | 115.2421 | 115.7574 | 116.4557 | 116.4656 | 115.7461 | 116.4702 | 116.4829 | 115.7322 | 116.4768 | 116.4892 | 115.7169 | 116.4791 | 116.4914
SW | 60322637 | F3253 | JELLICOE STREET | F3253_Jellicoe Street 33 kV | % of Rated A | 0.97193 | 0.68829 | 0.59511 | 0.97257 | 0.68908 | 0.59561 | 0.97299 | 0.68969 | 0.5961 | 0.97328 | 0.69018 | 0.59652 | 0.97346 | 0.69056 | 0.59685
SW | 60322637 | F3253 | JELLICOE STREET | F3253_Jellicoe Street 33 kV | Limiting Line Name | TR_LINE 23977_2 | TR_LINE 23977_2 | TR_LINE 23977_2 | TR_LINE 23977_2 | TR_LINE 23977_2 | TR_LINE 23977_2 | TR_LINE 23977_2 | TR_LINE 23977_2 | TR_LINE 23977_2 | TR_LINE 23977_2 | TR_LINE 23977_2 | TR_LINE 23977_2 | TR_LINE 23977_2 | TR_LINE 23977_2 | TR_LINE 23977_2
SW | 60322637 | F3253 | JELLICOE STREET | F3253_Jellicoe Street 33 kV | Loading (A) | 2.148 | 2.1475 | 2.1484 | 2.1494 | 2.1499 | 2.1502 | 2.1503 | 2.1518 | 2.1519 | 2.1509 | 2.1534 | 2.1534 | 2.1513 | 2.1546 | 2.1546
SW | 60322637 | F3253 | JELLICOE STREET | F3253_Jellicoe Street 33 kV | Loading (MVA) | 0.12675 | 0.12669 | 0.12679 | 0.12692 | 0.12698 | 0.12701 | 0.12703 | 0.12721 | 0.12721 | 0.1271 | 0.12739 | 0.12739 | 0.12715 | 0.12753 | 0.12753
SW | 60322637 | F3253 | JELLICOE STREET | F3253_Jellicoe Street 33 kV | Loading (MW) | 0.0022452 | 0.0022442 | 0.0022461 | 0.0022482 | 0.0022494 | 0.0022499 | 0.0022502 | 0.0022534 | 0.0022535 | 0.0022515 | 0.0022565 | 0.0022567 | 0.0022523 | 0.002259 | 0.0022592
SW | 60322637 | F3253 | JELLICOE STREET | F3253_Jellicoe Street 33 kV | Power Factor | 0.017714 | 0.017714 | 0.017714 | 0.017714 | 0.017714 | 0.017714 | 0.017714 | 0.017714 | 0.017714 | 0.017714 | 0.017714 | 0.017714 | 0.017714 | 0.017714 | 0.017714
SW | 60322637 | F3253 | JELLICOE STREET | F3253_Jellicoe Street 33 kV | Rating (A) | 221 | 312 | 361 | 221 | 312 | 361 | 221 | 312 | 361 | 221 | 312 | 361 | 221 | 312 | 361
SW | 60322637 | F3253 | JELLICOE STREET | F3253_Jellicoe Street 33 kV | Time | 16:00 | 17:30 | 6:30 | 16:00 | 21:00 | 6:30 | 16:00 | 21:00 | 4:00 | 16:00 | 21:00 | 4:00 | 16:00 | 21:00 | 4:00
SW | 60322637 | F3253 | JELLICOE STREET | F3253_Jellicoe Street 33 kV | Voltage at Constrained Conductor | 34.0685 | 34.0604 | 34.0747 | 34.091 | 34.0997 | 34.1035 | 34.1058 | 34.13 | 34.1312 | 34.1157 | 34.1541 | 34.1553 | 34.1221 | 34.173 | 34.1741
SW | 60327274 | F4132 | SHIRLEY ROAD FEEDER | F4132_Shirley Road 33 kV | % of Rated A | 16.2948 | 10.1735 | 10.1767 | 21.8475 | 13.6145 | 13.6189 | 26.9963 | 16.8096 | 16.8151 | 31.7962 | 19.7937 | 19.8002 | 36.107 | 22.4728 | 22.4807
SW | 60327274 | F4132 | SHIRLEY ROAD FEEDER | F4132_Shirley Road 33 kV | Limiting Line Name | TR_LINE 157941_1 | TR_CABLE 561_1 | TR_CABLE 561_1 | TR_LINE 157941_1 | TR_CABLE 561_1 | TR_CABLE 561_1 | TR_LINE 157941_1 | TR_CABLE 239_1 | TR_CABLE 239_1 | TR_LINE 108727_1 | TR_CABLE 239_1 | TR_CABLE 239_1 | TR_LINE 108727_1 | TR_CABLE 239_1 | TR_CABLE 239_1
SW | 60327274 | F4132 | SHIRLEY ROAD FEEDER | F4132_Shirley Road 33 kV | Loading (A) | 68.4381 | 68.6708 | 68.693 | 91.7597 | 91.8976 | 91.9276 | 113.3845 | 113.4646 | 113.502 | 133.5442 | 133.6076 | 133.6516 | 151.6495 | 151.6915 | 151.7444
SW | 60327274 | F4132 | SHIRLEY ROAD FEEDER | F4132_Shirley Road 33 kV | Loading (MVA) | 4.0115 | 4.02 | 4.0199 | 5.3794 | 5.3813 | 5.3812 | 6.6472 | 6.6534 | 6.6533 | 7.8749 | 7.8356 | 7.8356 | 8.9453 | 8.8963 | 8.8964
SW | 60327274 | F4132 | SHIRLEY ROAD FEEDER | F4132_Shirley Road 33 kV | Loading (MW) | 4.0043 | 4.0001 | 4.0001 | 5.3774 | 5.3725 | 5.3725 | 6.647 | 6.6533 | 6.6533 | 7.8748 | 7.8351 | 7.8351 | 8.9452 | 8.8938 | 8.894
SW | 60327274 | F4132 | SHIRLEY ROAD FEEDER | F4132_Shirley Road 33 kV | Power Factor | 0.9982 | 0.99505 | 0.99506 | 0.99962 | 0.99837 | 0.99837 | 0.99998 | 0.99999 | 0.99999 | 0.99999 | 0.99994 | 0.99994 | 0.99999 | 0.99972 | 0.99973
SW | 60327274 | F4132 | SHIRLEY ROAD FEEDER | F4132_Shirley Road 33 kV | Rating (A) | 420 | 675 | 675 | 420 | 675 | 675 | 420 | 675 | 675 | 420 | 675 | 675 | 420 | 675 | 675
SW | 60327274 | F4132 | SHIRLEY ROAD FEEDER | F4132_Shirley Road 33 kV | Time | 16:30 | 18:00 | 6:00 | 16:30 | 18:00 | 6:00 | 16:30 | 18:00 | 6:00 | 16:30 | 18:00 | 6:00 | 16:30 | 18:00 | 6:00
SW | 60327274 | F4132 | SHIRLEY ROAD FEEDER | F4132_Shirley Road 33 kV | Voltage at Constrained Conductor | 33.8414 | 33.7982 | 33.7868 | 33.8472 | 33.8079 | 33.7966 | 33.8471 | 33.8549 | 33.8436 | 34.0453 | 33.8596 | 33.8483 | 34.056 | 33.8599 | 33.8488
SW | 60330365 | 7235 | Bulli Creek - Waggamba 132 kV | 7235_Bulli Creek - Waggamba 132 kV | % of Rated A | 13.9355 | 13.7435 | 15.7529 | 13.9968 | 13.8038 | 15.8223 | 14.12 | 13.925 | 15.9616 | 14.1818 | 13.9856 | 16.0312 | 14.185 | 13.9851 | 16.0309
SW | 60330365 | 7235 | Bulli Creek - Waggamba 132 kV | 7235_Bulli Creek - Waggamba 132 kV | Limiting Line Name | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1
SW | 60330365 | 7235 | Bulli Creek - Waggamba 132 kV | 7235_Bulli Creek - Waggamba 132 kV | Loading (A) | 90.5806 | 90.5699 | 90.5792 | 90.9794 | 90.9669 | 90.9782 | 91.7802 | 91.7656 | 91.7789 | 92.1814 | 92.165 | 92.1796 | 92.2026 | 92.1615 | 92.1777
SW | 60330365 | 7235 | Bulli Creek - Waggamba 132 kV | 7235_Bulli Creek - Waggamba 132 kV | Loading (MVA) | 21.6801 | 21.6806 | 21.6802 | 21.7762 | 21.7768 | 21.7763 | 21.9677 | 21.9683 | 21.9677 | 22.0639 | 22.0646 | 22.0639 | 22.0629 | 22.0647 | 22.064
SW | 60330365 | 7235 | Bulli Creek - Waggamba 132 kV | 7235_Bulli Creek - Waggamba 132 kV | Loading (MW) | 21.0673 | 21.0672 | 21.0673 | 21.1697 | 21.1696 | 21.1697 | 21.3746 | 21.3745 | 21.3745 | 21.477 | 21.4769 | 21.477 | 21.4771 | 21.4769 | 21.477
SW | 60330365 | 7235 | Bulli Creek - Waggamba 132 kV | 7235_Bulli Creek - Waggamba 132 kV | Power Factor | 0.97173 | 0.97171 | 0.97173 | 0.97215 | 0.97212 | 0.97214 | 0.973 | 0.97297 | 0.973 | 0.9734 | 0.97337 | 0.9734 | 0.97345 | 0.97336 | 0.97339
SW | 60330365 | 7235 | Bulli Creek - Waggamba 132 kV | 7235_Bulli Creek - Waggamba 132 kV | Rating (A) | 650 | 659 | 575 | 650 | 659 | 575 | 650 | 659 | 575 | 650 | 659 | 575 | 650 | 659 | 575
SW | 60330365 | 7235 | Bulli Creek - Waggamba 132 kV | 7235_Bulli Creek - Waggamba 132 kV | Time | 11:00 | 17:00 | 8:30 | 9:00 | 17:00 | 8:30 | 9:00 | 17:00 | 8:30 | 9:00 | 17:00 | 8:30 | 9:00 | 17:00 | 8:30
SW | 60330365 | 7235 | Bulli Creek - Waggamba 132 kV | 7235_Bulli Creek - Waggamba 132 kV | Voltage at Constrained Conductor | 138.1868 | 138.2062 | 138.1893 | 138.1908 | 138.2134 | 138.1929 | 138.1892 | 138.2153 | 138.1915 | 138.1903 | 138.2195 | 138.1936 | 138.1527 | 138.2255 | 138.1969
SW | 60330908 | F7234 | 7234 MR - Torrington | 7234_Middle Ridge-Torrington 110 kV | % of Rated A | 2.1484 | 1.938 | 2.2088 | 1.6301 | 1.4738 | 1.6759 | 2.5542 | 2.3026 | 2.6258 | 3.826 | 3.4474 | 3.9317 | 5.0586 | 4.557 | 5.1978
SW | 60330908 | F7234 | 7234 MR - Torrington | 7234_Middle Ridge-Torrington 110 kV | Limiting Line Name | TR_LINE 27022_1 | TR_LINE 27022_1 | TR_LINE 27022_1 | TR_LINE 27022_1 | TR_LINE 27022_1 | TR_LINE 27022_1 | TR_LINE 27022_1 | TR_LINE 27022_1 | TR_LINE 27022_1 | TR_LINE 27022_1 | TR_LINE 27022_1 | TR_LINE 27022_1 | TR_LINE 27022_1 | TR_LINE 27022_1 | TR_LINE 27022_1
SW | 60330908 | F7234 | 7234 MR - Torrington | 7234_Middle Ridge-Torrington 110 kV | Loading (A) | 18.863 | 18.6828 | 18.863 | 14.3122 | 14.2076 | 14.3123 | 22.426 | 22.1969 | 22.4239 | 33.5926 | 33.2329 | 33.5765 | 44.4148 | 43.9293 | 44.3895
SW | 60330908 | F7234 | 7234 MR - Torrington | 7234_Middle Ridge-Torrington 110 kV | Loading (MVA) | 3.7438 | 3.7532 | 3.7438 | 2.8396 | 2.8546 | 2.8396 | 4.4368 | 4.4403 | 4.4394 | 6.6431 | 6.646 | 6.6451 | 8.78 | 8.7825 | 8.7814
SW | 60330908 | F7234 | 7234 MR - Torrington | 7234_Middle Ridge-Torrington 110 kV | Loading (MW) | 2.5015 | 2.5011 | 2.5014 | 0.7007 | 0.70098 | 0.7007 | 3.5653 | 3.5655 | 3.5653 | 6.1539 | 6.1541 | 6.1539 | 8.4632 | 8.4635 | 8.4633
SW | 60330908 | F7234 | 7234 MR - Torrington | 7234_Middle Ridge-Torrington 110 kV | Power Factor | 0.66817 | 0.66639 | 0.66814 | 0.24676 | 0.24556 | 0.24676 | 0.80357 | 0.80301 | 0.80311 | 0.92635 | 0.92599 | 0.92608 | 0.96392 | 0.96367 | 0.96377
SW | 60330908 | F7234 | 7234 MR - Torrington | 7234_Middle Ridge-Torrington 110 kV | Rating (A) | 878 | 964 | 854 | 878 | 964 | 854 | 878 | 964 | 854 | 878 | 964 | 854 | 878 | 964 | 854
SW | 60330908 | F7234 | 7234 MR - Torrington | 7234_Middle Ridge-Torrington 110 kV | Time | 16:00 | 21:00 | 8:00 | 16:00 | 21:00 | 8:00 | 9:00 | 17:00 | 8:30 | 9:00 | 17:00 | 8:30 | 14:30 | 17:00 | 8:30
SW | 60330908 | F7234 | 7234 MR - Torrington | 7234_Middle Ridge-Torrington 110 kV | Voltage at Constrained Conductor | 114.5871 | 115.9846 | 114.5886 | 114.5465 | 116.0034 | 114.5471 | 114.2247 | 115.4929 | 114.3007 | 114.1742 | 115.46 | 114.2634 | 114.1315 | 115.4265 | 114.2152
SW | 82639691 | 3900 | PERANGA | 3900_Peranga 33 kV | % of Rated A | 3.7798 | 3.785 | 3.802 | 4.8619 | 4.8802 | 4.8903 | 6.4518 | 6.4679 | 6.4804 | 8.1127 | 8.1172 | 8.1331 | 9.584 | 9.5801 | 9.5971
SW | 82639691 | 3900 | PERANGA | 3900_Peranga 33 kV | Limiting Line Name | TR_CABLE 9120_1 | TR_CABLE 9120_1 | TR_CABLE 9120_1 | TR_CABLE 9120_1 | TR_CABLE 9120_1 | TR_CABLE 9120_1 | TR_CABLE 9120_1 | TR_CABLE 9120_1 | TR_CABLE 9120_1 | TR_CABLE 9120_1 | TR_CABLE 9120_1 | TR_CABLE 9120_1 | TR_CABLE 9120_1 | TR_CABLE 9120_1 | TR_CABLE 9120_1
SW | 82639691 | 3900 | PERANGA | 3900_Peranga 33 kV | Loading (A) | 3.7798 | 3.785 | 3.802 | 4.8619 | 4.8802 | 4.8903 | 6.4518 | 6.4679 | 6.4804 | 8.1127 | 8.1172 | 8.1331 | 9.584 | 9.5801 | 9.5971
SW | 82639691 | 3900 | PERANGA | 3900_Peranga 33 kV | Loading (MVA) | 0.22252 | 0.22218 | 0.2239 | 0.28623 | 0.2865 | 0.28711 | 0.37699 | 0.37972 | 0.37978 | 0.474 | 0.47599 | 0.47665 | 0.55966 | 0.56178 | 0.56246
SW | 82639691 | 3900 | PERANGA | 3900_Peranga 33 kV | Loading (MW) | 0.053124 | 0.054189 | 0.054605 | 0.18856 | 0.18962 | 0.19014 | 0.31288 | 0.31423 | 0.31465 | 0.4259 | 0.42703 | 0.42768 | 0.52066 | 0.52195 | 0.52261
SW | 82639691 | 3900 | PERANGA | 3900_Peranga 33 kV | Power Factor | 0.23874 | 0.2439 | 0.24388 | 0.65876 | 0.66185 | 0.66226 | 0.82995 | 0.82753 | 0.82852 | 0.89854 | 0.89715 | 0.89726 | 0.93031 | 0.9291 | 0.92914
SW | 82639691 | 3900 | PERANGA | 3900_Peranga 33 kV | Rating (A) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
SW | 82639691 | 3900 | PERANGA | 3900_Peranga 33 kV | Time | 16:30 | 21:00 | 5:30 | 16:30 | 21:00 | 4:00 | 15:30 | 21:00 | 5:30 | 15:30 | 18:30 | 5:30 | 15:00 | 18:30 | 5:30
SW | 82639691 | 3900 | PERANGA | 3900_Peranga 33 kV | Voltage at Constrained Conductor | 33.9897 | 33.8904 | 33.9997 | 33.9892 | 33.8936 | 33.8961 | 33.7353 | 33.8956 | 33.8354 | 33.7324 | 33.8555 | 33.8364 | 33.7145 | 33.856 | 33.8369
SW | 82640976 | EB10 | ACLAND | EB10_Acland 33 kV | % of Rated A | 12.3201 | 8.9352 | 11.0461 | 12.3211 | 8.9352 | 11.0469 | 12.3223 | 8.9354 | 11.0479 | 12.3236 | 8.9357 | 11.0487 | 12.3249 | 8.936 | 11.0498
SW | 82640976 | EB10 | ACLAND | EB10_Acland 33 kV | Limiting Line Name | TR_CABLE 104_1 | TR_CABLE 104_1 | TR_CABLE 104_1 | TR_CABLE 104_1 | TR_CABLE 104_1 | TR_CABLE 104_1 | TR_CABLE 104_1 | TR_CABLE 104_1 | TR_CABLE 104_1 | TR_CABLE 104_1 | TR_CABLE 104_1 | TR_CABLE 104_1 | TR_CABLE 104_1 | TR_CABLE 104_1 | TR_CABLE 104_1
SW | 82640976 | EB10 | ACLAND | EB10_Acland 33 kV | Loading (A) | 11.4577 | 8.3098 | 10.2729 | 11.4587 | 8.3098 | 10.2736 | 11.4597 | 8.3099 | 10.2745 | 11.4609 | 8.3102 | 10.2753 | 11.4621 | 8.3105 | 10.2763
SW | 82640976 | EB10 | ACLAND | EB10_Acland 33 kV | Loading (MVA) | 0.66893 | 0.48749 | 0.60027 | 0.66894 | 0.48749 | 0.60028 | 0.66895 | 0.48749 | 0.60028 | 0.66896 | 0.48749 | 0.60029 | 0.66897 | 0.4875 | 0.6003
SW | 82640976 | EB10 | ACLAND | EB10_Acland 33 kV | Loading (MW) | 0.56128 | 0.41657 | 0.5069 | 0.56128 | 0.41657 | 0.5069 | 0.56128 | 0.41657 | 0.5069 | 0.56129 | 0.41657 | 0.5069 | 0.56129 | 0.41657 | 0.5069
SW | 82640976 | EB10 | ACLAND | EB10_Acland 33 kV | Power Factor | 0.83907 | 0.85453 | 0.84445 | 0.83906 | 0.85453 | 0.84444 | 0.83906 | 0.85452 | 0.84443 | 0.83905 | 0.85452 | 0.84443 | 0.83904 | 0.85452 | 0.84442
SW | 82640976 | EB10 | ACLAND | EB10_Acland 33 kV | Rating (A) | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93
SW | 82640976 | EB10 | ACLAND | EB10_Acland 33 kV | Time | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30
SW | 82640976 | EB10 | ACLAND | EB10_Acland 33 kV | Voltage at Constrained Conductor | 33.7071 | 33.8701 | 33.736 | 33.7047 | 33.8702 | 33.7339 | 33.7021 | 33.8696 | 33.7313 | 33.6991 | 33.8687 | 33.7292 | 33.6962 | 33.8675 | 33.7263
SW | 83015720 | 7174 | 7174 FDR | 7174_Roma-Columboola 2 132 kV | % of Rated A | 31.8198 | 20.1796 | 21.1414 | 32.5882 | 20.6713 | 21.6888 | 33.4297 | 21.2119 | 22.2774 | 34.2524 | 21.7257 | 22.8328 | 34.9777 | 22.1858 | 23.3265
SW | 83015720 | 7174 | 7174 FDR | 7174_Roma-Columboola 2 132 kV | Limiting Line Name | TR_LINE 158493_a | TR_LINE 158493_a | TR_LINE 158493_a | TR_LINE 158493_a | TR_LINE 158493_a | TR_LINE 158493_a | TR_LINE 158493_a | TR_LINE 158493_a | TR_LINE 158493_a | TR_LINE 158493_a | TR_LINE 158493_a | TR_LINE 158493_a | TR_LINE 158493_a | TR_LINE 158493_a | TR_LINE 158493_a
SW | 83015720 | 7174 | 7174 FDR | 7174_Roma-Columboola 2 132 kV | Loading (A) | 55.0483 | 56.0993 | 58.773 | 56.3776 | 57.4662 | 60.2949 | 57.8333 | 58.969 | 61.9311 | 59.2566 | 60.3975 | 63.4752 | 60.5114 | 61.6765 | 64.8478
SW | 83015720 | 7174 | 7174 FDR | 7174_Roma-Columboola 2 132 kV | Loading (MVA) | 12.8801 | 13.1372 | 13.7903 | 13.2018 | 13.4681 | 14.1584 | 13.5531 | 13.8306 | 14.5531 | 13.8956 | 14.1749 | 14.9253 | 14.1979 | 14.4831 | 15.2561
SW | 83015720 | 7174 | 7174 FDR | 7174_Roma-Columboola 2 132 kV | Loading (MW) | 6.2123 | 6.5492 | 7.7965 | 6.8243 | 7.1594 | 8.4037 | 7.4403 | 7.772 | 9.0114 | 7.9953 | 8.3252 | 9.5602 | 8.4762 | 8.8042 | 10.0354
SW | 83015720 | 7174 | 7174 FDR | 7174_Roma-Columboola 2 132 kV | Power Factor | 0.48232 | 0.49852 | 0.56536 | 0.51692 | 0.53158 | 0.59355 | 0.54897 | 0.56194 | 0.61921 | 0.57539 | 0.58732 | 0.64054 | 0.597 | 0.60789 | 0.65779
SW | 83015720 | 7174 | 7174 FDR | 7174_Roma-Columboola 2 132 kV | Rating (A) | 173 | 278 | 278 | 173 | 278 | 278 | 173 | 278 | 278 | 173 | 278 | 278 | 173 | 278 | 278
SW | 83015720 | 7174 | 7174 FDR | 7174_Roma-Columboola 2 132 kV | Time | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00
SW | 83015720 | 7174 | 7174 FDR | 7174_Roma-Columboola 2 132 kV | Voltage at Constrained Conductor | 135.0869 | 135.2031 | 135.4676 | 135.1962 | 135.3112 | 135.5728 | 135.3011 | 135.4119 | 135.6708 | 135.3877 | 135.4999 | 135.7555 | 135.4647 | 135.5753 | 135.8276
SW | 83015723 | 7164 | 7164 FDR | 7164_Roma-Columboola 1 132 kV | % of Rated A | 345.6661 | 215.9506 | 217.7455 | 347.0523 | 216.8093 | 218.5972 | 348.4511 | 217.6743 | 219.4534 | 349.7116 | 218.4525 | 220.2241 | 350.7953 | 219.124 | 220.889
SW | 83015723 | 7164 | 7164 FDR | 7164_Roma-Columboola 1 132 kV | Limiting Line Name | TR_LINE 158494_b | TR_LINE 158494_b | TR_LINE 158494_b | TR_LINE 158494_b | TR_LINE 158494_b | TR_LINE 158494_b | TR_LINE 158494_b | TR_LINE 158494_b | TR_LINE 158494_b | TR_LINE 158494_b | TR_LINE 158494_b | TR_LINE 158494_b | TR_LINE 158494_b | TR_LINE 158494_b | TR_LINE 158494_b
SW | 83015723 | 7164 | 7164 FDR | 7164_Roma-Columboola 1 132 kV | Loading (A) | 592.8674 | 595.1773 | 600.18 | 595.2748 | 597.5736 | 602.557 | 597.704 | 599.9877 | 604.9462 | 599.8933 | 602.1596 | 607.0972 | 601.7758 | 604.0339 | 608.9532
SW | 83015723 | 7164 | 7164 FDR | 7164_Roma-Columboola 1 132 kV | Loading (MVA) | 140.8714 | 141.5145 | 142.6969 | 141.4309 | 142.0718 | 143.2491 | 141.9953 | 142.6328 | 143.804 | 142.5026 | 143.1363 | 144.3023 | 142.938 | 143.5701 | 144.7315
SW | 83015723 | 7164 | 7164 FDR | 7164_Roma-Columboola 1 132 kV | Loading (MW) | 117.0253 | 117.2855 | 118.3204 | 117.5404 | 117.7983 | 118.8289 | 118.0588 | 118.3137 | 119.3384 | 118.5269 | 118.7791 | 119.7986 | 118.9313 | 119.1816 | 120.1967
SW | 83015723 | 7164 | 7164 FDR | 7164_Roma-Columboola 1 132 kV | Power Factor | 0.83072 | 0.82879 | 0.82917 | 0.83108 | 0.82915 | 0.82953 | 0.83143 | 0.8295 | 0.82987 | 0.83175 | 0.82983 | 0.83019 | 0.83205 | 0.83013 | 0.83048
SW | 83015723 | 7164 | 7164 FDR | 7164_Roma-Columboola 1 132 kV | Rating (A) | 173 | 278 | 278 | 173 | 278 | 278 | 173 | 278 | 278 | 173 | 278 | 278 | 173 | 278 | 278
SW | 83015723 | 7164 | 7164 FDR | 7164_Roma-Columboola 1 132 kV | Time | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00
SW | 83015723 | 7164 | 7164 FDR | 7164_Roma-Columboola 1 132 kV | Voltage at Constrained Conductor | 137.1844 | 137.2758 | 137.269 | 137.1722 | 137.2637 | 137.2566 | 137.1599 | 137.2513 | 137.2441 | 137.1476 | 137.2389 | 137.2317 | 137.1363 | 137.2278 | 137.2204
SW | 83921739 | 3153 | CECIL PLAINS ROAD | 3153_Cecil Plains Road 33 kV | % of Rated A | 63.5972 | 58.3132 | 59.4004 | 64.4928 | 58.6824 | 59.3143 | 64.4162 | 59.013 | 59.2444 | 64.3544 | 58.9444 | 59.1842 | 64.3074 | 58.8913 | 59.1411
SW | 83921739 | 3153 | CECIL PLAINS ROAD | 3153_Cecil Plains Road 33 kV | Limiting Line Name | TR_LINE 183124_2 | TR_CABLE 5205_1 | TR_CABLE 5205_1 | TR_LINE 183124_2 | TR_CABLE 5205_1 | TR_CABLE 5205_1 | TR_LINE 183124_2 | TR_CABLE 5205_1 | TR_CABLE 5205_1 | TR_LINE 183124_2 | TR_CABLE 5205_1 | TR_CABLE 5205_1 | TR_LINE 183124_2 | TR_CABLE 5205_1 | TR_CABLE 5205_1
SW | 83921739 | 3153 | CECIL PLAINS ROAD | 3153_Cecil Plains Road 33 kV | Loading (A) | 59.1452 | 58.3132 | 59.4004 | 59.9781 | 58.6824 | 59.3143 | 59.9069 | 59.013 | 59.2444 | 59.8494 | 58.9444 | 59.1842 | 59.8057 | 58.8913 | 59.1411
SW | 83921739 | 3153 | CECIL PLAINS ROAD | 3153_Cecil Plains Road 33 kV | Loading (MVA) | 3.4833 | 3.4261 | 3.4492 | 3.4854 | 3.4096 | 3.449 | 3.4852 | 3.4273 | 3.4488 | 3.4851 | 3.4272 | 3.4487 | 3.485 | 3.4271 | 3.4486
SW | 83921739 | 3153 | CECIL PLAINS ROAD | 3153_Cecil Plains Road 33 kV | Loading (MW) | 3.466 | 3.4172 | 3.4339 | 3.467 | 3.3997 | 3.4338 | 3.4669 | 3.4178 | 3.4337 | 3.4669 | 3.4177 | 3.4337 | 3.4668 | 3.4177 | 3.4336
SW | 83921739 | 3153 | CECIL PLAINS ROAD | 3153_Cecil Plains Road 33 kV | Power Factor | 0.99503 | 0.9974 | 0.99557 | 0.99473 | 0.9971 | 0.9956 | 0.99475 | 0.99721 | 0.99562 | 0.99478 | 0.99723 | 0.99564 | 0.99479 | 0.99724 | 0.99565
SW | 83921739 | 3153 | CECIL PLAINS ROAD | 3153_Cecil Plains Road 33 kV | Rating (A) | 93 | 100 | 100 | 93 | 100 | 100 | 93 | 100 | 100 | 93 | 100 | 100 | 93 | 100 | 100
SW | 83921739 | 3153 | CECIL PLAINS ROAD | 3153_Cecil Plains Road 33 kV | Time | 12:00 | 18:30 | 8:30 | 12:00 | 18:00 | 8:30 | 12:00 | 18:30 | 8:30 | 12:00 | 18:30 | 8:30 | 12:00 | 18:30 | 8:30
SW | 83921739 | 3153 | CECIL PLAINS ROAD | 3153_Cecil Plains Road 33 kV | Voltage at Constrained Conductor | 34.0029 | 33.9213 | 33.5249 | 33.5505 | 33.5458 | 33.5717 | 33.5886 | 33.531 | 33.6098 | 33.6195 | 33.5689 | 33.6426 | 33.643 | 33.5982 | 33.6662
SW | 83921742 | 3154 | CENTRAL DALBY 1 | 3154_Central Dalby 1 33 kV | % of Rated A | 2.8383 | 2.6471 | 3.0934 | 0.78944 | 0.82521 | 0.9155 | 1.5948 | 1.7632 | 2.3932 | 3.3832 | 3.5526 | 4.3235 | 4.8916 | 5.0675 | 5.9691
SW | 83921742 | 3154 | CENTRAL DALBY 1 | 3154_Central Dalby 1 33 kV | Limiting Line Name | TR_CABLE 4402_1 | TR_CABLE 4402_1 | TR_LINE 92495_1 | TR_CABLE 5202_1 | TR_CABLE 5202_1 | TR_CABLE 5202_1 | TR_CABLE 4402_1 | TR_CABLE 4402_1 | TR_LINE 92495_1 | TR_CABLE 4402_1 | TR_CABLE 4402_1 | TR_LINE 92495_1 | TR_CABLE 4402_1 | TR_CABLE 4402_1 | TR_LINE 92495_1
SW | 83921742 | 3154 | CENTRAL DALBY 1 | 3154_Central Dalby 1 33 kV | Loading (A) | 12.7724 | 11.9118 | 12.6829 | 3.9472 | 4.1261 | 4.5775 | 7.1764 | 7.9346 | 9.8122 | 15.2245 | 15.9868 | 17.7265 | 22.0123 | 22.8039 | 24.4701
SW | 83921742 | 3154 | CENTRAL DALBY 1 | 3154_Central Dalby 1 33 kV | Loading (MVA) | 0.75181 | 0.69744 | 0.73647 | 0.22938 | 0.24298 | 0.26601 | 0.42051 | 0.46139 | 0.57099 | 0.89332 | 0.93105 | 1.0327 | 1.2872 | 1.3297 | 1.4277
SW | 83921742 | 3154 | CENTRAL DALBY 1 | 3154_Central Dalby 1 33 kV | Loading (MW) | 0.74884 | 0.68971 | 0.73016 | 0.16649 | 0.069764 | 0.031564 | 0.42008 | 0.45843 | 0.55958 | 0.89141 | 0.93058 | 1.0301 | 1.2832 | 1.328 | 1.4274
SW | 83921742 | 3154 | CENTRAL DALBY 1 | 3154_Central Dalby 1 33 kV | Power Factor | 0.99604 | 0.98892 | 0.99144 | 0.72581 | 0.28712 | 0.11866 | 0.99896 | 0.99357 | 0.98001 | 0.99785 | 0.9995 | 0.9975 | 0.99696 | 0.99874 | 0.99982
SW | 83921742 | 3154 | CENTRAL DALBY 1 | 3154_Central Dalby 1 33 kV | Rating (A) | 450 | 450 | 410 | 500 | 500 | 500 | 450 | 450 | 410 | 450 | 450 | 410 | 450 | 450 | 410
SW | 83921742 | 3154 | CENTRAL DALBY 1 | 3154_Central Dalby 1 33 kV | Time | 12:00 | 17:00 | 8:30 | 12:00 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00 | 16:00 | 21:00 | 4:00
SW | 83921742 | 3154 | CENTRAL DALBY 1 | 3154_Central Dalby 1 33 kV | Voltage at Constrained Conductor | 33.9841 | 33.8043 | 33.5253 | 33.5514 | 33.9991 | 33.5513 | 33.8309 | 33.5726 | 33.5972 | 33.8769 | 33.6241 | 33.6353 | 33.7604 | 33.6645 | 33.685
SW | 84000793 | 3178 | WILKIE CREEK | 3178_Wilkie Creek 33 kV | % of Rated A | 4.1677 | 4.1354 | 4.1721 | 4.1738 | 4.1423 | 4.1789 | 4.1789 | 4.1481 | 4.1848 | 4.1828 | 4.1531 | 4.1897 | 4.1843 | 4.157 | 4.1936
SW | 84000793 | 3178 | WILKIE CREEK | 3178_Wilkie Creek 33 kV | Limiting Line Name | TR_CABLE 3771_1 | TR_CABLE 3771_1 | TR_CABLE 3771_1 | TR_CABLE 3771_1 | TR_CABLE 3771_1 | TR_CABLE 3771_1 | TR_CABLE 3771_1 | TR_CABLE 3771_1 | TR_CABLE 3771_1 | TR_CABLE 3771_1 | TR_CABLE 3771_1 | TR_CABLE 3771_1 | TR_CABLE 3771_1 | TR_CABLE 3771_1 | TR_CABLE 3771_1
SW | 84000793 | 3178 | WILKIE CREEK | 3178_Wilkie Creek 33 kV | Loading (A) | 3.876 | 3.8459 | 3.8801 | 3.8816 | 3.8524 | 3.8864 | 3.8863 | 3.8577 | 3.8919 | 3.89 | 3.8624 | 3.8965 | 3.8914 | 3.866 | 3.9001
SW | 84000793 | 3178 | WILKIE CREEK | 3178_Wilkie Creek 33 kV | Loading (MVA) | 0.22365 | 0.22141 | 0.22337 | 0.2243 | 0.22181 | 0.2241 | 0.22484 | 0.22242 | 0.22472 | 0.22526 | 0.22295 | 0.22525 | 0.2251 | 0.22336 | 0.22566
SW | 84000793 | 3178 | WILKIE CREEK | 3178_Wilkie Creek 33 kV | Loading (MW) | 0.0091304 | 0.013427 | 0.0065533 | 0.0091349 | 0.012156 | 0.0065583 | 0.0091387 | 0.01216 | 0.0065627 | 0.0091416 | 0.012164 | 0.0065664 | 0.0080141 | 0.012167 | 0.0065693
SW | 84000793 | 3178 | WILKIE CREEK | 3178_Wilkie Creek 33 kV | Power Factor | 0.040824 | 0.060643 | 0.029338 | 0.040726 | 0.054804 | 0.029266 | 0.040645 | 0.054673 | 0.029204 | 0.040582 | 0.054559 | 0.029152 | 0.035603 | 0.05447 | 0.029111
SW | 84000793 | 3178 | WILKIE CREEK | 3178_Wilkie Creek 33 kV | Rating (A) | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93
SW | 84000793 | 3178 | WILKIE CREEK | 3178_Wilkie Creek 33 kV | Time | 16:00 | 18:00 | 4:00 | 16:00 | 21:30 | 4:00 | 16:00 | 21:30 | 4:00 | 16:00 | 21:30 | 4:00 | 11:00 | 21:30 | 4:00
SW | 84000793 | 3178 | WILKIE CREEK | 3178_Wilkie Creek 33 kV | Voltage at Constrained Conductor | 33.3145 | 33.2385 | 33.2372 | 33.3623 | 33.2421 | 33.2908 | 33.4019 | 33.2871 | 33.3371 | 33.433 | 33.3262 | 33.3759 | 33.3964 | 33.3569 | 33.4064
SW | 84109456 | 7314 | 7314 DALBY EAST | 7314_Dalby East 110 kV | % of Rated A | 4.6514 | 4.3993 | 5.0038 | 4.6488 | 4.3986 | 5.0079 | 4.65 | 4.4008 | 5.0144 | 4.6399 | 4.4045 | 5.0211 | 4.641 | 4.4081 | 5.027
SW | 84109456 | 7314 | 7314 DALBY EAST | 7314_Dalby East 110 kV | Limiting Line Name | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1
SW | 84109456 | 7314 | 7314 DALBY EAST | 7314_Dalby East 110 kV | Loading (A) | 12.8844 | 12.978 | 13.1599 | 12.8773 | 12.9758 | 13.1708 | 12.8805 | 12.9823 | 13.1878 | 12.8525 | 12.9932 | 13.2056 | 12.8556 | 13.0039 | 13.2209
SW | 84109456 | 7314 | 7314 DALBY EAST | 7314_Dalby East 110 kV | Loading (MVA) | 2.5723 | 2.6183 | 2.6575 | 2.5743 | 2.6219 | 2.6637 | 2.5777 | 2.6266 | 2.6706 | 2.5745 | 2.6317 | 2.6772 | 2.5733 | 2.6362 | 2.6826
SW | 84109456 | 7314 | 7314 DALBY EAST | 7314_Dalby East 110 kV | Loading (MW) | 0.30887 | 0.30486 | 0.21193 | 0.2235 | 0.21945 | 0.12678 | 0.16032 | 0.15626 | 0.063777 | 0.11435 | 0.11047 | 0.018124 | 0.087139 | 0.080326 | 0.011932
SW | 84109456 | 7314 | 7314 DALBY EAST | 7314_Dalby East 110 kV | Power Factor | 0.12008 | 0.11643 | 0.079747 | 0.086821 | 0.083698 | 0.047596 | 0.062193 | 0.059491 | 0.023881 | 0.044418 | 0.041977 | 0.0067699 | 0.033863 | 0.030471 | 0.0044478
SW | 84109456 | 7314 | 7314 DALBY EAST | 7314_Dalby East 110 kV | Rating (A) | 277 | 295 | 263 | 277 | 295 | 263 | 277 | 295 | 263 | 277 | 295 | 263 | 277 | 295 | 263
SW | 84109456 | 7314 | 7314 DALBY EAST | 7314_Dalby East 110 kV | Time | 16:00 | 21:00 | 4:00 | 16:00 | 21:00 | 4:00 | 16:00 | 21:00 | 4:00 | 16:00 | 21:00 | 4:00 | 15:30 | 21:00 | 4:00
SW | 84109456 | 7314 | 7314 DALBY EAST | 7314_Dalby East 110 kV | Voltage at Constrained Conductor | 115.2648 | 116.4788 | 116.59 | 115.4165 | 116.6604 | 116.7645 | 115.5437 | 116.8083 | 116.9172 | 115.6486 | 116.9385 | 117.0465 | 115.5662 | 117.0415 | 117.1492
SW | 84170804 | 3196 | TARA | 3196_Tara 33 kV | % of Rated A | 9.2656 | 7.5684 | 7.6862 | 8.7674 | 7.1429 | 7.3897 | 8.5662 | 6.96 | 7.3522 | 8.4533 | 6.9044 | 7.3979 | 8.4658 | 6.9043 | 7.4615
SW | 84170804 | 3196 | TARA | 3196_Tara 33 kV | Limiting Line Name | TR_LINE 27355_1 | TR_LINE 24024_1 | TR_LINE 24024_1 | TR_LINE 27355_1 | TR_LINE 24024_1 | TR_LINE 24024_1 | TR_LINE 27355_1 | TR_LINE 24024_1 | TR_LINE 24024_1 | TR_LINE 27355_1 | TR_LINE 24024_1 | TR_LINE 24024_1 | TR_LINE 27355_1 | TR_LINE 24024_1 | TR_LINE 24024_1
SW | 84170804 | 3196 | TARA | 3196_Tara 33 kV | Loading (A) | 8.617 | 8.7793 | 8.916 | 8.1537 | 8.2858 | 8.572 | 7.9666 | 8.0735 | 8.5285 | 7.8616 | 8.0091 | 8.5816 | 7.8732 | 8.009 | 8.6554
SW | 84170804 | 3196 | TARA | 3196_Tara 33 kV | Loading (MVA) | 0.49802 | 0.50555 | 0.51375 | 0.47215 | 0.47817 | 0.49561 | 0.46203 | 0.46672 | 0.49396 | 0.45583 | 0.46366 | 0.49774 | 0.45692 | 0.46416 | 0.50256
SW | 84170804 | 3196 | TARA | 3196_Tara 33 kV | Loading (MW) | 0.21368 | 0.22584 | 0.21714 | 0.12846 | 0.14059 | 0.069187 | 0.06533 | 0.077453 | 0.0061721 | 0.020057 | 0.031669 | 0.039523 | 0.010101 | 0.0015103 | 0.069625
SW | 84170804 | 3196 | TARA | 3196_Tara 33 kV | Power Factor | 0.42907 | 0.44673 | 0.42265 | 0.27208 | 0.29403 | 0.1396 | 0.1414 | 0.16595 | 0.012495 | 0.044001 | 0.068303 | 0.079404 | 0.022107 | 0.0032537 | 0.13854
SW | 84170804 | 3196 | TARA | 3196_Tara 33 kV | Rating (A) | 93 | 116 | 116 | 93 | 116 | 116 | 93 | 116 | 116 | 93 | 116 | 116 | 93 | 116 | 116
SW | 84170804 | 3196 | TARA | 3196_Tara 33 kV | Time | 16:00 | 21:00 | 0:00 | 16:00 | 21:00 | 4:00 | 16:00 | 21:00 | 4:00 | 15:30 | 21:00 | 4:00 | 15:30 | 21:00 | 4:00
SW | 84170804 | 3196 | TARA | 3196_Tara 33 kV | Voltage at Constrained Conductor | 33.368 | 33.2459 | 33.2676 | 33.4323 | 33.3185 | 33.3806 | 33.484 | 33.3758 | 33.4392 | 33.4761 | 33.4238 | 33.4868 | 33.5065 | 33.4604 | 33.5232
SW | 84301618 | 3203 | MILES | 3203_Miles 33 kV | % of Rated A | 22.3279 | 20.1465 | 21.6263 | 14.7418 | 12.7692 | 14.0817 | 7.9544 | 6.554 | 7.441 | 3.7117 | 5.481 | 8.1906 | 6.9592 | 8.9996 | 12.0951
SW | 84301618 | 3203 | MILES | 3203_Miles 33 kV | Limiting Line Name | HV_CABLE 219934_1 | HV_CABLE 219934_1 | HV_CABLE 219934_1 | HV_CABLE 219934_1 | HV_CABLE 219934_1 | HV_CABLE 219934_1 | HV_CABLE 219934_1 | HV_CABLE 219934_1 | HV_CABLE 219934_1 | HV_CABLE 219934_1 | HV_CABLE 219934_1 | HV_CABLE 219934_1 | HV_CABLE 219934_1 | HV_CABLE 219934_1 | HV_CABLE 219934_1
SW | 84301618 | 3203 | MILES | 3203_Miles 33 kV | Loading (A) | 40.4134 | 36.4652 | 39.1436 | 26.6827 | 23.1123 | 25.4878 | 14.3975 | 11.8628 | 13.4682 | 6.7182 | 9.9205 | 14.825 | 12.5962 | 16.2893 | 21.8922
SW | 84301618 | 3203 | MILES | 3203_Miles 33 kV | Loading (MVA) | 2.3407 | 2.1151 | 2.2681 | 1.5461 | 1.3411 | 1.4774 | 0.83444 | 0.68858 | 0.78092 | 0.38991 | 0.57659 | 0.86238 | 0.73108 | 0.94684 | 1.2736
SW | 84301618 | 3203 | MILES | 3203_Miles 33 kV | Loading (MW) | 2.3327 | 2.0791 | 2.2523 | 1.5317 | 1.279 | 1.4518 | 0.8093 | 0.55731 | 0.72943 | 0.081602 | 0.24343 | 0.53604 | 0.63856 | 0.80005 | 1.0921
SW | 84301618 | 3203 | MILES | 3203_Miles 33 kV | Power Factor | 0.99657 | 0.98297 | 0.99303 | 0.99069 | 0.95369 | 0.98267 | 0.96987 | 0.80936 | 0.93407 | 0.20929 | 0.42219 | 0.62159 | 0.87345 | 0.84496 | 0.85749
SW | 84301618 | 3203 | MILES | 3203_Miles 33 kV | Rating (A) | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181
SW | 84301618 | 3203 | MILES | 3203_Miles 33 kV | Time | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00
SW | 84301618 | 3203 | MILES | 3203_Miles 33 kV | Voltage at Constrained Conductor | 33.4398 | 33.4886 | 33.4538 | 33.4538 | 33.502 | 33.466 | 33.4617 | 33.5125 | 33.476 | 33.5078 | 33.5563 | 33.5846 | 33.5095 | 33.5595 | 33.587
SW | 84976334 | 7448 | 7448 SOTO - TOCE 110KV | 7448_South Toowoomba-TWCE 110 kV | % of Rated A | 12.0798 | 12.0417 | 12.078 | 11.6082 | 11.5789 | 11.6068 | 11.1635 | 11.1432 | 11.1626 | 10.7708 | 10.7588 | 10.7702 | 10.4662 | 10.4622 | 10.466
SW | 84976334 | 7448 | 7448 SOTO - TOCE 110KV | 7448_South Toowoomba-TWCE 110 kV | Limiting Line Name | TR_CABLE 13760_1 | TR_CABLE 13760_1 | TR_CABLE 13760_1 | TR_CABLE 13760_1 | TR_CABLE 13760_1 | TR_CABLE 13760_1 | TR_CABLE 13760_1 | TR_CABLE 13760_1 | TR_CABLE 13760_1 | TR_CABLE 13760_1 | TR_CABLE 13760_1 | TR_CABLE 13760_1 | TR_CABLE 13760_1 | TR_CABLE 13760_1 | TR_CABLE 13760_1
SW | 84976334 | 7448 | 7448 SOTO - TOCE 110KV | 7448_South Toowoomba-TWCE 110 kV | Loading (A) | 50.7353 | 50.575 | 50.7275 | 48.7543 | 48.6312 | 48.7484 | 46.8869 | 46.8013 | 46.883 | 45.2373 | 45.1869 | 45.2348 | 43.9579 | 43.9412 | 43.9574
SW | 84976334 | 7448 | 7448 SOTO - TOCE 110KV | 7448_South Toowoomba-TWCE 110 kV | Loading (MVA) | 10.0697 | 10.1453 | 10.0742 | 9.6732 | 9.7539 | 9.678 | 9.2993 | 9.385 | 9.3043 | 8.9685 | 9.0591 | 8.9751 | 8.712 | 8.8789 | 8.7183
SW | 84976334 | 7448 | 7448 SOTO - TOCE 110KV | 7448_South Toowoomba-TWCE 110 kV | Loading (MW) | 8.3243 | 8.3269 | 8.3244 | 7.8074 | 7.8101 | 7.8075 | 7.3078 | 7.3105 | 7.308 | 6.8545 | 6.8572 | 6.8546 | 6.4936 | 6.4983 | 6.4938
SW | 84976334 | 7448 | 7448 SOTO - TOCE 110KV | 7448_South Toowoomba-TWCE 110 kV | Power Factor | 0.82667 | 0.82076 | 0.82631 | 0.80712 | 0.80071 | 0.80673 | 0.78585 | 0.77896 | 0.78544 | 0.76428 | 0.75694 | 0.76374 | 0.74537 | 0.73189 | 0.74485
SW | 84976334 | 7448 | 7448 SOTO - TOCE 110KV | 7448_South Toowoomba-TWCE 110 kV | Rating (A) | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420
SW | 84976334 | 7448 | 7448 SOTO - TOCE 110KV | 7448_South Toowoomba-TWCE 110 kV | Time | 9:00 | 17:00 | 8:30 | 9:00 | 17:00 | 8:30 | 9:00 | 17:00 | 8:30 | 9:00 | 17:00 | 8:30 | 14:30 | 18:00 | 8:30
SW | 84976334 | 7448 | 7448 SOTO - TOCE 110KV | 7448_South Toowoomba-TWCE 110 kV | Voltage at Constrained Conductor | 114.5896 | 115.8161 | 114.6581 | 114.5505 | 115.7986 | 114.6208 | 114.508 | 115.7749 | 114.5794 | 114.4628 | 115.7473 | 114.5523 | 114.4247 | 116.6607 | 114.5086
SW | 84976560 | 7449 | SOTO - TWCE 110KV 7449 FDR | 7449 South Toowoomba-TWCE 110 kV | % of Rated A | 8.7869 | 8.8279 | 8.8267 | 8.6262 | 8.6722 | 8.6708 | 8.4774 | 8.5283 | 8.5268 | 8.3483 | 8.4035 | 8.4019 | 8.2549 | 8.3082 | 8.3065
SW | 84976560 | 7449 | SOTO - TWCE 110KV 7449 FDR | 7449 South Toowoomba-TWCE 110 kV | Limiting Line Name | TR_CABLE 13761_1 | TR_CABLE 13761_1 | TR_CABLE 13761_1 | TR_CABLE 13761_1 | TR_CABLE 13761_1 | TR_CABLE 13761_1 | TR_CABLE 13761_1 | TR_CABLE 13761_1 | TR_CABLE 13761_1 | TR_CABLE 13761_1 | TR_CABLE 13761_1 | TR_CABLE 13761_1 | TR_CABLE 13761_1 | TR_CABLE 13761_1 | TR_CABLE 13761_1
SW | 84976560 | 7449 | SOTO - TWCE 110KV 7449 FDR | 7449 South Toowoomba-TWCE 110 kV | Loading (A) | 36.9049 | 37.0774 | 37.0721 | 36.2299 | 36.4232 | 36.4174 | 35.6052 | 35.8187 | 35.8124 | 35.0628 | 35.2947 | 35.2879 | 34.6705 | 34.8944 | 34.8873
SW | 84976560 | 7449 | SOTO - TWCE 110KV 7449 FDR | 7449 South Toowoomba-TWCE 110 kV | Loading (MVA) | 7.377 | 7.4946 | 7.491 | 7.2405 | 7.3622 | 7.3586 | 7.1139 | 7.2395 | 7.2358 | 7.0035 | 7.1328 | 7.129 | 6.9308 | 7.0508 | 7.047
SW | 84976560 | 7449 | SOTO - TWCE 110KV 7449 FDR | 7449 South Toowoomba-TWCE 110 kV | Loading (MW) | 4.2219 | 4.2246 | 4.2245 | 3.9638 | 3.9665 | 3.9664 | 3.7142 | 3.7171 | 3.717 | 3.4878 | 3.4907 | 3.4906 | 3.3078 | 3.3104 | 3.3104
SW | 84976560 | 7449 | SOTO - TWCE 110KV 7449 FDR | 7449 South Toowoomba-TWCE 110 kV | Power Factor | 0.5723 | 0.56369 | 0.56394 | 0.54744 | 0.53877 | 0.53902 | 0.52211 | 0.51344 | 0.51369 | 0.49801 | 0.48938 | 0.48963 | 0.47726 | 0.46951 | 0.46975
SW | 84976560 | 7449 | SOTO - TWCE 110KV 7449 FDR | 7449 South Toowoomba-TWCE 110 kV | Rating (A) | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420
SW | 84976560 | 7449 | SOTO - TWCE 110KV 7449 FDR | 7449 South Toowoomba-TWCE 110 kV | Time | 16:30 | 18:00 | 6:00 | 16:30 | 18:00 | 6:00 | 16:30 | 18:00 | 6:00 | 16:30 | 18:00 | 6:00 | 9:00 | 18:00 | 6:00
SW | 84976560 | 7449 | SOTO - TWCE 110KV 7449 FDR | 7449 South Toowoomba-TWCE 110 kV | Voltage at Constrained Conductor | 115.4075 | 116.702 | 116.6629 | 115.383 | 116.6998 | 116.6608 | 115.3536 | 116.6914 | 116.6524 | 115.3207 | 116.6783 | 116.6393 | 115.4144 | 116.6607 | 116.6217
SW | 85177784 | 7374 | Roma Power Station 132 kV | 7374_Roma Power Station 132 kV | % of Rated A | 0.0074936 | 0.0075 | 0.0075147 | 0.0074996 | 0.007506 | 0.0075205 | 0.0075055 | 0.0075116 | 0.007526 | 0.0075103 | 0.0075165 | 0.0075307 | 0.0075145 | 0.0075207 | 0.0075347
SW | 85177784 | 7374 | Roma Power Station 132 kV | 7374_Roma Power Station 132 kV | Limiting Line Name | 7374 ROPS-ROMA | 7374 ROPS-ROMA | 7374 ROPS-ROMA | 7374 ROPS-ROMA | 7374 ROPS-ROMA | 7374 ROPS-ROMA | 7374 ROPS-ROMA | 7374 ROPS-ROMA | 7374 ROPS-ROMA | 7374 ROPS-ROMA | 7374 ROPS-ROMA | 7374 ROPS-ROMA | 7374 ROPS-ROMA | 7374 ROPS-ROMA | 7374 ROPS-ROMA
SW | 85177784 | 7374 | Roma Power Station 132 kV | 7374_Roma Power Station 132 kV | Loading (A) | 0.032672 | 0.0327 | 0.032764 | 0.032698 | 0.032726 | 0.03279 | 0.032724 | 0.032751 | 0.032813 | 0.032745 | 0.032772 | 0.032834 | 0.032763 | 0.03279 | 0.032851
SW | 85177784 | 7374 | Roma Power Station 132 kV | 7374_Roma Power Station 132 kV | Loading (MVA) | 0.0076445 | 0.0076577 | 0.0076877 | 0.0076569 | 0.0076699 | 0.0076996 | 0.0076688 | 0.0076813 | 0.0077107 | 0.0076786 | 0.0076913 | 0.0077204 | 0.0076873 | 0.0076999 | 0.0077286
SW | 85177784 | 7374 | Roma Power Station 132 kV | 7374_Roma Power Station 132 kV | Loading (MW) | 2.3056e-08 | 2.3113e-08 | 2.3162e-08 | 2.3124e-08 | 2.3159e-08 | 2.3246e-08 | 2.3104e-08 | 2.3137e-08 | 2.3246e-08 | 2.3152e-08 | 2.3246e-08 | 2.3293e-08 | 2.3234e-08 | 2.3252e-08 | 2.3333e-08
SW | 85177784 | 7374 | Roma Power Station 132 kV | 7374_Roma Power Station 132 kV | Power Factor | 3.016e-06 | 3.0183e-06 | 3.0128e-06 | 3.02e-06 | 3.0195e-06 | 3.0192e-06 | 3.0128e-06 | 3.0121e-06 | 3.0148e-06 | 3.0152e-06 | 3.0223e-06 | 3.0171e-06 | 3.0224e-06 | 3.0198e-06 | 3.019e-06
SW | 85177784 | 7374 | Roma Power Station 132 kV | 7374_Roma Power Station 132 kV | Rating (A) | 436 | 436 | 436 | 436 | 436 | 436 | 436 | 436 | 436 | 436 | 436 | 436 | 436 | 436 | 436
SW | 85177784 | 7374 | Roma Power Station 132 kV | 7374_Roma Power Station 132 kV | Time | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00 | 16:30 | 21:00 | 4:00
SW | 85177784 | 7374 | Roma Power Station 132 kV | 7374_Roma Power Station 132 kV | Voltage at Constrained Conductor | 135.0869 | 135.2031 | 135.4676 | 135.1962 | 135.3112 | 135.5728 | 135.3011 | 135.4119 | 135.6708 | 135.3877 | 135.4999 | 135.7555 | 135.4647 | 135.5753 | 135.8276
WB | 50000001 | 7187 | 7187 GIN GIN - BUNDABERG T/LINE | 7187_Gin Gin - Bundaberg 132 kV | % of Rated A | 13.9578 | 22.0841 | 24.3621 | 12.2636 | 20.3715 | 22.4734 | 10.3115 | 18.6544 | 20.5796 | 9.1451 | 17.1391 | 18.9082 | 8.5254 | 15.8696 | 17.5077
WB | 50000001 | 7187 | 7187 GIN GIN - BUNDABERG T/LINE | 7187_Gin Gin - Bundaberg 132 kV | Limiting Line Name | TR_LINE 6941_1 | TR_LINE 6941_1 | TR_LINE 6941_1 | TR_LINE 6941_1 | TR_LINE 6941_1 | TR_LINE 6941_1 | TR_LINE 6941_1 | TR_LINE 6941_1 | TR_LINE 6941_1 | TR_LINE 6941_1 | TR_LINE 6941_1 | TR_LINE 6941_1 | TR_LINE 6941_1 | TR_LINE 6941_1 | TR_LINE 6941_1
WB | 50000001 | 7187 | 7187 GIN GIN - BUNDABERG T/LINE | 7187_Gin Gin - Bundaberg 132 kV | Loading (A) | 94.7737 | 161.4351 | 161.5204 | 83.2701 | 148.916 | 148.9984 | 70.015 | 136.3638 | 136.4426 | 62.095 | 125.2871 | 125.3614 | 57.8878 | 116.007 | 116.0759
WB | 50000001 | 7187 | 7187 GIN GIN - BUNDABERG T/LINE | 7187_Gin Gin - Bundaberg 132 kV | Loading (MVA) | 22.8744 | 38.6375 | 38.658 | 20.0986 | 35.6492 | 35.669 | 16.8885 | 32.6473 | 32.6662 | 14.975 | 29.9962 | 30.014 | 13.957 | 27.7726 | 27.7892
WB | 50000001 | 7187 | 7187 GIN GIN - BUNDABERG T/LINE | 7187_Gin Gin - Bundaberg 132 kV | Loading (MW) | 15.0268 | 28.1743 | 28.1972 | 10.9996 | 24.1183 | 24.1411 | 6.8635 | 19.9331 | 19.9558 | 2.929 | 15.9637 | 15.9863 | 0.6287 | 12.3707 | 12.3932
WB | 50000001 | 7187 | 7187 GIN GIN - BUNDABERG T/LINE | 7187_Gin Gin - Bundaberg 132 kV | Power Factor | 0.65693 | 0.7292 | 0.7294 | 0.54728 | 0.67655 | 0.67681 | 0.4064 | 0.61056 | 0.6109 | 0.1956 | 0.53219 | 0.53263 | 0.045046 | 0.44543 | 0.44597
WB | 50000001 | 7187 | 7187 GIN GIN - BUNDABERG T/LINE | 7187_Gin Gin - Bundaberg 132 kV | Rating (A) | 679 | 731 | 663 | 679 | 731 | 663 | 679 | 731 | 663 | 679 | 731 | 663 | 679 | 731 | 663
WB | 50000001 | 7187 | 7187 GIN GIN - BUNDABERG T/LINE | 7187_Gin Gin - Bundaberg 132 kV | Time | 16:30 | 18:30 | 4:30 | 16:30 | 18:30 | 4:30 | 16:30 | 18:30 | 4:30 | 16:30 | 18:30 | 4:30 | 16:30 | 18:30 | 4:30
WB | 50000001 | 7187 | 7187 GIN GIN - BUNDABERG T/LINE | 7187_Gin Gin - Bundaberg 132 kV | Voltage at Constrained Conductor | 139.3482 | 138.1816 | 138.1818 | 139.3527 | 138.2126 | 138.2128 | 139.2641 | 138.2253 | 138.2255 | 139.2354 | 138.2289 | 138.2292 | 139.2016 | 138.2204 | 138.2208
WB | 50000003 | 7215 | 7215 BUNDABERG - ISIS NO.1 | 7215_Bundaberg - ISIS No 1 132 kV | % of Rated A | 30.0231 | 33.2967 | 33.5755 | 30.5602 | 33.4092 | 33.6887 | 30.6815 | 32.9804 | 33.2566 | 30.5332 | 32.594 | 32.8672 | 30.3934 | 32.2446 | 32.5152
WB | 50000003 | 7215 | 7215 BUNDABERG - ISIS NO.1 | 7215_Bundaberg - ISIS No 1 132 kV | Limiting Line Name | TR_LINE 6780_1 | TR_LINE 6780_2 | TR_LINE 6780_2 | TR_LINE 6780_1 | TR_LINE 6780_2 | TR_LINE 6780_2 | TR_LINE 6780_1 | TR_LINE 6780_2 | TR_LINE 6780_2 | TR_LINE 6780_1 | TR_LINE 6780_2 | TR_LINE 6780_2 | TR_LINE 6780_1 | TR_LINE 6780_2 | TR_LINE 6780_2
WB | 50000003 | 7215 | 7215 BUNDABERG - ISIS NO.1 | 7215_Bundaberg - ISIS No 1 132 kV | Loading (A) | 74.4572 | 131.8551 | 131.9516 | 75.7892 | 132.3003 | 132.3967 | 76.0902 | 130.6022 | 130.6985 | 75.7223 | 129.0721 | 129.1682 | 75.3757 | 127.6885 | 127.7846
WB | 50000003 | 7215 | 7215 BUNDABERG - ISIS NO.1 | 7215_Bundaberg - ISIS No 1 132 kV | Loading (MVA) | 18.0823 | 32.2058 | 32.2294 | 18.4083 | 32.3464 | 32.37 | 18.4425 | 31.953 | 31.9766 | 18.3467 | 31.5949 | 31.6185 | 18.2552 | 31.2649 | 31.2885
WB | 50000003 | 7215 | 7215 BUNDABERG - ISIS NO.1 | 7215_Bundaberg - ISIS No 1 132 kV | Loading (MW) | 17.8272 | 30.8069 | 30.8294 | 18.0761 | 31.0604 | 31.0829 | 17.8191 | 30.7795 | 30.802 | 17.5629 | 30.5177 | 30.5401 | 17.3193 | 30.2672 | 30.2895
WB | 50000003 | 7215 | 7215 BUNDABERG - ISIS NO.1 | 7215_Bundaberg - ISIS No 1 132 kV | Power Factor | 0.98589 | 0.95657 | 0.95656 | 0.98195 | 0.96024 | 0.96024 | 0.96619 | 0.96328 | 0.96327 | 0.95728 | 0.96591 | 0.96589 | 0.94873 | 0.96809 | 0.96807
WB | 50000003 | 7215 | 7215 BUNDABERG - ISIS NO.1 | 7215_Bundaberg - ISIS No 1 132 kV | Rating (A) | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393
WB | 50000003 | 7215 | 7215 BUNDABERG - ISIS NO.1 | 7215_Bundaberg - ISIS No 1 132 kV | Time | 16:30 | 18:30 | 4:30 | 16:30 | 18:30 | 4:30 | 16:30 | 18:30 | 4:30 | 16:30 | 18:30 | 4:30 | 16:30 | 18:30 | 4:30
WB | 50000003 | 7215 | 7215 BUNDABERG - ISIS NO.1 | 7215_Bundaberg - ISIS No 1 132 kV | Voltage at Constrained Conductor | 140.2123 | 141.0185 | 141.0188 | 140.2317 | 141.1575 | 141.1579 | 139.9364 | 141.2537 | 141.2541 | 139.8856 | 141.3265 | 141.327 | 139.8282 | 141.3658 | 141.3664
WB | 50000006 | 786 | 786 GIN GIN - BUNDABERG T/LINE | 786_Gin Gin - Bundaberg 132 kV | % of Rated A | 33.5286 | 33.5993 | 33.5473 | 29.4596 | 30.994 | 30.9468 | 24.7708 | 28.3818 | 28.3392 | 21.9686 | 26.0766 | 26.0379 | 20.4792 | 24.1452 | 24.1094
WB | 50000006 | 786 | 786 GIN GIN - BUNDABERG T/LINE | 786_Gin Gin - Bundaberg 132 kV | Limiting Line Name | TR_LINE 112963_1 | TR_LINE 112963_1 | TR_LINE 112963_1 | TR_LINE 112963_1 | TR_LINE 112963_1 | TR_LINE 112963_1 | TR_LINE 112963_1 | TR_LINE 112963_1 | TR_LINE 112963_1 | TR_LINE 112963_1 | TR_LINE 112963_1 | TR_LINE 112963_1 | TR_LINE 112963_1 | TR_LINE 112963_1 | TR_LINE 112963_1
WB | 50000006 | 786 | 786 GIN GIN - BUNDABERG T/LINE | 786_Gin Gin - Bundaberg 132 kV | Loading (A) | 94.886 | 161.6125 | 161.6979 | 83.3706 | 149.081 | 149.1635 | 70.1013 | 136.5162 | 136.5952 | 62.1711 | 125.4282 | 125.5026 | 57.9562 | 116.1383 | 116.2073
WB | 50000006 | 786 | 786 GIN GIN - BUNDABERG T/LINE | 786_Gin Gin - Bundaberg 132 kV | Loading (MVA) | 22.9015 | 38.68 | 38.7004 | 20.1228 | 35.6887 | 35.7085 | 16.9093 | 32.6838 | 32.7027 | 14.9934 | 30.03 | 30.0478 | 13.9735 | 27.8041 | 27.8207
WB | 50000006 | 786 | 786 GIN GIN - BUNDABERG T/LINE | 786_Gin Gin - Bundaberg 132 kV | Loading (MW) | 15.02 | 28.1668 | 28.1898 | 10.9895 | 24.1071 | 24.13 | 6.8514 | 19.9184 | 19.9412 | 2.9142 | 15.9458 | 15.9685 | 0.64592 | 12.3501 | 12.3727
WB | 50000006 | 786 | 786 GIN GIN - BUNDABERG T/LINE | 786_Gin Gin - Bundaberg 132 kV | Power Factor | 0.65585 | 0.7282 | 0.72841 | 0.54612 | 0.67548 | 0.67575 | 0.40518 | 0.60943 | 0.60977 | 0.19437 | 0.531 | 0.53144 | 0.046224 | 0.44418 | 0.44473
WB | 50000006 | 786 | 786 GIN GIN - BUNDABERG T/LINE | 786_Gin Gin - Bundaberg 132 kV | Rating (A) | 283 | 481 | 482 | 283 | 481 | 482 | 283 | 481 | 482 | 283 | 481 | 482 | 283 | 481 | 482
WB | 50000006 | 786 | 786 GIN GIN - BUNDABERG T/LINE | 786_Gin Gin - Bundaberg 132 kV | Time | 16:30 | 18:30 | 4:30 | 16:30 | 18:30 | 4:30 | 16:30 | 18:30 | 4:30 | 16:30 | 18:30 | 4:30 | 16:30 | 18:30 | 4:30
WB | 50000006 | 786 | 786 GIN GIN - BUNDABERG T/LINE | 786_Gin Gin - Bundaberg 132 kV | Voltage at Constrained Conductor | 139.3482 | 138.1816 | 138.1818 | 139.3527 | 138.2126 | 138.2128 | 139.2641 | 138.2253 | 138.2255 | 139.2354 | 138.2289 | 138.2292 | 139.2016 | 138.2204 | 138.2208
WB | 50000008 | M029 | BUNDABERG - FARNSFIELD T/LINE | M029_Bundaberg - Farnsfield 66 kV | % of Rated A | 1.3055 | 1.0306 | 1.0843 | 1.3064 | 1.0317 | 1.085 | 1.305 | 1.0324 | 1.0853 | 1.3049 | 1.0328 | 1.0853 | 1.3046 | 1.0329 | 1.0849
WB | 50000008 | M029 | BUNDABERG - FARNSFIELD T/LINE | M029_Bundaberg - Farnsfield 66 kV | Limiting Line Name | TR_LINE 7163_1 | TR_LINE 7163_1 | TR_LINE 7163_1 | TR_LINE 7163_1 | TR_LINE 7163_1 | TR_LINE 7163_1 | TR_LINE 7163_1 | TR_LINE 7163_1 | TR_LINE 7163_1 | TR_LINE 7163_1 | TR_LINE 7163_1 | TR_LINE 7163_1 | TR_LINE 7163_1 | TR_LINE 7163_1 | TR_LINE 7163_1
WB | 50000008 | M029 | BUNDABERG - FARNSFIELD T/LINE | M029_Bundaberg - Farnsfield 66 kV | Loading (A) | 1.7233 | 1.7211 | 1.724 | 1.7245 | 1.723 | 1.7251 | 1.7226 | 1.7241 | 1.7256 | 1.7225 | 1.7248 | 1.7256 | 1.7221 | 1.7249 | 1.7249
WB | 50000008 | M029 | BUNDABERG - FARNSFIELD T/LINE | M029_Bundaberg - Farnsfield 66 kV | Loading (MVA) | 0.19873 | 0.19823 | 0.19889 | 0.19899 | 0.19865 | 0.19914 | 0.19857 | 0.19891 | 0.19926 | 0.19854 | 0.19907 | 0.19927 | 0.19845 | 0.19911 | 0.19911
WB | 50000008 | M029 | BUNDABERG - FARNSFIELD T/LINE | M029_Bundaberg - Farnsfield 66 kV | Loading (MW) | 2.1581e-05 | 2.1528e-05 | 2.1599e-05 | 2.161e-05 | 2.1573e-05 | 2.1626e-05 | 2.1564e-05 | 2.1601e-05 | 2.1639e-05 | 2.1561e-05 | 2.1619e-05 | 2.164e-05 | 2.1551e-05 | 2.1623e-05 | 2.1623e-05
WB | 50000008 | M029 | BUNDABERG - FARNSFIELD T/LINE | M029_Bundaberg - Farnsfield 66 kV | Power Factor | 0.0001086 | 0.0001086 | 0.0001086 | 0.0001086 | 0.0001086 | 0.0001086 | 0.0001086 | 0.0001086 | 0.0001086 | 0.0001086 | 0.0001086 | 0.0001086 | 0.0001086 | 0.0001086 | 0.0001086
WB | 50000008 | M029 | BUNDABERG - FARNSFIELD T/LINE | M029_Bundaberg - Farnsfield 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
WB | 50000008 | M029 | BUNDABERG - FARNSFIELD T/LINE | M029_Bundaberg - Farnsfield 66 kV | Time | 16:30 | 18:30 | 6:30 | 16:30 | 18:30 | 6:30 | 16:30 | 18:30 | 6:30 | 16:30 | 18:30 | 6:30 | 16:30 | 18:30 | 4:30
WB | 50000008 | M029 | BUNDABERG - FARNSFIELD T/LINE | M029_Bundaberg - Farnsfield 66 kV | Voltage at Constrained Conductor | 66.5788 | 66.4961 | 66.6055 | 66.6237 | 66.5662 | 66.648 | 66.5521 | 66.6094 | 66.6677 | 66.5482 | 66.637 | 66.6698 | 66.5327 | 66.6425 | 66.6428
WB | 50000009 | M036 | BBERG - STH BUNDABERG T/LINE | M036_Bundaberg-South Bundaberg 66 kV | % of Rated A | 17.5457 | 16.0354 | 19.8055 | 19.8709 | 18.1699 | 22.427 | 22.5159 | 20.5895 | 25.41 | 25.331 | 23.1884 | 28.611 | 28.0586 | 25.7043 | 31.7137
WB | 50000009 | M036 | BBERG - STH BUNDABERG T/LINE | M036_Bundaberg-South Bundaberg 66 kV | Limiting Line Name | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1
WB | 50000009 | M036 | BBERG - STH BUNDABERG T/LINE | M036_Bundaberg-South Bundaberg 66 kV | Loading (A) | 77.0254 | 76.9699 | 77.0434 | 86.1836 | 86.1673 | 86.1905 | 97.9573 | 97.9329 | 97.9574 | 110.4388 | 110.5509 | 110.5429 | 122.5097 | 122.7229 | 122.7083
WB | 50000009 | M036 | BBERG - STH BUNDABERG T/LINE | M036_Bundaberg-South Bundaberg 66 kV | Loading (MVA) | 8.8777 | 8.8603 | 8.8833 | 10.0662 | 10.0557 | 10.0706 | 11.3849 | 11.432 | 11.3847 | 12.8472 | 12.7918 | 12.7943 | 14.26 | 14.2113 | 14.2138
WB | 50000009 | M036 | BBERG - STH BUNDABERG T/LINE | M036_Bundaberg-South Bundaberg 66 kV | Loading (MW) | 4.6138 | 4.6124 | 4.6142 | 6.8934 | 6.8923 | 6.8938 | 8.9357 | 8.9411 | 8.9357 | 10.8626 | 10.8541 | 10.8545 | 12.6067 | 12.5985 | 12.5989
WB | 50000009 | M036 | BBERG - STH BUNDABERG T/LINE | M036_Bundaberg-South Bundaberg 66 kV | Power Factor | 0.5197 | 0.52057 | 0.51943 | 0.6848 | 0.68542 | 0.68454 | 0.78487 | 0.78211 | 0.78489 | 0.84552 | 0.84852 | 0.84838 | 0.88407 | 0.88651 | 0.88638
WB | 50000009 | M036 | BBERG - STH BUNDABERG T/LINE | M036_Bundaberg-South Bundaberg 66 kV | Rating (A) | 439 | 480 | 389 | 439 | 480 | 389 | 439 | 480 | 389 | 439 | 480 | 389 | 439 | 480 | 389
WB | 50000009 | M036 | BBERG - STH BUNDABERG T/LINE | M036_Bundaberg-South Bundaberg 66 kV | Time | 16:30 | 18:30 | 6:30 | 16:30 | 18:30 | 6:30 | 9:00 | 19:00 | 8:30 | 9:00 | 17:00 | 6:00 | 9:00 | 17:00 | 6:00
WB | 50000009 | M036 | BBERG - STH BUNDABERG T/LINE | M036_Bundaberg-South Bundaberg 66 kV | Voltage at Constrained Conductor | 66.5434 | 66.4607 | 66.5701 | 67.4342 | 67.3764 | 67.4586 | 67.1013 | 67.3958 | 67.1001 | 67.1625 | 66.8049 | 66.8229 | 67.2028 | 66.8571 | 66.8768
WB | 50000018 | M046 | TARONG-CABOONBAH T/LINE | M046_Tarong-Caboonbah 66 kV | % of Rated A | 29.039 | 18.933 | 19.6017 | 29.0353 | 18.9303 | 19.599 | 29.3831 | 19.1567 | 19.831 | 29.7287 | 19.3819 | 20.0617 | 29.7266 | 19.3804 | 20.0602
WB | 50000018 | M046 | TARONG-CABOONBAH T/LINE | M046_Tarong-Caboonbah 66 kV | Limiting Line Name | TR_LINE 9243_1 | TR_LINE 9243_1 | TR_LINE 7833_1 | TR_LINE 9243_1 | TR_LINE 9243_1 | TR_LINE 7833_1 | TR_LINE 9243_1 | TR_LINE 9243_1 | TR_LINE 7833_1 | TR_LINE 9243_1 | TR_LINE 9243_1 | TR_LINE 7833_1 | TR_LINE 9243_1 | TR_LINE 9243_1 | TR_LINE 7833_1
WB | 50000018 | M046 | TARONG-CABOONBAH T/LINE | M046_Tarong-Caboonbah 66 kV | Loading (A) | 72.3071 | 72.3239 | 72.5263 | 72.298 | 72.3139 | 72.5164 | 73.1638 | 73.1788 | 73.3748 | 74.0245 | 74.039 | 74.2284 | 74.0192 | 74.0331 | 74.2226
WB | 50000018 | M046 | TARONG-CABOONBAH T/LINE | M046_Tarong-Caboonbah 66 kV | Loading (MVA) | 8.5765 | 8.5765 | 8.7036 | 8.5765 | 8.5765 | 8.7036 | 8.6784 | 8.6785 | 8.8075 | 8.7796 | 8.7796 | 8.9107 | 8.7796 | 8.7796 | 8.9107
WB | 50000018 | M046 | TARONG-CABOONBAH T/LINE | M046_Tarong-Caboonbah 66 kV | Loading (MW) | 8.5675 | 8.5676 | 8.6818 | 8.5675 | 8.5675 | 8.6817 | 8.6699 | 8.6699 | 8.7869 | 8.7715 | 8.7715 | 8.8912 | 8.7715 | 8.7715 | 8.8912
WB | 50000018 | M046 | TARONG-CABOONBAH T/LINE | M046_Tarong-Caboonbah 66 kV | Power Factor | 0.99895 | 0.99895 | 0.9975 | 0.99895 | 0.99895 | 0.99749 | 0.99902 | 0.99902 | 0.99766 | 0.99908 | 0.99908 | 0.99781 | 0.99908 | 0.99908 | 0.99781
WB | 50000018 | M046 | TARONG-CABOONBAH T/LINE | M046_Tarong-Caboonbah 66 kV | Rating (A) | 249 | 382 | 370 | 249 | 382 | 370 | 249 | 382 | 370 | 249 | 382 | 370 | 249 | 382 | 370
WB | 50000018 | M046 | TARONG-CABOONBAH T/LINE | M046_Tarong-Caboonbah 66 kV | Time | 16:30 | 18:00 | 4:30 | 16:30 | 18:00 | 4:30 | 16:30 | 18:00 | 4:30 | 16:30 | 18:00 | 4:30 | 16:30 | 18:00 | 4:30
WB | 50000018 | M046 | TARONG-CABOONBAH T/LINE | M046_Tarong-Caboonbah 66 kV | Voltage at Constrained Conductor | 68.4811 | 68.4652 | 69.2854 | 68.4896 | 68.4746 | 69.2947 | 68.4833 | 68.4694 | 69.3022 | 68.4757 | 68.4624 | 69.308 | 68.4806 | 68.4679 | 69.3133
WB | 50000048 | M030 | FARNSFIELD - CHILDERS T/LINE | M030_Farnsfield - Childers 66 kV | % of Rated A | 16.8084 | 13.5543 | 14.2365 | 16.9149 | 13.644 | 14.331 | 17.3883 | 13.7139 | 14.4112 | 17.1606 | 13.8039 | 14.5062 | 17.2436 | 13.8772 | 14.5836
WB | 50000048 | M030 | FARNSFIELD - CHILDERS T/LINE | M030_Farnsfield - Childers 66 kV | Limiting Line Name | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1
WB | 50000048 | M030 | FARNSFIELD - CHILDERS T/LINE | M030_Farnsfield - Childers 66 kV | Loading (A) | 22.1871 | 22.6357 | 22.636 | 22.3276 | 22.7855 | 22.7863 | 22.9526 | 22.9023 | 22.9139 | 22.652 | 23.0525 | 23.0649 | 22.7615 | 23.175 | 23.188
WB | 50000048 | M030 | FARNSFIELD - CHILDERS T/LINE | M030_Farnsfield - Childers 66 kV | Loading (MVA) | 2.6733 | 2.719 | 2.7191 | 2.6917 | 2.7398 | 2.74 | 2.7625 | 2.75 | 2.7529 | 2.7345 | 2.7687 | 2.7718 | 2.7463 | 2.7837 | 2.787
WB | 50000048 | M030 | FARNSFIELD - CHILDERS T/LINE | M030_Farnsfield - Childers 66 kV | Loading (MW) | 0.20225 | 0.20204 | 0.20204 | 0.35056 | 0.35034 | 0.35034 | 0.46843 | 0.46846 | 0.46845 | 0.56241 | 0.56222 | 0.56221 | 0.62996 | 0.62976 | 0.62975
WB | 50000048 | M030 | FARNSFIELD - CHILDERS T/LINE | M030_Farnsfield - Childers 66 kV | Power Factor | 0.075656 | 0.074306 | 0.074304 | 0.13024 | 0.12787 | 0.12786 | 0.16957 | 0.17035 | 0.17017 | 0.20567 | 0.20307 | 0.20284 | 0.22939 | 0.22623 | 0.22596
WB | 50000048 | M030 | FARNSFIELD - CHILDERS T/LINE | M030_Farnsfield - Childers 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
WB | 50000048 | M030 | FARNSFIELD - CHILDERS T/LINE | M030_Farnsfield - Childers 66 kV | Time | 12:30 | 17:30 | 5:30 | 16:30 | 17:30 | 5:30 | 16:30 | 17:00 | 6:00 | 16:00 | 17:00 | 6:00 | 16:00 | 17:00 | 6:00
WB | 50000048 | M030 | FARNSFIELD - CHILDERS T/LINE | M030_Farnsfield - Childers 66 kV | Voltage at Constrained Conductor | 69.5646 | 69.3512 | 69.3521 | 69.6017 | 69.4218 | 69.4244 | 69.4872 | 69.3253 | 69.3627 | 69.6977 | 69.3412 | 69.3819 | 69.6592 | 69.3498 | 69.393
WB | 50000069 | M024 | GAYNDAH - MUNDUBBERA T/LINE | M024_Gayndah - Mundubbera 66 kV | % of Rated A | 20.7787 | 15.7434 | 16.3918 | 20.9111 | 15.5508 | 16.2309 | 21.3017 | 15.8497 | 16.5373 | 21.742 | 16.2023 | 16.8846 | 22.5248 | 16.7994 | 17.5001
WB | 50000069 | M024 | GAYNDAH - MUNDUBBERA T/LINE | M024_Gayndah - Mundubbera 66 kV | Limiting Line Name | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1
WB | 50000069 | M024 | GAYNDAH - MUNDUBBERA T/LINE | M024_Gayndah - Mundubbera 66 kV | Loading (A) | 27.4279 | 27.8657 | 27.8661 | 27.6026 | 27.5249 | 27.5925 | 28.1183 | 28.054 | 28.1135 | 28.6994 | 28.678 | 28.7039 | 29.7328 | 29.735 | 29.7502
WB | 50000069 | M024 | GAYNDAH - MUNDUBBERA T/LINE | M024_Gayndah - Mundubbera 66 kV | Loading (MVA) | 3.1928 | 3.2336 | 3.2337 | 3.2224 | 3.2041 | 3.22 | 3.2835 | 3.2678 | 3.2825 | 3.3175 | 3.312 | 3.3187 | 3.4419 | 3.4426 | 3.4469
WB | 50000069 | M024 | GAYNDAH - MUNDUBBERA T/LINE | M024_Gayndah - Mundubbera 66 kV | Loading (MW) | 0.19331 | 0.19434 | 0.19434 | 0.24737 | 0.24754 | 0.24739 | 0.65139 | 0.65152 | 0.65138 | 1.0306 | 1.0306 | 1.0306 | 1.3651 | 1.3651 | 1.3651
WB | 50000069 | M024 | GAYNDAH - MUNDUBBERA T/LINE | M024_Gayndah - Mundubbera 66 kV | Power Factor | 0.060548 | 0.060101 | 0.0601 | 0.076766 | 0.077256 | 0.076829 | 0.19838 | 0.19937 | 0.19844 | 0.31065 | 0.31118 | 0.31054 | 0.39662 | 0.39655 | 0.39604
WB | 50000069 | M024 | GAYNDAH - MUNDUBBERA T/LINE | M024_Gayndah - Mundubbera 66 kV | Rating (A) | 132 | 177 | 170 | 132 | 177 | 170 | 132 | 177 | 170 | 132 | 177 | 170 | 132 | 177 | 170
WB | 50000069 | M024 | GAYNDAH - MUNDUBBERA T/LINE | M024_Gayndah - Mundubbera 66 kV | Time | 12:30 | 17:30 | 5:30 | 16:30 | 17:30 | 7:30 | 16:30 | 17:00 | 5:30 | 16:00 | 18:00 | 6:30 | 16:00 | 18:00 | 7:00
WB | 50000069 | M024 | GAYNDAH - MUNDUBBERA T/LINE | M024_Gayndah - Mundubbera 66 kV | Voltage at Constrained Conductor | 67.2065 | 66.9963 | 66.9973 | 67.401 | 67.2083 | 67.376 | 67.4204 | 67.2523 | 67.4104 | 66.7392 | 66.6775 | 66.752 | 66.8354 | 66.8426 | 66.8918
WB | 50000079 | M027 | ISIS - CHILDERS 66KV FDR | M027_ISIS - Childers 66 kV | % of Rated A | 83.4318 | 81.7639 | 92.5958 | 86.6438 | 84.8845 | 96.1297 | 89.721 | 87.7069 | 99.3259 | 92.5413 | 90.6392 | 102.647 | 95.1078 | 93.0781 | 105.4089
WB | 50000079 | M027 | ISIS - CHILDERS 66KV FDR | M027_ISIS - Childers 66 kV | Limiting Line Name | TR_LINE 183684_1 | TR_LINE 183684_1 | TR_LINE 183684_1 | TR_LINE 183684_1 | TR_LINE 183684_1 | TR_LINE 183684_1 | TR_LINE 183684_1 | TR_LINE 183684_1 | TR_LINE 183684_1 | TR_LINE 183684_1 | TR_LINE 183684_1 | TR_LINE 183684_1 | TR_LINE 183684_1 | TR_LINE 183684_1 | TR_LINE 183684_1
WB | 50000079 | M027 | ISIS - CHILDERS 66KV FDR | M027_ISIS - Childers 66 kV | Loading (A) | 215.194 | 216.6159 | 216.6155 | 223.4835 | 224.8872 | 224.8867 | 231.4248 | 232.3692 | 232.3685 | 238.7045 | 240.1425 | 240.1425 | 245.3282 | 246.608 | 246.608
WB | 50000079 | M027 | ISIS - CHILDERS 66KV FDR | M027_ISIS - Childers 66 kV | Loading (MVA) | 25.7913 | 25.7612 | 25.7613 | 26.7917 | 26.7764 | 26.7765 | 27.7169 | 27.6861 | 27.6861 | 28.5802 | 28.5671 | 28.5671 | 29.3668 | 29.3469 | 29.3469
WB | 50000079 | M027 | ISIS - CHILDERS 66KV FDR | M027_ISIS - Childers 66 kV | Loading (MW) | 25.3035 | 25.2919 | 25.2919 | 26.3291 | 26.3186 | 26.3186 | 27.2692 | 27.2565 | 27.2565 | 28.1724 | 28.1627 | 28.1627 | 28.9788 | 28.9706 | 28.9706
WB | 50000079 | M027 | ISIS - CHILDERS 66KV FDR | M027_ISIS - Childers 66 kV | Power Factor | 0.98109 | 0.98178 | 0.98178 | 0.98273 | 0.9829 | 0.9829 | 0.98384 | 0.98448 | 0.98448 | 0.98573 | 0.98585 | 0.98585 | 0.98679 | 0.98718 | 0.98718
WB | 50000079 | M027 | ISIS - CHILDERS 66KV FDR | M027_ISIS - Childers 66 kV | Rating (A) | 258 | 265 | 234 | 258 | 265 | 234 | 258 | 265 | 234 | 258 | 265 | 234 | 258 | 265 | 234
WB | 50000079 | M027 | ISIS - CHILDERS 66KV FDR | M027_ISIS - Childers 66 kV | Time | 16:00 | 18:30 | 5:00 | 16:00 | 18:30 | 5:00 | 16:30 | 18:30 | 5:00 | 16:30 | 19:00 | 0:00 | 16:30 | 19:00 | 0:00
WB | 50000079 | M027 | ISIS - CHILDERS 66KV FDR | M027_ISIS - Childers 66 kV | Voltage at Constrained Conductor | 69.1963 | 68.6619 | 68.662 | 69.2141 | 68.7429 | 68.743 | 69.1472 | 68.7896 | 68.7899 | 69.1265 | 68.681 | 68.681 | 69.1112 | 68.7059 | 68.7059
WB | 50000080 | M049 | ISIS - GAYNDAH 66KV FDR | M049_ISIS - Gayndah 66 kV | % of Rated A | 15.9311 | 15.3937 | 17.2613 | 15.003 | 14.4759 | 16.2365 | 14.168 | 13.6349 | 15.2897 | 13.1759 | 12.6976 | 14.2419 | 12.7707 | 12.3432 | 13.8444
WB | 50000080 | M049 | ISIS - GAYNDAH 66KV FDR | M049_ISIS - Gayndah 66 kV | Limiting Line Name | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 33779_1 | TR_LINE 33779_1 | TR_LINE 33779_1
WB | 50000080 | M049 | ISIS - GAYNDAH 66KV FDR | M049_ISIS - Gayndah 66 kV | Loading (A) | 63.5651 | 63.884 | 63.8669 | 59.8621 | 60.075 | 60.0749 | 56.5303 | 56.585 | 56.572 | 52.572 | 52.6949 | 52.6949 | 50.955 | 51.2243 | 51.2243
WB | 50000080 | M049 | ISIS - GAYNDAH 66KV FDR | M049_ISIS - Gayndah 66 kV | Loading (MVA) | 7.4902 | 7.4945 | 7.4961 | 7.0523 | 7.0277 | 7.0277 | 6.65 | 6.6405 | 6.6426 | 6.1804 | 6.1535 | 6.1535 | 5.9848 | 5.9786 | 5.9786
WB | 50000080 | M049 | ISIS - GAYNDAH 66KV FDR | M049_ISIS - Gayndah 66 kV | Loading (MW) | 7.0296 | 7.0343 | 7.0344 | 6.5195 | 6.5175 | 6.5175 | 6.0459 | 6.0452 | 6.0453 | 5.5108 | 5.5088 | 5.5088 | 5.6319 | 5.6365 | 5.6365
WB | 50000080 | M049 | ISIS - GAYNDAH 66KV FDR | M049_ISIS - Gayndah 66 kV | Power Factor | 0.93852 | 0.93859 | 0.9384 | 0.92444 | 0.92741 | 0.92741 | 0.90915 | 0.91035 | 0.91008 | 0.89166 | 0.89522 | 0.89522 | 0.94104 | 0.94279 | 0.94279
WB | 50000080 | M049 | ISIS - GAYNDAH 66KV FDR | M049_ISIS - Gayndah 66 kV | Rating (A) | 399 | 415 | 370 | 399 | 415 | 370 | 399 | 415 | 370 | 399 | 415 | 370 | 399 | 415 | 370
WB | 50000080 | M049 | ISIS - GAYNDAH 66KV FDR | M049_ISIS - Gayndah 66 kV | Time | 16:00 | 17:00 | 6:00 | 16:00 | 18:30 | 5:00 | 16:30 | 17:00 | 6:00 | 16:30 | 19:00 | 0:00 | 16:30 | 19:00 | 0:00
WB | 50000080 | M049 | ISIS - GAYNDAH 66KV FDR | M049_ISIS - Gayndah 66 kV | Voltage at Constrained Conductor | 68.0317 | 67.7315 | 67.7644 | 68.0173 | 67.5392 | 67.5394 | 67.9176 | 67.7544 | 67.7921 | 67.8736 | 67.421 | 67.421 | 67.8113 | 67.3847 | 67.3847
WB | 50000081 | M022 | HOWARD TEE ISIS RIVER 66KV FDR | M022_Howard - ISIS 66 kV | % of Rated A | 101.8697 | 49.305 | 107.7792 | 103.4832 | 50.5412 | 109.4777 | 104.8449 | 51.759 | 110.912 | 106.118 | 52.9667 | 112.253 | 107.1917 | 54.1017 | 113.3845
WB | 50000081 | M022 | HOWARD TEE ISIS RIVER 66KV FDR | M022_Howard - ISIS 66 kV | Limiting Line Name | TR_LINE 118970_3 | TR_LINE 118970_3 | TR_LINE 118970_3 | TR_LINE 118970_3 | TR_LINE 118970_3 | TR_LINE 118970_3 | TR_LINE 118970_3 | TR_LINE 118970_3 | TR_LINE 118970_3 | TR_LINE 118970_3 | TR_LINE 118970_3 | TR_LINE 118970_3 | TR_LINE 118970_3 | TR_LINE 118970_3 | TR_LINE 118970_3
WB | 50000081 | M022 | HOWARD TEE ISIS RIVER 66KV FDR | M022_Howard - ISIS 66 kV | Loading (A) | 558.0126 | 285.1387 | 561.2976 | 566.8578 | 292.3033 | 570.1498 | 574.3241 | 299.3608 | 577.6269 | 581.305 | 306.3591 | 584.6176 | 587.1926 | 312.9363 | 590.5164
WB | 50000081 | M022 | HOWARD TEE ISIS RIVER 66KV FDR | M022_Howard - ISIS 66 kV | Loading (MVA) | 65.5383 | 33.3023 | 65.9209 | 66.5685 | 34.1495 | 66.9519 | 67.4312 | 34.9787 | 67.8157 | 68.2367 | 35.7887 | 68.6221 | 68.9112 | 36.5463 | 69.2978
WB | 50000081 | M022 | HOWARD TEE ISIS RIVER 66KV FDR | M022_Howard - ISIS 66 kV | Loading (MW) | 55.6917 | 21.7596 | 56.1132 | 56.8611 | 22.9376 | 57.2825 | 57.963 | 24.0412 | 58.3843 | 58.9987 | 25.0773 | 59.42 | 59.9416 | 26.0165 | 60.3629
WB | 50000081 | M022 | HOWARD TEE ISIS RIVER 66KV FDR | M022_Howard - ISIS 66 kV | Power Factor | 0.84976 | 0.6534 | 0.85122 | 0.85417 | 0.67168 | 0.85558 | 0.85959 | 0.68731 | 0.86093 | 0.86462 | 0.7007 | 0.8659 | 0.86984 | 0.71188 | 0.87107
WB | 50000081 | M022 | HOWARD TEE ISIS RIVER 66KV FDR | M022_Howard - ISIS 66 kV | Rating (A) | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521
WB | 50000081 | M022 | HOWARD TEE ISIS RIVER 66KV FDR | M022_Howard - ISIS 66 kV | Time | 9:00 | 17:00 | 8:30 | 9:00 | 17:00 | 8:30 | 9:00 | 17:00 | 8:30 | 9:00 | 17:00 | 8:30 | 9:00 | 17:00 | 8:30
WB | 50000081 | M022 | HOWARD TEE ISIS RIVER 66KV FDR | M022_Howard - ISIS 66 kV | Voltage at Constrained Conductor | 67.8095 | 67.4307 | 67.8062 | 67.8007 | 67.4513 | 67.7974 | 67.7865 | 67.4603 | 67.7832 | 67.7724 | 67.4458 | 67.7691 | 67.7561 | 67.4259 | 67.7527
WB | 50000088 | M001 | TARONG - KINGAROY EAST T/LINE | M001_Tarong-Kingaroy East 66 kV | % of Rated A | 3.7474 | 3.5471 | 3.9419 | 2.5143 | 2.3796 | 2.6446 | 1.9114 | 1.8087 | 2.0105 | 2.3074 | 2.1836 | 2.4269 | 3.2534 | 3.0793 | 3.4221
WB | 50000088 | M001 | TARONG - KINGAROY EAST T/LINE | M001_Tarong-Kingaroy East 66 kV | Limiting Line Name | TR_LINE 7977_1 | TR_LINE 7977_1 | TR_LINE 7977_1 | TR_LINE 7977_1 | TR_LINE 7977_1 | TR_LINE 7977_1 | TR_LINE 7977_1 | TR_LINE 7977_1 | TR_LINE 7977_1 | TR_LINE 7977_1 | TR_LINE 7977_1 | TR_LINE 7977_1 | TR_LINE 7977_1 | TR_LINE 7977_1 | TR_LINE 7977_1
WB | 50000088 | M001 | TARONG - KINGAROY EAST T/LINE | M001_Tarong-Kingaroy East 66 kV | Loading (A) | 20.5355 | 20.5376 | 20.5375 | 13.7786 | 13.7779 | 13.7786 | 10.4747 | 10.4724 | 10.4747 | 12.6444 | 12.6432 | 12.6444 | 17.8284 | 17.8291 | 17.8291
WB | 50000088 | M001 | TARONG - KINGAROY EAST T/LINE | M001_Tarong-Kingaroy East 66 kV | Loading (MVA) | 2.4649 | 2.4646 | 2.4646 | 1.6542 | 1.6538 | 1.6542 | 1.2577 | 1.2572 | 1.2577 | 1.5183 | 1.5179 | 1.5183 | 2.1407 | 2.1404 | 2.1405
WB | 50000088 | M001 | TARONG - KINGAROY EAST T/LINE | M001_Tarong-Kingaroy East 66 kV | Loading (MW) | 2.1306 | 2.1306 | 2.1306 | 1.0781 | 1.0781 | 1.0781 | 0.08494 | 0.084947 | 0.08494 | 0.87328 | 0.87327 | 0.87328 | 1.7595 | 1.7595 | 1.7595
WB | 50000088 | M001 | TARONG - KINGAROY EAST T/LINE | M001_Tarong-Kingaroy East 66 kV | Power Factor | 0.86437 | 0.86448 | 0.86448 | 0.65175 | 0.6519 | 0.65175 | 0.067537 | 0.067569 | 0.067537 | 0.57516 | 0.57531 | 0.57516 | 0.82193 | 0.82204 | 0.82204
WB | 50000088 | M001 | TARONG - KINGAROY EAST T/LINE | M001_Tarong-Kingaroy East 66 kV | Rating (A) | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521
WB | 50000088 | M001 | TARONG - KINGAROY EAST T/LINE | M001_Tarong-Kingaroy East 66 kV | Time | 16:30 | 18:00 | 4:30 | 9:00 | 17:00 | 8:30 | 9:00 | 17:00 | 8:30 | 9:00 | 17:00 | 8:30 | 16:30 | 18:00 | 4:30
WB | 50000088 | M001 | TARONG - KINGAROY EAST T/LINE | M001_Tarong-Kingaroy East 66 kV | Voltage at Constrained Conductor | 69.3005 | 69.2849 | 69.2854 | 69.3154 | 69.3024 | 69.3155 | 69.3219 | 69.3095 | 69.3219 | 69.3268 | 69.3147 | 69.3268 | 69.3254 | 69.3129 | 69.3133
WB | 50000089 | M002 | TARONG - KINGAROY WEST T/LINE | M002_Tarong-Kingaroy West 66 kV | % of Rated A | 3.7466 | 3.5463 | 3.9411 | 2.5113 | 2.3767 | 2.6414 | 1.9065 | 1.8041 | 2.0053 | 2.3038 | 2.1803 | 2.4232 | 3.2519 | 3.0779 | 3.4205
WB | 50000089 | M002 | TARONG - KINGAROY WEST T/LINE | M002_Tarong-Kingaroy West 66 kV | Limiting Line Name | TR_LINE 7252_2 | TR_LINE 7252_2 | TR_LINE 7252_2 | TR_LINE 7252_2 | TR_LINE 7252_2 | TR_LINE 7252_2 | TR_LINE 7252_2 | TR_LINE 7252_2 | TR_LINE 7252_2 | TR_LINE 7252_2 | TR_LINE 7252_2 | TR_LINE 7252_2 | TR_LINE 7252_2 | TR_LINE 7252_2 | TR_LINE 7252_2
WB | 50000089 | M002 | TARONG - KINGAROY WEST T/LINE | M002_Tarong-Kingaroy West 66 kV | Loading (A) | 20.5312 | 20.5333 | 20.5332 | 13.7617 | 13.7611 | 13.7617 | 10.4478 | 10.4456 | 10.4478 | 12.6248 | 12.6237 | 12.6248 | 17.8202 | 17.8209 | 17.8209
WB | 50000089 | M002 | TARONG - KINGAROY WEST T/LINE | M002_Tarong-Kingaroy West 66 kV | Loading (MVA) | 2.4644 | 2.4641 | 2.4641 | 1.6522 | 1.6518 | 1.6522 | 1.2545 | 1.254 | 1.2545 | 1.516 | 1.5156 | 1.516 | 2.1398 | 2.1395 | 2.1395
WB | 50000089 | M002 | TARONG - KINGAROY WEST T/LINE | M002_Tarong-Kingaroy West 66 kV | Loading (MW) | 2.1319 | 2.1319 | 2.1319 | 1.0788 | 1.0788 | 1.0788 | 0.08496 | 0.084967 | 0.08496 | 0.87383 | 0.87382 | 0.87383 | 1.7606 | 1.7606 | 1.7606
WB | 50000089 | M002 | TARONG - KINGAROY WEST T/LINE | M002_Tarong-Kingaroy West 66 kV | Power Factor | 0.86506 | 0.86517 | 0.86517 | 0.65292 | 0.65308 | 0.65292 | 0.067726 | 0.067758 | 0.067726 | 0.57642 | 0.57657 | 0.57642 | 0.82282 | 0.82293 | 0.82292
WB | 50000089 | M002 | TARONG - KINGAROY WEST T/LINE | M002_Tarong-Kingaroy West 66 kV | Rating (A) | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521
WB | 50000089 | M002 | TARONG - KINGAROY WEST T/LINE | M002_Tarong-Kingaroy West 66 kV | Time | 16:30 | 18:00 | 4:30 | 9:00 | 17:00 | 8:30 | 9:00 | 17:00 | 8:30 | 9:00 | 17:00 | 8:30 | 16:30 | 18:00 | 4:30
WB | 50000089 | M002 | TARONG - KINGAROY WEST T/LINE | M002_Tarong-Kingaroy West 66 kV | Voltage at Constrained Conductor | 69.3005 | 69.2849 | 69.2854 | 69.3154 | 69.3024 | 69.3155 | 69.3219 | 69.3095 | 69.3219 | 69.3268 | 69.3147 | 69.3268 | 69.3254 | 69.3129 | 69.3133
WB | 50000100 | T014 | 66KV MARY-PIAL TEE HOWA FDR | T014_Maryborough-Pialba Tee Howard 66 kV | % of Rated A | 15.3467 | 10.2588 | 16.9658 | 19.2185 | 12.7923 | 21.2477 | 22.8199 | 15.672 | 25.2305 | 26.2044 | 18.4839 | 28.9737 | 29.2644 | 21.0933 | 32.358
WB | 50000100 | T014 | 66KV MARY-PIAL TEE HOWA FDR | T014_Maryborough-Pialba Tee Howard 66 kV | Limiting Line Name | TR_LINE 224569_1 | TR_LINE 224569_1 | TR_LINE 224569_1 | TR_LINE 224569_1 | TR_LINE 224569_1 | TR_LINE 224569_1 | TR_LINE 224569_1 | TR_LINE 224569_1 | TR_LINE 224569_1 | TR_LINE 224569_1 | TR_LINE 224569_1 | TR_LINE 224569_1 | TR_LINE 224569_1 | TR_LINE 224569_1 | TR_LINE 224569_1
WB | 50000100 | T014 | 66KV MARY-PIAL TEE HOWA FDR | T014_Maryborough-Pialba Tee Howard 66 kV | Loading (A) | 92.781 | 68.529 | 92.7366 | 116.2177 | 85.4524 | 116.1703 | 138.0136 | 104.6003 | 137.9644 | 158.4958 | 123.3975 | 158.4453 | 177.0129 | 140.8378 | 176.9614
WB | 50000100 | T014 | 66KV MARY-PIAL TEE HOWA FDR | T014_Maryborough-Pialba Tee Howard 66 kV | Loading (MVA) | 11.1454 | 8.2059 | 11.1401 | 13.9775 | 10.2756 | 13.9719 | 16.6151 | 12.6102 | 16.6092 | 19.0941 | 14.8911 | 19.088 | 21.3325 | 17.009 | 21.3263
WB | 50000100 | T014 | 66KV MARY-PIAL TEE HOWA FDR | T014_Maryborough-Pialba Tee Howard 66 kV | Loading (MW) | 10.4754 | 2.9882 | 10.4686 | 13.4204 | 8.5265 | 13.4136 | 16.1319 | 11.2305 | 16.125 | 18.6629 | 13.7513 | 18.656 | 20.9435 | 16.0221 | 20.9366
WB | 50000100 | T014 | 66KV MARY-PIAL TEE HOWA FDR | T014_Maryborough-Pialba Tee Howard 66 kV | Power Factor | 0.93988 | 0.36415 | 0.93972 | 0.96014 | 0.82978 | 0.96004 | 0.97092 | 0.89058 | 0.97085 | 0.97742 | 0.92346 | 0.97737 | 0.98177 | 0.94198 | 0.98173
WB | 50000100 | T014 | 66KV MARY-PIAL TEE HOWA FDR | T014_Maryborough-Pialba Tee Howard 66 kV | Rating (A) | 605 | 668 | 547 | 605 | 668 | 547 | 605 | 668 | 547 | 605 | 668 | 547 | 605 | 668 | 547
WB | 50000100 | T014 | 66KV MARY-PIAL TEE HOWA FDR | T014_Maryborough-Pialba Tee Howard 66 kV | Time | 9:00 | 19:00 | 8:30 | 9:00 | 17:00 | 8:30 | 9:00 | 17:00 | 8:30 | 9:00 | 17:00 | 8:30 | 9:00 | 17:00 | 8:30
WB | 50000100 | T014 | 66KV MARY-PIAL TEE HOWA FDR | T014_Maryborough-Pialba Tee Howard 66 kV | Voltage at Constrained Conductor | 69.3547 | 69.1341 | 69.3548 | 69.4382 | 69.426 | 69.4383 | 69.5055 | 69.6031 | 69.5057 | 69.5537 | 69.6722 | 69.5538 | 69.5785 | 69.7266 | 69.5786
WB | 50000102 | M012 | MARYBOROUGH- ROCKY ST T/LINE | M012_Maryborough-Rocky St 66 kV | % of Rated A | 11.9525 | 11.2957 | 12.5739 | 10.6129 | 10.0266 | 11.1428 | 9.6909 | 9.1712 | 10.1842 | 9.2932 | 8.7902 | 9.7612 | 9.3534 | 8.8445 | 9.8377
WB | 50000102 | M012 | MARYBOROUGH- ROCKY ST T/LINE | M012_Maryborough-Rocky St 66 kV | Limiting Line Name | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1
WB | 50000102 | M012 | MARYBOROUGH- ROCKY ST T/LINE | M012_Maryborough-Rocky St 66 kV | Loading (A) | 65.4995 | 65.4023 | 65.51 | 58.1589 | 58.0539 | 58.0539 | 53.1059 | 53.1012 | 53.0595 | 50.9267 | 50.8951 | 50.8556 | 51.2566 | 51.2099 | 51.2543
WB | 50000102 | M012 | MARYBOROUGH- ROCKY ST T/LINE | M012_Maryborough-Rocky St 66 kV | Loading (MVA) | 7.7169 | 7.6844 | 7.7224 | 6.8509 | 6.8283 | 6.8283 | 6.2915 | 6.2904 | 6.2867 | 6.0312 | 6.0296 | 6.0151 | 6.0719 | 6.0665 | 6.0713
WB | 50000102 | M012 | MARYBOROUGH- ROCKY ST T/LINE | M012_Maryborough-Rocky St 66 kV | Loading (MW) | 4.7852 | 4.7838 | 4.7852 | 3.1799 | 3.1785 | 3.1785 | 1.7365 | 1.7365 | 1.7352 | 0.32151 | 0.32022 | 0.32146 | 0.97887 | 0.98017 | 0.97887
WB | 50000102 | M012 | MARYBOROUGH- ROCKY ST T/LINE | M012_Maryborough-Rocky St 66 kV | Power Factor | 0.62009 | 0.62253 | 0.61965 | 0.46415 | 0.46549 | 0.46549 | 0.276 | 0.27605 | 0.27601 | 0.053309 | 0.053108 | 0.053443 | 0.16121 | 0.16157 | 0.16123
WB | 50000102 | M012 | MARYBOROUGH- ROCKY ST T/LINE | M012_Maryborough-Rocky St 66 kV | Rating (A) | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521
WB | 50000102 | M012 | MARYBOROUGH- ROCKY ST T/LINE | M012_Maryborough-Rocky St 66 kV | Time | 16:30 | 19:00 | 6:30 | 16:30 | 19:00 | 0:00 | 16:30 | 17:30 | 5:30 | 16:30 | 17:30 | 7:30 | 16:00 | 17:30 | 6:30
WB | 50000102 | M012 | MARYBOROUGH- ROCKY ST T/LINE | M012_Maryborough-Rocky St 66 kV | Voltage at Constrained Conductor | 68.0207 | 67.8355 | 68.0588 | 68.01 | 67.9076 | 67.9076 | 68.3993 | 68.3934 | 68.4067 | 68.3749 | 68.399 | 68.2875 | 68.3929 | 68.3952 | 68.3901
WB | 50000103 | TORQUAY TEE | 66KV TORQUAY TEE FDR T015 | M020_Maryborough-Torquay 66 kV | % of Rated A | 88.3562 | 31.8416 | 92.8258 | 91.232 | 34.7014 | 95.8497 | 93.8751 | 37.36 | 98.6291 | 96.3048 | 39.7759 | 101.184 | 98.4596 | 41.9179 | 103.4498
WB | 50000103 | TORQUAY TEE | 66KV TORQUAY TEE FDR T015 | M020_Maryborough-Torquay 66 kV | Limiting Line Name | TR_LINE 63143546_1 | TR_LINE 63143546_1 | TR_LINE 63143546_1 | TR_LINE 63143546_1 | TR_LINE 63143546_1 | TR_LINE 63143546_1 | TR_LINE 63143546_1 | TR_LINE 63143546_1 | TR_LINE 63143546_1 | TR_LINE 63143546_1 | TR_LINE 63143546_1 | TR_LINE 63143546_1 | TR_LINE 63143546_1 | TR_LINE 63143546_1 | TR_LINE 63143546_1
WB | 50000103 | TORQUAY TEE | 66KV TORQUAY TEE FDR T015 | M020_Maryborough-Torquay 66 kV | Loading (A) | 486.2931 | 185.318 | 485.8575 | 502.1496 | 201.962 | 501.7139 | 516.7233 | 217.4352 | 516.2877 | 530.1217 | 231.4957 | 529.6862 | 542.0059 | 243.9622 | 541.5704
WB | 50000103 | TORQUAY TEE | 66KV TORQUAY TEE FDR T015 | M020_Maryborough-Torquay 66 kV | Loading (MVA) | 57.5733 | 21.8759 | 57.5216 | 59.4254 | 23.8448 | 59.3737 | 61.1235 | 25.676 | 61.0718 | 62.6727 | 27.338 | 62.621 | 64.0338 | 28.8103 | 63.9822
WB | 50000103 | TORQUAY TEE | 66KV TORQUAY TEE FDR T015 | M020_Maryborough-Torquay 66 kV | Loading (MW) | 52.5671 | 20.1525 | 52.5217 | 54.4297 | 22.0804 | 54.3844 | 56.14 | 23.8491 | 56.0948 | 57.7349 | 25.4976 | 57.6898 | 59.1717 | 26.982 | 59.1266
WB | 50000103 | TORQUAY TEE | 66KV TORQUAY TEE FDR T015 | M020_Maryborough-Torquay 66 kV | Power Factor | 0.91305 | 0.92122 | 0.91308 | 0.91593 | 0.92601 | 0.91597 | 0.91847 | 0.92885 | 0.91851 | 0.92121 | 0.93268 | 0.92125 | 0.92407 | 0.93654 | 0.92411
WB | 50000103 | TORQUAY TEE | 66KV TORQUAY TEE FDR T015 | M020_Maryborough-Torquay 66 kV | Rating (A) | 551 | 582 | 524 | 551 | 582 | 524 | 551 | 582 | 524 | 551 | 582 | 524 | 551 | 582 | 524
WB | 50000103 | TORQUAY TEE | 66KV TORQUAY TEE FDR T015 | M020_Maryborough-Torquay 66 kV | Time | 9:00 | 17:00 | 8:30 | 9:00 | 17:00 | 8:30 | 9:00 | 17:00 | 8:30 | 9:00 | 17:00 | 8:30 | 9:00 | 17:00 | 8:30
WB | 50000103 | TORQUAY TEE | 66KV TORQUAY TEE FDR T015 | M020_Maryborough-Torquay 66 kV | Voltage at Constrained Conductor | 68.3538 | 68.1535 | 68.3536 | 68.3248 | 68.1652 | 68.3246 | 68.2951 | 68.1769 | 68.2949 | 68.2562 | 68.1809 | 68.256 | 68.2095 | 68.1811 | 68.2093
WB | 50000122 | M008 | KILKIVAN - MURGON NO1 T/LINE | M008_Kilkivan-Murgon No 1 66 kV | % of Rated A | 4.8666 | 3.4954 | 3.5953 | 5.007 | 3.5962 | 3.6991 | 5.926 | 4.2565 | 4.3781 | 7.4049 | 5.3186 | 5.4706 | 8.9658 | 6.4398 | 6.6238
WB | 50000122 | M008 | KILKIVAN - MURGON NO1 T/LINE | M008_Kilkivan-Murgon No 1 66 kV | Limiting Line Name | TR_LINE 116487_1 | TR_LINE 116487_1 | TR_LINE 116487_1 | TR_LINE 116487_1 | TR_LINE 116487_1 | TR_LINE 116487_1 | TR_LINE 7214_1 | TR_LINE 7214_1 | TR_LINE 7214_1 | TR_LINE 7214_1 | TR_LINE 7214_1 | TR_LINE 7214_1 | TR_LINE 7214_1 | TR_LINE 7214_1 | TR_LINE 7214_1
WB | 50000122 | M008 | KILKIVAN - MURGON NO1 T/LINE | M008_Kilkivan-Murgon No 1 66 kV | Loading (A) | 8.8085 | 8.8083 | 8.8086 | 9.0628 | 9.0624 | 9.0627 | 10.7261 | 10.7263 | 10.7264 | 13.4029 | 13.403 | 13.403 | 16.2281 | 16.2283 | 16.2283
WB | 50000122 | M008 | KILKIVAN - MURGON NO1 T/LINE | M008_Kilkivan-Murgon No 1 66 kV | Loading (MVA) | 1.0299 | 1.0298 | 1.0299 | 1.0599 | 1.0598 | 1.0599 | 1.2545 | 1.2545 | 1.2545 | 1.5677 | 1.5677 | 1.5677 | 1.8983 | 1.8983 | 1.8983
WB | 50000122 | M008 | KILKIVAN - MURGON NO1 T/LINE | M008_Kilkivan-Murgon No 1 66 kV | Loading (MW) | 0.12836 | 0.12836 | 0.12836 | 0.26894 | 0.26894 | 0.26894 | 0.78704 | 0.78704 | 0.78704 | 1.23 | 1.23 | 1.23 | 1.6353 | 1.6353 | 1.6353
WB | 50000122 | M008 | KILKIVAN - MURGON NO1 T/LINE | M008_Kilkivan-Murgon No 1 66 kV | Power Factor | 0.12464 | 0.12465 | 0.12464 | 0.25374 | 0.25376 | 0.25374 | 0.62738 | 0.62739 | 0.62736 | 0.78455 | 0.78458 | 0.78458 | 0.86142 | 0.86144 | 0.86144
WB | 50000122 | M008 | KILKIVAN - MURGON NO1 T/LINE | M008_Kilkivan-Murgon No 1 66 kV | Rating (A) | 181 | 252 | 245 | 181 | 252 | 245 | 181 | 252 | 245 | 181 | 252 | 245 | 181 | 252 | 245
WB | 50000122 | M008 | KILKIVAN - MURGON NO1 T/LINE | M008_Kilkivan-Murgon No 1 66 kV | Time | 16:00 | 18:30 | 7:00 | 16:30 | 19:00 | 7:00 | 16:30 | 19:00 | 7:00 | 16:00 | 18:30 | 5:00 | 9:00 | 17:30 | 5:30
WB | 50000122 | M008 | KILKIVAN - MURGON NO1 T/LINE | M008_Kilkivan-Murgon No 1 66 kV | Voltage at Constrained Conductor | 67.5029 | 67.5005 | 67.503 | 67.5233 | 67.5207 | 67.5231 | 67.525 | 67.5225 | 67.5249 | 67.5333 | 67.531 | 67.531 | 67.5378 | 67.5354 | 67.5354
WB | 50000123 | M009 | KILKIVAN - MURGON NO2 T/LINE | M009_Kilkivan-Murgon No 2 66 kV | % of Rated A | 5.3542 | 3.7859 | 3.8835 | 5.502 | 3.8904 | 3.9907 | 6.285 | 4.4443 | 4.5588 | 7.4586 | 5.2741 | 5.4099 | 8.7593 | 6.1939 | 6.3534
WB | 50000123 | M009 | KILKIVAN - MURGON NO2 T/LINE | M009_Kilkivan-Murgon No 2 66 kV | Limiting Line Name | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1
WB | 50000123 | M009 | KILKIVAN - MURGON NO2 T/LINE | M009_Kilkivan-Murgon No 2 66 kV | Loading (A) | 9.0486 | 9.0483 | 9.0487 | 9.2984 | 9.2981 | 9.2984 | 10.6217 | 10.6219 | 10.622 | 12.6051 | 12.6051 | 12.6051 | 14.8032 | 14.8034 | 14.8034
WB | 50000123 | M009 | KILKIVAN - MURGON NO2 T/LINE | M009_Kilkivan-Murgon No 2 66 kV | Loading (MVA) | 1.0578 | 1.0578 | 1.0578 | 1.0873 | 1.0872 | 1.0873 | 1.2423 | 1.2423 | 1.2423 | 1.4744 | 1.4744 | 1.4744 | 1.7317 | 1.7316 | 1.7316
WB | 50000123 | M009 | KILKIVAN - MURGON NO2 T/LINE | M009_Kilkivan-Murgon No 2 66 kV | Loading (MW) | 0.1238 | 0.1238 | 0.1238 | 0.28268 | 0.28268 | 0.28268 | 0.67102 | 0.67102 | 0.67102 | 1.0474 | 1.0474 | 1.0474 | 1.394 | 1.394 | 1.394
WB | 50000123 | M009 | KILKIVAN - MURGON NO2 T/LINE | M009_Kilkivan-Murgon No 2 66 kV | Power Factor | 0.11703 | 0.11704 | 0.11703 | 0.25998 | 0.25999 | 0.25998 | 0.54015 | 0.54016 | 0.54013 | 0.71034 | 0.71037 | 0.71034 | 0.80499 | 0.80501 | 0.80501
WB | 50000123 | M009 | KILKIVAN - MURGON NO2 T/LINE | M009_Kilkivan-Murgon No 2 66 kV | Rating (A) | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233
WB | 50000123 | M009 | KILKIVAN - MURGON NO2 T/LINE | M009_Kilkivan-Murgon No 2 66 kV | Time | 16:00 | 18:30 | 7:00 | 16:30 | 19:00 | 7:00 | 16:30 | 19:00 | 7:00 | 16:30 | 18:30 | 6:00 | 9:00 | 17:30 | 5:30
WB | 50000123 | M009 | KILKIVAN - MURGON NO2 T/LINE | M009_Kilkivan-Murgon No 2 66 kV | Voltage at Constrained Conductor | 67.4952 | 67.4928 | 67.4952 | 67.5126 | 67.51 | 67.5124 | 67.525 | 67.5225 | 67.5249 | 67.5335 | 67.531 | 67.5338 | 67.5378 | 67.5354 | 67.5354
WB | 50000131 | M004 | MURGON - KINGAROY T/LINE | M004_Murgon-Kingaroy 66 kV | % of Rated A | 4.911 | 3.4725 | 3.5621 | 5.0455 | 3.5676 | 3.6596 | 5.2451 | 3.7088 | 3.8044 | 5.4968 | 3.8868 | 3.9869 | 5.7724 | 4.0817 | 4.1869
WB | 50000131 | M004 | MURGON - KINGAROY T/LINE | M004_Murgon-Kingaroy 66 kV | Limiting Line Name | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1
WB | 50000131 | M004 | MURGON - KINGAROY T/LINE | M004_Murgon-Kingaroy 66 kV | Loading (A) | 8.2996 | 8.2993 | 8.2996 | 8.5269 | 8.5267 | 8.5269 | 8.8643 | 8.864 | 8.8643 | 9.2896 | 9.2896 | 9.2896 | 9.7554 | 9.7554 | 9.7554
WB | 50000131 | M004 | MURGON - KINGAROY T/LINE | M004_Murgon-Kingaroy 66 kV | Loading (MVA) | 0.97282 | 0.97275 | 0.97282 | 1.0008 | 1.0007 | 1.0008 | 1.0416 | 1.0415 | 1.0416 | 1.0927 | 1.0927 | 1.0927 | 1.1485 | 1.1485 | 1.1485
WB | 50000131 | M004 | MURGON - KINGAROY T/LINE | M004_Murgon-Kingaroy 66 kV | Loading (MW) | 0.13644 | 0.13644 | 0.13644 | 0.26745 | 0.26745 | 0.26745 | 0.3942 | 0.3942 | 0.3942 | 0.51688 | 0.51688 | 0.51688 | 0.62984 | 0.62984 | 0.62984
WB | 50000131 | M004 | MURGON - KINGAROY T/LINE | M004_Murgon-Kingaroy 66 kV | Power Factor | 0.14025 | 0.14026 | 0.14025 | 0.26724 | 0.26726 | 0.26725 | 0.37847 | 0.37849 | 0.37847 | 0.47303 | 0.47303 | 0.47303 | 0.54839 | 0.54839 | 0.54839
WB | 50000131 | M004 | MURGON - KINGAROY T/LINE | M004_Murgon-Kingaroy 66 kV | Rating (A) | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233
WB | 50000131 | M004 | MURGON - KINGAROY T/LINE | M004_Murgon-Kingaroy 66 kV | Time | 16:00 | 18:30 | 7:00 | 16:30 | 19:00 | 7:00 | 16:30 | 19:00 | 6:30 | 16:30 | 17:00 | 6:00 | 16:30 | 17:00 | 6:00
WB | 50000131 | M004 | MURGON - KINGAROY T/LINE | M004_Murgon-Kingaroy 66 kV | Voltage at Constrained Conductor | 67.6725 | 67.6701 | 67.6725 | 67.7603 | 67.7577 | 67.7601 | 67.839 | 67.8365 | 67.8391 | 67.9111 | 67.9112 | 67.9114 | 67.9734 | 67.9736 | 67.9737
WB | 50000146 | M003 | KINGAROY - YARRAMAN T/LINE | M003_Kingaroy- Yarraman 66 kV | % of Rated A | 10.586 | 8.3687 | 8.7897 | 15.3596 | 12.1427 | 12.7536 | 19.9423 | 15.7656 | 16.5588 | 24.3317 | 19.2355 | 20.2033 | 28.3876 | 22.4419 | 23.5709
WB | 50000146 | M003 | KINGAROY - YARRAMAN T/LINE | M003_Kingaroy- Yarraman 66 kV | Limiting Line Name | TR_LINE 7254_1 | TR_LINE 7254_1 | TR_LINE 7254_1 | TR_LINE 7254_1 | TR_LINE 7254_1 | TR_LINE 7254_1 | TR_LINE 7254_1 | TR_LINE 7254_1 | TR_LINE 7254_1 | TR_LINE 7254_1 | TR_LINE 7254_1 | TR_LINE 7254_1 | TR_LINE 7254_1 | TR_LINE 7254_1 | TR_LINE 7254_1
WB | 50000146 | M003 | KINGAROY - YARRAMAN T/LINE | M003_Kingaroy- Yarraman 66 kV | Loading (A) | 13.9735 | 13.9757 | 13.9756 | 20.2747 | 20.2783 | 20.2782 | 26.3239 | 26.3285 | 26.3284 | 31.9429 | 31.9486 | 31.9484 | 37.3322 | 37.3386 | 37.3383
WB | 50000146 | M003 | KINGAROY - YARRAMAN T/LINE | M003_Kingaroy- Yarraman 66 kV | Loading (MVA) | 1.6782 | 1.6781 | 1.6781 | 2.4377 | 2.4376 | 2.4376 | 3.1683 | 3.1682 | 3.1682 | 3.8698 | 3.8698 | 3.8698 | 4.5302 | 4.5301 | 4.5301
WB | 50000146 | M003 | KINGAROY - YARRAMAN T/LINE | M003_Kingaroy- Yarraman 66 kV | Loading (MW) | 1.5559 | 1.5559 | 1.5559 | 2.3602 | 2.3602 | 2.3602 | 3.114 | 3.114 | 3.114 | 3.8494 | 3.8494 | 3.8494 | 4.5153 | 4.5153 | 4.5153
WB | 50000146 | M003 | KINGAROY - YARRAMAN T/LINE | M003_Kingaroy- Yarraman 66 kV | Power Factor | 0.92714 | 0.9272 | 0.92719 | 0.96822 | 0.96825 | 0.96825 | 0.98289 | 0.9829 | 0.9829 | 0.99474 | 0.99475 | 0.99475 | 0.99672 | 0.99672 | 0.99672
WB | 50000146 | M003 | KINGAROY - YARRAMAN T/LINE | M003_Kingaroy- Yarraman 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
WB | 50000146 | M003 | KINGAROY - YARRAMAN T/LINE | M003_Kingaroy- Yarraman 66 kV | Time | 16:30 | 18:00 | 4:30 | 16:30 | 18:00 | 4:30 | 16:30 | 18:00 | 4:30 | 16:30 | 18:00 | 4:30 | 16:30 | 18:00 | 4:30
WB | 50000146 | M003 | KINGAROY - YARRAMAN T/LINE | M003_Kingaroy- Yarraman 66 kV | Voltage at Constrained Conductor | 69.3395 | 69.3238 | 69.3244 | 69.4176 | 69.4028 | 69.4034 | 69.488 | 69.4743 | 69.4747 | 69.9444 | 69.9314 | 69.9318 | 70.0602 | 70.0477 | 70.0481
WB | 50000176 | M037 | SOUTH - EAST BUNDABERG T/LINE | M037_South - East Bundaberg 66 kV | % of Rated A | 8.3732 | 6.0824 | 7.3355 | 7.6434 | 5.5522 | 6.6965 | 6.9583 | 5.0593 | 6.1021 | 6.3058 | 4.5878 | 5.5327 | 5.7199 | 4.1645 | 5.02
WB | 50000176 | M037 | SOUTH - EAST BUNDABERG T/LINE | M037_South - East Bundaberg 66 kV | Limiting Line Name | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1
WB | 50000176 | M037 | SOUTH - EAST BUNDABERG T/LINE | M037_South - East Bundaberg 66 kV | Loading (A) | 18.9234 | 18.9163 | 18.9257 | 17.2742 | 17.2673 | 17.2771 | 15.7257 | 15.7345 | 15.7435 | 14.2511 | 14.268 | 14.2743 | 12.9269 | 12.9516 | 12.9516
WB | 50000176 | M037 | SOUTH - EAST BUNDABERG T/LINE | M037_South - East Bundaberg 66 kV | Loading (MVA) | 2.2067 | 2.2031 | 2.2078 | 2.0181 | 2.0156 | 2.0192 | 1.8373 | 1.8399 | 1.8425 | 1.6666 | 1.6707 | 1.6723 | 1.5127 | 1.518 | 1.518
WB | 50000176 | M037 | SOUTH - EAST BUNDABERG T/LINE | M037_South - East Bundaberg 66 kV | Loading (MW) | 1.1197 | 1.1212 | 1.1192 | 0.96739 | 0.96842 | 0.96695 | 0.82519 | 0.82416 | 0.82311 | 0.68372 | 0.68213 | 0.68153 | 0.5567 | 0.55472 | 0.55472
WB | 50000176 | M037 | SOUTH - EAST BUNDABERG T/LINE | M037_South - East Bundaberg 66 kV | Power Factor | 0.50742 | 0.50891 | 0.50693 | 0.47935 | 0.48046 | 0.47888 | 0.44914 | 0.44795 | 0.44673 | 0.41026 | 0.40828 | 0.40755 | 0.36802 | 0.36542 | 0.36541
WB | 50000176 | M037 | SOUTH - EAST BUNDABERG T/LINE | M037_South - East Bundaberg 66 kV | Rating (A) | 226 | 311 | 258 | 226 | 311 | 258 | 226 | 311 | 258 | 226 | 311 | 258 | 226 | 311 | 258
WB | 50000176 | M037 | SOUTH - EAST BUNDABERG T/LINE | M037_South - East Bundaberg 66 kV | Time | 16:30 | 18:30 | 6:30 | 16:30 | 18:30 | 6:30 | 16:30 | 18:30 | 6:30 | 16:30 | 18:30 | 6:30 | 16:30 | 18:30 | 4:30
WB | 50000176 | M037 | SOUTH - EAST BUNDABERG T/LINE | M037_South - East Bundaberg 66 kV | Voltage at Constrained Conductor | 67.3251 | 67.2418 | 67.352 | 67.4518 | 67.394 | 67.4762 | 67.453 | 67.5106 | 67.5691 | 67.5163 | 67.6054 | 67.6384 | 67.5602 | 67.6703 | 67.6707
WB | 50000182 | M035 | BBERG - STH KOLAN NO2 T/LINE | M035_Bundaberg-South Kolan No 2 66 kV | % of Rated A | 2.8678 | 2.7003 | 3.0169 | 3.2242 | 3.0773 | 3.4199 | 3.6991 | 3.5329 | 3.9259 | 4.241 | 4.0465 | 4.4967 | 4.7791 | 4.5325 | 5.0364
WB | 50000182 | M035 | BBERG - STH KOLAN NO2 T/LINE | M035_Bundaberg-South Kolan No 2 66 kV | Limiting Line Name | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1
WB | 50000182 | M035 | BBERG - STH KOLAN NO2 T/LINE | M035_Bundaberg-South Kolan No 2 66 kV | Loading (A) | 15.7158 | 15.6347 | 15.7182 | 17.6685 | 17.8178 | 17.8179 | 20.2712 | 20.4557 | 20.4541 | 23.2406 | 23.4292 | 23.4279 | 26.1892 | 26.243 | 26.2399
WB | 50000182 | M035 | BBERG - STH KOLAN NO2 T/LINE | M035_Bundaberg-South Kolan No 2 66 kV | Loading (MVA) | 1.8049 | 1.7829 | 1.8055 | 2.0404 | 2.034 | 2.034 | 2.3386 | 2.3395 | 2.3366 | 2.6677 | 2.6749 | 2.6755 | 3.0054 | 2.996 | 2.9965
WB | 50000182 | M035 | BBERG - STH KOLAN NO2 T/LINE | M035_Bundaberg-South Kolan No 2 66 kV | Loading (MW) | 0.68819 | 0.68821 | 0.68818 | 1.2024 | 1.202 | 1.202 | 1.6735 | 1.6731 | 1.673 | 2.1332 | 2.1326 | 2.1326 | 2.5539 | 2.5539 | 2.5539
WB | 50000182 | M035 | BBERG - STH KOLAN NO2 T/LINE | M035_Bundaberg-South Kolan No 2 66 kV | Power Factor | 0.38129 | 0.386 | 0.38116 | 0.58927 | 0.59097 | 0.59095 | 0.71558 | 0.71517 | 0.71602 | 0.79963 | 0.79726 | 0.79709 | 0.84976 | 0.85244 | 0.85229
WB | 50000182 | M035 | BBERG - STH KOLAN NO2 T/LINE | M035_Bundaberg-South Kolan No 2 66 kV | Rating (A) | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521
WB | 50000182 | M035 | BBERG - STH KOLAN NO2 T/LINE | M035_Bundaberg-South Kolan No 2 66 kV | Time | 16:00 | 17:30 | 7:00 | 16:30 | 17:30 | 5:30 | 16:30 | 18:00 | 5:30 | 9:00 | 17:00 | 6:00 | 9:00 | 17:00 | 6:00
WB | 50000182 | M035 | BBERG - STH KOLAN NO2 T/LINE | M035_Bundaberg-South Kolan No 2 66 kV | Voltage at Constrained Conductor | 66.3056 | 65.8396 | 66.3188 | 66.6743 | 65.9073 | 65.9087 | 66.6074 | 66.0318 | 65.9535 | 66.2715 | 65.9168 | 65.9347 | 66.2558 | 65.9115 | 65.9312
WB | 50000183 | M032 | BBERG - STH KOLAN NO1 T/LINE | M032_Bundaberg-South Kolan No 1 66 kV | % of Rated A | 21.5995 | 15.9949 | 16.7747 | 21.9071 | 16.4783 | 17.1572 | 23.1638 | 17.4646 | 18.1683 | 24.9483 | 18.7885 | 19.5646 | 27.0058 | 20.1416 | 20.9718
WB | 50000183 | M032 | BBERG - STH KOLAN NO1 T/LINE | M032_Bundaberg-South Kolan No 1 66 kV | Limiting Line Name | TR_LINE 138990_1 | TR_LINE 138990_1 | TR_LINE 138990_1 | TR_LINE 138990_1 | TR_LINE 138990_1 | TR_LINE 138990_1 | TR_LINE 138990_1 | TR_LINE 138990_1 | TR_LINE 138990_1 | TR_LINE 138990_1 | TR_LINE 138990_1 | TR_LINE 138990_1 | TR_LINE 138990_1 | TR_LINE 138990_1 | TR_LINE 138990_1
WB | 50000183 | M032 | BBERG - STH KOLAN NO1 T/LINE | M032_Bundaberg-South Kolan No 1 66 kV | Loading (A) | 28.5114 | 28.3109 | 28.517 | 28.9173 | 29.1667 | 29.1672 | 30.5763 | 30.9124 | 30.8861 | 32.9318 | 33.2556 | 33.2598 | 35.6477 | 35.6506 | 35.6521
WB | 50000183 | M032 | BBERG - STH KOLAN NO1 T/LINE | M032_Bundaberg-South Kolan No 1 66 kV | Loading (MVA) | 3.2795 | 3.2336 | 3.2808 | 3.3451 | 3.3352 | 3.3354 | 3.5339 | 3.542 | 3.5348 | 3.8067 | 3.8044 | 3.8059 | 4.1204 | 4.1221 | 4.1229
WB | 50000183 | M032 | BBERG - STH KOLAN NO1 T/LINE | M032_Bundaberg-South Kolan No 1 66 kV | Loading (MW) | 0.11414 | 0.11446 | 0.11412 | 0.76021 | 0.75966 | 0.75966 | 1.3786 | 1.378 | 1.3778 | 1.9798 | 1.9791 | 1.9791 | 2.5421 | 2.5421 | 2.5421
WB | 50000183 | M032 | BBERG - STH KOLAN NO1 T/LINE | M032_Bundaberg-South Kolan No 1 66 kV | Power Factor | 0.034804 | 0.035398 | 0.034784 | 0.22726 | 0.22777 | 0.22776 | 0.3901 | 0.38905 | 0.38979 | 0.5201 | 0.52021 | 0.52 | 0.61696 | 0.61671 | 0.61658
WB | 50000183 | M032 | BBERG - STH KOLAN NO1 T/LINE | M032_Bundaberg-South Kolan No 1 66 kV | Rating (A) | 132 | 177 | 170 | 132 | 177 | 170 | 132 | 177 | 170 | 132 | 177 | 170 | 132 | 177 | 170
WB | 50000183 | M032 | BBERG - STH KOLAN NO1 T/LINE | M032_Bundaberg-South Kolan No 1 66 kV | Time | 16:00 | 17:30 | 7:00 | 16:30 | 17:30 | 5:30 | 16:30 | 18:00 | 5:30 | 16:30 | 17:00 | 6:00 | 16:30 | 19:00 | 6:30
WB | 50000183 | M032 | BBERG - STH KOLAN NO1 T/LINE | M032_Bundaberg-South Kolan No 1 66 kV | Voltage at Constrained Conductor | 66.4094 | 65.9429 | 66.4227 | 66.7866 | 66.0205 | 66.0219 | 66.7284 | 66.154 | 66.0755 | 66.7377 | 66.0473 | 66.0653 | 66.734 | 66.7558 | 66.7669
WB | 50000197 | M014 | TORQUAY - PIALBA T/LINE | M014_Torquay-Pialba 66 kV | % of Rated A | 10.0597 | 2.9876 | 11.0891 | 8.9946 | 2.9333 | 9.9138 | 8.0423 | 3.7049 | 8.8631 | 7.1584 | 4.4744 | 7.8879 | 6.3359 | 5.1774 | 6.9805
WB | 50000197 | M014 | TORQUAY - PIALBA T/LINE | M014_Torquay-Pialba 66 kV | Limiting Line Name | TR_LINE 7168_1 | TR_LINE 7168_1 | TR_LINE 7168_1 | TR_LINE 7168_1 | TR_LINE 7168_1 | TR_LINE 7168_1 | TR_LINE 7168_1 | TR_LINE 7168_1 | TR_LINE 7168_1 | TR_LINE 7168_1 | TR_LINE 7168_1 | TR_LINE 7168_1 | TR_LINE 7168_1 | TR_LINE 7168_1 | TR_LINE 7168_1
WB | 50000197 | M014 | TORQUAY - PIALBA T/LINE | M014_Torquay-Pialba 66 kV | Loading (A) | 61.1632 | 20.0766 | 61.1008 | 54.687 | 19.7115 | 54.6249 | 48.8973 | 24.8968 | 48.8357 | 43.5232 | 30.0683 | 43.4624 | 38.5226 | 34.7924 | 38.4626
WB | 50000197 | M014 | TORQUAY - PIALBA T/LINE | M014_Torquay-Pialba 66 kV | Loading (MVA) | 7.3564 | 2.4163 | 7.3489 | 6.5869 | 2.3767 | 6.5794 | 5.8965 | 3.0071 | 5.8891 | 5.2532 | 3.6369 | 5.2459 | 4.6523 | 4.2131 | 4.645
WB | 50000197 | M014 | TORQUAY - PIALBA T/LINE | M014_Torquay-Pialba 66 kV | Loading (MW) | 6.3131 | 1.4258 | 6.3062 | 5.4938 | 1.9969 | 5.487 | 4.7566 | 2.752 | 4.7497 | 4.0727 | 3.4522 | 4.0658 | 3.462 | 4.0774 | 3.455
WB | 50000197 | M014 | TORQUAY - PIALBA T/LINE | M014_Torquay-Pialba 66 kV | Power Factor | 0.85817 | 0.59007 | 0.85812 | 0.83406 | 0.8402 | 0.83396 | 0.80668 | 0.91517 | 0.80653 | 0.77529 | 0.94921 | 0.77505 | 0.74414 | 0.9678 | 0.74381
WB | 50000197 | M014 | TORQUAY - PIALBA T/LINE | M014_Torquay-Pialba 66 kV | Rating (A) | 608 | 672 | 551 | 608 | 672 | 551 | 608 | 672 | 551 | 608 | 672 | 551 | 608 | 672 | 551
WB | 50000197 | M014 | TORQUAY - PIALBA T/LINE | M014_Torquay-Pialba 66 kV | Time | 9:00 | 17:00 | 8:30 | 9:00 | 18:30 | 8:30 | 9:00 | 18:30 | 8:30 | 9:00 | 18:30 | 8:30 | 9:00 | 18:30 | 8:30
WB | 50000197 | M014 | TORQUAY - PIALBA T/LINE | M014_Torquay-Pialba 66 kV | Voltage at Constrained Conductor | 69.4409 | 69.4852 | 69.4411 | 69.5403 | 69.6141 | 69.5404 | 69.6226 | 69.7332 | 69.6227 | 69.6855 | 69.8341 | 69.6856 | 69.725 | 69.9127 | 69.7251
WB | 50000200 | M039 | BBERG - WST BBERG NO1 T/LINE | M039_Bundaberg-West Bundaberg No 1 66 kV | % of Rated A | 11.1235 | 9.9166 | 12.039 | 11.9649 | 10.673 | 12.9479 | 13.1887 | 11.7762 | 14.2788 | 14.6514 | 13.0801 | 15.8553 | 16.1608 | 14.429 | 17.4873
WB | 50000200 | M039 | BBERG - WST BBERG NO1 T/LINE | M039_Bundaberg-West Bundaberg No 1 66 kV | Limiting Line Name | TR_LINE 200241_1 | TR_LINE 200241_1 | TR_LINE 200241_1 | TR_LINE 200241_1 | TR_LINE 200241_1 | TR_LINE 200241_1 | TR_LINE 200241_1 | TR_LINE 200241_1 | TR_LINE 200241_1 | TR_LINE 200241_1 | TR_LINE 200241_1 | TR_LINE 200241_1 | TR_LINE 200241_1 | TR_LINE 200241_1 | TR_LINE 200241_1
WB | 50000200 | M039 | BBERG - WST BBERG NO1 T/LINE | M039_Bundaberg-West Bundaberg No 1 66 kV | Loading (A) | 89.6557 | 89.547 | 89.6909 | 96.4369 | 96.3776 | 96.462 | 106.2896 | 106.3272 | 106.3655 | 118.0794 | 118.1026 | 118.1113 | 130.2468 | 130.2842 | 130.2707
WB | 50000200 | M039 | BBERG - WST BBERG NO1 T/LINE | M039_Bundaberg-West Bundaberg No 1 66 kV | Loading (MVA) | 10.3334 | 10.3081 | 10.3416 | 11.1221 | 11.1057 | 11.1291 | 12.2463 | 12.2612 | 12.2763 | 13.6036 | 13.6245 | 13.6322 | 14.9247 | 14.8677 | 14.8862
WB | 50000200 | M039 | BBERG - WST BBERG NO1 T/LINE | M039_Bundaberg-West Bundaberg No 1 66 kV | Loading (MW) | 1.6417 | 1.6424 | 1.6414 | 4.2864 | 4.2869 | 4.2862 | 6.7048 | 6.7043 | 6.7038 | 8.9742 | 8.9734 | 8.9732 | 11.0221 | 11.0241 | 11.0234
WB | 50000200 | M039 | BBERG - WST BBERG NO1 T/LINE | M039_Bundaberg-West Bundaberg No 1 66 kV | Power Factor | 0.15887 | 0.15934 | 0.15872 | 0.38539 | 0.38601 | 0.38513 | 0.5475 | 0.54679 | 0.54608 | 0.65969 | 0.65863 | 0.65824 | 0.73851 | 0.74148 | 0.74051
WB | 50000200 | M039 | BBERG - WST BBERG NO1 T/LINE | M039_Bundaberg-West Bundaberg No 1 66 kV | Rating (A) | 806 | 903 | 745 | 806 | 903 | 745 | 806 | 903 | 745 | 806 | 903 | 745 | 806 | 903 | 745
WB | 50000200 | M039 | BBERG - WST BBERG NO1 T/LINE | M039_Bundaberg-West Bundaberg No 1 66 kV | Time | 16:30 | 18:30 | 6:30 | 16:30 | 18:30 | 6:30 | 16:30 | 18:30 | 6:30 | 16:30 | 18:30 | 6:30 | 9:00 | 17:30 | 5:30
WB | 50000200 | M039 | BBERG - WST BBERG NO1 T/LINE | M039_Bundaberg-West Bundaberg No 1 66 kV | Voltage at Constrained Conductor | 66.5434 | 66.4607 | 66.5701 | 66.5861 | 66.5286 | 66.6104 | 66.5202 | 66.5775 | 66.6357 | 66.515 | 66.6038 | 66.6366 | 66.1572 | 65.8857 | 65.9744
WB | 50000201 | M040 | B'BERG - WEST B'BERG NO2 T/LINE | M040_Bundaberg-West Bundaberg No 2 66 kV | % of Rated A | 10.714 | 9.5515 | 11.5958 | 11.5238 | 10.2795 | 12.4706 | 12.7017 | 11.3413 | 13.7516 | 14.1096 | 12.5964 | 15.269 | 15.5626 | 13.8948 | 16.8399
WB | 50000201 | M040 | B'BERG - WEST B'BERG NO2 T/LINE | M040_Bundaberg-West Bundaberg No 2 66 kV | Limiting Line Name | TR_LINE 169764_1 | TR_LINE 169764_1 | TR_LINE 169764_1 | TR_LINE 169764_1 | TR_LINE 169764_1 | TR_LINE 169764_1 | TR_LINE 169764_1 | TR_LINE 169764_1 | TR_LINE 169764_1 | TR_LINE 169764_1 | TR_LINE 169764_1 | TR_LINE 169764_1 | TR_LINE 169764_1 | TR_LINE 169764_1 | TR_LINE 169764_1
WB | 50000201 | M040 | B'BERG - WEST B'BERG NO2 T/LINE | M040_Bundaberg-West Bundaberg No 2 66 kV | Loading (A) | 86.3546 | 86.2499 | 86.3885 | 92.8815 | 92.8243 | 92.9056 | 102.3761 | 102.4124 | 102.4493 | 113.4407 | 113.4624 | 113.4705 | 125.1821 | 125.2201 | 125.2065
WB | 50000201 | M040 | B'BERG - WEST B'BERG NO2 T/LINE | M040_Bundaberg-West Bundaberg No 2 66 kV | Loading (MVA) | 9.9529 | 9.9285 | 9.9608 | 10.7121 | 10.6962 | 10.7188 | 11.794 | 11.8084 | 11.823 | 13.1078 | 13.1278 | 13.1352 | 14.3882 | 14.3336 | 14.3513
WB | 50000201 | M040 | B'BERG - WEST B'BERG NO2 T/LINE | M040_Bundaberg-West Bundaberg No 2 66 kV | Loading (MW) | 1.5819 | 1.5826 | 1.5816 | 4.1283 | 4.1288 | 4.1281 | 6.4564 | 6.4559 | 6.4555 | 8.6517 | 8.651 | 8.6508 | 10.6256 | 10.6275 | 10.6269
WB | 50000201 | M040 | B'BERG - WEST B'BERG NO2 T/LINE | M040_Bundaberg-West Bundaberg No 2 66 kV | Power Factor | 0.15894 | 0.1594 | 0.15879 | 0.38538 | 0.386 | 0.38512 | 0.54743 | 0.54672 | 0.54601 | 0.66005 | 0.65899 | 0.6586 | 0.73849 | 0.74144 | 0.74048
WB | 50000201 | M040 | B'BERG - WEST B'BERG NO2 T/LINE | M040_Bundaberg-West Bundaberg No 2 66 kV | Rating (A) | 806 | 903 | 745 | 806 | 903 | 745 | 806 | 903 | 745 | 806 | 903 | 745 | 806 | 903 | 745
WB | 50000201 | M040 | B'BERG - WEST B'BERG NO2 T/LINE | M040_Bundaberg-West Bundaberg No 2 66 kV | Time | 16:30 | 18:30 | 6:30 | 16:30 | 18:30 | 6:30 | 16:30 | 18:30 | 6:30 | 16:30 | 18:30 | 6:30 | 9:00 | 17:30 | 5:30
WB | 50000201 | M040 | B'BERG - WEST B'BERG NO2 T/LINE | M040_Bundaberg-West Bundaberg No 2 66 kV | Voltage at Constrained Conductor | 66.5434 | 66.4607 | 66.5701 | 66.5861 | 66.5286 | 66.6104 | 66.5126 | 66.5699 | 66.6281 | 66.7113 | 66.8003 | 66.8331 | 66.3598 | 66.0878 | 66.1766
WB | 50016424 | 764 | 764 WOOLOOGA - KILKIVAN NO1 T/LINE | 764_Woolooga-Kilkivan No 1 132 kV | % of Rated A | 3.6309 | 2.2739 | 2.2913 | 3.66 | 2.292 | 2.3096 | 3.8136 | 2.3883 | 2.4066 | 4.0659 | 2.5462 | 2.5658 | 4.3716 | 2.7378 | 2.7587
WB | 50016424 | 764 | 764 WOOLOOGA - KILKIVAN NO1 T/LINE | 764_Woolooga-Kilkivan No 1 132 kV | Limiting Line Name | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1
WB | 50016424 | 764 | 764 WOOLOOGA - KILKIVAN NO1 T/LINE | 764_Woolooga-Kilkivan No 1 132 kV | Loading (A) | 9.0048 | 9.0045 | 9.0048 | 9.0767 | 9.0763 | 9.0767 | 9.4578 | 9.4577 | 9.4579 | 10.0834 | 10.0831 | 10.0834 | 10.8415 | 10.8415 | 10.8415
WB | 50016424 | 764 | 764 WOOLOOGA - KILKIVAN NO1 T/LINE | 764_Woolooga-Kilkivan No 1 132 kV | Loading (MVA) | 2.1618 | 2.1617 | 2.1618 | 2.1791 | 2.1789 | 2.1791 | 2.2706 | 2.2704 | 2.2706 | 2.4207 | 2.4206 | 2.4208 | 2.6027 | 2.6028 | 2.6028
WB | 50016424 | 764 | 764 WOOLOOGA - KILKIVAN NO1 T/LINE | 764_Woolooga-Kilkivan No 1 132 kV | Loading (MW) | 0.14141 | 0.14141 | 0.14141 | 0.30387 | 0.30387 | 0.30387 | 0.72797 | 0.72797 | 0.72797 | 1.1372 | 1.1372 | 1.1372 | 1.5126 | 1.5126 | 1.5126
WB | 50016424 | 764 | 764 WOOLOOGA - KILKIVAN NO1 T/LINE | 764_Woolooga-Kilkivan No 1 132 kV | Power Factor | 0.065414 | 0.065418 | 0.065413 | 0.13945 | 0.13946 | 0.13945 | 0.32061 | 0.32063 | 0.32061 | 0.46978 | 0.46981 | 0.46977 | 0.58117 | 0.58116 | 0.58116
WB | 50016424 | 764 | 764 WOOLOOGA - KILKIVAN NO1 T/LINE | 764_Woolooga-Kilkivan No 1 132 kV | Rating (A) | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393
WB | 50016424 | 764 | 764 WOOLOOGA - KILKIVAN NO1 T/LINE | 764_Woolooga-Kilkivan No 1 132 kV | Time | 16:00 | 18:30 | 7:00 | 16:30 | 19:00 | 7:00 | 16:30 | 19:00 | 7:00 | 16:30 | 18:30 | 6:00 | 16:30 | 17:00 | 6:00
WB | 50016424 | 764 | 764 WOOLOOGA - KILKIVAN NO1 T/LINE | 764_Woolooga-Kilkivan No 1 132 kV | Voltage at Constrained Conductor | 138.6062 | 138.6012 | 138.6062 | 138.6064 | 138.601 | 138.606 | 138.6061 | 138.6008 | 138.6057 | 138.6058 | 138.6006 | 138.6064 | 138.6056 | 138.6061 | 138.6062
WB | 50016425 | 765 | 765 WOOLOOGA - KILKIVAN NO2 T/LINE | 765_Woolooga-Kilkivan No 2 132 kV | % of Rated A | 3.6308 | 2.2738 | 2.2912 | 3.6598 | 2.2919 | 2.3095 | 3.8135 | 2.3882 | 2.4065 | 4.0657 | 2.5462 | 2.5657 | 4.3714 | 2.7376 | 2.7585
WB | 50016425 | 765 | 765 WOOLOOGA - KILKIVAN NO2 T/LINE | 765_Woolooga-Kilkivan No 2 132 kV | Limiting Line Name | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1
WB | 50016425 | 765 | 765 WOOLOOGA - KILKIVAN NO2 T/LINE | 765_Woolooga-Kilkivan No 2 132 kV | Loading (A) | 9.0045 | 9.0042 | 9.0045 | 9.0764 | 9.0761 | 9.0764 | 9.4574 | 9.4573 | 9.4576 | 10.083 | 10.0828 | 10.083 | 10.8411 | 10.8411 | 10.8411
WB | 50016425 | 765 | 765 WOOLOOGA - KILKIVAN NO2 T/LINE | 765_Woolooga-Kilkivan No 2 132 kV | Loading (MVA) | 2.1617 | 2.1616 | 2.1617 | 2.179 | 2.1788 | 2.179 | 2.2705 | 2.2704 | 2.2705 | 2.4206 | 2.4205 | 2.4207 | 2.6026 | 2.6026 | 2.6026
WB | 50016425 | 765 | 765 WOOLOOGA - KILKIVAN NO2 T/LINE | 765_Woolooga-Kilkivan No 2 132 kV | Loading (MW) | 0.1414 | 0.1414 | 0.1414 | 0.30385 | 0.30385 | 0.30385 | 0.72792 | 0.72792 | 0.72792 | 1.1371 | 1.1371 | 1.1371 | 1.5125 | 1.5125 | 1.5125
WB | 50016425 | 765 | 765 WOOLOOGA - KILKIVAN NO2 T/LINE | 765_Woolooga-Kilkivan No 2 132 kV | Power Factor | 0.065411 | 0.065416 | 0.065411 | 0.13944 | 0.13946 | 0.13945 | 0.3206 | 0.32062 | 0.3206 | 0.46976 | 0.46979 | 0.46976 | 0.58115 | 0.58115 | 0.58115
WB | 50016425 | 765 | 765 WOOLOOGA - KILKIVAN NO2 T/LINE | 765_Woolooga-Kilkivan No 2 132 kV | Rating (A) | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393
WB | 50016425 | 765 | 765 WOOLOOGA - KILKIVAN NO2 T/LINE | 765_Woolooga-Kilkivan No 2 132 kV | Time | 16:00 | 18:30 | 7:00 | 16:30 | 19:00 | 7:00 | 16:30 | 19:00 | 7:00 | 16:30 | 18:30 | 6:00 | 16:30 | 17:00 | 6:00
WB | 50016425 | 765 | 765 WOOLOOGA - KILKIVAN NO2 T/LINE | 765_Woolooga-Kilkivan No 2 132 kV | Voltage at Constrained Conductor | 138.6062 | 138.6012 | 138.6062 | 138.6064 | 138.601 | 138.606 | 138.6061 | 138.6008 | 138.6057 | 138.6058 | 138.6006 | 138.6064 | 138.6056 | 138.6061 | 138.6062
WB | 50021248 | 7204 | 7204 BUNDABERG - CLAYTON T/LINE | 7204_Bundaberg - Clayton 132 kV | % of Rated A | 0.91334 | 0.82275 | 0.96452 | 0.91301 | 0.82197 | 0.96417 | 0.9129 | 0.82135 | 0.96406 | 0.9129 | 0.82097 | 0.96406 | 0.91301 | 0.82071 | 0.96417
WB | 50021248 | 7204 | 7204 BUNDABERG - CLAYTON T/LINE | 7204_Bundaberg - Clayton 132 kV | Limiting Line Name | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1
WB | 50021248 | 7204 | 7204 BUNDABERG - CLAYTON T/LINE | 7204_Bundaberg - Clayton 132 kV | Loading (A) | 8.0922 | 8.0712 | 8.0923 | 8.0893 | 8.0635 | 8.0894 | 8.0883 | 8.0575 | 8.0884 | 8.0883 | 8.0537 | 8.0884 | 8.0893 | 8.0512 | 8.0894
WB | 50021248 | 7204 | 7204 BUNDABERG - CLAYTON T/LINE | 7204_Bundaberg - Clayton 132 kV | Loading (MVA) | 1.9669 | 1.9677 | 1.9669 | 1.967 | 1.968 | 1.967 | 1.967 | 1.9682 | 1.967 | 1.967 | 1.9684 | 1.967 | 1.967 | 1.9685 | 1.967
WB | 50021248 | 7204 | 7204 BUNDABERG - CLAYTON T/LINE | 7204_Bundaberg - Clayton 132 kV | Loading (MW) | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9
WB | 50021248 | 7204 | 7204 BUNDABERG - CLAYTON T/LINE | 7204_Bundaberg - Clayton 132 kV | Power Factor | 0.96599 | 0.9656 | 0.96599 | 0.96594 | 0.96546 | 0.96594 | 0.96592 | 0.96534 | 0.96592 | 0.96592 | 0.96527 | 0.96592 | 0.96594 | 0.96522 | 0.96594
WB | 50021248 | 7204 | 7204 BUNDABERG - CLAYTON T/LINE | 7204_Bundaberg - Clayton 132 kV | Rating (A) | 886 | 981 | 839 | 886 | 981 | 839 | 886 | 981 | 839 | 886 | 981 | 839 | 886 | 981 | 839
WB | 50021248 | 7204 | 7204 BUNDABERG - CLAYTON T/LINE | 7204_Bundaberg - Clayton 132 kV | Time | 9:00 | 19:00 | 8:30 | 9:00 | 19:00 | 8:30 | 9:00 | 19:00 | 8:30 | 9:00 | 19:00 | 8:30 | 9:00 | 19:00 | 8:30
WB | 50021248 | 7204 | 7204 BUNDABERG - CLAYTON T/LINE | 7204_Bundaberg - Clayton 132 kV | Voltage at Constrained Conductor | 140.3304 | 140.7527 | 140.3282 | 140.3899 | 140.9084 | 140.3875 | 140.4088 | 141.0301 | 140.4062 | 140.409 | 141.1066 | 140.4063 | 140.3895 | 141.1575 | 140.3866
WB | 50021251 | M045 | TARONG - PACIFIC COAL T/LINE | M045_Tarong-Pacific Coal 66 kV | % of Rated A | 54.7953 | 40.5758 | 41.9667 | 55.4122 | 41.0321 | 42.4386 | 56.0305 | 41.4893 | 42.9116 | 56.6498 | 41.9475 | 43.3854 | 56.0223 | 41.4826 | 42.9046
WB | 50021251 | M045 | TARONG - PACIFIC COAL T/LINE | M045_Tarong-Pacific Coal 66 kV | Limiting Line Name | TR_LINE 7237_1 | TR_LINE 7237_1 | TR_LINE 7237_1 | TR_LINE 7237_1 | TR_LINE 7237_1 | TR_LINE 7237_1 | TR_LINE 7237_1 | TR_LINE 7237_1 | TR_LINE 7237_1 | TR_LINE 7237_1 | TR_LINE 7237_1 | TR_LINE 7237_1 | TR_LINE 7237_1 | TR_LINE 7237_1 | TR_LINE 7237_1
WB | 50021251 | M045 | TARONG - PACIFIC COAL T/LINE | M045_Tarong-Pacific Coal 66 kV | Loading (A) | 73.4257 | 73.4423 | 73.4417 | 74.2523 | 74.2682 | 74.2675 | 75.0808 | 75.0957 | 75.0952 | 75.9107 | 75.925 | 75.9245 | 75.0699 | 75.0835 | 75.0831
WB | 50021251 | M045 | TARONG - PACIFIC COAL T/LINE | M045_Tarong-Pacific Coal 66 kV | Loading (MVA) | 8.8134 | 8.8134 | 8.8134 | 8.9137 | 8.9137 | 8.9137 | 9.014 | 9.014 | 9.014 | 9.1144 | 9.1144 | 9.1144 | 9.014 | 9.014 | 9.014
WB | 50021251 | M045 | TARONG - PACIFIC COAL T/LINE | M045_Tarong-Pacific Coal 66 kV | Loading (MW) | 8.8134 | 8.8134 | 8.8134 | 8.9137 | 8.9137 | 8.9137 | 9.014 | 9.014 | 9.014 | 9.1143 | 9.1143 | 9.1143 | 9.014 | 9.014 | 9.014
WB | 50021251 | M045 | TARONG - PACIFIC COAL T/LINE | M045_Tarong-Pacific Coal 66 kV | Power Factor | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
WB | 50021251 | M045 | TARONG - PACIFIC COAL T/LINE | M045_Tarong-Pacific Coal 66 kV | Rating (A) | 134 | 181 | 175 | 134 | 181 | 175 | 134 | 181 | 175 | 134 | 181 | 175 | 134 | 181 | 175
WB | 50021251 | M045 | TARONG - PACIFIC COAL T/LINE | M045_Tarong-Pacific Coal 66 kV | Time | 16:30 | 18:00 | 4:30 | 16:30 | 18:00 | 4:30 | 16:30 | 18:00 | 4:30 | 16:30 | 18:00 | 4:30 | 16:30 | 18:00 | 4:30
WB | 50021251 | M045 | TARONG - PACIFIC COAL T/LINE | M045_Tarong-Pacific Coal 66 kV | Voltage at Constrained Conductor | 69.3005 | 69.2849 | 69.2854 | 69.3089 | 69.2941 | 69.2947 | 69.3154 | 69.3018 | 69.3022 | 69.3206 | 69.3076 | 69.308 | 69.3254 | 69.3129 | 69.3133
WB | 50078755 | M028 | CHILDERS - GAYNDAH T/LINE | M028_Childers - Gayndah 66 kV | % of Rated A | 30.7295 | 24.4011 | 25.6288 | 28.711 | 22.7671 | 23.9126 | 26.8551 | 21.2485 | 22.3122 | 24.8426 | 19.673 | 20.6629 | 23.1585 | 18.332 | 19.2544
WB | 50078755 | M028 | CHILDERS - GAYNDAH T/LINE | M028_Childers - Gayndah 66 kV | Limiting Line Name | TR_LINE 12103276_2 | TR_LINE 12103276_2 | TR_LINE 12103276_2 | TR_LINE 12103276_2 | TR_LINE 12103276_2 | TR_LINE 12103276_2 | TR_LINE 12103276_2 | TR_LINE 12103276_2 | TR_LINE 12103276_2 | TR_LINE 12103276_2 | TR_LINE 12103276_2 | TR_LINE 12103276_2 | TR_LINE 12103276_2 | TR_LINE 12103276_2 | TR_LINE 12103276_2
WB | 50078755 | M028 | CHILDERS - GAYNDAH T/LINE | M028_Childers - Gayndah 66 kV | Loading (A) | 40.5629 | 40.7499 | 40.7499 | 37.8986 | 38.021 | 38.021 | 35.4487 | 35.485 | 35.4765 | 32.7922 | 32.854 | 32.854 | 30.5693 | 30.6145 | 30.6145
WB | 50078755 | M028 | CHILDERS - GAYNDAH T/LINE | M028_Childers - Gayndah 66 kV | Loading (MVA) | 4.8731 | 4.8579 | 4.8579 | 4.5545 | 4.5383 | 4.5383 | 4.2563 | 4.2508 | 4.252 | 3.9364 | 3.9186 | 3.9186 | 3.669 | 3.653 | 3.653
WB | 50078755 | M028 | CHILDERS - GAYNDAH T/LINE | M028_Childers - Gayndah 66 kV | Loading (MW) | 4.0385 | 4.0468 | 4.0468 | 3.6695 | 3.6767 | 3.6767 | 3.3247 | 3.3271 | 3.3265 | 2.9697 | 2.976 | 2.976 | 2.642 | 2.6475 | 2.6475
WB | 50078755 | M028 | CHILDERS - GAYNDAH T/LINE | M028_Childers - Gayndah 66 kV | Power Factor | 0.82874 | 0.83304 | 0.83304 | 0.80568 | 0.81014 | 0.81014 | 0.78112 | 0.78269 | 0.78234 | 0.7544 | 0.75946 | 0.75946 | 0.72008 | 0.72475 | 0.72475
WB | 50078755 | M028 | CHILDERS - GAYNDAH T/LINE | M028_Childers - Gayndah 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
WB | 50078755 | M028 | CHILDERS - GAYNDAH T/LINE | M028_Childers - Gayndah 66 kV | Time | 16:00 | 18:30 | 5:00 | 16:00 | 18:30 | 5:00 | 16:30 | 17:00 | 6:00 | 16:30 | 19:00 | 0:00 | 16:30 | 19:00 | 0:00
WB | 50078755 | M028 | CHILDERS - GAYNDAH T/LINE | M028_Childers - Gayndah 66 kV | Voltage at Constrained Conductor | 69.361 | 68.8274 | 68.8275 | 69.3842 | 68.914 | 68.9141 | 69.3227 | 69.1611 | 69.1984 | 69.3062 | 68.8617 | 68.8617 | 69.2951 | 68.8905 | 68.8905
WB | 50078756 | 6205 | EAST B'BERG - B'BERG CENTRAL | 6205_East Bundaberg-BUCE 66 kV | % of Rated A | 8.2604 | 7.5232 | 9.2126 | 11.016 | 10.0711 | 12.3329 | 13.9413 | 12.7542 | 15.6177 | 16.8565 | 15.4242 | 18.8862 | 19.5963 | 17.9318 | 21.9558
WB | 50078756 | 6205 | EAST B'BERG - B'BERG CENTRAL | 6205_East Bundaberg-BUCE 66 kV | Limiting Line Name | TR_LINE 176527_1 | TR_LINE 176527_1 | TR_LINE 176527_1 | TR_LINE 176527_1 | TR_LINE 176527_1 | TR_LINE 176527_1 | TR_LINE 176527_1 | TR_LINE 176527_1 | TR_LINE 176527_1 | TR_LINE 176527_1 | TR_LINE 176527_1 | TR_LINE 176527_1 | TR_LINE 176527_1 | TR_LINE 176527_1 | TR_LINE 176527_1
WB | 50078756 | 6205 | EAST B'BERG - B'BERG CENTRAL | 6205_East Bundaberg-BUCE 66 kV | Loading (A) | 32.7937 | 32.801 | 32.7969 | 43.7336 | 43.9098 | 43.9052 | 55.3471 | 55.6085 | 55.5992 | 66.9133 | 67.2426 | 67.2279 | 77.7912 | 78.1766 | 78.1565
WB | 50078756 | 6205 | EAST B'BERG - B'BERG CENTRAL | 6205_East Bundaberg-BUCE 66 kV | Loading (MVA) | 3.7976 | 3.7745 | 3.7747 | 5.0712 | 5.0611 | 5.0617 | 6.4232 | 6.4172 | 6.4177 | 7.7707 | 7.7671 | 7.7675 | 9.0367 | 9.0344 | 9.0348
WB | 50078756 | 6205 | EAST B'BERG - B'BERG CENTRAL | 6205_East Bundaberg-BUCE 66 kV | Loading (MW) | 2.3548 | 2.3623 | 2.3621 | 4.0225 | 4.0315 | 4.0312 | 5.5871 | 5.5956 | 5.5954 | 7.0713 | 7.0794 | 7.0791 | 8.4313 | 8.4391 | 8.4387
WB | 50078756 | 6205 | EAST B'BERG - B'BERG CENTRAL | 6205_East Bundaberg-BUCE 66 kV | Power Factor | 0.62009 | 0.62587 | 0.62577 | 0.7932 | 0.79655 | 0.79642 | 0.86984 | 0.87197 | 0.87187 | 0.90999 | 0.91146 | 0.91137 | 0.93301 | 0.9341 | 0.93403
WB | 50078756 | 6205 | EAST B'BERG - B'BERG CENTRAL | 6205_East Bundaberg-BUCE 66 kV | Rating (A) | 397 | 436 | 356 | 397 | 436 | 356 | 397 | 436 | 356 | 397 | 436 | 356 | 397 | 436 | 356
WB | 50078756 | 6205 | EAST B'BERG - B'BERG CENTRAL | 6205_East Bundaberg-BUCE 66 kV | Time | 9:00 | 17:00 | 6:00 | 9:00 | 17:00 | 6:00 | 9:00 | 17:00 | 6:00 | 9:00 | 17:00 | 6:00 | 9:00 | 17:00 | 6:00
WB | 50078756 | 6205 | EAST B'BERG - B'BERG CENTRAL | 6205_East Bundaberg-BUCE 66 kV | Voltage at Constrained Conductor | 66.8578 | 66.4369 | 66.4494 | 66.9472 | 66.5465 | 66.5607 | 67.003 | 66.6264 | 66.6422 | 67.0483 | 66.6891 | 66.7072 | 67.0682 | 66.721 | 66.7407
WB | 50079711 | M010 | MARYBOROUGH - OWANYILLA T/LINE | M010_Maryborough - Owanyilla 66 kV | % of Rated A | 10.0051 | 6.5332 | 6.782 | 13.768 | 8.9859 | 9.303 | 17.4073 | 11.3574 | 11.7447 | 20.8983 | 13.6225 | 14.0822 | 24.0203 | 15.7006 | 16.224
WB | 50079711 | M010 | MARYBOROUGH - OWANYILLA T/LINE | M010_Maryborough - Owanyilla 66 kV | Limiting Line Name | TR_LINE 199623_1 | TR_LINE 199623_1 | TR_LINE 7259_1 | TR_LINE 199623_1 | TR_LINE 199623_1 | TR_LINE 7259_1 | TR_LINE 199623_1 | TR_LINE 199623_1 | TR_LINE 7259_1 | TR_LINE 199623_1 | TR_LINE 199623_1 | TR_LINE 7259_1 | TR_LINE 199623_1 | TR_LINE 199623_1 | TR_LINE 7259_1
WB | 50079711 | M010 | MARYBOROUGH - OWANYILLA T/LINE | M010_Maryborough - Owanyilla 66 kV | Loading (A) | 24.9128 | 24.9567 | 25.0936 | 34.2823 | 34.3261 | 34.4211 | 43.3442 | 43.3852 | 43.4556 | 52.0367 | 52.0381 | 52.0998 | 59.8053 | 59.9712 | 60.0255
WB | 50079711 | M010 | MARYBOROUGH - OWANYILLA T/LINE | M010_Maryborough - Owanyilla 66 kV | Loading (MVA) | 2.9367 | 2.9339 | 2.9484 | 4.0409 | 4.04 | 4.0486 | 5.1128 | 5.112 | 5.1166 | 6.1357 | 6.1352 | 6.1369 | 7.0734 | 7.0717 | 7.0701
WB | 50079711 | M010 | MARYBOROUGH - OWANYILLA T/LINE | M010_Maryborough - Owanyilla 66 kV | Loading (MW) | 2.7202 | 2.72 | 2.7192 | 3.9016 | 3.9015 | 3.8999 | 5.0172 | 5.017 | 5.0145 | 6.0692 | 6.0691 | 6.066 | 7.0262 | 7.0254 | 7.0204
WB | 50079711 | M010 | MARYBOROUGH - OWANYILLA T/LINE | M010_Maryborough - Owanyilla 66 kV | Power Factor | 0.92627 | 0.92711 | 0.92226 | 0.96551 | 0.96571 | 0.96327 | 0.9813 | 0.98142 | 0.98004 | 0.98916 | 0.98922 | 0.98844 | 0.99333 | 0.99345 | 0.99297
WB | 50079711 | M010 | MARYBOROUGH - OWANYILLA T/LINE | M010_Maryborough - Owanyilla 66 kV | Rating (A) | 249 | 382 | 370 | 249 | 382 | 370 | 249 | 382 | 370 | 249 | 382 | 370 | 249 | 382 | 370
WB | 50079711 | M010 | MARYBOROUGH - OWANYILLA T/LINE | M010_Maryborough - Owanyilla 66 kV | Time | 16:30 | 19:00 | 0:00 | 16:30 | 19:00 | 0:00 | 16:00 | 19:00 | 0:00 | 16:00 | 18:00 | 5:30 | 9:00 | 18:00 | 5:30
WB | 50079711 | M010 | MARYBOROUGH - OWANYILLA T/LINE | M010_Maryborough - Owanyilla 66 kV | Voltage at Constrained Conductor | 68.0572 | 67.872 | 67.8355 | 68.0533 | 67.951 | 67.9076 | 68.1033 | 68.028 | 67.9785 | 68.0764 | 68.0685 | 68.0066 | 68.2851 | 68.0803 | 68.0032
WB | 50079712 | M011 | KILKIVAN-MARYBOROUGH | M011_Kilkivan-Maryborough 66 kV | % of Rated A | 7.9441 | 6.2958 | 6.6125 | 10.5994 | 8.3903 | 8.8125 | 13.0654 | 10.3381 | 10.8583 | 15.3592 | 12.1413 | 12.7548 | 17.3482 | 13.7517 | 14.4469
WB | 50079712 | M011 | KILKIVAN-MARYBOROUGH | M011_Kilkivan-Maryborough 66 kV | Limiting Line Name | TR_LINE 33838_1 | TR_LINE 33838_1 | TR_LINE 33838_1 | TR_LINE 33838_1 | TR_LINE 33838_1 | TR_LINE 33838_1 | TR_LINE 33838_1 | TR_LINE 33838_1 | TR_LINE 33838_1 | TR_LINE 33838_1 | TR_LINE 33838_1 | TR_LINE 33838_1 | TR_LINE 33838_1 | TR_LINE 33838_1 | TR_LINE 33838_1
WB | 50079712 | M011 | KILKIVAN-MARYBOROUGH | M011_Kilkivan-Maryborough 66 kV | Loading (A) | 10.4862 | 10.5139 | 10.5139 | 13.9912 | 14.0118 | 14.0118 | 17.2463 | 17.2646 | 17.2646 | 20.2741 | 20.276 | 20.2802 | 22.8996 | 22.9653 | 22.9705
WB | 50079712 | M011 | KILKIVAN-MARYBOROUGH | M011_Kilkivan-Maryborough 66 kV | Loading (MVA) | 1.2568 | 1.2567 | 1.2567 | 1.684 | 1.684 | 1.684 | 2.0855 | 2.0855 | 2.0855 | 2.4596 | 2.4596 | 2.4596 | 2.7949 | 2.795 | 2.7949
WB | 50079712 | M011 | KILKIVAN-MARYBOROUGH | M011_Kilkivan-Maryborough 66 kV | Loading (MW) | 1.2566 | 1.2566 | 1.2566 | 1.6836 | 1.6837 | 1.6837 | 2.0849 | 2.0848 | 2.0848 | 2.4586 | 2.4585 | 2.4586 | 2.7934 | 2.7935 | 2.7933
WB | 50079712 | M011 | KILKIVAN-MARYBOROUGH | M011_Kilkivan-Maryborough 66 kV | Power Factor | 0.99989 | 0.99988 | 0.99988 | 0.9998 | 0.9998 | 0.9998 | 0.99969 | 0.99969 | 0.99969 | 0.99958 | 0.99956 | 0.99958 | 0.99944 | 0.99946 | 0.99943
WB | 50079712 | M011 | KILKIVAN-MARYBOROUGH | M011_Kilkivan-Maryborough 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
WB | 50079712 | M011 | KILKIVAN-MARYBOROUGH | M011_Kilkivan-Maryborough 66 kV | Time | 16:30 | 19:00 | 0:00 | 16:30 | 19:00 | 0:00 | 16:00 | 19:00 | 0:00 | 16:00 | 18:00 | 5:30 | 9:00 | 18:00 | 5:30
WB | 50079712 | M011 | KILKIVAN-MARYBOROUGH | M011_Kilkivan-Maryborough 66 kV | Voltage at Constrained Conductor | 69.1956 | 69.0114 | 69.0114 | 69.4899 | 69.389 | 69.389 | 69.8155 | 69.7413 | 69.7413 | 70.0438 | 70.0351 | 70.0228 | 70.4668 | 70.2668 | 70.2487
WB | 50079714 | M017 | ROCKY ST - MBOROUGH CITY T/LINE | M017_Rocky St - Maryborough City 66 kV | % of Rated A | 6.8205 | 6.465 | 7.1847 | 6.9068 | 6.5383 | 7.2662 | 7.1289 | 6.7509 | 7.5024 | 7.3366 | 6.9445 | 7.7173 | 7.5637 | 7.1757 | 7.9783
WB | 50079714 | M017 | ROCKY ST - MBOROUGH CITY T/LINE | M017_Rocky St - Maryborough City 66 kV | Limiting Line Name | TR_LINE 7924_1 | TR_LINE 7924_1 | TR_LINE 7924_1 | TR_LINE 7924_1 | TR_LINE 7924_1 | TR_LINE 7924_1 | TR_LINE 7924_1 | TR_LINE 7924_1 | TR_LINE 7924_1 | TR_LINE 7924_1 | TR_LINE 7924_1 | TR_LINE 7924_1 | TR_LINE 7924_1 | TR_LINE 7924_1 | TR_LINE 7924_1
WB | 50079714 | M017 | ROCKY ST - MBOROUGH CITY T/LINE | M017_Rocky St - Maryborough City 66 kV | Loading (A) | 37.3764 | 37.4325 | 37.4325 | 37.8492 | 37.8565 | 37.857 | 39.0662 | 39.0877 | 39.0877 | 40.2045 | 40.2087 | 40.2073 | 41.449 | 41.5473 | 41.5668
WB | 50079714 | M017 | ROCKY ST - MBOROUGH CITY T/LINE | M017_Rocky St - Maryborough City 66 kV | Loading (MVA) | 4.4152 | 4.4059 | 4.4059 | 4.4705 | 4.4616 | 4.4705 | 4.615 | 4.6124 | 4.6124 | 4.7482 | 4.7481 | 4.7482 | 4.9102 | 4.9071 | 4.9093
WB | 50079714 | M017 | ROCKY ST - MBOROUGH CITY T/LINE | M017_Rocky St - Maryborough City 66 kV | Loading (MW) | 4.3558 | 4.3545 | 4.3545 | 4.4103 | 4.409 | 4.4103 | 4.5549 | 4.5536 | 4.5536 | 4.6873 | 4.6873 | 4.6873 | 4.8475 | 4.8461 | 4.8474
WB | 50079714 | M017 | ROCKY ST - MBOROUGH CITY T/LINE | M017_Rocky St - Maryborough City 66 kV | Power Factor | 0.98655 | 0.98835 | 0.98835 | 0.98652 | 0.98821 | 0.98653 | 0.98699 | 0.98726 | 0.98726 | 0.98718 | 0.98719 | 0.98719 | 0.98722 | 0.98758 | 0.9874
WB | 50079714 | M017 | ROCKY ST - MBOROUGH CITY T/LINE | M017_Rocky St - Maryborough City 66 kV | Rating (A) | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521
WB | 50079714 | M017 | ROCKY ST - MBOROUGH CITY T/LINE | M017_Rocky St - Maryborough City 66 kV | Time | 16:00 | 19:00 | 0:00 | 16:00 | 19:00 | 6:30 | 16:00 | 19:00 | 0:00 | 16:00 | 18:00 | 6:30 | 9:00 | 18:00 | 7:00
WB | 50079714 | M017 | ROCKY ST - MBOROUGH CITY T/LINE | M017_Rocky St - Maryborough City 66 kV | Voltage at Constrained Conductor | 68.2007 | 67.9549 | 67.9549 | 68.1933 | 68.0445 | 68.1781 | 68.2037 | 68.1281 | 68.1281 | 68.1854 | 68.1775 | 68.1803 | 68.3953 | 68.1898 | 68.1885
WB | 50079715 | M018 | MBOROUGH - MBOROUGH CITY T/TUAN | M018_Maryborough-Maryborough City 66 kV | % of Rated A | 10.03 | 9.4934 | 10.5503 | 9.0301 | 8.5408 | 9.4917 | 8.1933 | 7.7546 | 8.6172 | 7.4686 | 7.0613 | 7.8527 | 6.8882 | 6.5156 | 7.245
WB | 50079715 | M018 | MBOROUGH - MBOROUGH CITY T/TUAN | M018_Maryborough-Maryborough City 66 kV | Limiting Line Name | TR_LINE 122105_1 | TR_LINE 122105_1 | TR_LINE 122105_1 | TR_LINE 122105_1 | TR_LINE 122105_1 | TR_LINE 122105_1 | TR_LINE 122105_1 | TR_LINE 122105_1 | TR_LINE 122105_1 | TR_LINE 122105_1 | TR_LINE 122105_1 | TR_LINE 122105_1 | TR_LINE 122105_1 | TR_LINE 122105_1 | TR_LINE 122105_1
WB | 50079715 | M018 | MBOROUGH - MBOROUGH CITY T/TUAN | M018_Maryborough-Maryborough City 66 kV | Loading (A) | 54.9642 | 54.967 | 54.967 | 49.4852 | 49.4515 | 49.4515 | 44.8991 | 44.8992 | 44.8957 | 40.9277 | 40.8847 | 40.9127 | 37.7473 | 37.7252 | 37.7464
WB | 50079715 | M018 | MBOROUGH - MBOROUGH CITY T/TUAN | M018_Maryborough-Maryborough City 66 kV | Loading (MVA) | 6.4852 | 6.4679 | 6.4679 | 5.8393 | 5.8265 | 5.8265 | 5.3295 | 5.329 | 5.3233 | 4.8573 | 4.8539 | 4.8493 | 4.4818 | 4.4739 | 4.4815
WB | 50079715 | M018 | MBOROUGH - MBOROUGH CITY T/TUAN | M018_Maryborough-Maryborough City 66 kV | Loading (MW) | 5.256 | 5.2547 | 5.2547 | 4.4298 | 4.4285 | 4.4285 | 3.7303 | 3.7303 | 3.7303 | 3.0332 | 3.0318 | 3.0332 | 2.4072 | 2.4072 | 2.4072
WB | 50079715 | M018 | MBOROUGH - MBOROUGH CITY T/TUAN | M018_Maryborough-Maryborough City 66 kV | Power Factor | 0.81045 | 0.81244 | 0.81244 | 0.75862 | 0.76006 | 0.76006 | 0.69993 | 0.69999 | 0.70074 | 0.62446 | 0.62462 | 0.62549 | 0.5371 | 0.53805 | 0.53714
WB | 50079715 | M018 | MBOROUGH - MBOROUGH CITY T/TUAN | M018_Maryborough-Maryborough City 66 kV | Rating (A) | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521
WB | 50079715 | M018 | MBOROUGH - MBOROUGH CITY T/TUAN | M018_Maryborough-Maryborough City 66 kV | Time | 16:30 | 19:00 | 0:00 | 16:30 | 19:00 | 0:00 | 16:30 | 17:30 | 7:30 | 16:30 | 17:30 | 7:30 | 16:00 | 18:30 | 6:30
WB | 50079715 | M018 | MBOROUGH - MBOROUGH CITY T/TUAN | M018_Maryborough-Maryborough City 66 kV | Voltage at Constrained Conductor | 68.1219 | 67.9356 | 67.9356 | 68.1278 | 68.0248 | 68.0248 | 68.5308 | 68.5249 | 68.4569 | 68.5196 | 68.5435 | 68.4319 | 68.5495 | 68.4685 | 68.5466
WB | 50079735 | M007 | PROSTON T/LINE | M007_Proston 66 kV | % of Rated A | 4.0631 | 3.1672 | 3.3243 | 4.514 | 3.5187 | 3.6932 | 5.141 | 4.0075 | 4.2063 | 5.8698 | 4.5757 | 4.8026 | 6.6118 | 5.1541 | 5.4097
WB | 50079735 | M007 | PROSTON T/LINE | M007_Proston 66 kV | Limiting Line Name | TR_LINE 7264_1 | TR_LINE 7264_1 | TR_LINE 7264_1 | TR_LINE 7264_1 | TR_LINE 7264_1 | TR_LINE 7264_1 | TR_LINE 7264_1 | TR_LINE 7264_1 | TR_LINE 7264_1 | TR_LINE 7264_1 | TR_LINE 7264_1 | TR_LINE 7264_1 | TR_LINE 7264_1 | TR_LINE 7264_1 | TR_LINE 7264_1
WB | 50079735 | M007 | PROSTON T/LINE | M007_Proston 66 kV | Loading (A) | 4.0224 | 4.0223 | 4.0224 | 4.4688 | 4.4687 | 4.4688 | 5.0896 | 5.0895 | 5.0896 | 5.8111 | 5.8111 | 5.8111 | 6.5457 | 6.5457 | 6.5457
WB | 50079735 | M007 | PROSTON T/LINE | M007_Proston 66 kV | Loading (MVA) | 0.47159 | 0.47155 | 0.47159 | 0.52461 | 0.52458 | 0.52461 | 0.59819 | 0.59816 | 0.59819 | 0.68372 | 0.6837 | 0.6837 | 0.77087 | 0.77085 | 0.77085
WB | 50079735 | M007 | PROSTON T/LINE | M007_Proston 66 kV | Loading (MW) | 0.1367 | 0.1367 | 0.1367 | 0.26772 | 0.26772 | 0.26772 | 0.39448 | 0.39448 | 0.39448 | 0.51717 | 0.51717 | 0.51717 | 0.63016 | 0.63016 | 0.63016
WB | 50079735 | M007 | PROSTON T/LINE | M007_Proston 66 kV | Power Factor | 0.28987 | 0.28989 | 0.28987 | 0.51031 | 0.51034 | 0.51032 | 0.65946 | 0.65948 | 0.65945 | 0.75641 | 0.75643 | 0.75643 | 0.81746 | 0.81748 | 0.81748
WB | 50079735 | M007 | PROSTON T/LINE | M007_Proston 66 kV | Rating (A) | 99 | 127 | 121 | 99 | 127 | 121 | 99 | 127 | 121 | 99 | 127 | 121 | 99 | 127 | 121
WB | 50079735 | M007 | PROSTON T/LINE | M007_Proston 66 kV | Time | 16:00 | 18:30 | 7:00 | 16:30 | 19:00 | 7:00 | 16:30 | 19:00 | 6:30 | 9:00 | 17:30 | 5:30 | 9:00 | 17:30 | 5:30
WB | 50079735 | M007 | PROSTON T/LINE | M007_Proston 66 kV | Voltage at Constrained Conductor | 67.6881 | 67.6856 | 67.6881 | 67.7772 | 67.7745 | 67.777 | 67.8572 | 67.8547 | 67.8572 | 67.9301 | 67.9277 | 67.9277 | 67.9937 | 67.9913 | 67.9913
WB | 50079738 | M051 | TARONG TIE 66KV T/LINE | M051_Tarong Tie 66 kV | % of Rated A | 6.983 | 5.4152 | 5.6613 | 9.4849 | 7.3555 | 7.6898 | 11.863 | 9.1997 | 9.6178 | 14.112 | 10.9437 | 11.4411 | 16.1646 | 12.5355 | 13.1052
WB | 50079738 | M051 | TARONG TIE 66KV T/LINE | M051_Tarong Tie 66 kV | Limiting Line Name | TR_LINE 37804_1 | TR_LINE 37804_1 | TR_LINE 37804_1 | TR_LINE 37804_1 | TR_LINE 37804_1 | TR_LINE 37804_1 | TR_LINE 37804_1 | TR_LINE 37804_1 | TR_LINE 37804_1 | TR_LINE 37804_1 | TR_LINE 37804_1 | TR_LINE 37804_1 | TR_LINE 37804_1 | TR_LINE 37804_1 | TR_LINE 37804_1
WB | 50079738 | M051 | TARONG TIE 66KV T/LINE | M051_Tarong Tie 66 kV | Loading (A) | 7.4718 | 7.473 | 7.4729 | 10.1488 | 10.1506 | 10.1505 | 12.6934 | 12.6956 | 12.6955 | 15.0998 | 15.1023 | 15.1023 | 17.2961 | 17.299 | 17.2989
WB | 50079738 | M051 | TARONG TIE 66KV T/LINE | M051_Tarong Tie 66 kV | Loading (MVA) | 0.90148 | 0.90142 | 0.90142 | 1.228 | 1.228 | 1.228 | 1.54 | 1.54 | 1.54 | 1.8365 | 1.8365 | 1.8365 | 2.1084 | 2.1083 | 2.1083
WB | 50079738 | M051 | TARONG TIE 66KV T/LINE | M051_Tarong Tie 66 kV | Loading (MW) | 0.83457 | 0.83457 | 0.83457 | 1.1821 | 1.1821 | 1.1821 | 1.506 | 1.506 | 1.506 | 1.8105 | 1.8105 | 1.8105 | 2.0878 | 2.0878 | 2.0878
WB | 50079738 | M051 | TARONG TIE 66KV T/LINE | M051_Tarong Tie 66 kV | Power Factor | 0.92578 | 0.92584 | 0.92584 | 0.96259 | 0.96262 | 0.96262 | 0.97789 | 0.97791 | 0.97791 | 0.98582 | 0.98583 | 0.98583 | 0.99024 | 0.99025 | 0.99024
WB | 50079738 | M051 | TARONG TIE 66KV T/LINE | M051_Tarong Tie 66 kV | Rating (A) | 107 | 138 | 132 | 107 | 138 | 132 | 107 | 138 | 132 | 107 | 138 | 132 | 107 | 138 | 132
WB | 50079738 | M051 | TARONG TIE 66KV T/LINE | M051_Tarong Tie 66 kV | Time | 16:30 | 18:00 | 4:30 | 16:30 | 18:00 | 4:30 | 16:30 | 18:00 | 4:30 | 16:30 | 18:00 | 4:30 | 16:30 | 18:00 | 4:30
WB | 50079738 | M051 | TARONG TIE 66KV T/LINE | M051_Tarong Tie 66 kV | Voltage at Constrained Conductor | 69.658 | 69.6424 | 69.643 | 69.8608 | 69.846 | 69.8466 | 70.0466 | 70.033 | 70.0334 | 70.2201 | 70.2071 | 70.2075 | 70.3776 | 70.3652 | 70.3656
WB | 50079742 | M033 | Wallaville 66 kV | M033_Wallaville 66 kV | % of Rated A | 10.5435 | 10.1933 | 11.6272 | 10.4382 | 10.2591 | 11.6185 | 10.7254 | 10.5696 | 11.9572 | 11.229 | 11.0487 | 12.5148 | 11.8696 | 11.5581 | 13.0905
WB | 50079742 | M033 | Wallaville 66 kV | M033_Wallaville 66 kV | Limiting Line Name | TR_LINE 214482_2 | TR_LINE 214482_2 | TR_LINE 214482_2 | TR_LINE 214482_2 | TR_LINE 214482_2 | TR_LINE 214482_2 | TR_LINE 214482_2 | TR_LINE 214482_2 | TR_LINE 214482_2 | TR_LINE 214482_2 | TR_LINE 214482_2 | TR_LINE 214482_2 | TR_LINE 214482_2 | TR_LINE 214482_2 | TR_LINE 214482_2
WB | 50079742 | M033 | Wallaville 66 kV | M033_Wallaville 66 kV | Loading (A) | 27.2021 | 27.0122 | 27.2075 | 26.9306 | 27.1867 | 27.1873 | 27.6716 | 28.0094 | 27.9798 | 28.9709 | 29.279 | 29.2846 | 30.6236 | 30.6289 | 30.6317
WB | 50079742 | M033 | Wallaville 66 kV | M033_Wallaville 66 kV | Loading (MVA) | 3.1414 | 3.0975 | 3.1426 | 3.13 | 3.1238 | 3.1239 | 3.2158 | 3.2273 | 3.2201 | 3.3697 | 3.3708 | 3.3723 | 3.5642 | 3.566 | 3.5669
WB | 50079742 | M033 | Wallaville 66 kV | M033_Wallaville 66 kV | Loading (MW) | 0.20402 | 0.20388 | 0.20403 | 0.3072 | 0.30689 | 0.30689 | 0.79903 | 0.7988 | 0.79861 | 1.2808 | 1.2804 | 1.2803 | 1.7347 | 1.7347 | 1.7347
WB | 50079742 | M033 | Wallaville 66 kV | M033_Wallaville 66 kV | Power Factor | 0.064946 | 0.065819 | 0.064924 | 0.098147 | 0.098243 | 0.098239 | 0.24847 | 0.24751 | 0.248 | 0.38008 | 0.37984 | 0.37966 | 0.4867 | 0.48645 | 0.48633
WB | 50079742 | M033 | Wallaville 66 kV | M033_Wallaville 66 kV | Rating (A) | 258 | 265 | 234 | 258 | 265 | 234 | 258 | 265 | 234 | 258 | 265 | 234 | 258 | 265 | 234
WB | 50079742 | M033 | Wallaville 66 kV | M033_Wallaville 66 kV | Time | 16:00 | 17:30 | 7:00 | 16:30 | 17:30 | 5:30 | 16:30 | 18:00 | 5:30 | 16:30 | 17:00 | 6:00 | 16:30 | 19:00 | 6:30
WB | 50079742 | M033 | Wallaville 66 kV | M033_Wallaville 66 kV | Voltage at Constrained Conductor | 66.6739 | 66.2056 | 66.6872 | 67.1016 | 66.3385 | 66.3398 | 67.0948 | 66.5244 | 66.4458 | 67.154 | 66.4679 | 66.4859 | 67.1966 | 67.2183 | 67.2294
WB | 50079743 | M034 | Monduran Dam 66 kV | M034_Monduran Dam 66 kV | % of Rated A | 1.6404 | 1.2218 | 1.2742 | 1.6435 | 1.2246 | 1.2766 | 1.6548 | 1.2351 | 1.287 | 1.6766 | 1.2519 | 1.3042 | 1.704 | 1.2727 | 1.3251
WB | 50079743 | M034 | Monduran Dam 66 kV | M034_Monduran Dam 66 kV | Limiting Line Name | TR_LINE 209283_1 | TR_LINE 209283_1 | TR_LINE 209283_1 | TR_LINE 209283_1 | TR_LINE 209283_1 | TR_LINE 209283_1 | TR_LINE 209283_1 | TR_LINE 209283_1 | TR_LINE 209283_1 | TR_LINE 209283_1 | TR_LINE 209283_1 | TR_LINE 209283_1 | TR_LINE 209283_1 | TR_LINE 209283_1 | TR_LINE 209283_1
WB | 50079743 | M034 | Monduran Dam 66 kV | M034_Monduran Dam 66 kV | Loading (A) | 2.1653 | 2.1626 | 2.1662 | 2.1694 | 2.1676 | 2.1702 | 2.1843 | 2.1861 | 2.1879 | 2.2131 | 2.2158 | 2.2172 | 2.2493 | 2.2526 | 2.2526
WB | 50079743 | M034 | Monduran Dam 66 kV | M034_Monduran Dam 66 kV | Loading (MVA) | 0.25187 | 0.25125 | 0.25208 | 0.2529 | 0.25247 | 0.25309 | 0.25474 | 0.25516 | 0.2556 | 0.25844 | 0.25909 | 0.25938 | 0.26294 | 0.26371 | 0.26371
WB | 50079743 | M034 | Monduran Dam 66 kV | M034_Monduran Dam 66 kV | Loading (MW) | 0.012067 | 0.01204 | 0.012075 | 0.010055 | 0.010073 | 0.010047 | 0.030674 | 0.030655 | 0.030637 | 0.050101 | 0.050072 | 0.050313 | 0.067833 | 0.068053 | 0.068053
WB | 50079743 | M034 | Monduran Dam 66 kV | M034_Monduran Dam 66 kV | Power Factor | 0.047907 | 0.047919 | 0.047903 | 0.039757 | 0.039899 | 0.039697 | 0.12042 | 0.12014 | 0.11986 | 0.19386 | 0.19326 | 0.19397 | 0.25798 | 0.25806 | 0.25806
WB | 50079743 | M034 | Monduran Dam 66 kV | M034_Monduran Dam 66 kV | Rating (A) | 132 | 177 | 170 | 132 | 177 | 170 | 132 | 177 | 170 | 132 | 177 | 170 | 132 | 177 | 170
WB | 50079743 | M034 | Monduran Dam 66 kV | M034_Monduran Dam 66 kV | Time | 16:30 | 18:30 | 6:30 | 16:30 | 18:30 | 6:30 | 16:30 | 18:30 | 6:30 | 16:30 | 18:30 | 6:30 | 16:30 | 18:30 | 4:30
WB | 50079743 | M034 | Monduran Dam 66 kV | M034_Monduran Dam 66 kV | Voltage at Constrained Conductor | 67.1583 | 67.0749 | 67.1853 | 67.3062 | 67.2483 | 67.3306 | 67.3308 | 67.3884 | 67.4469 | 67.4205 | 67.5096 | 67.5426 | 67.4916 | 67.5898 | 67.5902
WB | 50079744 | M041 | WST BBERG - MEADOWVALE T/LINE | M041_West Bundaberg-Meadowvale 66 kV | % of Rated A | 12.5454 | 9.1077 | 10.9893 | 15.0232 | 11.0479 | 13.3168 | 17.835 | 13.0916 | 15.7793 | 20.6709 | 15.154 | 18.2642 | 23.344 | 17.0993 | 20.6079
WB | 50079744 | M041 | WST BBERG - MEADOWVALE T/LINE | M041_West Bundaberg-Meadowvale 66 kV | Limiting Line Name | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1
WB | 50079744 | M041 | WST BBERG - MEADOWVALE T/LINE | M041_West Bundaberg-Meadowvale 66 kV | Loading (A) | 28.3526 | 28.3251 | 28.3523 | 33.9525 | 34.3588 | 34.3573 | 40.307 | 40.7147 | 40.7106 | 46.7163 | 47.129 | 47.1216 | 52.7575 | 53.1789 | 53.1685
WB | 50079744 | M041 | WST BBERG - MEADOWVALE T/LINE | M041_West Bundaberg-Meadowvale 66 kV | Loading (MVA) | 3.2644 | 3.2417 | 3.2641 | 3.9156 | 3.9384 | 3.9391 | 4.654 | 4.6743 | 4.6749 | 5.3989 | 5.417 | 5.4177 | 6.1007 | 6.1172 | 6.1178
WB | 50079744 | M041 | WST BBERG - MEADOWVALE T/LINE | M041_West Bundaberg-Meadowvale 66 kV | Loading (MW) | 2.0704 | 2.0704 | 2.0703 | 3.0199 | 3.02 | 3.02 | 3.9059 | 3.906 | 3.906 | 4.7468 | 4.7467 | 4.7467 | 5.5119 | 5.5119 | 5.5119
WB | 50079744 | M041 | WST BBERG - MEADOWVALE T/LINE | M041_West Bundaberg-Meadowvale 66 kV | Power Factor | 0.63423 | 0.63868 | 0.63428 | 0.77126 | 0.7668 | 0.76667 | 0.83927 | 0.83564 | 0.83552 | 0.87921 | 0.87626 | 0.87616 | 0.90348 | 0.90105 | 0.90096
WB | 50079744 | M041 | WST BBERG - MEADOWVALE T/LINE | M041_West Bundaberg-Meadowvale 66 kV | Rating (A) | 226 | 311 | 258 | 226 | 311 | 258 | 226 | 311 | 258 | 226 | 311 | 258 | 226 | 311 | 258
WB | 50079744 | M041 | WST BBERG - MEADOWVALE T/LINE | M041_West Bundaberg-Meadowvale 66 kV | Time | 15:30 | 17:30 | 7:30 | 9:00 | 17:00 | 6:00 | 9:00 | 17:00 | 6:00 | 9:00 | 17:00 | 6:00 | 9:00 | 17:00 | 6:00
WB | 50079744 | M041 | WST BBERG - MEADOWVALE T/LINE | M041_West Bundaberg-Meadowvale 66 kV | Voltage at Constrained Conductor | 66.4729 | 66.0758 | 66.4679 | 66.5832 | 66.1793 | 66.1935 | 66.663 | 66.2832 | 66.2989 | 66.7235 | 66.3612 | 66.3791 | 66.7632 | 66.4129 | 66.4325
WB | 50079745 | M042 | MEADOWVALE - GOOBURRUM T/LINE | M042_Meadowvale-Gooburrum 66 kV | % of Rated A | 3.084 | 2.3563 | 2.8905 | 5.064 | 3.8717 | 4.7493 | 6.9622 | 5.3225 | 6.5286 | 8.8001 | 6.7256 | 8.2494 | 10.5036 | 8.0265 | 9.8448
WB | 50079745 | M042 | MEADOWVALE - GOOBURRUM T/LINE | M042_Meadowvale-Gooburrum 66 kV | Limiting Line Name | TR_LINE 7779_2 | TR_LINE 7779_2 | TR_LINE 7779_2 | TR_LINE 7779_2 | TR_LINE 7779_2 | TR_LINE 7779_2 | TR_LINE 7779_2 | TR_LINE 7779_2 | TR_LINE 7779_2 | TR_LINE 7779_2 | TR_LINE 7779_2 | TR_LINE 7779_2 | TR_LINE 7779_2 | TR_LINE 7779_2 | TR_LINE 7779_2
WB | 50079745 | M042 | MEADOWVALE - GOOBURRUM T/LINE | M042_Meadowvale-Gooburrum 66 kV | Loading (A) | 3.4232 | 3.4403 | 3.4397 | 5.621 | 5.6527 | 5.6516 | 7.7281 | 7.7708 | 7.7691 | 9.7681 | 9.8193 | 9.8168 | 11.659 | 11.7187 | 11.7153
WB | 50079745 | M042 | MEADOWVALE - GOOBURRUM T/LINE | M042_Meadowvale-Gooburrum 66 kV | Loading (MVA) | 0.39407 | 0.39354 | 0.39356 | 0.64826 | 0.64796 | 0.64797 | 0.89233 | 0.89216 | 0.89217 | 1.1289 | 1.1287 | 1.1287 | 1.3483 | 1.3481 | 1.3481
WB | 50079745 | M042 | MEADOWVALE - GOOBURRUM T/LINE | M042_Meadowvale-Gooburrum 66 kV | Loading (MW) | 0.37024 | 0.3703 | 0.3703 | 0.63441 | 0.63446 | 0.63446 | 0.88275 | 0.8828 | 0.8828 | 1.1218 | 1.1217 | 1.1217 | 1.3427 | 1.3426 | 1.3426
WB | 50079745 | M042 | MEADOWVALE - GOOBURRUM T/LINE | M042_Meadowvale-Gooburrum 66 kV | Power Factor | 0.93954 | 0.94095 | 0.94091 | 0.97863 | 0.97916 | 0.97914 | 0.98926 | 0.9895 | 0.98949 | 0.99369 | 0.99382 | 0.99381 | 0.99588 | 0.99596 | 0.99596
WB | 50079745 | M042 | MEADOWVALE - GOOBURRUM T/LINE | M042_Meadowvale-Gooburrum 66 kV | Rating (A) | 111 | 146 | 119 | 111 | 146 | 119 | 111 | 146 | 119 | 111 | 146 | 119 | 111 | 146 | 119
WB | 50079745 | M042 | MEADOWVALE - GOOBURRUM T/LINE | M042_Meadowvale-Gooburrum 66 kV | Time | 9:00 | 17:00 | 6:00 | 9:00 | 17:00 | 6:00 | 9:00 | 17:00 | 6:00 | 9:00 | 17:00 | 6:00 | 9:00 | 17:00 | 6:00
WB | 50079745 | M042 | MEADOWVALE - GOOBURRUM T/LINE | M042_Meadowvale-Gooburrum 66 kV | Voltage at Constrained Conductor | 66.4625 | 66.0448 | 66.0573 | 66.5844 | 66.1805 | 66.1947 | 66.6646 | 66.2849 | 66.3005 | 66.7255 | 66.3632 | 66.3811 | 66.7656 | 66.4153 | 66.4349
WB | 50079747 | M025 | 66kV EIDSVOLD T/LINE | M025_Eidsvold 66 kV | % of Rated A | 2.4624 | 1.9108 | 1.9983 | 2.9836 | 2.3112 | 2.4183 | 3.8938 | 3.0242 | 3.1617 | 4.9866 | 3.8805 | 4.0569 | 6.0741 | 4.7305 | 4.9455
WB | 50079747 | M025 | 66kV EIDSVOLD T/LINE | M025_Eidsvold 66 kV | Limiting Line Name | TR_LINE 77926_1 | TR_LINE 77926_1 | TR_LINE 77926_1 | TR_LINE 77926_1 | TR_LINE 77926_1 | TR_LINE 77926_1 | TR_LINE 77926_1 | TR_LINE 77926_1 | TR_LINE 77926_1 | TR_LINE 77926_1 | TR_LINE 77926_1 | TR_LINE 77926_1 | TR_LINE 77926_1 | TR_LINE 77926_1 | TR_LINE 77926_1
WB | 50079747 | M025 | 66kV EIDSVOLD T/LINE | M025_Eidsvold 66 kV | Loading (A) | 2.6348 | 2.6369 | 2.6378 | 3.1925 | 3.1895 | 3.1921 | 4.1664 | 4.1734 | 4.1734 | 5.3357 | 5.3551 | 5.3551 | 6.4993 | 6.5281 | 6.5281
WB | 50079747 | M025 | 66kV EIDSVOLD T/LINE | M025_Eidsvold 66 kV | Loading (MVA) | 0.30935 | 0.30986 | 0.31007 | 0.37644 | 0.37502 | 0.37626 | 0.48515 | 0.48257 | 0.48257 | 0.62241 | 0.62043 | 0.62043 | 0.7604 | 0.75908 | 0.75908
WB | 50079747 | M025 | 66kV EIDSVOLD T/LINE | M025_Eidsvold 66 kV | Loading (MW) | 0.055497 | 0.055497 | 0.055497 | 0.21968 | 0.21968 | 0.21968 | 0.38521 | 0.3852 | 0.3852 | 0.55013 | 0.5501 | 0.5501 | 0.70438 | 0.70438 | 0.70438
WB | 50079747 | M025 | 66kV EIDSVOLD T/LINE | M025_Eidsvold 66 kV | Power Factor | 0.1794 | 0.17911 | 0.17898 | 0.58357 | 0.58579 | 0.58386 | 0.79401 | 0.79823 | 0.79823 | 0.88387 | 0.88665 | 0.88665 | 0.92634 | 0.92795 | 0.92795
WB | 50079747 | M025 | 66kV EIDSVOLD T/LINE | M025_Eidsvold 66 kV | Rating (A) | 107 | 138 | 132 | 107 | 138 | 132 | 107 | 138 | 132 | 107 | 138 | 132 | 107 | 138 | 132
WB | 50079747 | M025 | 66kV EIDSVOLD T/LINE | M025_Eidsvold 66 kV | Time | 12:30 | 19:00 | 6:30 | 16:30 | 17:30 | 7:30 | 9:00 | 18:30 | 5:00 | 16:30 | 19:00 | 0:00 | 16:30 | 19:00 | 0:00
WB | 50079747 | M025 | 66kV EIDSVOLD T/LINE | M025_Eidsvold 66 kV | Voltage at Constrained Conductor | 67.7854 | 67.843 | 67.8667 | 68.0785 | 67.8842 | 68.0533 | 67.2293 | 66.7577 | 66.758 | 67.3488 | 66.8899 | 66.8899 | 67.5482 | 67.1336 | 67.1336
WB | 82554175 | M023 | 6242 PIALBA - POINT VERNON | M023_6242 (Pialba-Point Vernon) 66 kV | % of Rated A | 8.6029 | 7.7959 | 9.5202 | 10.6352 | 9.6299 | 11.7623 | 12.8302 | 11.6171 | 14.1897 | 15.0125 | 13.5877 | 16.6007 | 17.0218 | 15.4192 | 18.8451
WB | 82554175 | M023 | 6242 PIALBA - POINT VERNON | M023_6242 (Pialba-Point Vernon) 66 kV | Limiting Line Name | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1
WB | 82554175 | M023 | 6242 PIALBA - POINT VERNON | M023_6242 (Pialba-Point Vernon) 66 kV | Loading (A) | 52.0476 | 52.0766 | 52.0753 | 64.3427 | 64.3276 | 64.3398 | 77.623 | 77.6024 | 77.6176 | 90.8226 | 90.7629 | 90.803 | 102.9791 | 102.9973 | 103.08
WB | 82554175 | M023 | 6242 PIALBA - POINT VERNON | M023_6242 (Pialba-Point Vernon) 66 kV | Loading (MVA) | 6.2673 | 6.2804 | 6.2798 | 7.7365 | 7.7518 | 7.7394 | 9.3475 | 9.3515 | 9.3485 | 10.9485 | 10.9545 | 10.9505 | 12.447 | 12.4458 | 12.4403
WB | 82554175 | M023 | 6242 PIALBA - POINT VERNON | M023_6242 (Pialba-Point Vernon) 66 kV | Loading (MW) | 3.5635 | 3.5635 | 3.5635 | 5.8139 | 5.8139 | 5.8139 | 7.853 | 7.853 | 7.853 | 9.7298 | 9.7298 | 9.7298 | 11.4058 | 11.4058 | 11.4057
WB | 82554175 | M023 | 6242 PIALBA - POINT VERNON | M023_6242 (Pialba-Point Vernon) 66 kV | Power Factor | 0.56859 | 0.56741 | 0.56746 | 0.75148 | 0.75 | 0.75121 | 0.84012 | 0.83976 | 0.84003 | 0.88868 | 0.8882 | 0.88853 | 0.91635 | 0.91644 | 0.91683
WB | 82554175 | M023 | 6242 PIALBA - POINT VERNON | M023_6242 (Pialba-Point Vernon) 66 kV | Rating (A) | 605 | 668 | 547 | 605 | 668 | 547 | 605 | 668 | 547 | 605 | 668 | 547 | 605 | 668 | 547
WB | 82554175 | M023 | 6242 PIALBA - POINT VERNON | M023_6242 (Pialba-Point Vernon) 66 kV | Time | 15:30 | 18:00 | 5:30 | 16:00 | 19:00 | 7:00 | 16:00 | 18:00 | 7:00 | 16:00 | 18:00 | 7:00 | 9:00 | 18:00 | 7:00
WB | 82554175 | M023 | 6242 PIALBA - POINT VERNON | M023_6242 (Pialba-Point Vernon) 66 kV | Voltage at Constrained Conductor | 69.5217 | 69.6278 | 69.6231 | 69.4204 | 69.5734 | 69.4487 | 69.5257 | 69.5737 | 69.5382 | 69.5988 | 69.6826 | 69.6262 | 69.7838 | 69.7646 | 69.6781
WB | 82624538 | SOBU-BARG-1 | STH BUNDABERG-BARGARA 66KV FDR | SOBU-BARG-1_SOBU-Bargara-1 66 kV | % of Rated A | 8.5031 | 5.5423 | 6.5076 | 11.0476 | 7.1984 | 8.452 | 13.433 | 8.7495 | 10.2729 | 15.6993 | 10.2228 | 12.0024 | 17.7916 | 11.5831 | 13.5992
WB | 82624538 | SOBU-BARG-1 | STH BUNDABERG-BARGARA 66KV FDR | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Limiting Line Name | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1
WB | 82624538 | SOBU-BARG-1 | STH BUNDABERG-BARGARA 66KV FDR | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Loading (A) | 34.8627 | 35.0828 | 35.0759 | 45.2951 | 45.5658 | 45.5561 | 55.0754 | 55.3841 | 55.371 | 64.3671 | 64.7105 | 64.6931 | 72.9454 | 73.3212 | 73.2997
WB | 82624538 | SOBU-BARG-1 | STH BUNDABERG-BARGARA 66KV FDR | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Loading (MVA) | 4.0434 | 4.0435 | 4.0434 | 5.2637 | 5.2637 | 5.2637 | 6.4092 | 6.4092 | 6.4092 | 7.4987 | 7.4986 | 7.4986 | 8.5044 | 8.5044 | 8.5044
WB | 82624538 | SOBU-BARG-1 | STH BUNDABERG-BARGARA 66KV FDR | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Loading (MW) | 4.0431 | 4.0431 | 4.043 | 5.2628 | 5.2628 | 5.2628 | 6.4077 | 6.4076 | 6.4076 | 7.4962 | 7.4961 | 7.4961 | 8.5009 | 8.5007 | 8.5008
WB | 82624538 | SOBU-BARG-1 | STH BUNDABERG-BARGARA 66KV FDR | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Power Factor | 0.9999 | 0.99991 | 0.9999 | 0.99984 | 0.99983 | 0.99983 | 0.99976 | 0.99975 | 0.99975 | 0.99967 | 0.99966 | 0.99966 | 0.99958 | 0.99957 | 0.99957
WB | 82624538 | SOBU-BARG-1 | STH BUNDABERG-BARGARA 66KV FDR | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Rating (A) | 410 | 633 | 539 | 410 | 633 | 539 | 410 | 633 | 539 | 410 | 633 | 539 | 410 | 633 | 539
WB | 82624538 | SOBU-BARG-1 | STH BUNDABERG-BARGARA 66KV FDR | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Time | 9:00 | 17:00 | 6:00 | 9:00 | 17:00 | 6:00 | 9:00 | 17:00 | 6:00 | 9:00 | 17:00 | 6:00 | 9:00 | 17:00 | 6:00
WB | 82624538 | SOBU-BARG-1 | STH BUNDABERG-BARGARA 66KV FDR | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Voltage at Constrained Conductor | 66.9622 | 66.5425 | 66.5548 | 67.093 | 66.6941 | 66.7083 | 67.1872 | 66.8124 | 66.8281 | 67.2603 | 66.903 | 66.921 | 67.3111 | 66.9658 | 66.9855
WB | 83859989 | 785 | 785 ISIS 132KV | 785_ISIS 132 kV | % of Rated A | 83.4313 | 47.1829 | 52.8011 | 86.106 | 48.8349 | 54.4878 | 87.5849 | 49.8443 | 55.54 | 89.2296 | 50.8726 | 56.4758 | 90.6119 | 51.7963 | 57.4052
WB | 83859989 | 785 | 785 ISIS 132KV | 785_ISIS 132 kV | Limiting Line Name | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1
WB | 83859989 | 785 | 785 ISIS 132KV | 785_ISIS 132 kV | Loading (A) | 206.9097 | 186.8441 | 207.5082 | 213.5428 | 193.3862 | 214.1371 | 217.2105 | 197.3834 | 218.2723 | 221.2895 | 201.4556 | 221.95 | 224.7176 | 205.1133 | 225.6026
WB | 83859989 | 785 | 785 ISIS 132KV | 785_ISIS 132 kV | Loading (MVA) | 49.9044 | 45.5017 | 50.0626 | 51.5001 | 47.1093 | 51.6583 | 52.4112 | 48.0898 | 52.6359 | 53.3785 | 49.0775 | 53.5464 | 54.1046 | 49.958 | 54.4067
WB | 83859989 | 785 | 785 ISIS 132KV | 785_ISIS 132 kV | Loading (MW) | 48.7644 | 44.4374 | 48.9147 | 50.4489 | 46.1394 | 50.5993 | 51.5442 | 47.2125 | 51.6583 | 52.5976 | 48.2712 | 52.7417 | 53.5596 | 49.2092 | 53.6764
WB | 83859989 | 785 | 785 ISIS 132KV | 785_ISIS 132 kV | Power Factor | 0.97716 | 0.97661 | 0.97707 | 0.97959 | 0.97941 | 0.9795 | 0.98346 | 0.98176 | 0.98143 | 0.98537 | 0.98357 | 0.98497 | 0.98993 | 0.98501 | 0.98658
WB | 83859989 | 785 | 785 ISIS 132KV | 785_ISIS 132 kV | Rating (A) | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393
WB | 83859989 | 785 | 785 ISIS 132KV | 785_ISIS 132 kV | Time | 16:00 | 17:00 | 7:00 | 16:00 | 17:00 | 7:00 | 16:00 | 17:00 | 7:00 | 16:00 | 17:00 | 7:00 | 16:00 | 17:00 | 7:00
WB | 83859989 | 785 | 785 ISIS 132KV | 785_ISIS 132 kV | Voltage at Constrained Conductor | 139.2507 | 140.6009 | 139.2892 | 139.2396 | 140.6438 | 139.2797 | 139.3101 | 140.6635 | 139.2267 | 139.2659 | 140.6508 | 139.2883 | 139.0069 | 140.6212 | 139.2347
WB | 83859994 | 784 | 784 ISIS 132KV | 784_ISIS 132 kV | % of Rated A | 82.2344 | 46.5064 | 52.0436 | 84.8702 | 48.1344 | 53.7058 | 86.3275 | 49.1291 | 54.7428 | 87.9483 | 50.1425 | 55.6648 | 89.3101 | 51.0527 | 56.5807
WB | 83859994 | 784 | 784 ISIS 132KV | 784_ISIS 132 kV | Limiting Line Name | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1
WB | 83859994 | 784 | 784 ISIS 132KV | 784_ISIS 132 kV | Loading (A) | 203.9413 | 184.1652 | 204.5312 | 210.4782 | 190.6123 | 211.064 | 214.0921 | 194.5513 | 215.1391 | 218.1117 | 198.5643 | 218.7628 | 221.489 | 202.1689 | 222.3623
WB | 83859994 | 784 | 784 ISIS 132KV | 784_ISIS 132 kV | Loading (MVA) | 49.1875 | 44.8486 | 49.3434 | 50.7598 | 46.4326 | 50.9157 | 51.6571 | 47.3985 | 51.8788 | 52.61 | 48.3717 | 52.7756 | 53.3246 | 49.2392 | 53.6231
WB | 83859994 | 784 | 784 ISIS 132KV | 784_ISIS 132 kV | Loading (MW) | 48.0516 | 43.7883 | 48.1997 | 49.7116 | 45.4657 | 49.8599 | 50.7915 | 46.5234 | 50.9036 | 51.8297 | 47.5668 | 51.9716 | 52.7785 | 48.4913 | 52.8929
WB | 83859994 | 784 | 784 ISIS 132KV | 784_ISIS 132 kV | Power Factor | 0.97691 | 0.97636 | 0.97682 | 0.97935 | 0.97918 | 0.97926 | 0.98324 | 0.98154 | 0.9812 | 0.98517 | 0.98336 | 0.98477 | 0.98976 | 0.98481 | 0.98638
WB | 83859994 | 784 | 784 ISIS 132KV | 784_ISIS 132 kV | Rating (A) | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393
WB | 83859994 | 784 | 784 ISIS 132KV | 784_ISIS 132 kV | Time | 16:00 | 17:00 | 7:00 | 16:00 | 17:00 | 7:00 | 16:00 | 17:00 | 7:00 | 16:00 | 17:00 | 7:00 | 16:00 | 17:00 | 7:00
WB | 83859994 | 784 | 784 ISIS 132KV | 784_ISIS 132 kV | Voltage at Constrained Conductor | 139.248 | 140.5985 | 139.2865 | 139.2362 | 140.6407 | 139.2763 | 139.3056 | 140.6599 | 139.2228 | 139.2607 | 140.6466 | 139.2832 | 139.0001 | 140.6165 | 139.229
WB | 83859997 | 7330 | 7330 MBH 132KV | 7330_Maryborough 132 kV | % of Rated A | 24.4678 | 11.5468 | 25.4345 | 26.8738 | 11.3354 | 27.9382 | 30.3851 | 12.6656 | 31.5922 | 33.6753 | 15.4573 | 35.016 | 36.6925 | 18.0777 | 38.1557
WB | 83859997 | 7330 | 7330 MBH 132KV | 7330_Maryborough 132 kV | Limiting Line Name | TR_LINE 156755_1 | TR_LINE 7684_1 | TR_LINE 156755_1 | TR_LINE 156755_1 | TR_LINE 7684_1 | TR_LINE 156755_1 | TR_LINE 156755_1 | TR_LINE 7684_1 | TR_LINE 156755_1 | TR_LINE 156755_1 | TR_LINE 7684_1 | TR_LINE 156755_1 | TR_LINE 156755_1 | TR_LINE 7684_1 | TR_LINE 156755_1
WB | 83859997 | 7330 | 7330 MBH 132KV | 7330_Maryborough 132 kV | Loading (A) | 137.9982 | 69.281 | 137.855 | 151.5682 | 68.0124 | 151.4253 | 171.3719 | 75.9936 | 171.2295 | 189.9289 | 92.7437 | 189.7869 | 206.9455 | 108.4664 | 206.8039
WB | 83859997 | 7330 | 7330 MBH 132KV | 7330_Maryborough 132 kV | Loading (MVA) | 33.2036 | 16.7348 | 33.1686 | 36.4611 | 16.4344 | 36.4261 | 41.2179 | 18.4405 | 41.1829 | 45.6668 | 22.4946 | 45.6319 | 49.7366 | 26.294 | 49.7016
WB | 83859997 | 7330 | 7330 MBH 132KV | 7330_Maryborough 132 kV | Loading (MW) | 32.7226 | 2.894 | 32.6903 | 35.9513 | 0.37971 | 35.9191 | 40.6737 | 17.506 | 40.6415 | 45.0853 | 21.9014 | 45.0531 | 49.1156 | 25.9074 | 49.0835
WB | 83859997 | 7330 | 7330 MBH 132KV | 7330_Maryborough 132 kV | Power Factor | 0.98551 | 0.17293 | 0.98558 | 0.98602 | 0.023105 | 0.98608 | 0.9868 | 0.94932 | 0.98685 | 0.98726 | 0.97363 | 0.98732 | 0.98751 | 0.9853 | 0.98756
WB | 83859997 | 7330 | 7330 MBH 132KV | 7330_Maryborough 132 kV | Rating (A) | 564 | 600 | 542 | 564 | 600 | 542 | 564 | 600 | 542 | 564 | 600 | 542 | 564 | 600 | 542
WB | 83859997 | 7330 | 7330 MBH 132KV | 7330_Maryborough 132 kV | Time | 9:00 | 19:00 | 8:30 | 9:00 | 19:00 | 8:30 | 9:00 | 17:00 | 8:30 | 9:00 | 17:00 | 8:30 | 9:00 | 17:00 | 8:30
WB | 83859997 | 7330 | 7330 MBH 132KV | 7330_Maryborough 132 kV | Voltage at Constrained Conductor | 138.9157 | 139.4591 | 138.9134 | 138.8867 | 139.5098 | 138.8844 | 138.8627 | 140.0989 | 138.8603 | 138.8191 | 140.034 | 138.8166 | 138.7583 | 139.959 | 138.7558
WB | 83860003 | 7329 | 7329 MBH 132KV | 7329_Maryborough 132 kV | % of Rated A | 24.4788 | 11.5524 | 25.4459 | 26.8859 | 11.3409 | 27.9508 | 30.3987 | 12.6714 | 31.6064 | 33.6905 | 15.4643 | 35.0318 | 36.709 | 18.0859 | 38.1728
WB | 83860003 | 7329 | 7329 MBH 132KV | 7329_Maryborough 132 kV | Limiting Line Name | TR_LINE 156753_1 | TR_LINE 120325_1 | TR_LINE 156753_1 | TR_LINE 156753_1 | TR_LINE 120325_1 | TR_LINE 156753_1 | TR_LINE 156753_1 | TR_LINE 120325_1 | TR_LINE 156753_1 | TR_LINE 156753_1 | TR_LINE 120325_1 | TR_LINE 156753_1 | TR_LINE 156753_1 | TR_LINE 120325_1 | TR_LINE 156753_1
WB | 83860003 | 7329 | 7329 MBH 132KV | 7329_Maryborough 132 kV | Loading (A) | 138.0602 | 69.3143 | 137.9169 | 151.6363 | 68.0452 | 151.4933 | 171.4489 | 76.0284 | 171.3065 | 190.0142 | 92.7859 | 189.8722 | 207.0385 | 108.5155 | 206.8968
WB | 83860003 | 7329 | 7329 MBH 132KV | 7329_Maryborough 132 kV | Loading (MVA) | 33.2185 | 16.7428 | 33.1835 | 36.4775 | 16.4422 | 36.4424 | 41.2364 | 18.4488 | 41.2014 | 45.6874 | 22.5047 | 45.6524 | 49.7589 | 26.3058 | 49.7239
WB | 83860003 | 7329 | 7329 MBH 132KV | 7329_Maryborough 132 kV | Loading (MW) | 32.737 | 2.8941 | 32.7047 | 35.9671 | 0.38107 | 35.9349 | 40.6916 | 17.5143 | 40.6594 | 45.1051 | 21.9116 | 45.073 | 49.1372 | 25.9193 | 49.1051
WB | 83860003 | 7329 | 7329 MBH 132KV | 7329_Maryborough 132 kV | Power Factor | 0.9855 | 0.17285 | 0.98557 | 0.98601 | 0.023176 | 0.98607 | 0.98679 | 0.94934 | 0.98684 | 0.98726 | 0.97364 | 0.98731 | 0.98751 | 0.98531 | 0.98755
WB | 83860003 | 7329 | 7329 MBH 132KV | 7329_Maryborough 132 kV | Rating (A) | 564 | 600 | 542 | 564 | 600 | 542 | 564 | 600 | 542 | 564 | 600 | 542 | 564 | 600 | 542
WB | 83860003 | 7329 | 7329 MBH 132KV | 7329_Maryborough 132 kV | Time | 9:00 | 19:00 | 8:30 | 9:00 | 19:00 | 8:30 | 9:00 | 17:00 | 8:30 | 9:00 | 17:00 | 8:30 | 9:00 | 17:00 | 8:30
WB | 83860003 | 7329 | 7329 MBH 132KV | 7329_Maryborough 132 kV | Voltage at Constrained Conductor | 138.9157 | 139.458 | 138.9134 | 138.8867 | 139.5086 | 138.8844 | 138.8627 | 140.0982 | 138.8603 | 138.8191 | 140.0333 | 138.8166 | 138.7583 | 139.9582 | 138.7558
WB | 83860136 | 7316 | Aramara 132 kV | 7316_Aramara 132 kV | % of Rated A | 30.9033 | 18.2188 | 30.5222 | 32.7653 | 19.8999 | 32.359 | 34.9652 | 21.88 | 34.5291 | 37.0482 | 23.7525 | 36.584 | 38.9489 | 25.4554 | 38.4589
WB | 83860136 | 7316 | Aramara 132 kV | 7316_Aramara 132 kV | Limiting Line Name | TR_LINE 88015_1 | TR_LINE 88015_1 | TR_LINE 88015_1 | TR_LINE 88015_1 | TR_LINE 88015_1 | TR_LINE 88015_1 | TR_LINE 88015_1 | TR_LINE 88015_1 | TR_LINE 88015_1 | TR_LINE 88015_1 | TR_LINE 88015_1 | TR_LINE 88015_1 | TR_LINE 88015_1 | TR_LINE 88015_1 | TR_LINE 88015_1
WB | 83860136 | 7316 | Aramara 132 kV | 7316_Aramara 132 kV | Loading (A) | 337.4641 | 219.5361 | 337.8806 | 357.7974 | 239.7935 | 358.2142 | 381.8199 | 263.6536 | 382.2372 | 404.5667 | 286.2176 | 404.9845 | 425.3218 | 306.7371 | 425.7403
WB | 83860136 | 7316 | Aramara 132 kV | 7316_Aramara 132 kV | Loading (MVA) | 80.8501 | 53.2816 | 80.948 | 85.6692 | 58.1868 | 85.7669 | 91.3491 | 63.9576 | 91.4466 | 96.7082 | 69.3983 | 96.8056 | 101.5778 | 74.3331 | 101.675
WB | 83860136 | 7316 | Aramara 132 kV | 7316_Aramara 132 kV | Loading (MW) | 79.8587 | 53.2338 | 79.9551 | 84.6705 | 58.1311 | 84.7667 | 90.3389 | 63.8918 | 90.4349 | 95.6794 | 69.3175 | 95.7754 | 100.5232 | 74.2354 | 100.619
WB | 83860136 | 7316 | Aramara 132 kV | 7316_Aramara 132 kV | Power Factor | 0.98774 | 0.9991 | 0.98773 | 0.98834 | 0.99904 | 0.98834 | 0.98894 | 0.99897 | 0.98894 | 0.98936 | 0.99884 | 0.98936 | 0.98962 | 0.99869 | 0.98961
WB | 83860136 | 7316 | Aramara 132 kV | 7316_Aramara 132 kV | Rating (A) | 1092 | 1205 | 1107 | 1092 | 1205 | 1107 | 1092 | 1205 | 1107 | 1092 | 1205 | 1107 | 1092 | 1205 | 1107
WB | 83860136 | 7316 | Aramara 132 kV | 7316_Aramara 132 kV | Time | 9:00 | 17:00 | 8:30 | 9:00 | 17:00 | 8:30 | 9:00 | 17:00 | 8:30 | 9:00 | 17:00 | 8:30 | 9:00 | 17:00 | 8:30
WB | 83860136 | 7316 | Aramara 132 kV | 7316_Aramara 132 kV | Voltage at Constrained Conductor | 138.3224 | 140.1234 | 138.3191 | 138.2378 | 140.0962 | 138.2344 | 138.129 | 140.0547 | 138.1255 | 138.0107 | 139.9883 | 138.0071 | 137.8861 | 139.9121 | 137.8824
WB | 83860139 | 7315 | Aramara 132 kV | 7315_Aramara 132 kV | % of Rated A | 30.9076 | 18.2213 | 30.5265 | 32.7699 | 19.9027 | 32.3635 | 34.9701 | 21.883 | 34.534 | 37.0534 | 23.7558 | 36.5891 | 38.9544 | 25.4589 | 38.4643
WB | 83860139 | 7315 | Aramara 132 kV | 7315_Aramara 132 kV | Limiting Line Name | TR_LINE 86019_1 | TR_LINE 86019_1 | TR_LINE 86019_1 | TR_LINE 86019_1 | TR_LINE 86019_1 | TR_LINE 86019_1 | TR_LINE 86019_1 | TR_LINE 86019_1 | TR_LINE 86019_1 | TR_LINE 86019_1 | TR_LINE 86019_1 | TR_LINE 86019_1 | TR_LINE 86019_1 | TR_LINE 86019_1 | TR_LINE 86019_1
WB | 83860139 | 7315 | Aramara 132 kV | 7315_Aramara 132 kV | Loading (A) | 337.5115 | 219.567 | 337.928 | 357.8476 | 239.8273 | 358.2645 | 381.8735 | 263.6907 | 382.2909 | 404.6235 | 286.2578 | 405.0414 | 425.3815 | 306.7803 | 425.8001
WB | 83860139 | 7315 | Aramara 132 kV | 7315_Aramara 132 kV | Loading (MVA) | 80.8614 | 53.2891 | 80.9594 | 85.6812 | 58.195 | 85.7789 | 91.3619 | 63.9666 | 91.4594 | 96.7218 | 69.4081 | 96.8192 | 101.592 | 74.3435 | 101.6893
WB | 83860139 | 7315 | Aramara 132 kV | 7315_Aramara 132 kV | Loading (MW) | 79.87 | 53.2413 | 79.9664 | 84.6824 | 58.1393 | 84.7787 | 90.3516 | 63.9008 | 90.4477 | 95.6929 | 69.3272 | 95.7889 | 100.5373 | 74.2458 | 100.6332
WB | 83860139 | 7315 | Aramara 132 kV | 7315_Aramara 132 kV | Power Factor | 0.98774 | 0.9991 | 0.98773 | 0.98834 | 0.99904 | 0.98834 | 0.98894 | 0.99897 | 0.98894 | 0.98936 | 0.99884 | 0.98936 | 0.98962 | 0.99869 | 0.98961
WB | 83860139 | 7315 | Aramara 132 kV | 7315_Aramara 132 kV | Rating (A) | 1092 | 1205 | 1107 | 1092 | 1205 | 1107 | 1092 | 1205 | 1107 | 1092 | 1205 | 1107 | 1092 | 1205 | 1107
WB | 83860139 | 7315 | Aramara 132 kV | 7315_Aramara 132 kV | Time | 9:00 | 17:00 | 8:30 | 9:00 | 17:00 | 8:30 | 9:00 | 17:00 | 8:30 | 9:00 | 17:00 | 8:30 | 9:00 | 17:00 | 8:30
WB | 83860139 | 7315 | Aramara 132 kV | 7315_Aramara 132 kV | Voltage at Constrained Conductor | 138.3224 | 140.1234 | 138.3191 | 138.2378 | 140.0962 | 138.2344 | 138.129 | 140.0547 | 138.1255 | 138.0107 | 139.9883 | 138.0071 | 137.8861 | 139.9121 | 137.8824
WB | 83901293 | 6302 | BUNDABERG CENTRAL-WEST BUNDABERG | 6302_Bundaberg Central - WEBU 66 kV | % of Rated A | 29.463 | 26.8031 | 32.8659 | 31.8715 | 29.0082 | 35.5485 | 34.5391 | 31.4571 | 38.5355 | 37.3888 | 34.0488 | 41.7023 | 40.1819 | 36.6101 | 44.8363
WB | 83901293 | 6302 | BUNDABERG CENTRAL-WEST BUNDABERG | 6302_Bundaberg Central - WEBU 66 kV | Limiting Line Name | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1
WB | 83901293 | 6302 | BUNDABERG CENTRAL-WEST BUNDABERG | 6302_Bundaberg Central - WEBU 66 kV | Loading (A) | 116.6709 | 116.5647 | 116.7053 | 126.2522 | 126.1987 | 126.2748 | 136.863 | 136.8955 | 136.9287 | 148.1951 | 148.214 | 148.2211 | 159.3023 | 159.4029 | 159.3998
WB | 83901293 | 6302 | BUNDABERG CENTRAL-WEST BUNDABERG | 6302_Bundaberg Central - WEBU 66 kV | Loading (MVA) | 13.5896 | 13.5604 | 13.5991 | 14.7273 | 14.7084 | 14.7353 | 15.9593 | 15.9767 | 15.9945 | 17.2909 | 17.316 | 17.3253 | 18.4983 | 18.4141 | 18.4192
WB | 83901293 | 6302 | BUNDABERG CENTRAL-WEST BUNDABERG | 6302_Bundaberg Central - WEBU 66 kV | Loading (MW) | 4.9663 | 4.9677 | 4.9659 | 7.31 | 7.3109 | 7.3096 | 9.4785 | 9.4776 | 9.4766 | 11.5213 | 11.5199 | 11.5194 | 13.3717 | 13.3789 | 13.3786
WB | 83901293 | 6302 | BUNDABERG CENTRAL-WEST BUNDABERG | 6302_Bundaberg Central - WEBU 66 kV | Power Factor | 0.36545 | 0.36634 | 0.36517 | 0.49636 | 0.49706 | 0.49606 | 0.59392 | 0.59321 | 0.59249 | 0.66632 | 0.66528 | 0.66489 | 0.72286 | 0.72655 | 0.72634
WB | 83901293 | 6302 | BUNDABERG CENTRAL-WEST BUNDABERG | 6302_Bundaberg Central - WEBU 66 kV | Rating (A) | 397 | 436 | 356 | 397 | 436 | 356 | 397 | 436 | 356 | 397 | 436 | 356 | 397 | 436 | 356
WB | 83901293 | 6302 | BUNDABERG CENTRAL-WEST BUNDABERG | 6302_Bundaberg Central - WEBU 66 kV | Time | 16:30 | 18:30 | 6:30 | 16:30 | 18:30 | 6:30 | 16:30 | 18:30 | 6:30 | 16:30 | 18:30 | 6:30 | 9:00 | 17:00 | 6:00
WB | 83901293 | 6302 | BUNDABERG CENTRAL-WEST BUNDABERG | 6302_Bundaberg Central - WEBU 66 kV | Voltage at Constrained Conductor | 67.2486 | 67.1653 | 67.2756 | 67.3477 | 67.2898 | 67.3722 | 67.3234 | 67.3812 | 67.4398 | 67.3631 | 67.4525 | 67.4855 | 67.0424 | 66.6952 | 66.715
WB | 84050534 | 7328 | 7328 BBERG-ISIS NO.2 | 7328_Bundaberg - ISIS No 2 132 kV | % of Rated A | 29.9589 | 33.2268 | 33.5049 | 30.4949 | 33.3388 | 33.6178 | 30.6165 | 32.9108 | 33.1865 | 30.4687 | 32.5252 | 32.7979 | 30.3294 | 32.1764 | 32.4464
WB | 84050534 | 7328 | 7328 BBERG-ISIS NO.2 | 7328_Bundaberg - ISIS No 2 132 kV | Limiting Line Name | TR_LINE 98488_1 | TR_LINE 98484_1 | TR_LINE 98484_1 | TR_LINE 98488_1 | TR_LINE 98484_1 | TR_LINE 98484_1 | TR_LINE 98488_1 | TR_LINE 98484_1 | TR_LINE 98484_1 | TR_LINE 98488_1 | TR_LINE 98484_1 | TR_LINE 98484_1 | TR_LINE 98488_1 | TR_LINE 98484_1 | TR_LINE 98484_1
WB | 84050534 | 7328 | 7328 BBERG-ISIS NO.2 | 7328_Bundaberg - ISIS No 2 132 kV | Loading (A) | 74.298 | 131.5781 | 131.6744 | 75.6275 | 132.0218 | 132.1179 | 75.9289 | 130.3269 | 130.423 | 75.5623 | 128.7996 | 128.8956 | 75.2169 | 127.4187 | 127.5145
WB | 84050534 | 7328 | 7328 BBERG-ISIS NO.2 | 7328_Bundaberg - ISIS No 2 132 kV | Loading (MVA) | 18.0438 | 32.1382 | 32.1617 | 18.3692 | 32.2783 | 32.3019 | 18.4036 | 31.8857 | 31.9093 | 18.3081 | 31.5283 | 31.5519 | 18.217 | 31.1989 | 31.2225
WB | 84050534 | 7328 | 7328 BBERG-ISIS NO.2 | 7328_Bundaberg - ISIS No 2 132 kV | Loading (MW) | 17.7871 | 30.7437 | 30.7662 | 18.0352 | 30.9964 | 31.0189 | 17.7782 | 30.716 | 30.7384 | 17.5223 | 30.4545 | 30.4769 | 17.2791 | 30.2044 | 30.2267
WB | 84050534 | 7328 | 7328 BBERG-ISIS NO.2 | 7328_Bundaberg - ISIS No 2 132 kV | Power Factor | 0.98578 | 0.95661 | 0.95661 | 0.98182 | 0.96029 | 0.96028 | 0.96602 | 0.96332 | 0.96331 | 0.95708 | 0.96594 | 0.96593 | 0.94852 | 0.96812 | 0.9681
WB | 84050534 | 7328 | 7328 BBERG-ISIS NO.2 | 7328_Bundaberg - ISIS No 2 132 kV | Rating (A) | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393
WB | 84050534 | 7328 | 7328 BBERG-ISIS NO.2 | 7328_Bundaberg - ISIS No 2 132 kV | Time | 16:30 | 18:30 | 4:30 | 16:30 | 18:30 | 4:30 | 16:30 | 18:30 | 4:30 | 16:30 | 18:30 | 4:30 | 16:30 | 18:30 | 4:30
WB | 84050534 | 7328 | 7328 BBERG-ISIS NO.2 | 7328_Bundaberg - ISIS No 2 132 kV | Voltage at Constrained Conductor | 140.2136 | 141.0187 | 141.019 | 140.2331 | 141.1579 | 141.1582 | 139.9381 | 141.2541 | 141.2545 | 139.8874 | 141.3269 | 141.3275 | 139.8301 | 141.3663 | 141.367
WB | 85251782 | 6224 | 6366 66kV GOOTCHIE FDR | 6366_Gootchie 66 kV | % of Rated A | 15.6109 | 12.3612 | 12.9832 | 20.7495 | 16.422 | 17.2483 | 25.7079 | 20.3393 | 21.3626 | 30.4468 | 24.0663 | 25.2836 | 34.6624 | 27.4737 | 28.8604
WB | 85251782 | 6224 | 6366 66kV GOOTCHIE FDR | 6366_Gootchie 66 kV | Limiting Line Name | TR_LINE 7245_1 | TR_LINE 7245_1 | TR_LINE 7245_1 | TR_LINE 7245_1 | TR_LINE 7245_1 | TR_LINE 7245_1 | TR_LINE 7245_1 | TR_LINE 7245_1 | TR_LINE 7245_1 | TR_LINE 7245_1 | TR_LINE 7245_1 | TR_LINE 7245_1 | TR_LINE 7245_1 | TR_LINE 7245_1 | TR_LINE 7245_1
WB | 85251782 | 6224 | 6366 66kV GOOTCHIE FDR | 6366_Gootchie 66 kV | Loading (A) | 20.6063 | 20.6433 | 20.6433 | 27.3893 | 27.4248 | 27.4248 | 33.9344 | 33.9666 | 33.9666 | 39.7731 | 39.7756 | 39.7848 | 45.4205 | 45.5504 | 45.5592
WB | 85251782 | 6224 | 6366 66kV GOOTCHIE FDR | 6366_Gootchie 66 kV | Loading (MVA) | 2.4355 | 2.4332 | 2.4332 | 3.2386 | 3.238 | 3.238 | 4.0174 | 4.0167 | 4.0167 | 4.7907 | 4.7904 | 4.7907 | 5.4999 | 5.4997 | 5.4994
WB | 85251782 | 6224 | 6366 66kV GOOTCHIE FDR | 6366_Gootchie 66 kV | Loading (MW) | 2.2644 | 2.2643 | 2.2643 | 3.1234 | 3.1233 | 3.1233 | 3.9355 | 3.9353 | 3.9353 | 4.7736 | 4.7735 | 4.7736 | 5.4879 | 5.4879 | 5.4877
WB | 85251782 | 6224 | 6366 66kV GOOTCHIE FDR | 6366_Gootchie 66 kV | Power Factor | 0.92977 | 0.93057 | 0.93057 | 0.96442 | 0.96459 | 0.96459 | 0.97962 | 0.97973 | 0.97973 | 0.99642 | 0.99646 | 0.99643 | 0.99782 | 0.99784 | 0.99787
WB | 85251782 | 6224 | 6366 66kV GOOTCHIE FDR | 6366_Gootchie 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
WB | 85251782 | 6224 | 6366 66kV GOOTCHIE FDR | 6366_Gootchie 66 kV | Time | 16:30 | 19:00 | 0:00 | 16:30 | 19:00 | 0:00 | 16:00 | 19:00 | 0:00 | 16:00 | 18:00 | 5:30 | 9:00 | 18:00 | 5:30
WB | 85251782 | 6224 | 6366 66kV GOOTCHIE FDR | 6366_Gootchie 66 kV | Voltage at Constrained Conductor | 68.2377 | 68.0524 | 68.0524 | 68.2687 | 68.1664 | 68.1664 | 68.3501 | 68.2749 | 68.2749 | 69.5424 | 69.534 | 69.5213 | 69.9107 | 69.7092 | 69.6914