## 2023 - Regional Max Fault
Sub Code | Substation | Region | Voltage (kV) | 2023 3-Ph Fault Level (kA) (Power Factory) | 2023 3-Ph Fault Level (MVA) (Power Factory) | 2023 1-Ph-G Fault Level (kA) (Power Factory) | 2023 1-Ph-G Fault Level (MVA) (Power Factory) | R1 (Ohms) | X1 (Ohms) | R0 (Ohms) | X0 (Ohms) | R2 (Ohms) | X2 (Ohms)
ABPO | Abbot Point | NQ | 66 | 1.9239 | 219.9271 | 1.5023 | 57.2464 | 7.6843 | 20.4328 | 10.1684 | 39.0554 | 7.688 | 20.4088
AGWA | Agnes Water | CA | 22 | 2.0995 | 80.0001 | 2.6662 | 33.8648 | 1.0075 | 6.5832 | 0.11824 | 2.4151 | 1.0073 | 6.584
AGWA | Agnes Water | CA | 66 | 1.0945 | 125.1174 | 0.82063 | 31.2702 | 8.0158 | 37.4773 | 12.0591 | 75.7363 | 8.0139 | 37.4844
AITK | Aitkenvale (TF1) | NQ | 11 | 18.0134 | 343.2005 | 19.564 | 124.2479 | 0.03787 | 0.38726 | 0.016748 | 0.29712 | 0.037475 | 0.387
AITK | Aitkenvale (TF2) | NQ | 11 | 18.0134 | 343.2005 | 19.564 | 124.2479 | 0.03787 | 0.38726 | 0.016748 | 0.29712 | 0.037475 | 0.387
AITK | Aitkenvale | NQ | 66 | 12.6182 | 1442.4582 | 10.0075 | 381.3375 | 0.76037 | 3.2449 | 1.1573 | 5.8481 | 0.74618 | 3.2355
ALCR | Alligator Creek T065 | MK | 33 | 12.0539 | 688.9714 | 14.9293 | 284.4416 | 0.22744 | 1.7256 | 0.040375 | 0.71583 | 0.22431 | 1.7461
ALLO | Allora (TF1) | SW | 11 | 2.5104 | 47.8296 | 3.2728 | 20.7849 | 1.7573 | 2.1713 | 0.1469 | 0.9362 | 1.7533 | 2.1722
ALLO | Allora (TF2) | SW | 11 | 2.5104 | 47.8296 | 3.2728 | 20.7849 | 1.7573 | 2.1713 | 0.1469 | 0.9362 | 1.7533 | 2.1722
ALLO | Allora | SW | 33 | 1.1517 | 65.8302 | 0.87157 | 16.6055 | 14.494 | 11.1155 | 17.172 | 33.5069 | 14.458 | 11.1238
ALLO | Allora (Reg) | SW | 33 | 1.1517 | 65.8302 | 0.87157 | 16.6055 | 14.494 | 11.1155 | 17.172 | 33.5069 | 14.458 | 11.1238
ALSH | Alan Sherriff (TF1) | NQ | 11 | 17.3331 | 330.2403 | 15.7133 | 99.7927 | 0.025196 | 0.40368 | 1.6763e-09 | 0.53115 | 0.024976 | 0.40352
ALSH | Alan Sherriff (TF2) | NQ | 11 | 17.3331 | 330.2403 | 15.7133 | 99.7927 | 0.025196 | 0.40368 | 1.6763e-09 | 0.53115 | 0.024976 | 0.40352
ALST | Alfred Street | MK | 11 | 12.8479 | 244.7862 | 14.2395 | 90.4328 | 0.041523 | 0.54273 | 0.0097889 | 0.3844 | 0.041216 | 0.54351
ALST | Alfred Street | MK | 33 | 13.6958 | 782.8211 | 18.4267 | 351.0763 | 0.26882 | 1.5081 | 0.11212 | 0.33107 | 0.26668 | 1.515
ARAM | Aramara T173 | WB | 132 | 8.0796 | 1847.2424 | 7.8984 | 601.9373 | 1.4444 | 10.2919 | 1.839 | 10.9069 | 1.405 | 10.3208
ATHE | Atherton (TF1) | FN | 22 | 6.3473 | 241.865 | 8.1755 | 103.8422 | 0.37513 | 2.1723 | 0.0038827 | 0.7205 | 0.36863 | 2.188
ATHE | Atherton (TF2) | FN | 22 | 6.3473 | 241.865 | 8.1755 | 103.8422 | 0.37513 | 2.1723 | 0.0038827 | 0.7205 | 0.36863 | 2.188
ATHE | Atherton | FN | 66 | 3.1036 | 354.7904 | 2.4643 | 93.9031 | 3.1209 | 13.1602 | 4.3476 | 23.5552 | 3.0598 | 13.3004
AWOO | Awoonga | CA | 11 | 10.0991 | 192.4131 | 11.1951 | 71.0981 | 0.12463 | 0.68058 | 0.031304 | 0.4849 | 0.12293 | 0.68601
AWOO | Awoonga | CA | 66 | 4.7179 | 539.3306 | 3.1678 | 120.7084 | 3.3532 | 8.2295 | 5.9726 | 21.1328 | 3.3559 | 8.2604
AYRZ | Ayr (TF2) | NQ | 11 | 9.4199 | 179.474 | 10.2758 | 65.2603 | 0.0882 | 0.738 | 0.0317 | 0.5572 | 0.00843 | 0.7381
AYRZ | Ayr (TF3) | NQ | 11 | 9.4199 | 179.474 | 10.2758 | 65.2603 | 0.0882 | 0.738 | 0.0317 | 0.5572 | 0.00843 | 0.7381
AYRZ | Ayr | NQ | 66 | 6.1613 | 704.332 | 5.2333 | 199.4152 | 2.0321 | 6.508 | 2.1352 | 10.2804 | 1.8935 | 6.5109
BABI | Babinda | FN | 22 | 1.2457 | 47.4675 | 0.79165 | 10.0553 | 7.7465 | 8.1381 | 10.86 | 29.7595 | 7.7389 | 8.1533
BALB | Balberra (1 Regulator) | MK | 11 | 3.5019 | 66.7209 | 3.8099 | 24.196 | 0.30165 | 1.9741 | 0.088027 | 1.5054 | 0.29483 | 1.9709
BALB | Balberra (2 Regulator) | MK | 11 | 3.5019 | 66.7209 | 3.8099 | 24.196 | 0.30165 | 1.9741 | 0.088027 | 1.5054 | 0.29483 | 1.9709
BALB | Balberra (Unregulated) | MK | 11 | 3.5401 | 67.4484 | 3.8542 | 24.4774 | 0.28157 | 1.9553 | 0.074643 | 1.4929 | 0.28145 | 1.9584
BALB | Balberra | MK | 33 | 4.6015 | 263.012 | 2.9887 | 56.9425 | 1.8624 | 4.1617 | 2.7951 | 11.676 | 1.8613 | 4.1896
BAMB | Bambaroo | NQ | 11 | 1.2438 | 23.6978 | 1.2941 | 8.2183 | 0.92273 | 5.552 | 0.51738 | 4.9397 | 0.90787 | 5.5426
BAMB | Bambaroo | NQ | 66 | 1.6287 | 186.189 | 1.2826 | 48.8724 | 14.1245 | 21.5761 | 20.5845 | 42.0487 | 14.0574 | 21.7025
BARC | Barcaldine T072 (TF1) | CA | 11 | 9.8184 | 187.0649 | 0 | 0 | 0.066627 | 0.7223 | 268292680.0837 | 42.0092 | 0.0723 | 0.78706
BARC | Barcaldine T072 (TF2) | CA | 11 | 9.8184 | 187.0649 | 0 | 0 | 0.066627 | 0.7223 | 268292680.0837 | 42.0092 | 0.0723 | 0.78706
BARC | Barcaldine T072 | CA | 132 | 1.8046 | 412.5812 | 1.6277 | 124.0439 | 6.1882 | 46.6074 | 5.1732 | 53.014 | 7.6626 | 55.9233
BARC | Barcaldine T072 (TF5) | CA | 22 | 4.3848 | 167.0825 | 4.758 | 60.4349 | 0.25825 | 3.2361 | 0.10719 | 2.1433 | 0.23692 | 3.6032
BARC | Barcaldine T072 (TF6) | CA | 22 | 4.3848 | 167.0825 | 4.758 | 60.4349 | 0.25825 | 3.2361 | 0.10719 | 2.1433 | 0.23692 | 3.6032
BARC | Barcaldine T072 | CA | 66 | 2.3829 | 272.4068 | 2.8029 | 106.803 | 1.8262 | 17.8456 | 1.2136 | 7.6022 | 2.0246 | 20.1889
BARG | Bargara | WB | 11 | 9.732 | 185.4191 | 11.5887 | 73.5984 | 0.10519 | 0.71097 | 0.01704 | 0.37116 | 0.10468 | 0.71315
BARG | Bargara | WB | 66 | 3.3206 | 379.5984 | 2.3091 | 87.9869 | 3.1734 | 12.2334 | 6.1323 | 28.5023 | 3.1549 | 12.3117
BARR | Barratta | NQ | 11 | 3.3852 | 64.4959 | 3.6803 | 23.373 | 0.44743 | 2.0187 | 0.16328 | 1.5683 | 0.44259 | 2.0194
BARR | Barratta | NQ | 66 | 2.0683 | 236.443 | 1.4552 | 55.4488 | 10.2295 | 17.5398 | 14.949 | 43.9664 | 10.0552 | 17.5632
BEEC | Beecher Switching | CA | 66 | 5.1932 | 593.6652 | 3.6014 | 137.2307 | 3.2116 | 7.4068 | 4.9898 | 18.1832 | 3.2112 | 7.4151
BEGA | Belgian Gardens | NQ | 11 | 16.7954 | 319.9946 | 17.7466 | 112.7058 | 0.025122 | 0.41656 | 0.011212 | 0.35099 | 0.024719 | 0.41629
BEGA | Belgian Gardens (TF1) | NQ | 66 | 16.6276 | 1900.7915 | 18.4391 | 702.6232 | 0.60389 | 2.456 | 0.44321 | 1.7443 | 0.58936 | 2.4466
BEGA | Belgian Gardens (TF2) | NQ | 66 | 16.6375 | 1901.9173 | 18.4504 | 703.0542 | 0.60257 | 2.4548 | 0.44172 | 1.7434 | 0.58804 | 2.4454
BENA | Benarkin (TF1) | WB | 11 | 3.4987 | 66.6594 | 3.7775 | 23.9902 | 0.40076 | 1.9564 | 0.19625 | 1.5454 | 0.4008 | 1.9565
BENA | Benarkin | WB | 66 | 2.5362 | 289.9305 | 1.5523 | 59.1511 | 7.3632 | 14.7984 | 11.7567 | 46.9613 | 7.3646 | 14.8046
BERS | Berserker | CA | 11 | 14.7341 | 280.7229 | 16.1492 | 102.5611 | 0.041626 | 0.47249 | 0.011216 | 0.34925 | 0.041687 | 0.47308
BERS | Berserker | CA | 66 | 9.1765 | 1049.0101 | 8.5067 | 324.1476 | 1.0947 | 4.4364 | 1.4209 | 5.4456 | 1.097 | 4.4578
BEWE | Bedford Weir | CA | 22 | 4.1125 | 156.7074 | 4.8459 | 61.5511 | 0.82543 | 3.3011 | 0.13699 | 1.8801 | 0.82651 | 3.2956
BEWE | Bedford Weir | CA | 66 | 2.9543 | 337.7168 | 2.1204 | 80.7973 | 6.1959 | 12.7885 | 9.9737 | 29.4956 | 6.2057 | 12.7392
BILO | Biloela T026 (Regulated) | CA | 11 | 16.0462 | 305.7221 | 17.9304 | 113.8735 | 0.034387 | 0.43415 | 0.015371 | 0.2974 | 0.034383 | 0.43464
BILO | Biloela T026 | CA | 66 | 8.4363 | 964.4043 | 10.3839 | 395.6808 | 0.68458 | 4.9227 | 0.30166 | 2.1348 | 0.68443 | 4.9404
BING | Bingegang | CA | 22 | 1.8574 | 70.7776 | 2.3502 | 29.8514 | 2.7654 | 7.008 | 0.26352 | 2.8868 | 2.7665 | 7.0026
BING | Bingegang | CA | 66 | 0.96751 | 110.6017 | 0.60648 | 23.11 | 22.5166 | 37.0912 | 40.393 | 115.1495 | 22.5264 | 37.0419
BLAC | Blackwater T032 (TF4) | CA | 11 | 19.3028 | 367.7674 | 8.3595 | 53.0898 | 0.04074 | 0.36018 | 2.2166e-05 | 1.7907 | 0.041021 | 0.35887
BLAC | Blackwater T032 (TF5) | CA | 11 | 25.2693 | 481.4442 | 14.6628 | 93.1216 | 0.031609 | 0.27509 | 5.4388e-06 | 0.88154 | 0.031946 | 0.27359
BLAC | Blackwater T032 | CA | 22 | 6.3347 | 241.384 | 5.2448 | 66.6176 | 0.23399 | 2.1966 | 0.00025452 | 3.6033 | 0.23522 | 2.191
BLAC | Blackwater T032 | CA | 66 | 8.5021 | 971.9242 | 11.1135 | 423.4815 | 0.88124 | 4.8584 | 0.098346 | 1.5098 | 0.89102 | 4.8092
BLAK | Blackall (TF1) | CA | 22 | 1.0556 | 40.2232 | 1.2963 | 16.4651 | 3.7557 | 12.9657 | 0.52711 | 5.9056 | 3.7777 | 13.2261
BLAK | Blackall (TF2) | CA | 22 | 1.0556 | 40.2232 | 1.2963 | 16.4651 | 3.7557 | 12.9657 | 0.52711 | 5.9056 | 3.7777 | 13.2261
BLAK | Blackall | CA | 66 | 0.61181 | 69.9391 | 0.41205 | 15.7011 | 29.0573 | 63.5415 | 49.2791 | 163.7959 | 29.2557 | 65.8848
BLOO | Bloomfield SS | FN | 22 | 0.48303 | 18.4058 | 0.34804 | 4.4207 | 11.4745 | 26.6039 | 14.6759 | 61.4005 | 11.3624 | 26.649
BLRI | Black River (TF1) | NQ | 11 | 13.3154 | 253.6923 | 14.3561 | 91.1737 | 0.039602 | 0.52464 | 0.017055 | 0.41214 | 0.038489 | 0.52472
BLRI | Black River (TF2) | NQ | 11 | 13.3154 | 253.6923 | 14.3561 | 91.1737 | 0.039602 | 0.52464 | 0.017055 | 0.41214 | 0.038489 | 0.52472
BLRI | Black River | NQ | 66 | 10.1764 | 1163.3148 | 8.8466 | 337.1019 | 0.81169 | 4.05 | 0.93259 | 5.9338 | 0.77164 | 4.0528
BLUE | Bluewater | NQ | 11 | 3.712 | 70.7231 | 3.9153 | 24.8656 | 0.26889 | 1.8681 | 0.079924 | 1.5985 | 0.26778 | 1.8681
BLUE | Bluewater | NQ | 66 | 3.5467 | 405.4406 | 2.5609 | 97.5825 | 6.8028 | 9.7048 | 9.148 | 24.3014 | 6.7628 | 9.7076
BLVA | Blue Valley T183 | NQ | 11 | 8.2348 | 156.8946 | 5.6855 | 36.1079 | 0.089635 | 0.8455 | 4.9091e-09 | 2 | 0.088933 | 0.84496
BLVA | Blue Valley T183 | NQ | 132 | 3.5646 | 814.9805 | 2.3596 | 179.8279 | 7.6688 | 22.2878 | 17.0354 | 57.3423 | 7.5677 | 22.2096
BOCR | Boat Creek T130 (TF1) | CA | 11 | 22.772 | 433.8644 | 0 | 0 | 0.016795 | 0.30639 | 135802467.1961 | 4.0433 | 0.016583 | 0.30652
BOCR | Boat Creek T130 (TF2) | CA | 11 | 23.066 | 439.4655 | 0 | 0 | 0.016893 | 0.30247 | 135802469.4569 | -2.6722 | 0.01668 | 0.30259
BOCR | Boat Creek T130 (TF1) | CA | 132 | 12.4944 | 2856.6116 | 13.7097 | 1044.8222 | 0.40464 | 6.6989 | 0.59135 | 4.8764 | 0.4001 | 6.7192
BOCR | Boat Creek T130 (TF2) | CA | 132 | 12.5581 | 2871.1608 | 13.8096 | 1052.4295 | 0.39719 | 6.6653 | 0.57541 | 4.813 | 0.39267 | 6.6856
BOCR | Boat Creek T130 | CA | 66 | 10.4391 | 1193.3531 | 12.6077 | 480.4183 | 0.15352 | 4.0132 | 0.17915 | 1.933 | 0.14524 | 4.018
BODA | Boondooma Dam (TF1) | WB | 11 | 2.8944 | 55.1461 | 3.4275 | 21.7677 | 0.6293 | 2.3305 | 0.14664 | 1.2905 | 0.62934 | 2.3306
BODA | Boondooma Dam (TF2) | WB | 11 | 2.8944 | 55.1461 | 3.4275 | 21.7677 | 0.6293 | 2.3305 | 0.14664 | 1.2905 | 0.62934 | 2.3306
BODA | Boondooma Dam | WB | 66 | 1.0157 | 116.1113 | 0.57757 | 22.0085 | 17.3757 | 37.4374 | 30.4763 | 132.8604 | 17.3771 | 37.4436
BOHL | Bohle (TF1) | NQ | 11 | 19.1985 | 365.7806 | 20.9453 | 133.0202 | 0.032361 | 0.36355 | 0.013388 | 0.2741 | 0.03165 | 0.36346
BOHL | Bohle (TF2) | NQ | 11 | 19.1985 | 365.7806 | 20.9453 | 133.0202 | 0.032361 | 0.36355 | 0.013388 | 0.2741 | 0.03165 | 0.36346
BOHL | Bohle | NQ | 66 | 12.7717 | 1460.0063 | 10.7147 | 408.2863 | 0.68302 | 3.2202 | 1.0017 | 5.1042 | 0.65743 | 3.2172
BOPU | Bocoolima Pumps | CA | 11 | 3.7633 | 71.7009 | 4.3837 | 27.8401 | 0.45359 | 1.8005 | 0.054128 | 1.0826 | 0.45355 | 1.801
BOPU | Bocoolima Pumps | CA | 66 | 1.4175 | 162.0425 | 0.85887 | 32.7273 | 14.3807 | 25.8456 | 25.4302 | 84.3301 | 14.379 | 25.8639
BORE | Boyne Residential | CA | 11 | 8.7186 | 166.1109 | 9.8287 | 62.4208 | 0.16402 | 0.7845 | 0.038651 | 0.53138 | 0.16402 | 0.78503
BORE | Boyne Residential | CA | 66 | 4.123 | 471.3229 | 2.8219 | 107.5305 | 4.5133 | 9.1122 | 7.4104 | 23.1828 | 4.5134 | 9.1314
BOWE | Bowen | NQ | 11 | 8.0496 | 153.3645 | 9.6771 | 61.4579 | 0.19986 | 0.84629 | 0.018473 | 0.43772 | 0.19996 | 0.84562
BOWE | Bowen | NQ | 66 | 2.6097 | 298.3341 | 2.5089 | 95.6028 | 6.5298 | 14.7084 | 6.0149 | 17.0696 | 6.5335 | 14.6844
BROD | Broadlea | MK | 132 | 3.9168 | 895.5049 | 4.3036 | 327.9755 | 5.0091 | 20.8323 | 1.7575 | 15.6429 | 4.9921 | 20.838
BROD | Broadlea | MK | 66 | 5.1654 | 590.4811 | 6.4842 | 247.0808 | 1.3271 | 8.0144 | 0.17096 | 3.1794 | 1.3228 | 8.0158
BROX | Broxburn | SW | 11 | 3.7002 | 70.4987 | 4.6742 | 29.6855 | 0.59063 | 1.799 | 0.037158 | 0.74315 | 0.57892 | 1.7926
BROX | Broxburn | SW | 33 | 1.9336 | 110.5189 | 1.2896 | 24.5705 | 5.2937 | 9.4945 | 7.9852 | 26.3765 | 5.1884 | 9.4371
BUCE | Bundaberg Central | WB | 11 | 15.2038 | 289.6713 | 16.3561 | 103.8752 | 0.054134 | 0.45678 | 0.011314 | 0.34674 | 0.048613 | 0.47342
BUCE | Bundaberg Central | WB | 66 | 5.5686 | 636.5821 | 4.9203 | 187.4891 | 1.4694 | 7.3916 | 2.3597 | 10.1361 | 1.4535 | 7.4928
BUDA | Burdekin Dam (TF1) | NQ | 11 | 0.56816 | 10.8248 | 0.64645 | 4.1055 | 3.6472 | 11.7917 | 1.4754 | 7.7703 | 3.6699 | 11.7767
BUDA | Burdekin Dam (TF2) | NQ | 11 | 0.84365 | 16.0738 | 1.0289 | 6.5345 | 2.5653 | 7.9065 | 0.39343 | 3.8852 | 2.5879 | 7.8915
BUDA | Burdekin Dam | NQ | 33 | 0.51146 | 29.2339 | 0.29251 | 5.573 | 19.5468 | 36.1919 | 31.5805 | 131.5814 | 19.7504 | 36.0572
BUDG | Burnett Dam Generator | WB | 11 | 0.59096 | 11.2592 | 0.35781 | 2.2724 | 3.2208 | 11.4057 | 5.6718 | 34.5663 | 3.219 | 11.4058
BULL | Bullyard | WB | 11 | 5.3234 | 101.4249 | 5.9649 | 37.8823 | 0.27515 | 1.2848 | 0.066607 | 0.89012 | 0.27459 | 1.2863
BULL | Bullyard | WB | 66 | 2.6116 | 298.542 | 1.8727 | 71.3582 | 7.5076 | 14.2084 | 10.6624 | 33.6268 | 7.4875 | 14.2629
BUND | Bundaberg T020 | WB | 11 | 14.3408 | 273.2297 | 0 | 0 | 0.030674 | 0.48678 | 154929577.3869 | 1.1069 | 0.03011 | 0.48826
BUND | Bundaberg T020 | WB | 132 | 7.1236 | 1628.6687 | 7.1112 | 541.9471 | 2.2267 | 11.5709 | 1.5854 | 11.6646 | 2.2005 | 11.6382
BUND | Bundaberg T020 | WB | 66 | 7.3946 | 845.3191 | 8.7418 | 333.1084 | 0.63851 | 5.6394 | 0.23754 | 2.9823 | 0.61837 | 5.6939
CABO | Caboonbah | WB | 11 | 3.2602 | 62.1151 | 3.9478 | 25.0719 | 0.64672 | 2.0432 | 0.090686 | 1.0392 | 0.64676 | 2.0434
CABO | Caboonbah | WB | 66 | 1.0146 | 115.9898 | 0.59753 | 22.7688 | 20.0172 | 36.1435 | 32.2717 | 125.3668 | 20.0187 | 36.1497
CACI | Cairns City (TF1) | FN | 132 | 6.1704 | 1410.7366 | 7.2248 | 550.6008 | 2.1899 | 13.4336 | 1.4892 | 7.6044 | 2.1489 | 13.3556
CACI | Cairns City (TF2) | FN | 132 | 6.1712 | 1410.9263 | 7.2168 | 549.9917 | 2.1874 | 13.4322 | 1.3183 | 7.6758 | 2.1465 | 13.3542
CACI | Cairns City | FN | 22 | 12.5374 | 477.7388 | 9.087 | 115.4208 | 0.063047 | 1.1147 | 2.0964e-08 | 2.3936 | 0.06191 | 1.1125
CAFE | Cape Ferguson | NQ | 11 | 2.3991 | 45.7087 | 2.6823 | 17.0349 | 1.2735 | 2.6296 | 0.19398 | 2.0891 | 1.2731 | 2.6292
CAFE | Cape Ferguson | NQ | 66 | 0.9677 | 110.6232 | 0.80389 | 30.6322 | 38.8616 | 19.4589 | 44.6309 | 59.5013 | 38.8473 | 19.4428
CALE | Calen | MK | 11 | 3.1714 | 60.4231 | 4.082 | 25.9244 | 1.0849 | 1.9219 | 0.04959 | 0.80044 | 1.0839 | 1.9195
CALE | Calen | MK | 66 | 0.76432 | 87.3736 | 0.53511 | 20.3904 | 37.2698 | 40.3714 | 47.4751 | 120.7657 | 37.2339 | 40.2847
CALL | Calliope | CA | 11 | 9.3537 | 178.2127 | 10.3629 | 65.8133 | 0.097551 | 0.74064 | 0.03648 | 0.52766 | 0.097504 | 0.74115
CALL | Calliope | CA | 66 | 5.2562 | 600.8655 | 3.5175 | 134.0361 | 2.1986 | 7.6674 | 4.2034 | 19.3523 | 2.1969 | 7.6857
CANN | Cannonvale (TF1) | MK | 11 | 8.5394 | 162.6972 | 10.0539 | 63.8506 | 0.17001 | 0.8018 | 0.022845 | 0.45662 | 0.16853 | 0.79889
CANN | Cannonvale (TF2) | MK | 11 | 8.5394 | 162.6972 | 10.0539 | 63.8506 | 0.17001 | 0.8018 | 0.022845 | 0.45662 | 0.16853 | 0.79889
CANN | Cannonvale (FDR P6/3) | MK | 66 | 3.1087 | 355.3776 | 2.5205 | 96.0423 | 5.298 | 12.4262 | 5.7456 | 22.5167 | 5.2446 | 12.3217
CANN | Cannonvale (FDR P6/8) | MK | 66 | 3.1087 | 355.3776 | 2.5205 | 96.0423 | 5.298 | 12.4262 | 5.7456 | 22.5167 | 5.2446 | 12.3217
CANO | Cairns North T093 (TF1) | FN | 132 | 6.4199 | 1467.7937 | 7.9995 | 609.6447 | 1.8858 | 12.9452 | 1.717 | 5.2185 | 1.8449 | 12.8672
CANO | Cairns North T093 (TF2) | FN | 132 | 6.4472 | 1474.0384 | 8.0636 | 614.5317 | 1.8621 | 12.8926 | 1.669 | 5.0859 | 1.8212 | 12.8147
CANO | Cairns North T093 | FN | 22 | 11.9636 | 455.8728 | 8.5769 | 108.9412 | 0.06441 | 1.1682 | 1.8938e-08 | 2.5615 | 0.063273 | 1.1661
CARD | Cardwell T134 | FN | 22 | 6.4891 | 247.269 | 6.4479 | 81.8987 | 0.15476 | 2.1523 | 0.1095 | 2.1975 | 0.15298 | 2.1543
CARI | Cape River | NQ | 11 | 1.0361 | 19.7404 | 1.0309 | 6.5468 | 0.63593 | 7.0177 | 0.41671 | 6.4713 | 0.62538 | 7.0211
CARI | Cape River | NQ | 66 | 2.0667 | 236.2516 | 2.7183 | 103.5829 | 7.8919 | 19.6722 | 0.14247 | 4.7024 | 7.5122 | 19.7921
CARM | Carmila | MK | 11 | 0.55902 | 10.6507 | 0.68072 | 4.3232 | 7.5548 | 9.9697 | 0.65307 | 6.5307 | 7.5598 | 9.9811
CARM | Carmila | MK | 33 | 0.30228 | 17.2774 | 0.23411 | 4.4603 | 62.1156 | 30.9509 | 76.2819 | 117.0423 | 62.1609 | 31.0536
CAST | Canning Street | CA | 11 | 18.1882 | 346.532 | 20.2366 | 128.5198 | 0.04021 | 0.38213 | 0.013357 | 0.26693 | 0.040272 | 0.38272
CAST | Canning Street | CA | 66 | 9.8449 | 1125.4286 | 9.8418 | 375.0238 | 0.96682 | 4.148 | 1.2756 | 4.0543 | 0.96904 | 4.1694
CATE | Cairns Terminal T051 | FN | 22 | 11.8795 | 452.6681 | 10.6166 | 134.8485 | 0.058719 | 1.1768 | 1.075e-08 | 1.6033 | 0.057582 | 1.1747
CAWD | Cawdor | SW | 11 | 4.3785 | 83.4218 | 4.9728 | 31.5818 | 0.23197 | 1.5798 | 0.10227 | 1.0203 | 0.23197 | 1.5794
CAWD | Cawdor | SW | 33 | 4.0577 | 231.9283 | 1.0037 | 19.1235 | 1.1673 | 5.0356 | 56.6057 | 11.2876 | 1.1672 | 5.0315
CEPL | Cecil Plains (TF1) | SW | 11 | 1.8044 | 34.3792 | 2.2849 | 14.5109 | 1.3875 | 3.6264 | 0.075493 | 1.5099 | 1.3758 | 3.6201
CEPL | Cecil Plains (TF3) | SW | 11 | 1.7941 | 34.1825 | 2.2681 | 14.4044 | 1.3887 | 3.6499 | 0.076667 | 1.5333 | 1.377 | 3.6435
CEPL | Cecil Plains | SW | 33 | 0.93783 | 53.6044 | 0.56222 | 10.7118 | 11.8085 | 19.0492 | 18.7897 | 65.9097 | 11.7032 | 18.9918
CHAL | Charlton | SW | 11 | 4.8252 | 91.932 | 5.3267 | 33.8292 | 0.24495 | 1.4281 | 0.052178 | 1.0443 | 0.24494 | 1.4277
CHAL | Charlton | SW | 33 | 5.4793 | 313.1815 | 1.0466 | 19.941 | 1.6381 | 3.4598 | 55.8935 | 3.728 | 1.638 | 3.4557
CHAR | Charleville | SW | 11 | 1.478 | 28.1599 | 2.0888 | 13.2655 | 1.2427 | 4.5606 | 0.016458 | 0.59544 | 1.2384 | 4.5623
CHAR | Charleville | SW | 22 | 0.73569 | 28.0335 | 0.99119 | 12.5898 | 4.9751 | 18.3294 | 0.21941 | 4.3883 | 4.9578 | 18.3362
CHAR | Charleville | SW | 66 | 0.3162 | 36.146 | 0.13815 | 5.2643 | 42.8011 | 125.4706 | 190.0816 | 616.5552 | 42.6455 | 125.5313
CHIA | Chillagoe | FN | 22 | 0.94726 | 36.0956 | 1.1283 | 14.3312 | 3.1285 | 14.4336 | 0.35557 | 7.7096 | 3.1266 | 14.4688
CHIA | Chillagoe | FN | 66 | 0.64115 | 73.2938 | 0.36255 | 13.815 | 24.9564 | 60.5155 | 50.7755 | 211.0911 | 24.9388 | 60.8325
CHIL | Childers | WB | 11 | 7.858 | 149.7149 | 8.5953 | 54.5873 | 0.10636 | 0.88488 | 0.041492 | 0.65795 | 0.10415 | 0.88525
CHIL | Childers | WB | 66 | 4.9456 | 565.3574 | 4.5156 | 172.0685 | 2.3352 | 8.1693 | 2.4607 | 10.6207 | 2.2558 | 8.1827
CHIN | Chinchilla T013 | SW | 110 | 2.2137 | 421.7711 | 2.238 | 142.13 | 3.3669 | 31.3853 | 3.2168 | 30.3501 | 3.3587 | 31.4048
CHIN | Chinchilla T013 | SW | 33 | 8.1503 | 465.854 | 8.0885 | 154.1059 | 0.59775 | 2.5033 | 0.30344 | 2.6265 | 0.5814 | 2.5076
CHIN | Chinchilla T013 (TF3) | SW | 33 | 8.1503 | 465.854 | 8.0885 | 154.1059 | 0.59775 | 2.5033 | 0.30344 | 2.6265 | 0.5814 | 2.5076
CHIN | Chinchilla T013 | SW | 132 | 8.6108 | 1968.7025 | 7.3879 | 563.0326 | 3.0519 | 9.2474 | 4.0767 | 13.9729 | 3.04 | 9.2754
CHTO | Charters Towers (TF1) | NQ | 11 | 7.6899 | 146.5124 | 8.7176 | 55.3645 | 0.17664 | 0.90719 | 0.026297 | 0.57641 | 0.1749 | 0.90678
CHTO | Charters Towers (TF2) | NQ | 11 | 7.6899 | 146.5124 | 8.7176 | 55.3645 | 0.17664 | 0.90719 | 0.026297 | 0.57641 | 0.1749 | 0.90678
CHTO | Charters Towers | NQ | 66 | 3.2601 | 372.6793 | 3.2365 | 123.3267 | 5.4124 | 11.9081 | 2.784 | 12.8893 | 5.3498 | 11.8931
CHTW | Chinchilla Town (TF1) | SW | 11 | 6.0006 | 114.3262 | 6.7753 | 43.0287 | 0.16587 | 1.1536 | 0.038333 | 0.76667 | 0.16308 | 1.1545
CHTW | Chinchilla Town (TF2) | SW | 11 | 6.0006 | 114.3262 | 6.7753 | 43.0287 | 0.16587 | 1.1536 | 0.038333 | 0.76667 | 0.16308 | 1.1545
CHTW | Chinchilla Town | SW | 33 | 5.7217 | 327.0385 | 5.0749 | 96.6899 | 1.1478 | 3.4826 | 0.90089 | 5.0172 | 1.1227 | 3.4904
CHUM | Chumvale | NQ - MI | 220 | 1.4476 | 551.5976 | 1.8443 | 234.2575 | 8.832 | 96.1147 | 3.2978 | 32.2693 | 7.7353 | 98.0174
CHUM | Chumvale | NQ - MI | 66 | 2.2527 | 257.5237 | 2.6613 | 101.411 | 1.127 | 18.5723 | 0.059209 | 9.8816 | 1.0283 | 18.7435
CLER | Clermont T071 (TF1) | CA | 11 | 9.6875 | 184.572 | 6.5394 | 41.5309 | 0.074737 | 0.72038 | 0.01974 | 1.7231 | 0.083103 | 0.76955
CLER | Clermont T071 (TF2) | CA | 11 | 9.6822 | 184.4701 | 6.5403 | 41.5367 | 0.074869 | 0.72077 | 0.018491 | 1.7221 | 0.083215 | 0.76983
CLER | Clermont T071 | CA | 132 | 2.6908 | 615.1989 | 2.4364 | 185.6758 | 6.889 | 30.5181 | 4.3465 | 37.0706 | 7.9257 | 34.287
CLER | Clermont T071 | CA | 22 | 3.9298 | 149.7457 | 3.9602 | 50.3019 | 0.35049 | 3.5535 | 0.057203 | 3.2944 | 0.38391 | 3.75
CLER | Clermont T071 | CA | 66 | 4.0729 | 465.5978 | 4.1088 | 156.5665 | 1.6672 | 10.2006 | 1.0307 | 8.1043 | 2.0265 | 12.0589
CLIF | Clifton (TF1) | SW | 11 | 1.4951 | 28.486 | 1.9047 | 12.0965 | 1.9536 | 4.2486 | 0.088232 | 1.7646 | 1.9536 | 4.2481
CLIF | Clifton (TF2) | SW | 11 | 1.5059 | 28.6913 | 1.9226 | 12.2103 | 1.9518 | 4.2126 | 0.086431 | 1.7286 | 1.9518 | 4.2121
CLIF | Clifton | SW | 33 | 0.75024 | 42.8819 | 0.36636 | 6.9801 | 16.7882 | 22.3556 | 80.9313 | 83.3031 | 16.7881 | 22.3514
CLIN | Clinton | CA | 11 | 14.6727 | 279.5518 | 15.6198 | 99.1988 | 0.030968 | 0.47523 | 0.019411 | 0.38884 | 0.030956 | 0.47545
CLIN | Clinton | CA | 66 | 13.3627 | 1527.5575 | 13.882 | 528.9754 | 0.41605 | 3.1098 | 0.49552 | 2.7342 | 0.41559 | 3.1181
CLON | Cloncurry (TF1) | NQ - MI | 11 | 3.0814 | 58.7088 | 3.4017 | 21.6039 | 0.30534 | 2.2465 | 0.15163 | 1.6162 | 0.3026 | 2.2512
CLON | Cloncurry (TF2) | NQ - MI | 11 | 3.0814 | 58.7088 | 3.4017 | 21.6039 | 0.30534 | 2.2465 | 0.15163 | 1.6162 | 0.3026 | 2.2512
CLON | Cloncurry | NQ - MI | 66 | 1.7948 | 205.1751 | 1.7575 | 66.971 | 5.5336 | 22.6887 | 5.816 | 24.0022 | 5.4349 | 22.8599
CLSO | Clare South T193 | NQ | 11 | 3.51 | 66.8736 | 3.5702 | 22.6736 | 0.21113 | 1.9849 | 0.18852 | 1.8852 | 0.20806 | 1.9838
CLSO | Clare South T193 | NQ | 66 | 11.4228 | 1305.8054 | 13.9136 | 530.1805 | 0.81384 | 3.5891 | 0.22345 | 1.7535 | 0.7032 | 3.5498
COCO | Cook Colliery | CA | 66 | 2.0761 | 237.3299 | 1.4016 | 53.4068 | 9.5951 | 17.7979 | 16.1988 | 47.0421 | 9.6051 | 17.7474
COCR | Cooby Creek | SW | 0.415 | 46.3315 | 31.9688 | 51.2115 | 11.7786 | 0.0010755 | 0.0051046 | 0.00031578 | 0.0037331 | 0.0010755 | 0.0051041
COCR | Cooby Creek | SW | 33 | 2.1156 | 120.9211 | 0.84038 | 16.0114 | 4.8041 | 8.6721 | 8.4055 | 55.3289 | 4.8041 | 8.669
COLL | Collinsville | NQ | 33 | 12.2347 | 699.3096 | 14.0983 | 268.6079 | 0.20707 | 1.7055 | 0.12055 | 1.0647 | 0.28145 | 1.6617
COLU | Columboola T194 | SW | 132 | 18.0649 | 4130.1928 | 24.0583 | 1833.4855 | 0.62582 | 4.5987 | 0.16848 | 1.126 | 0.62661 | 4.633
COLU | Columboola T194 | SW | 33 | 4.1843 | 239.1646 | 5.6771 | 108.1626 | 0.22891 | 5.0041 | 0.014524 | 1.0559 | 0.22896 | 5.0062
COME | Comet (TF1) | CA | 22 | 2.2491 | 85.7012 | 2.4523 | 31.1486 | 1.1422 | 6.1231 | 0.47336 | 4.7562 | 1.1087 | 6.0408
COME | Comet (TF2) | CA | 22 | 2.2491 | 85.7012 | 2.4523 | 31.1486 | 1.1422 | 6.1231 | 0.47336 | 4.7562 | 1.1087 | 6.0408
COME | Comet | CA | 66 | 3.0686 | 350.783 | 2.0652 | 78.6957 | 6.0197 | 12.302 | 10.3354 | 33.057 | 5.7181 | 11.5617
COOK | Cooktown (TF1) | FN | 22 | 2.067 | 78.7623 | 2.7998 | 35.5623 | 1.6066 | 6.5759 | 0.0028278 | 1.4613 | 1.3786 | 6.6549
COOK | Cooktown (TF2) | FN | 22 | 2.067 | 78.7623 | 2.7998 | 35.5623 | 1.6066 | 6.5759 | 0.0028278 | 1.4613 | 1.3786 | 6.6549
COOK | Cooktown | FN | 66 | 0.79637 | 91.0369 | 0.48089 | 18.3245 | 15.3354 | 50.4358 | 37.9177 | 151.6204 | 14.0049 | 51.0622
COOM | Coominglah (TF1) | CA | 22 | 1.3031 | 49.6556 | 1.461 | 18.557 | 3.3569 | 10.1865 | 0.80066 | 7.3231 | 3.3569 | 10.1885
COOM | Coominglah (TF2) | CA | 22 | 1.3031 | 49.6556 | 1.461 | 18.557 | 3.3569 | 10.1865 | 0.80066 | 7.3231 | 3.3569 | 10.1885
COOM | Coominglah | CA | 66 | 1.213 | 138.6598 | 0.85568 | 32.6058 | 23.0208 | 25.7872 | 31.5152 | 73.287 | 23.0207 | 25.8049
COPP | Coppabella Dragline | MK | 66 | 1.6655 | 190.3868 | 1.2025 | 45.8233 | 9.8856 | 23.1746 | 20.0595 | 50.4676 | 9.8813 | 23.176
CORF | Corfield | NQ | 66 | 0.51888 | 59.3163 | 0.32155 | 12.2527 | 37.5573 | 79.0692 | 67.1841 | 212.766 | 37.532 | 79.9268
CORI | Corella River | NQ - MI | 11 | 0.13486 | 2.5695 | 0.1379 | 0.8758 | 17.6077 | 48.7158 | 16.3425 | 45.5265 | 17.605 | 48.7206
CORI | Corella River | NQ - MI | 66 | 0.33935 | 38.7929 | 0.27475 | 10.4692 | 45.5467 | 114.8132 | 59.6562 | 202.383 | 45.448 | 114.9845
CRAI | Craiglie (TF1) | FN | 132 | 1.4409 | 329.439 | 0.98971 | 75.4262 | 16.9238 | 55.7581 | 40.0857 | 131.714 | 16.7536 | 56.1642
CRAI | Craiglie (TF2) | FN | 132 | 1.4861 | 339.7746 | 1.0778 | 82.1358 | 16.1513 | 54.1413 | 34.5565 | 115.373 | 15.8748 | 54.5678
CRAI | Craiglie (TF1) | FN | 22 | 5.7907 | 220.6565 | 7.5793 | 96.2698 | 0.3958 | 2.384 | 4.7661e-05 | 0.70467 | 0.38975 | 2.3955
CRAI | Craiglie (TF2) | FN | 22 | 5.7907 | 220.6565 | 7.5793 | 96.2698 | 0.3958 | 2.384 | 4.7661e-05 | 0.70467 | 0.38975 | 2.3955
CRAN | Cranbrook (TF1) | NQ | 11 | 13.1003 | 249.5938 | 13.9282 | 88.456 | 0.039996 | 0.53354 | 0.018117 | 0.44047 | 0.039608 | 0.53328
CRAN | Cranbrook (TF2) | NQ | 11 | 13.1003 | 249.5938 | 13.9282 | 88.456 | 0.039996 | 0.53354 | 0.018117 | 0.44047 | 0.039608 | 0.53328
CRAN | Cranbrook | NQ | 66 | 12.218 | 1396.7097 | 9.7427 | 371.2469 | 0.78766 | 3.3507 | 1.3228 | 5.939 | 0.77368 | 3.3413
CRED | Crediton | MK | 11 | 0.63246 | 12.0499 | 0.65187 | 4.1399 | 1.6667 | 10.9299 | 0.71493 | 10.0662 | 1.6665 | 10.9324
CRED | Crediton | MK | 66 | 0.90677 | 103.6583 | 0.64876 | 24.721 | 34.2655 | 31.0918 | 44.498 | 95.4433 | 34.2582 | 31.1801
CRNA | Cressbrook No. 1 | SW | 3.3 | 6.1813 | 35.3308 | 7.1815 | 13.6825 | 0.090833 | 0.32692 | 0.010054 | 0.20108 | 0.090833 | 0.32689
CRNA | Cressbrook No. 1 | SW | 33 | 1.4026 | 80.1688 | 0.62492 | 11.9062 | 8.0778 | 12.5838 | 13.9341 | 70.918 | 8.0779 | 12.5807
CRNB | Cressbrook No. 2 | SW | 3.3 | 6.9124 | 39.5096 | 7.794 | 14.8495 | 0.067174 | 0.29589 | 0.010125 | 0.20249 | 0.067174 | 0.29586
CRNB | Cressbrook No. 2 | SW | 33 | 1.9164 | 109.5389 | 0.79323 | 15.1131 | 5.7049 | 9.3394 | 9.6733 | 57.7906 | 5.7049 | 9.3364
CRNE | Crows Nest (TF1) | SW | 11 | 2.6561 | 50.606 | 3.1978 | 20.3085 | 0.79374 | 2.5096 | 0.06642 | 1.3279 | 0.79375 | 2.5092
CRNE | Crows Nest | SW | 33 | 1.6795 | 95.9963 | 0.71597 | 13.6411 | 6.5459 | 10.6348 | 11.062 | 63.2279 | 6.5459 | 10.6317
CROY | Croydon | FN | 22 | 0.65539 | 24.9739 | 0.77844 | 9.8875 | 4.0793 | 25.3864 | 0.0053536 | 15.7153 | 3.9535 | 25.4425
CROY | Croydon | FN | 66 | 0.56836 | 64.9724 | 0.51725 | 19.7099 | 25.1063 | 85.3314 | 23.2666 | 122.6793 | 23.9742 | 85.8359
CUNN | Cunnamulla | SW | 11 | 0.88282 | 16.8201 | 1.2127 | 7.7019 | 2.8566 | 7.38 | 0.07618 | 1.5236 | 2.8523 | 7.3817
CUNN | Cunnamulla | SW | 22 | 0.44129 | 16.8153 | 0.63 | 8.0021 | 11.427 | 29.5296 | 0.094364 | 3.3943 | 11.4097 | 29.5363
CUNN | Cunnamulla | SW | 66 | 0.1795 | 20.5192 | 0.083148 | 3.1684 | 100.1043 | 210.9885 | 323.6144 | 996.807 | 99.9487 | 211.0492
DAAN | Daandine T188 | SW | 110 | 1.6175 | 308.1792 | 1.269 | 80.5942 | 22.5772 | 36.8642 | 19.3231 | 78.4338 | 22.5767 | 36.8748
DAAN | Daandine T188 | SW | 33 | 2.653 | 151.6376 | 2.3784 | 45.3143 | 2.251 | 7.5798 | 1.8277 | 10.5258 | 2.251 | 7.5807
DABA | Dalrymple Bay | MK | 33 | 7.1062 | 406.1731 | 5.7654 | 109.8454 | 0.39533 | 2.9259 | 0.65216 | 4.9607 | 0.39466 | 2.9364
DACE | Dalby Central (TF1) | SW | 11 | 8.6215 | 164.2609 | 10.4261 | 66.2149 | 0.16681 | 0.79369 | 0.020917 | 0.39261 | 0.1668 | 0.7938
DACE | Dalby Central (TF1) | SW | 11 | 8.6215 | 164.2609 | 10.4261 | 66.2149 | 0.16681 | 0.79369 | 0.020917 | 0.39261 | 0.1668 | 0.7938
DACE | Dalby Central | SW | 33 | 5.4611 | 312.1429 | 5.1718 | 98.5351 | 1.313 | 3.6098 | 0.93122 | 4.4138 | 1.313 | 3.6107
DACG | Dalby Cotton Gin | SW | 33 | 2.3496 | 134.3002 | 1.5915 | 30.3223 | 4.4823 | 7.7209 | 5.8957 | 21.1925 | 4.4823 | 7.7219
DAEA | Dalby East | SW | 110 | 3.5659 | 679.4012 | 3.8082 | 241.8536 | 9.9397 | 16.9027 | 2.0528 | 16.7023 | 9.9392 | 16.9133
DAEA | Dalby East | SW | 33 | 7.0777 | 404.5426 | 8.926 | 170.0633 | 0.9352 | 2.8124 | 0.061573 | 1.1533 | 0.93515 | 2.8134
DAGL | Dan Gleeson T092 (TF1) | NQ | 11 | 19.7675 | 376.6221 | 21.1076 | 134.0512 | 0.024971 | 0.35371 | 0.01504 | 0.28748 | 0.024588 | 0.35345
DAGL | Dan Gleeson T092 (TF2) | NQ | 11 | 19.7675 | 376.6221 | 21.1076 | 134.0512 | 0.024971 | 0.35371 | 0.01504 | 0.28748 | 0.024588 | 0.35345
DAGL | Dan Gleeson T092 | NQ | 66 | 17.4435 | 1994.0586 | 19.8707 | 757.1761 | 0.35754 | 2.3843 | 0.18696 | 1.5309 | 0.34376 | 2.375
DEGI | Degilbo | WB | 11 | 2.6579 | 50.6391 | 2.9056 | 18.4528 | 0.45748 | 2.5951 | 0.0062069 | 1.9724 | 0.45568 | 2.5953
DEGI | Degilbo | WB | 66 | 1.5175 | 173.476 | 1.0573 | 40.2871 | 16.2458 | 22.4257 | 22.7303 | 60.6754 | 16.1813 | 22.4312
DIMB | Dimbulah (TF1) | FN | 22 | 3.2005 | 121.9537 | 4.0936 | 51.9958 | 1.362 | 4.1536 | 0.1063 | 1.514 | 1.36 | 4.1888
DIMB | Dimbulah (TF2) | FN | 22 | 3.2005 | 121.9537 | 4.0936 | 51.9958 | 1.362 | 4.1536 | 0.1063 | 1.514 | 1.36 | 4.1888
DIMB | Dimbulah | FN | 66 | 1.5954 | 182.374 | 1.0122 | 38.5709 | 11.3011 | 23.7563 | 19.4847 | 69.2517 | 11.2836 | 24.0733
DIRE | Dirranbandi Regulator (Regulated) | SW | 33 | 0.36726 | 20.9919 | 0.26121 | 4.9767 | 21.0572 | 53.0411 | 24.3191 | 125.2808 | 21.0183 | 53.0562
DIRE | Dirranbandi Regulator (Unregulated) | SW | 33 | 0.36726 | 20.9919 | 0.26121 | 4.9767 | 21.0572 | 53.0411 | 24.3191 | 125.2808 | 21.0183 | 53.0562
DISR | Disraeli | NQ | 11 | 3.4985 | 66.6553 | 3.927 | 24.9398 | 0.5489 | 1.9497 | 0.0036958 | 1.3551 | 0.54728 | 1.9491
DISR | Disraeli | NQ | 66 | 1.4598 | 166.8778 | 1.0882 | 41.4669 | 19.752 | 21.4034 | 22.774 | 55.3774 | 19.6939 | 21.384
DURI | Dugald River (TF1) | NQ - MI | 11 | 15.4312 | 294.004 | 0.15346 | 0.97462 | 0.032386 | 0.45156 | 136.4998 | 0.0669 | 0.029644 | 0.45631
DURI | Dugald River (TF2) | NQ - MI | 11 | 15.4312 | 294.004 | 0.15346 | 0.97462 | 0.032386 | 0.45156 | 136.4998 | 0.0669 | 0.029644 | 0.45631
DURI | Dugald River | NQ - MI | 220 | 1.1359 | 432.8363 | 1.4547 | 184.7693 | 12.7961 | 122.3352 | 1.7304 | 40.3741 | 11.6995 | 124.2379
DURO | Duchess Road (TF1) | NQ - MI | 11 | 36.2052 | 689.8022 | 6.1362 | 38.9704 | 0.012623 | 0.19254 | 1.0485e-07 | 3.0255 | 0.0098809 | 0.1973
DURO | Duchess Road (TF2) | NQ - MI | 11 | 36.2052 | 689.8022 | 6.1362 | 38.9704 | 0.012623 | 0.19254 | 1.0485e-07 | 3.0255 | 0.0098809 | 0.1973
DURO | Duchess Road (TF1) | NQ - MI | 132 | 5.9609 | 1362.8378 | 6.4018 | 487.8799 | 1.6168 | 13.9703 | 1.2855 | 10.4423 | 1.222 | 14.6553
DURO | Duchess Road (TF2) | NQ - MI | 132 | 6.4529 | 1475.3265 | 7.1861 | 547.657 | 1.7434 | 12.8738 | 1.3578 | 8.2805 | 1.3486 | 13.5587
DURO | Duchess Road | NQ - MI | 66 | 0.53965 | 61.6901 | 0.55378 | 21.1019 | 5.5761 | 77.4716 | 5.2467 | 71.3689 | 5.4774 | 77.6429
DYSA | Dysart T035 (R01) | CA | 22 | 5.5393 | 211.0755 | 1.3488 | 17.1315 | 0.18817 | 2.5183 | 0.035995 | 26.0763 | 0.18812 | 2.5193
DYSA | Dysart T035 (R02) | CA | 22 | 5.5393 | 211.0755 | 1.3488 | 17.1315 | 0.18817 | 2.5183 | 0.035995 | 26.0763 | 0.18812 | 2.5193
DYSA | Dysart T035 | CA | 66 | 6.2237 | 711.4661 | 7.8749 | 300.0749 | 1.3767 | 6.6008 | 0.2141 | 2.5 | 1.3762 | 6.6097
EAAY | East Ayr (TF1) | NQ | 11 | 14.1085 | 268.8025 | 16.4027 | 104.71 | 0.0876 | 0.4885 | 0.0151 | 0.2898 | 0.084 | 0.4883
EAAY | East Ayr (TF2) | NQ | 11 | 14.1085 | 268.8025 | 16.4027 | 104.71 | 0.0876 | 0.4885 | 0.0151 | 0.2898 | 0.084 | 0.4883
EAAY | East Ayr | NQ | 66 | 5.5186 | 630.8639 | 4.2701 | 162.7126 | 2.6079 | 7.1521 | 3.5009 | 13.9349 | 2.4794 | 7.1438
EABU | East Bundaberg | WB | 11 | 10.1581 | 193.5382 | 11.3941 | 72.3623 | 0.07261 | 0.68472 | 0.01797 | 0.46124 | 0.072131 | 0.6873
EABU | East Bundaberg | WB | 66 | 5.0671 | 579.2517 | 4.283 | 163.2041 | 1.967 | 8.0452 | 3.1421 | 12.3334 | 1.9498 | 8.1381
EATO | East Toowoomba | SW | 11 | 9.8556 | 187.7746 | 2.2437 | 14.2495 | 0.063105 | 0.70659 | 9.0248 | 0.49615 | 0.063103 | 0.70613
EATO | East Toowoomba (TF1) | SW | 33 | 8.5627 | 489.4224 | 1.1028 | 21.0108 | 0.52149 | 2.3934 | 55.2927 | 4.2694 | 0.52146 | 2.3893
EATO | East Toowoomba (TF2) | SW | 33 | 8.2294 | 470.3753 | 1.0954 | 20.8692 | 0.58072 | 2.4817 | 55.4785 | 4.6261 | 0.5807 | 2.4776
EDMO | Edmonton | FN | 22 | 8.4608 | 322.3998 | 7.6053 | 96.6001 | 0.074224 | 1.6527 | 0.016973 | 2.2171 | 0.073048 | 1.6508
EGHI | Egans Hill T127 | CA | 66 | 10.525 | 1203.1726 | 11.7584 | 448.0564 | 0.76393 | 3.9101 | 0.47617 | 2.6672 | 0.76614 | 3.9313
EIDS | Eidsvold | WB | 11 | 1.807 | 34.427 | 2.083 | 13.2286 | 1.5526 | 3.5518 | 0.2487 | 2.396 | 1.5512 | 3.5518
EIDS | Eidsvold | WB | 66 | 0.59806 | 68.3674 | 0.41061 | 15.6464 | 47.2678 | 51.9969 | 74.6343 | 151.7645 | 47.2191 | 51.9956
ELAR | El Arish | FN | 22 | 11.0274 | 420.1994 | 8.3342 | 105.8587 | 0.10547 | 1.2651 | 1.4689e-08 | 2.505 | 0.10359 | 1.2664
ELRO | Ellwoods Road (TF1) | WB | 11 | 5.6205 | 107.0856 | 6.4375 | 40.8836 | 0.24972 | 1.2178 | 0.096857 | 0.76519 | 0.24976 | 1.2179
ELRO | Ellwoods Road (TF2) | WB | 11 | 5.6205 | 107.0856 | 6.4375 | 40.8836 | 0.24972 | 1.2178 | 0.096857 | 0.76519 | 0.24976 | 1.2179
ELRO | Ellwoods Road | WB | 66 | 2.4377 | 278.6696 | 1.4037 | 53.4898 | 5.503 | 16.2928 | 10.6983 | 54.3293 | 5.5044 | 16.2989
EMER | Emerald | CA | 22 | 6.9119 | 263.3773 | 9.5069 | 120.7539 | 0.38577 | 1.993 | 0.035524 | 0.71002 | 0.21935 | 1.6781
EMER | Emerald | CA | 66 | 3.5168 | 402.0195 | 2.6232 | 99.9564 | 3.1523 | 11.5466 | 13.2146 | 24.3807 | 1.6545 | 8.7127
EMWE | Emerald West | CA | 66 | 3.7069 | 423.7608 | 2.877 | 109.628 | 2.7789 | 11.0111 | 13.35 | 21.3807 | 1.2213 | 7.9324
ERHE | Ernest Henry (TF1) | NQ - MI | 11 | 17.2088 | 327.8716 | 0.2198 | 1.3959 | 0.035918 | 0.40436 | 95.2499 | 1.675 | 0.033176 | 0.40912
ERHE | Ernest Henry (TF1) | NQ - MI | 11 | 17.2088 | 327.8716 | 0.2198 | 1.3959 | 0.035918 | 0.40436 | 95.2499 | 1.675 | 0.033176 | 0.40912
ERHE | Ernest Henry | NQ - MI | 220 | 1.1757 | 447.9959 | 1.5451 | 196.2599 | 12.1848 | 118.2141 | 2.6254 | 31.7031 | 11.0882 | 120.1167
ETON | Eton (TF1) | MK | 11 | 2.8388 | 54.0867 | 3.7073 | 23.5442 | 0.9953 | 2.2534 | 0.038676 | 0.77352 | 0.99518 | 2.2566
ETON | Eton (TF1) | MK | 11 | 2.8388 | 54.0867 | 3.7073 | 23.5442 | 0.9953 | 2.2534 | 0.038676 | 0.77352 | 0.99518 | 2.2566
ETON | Eton | MK | 33 | 1.3228 | 75.6108 | 0.76637 | 14.6014 | 8.6097 | 13.3193 | 13.1057 | 49.6666 | 8.6086 | 13.3473
EUDA | Eungella Dam (TF1) | MK | 11 | 0.62908 | 11.9856 | 0.65561 | 4.1637 | 2.0593 | 10.9231 | 0.59614 | 9.8025 | 2.0591 | 10.9256
EUDA | Eungella Dam (TF2) | MK | 11 | 2.0219 | 38.5221 | 2.4052 | 15.2751 | 1.6647 | 3.0314 | 0.20155 | 1.9108 | 1.6645 | 3.0339
EUDA | Eungella Dam | MK | 66 | 0.63236 | 72.288 | 0.46801 | 17.8337 | 52.674 | 40.3425 | 68.2098 | 124.7073 | 52.6667 | 40.4308
EUMA | Eumamurrin Regulator (Regulated) | SW | 33 | 0.51689 | 29.5445 | 0.38095 | 7.258 | 32.8566 | 23.7609 | 40.5403 | 78.8012 | 32.8177 | 23.7762
EUMA | Eumamurrin Regulator (Unregulated) | SW | 33 | 0.51689 | 29.5445 | 0.38095 | 7.258 | 32.8566 | 23.7609 | 40.5403 | 78.8012 | 32.8177 | 23.7762
EVEL | Evelyn | FN | 22 | 1.5564 | 59.3055 | 1.755 | 22.2921 | 1.7663 | 8.8152 | 0.45383 | 5.9433 | 1.7596 | 8.8307
EVEL | Evelyn | FN | 66 | 1.4771 | 168.8583 | 0.96583 | 36.8029 | 11.8125 | 25.8465 | 17.7972 | 71.8465 | 11.7515 | 25.9867
FARB | Farnborough | CA | 66 | 2.4638 | 281.6487 | 1.5806 | 60.2299 | 8.0183 | 15.0121 | 13.239 | 43.9594 | 8.0205 | 15.0334
FARL | Farleigh | MK | 11 | 8.8569 | 168.7472 | 10.6106 | 67.3861 | 0.1772 | 0.76895 | 0.036039 | 0.39528 | 0.14989 | 0.77828
FARL | Farleigh | MK | 33 | 2.5567 | 146.1368 | 1.2747 | 24.2854 | 3.7096 | 7.317 | 9.9803 | 31.534 | 3.6581 | 7.3695
FARN | Farnsfield | WB | 11 | 6.9497 | 132.4099 | 8.1422 | 51.7098 | 0.22597 | 0.98206 | 0.031705 | 0.56709 | 0.22377 | 0.98243
FARN | Farnsfield | WB | 66 | 2.5475 | 291.2158 | 1.8096 | 68.9548 | 6.9937 | 14.9389 | 9.8859 | 35.4828 | 6.9144 | 14.9523
FILA | Fisherman's Landing | CA | 11 | 15.8449 | 301.8856 | 18.2479 | 115.89 | 0.039463 | 0.43923 | 0.016466 | 0.26618 | 0.039233 | 0.43936
FILA | Fisherman's Landing | CA | 66 | 6.6876 | 764.4962 | 5.7289 | 218.3001 | 0.8039 | 6.2174 | 1.9861 | 9.2195 | 0.79562 | 6.2221
FILA | Fisherman's Landing | CA | 66 | 6.6711 | 762.6138 | 5.7075 | 217.4839 | 0.8279 | 6.2298 | 2.0119 | 9.2657 | 0.81962 | 6.2346
FITR | Fig Tree T185 | NQ | 11 | 7.7559 | 147.7705 | 5.5319 | 35.132 | 0.12208 | 0.89397 | 4.9091e-09 | 2 | 0.12218 | 0.89377
FITR | Fig Tree T185 | NQ | 132 | 2.8119 | 642.8921 | 1.9083 | 145.4311 | 12.3462 | 27.1923 | 23.7004 | 68.4846 | 12.3607 | 27.1645
FOXL | Foxleigh | CA | 22 | 1.6417 | 62.5559 | 1.8005 | 22.8688 | 1.3982 | 8.4173 | 0.31407 | 6.2815 | 1.3778 | 8.4369
FOXL | Foxleigh | CA | 66 | 1.9494 | 222.8457 | 1.0722 | 40.8559 | 9.7575 | 19.2223 | 20.3555 | 72.0648 | 9.5731 | 19.3986
FREN | Frenchville | CA | 11 | 14.5214 | 276.6703 | 15.9646 | 101.3891 | 0.050092 | 0.47865 | 0.017529 | 0.35009 | 0.050154 | 0.47924
FREN | Frenchville | CA | 66 | 8.7825 | 1003.9754 | 8.285 | 315.7025 | 1.1723 | 4.6283 | 1.7842 | 5.3327 | 1.1745 | 4.6497
GARB | Garbutt T046 (TF3) | NQ | 11 | 20.0545 | 382.0894 | 20.7895 | 132.0313 | 0.024296 | 0.34858 | 0.012296 | 0.31334 | 0.021159 | 0.3481
GARB | Garbutt T046 (TF5) | NQ | 11 | 20.0545 | 382.0894 | 20.7895 | 132.0313 | 0.024296 | 0.34858 | 0.012296 | 0.31334 | 0.021159 | 0.3481
GARB | Garbutt T046 | NQ | 66 | 18.2855 | 2090.3139 | 20.3302 | 774.6828 | 0.39676 | 2.2653 | 0.21101 | 1.6079 | 0.38223 | 2.256
GAVI | Gavial 66kV Switching Station | CA | 66 | 5.9261 | 677.4417 | 4.8963 | 186.5723 | 2.0457 | 6.7736 | 3.2336 | 11.0572 | 2.048 | 6.7943
GAYN | Gayndah | WB | 11 | 5.1048 | 97.2596 | 6.4502 | 40.9642 | 0.46623 | 1.2905 | 0.026439 | 0.52812 | 0.46487 | 1.2904
GAYN | Gayndah (Regulated) | WB | 66 | 1.3402 | 153.2049 | 0.87077 | 33.1808 | 15.7473 | 27.1174 | 27.5028 | 77.7886 | 15.6985 | 27.1161
GAYN | Gayndah (Unregulated) | WB | 66 | 1.3402 | 153.2049 | 0.87077 | 33.1808 | 15.7473 | 27.1174 | 27.5028 | 77.7886 | 15.6985 | 27.1161
GEOR | Georgetown | FN | 132 | 0.67151 | 153.5267 | 0.87903 | 66.9914 | 48.1603 | 128.9192 | 5.3287 | 53.5866 | 46.3345 | 129.9964
GEOR | Georgetown | FN | 22 | 1.2272 | 46.7637 | 1.4636 | 18.5898 | 1.9937 | 12.5922 | 0.0026787 | 7.8633 | 1.9356 | 12.6221
GEOR | Georgetown | FN | 6.6 | 8.2715 | 94.5555 | 0 | 0 | 0.12835 | 0.55241 | 116470583.9317 | 9.7992 | 0.12314 | 0.55509
GEOR | Georgetown | FN | 66 | 1.0491 | 119.9286 | 1.4724 | 56.1061 | 12.135 | 43.0638 | 0.4114 | 9.9523 | 11.612 | 43.3332
GIRU | Giru (TF1) | NQ | 11 | 3.7808 | 72.0345 | 4.486 | 28.4897 | 0.77106 | 1.6831 | 0.088045 | 1.0218 | 0.76622 | 1.6838
GIRU | Giru (TF1) | NQ | 11 | 3.7808 | 72.0345 | 4.486 | 28.4897 | 0.77106 | 1.6831 | 0.088045 | 1.0218 | 0.76622 | 1.6838
GIRU | Giru | NQ | 66 | 1.227 | 140.2701 | 0.90966 | 34.6626 | 24.5885 | 23.8086 | 31.4627 | 65.0561 | 24.4141 | 23.8321
GIVE | Givelda | WB | 11 | 7.5158 | 143.1953 | 8.6006 | 54.621 | 0.13295 | 0.92111 | 0.024501 | 0.57727 | 0.13239 | 0.92262
GIVE | Givelda | WB | 66 | 3.2335 | 369.6338 | 2.3202 | 88.4123 | 3.9043 | 12.3781 | 7.2195 | 27.3007 | 3.8841 | 12.4326
GLEE | Glenelg | NQ | 33 | 0.15917 | 9.0975 | 0.15628 | 2.9776 | 23.9776 | 140.6547 | 15.6085 | 123.0127 | 23.9713 | 140.8691
GLEE | Glenelg | NQ | 66 | 0.58153 | 66.4777 | 0.37063 | 14.123 | 33.4764 | 70.568 | 56.9055 | 180.3815 | 33.4511 | 71.4256
GLEL | Glenella | MK | 11 | 12.6631 | 241.265 | 14.4433 | 91.7274 | 0.0429 | 0.55051 | 0.011223 | 0.34723 | 0.041543 | 0.55161
GLEL | Glenella (TF5) | MK | 33 | 4.7182 | 269.683 | 5.7435 | 109.4277 | 0.3408 | 4.4328 | 0.10523 | 2.0549 | 0.32864 | 4.4428
GLEL | Glenella (TF6) | MK | 33 | 4.7214 | 269.867 | 5.6891 | 108.3922 | 0.34079 | 4.4298 | 0.10622 | 2.1658 | 0.32863 | 4.4397
GLEL | Glenella | MK | 66 | 5.6645 | 647.5395 | 5.8712 | 223.7239 | 1.1404 | 7.3182 | 0.71713 | 6.5594 | 1.0915 | 7.3577
GLEN | Glenden | MK | 11 | 6.0698 | 115.645 | 7.2546 | 46.073 | 0.36251 | 1.0942 | 0.03025 | 0.605 | 0.36255 | 1.0941
GLEN | Glenden | MK | 66 | 1.9722 | 225.4584 | 1.5643 | 59.6076 | 11.9602 | 17.6068 | 12.9978 | 36.3437 | 11.9616 | 17.604
GLFS | Gladstone Friend Street | CA | 11 | 18.0016 | 342.9762 | 19.5961 | 124.4517 | 0.036105 | 0.38648 | 0.016363 | 0.29279 | 0.036084 | 0.38674
GLFS | Gladstone Friend Street | CA | 66 | 12.1628 | 1390.3949 | 11.1154 | 423.5531 | 0.7107 | 3.373 | 1.2396 | 4.2427 | 0.70995 | 3.382
GLFS | Gladstone Friend Street | CA | 66 | 12.1628 | 1390.3949 | 11.1154 | 423.5531 | 0.7107 | 3.373 | 1.2396 | 4.2427 | 0.70995 | 3.382
GLNO | Gladstone North T074 (TF1) | CA | 11 | 21.6915 | 413.2779 | 0 | 0 | 0.025658 | 0.32111 | 135802465.6733 | 5.0553 | 0.025649 | 0.32134
GLNO | Gladstone North T074 (TF2) | CA | 11 | 21.5179 | 409.9719 | 0 | 0 | 0.025368 | 0.32374 | 135802465.5596 | -9.6543 | 0.025359 | 0.32397
GLNO | Gladstone North T074 (TF1) | CA | 132 | 27.7378 | 6341.7121 | 33.2397 | 2533.2053 | 0.13904 | 3.0198 | 0.055432 | 1.4893 | 0.13924 | 3.051
GLNO | Gladstone North T074 (TF2) | CA | 132 | 27.7378 | 6341.7121 | 33.2397 | 2533.2053 | 0.13904 | 3.0198 | 0.055432 | 1.4893 | 0.13924 | 3.051
GLNO | Gladstone North T074 | CA | 66 | 14.6479 | 1674.4794 | 17.5558 | 668.9661 | 0.26043 | 2.8504 | 0.063066 | 1.4313 | 0.26009 | 2.8585
GLSO | Gladstone South T152 (TF 1) | CA | 11 | 13.445 | 256.1619 | 14.1953 | 90.1524 | 0.026384 | 0.51905 | 0.017395 | 0.43661 | 0.026356 | 0.51932
GLSO | Gladstone South T152 (TF 2) | CA | 11 | 13.445 | 256.1619 | 14.1953 | 90.1524 | 0.026384 | 0.51905 | 0.017395 | 0.43661 | 0.026356 | 0.51932
GLSO | Gladstone South T152 | CA | 66 | 14.0443 | 1605.4744 | 16.3698 | 623.773 | 0.3236 | 2.9677 | 0.19188 | 1.6919 | 0.32261 | 2.9776
GOOB | Gooburrum | WB | 11 | 4.6988 | 89.5242 | 5.4564 | 34.6526 | 0.51208 | 1.3977 | 0.07874 | 0.88432 | 0.51145 | 1.3998
GOOB | Gooburrum | WB | 3.3 | 6.7464 | 38.5607 | 7.1234 | 13.5719 | 0.039001 | 0.30858 | 1.3614e-10 | 0.26237 | 0.038944 | 0.30877
GOOB | Gooburrum | WB | 66 | 1.7352 | 198.3554 | 1.2648 | 48.196 | 15.6003 | 18.4826 | 20.756 | 47.8062 | 15.5774 | 18.5584
GOOT | Gootchie (TF1) | WB | 11 | 3.0686 | 58.4656 | 3.4708 | 22.0424 | 0.62942 | 2.1943 | 0.00013316 | 1.5247 | 0.6284 | 2.1946
GOOT | Gootchie (TF2) | WB | 11 | 3.0686 | 58.4656 | 3.4708 | 22.0424 | 0.62942 | 2.1943 | 0.00013316 | 1.5247 | 0.6284 | 2.1946
GOOT | Gootchie | WB | 66 | 1.2419 | 141.9704 | 0.83272 | 31.7308 | 19.4475 | 27.6975 | 26.76 | 80.8103 | 19.4109 | 27.7092
GORD | Gordonvale SS | FN | 22 | 4.0341 | 153.7181 | 3.0687 | 38.9778 | 1.7403 | 3.0019 | 2.2867 | 6.4126 | 1.7391 | 3
GRCR | Granite Creek T166 | CA | 132 | 2.4347 | 593.7 | 2.312 | 176.2009 | 12.596 | 32.0729 | 4.6059 | 40.4882 | 12.5887 | 32.1012
GRCR | Granite Creek T166 | CA | 22 | 3.3076 | 150.8 | 3.5612 | 45.2328 | 0.48377 | 4.1996 | 0.333 | 3.303 | 0.48357 | 4.2003
GRCR | Granite Creek T166 | CA | 66 | 1.9782 | 239.9 | 2.3682 | 90.2413 | 3.4918 | 20.9154 | 0.97774 | 10.6814 | 3.49 | 20.9225
GREN | Greenvale | NQ | 11 | 0.49468 | 9.4248 | 0.52119 | 3.31 | 2.4431 | 13.9389 | 1.1966 | 11.9661 | 2.4412 | 13.9424
GREN | Greenvale | NQ | 66 | 0.49998 | 57.155 | 0.31448 | 11.9832 | 44.8722 | 71.0198 | 80.743 | 220.627 | 44.8051 | 71.1463
GUML | Gumlu (TF1) | NQ | 11 | 0.54991 | 10.4772 | 0.56355 | 3.579 | 3.0513 | 12.3678 | 2.5335 | 11.5316 | 3.0479 | 12.3669
GUML | Gumlu (TF2) | NQ | 11 | 0.79217 | 15.0929 | 0.81918 | 5.2025 | 0.91616 | 8.7954 | 0.39847 | 7.9594 | 0.91274 | 8.7945
GUML | Gumlu (TF1) | NQ | 66 | 1.187 | 135.6953 | 0.72627 | 27.6747 | 18.6418 | 30.104 | 29.5583 | 100.0505 | 18.5186 | 30.0726
GUML | Gumlu (TF2) | NQ | 66 | 1.187 | 135.6953 | 0.72627 | 27.6747 | 18.6418 | 30.104 | 29.5583 | 100.0505 | 18.5186 | 30.0726
GUNP | Gunpowder (TF2) | NQ - MI | 11 | 20.1192 | 383.3222 | 0.019128 | 0.12148 | 0.02915 | 0.346 | 0.013625 | 1094.9737 | 0.026408 | 0.35076
GUNP | Gunpowder (TF1) | NQ - MI | 11 | 20.1192 | 383.3222 | 0.019128 | 0.12148 | 0.02915 | 0.346 | 0.013625 | 1094.9737 | 0.026408 | 0.35076
GUNP | Gunpowder | NQ - MI | 220 | 1.2859 | 490.0082 | 1.7504 | 222.325 | 10.6483 | 108.1282 | 0.54814 | 20.4096 | 9.5516 | 110.0309
GUTH | Guthalungra | NQ | 11 | 0.39546 | 7.5345 | 0.40346 | 2.5623 | 1.472 | 17.6526 | 0.83189 | 16.6314 | 1.4686 | 17.6517
GUTH | Guthalungra | NQ | 66 | 0.96868 | 110.7346 | 0.58984 | 22.4759 | 23.0445 | 36.7647 | 37.8062 | 123.1077 | 22.9214 | 36.7333
HAIS | Hayman Island | MK | 11 | 1.9477 | 37.1089 | 2.3721 | 15.0652 | 1.472 | 3.2782 | 0.17532 | 1.7324 | 1.4705 | 3.2753
HAIS | Hayman Island | MK | 22 | 1.7345 | 66.0928 | 1.0312 | 13.0975 | 5.1868 | 6.1831 | 26.5679 | 4.8173 | 5.1808 | 6.1715
HAUG | Haughton (TF1) | NQ | 11 | 5.0653 | 96.5073 | 5.6394 | 35.8152 | 0.36345 | 1.3343 | 0.10246 | 0.963 | 0.35899 | 1.332
HAUG | Haughton (TF2) | NQ | 11 | 5.0653 | 96.5073 | 5.6394 | 35.8152 | 0.36345 | 1.3343 | 0.10246 | 0.963 | 0.35899 | 1.332
HAUG | Haughton | NQ | 66 | 2.5842 | 295.4179 | 1.7956 | 68.4231 | 9.3479 | 13.3083 | 13.912 | 35.636 | 9.2366 | 13.2767
HAVI | Havilah T184 | NQ | 11 | 7.8589 | 149.7317 | 5.5668 | 35.3536 | 0.12197 | 0.88205 | 4.9091e-09 | 2 | 0.12207 | 0.88186
HAVI | Havilah T184 | NQ | 132 | 2.8164 | 643.9099 | 1.9118 | 145.6977 | 12.326 | 27.1496 | 23.6559 | 68.3437 | 12.3404 | 27.1219
HELE | Helenvale | FN | 22 | 1.0369 | 39.5126 | 1.2821 | 16.2849 | 2.0693 | 13.3366 | 0.0053571 | 5.7799 | 1.9573 | 13.3817
HELE | Helenvale | FN | 66 | 0.91784 | 104.9229 | 0.60441 | 23.0312 | 12.5065 | 43.9996 | 27.8389 | 113.4382 | 11.4981 | 44.4053
HEPA | Hermit Park (TF1) | NQ | 11 | 14.0451 | 267.5951 | 14.8856 | 94.5363 | 0.040428 | 0.4974 | 0.017839 | 0.41531 | 0.040043 | 0.4971
HEPA | Hermit Park (TF2) | NQ | 11 | 14.0451 | 267.5951 | 14.8856 | 94.5363 | 0.040428 | 0.4974 | 0.017839 | 0.41531 | 0.040043 | 0.4971
HEPA | Hermit Park | NQ | 66 | 13.7303 | 1569.5848 | 11.6561 | 444.1587 | 0.81314 | 2.953 | 1.0675 | 4.5966 | 0.79894 | 2.9423
HIGH | Highfields (Unregulated) | SW | 0.415 | 23.4941 | 16.211 | 24.4214 | 5.6169 | 0.0010009 | 0.010239 | 0.0005 | 0.0091 | 0.0010009 | 0.010238
HIGH | Highfields | SW | 11 | 2.9784 | 56.7453 | 3.3861 | 21.5049 | 0.45883 | 2.302 | 0.075588 | 1.5099 | 0.45883 | 2.3017
HIGH | Highfields | SW | 33 | 2.6481 | 151.3608 | 0.97134 | 18.5064 | 3.4492 | 7.1296 | 6.195 | 49.1824 | 3.4492 | 7.1265
HILL | Hillsborough | NQ | 66 | 2.7994 | 320.0096 | 1.8926 | 72.119 | 7.5123 | 13.0739 | 11.0502 | 35.2973 | 7.4335 | 13.0425
HOHI | Home Hill (TF1) | NQ | 11 | 16.0873 | 306.505 | 18.1456 | 115.2397 | 0.0923 | 0.4253 | 0.0148 | 0.2911 | 0.0879 | 0.4243
HOHI | Home Hill (TF2) | NQ | 11 | 16.0873 | 306.505 | 18.1456 | 115.2397 | 0.0923 | 0.4253 | 0.0148 | 0.2911 | 0.0879 | 0.4243
HOHI | Home Hill | NQ | 66 | 5.7532 | 657.6783 | 4.2035 | 160.1745 | 2.6748 | 6.796 | 3.9486 | 14.9693 | 2.5557 | 6.7749
HOWA | Howard | WB | 11 | 4.6163 | 87.9518 | 5.1707 | 32.8382 | 0.1741 | 1.5089 | 0.0549 | 1.0223 | 0.1733 | 1.5089
HOWA | Howard | WB | 66 | 2.6049 | 297.7826 | 1.7215 | 65.597 | 4.2909 | 15.57 | 7.9963 | 40.1351 | 4.2599 | 15.5689
HPCT | Hay Point | MK | 33 | 6.7915 | 388.1852 | 5.6624 | 107.8823 | 0.75737 | 2.995 | 0.96544 | 4.8361 | 0.75666 | 3.0061
HUGH | Hughenden | NQ | 33 | 1.6998 | 97.1552 | 2.0583 | 39.2158 | 2.7334 | 13.5857 | 0.038682 | 2.6004 | 2.9147 | 14.5282
HUGH | Hughenden | NQ | 66 | 1.6813 | 192.2008 | 1.8852 | 71.8369 | 8.6837 | 25.5813 | 1.3599 | 13.2466 | 8.6584 | 26.4389
ILBI | Ilbilbie | MK | 11 | 0.78025 | 14.8658 | 0.86123 | 5.4695 | 2.3715 | 8.6425 | 0.64594 | 6.4594 | 2.3765 | 8.6539
ILBI | Ilbilbie | MK | 33 | 0.83762 | 47.8766 | 0.49249 | 9.3832 | 15.53 | 19.6481 | 25.6699 | 75.0974 | 15.5753 | 19.7508
ILRE | Ilbilbie Regulator (Primary) | MK | 33 | 0.82019 | 46.88 | 0.48201 | 9.1836 | 15.8205 | 20.0971 | 26.3402 | 76.6792 | 15.8657 | 20.1998
ILRE | Ilbilbie Regulator (Secondary) | MK | 33 | 0.82019 | 46.88 | 0.48201 | 9.1836 | 15.8205 | 20.0971 | 26.3402 | 76.6792 | 15.8657 | 20.1998
INGH | Ingham T047 | NQ | 11 | 8.6587 | 164.9696 | 9.6728 | 61.4306 | 0.060358 | 0.80622 | 0.028761 | 0.55093 | 0.058495 | 0.80973
INGH | Ingham T047 | NQ | 66 | 4.5355 | 518.4803 | 5.0501 | 192.4356 | 1.1375 | 9.1905 | 0.53414 | 6.3013 | 1.0705 | 9.317
INNI | Innisfail T050 | FN | 22 | 11.5372 | 439.6248 | 8.6951 | 110.4429 | 0.13811 | 1.2052 | 0.56902 | 2.3315 | 0.13043 | 1.2204
ISIS | Isis T131 | WB | 132 | 7.0678 | 1615.9115 | 6.9973 | 533.2634 | 2.2074 | 11.675 | 1.7799 | 12.0542 | 2.1613 | 11.7133
ISIS | Isis T131 | WB | 66 | 7.8906 | 902.0129 | 9.1491 | 348.6268 | 0.7754 | 5.2693 | 0.3368 | 3.095 | 0.7459 | 5.2706
ISPL | Isaac Plains | MK | 66 | 2.8519 | 326.0215 | 2.3618 | 89.9979 | 4.4496 | 14.0241 | 7.5998 | 22.6376 | 4.4454 | 14.0256
JAND | Jandowae (TF1) | SW | 11 | 0.55018 | 10.4823 | 0.61792 | 3.9243 | 4.6843 | 11.8169 | 0.44354 | 8.8709 | 4.6816 | 11.8178
JAND | Jandowae (TF2) | SW | 11 | 1.0004 | 19.0604 | 1.3037 | 8.2795 | 4.355 | 5.4684 | 0.1142 | 2.5224 | 4.3522 | 5.4693
JAND | Jandowae | SW | 33 | 0.45146 | 25.8043 | 0.32854 | 6.2595 | 38.1672 | 26.5144 | 46.4419 | 94.0521 | 38.1421 | 26.5223
JARV | Jarvisfield (TF1) | NQ | 11 | 6.7958 | 129.4767 | 7.3074 | 46.408 | 0.1581 | 1.0181 | 0.0737 | 0.8118 | 0.1546 | 1.0179
JARV | Jarvisfield (TF2) | NQ | 11 | 6.7958 | 129.4767 | 7.3074 | 46.408 | 0.1581 | 1.0181 | 0.0737 | 0.8118 | 0.1546 | 1.0179
JARV | Jarvisfield | NQ | 66 | 5.2337 | 598.2886 | 3.976 | 151.5071 | 3.0407 | 7.4291 | 4.0194 | 15.2318 | 2.9129 | 7.4198
JUCR | Julia Creek | NQ | 33 | 0.4674 | 26.7156 | 0.55205 | 10.518 | 18.6979 | 44.8468 | 1.2816 | 19.3782 | 18.6915 | 45.0612
JUCR | Julia Creek | NQ | 66 | 0.29649 | 33.8937 | 0.31892 | 12.1526 | 72.3055 | 135.0562 | 10.9238 | 99.0112 | 72.2802 | 135.9138
JUPO | Jubilee Pocket | MK | 11 | 5.5379 | 105.511 | 6.5383 | 41.5235 | 0.28493 | 1.2313 | 0.022269 | 0.69804 | 0.28292 | 1.2279
JUPO | Jubilee Pocket | MK | 66 | 1.9624 | 224.3291 | 1.3739 | 52.3538 | 9.4557 | 19.1969 | 12.9073 | 47.7668 | 9.3834 | 19.0742
KAIM | Kaimkillenbun | SW | 11 | 1.3147 | 25.0478 | 1.5244 | 9.6811 | 2.2868 | 4.8019 | 0.1828 | 3.3062 | 2.2868 | 4.802
KAIM | Kaimkillenbun | SW | 33 | 0.90286 | 51.6054 | 0.68316 | 13.0159 | 18.9364 | 13.4619 | 22.0284 | 43.0351 | 18.9364 | 13.4628
KALA | Kalamia | NQ | 11 | 7.8561 | 149.6787 | 7.3029 | 46.3795 | 0.15271 | 0.87713 | 0.072446 | 1.0923 | 0.10601 | 0.88429
KALA | Kalamia | NQ | 66 | 2.8437 | 325.0831 | 1.9892 | 75.7992 | 6.8193 | 13.098 | 10.6951 | 32.2442 | 6.5955 | 13.206
KAME | Kamerunga T053 | FN | 22 | 12.8852 | 490.9916 | 9.2041 | 116.9083 | 0.092981 | 1.0823 | 0.57342 | 2.3394 | 0.090837 | 1.0784
KEBE | Kewerra Beach | CA | 22 | 4.9363 | 188.0977 | 4.034 | 51.2385 | 2.2683 | 1.7013 | 3.2937 | 3.4664 | 2.2662 | 1.6975
KECE | Kelsey Creek East (TF1) | MK | 11 | 12.5198 | 238.5345 | 14.2694 | 90.623 | 0.074177 | 0.5541 | 0.015164 | 0.35693 | 0.073189 | 0.5517
KECE | Kelsey Creek East (TF2) | MK | 11 | 12.5198 | 238.5345 | 14.2694 | 90.623 | 0.074177 | 0.5541 | 0.015164 | 0.35693 | 0.073189 | 0.5517
KECE | Kelsey Creek East (TF1) | MK | 66 | 5.6354 | 644.2164 | 7.2037 | 274.4979 | 2.1497 | 7.1352 | 0.41311 | 2.6714 | 2.1139 | 7.0485
KECE | Kelsey Creek East (TF2) | MK | 66 | 5.6431 | 645.0891 | 7.2246 | 275.2953 | 2.144 | 7.1264 | 0.40233 | 2.6426 | 2.1081 | 7.0397
KEMM | Kemmis T067 | MK | 66 | 5.3285 | 609.1293 | 6.6981 | 255.2337 | 0.89796 | 7.8241 | 0.98783 | 2.927 | 0.89848 | 7.8388
KESP | Kearneys Spring T167 (TF1) | SW | 110 | 19.1993 | 3657.9551 | 17.2169 | 1093.4216 | 0.31314 | 3.6281 | 0.65226 | 4.9049 | 0.31287 | 3.5821
KESP | Kearneys Spring T167 (TF2) | SW | 110 | 19.1778 | 3653.863 | 17.1818 | 1091.1914 | 0.31384 | 3.6321 | 0.65478 | 4.9215 | 0.31357 | 3.5861
KESP | Kearneys Spring T167 | SW | 11 | 18.5765 | 353.93 | 4.0751 | 25.8802 | 0.011697 | 0.37618 | 1.4224e-07 | 4.395 | 0.011694 | 0.37572
KIDS | Kidston T077 | FN | 132 | 0.8554 | 195.5618 | 1.2813 | 97.6469 | 34.3442 | 96.9387 | 0.1828 | 9.5025 | 32.7317 | 97.9891
KIDS | Kidston T077 | FN | 6.6 | 12.764 | 145.9125 | 0.0242 | 0.0921 | 0.0911 | 0.3323 | 569.999 | 0.0881 | 0.0871 | 0.335
KILK | Kilkivan T012 | WB | 132 | 7.9402 | 1815.3804 | 7.16 | 545.6666 | 2.3206 | 10.3053 | 2.0148 | 13.8656 | 2.3214 | 10.3281
KILK | Kilkivan T012 | WB | 66 | 2.5999 | 297.205 | 3.2519 | 123.9127 | 1.2164 | 16.0848 | 0.082931 | 6.4236 | 1.2166 | 16.0905
KILL | Killarney (TF1) | SW | 11 | 1.3229 | 25.2047 | 1.611 | 10.2315 | 2.1957 | 4.8248 | 0.12954 | 2.5907 | 2.1916 | 4.8259
KILL | Killarney (TF2) | SW | 11 | 1.3229 | 25.2047 | 1.611 | 10.2315 | 2.1957 | 4.8248 | 0.12954 | 2.5907 | 2.1916 | 4.8259
KILL | Killarney | SW | 33 | 0.76815 | 43.9058 | 0.49279 | 9.3889 | 18.5954 | 20.1071 | 24.9182 | 71.6873 | 18.5583 | 20.1163
KING | Kingaroy | WB | 11 | 10.808 | 205.9207 | 12.3629 | 78.5149 | 0.08187 | 0.64125 | 0.016867 | 0.40309 | 0.08191 | 0.64142
KING | Kingaroy | WB | 66 | 4.717 | 539.2225 | 2.9151 | 111.0808 | 2.3401 | 8.5738 | 4.5679 | 24.9843 | 2.3416 | 8.58
KIRK | Kirknie | NQ | 11 | 5.1898 | 98.8795 | 5.6237 | 35.7154 | 0.26304 | 1.3241 | 0.051676 | 1.0447 | 0.25997 | 1.323
KIRK | Kirknie | NQ | 66 | 3.3328 | 380.9877 | 2.6175 | 99.7392 | 7.6092 | 10.0598 | 10.3831 | 20.7871 | 7.4986 | 10.0206
KITO | Kilkivan Town (TF1) | WB | 11 | 1.3369 | 25.4721 | 1.4423 | 9.1596 | 0.84814 | 5.159 | 0.72977 | 4.0137 | 0.84814 | 5.1591
KITO | Kilkivan Town (TF1) | WB | 11 | 1.3369 | 25.4721 | 1.4423 | 9.1596 | 0.84814 | 5.159 | 0.72977 | 4.0137 | 0.84814 | 5.1591
KITO | Kilkivan Town | WB | 66 | 1.6105 | 184.1018 | 2.0263 | 77.2111 | 1.9194 | 25.9698 | 0.79917 | 9.9583 | 1.9196 | 25.9755
KOCR | Kogan Creek | SW | 11 | 1.9141 | 36.4678 | 2.1693 | 13.7769 | 0.78728 | 3.568 | 0.11929 | 2.3858 | 0.78449 | 3.5688
KOCR | Kogan Creek | SW | 33 | 1.7168 | 98.128 | 1.1075 | 21.1016 | 6.012 | 10.6398 | 8.269 | 31.8051 | 5.9868 | 10.6476
KOGA | Kogan Regulator (Regulated) | SW | 33 | 1.1032 | 63.0556 | 0.91964 | 17.5215 | 8.5244 | 16.997 | 7.8328 | 29.7376 | 8.5244 | 16.9979
KOGA | Kogan Regulator (Unregulated) | SW | 33 | 1.1826 | 67.5973 | 0.9684 | 18.4505 | 8.4542 | 15.5928 | 7.9299 | 28.8508 | 8.4542 | 15.5938
KOUM | Koumala (1 Regulator) | MK | 11 | 1.8463 | 35.1776 | 2.1818 | 13.8563 | 1.3899 | 3.523 | 0.20603 | 2.0815 | 1.3949 | 3.5344
KOUM | Koumala (2 Regulator) | MK | 11 | 1.8463 | 35.1776 | 2.1818 | 13.8563 | 1.3899 | 3.523 | 0.20603 | 2.0815 | 1.3949 | 3.5344
KOUM | Koumala | MK | 33 | 1.2495 | 71.4213 | 0.75451 | 14.3754 | 10.6547 | 12.9741 | 15.9458 | 48.5633 | 10.7 | 13.0768
KUNW | Kunwarara | CA | 11 | 3.7174 | 70.8269 | 4.4273 | 28.1169 | 0.49214 | 1.8144 | 0.013414 | 0.99995 | 0.49221 | 1.815
KUNW | Kunwarara | CA | 66 | 1.2329 | 140.942 | 0.76901 | 29.3033 | 17.2343 | 29.3201 | 25.96 | 93.3473 | 17.2365 | 29.3416
LACR | Lakes Creek | CA | 11 | 16.7477 | 319.0874 | 18.9886 | 120.5941 | 0.062665 | 0.41256 | 0.017172 | 0.26918 | 0.062726 | 0.41315
LACR | Lakes Creek | CA | 66 | 7.5472 | 862.7665 | 6.1986 | 236.1999 | 1.6377 | 5.309 | 2.292 | 8.8754 | 1.64 | 5.3304
LAKE | Lakeland | FN | 132 | 0.91135 | 208.362 | 0.90313 | 68.8279 | 23.3506 | 89.136 | 22.134 | 91.695 | 22.2336 | 89.797
LAKE | Lakeland | FN | 22 | 1.6971 | 64.6695 | 2.1159 | 26.8759 | 0.88981 | 8.1983 | 1.0472e-08 | 3.3523 | 0.86827 | 8.2166
LAKE | Lakeland (TF1) | FN | 66 | 1.4278 | 163.2228 | 1.3594 | 51.8017 | 5.6691 | 28.8572 | 8.6396 | 32.7192 | 5.1447 | 29.0262
LAKE | Lakeland (TF2) | FN | 66 | 1.4278 | 163.2228 | 1.3594 | 51.8017 | 5.6691 | 28.8572 | 8.6396 | 32.7192 | 5.1447 | 29.0262
LANN | Lannercost | NQ | 11 | 3.5497 | 67.6316 | 3.9277 | 24.9443 | 0.41305 | 1.9283 | 0.1038 | 1.4075 | 0.41119 | 1.9318
LANN | Lannercost | NQ | 66 | 1.9261 | 220.182 | 1.4745 | 56.1875 | 11.133 | 18.7508 | 14.1234 | 39.7561 | 11.0659 | 18.8773
LAQU | Laguna Quays (TF1) | MK | 11 | 4.913 | 93.6049 | 5.9176 | 37.5819 | 0.5111 | 1.3298 | 0.03651 | 0.73043 | 0.51011 | 1.3274
LAQU | Laguna Quays (TF1) | MK | 11 | 4.913 | 93.6049 | 5.9176 | 37.5819 | 0.5111 | 1.3298 | 0.03651 | 0.73043 | 0.51011 | 1.3274
LAQU | Laguna Quays (TF1) | MK | 66 | 1.5242 | 174.2372 | 1.1302 | 43.0646 | 17.106 | 21.5994 | 20.5049 | 54.0532 | 17.0701 | 21.5127
LAQU | Laguna Quays (TF2) | MK | 66 | 1.5248 | 174.3136 | 1.1307 | 43.0865 | 17.0978 | 21.5904 | 20.4937 | 54.0213 | 17.0619 | 21.5037
LARO | Landing Road | CA | 11 | 6.0235 | 114.7633 | 6.2783 | 39.8726 | 0.070736 | 1.1579 | 0.057765 | 1.0169 | 0.070506 | 1.158
LARO | Landing Road | CA | 66 | 8.2254 | 940.2944 | 7.7719 | 296.1474 | 0.46695 | 5.0756 | 0.91477 | 5.9219 | 0.45868 | 5.0803
LEIC | Leichhardt | CA | 66 | 3.6568 | 418.0334 | 2.7608 | 105.1991 | 4.4542 | 10.5808 | 6.9375 | 21.6644 | 4.464 | 10.5316
LILY | Lilyvale | CA | 66 | 17.1677 | 1962.5326 | 20.9118 | 796.846 | 0.32134 | 2.4238 | 0.073961 | 1.1479 | 0.30245 | 2.4098
LITT | Littlemore | CA | 11 | 2.4571 | 46.8134 | 2.8559 | 18.1372 | 0.95673 | 2.6781 | 0.24707 | 1.6579 | 0.95668 | 2.6786
LITT | Littlemore | CA | 66 | 0.9371 | 107.125 | 0.57704 | 21.9882 | 25.5476 | 36.7282 | 39.7811 | 124.6317 | 25.5459 | 36.7465
LOCR | Louisa Creek | MK | 11 | 3.139 | 59.8053 | 3.2576 | 20.6882 | 0.15371 | 2.2227 | 0.099226 | 1.982 | 0.15363 | 2.2239
LOCR | Louisa Creek (TF1) | MK | 132 | 3.9622 | 905.8883 | 4.4429 | 338.5917 | 4.3963 | 20.7197 | 2.1585 | 14.0029 | 4.3856 | 20.8868
LOCR | Louisa Creek (TF2) | MK | 132 | 3.9622 | 905.8883 | 4.4429 | 338.5917 | 4.3963 | 20.7197 | 2.1585 | 14.0029 | 4.3856 | 20.8868
LOCR | Louisa Creek | MK | 33 | 9.5547 | 546.1223 | 10.3534 | 197.2596 | 0.28182 | 2.1777 | 0.11366 | 1.6764 | 0.28115 | 2.1882
LONG | Longreach | CA | 22 | 1.769 | 67.4072 | 2.381 | 30.243 | 2.1445 | 8.1006 | 0.15016 | 1.9454 | 2.0797 | 8.3381
LONG | Longreach | CA | 66 | 0.76368 | 87.2998 | 0.62268 | 23.7273 | 17.9487 | 55.397 | 47.7544 | 87.3033 | 17.3663 | 57.5346
LUCI | Lucinda | NQ | 11 | 2.2116 | 42.1373 | 2.3528 | 14.9424 | 0.50616 | 3.1235 | 0.20141 | 2.5829 | 0.5115 | 3.1357
LUCI | Lucinda | NQ | 66 | 1.8795 | 214.857 | 1.2484 | 47.5712 | 10.971 | 19.4606 | 20.9091 | 51.9307 | 11.1633 | 19.8999
LYLA | Lyndley Lane | SW | 22 | 0.14443 | 5.5034 | 0.14811 | 1.8812 | 8.935 | 96.4152 | 4.4749 | 89.4979 | 8.935 | 96.4156
LYLA | Lyndley Lane | SW | 33 | 1.1327 | 64.7448 | 0.68582 | 13.0667 | 10.0353 | 15.5639 | 15.079 | 53.6136 | 10.0353 | 15.5648
MACI | Maryborough City | WB | 11 | 10.7694 | 205.1842 | 11.9982 | 76.1987 | 0.063337 | 0.64737 | 0.023248 | 0.44753 | 0.062321 | 0.6477
MACI | Maryborough City | WB | 66 | 5.7281 | 654.8071 | 5.5694 | 212.2211 | 1.4432 | 7.1943 | 1.6001 | 7.7642 | 1.4066 | 7.206
MACK | Mackay T038 | MK | 33 | 16.7084 | 955.0159 | 22.6695 | 431.9113 | 0.1655 | 1.2445 | 0.0325 | 0.2583 | 0.1547 | 1.251
MACN | Macknade | NQ | 11 | 8.611 | 164.0613 | 6.7736 | 43.018 | 0.0997 | 0.8058 | 0.1188 | 1.1879 | 0.15 | 1.0814
MACN | Macknade | NQ | 66 | 2.7417 | 313.4149 | 1.8631 | 70.9921 | 5.5649 | 14.268 | 13.1078 | 34.0729 | 5.7719 | 14.7188
MACT | Mackay City | MK | 11 | 14.0857 | 260.9722 | 15.2497 | 96.8487 | 0.047217 | 0.50837 | 0.012463 | 0.35428 | 0.04691 | 0.50915
MACT | Mackay City | MK | 33 | 15.436 | 882.2849 | 20.4903 | 390.3927 | 0.2539 | 1.335 | 0.1466 | 0.3268 | 0.2432 | 1.3415
MAFU | Max Fulton (TF1) | NQ | 11 | 21.5131 | 409.8805 | 23.7485 | 150.8229 | 0.045 | 0.3227 | 0.0306 | 0.2326 | 0.0446 | 0.3222
MAFU | Max Fulton (TF2) | NQ | 11 | 21.5131 | 409.8805 | 23.7485 | 150.8229 | 0.045 | 0.3227 | 0.0306 | 0.2326 | 0.0446 | 0.3222
MAFU | Max Fulton (TF1) | NQ | 66 | 11.1792 | 1277.9575 | 10.183 | 388.0256 | 1.0019 | 3.6257 | 1.0048 | 4.7905 | 0.98756 | 3.6108
MAFU | Max Fulton (TF2) | NQ | 66 | 11.4503 | 1308.9398 | 10.6063 | 404.1529 | 0.9596 | 3.545 | 0.88792 | 4.4922 | 0.94525 | 3.5301
MAKA | Mary Kathleen | NQ - MI | 11 | 0.27733 | 5.2839 | 0.28872 | 1.8336 | 3.4529 | 24.9521 | 2.512 | 22.0658 | 3.4502 | 24.9569
MAKA | Mary Kathleen | NQ - MI | 66 | 0.38353 | 43.8435 | 0.32365 | 12.3328 | 33.8742 | 103.9065 | 43.8158 | 164.2072 | 33.7755 | 104.0777
MALC | Malchi | CA | 11 | 8.8678 | 168.9537 | 10.2269 | 64.9492 | 0.1598 | 0.77172 | 0.030848 | 0.47588 | 0.15987 | 0.7723
MALC | Malchi | CA | 66 | 3.6091 | 412.5783 | 2.549 | 97.1297 | 4.6424 | 10.6504 | 7.4313 | 25.1112 | 4.6447 | 10.6711
MARE | Mareeba (TF1) | FN | 22 | 6.0008 | 228.6615 | 7.1132 | 90.3492 | 0.3041 | 2.3118 | 0.0521 | 1.2268 | 0.2976 | 2.3276
MARE | Mareeba (TF2) | FN | 22 | 6.0008 | 228.6615 | 7.1132 | 90.3492 | 0.3041 | 2.3118 | 0.0521 | 1.2268 | 0.2976 | 2.3276
MARE | Mareeba (TF1) | FN | 66 | 4.2481 | 485.6173 | 4.3286 | 164.9434 | 2.2677 | 9.6178 | 2.0898 | 8.9707 | 2.2091 | 9.7593
MARE | Mareeba (TF2) | FN | 66 | 4.2481 | 485.6173 | 4.3286 | 164.9434 | 2.2677 | 9.6178 | 2.0898 | 8.9707 | 2.2091 | 9.7593
MARY | Maryborough T059 | WB | 132 | 5.012 | 1145.8991 | 5.5861 | 425.7212 | 3.4126 | 16.4115 | 0.81334 | 11.5622 | 3.3331 | 16.4548
MARY | Maryborough T059 | WB | 66 | 7.3633 | 841.7372 | 9.2058 | 350.7878 | 0.86201 | 5.6426 | 0.12419 | 2.2592 | 0.82545 | 5.6544
MASO | Marian South | MK | 11 | 10.7624 | 205.0511 | 8.2312 | 52.2752 | 0.10863 | 0.64026 | 0.059667 | 1.1931 | 0.087475 | 0.70125
MASO | Marian South | MK | 66 | 4.3063 | 492.2793 | 3.1302 | 119.2756 | 3.3431 | 9.1511 | 5.8803 | 19.7844 | 3.3463 | 9.2636
MCCR | McKinley Creek (TF1) | MK | 11 | 5.3698 | 102.3082 | 5.9275 | 37.6446 | 0.18426 | 1.2892 | 0.041659 | 0.93641 | 0.18362 | 1.2903
MCCR | McKinley Creek (TF1) | MK | 11 | 5.3698 | 102.3082 | 5.9275 | 37.6446 | 0.18426 | 1.2892 | 0.041659 | 0.93641 | 0.18362 | 1.2903
MCCR | McKinley Creek | MK | 66 | 3.0631 | 350.1543 | 2.2478 | 85.6526 | 5.1337 | 12.6996 | 10.683 | 26.5089 | 5.1105 | 12.7387
MEAD | Meadowvale | WB | 11 | 7.6768 | 146.2624 | 8.9204 | 56.6523 | 0.17642 | 0.89388 | 0.033619 | 0.5291 | 0.17578 | 0.89599
MEAD | Meadowvale | WB | 66 | 2.9759 | 340.1866 | 2.1141 | 80.5561 | 5.1408 | 13.1321 | 8.2188 | 30.2367 | 5.1179 | 13.208
MEAN | Meandarra | SW | 22 | 0.26908 | 10.2535 | 0.314 | 3.9883 | 14.1027 | 49.9785 | 1.5099 | 30.1973 | 14.1027 | 49.9795
MEAN | Meandarra | SW | 33 | 0.39727 | 22.707 | 0.22845 | 4.3526 | 28.3338 | 44.5077 | 45.4959 | 166.5632 | 28.3339 | 44.5099
MELR | Melrose | WB | 11 | 2.9607 | 56.409 | 3.3411 | 21.2187 | 0.493 | 2.3078 | 0.19623 | 1.5453 | 0.49304 | 2.308
MELR | Melrose | WB | 66 | 1.4232 | 162.6926 | 0.80197 | 30.5593 | 10.6836 | 27.4503 | 20.1458 | 96.3137 | 10.685 | 27.4565
MEMO | Memooloo T236 | CA | 132 | 1.9574 | 447.529 | 1.7755 | 135.3112 | 9.6536 | 41.7883 | 7.3005 | 55.813 | 9.648 | 41.7382
MERI | Merinda | NQ | 11 | 6.7641 | 128.8728 | 7.506 | 47.6693 | 0.1009 | 1.0299 | 0.036578 | 0.7288 | 0.10101 | 1.0292
MERI | Merinda | NQ | 66 | 3.8307 | 437.906 | 5.0347 | 191.8474 | 2.3152 | 10.7163 | 0.32175 | 3.1252 | 2.3189 | 10.6923
MERN | Meringandan (TF1) | SW | 11 | 4.5832 | 87.3215 | 5.5955 | 35.536 | 0.23242 | 1.5077 | 0.035004 | 0.70008 | 0.23241 | 1.5072
MERN | Meringandan (TF3) | SW | 11 | 4.5832 | 87.3215 | 5.5955 | 35.536 | 0.23242 | 1.5077 | 0.035004 | 0.70008 | 0.23241 | 1.5072
MERN | Meringandan (Highfields) | SW | 33 | 2.8032 | 160.2258 | 0.88071 | 16.7798 | 1.7767 | 7.2683 | 58.3593 | 21.1217 | 1.7767 | 7.2642
MERN | Meringandan (T116) | SW | 33 | 2.8032 | 160.2258 | 0.88071 | 16.7798 | 1.7767 | 7.2683 | 58.3593 | 21.1217 | 1.7767 | 7.2642
MICB | Mica Creek B Yard | NQ - MI | 132 | 7.9766 | 1823.6861 | 10.3121 | 785.8841 | 0.65605 | 10.4892 | 0.15319 | 2.7014 | 0.26125 | 11.1742
MICC | Mica Creek C Yard (TF1) | NQ - MI | 132 | 7.9223 | 1811.2888 | 10.1699 | 775.0522 | 0.66755 | 10.5606 | 0.19167 | 2.8972 | 0.27274 | 11.2455
MICC | Mica Creek C Yard (TF2) | NQ - MI | 132 | 7.9268 | 1812.3028 | 10.1814 | 775.928 | 0.6666 | 10.5547 | 0.18856 | 2.8812 | 0.2718 | 11.2397
MICC | Mica Creek C Yard | NQ - MI | 220 | 2.574 | 980.8399 | 3.4547 | 438.8107 | 2.4985 | 54.2225 | 0.35525 | 10.9056 | 1.4018 | 56.1252
MICO | Miles-Condamine | SW | 22 | 0.37123 | 14.1456 | 0.39597 | 5.0295 | 4.6054 | 37.359 | 1.5301 | 30.6029 | 4.6054 | 37.36
MICO | Miles-Condamine | SW | 33 | 1.255 | 71.7315 | 0.80379 | 15.3143 | 6.9192 | 15.2012 | 11.8869 | 43.4749 | 6.9193 | 15.2033
MIDD | Middlemount | CA | 22 | 2.4853 | 94.7009 | 2.9245 | 37.146 | 1.4351 | 5.4515 | 0.26644 | 3.103 | 1.4099 | 5.4767
MIDD | Middlemount | CA | 66 | 1.7803 | 203.5138 | 0.95947 | 36.5607 | 10.5181 | 21.1359 | 22.993 | 81.4054 | 10.2916 | 21.3633
MILC | Millchester T095 (TF3) | NQ | 11 | 5.1281 | 97.7025 | 5.5224 | 35.0721 | 0.18714 | 1.3732 | 0.059351 | 1.0501 | 0.18547 | 1.3728
MILC | Millchester T095 | NQ | 132 | 2.2693 | 518.8292 | 2.1301 | 162.3373 | 14.6791 | 34.3315 | 4.166 | 45.2925 | 14.5848 | 34.3073
MILC | Millchester T095 | NQ | 66 | 3.4088 | 389.6824 | 4.1161 | 156.8459 | 4.6003 | 11.6324 | 0.4602 | 5.9683 | 4.5403 | 11.6172
MILE | Miles | SW | 11 | 3.6281 | 69.124 | 4.2371 | 26.9091 | 0.35538 | 1.893 | 0.076636 | 1.0985 | 0.35531 | 1.8931
MILE | Miles (Columboola) | SW | 33 | 2.4224 | 138.457 | 1.9059 | 36.3115 | 1.9528 | 8.4296 | 4.06 | 15.1559 | 1.9528 | 8.4318
MILE | Miles (Rywung) | SW | 33 | 2.4224 | 138.457 | 1.9059 | 36.3115 | 1.9528 | 8.4296 | 4.06 | 15.1559 | 1.9528 | 8.4318
MILL | Millaroo | NQ | 11 | 2.9517 | 56.2376 | 3.2314 | 20.5221 | 0.56385 | 2.3057 | 0.088896 | 1.7779 | 0.56077 | 2.3046
MILL | Millaroo | NQ | 66 | 1.6446 | 188.0029 | 1.2497 | 47.6195 | 17.0983 | 19.0007 | 25.467 | 43.4682 | 16.9876 | 18.9614
MILM | Millmerran Town | SW | 11 | 1.6833 | 32.0712 | 2.1773 | 13.8279 | 1.5675 | 3.8558 | 0.07056 | 1.4112 | 1.5558 | 3.8495
MILM | Millmerran Town | SW | 33 | 0.81473 | 46.568 | 0.3169 | 6.0377 | 13.4723 | 22.0017 | 14.3154 | 150.8644 | 13.367 | 21.9444
MILN | Millennium Substation | MK | 11 | 5.2358 | 99.7557 | 0.0097129 | 0.061685 | 0.10669 | 1.3314 | 2160.0511 | 1.0341 | 0.10658 | 1.3315
MILN | Millennium Substation | MK | 66 | 3.8543 | 440.6097 | 3.5651 | 135.8496 | 1.9797 | 10.7052 | 2.4976 | 13.3063 | 1.9754 | 10.7066
MING | Mingela | NQ | 11 | 0.3084 | 5.8757 | 0.30892 | 1.9619 | 3.019 | 22.7344 | 2.5608 | 22.2097 | 3.018 | 22.734
MING | Mingela | NQ | 66 | 1.692 | 193.4255 | 1.2281 | 46.7988 | 16.4967 | 18.891 | 20.2498 | 50.3809 | 16.4614 | 18.8759
MIRA | Mirani (Reg 1) | MK | 11 | 3.4438 | 65.614 | 3.6768 | 23.3505 | 0.29572 | 2.0088 | 0.12364 | 1.641 | 0.29551 | 2.0113
MIRA | Mirani (Reg 2) | MK | 11 | 3.4438 | 65.614 | 3.6768 | 23.3505 | 0.29572 | 2.0088 | 0.12364 | 1.641 | 0.29551 | 2.0113
MIRA | Mirani (Unregulated) | MK | 11 | 3.7824 | 72.0639 | 4.0637 | 25.8082 | 0.24531 | 1.8324 | 0.073231 | 1.4646 | 0.2451 | 1.8348
MIRA | Mirani | MK | 66 | 2.8703 | 328.1143 | 1.9442 | 74.0855 | 6.1947 | 13.2398 | 9.8618 | 34.2357 | 6.1874 | 13.3281
MITC | Mitchell | SW | 11 | 0.7417 | 14.1312 | 0.97964 | 6.2216 | 5.0718 | 7.9373 | 0.14423 | 2.8845 | 5.0675 | 7.939
MITC | Mitchell | SW | 33 | 0.32996 | 18.8597 | 0.2391 | 4.5554 | 44.3486 | 45.4754 | 42.6791 | 136.8637 | 44.3097 | 45.4906
MIVA | Miriam Vale | CA | 22 | 1.1941 | 45.5003 | 1.457 | 18.5069 | 4.4531 | 10.8236 | 0.3761 | 5.5852 | 4.4529 | 10.8256
MIVA | Miriam Vale | CA | 66 | 0.70179 | 80.2249 | 0.44119 | 16.8115 | 36.6928 | 47.1451 | 55.0342 | 160.1971 | 36.6911 | 47.1634
MOBA | Mt Bassett (TF1) | MK | 11 | 8.9162 | 169.8763 | 10.1843 | 64.6791 | 0.12344 | 0.77457 | 0.024621 | 0.49243 | 0.1232 | 0.77534
MOBA | Mt Bassett (TF2) | MK | 11 | 8.9162 | 169.8763 | 10.1843 | 64.6791 | 0.12344 | 0.77457 | 0.024621 | 0.49243 | 0.1232 | 0.77534
MOBA | Mt Bassett | MK | 33 | 7.7977 | 445.6996 | 6.3573 | 121.1223 | 0.88935 | 2.5393 | 1.2508 | 4.342 | 0.88721 | 2.5462
MODA | Monduran Dam | WB | 11 | 2.388 | 45.498 | 2.6349 | 16.734 | 0.57749 | 2.8715 | 2.0138e-09 | 2.13 | 0.57693 | 2.8731
MODA | Monduran Dam | WB | 3.3 | 9.8975 | 56.572 | 11.2374 | 21.4102 | 0.05172 | 0.20561 | 1.6348e-10 | 0.13887 | 0.051669 | 0.20574
MODA | Monduran Dam | WB | 66 | 1.2426 | 142.0446 | 0.84641 | 32.2525 | 20.6909 | 26.6952 | 28.1998 | 77.9322 | 20.6708 | 26.7497
MOFO | Mt Fox | NQ | 33 | 0.17969 | 10.2706 | 0.18461 | 3.5173 | 10.7034 | 116.3831 | 5.4868 | 107.5407 | 10.6866 | 116.4147
MOFO | Mt Fox | NQ | 66 | 1.0228 | 116.9211 | 0.68632 | 26.1524 | 20.8665 | 35.3694 | 34.0889 | 96.4442 | 20.7994 | 35.4959
MOGA | Mt Garnet | FN | 22 | 1.3223 | 50.388 | 1.6827 | 21.3731 | 3.8492 | 9.8565 | 0.44582 | 3.8584 | 3.8424 | 9.8721
MOGA | Mt Garnet | FN | 66 | 0.67631 | 77.3122 | 0.4206 | 16.0269 | 30.6305 | 53.9834 | 49.1018 | 170.3082 | 30.5694 | 54.1235
MOLE | Mt Leyshon | NQ | 11 | 4.0848 | 77.8251 | 4.6222 | 29.3551 | 0.34659 | 1.705 | 0.028526 | 1.0979 | 0.34492 | 1.7046
MOLE | Mt Leyshon | NQ | 66 | 1.7283 | 197.5679 | 1.3557 | 51.6593 | 11.4501 | 21.8549 | 11.0103 | 43.3301 | 11.3901 | 21.8397
MOMG | Mt Morgan | CA | 11 | 5.5575 | 105.8845 | 6.4452 | 40.9325 | 0.38477 | 1.1972 | 0.072579 | 0.74702 | 0.38483 | 1.1978
MOMG | Mt Morgan | CA | 66 | 2.1262 | 243.0565 | 1.4947 | 56.9558 | 11.2379 | 16.2063 | 16.9436 | 41.9223 | 11.24 | 16.2281
MOMO | Mt Molloy (TF2) | FN | 22 | 0.553 | 21.0722 | 0.57863 | 7.3496 | 4.1956 | 24.9523 | 2.1291 | 21.8742 | 4.1891 | 24.968
MOMO | Mt Molloy | FN | 66 | 1.258 | 143.8133 | 0.87564 | 33.3663 | 18.5987 | 27.7029 | 25.9343 | 73.7323 | 18.5402 | 27.8445
MOMO | Mt Molloy (TF1) | FN | 22 | 2.0989 | 79.9782 | 2.5538 | 32.4378 | 2.2655 | 6.2698 | 0.199 | 3.1917 | 2.259 | 6.2856
MOMW | Mt Mowbullan | SW | 11 | 0.62911 | 11.9862 | 0.71871 | 4.5644 | 4.6241 | 10.107 | 0.36689 | 7.3378 | 4.6241 | 10.1071
MOMW | Mt Mowbullan | SW | 33 | 0.45894 | 26.2318 | 0.34128 | 6.5022 | 38.3147 | 24.9232 | 45.9441 | 87.8686 | 38.3146 | 24.9241
MONT | Monto | CA | 11 | 4.2079 | 80.1718 | 5.289 | 33.5898 | 0.77 | 1.4713 | 0.057037 | 0.68448 | 0.76998 | 1.4717
MONT | Monto | CA | 66 | 0.62661 | 71.6307 | 0.4321 | 16.4652 | 46.5291 | 48.0889 | 64.8945 | 148.3282 | 46.5287 | 48.1068
MOOE | Moore | WB | 11 | 3.279 | 62.4736 | 3.6051 | 22.8954 | 0.47271 | 2.0777 | 0.19623 | 1.5453 | 0.47275 | 2.0779
MOOE | Moore | WB | 66 | 1.9411 | 221.8989 | 1.1694 | 44.5618 | 9.9534 | 19.1663 | 15.9716 | 63.039 | 9.9549 | 19.1725
MOOR | Moorvale | MK | 11 | 4.8713 | 92.8102 | 5.3528 | 33.9951 | 0.158 | 1.4269 | 0.069875 | 1.0469 | 0.15789 | 1.427
MOOR | Moorvale | MK | 66 | 2.9878 | 341.5519 | 2.3741 | 90.4653 | 3.1727 | 13.681 | 4.2765 | 24.5909 | 3.1684 | 13.6825
MOPA | Mona Park (TF1) | NQ | 11 | 5.4202 | 103.2681 | 5.791 | 36.7775 | 0.1908 | 1.2779 | 0.098949 | 1.0402 | 0.18743 | 1.2773
MOPA | Mona Park (TF2) | NQ | 11 | 5.4202 | 103.2681 | 5.791 | 36.7775 | 0.1908 | 1.2779 | 0.098949 | 1.0402 | 0.18743 | 1.2773
MOPA | Mona Park | NQ | 66 | 4.5809 | 523.6616 | 3.2664 | 124.4679 | 3.3067 | 8.5559 | 4.8283 | 19.7904 | 3.1852 | 8.5361
MORA | Moranbah T034 (TF1) | MK | 11 | 33.4974 | 638.2117 | 1.662 | 10.5551 | 0.02 | 0.2077 | 4.8231 | 11.2305 | 0.017 | 0.2077
MORA | Moranbah T034 (TF3) | MK | 11 | 33.4974 | 638.2117 | 1.662 | 10.5551 | 0.02 | 0.2077 | 4.8231 | 11.2305 | 0.017 | 0.2077
MORA | Moranbah T034 | MK | 66 | 13.7865 | 1576.0048 | 16.1078 | 613.7911 | 0.5154 | 2.9982 | 0.1663 | 1.7272 | 0.4699 | 3.0011
MORO | Mt Rooper | MK | 11 | 3.2539 | 61.9955 | 3.6187 | 22.9817 | 0.38136 | 2.1168 | 0.075667 | 1.5124 | 0.37935 | 2.1134
MORO | Mt Rooper | MK | 66 | 1.7204 | 196.6705 | 1.174 | 44.7372 | 11.0079 | 21.7857 | 15.4001 | 57.1663 | 10.9356 | 21.663
MORW | Mt Rawdon | WB | 66 | 1.0235 | 117.0042 | 0.62838 | 23.9445 | 19.178 | 36.3077 | 34.4227 | 114.0775 | 19.1352 | 36.306
MOSI | Mt Sibley (TF1) | SW | 11 | 2.9349 | 55.9175 | 3.7765 | 23.9841 | 0.84381 | 2.2278 | 0.041145 | 0.8229 | 0.84381 | 2.2273
MOSI | Mt Sibley (TF3) | SW | 11 | 2.9349 | 55.9175 | 3.7765 | 23.9841 | 0.84381 | 2.2278 | 0.041145 | 0.8229 | 0.84381 | 2.2273
MOSI | Mt Sibley | SW | 33 | 1.4404 | 82.3286 | 0.58024 | 11.0551 | 7.224 | 12.6437 | 66.5811 | 46.7865 | 7.224 | 12.6396
MOSS | Mossman (TF2) | FN | 22 | 3.2902 | 125.3752 | 4.0173 | 51.027 | 1.2384 | 4.0675 | 0.12144 | 1.9757 | 1.2066 | 4.0853
MOSS | Mossman | FN | 66 | 1.6929 | 193.5276 | 1.1252 | 42.8771 | 11.3632 | 22.0357 | 18.5921 | 59.8272 | 11.2364 | 22.2068
MOTY | Mt Tyson | SW | 33 | 1.1525 | 65.8719 | 0.8102 | 15.4364 | 12.4584 | 13.3202 | 15.9676 | 39.7656 | 12.3531 | 13.2628
MOUR | Moura T027 (TF1) | CA | 11 | 19.3346 | 368.3739 | 17.5463 | 111.4337 | 0.047308 | 0.35836 | 0.00061315 | 0.47163 | 0.047399 | 0.36113
MOUR | Moura T027 (TF2) | CA | 11 | 19.3346 | 368.3739 | 17.5463 | 111.4337 | 0.047308 | 0.35836 | 0.00061315 | 0.47163 | 0.047399 | 0.36113
MOUR | Moura T027 | CA | 22 | 5.1358 | 195.7011 | 4.7703 | 60.5907 | 0.30107 | 2.7049 | 0.0025289 | 3.3488 | 0.30143 | 2.716
MOUR | Moura T027 | CA | 66 | 5.884 | 672.6263 | 7.2899 | 277.7814 | 1.5256 | 6.9616 | 0.12805 | 2.9394 | 1.5306 | 7.0596
MUCK | Muckadilla Regulator (Regulated) | SW | 33 | 0.58394 | 33.3767 | 0.46663 | 8.8904 | 24.8375 | 25.9106 | 16.6626 | 65.4722 | 24.7986 | 25.9259
MUCK | Muckadilla Regulator (Unregulated) | SW | 33 | 0.55696 | 31.8346 | 0.45029 | 8.5792 | 24.9505 | 28.1703 | 16.4152 | 66.5481 | 24.9116 | 28.1855
MURG | Murgon (TF1) | WB | 11 | 4.6582 | 88.7516 | 5.9355 | 37.6955 | 0.2293 | 1.4829 | 0.0237 | 0.533 | 0.2293 | 1.483
MURG | Murgon (TF2) | WB | 11 | 4.6582 | 88.7516 | 5.9355 | 37.6955 | 0.2293 | 1.4829 | 0.0237 | 0.533 | 0.2293 | 1.483
MURG | Murgon | WB | 66 | 1.1987 | 137.0292 | 1.172 | 44.6578 | 7.4027 | 34.1941 | 11.1283 | 35.7541 | 7.4029 | 34.1998
MUTA | Mutarnee | NQ | 11 | 0.94692 | 18.0413 | 0.98714 | 6.2692 | 1.7372 | 7.1857 | 1.1464 | 6.4 | 1.7353 | 7.1892
MUTA | Mutarnee | NQ | 66 | 1.1868 | 135.6697 | 0.88987 | 33.9087 | 21.2692 | 28.2867 | 30.6629 | 64.6103 | 21.2021 | 28.4131
MUTO | Mundubbera Town | WB | 11 | 3.9728 | 75.6927 | 5.4113 | 34.3664 | 0.86389 | 1.5369 | 0.019458 | 0.38866 | 0.86254 | 1.5369
MUTO | Mundubbera Town | WB | 66 | 0.81991 | 93.7282 | 0.55079 | 20.9879 | 30.4978 | 41.1964 | 50.9672 | 116.9188 | 30.4491 | 41.1951
NANA | Nanango | WB | 11 | 4.9881 | 95.0361 | 5.8426 | 37.1052 | 0.46836 | 1.3201 | 0.096385 | 0.79518 | 0.4684 | 1.3203
NANA | Nanango | WB | 66 | 1.81 | 206.9135 | 1.159 | 44.1637 | 13.3911 | 18.8971 | 19.107 | 60.5271 | 13.3925 | 18.9033
NAND | Nandi | SW | 11 | 1.947 | 37.0944 | 2.1785 | 13.8355 | 1.0546 | 3.4331 | 0.10091 | 2.5038 | 1.0546 | 3.4332
NAND | Nandi | SW | 33 | 1.7504 | 100.049 | 1.3047 | 24.8577 | 8.5831 | 8.3634 | 10.035 | 23.0942 | 8.5831 | 8.3644
NEBO | Nebo H011 (TF3) | MK | 11 | 3.2547 | 62.0096 | 1.8319 | 11.6342 | 0.1182 | 2.1458 | 3.2633e-08 | 7.161 | 0.11825 | 2.1464
NEBO | Nebo H011 (TF4) | MK | 11 | 3.2582 | 62.0762 | 1.8326 | 11.6389 | 0.11772 | 2.1435 | 3.2633e-08 | 7.161 | 0.11778 | 2.1441
NESM | Neil Smith (TF1) | NQ | 11 | 19.368 | 369.0091 | 21.0307 | 133.5631 | 0.038202 | 0.35985 | 0.013965 | 0.27683 | 0.037813 | 0.35951
NESM | Neil Smith (TF2) | NQ | 11 | 19.368 | 369.0091 | 21.0307 | 133.5631 | 0.038202 | 0.35985 | 0.013965 | 0.27683 | 0.037813 | 0.35951
NESM | Neil Smith (TF1) | NQ | 66 | 8.3075 | 949.6758 | 6.17 | 235.1101 | 2.0175 | 4.6427 | 2.9463 | 9.9585 | 2.003 | 4.6333
NESM | Neil Smith (TF2) | NQ | 66 | 10.0357 | 1147.2368 | 8.7391 | 333.0059 | 1.2719 | 3.9925 | 1.4321 | 5.9179 | 1.2575 | 3.9776
NEWL | Newlands T069 | MK | 66 | 4.8139 | 550.2999 | 6.0167 | 229.2665 | 2.4377 | 8.3728 | 0.28884 | 3.5439 | 2.4391 | 8.3699
NOCL | North Cloncurry (TF1) | NQ - MI | 11 | 4.7809 | 91.0882 | 5.6737 | 36.0327 | 0.2355 | 1.4421 | 0.038558 | 0.76994 | 0.23276 | 1.4469
NOCL | North Cloncurry (TF2) | NQ - MI | 11 | 4.7809 | 91.0882 | 5.6737 | 36.0327 | 0.2355 | 1.4421 | 0.038558 | 0.76994 | 0.23276 | 1.4469
NOCL | North Cloncurry | NQ - MI | 66 | 1.6623 | 190.0236 | 1.553 | 59.176 | 7.09 | 24.1985 | 7.892 | 29.3653 | 6.9913 | 24.3698
NOMA | North Mackay (TF1) | MK | 11 | 10.4557 | 199.2084 | 12.7638 | 81.0613 | 0.060766 | 0.66599 | 0.015248 | 0.30496 | 0.059409 | 0.66709
NOMA | North Mackay (TF2) | MK | 11 | 10.4557 | 199.2084 | 12.7638 | 81.0613 | 0.060766 | 0.66599 | 0.015248 | 0.30496 | 0.059409 | 0.66709
NOMA | North Mackay (TF1) | MK | 33 | 6.4052 | 366.1071 | 7.8214 | 149.0183 | 0.40966 | 3.2493 | 0.22408 | 1.472 | 0.39745 | 3.2592
NOMA | North Mackay (TF2) | MK | 33 | 6.4052 | 366.1071 | 7.8214 | 149.0183 | 0.40966 | 3.2493 | 0.22408 | 1.472 | 0.39745 | 3.2592
NORM | Normanton | FN | 22 | 1.2491 | 47.5973 | 1.7985 | 22.8445 | 3.3173 | 14.6685 | 0.0070855 | 1.9736 | 2.9565 | 14.7999
NORM | Normanton | FN | 6.6 | 3.6537 | 41.767 | 0 | 0 | 0.30605 | 1.5118 | 329999990.0687 | 69.656 | 0.27343 | 1.5232
NORM | Normanton | FN | 66 | 0.43846 | 50.1224 | 0.61504 | 23.4361 | 32.041 | 120.1892 | 0.24539 | 24.3569 | 29.6591 | 121.2466
NORW | Norwin (TF1) | SW | 11 | 1.6078 | 30.6322 | 1.977 | 12.5555 | 1.7279 | 4.0006 | 0.10178 | 2.0356 | 1.7162 | 3.9942
NORW | Norwin (TF3) | SW | 11 | 1.6023 | 30.5279 | 1.9685 | 12.5018 | 1.7287 | 4.0164 | 0.10257 | 2.0515 | 1.717 | 4.0101
NORW | Norwin | SW | 33 | 0.91566 | 52.3368 | 0.59615 | 11.3583 | 14.6354 | 17.6845 | 21.6329 | 57.5417 | 14.5301 | 17.6272
NOST | North Street | SW | 11 | 9.8074 | 186.8555 | 2.2331 | 14.1819 | 0.097047 | 0.70625 | 9.0204 | 0.40809 | 0.097044 | 0.70579
NOST | North Street | SW | 33 | 7.5702 | 432.6941 | 1.1083 | 21.1165 | 0.68978 | 2.6835 | 55.2246 | -0.99167 | 0.68976 | 2.6793
OAKE | Oakey | SW | 11 | 14.9154 | 284.1766 | 17.0515 | 108.2918 | 0.024477 | 0.46885 | 0.014889 | 0.29151 | 0.023289 | 0.46896
OAKE | Oakey | SW | 33 | 13.1433 | 751.2377 | 1.4425 | 27.4829 | 0.086295 | 1.596 | 32.4143 | 25.8635 | 0.0756 | 1.597
OAKY | Oakey T189 (TF1) | SW | 110 | 10.1036 | 1924.9951 | 10.3442 | 656.9465 | 0.6564 | 6.8899 | 0.79739 | 6.3653 | 0.65386 | 6.9107
OAKY | Oakey T189 (TF2) | SW | 110 | 10.1035 | 1924.9829 | 10.3426 | 656.8416 | 0.65644 | 6.8899 | 0.79934 | 6.3682 | 0.6539 | 6.9107
OAKY | Oakey T189 (TF1) | SW | 33 | 13.1433 | 751.2377 | 1.4425 | 27.4829 | 0.086295 | 1.596 | 32.4143 | 25.8635 | 0.0756 | 1.597
OAKY | Oakey T189 (TF2) | SW | 33 | 13.1433 | 751.2377 | 1.4425 | 27.4829 | 0.086295 | 1.596 | 32.4143 | 25.8635 | 0.0756 | 1.597
OONN | Oonoonba | NQ | 11 | 15.7057 | 299.2346 | 16.9258 | 107.4933 | 0.043365 | 0.44418 | 0.011183 | 0.35103 | 0.042974 | 0.44381
OONN | Oonoonba | NQ | 66 | 11.8543 | 1355.1285 | 9.5279 | 363.0635 | 1.1586 | 3.3532 | 1.794 | 5.9044 | 1.1445 | 3.34
OWAN | Owanyilla | WB | 11 | 7.1344 | 135.9286 | 8.1389 | 51.6893 | 0.13707 | 0.97226 | 0.037607 | 0.61461 | 0.13605 | 0.97258
OWAN | Owanyilla | WB | 66 | 3.1451 | 359.5324 | 2.2163 | 84.4506 | 3.5805 | 12.8752 | 5.7182 | 29.5771 | 3.544 | 12.8869
PACO | Pacific Coal | WB | 66 | 12.0674 | 1379.4886 | 10.5437 | 401.7698 | 0.92958 | 3.3473 | 1.1153 | 4.8497 | 0.93103 | 3.3535
PAJI | Pajingo | NQ | 11 | 3.2644 | 62.1945 | 3.9482 | 25.0745 | 0.7879 | 2.0295 | 0.059052 | 1.0295 | 0.78623 | 2.0291
PAJI | Pajingo | NQ | 66 | 0.95719 | 109.4215 | 0.68295 | 26.0239 | 26.2384 | 36.0013 | 30.7727 | 93.655 | 26.1784 | 35.9861
PAMP | Pampas | SW | 11 | 3.277 | 62.4357 | 4.1797 | 26.5446 | 0.45741 | 2.0885 | 0.038624 | 0.77248 | 0.44571 | 2.0821
PAMP | Pampas | SW | 33 | 1.6911 | 96.6566 | 0.47325 | 9.0165 | 3.7691 | 11.8443 | 0.0057617 | 109.49 | 3.6638 | 11.787
PAND | Pandoin | CA | 22 | 5.2991 | 201.922 | 5.6717 | 72.0403 | 0.19821 | 2.6302 | 0.1192 | 2.1123 | 0.19845 | 2.6326
PAND | Pandoin | CA | 66 | 8.893 | 1016.6079 | 9.8951 | 377.0549 | 0.71107 | 4.6612 | 0.49722 | 3.2229 | 0.71327 | 4.6827
PAPS | Pajingo Pumps | NQ | 66 | 1.9146 | 218.8737 | 1.5616 | 59.504 | 10.1046 | 19.8468 | 8.9369 | 35.9902 | 10.0445 | 19.8316
PARK | Parkhurst | CA | 11 | 18.2543 | 347.7913 | 20.2635 | 128.6906 | 0.035572 | 0.38119 | 0.013411 | 0.26822 | 0.035633 | 0.38179
PARK | Parkhurst | CA | 66 | 10.1171 | 1156.5448 | 10.2056 | 388.8852 | 0.79779 | 4.0671 | 1.0627 | 3.8799 | 0.80001 | 4.0885
PEAR | Peter Arlett | NQ | 11 | 18.5182 | 352.8189 | 20.3468 | 129.2196 | 0.030918 | 0.37718 | 0.011349 | 0.27712 | 0.028964 | 0.37698
PEAR | Peter Arlett | NQ | 66 | 11.9201 | 1362.6456 | 9.0468 | 344.7275 | 0.74264 | 3.4491 | 1.4471 | 6.7562 | 0.72683 | 3.4387
PECR | Perseverance Creek (TF2) | SW | 11 | 2.9067 | 55.3805 | 3.8372 | 24.3695 | 0.66855 | 2.3104 | 1.2043 | 0.2185 | 0.66855 | 2.31
PECR | Perseverance Creek | SW | 33 | 2.0259 | 115.7944 | 0.82596 | 15.7366 | 5.3566 | 8.8593 | 9.0164 | 55.8624 | 5.3567 | 8.8562
PERA | Peranga (TF1) | SW | 11 | 1.6472 | 31.3843 | 2.0219 | 12.8405 | 1.6006 | 3.9383 | 0.098324 | 1.9665 | 1.5994 | 3.9384
PERA | Peranga (TF3) | SW | 11 | 1.6472 | 31.3843 | 2.0219 | 12.8405 | 1.6006 | 3.9383 | 0.098324 | 1.9665 | 1.5994 | 3.9384
PERA | Peranga | SW | 33 | 0.94165 | 53.8224 | 0.41787 | 7.9615 | 13.5201 | 17.7462 | 55.2362 | 90.7536 | 13.5094 | 17.7471
PIAL | Pialba | WB | 11 | 5.3439 | 101.8158 | 5.7976 | 36.8197 | 0.11394 | 1.3064 | 0.046512 | 0.99652 | 0.1125 | 1.3069
PIAL | Pialba | WB | 66 | 3.6829 | 421.0077 | 2.5286 | 96.351 | 2.4273 | 11.156 | 5.9876 | 26.291 | 2.3755 | 11.1718
PINN | Pinnacle | MK | 11 | 4.9901 | 95.0739 | 5.759 | 36.5747 | 0.33459 | 1.3608 | 0.063026 | 0.84464 | 0.3344 | 1.3632
PINN | Pinnacle | MK | 66 | 1.9997 | 228.5959 | 1.2907 | 49.1838 | 9.7783 | 18.563 | 15.4677 | 53.8072 | 9.771 | 18.6514
PIRR | Pirrinuan (TF1) | SW | 11 | 2.236 | 42.6009 | 2.6018 | 16.524 | 0.84796 | 3.01 | 0.023816 | 1.8551 | 0.84796 | 3.0101
PIRR | Pirrinuan (TF2) | SW | 11 | 1.8584 | 35.4073 | 2.1049 | 13.3681 | 0.92509 | 3.647 | 5.6654e-10 | 2.4964 | 0.92509 | 3.6471
PIRR | Pirrinuan | SW | 33 | 1.7196 | 98.2888 | 1.0948 | 20.8585 | 6.2969 | 10.4477 | 9.2821 | 32.2491 | 6.2969 | 10.4487
PIVA | Pioneer Valley T141 | MK | 66 | 8.8346 | 1009.9298 | 10.9763 | 418.252 | 0.52981 | 4.7196 | 0.2082 | 1.9229 | 0.50659 | 4.7587
PLAN | Planella (TF1) | MK | 11 | 5.6918 | 108.4433 | 7.3148 | 46.4555 | 0.26843 | 1.1988 | 0.020732 | 0.41482 | 0.26708 | 1.1999
PLAN | Planella (TF2) | MK | 11 | 5.6918 | 108.4433 | 7.3148 | 46.4555 | 0.26843 | 1.1988 | 0.020732 | 0.41482 | 0.26708 | 1.1999
PLAN | Planella | MK | 33 | 2.8349 | 162.0337 | 2.3263 | 44.3213 | 2.2293 | 7.0558 | 3.1218 | 11.853 | 2.2171 | 7.0658
PLEY | Pleystowe | MK | 11 | 6.5809 | 125.3826 | 7.8358 | 49.7637 | 0.2597 | 1.0303 | 0.027955 | 0.55909 | 0.25798 | 1.0318
PLEY | Pleystowe | MK | 33 | 4.4386 | 253.6977 | 2.6304 | 50.1167 | 2.0857 | 4.2411 | 3.9164 | 14.0287 | 2.0702 | 4.2545
POCU | Port Curtis | CA | 11 | 25.3769 | 483.4949 | 2.183 | 13.8638 | 0.021058 | 0.27455 | 9.5326 | 0.17789 | 0.021047 | 0.27477
POCU | Port Curtis | CA | 66 | 11.9336 | 1364.1959 | 11.915 | 454.0239 | 0.48483 | 3.4796 | 0.65669 | 3.4621 | 0.48444 | 3.4878
POVE | Point Vernon | WB | 11 | 12.4033 | 236.3149 | 16.0109 | 101.6831 | 0.098983 | 0.55626 | 0.0075568 | 0.18189 | 0.097544 | 0.5567
POVE | Point Vernon | WB | 66 | 3.0308 | 346.4654 | 1.9814 | 75.5 | 3.2913 | 13.4774 | 8.1345 | 34.8702 | 3.2396 | 13.4932
POZI | Pozieres | SW | 11 | 2.3542 | 44.8541 | 3.0501 | 19.3707 | 1.1177 | 2.7565 | 0.049101 | 0.98195 | 1.1166 | 2.7566
POZI | Pozieres | SW | 33 | 1.1269 | 64.4083 | 0.57677 | 10.989 | 9.617 | 15.9706 | 65.0341 | 37.5559 | 9.6079 | 15.9719
PROS | Proserpine T039 | MK | 66 | 5.704 | 652.0526 | 7.3922 | 281.6805 | 2.0985 | 7.057 | 0.31657 | 2.4198 | 2.0626 | 6.9703
PROT | Proston | WB | 11 | 1.9568 | 37.2812 | 2.3331 | 14.8169 | 1.3638 | 3.2996 | 0.2622 | 1.872 | 1.3637 | 3.2998
PROT | Proston | WB | 66 | 0.64571 | 73.8147 | 0.5315 | 20.2527 | 39.658 | 51.3957 | 49.5153 | 95.6594 | 39.6541 | 51.4012
PURR | Purrawunda (TF1) | SW | 11 | 3.0907 | 58.8866 | 3.9915 | 25.3493 | 0.72431 | 2.1429 | 0.037734 | 0.75469 | 0.7243 | 2.1424
PURR | Purrawunda (TF2) | SW | 11 | 3.0907 | 58.8866 | 3.9915 | 25.3493 | 0.72431 | 2.1429 | 0.037734 | 0.75469 | 0.7243 | 2.1424
PURR | Purrawunda | SW | 33 | 1.5047 | 86.0077 | 0.61536 | 11.7242 | 6.1791 | 12.4939 | 64.42 | 42.5466 | 6.1791 | 12.4897
QUIL | Quilpie (TF1) | SW | 11 | 0.75546 | 14.3934 | 1.0214 | 6.4866 | 4.0373 | 8.32 | 0.10891 | 2.1782 | 4.033 | 8.3217
QUIL | Quilpie (TF2) | SW | 11 | 0.75665 | 14.4161 | 1.0236 | 6.5006 | 4.0365 | 8.3042 | 0.10812 | 2.1624 | 4.0322 | 8.3059
QUIL | Quilpie | SW | 66 | 0.15971 | 18.2572 | 0.077629 | 2.9581 | 141.423 | 221.1051 | 387.3221 | 1032.6098 | 141.2674 | 221.1659
RAGL | Raglan | CA | 22 | 2.1037 | 80.1623 | 2.5607 | 32.5247 | 2.5906 | 6.1182 | 0.24239 | 3.2122 | 2.5909 | 6.1206
RAGL | Raglan | CA | 66 | 1.247 | 142.5543 | 0.84668 | 32.2627 | 21.1341 | 26.1538 | 31.4465 | 76.6692 | 21.1363 | 26.175
RASM | Rasmussen | NQ | 11 | 14.7733 | 281.4688 | 16.214 | 102.973 | 0.042828 | 0.47253 | 0.011128 | 0.34917 | 0.042446 | 0.47222
RASM | Rasmussen | NQ | 66 | 9.1723 | 1048.5328 | 6.5225 | 248.5416 | 1.1412 | 4.4409 | 2.2382 | 9.9497 | 1.1274 | 4.4298
RAVE | Ravenshoe | FN | 22 | 1.9667 | 74.9411 | 2.3638 | 30.0243 | 1.9137 | 6.8524 | 0.00054415 | 3.6254 | 1.9069 | 6.868
RAVE | Ravenshoe | FN | 66 | 1.2076 | 138.0424 | 0.77251 | 29.4364 | 15.3583 | 31.1851 | 23.3093 | 91.3486 | 15.2972 | 31.3253
RAVN | Ravenswood | NQ | 11 | 2.0722 | 39.4815 | 2.1597 | 13.7162 | 0.57665 | 3.3508 | 0.32962 | 2.9304 | 0.57469 | 3.35
RAVN | Ravenswood | NQ | 66 | 2.4081 | 275.2801 | 1.5994 | 60.9465 | 8.8933 | 15.1361 | 12.7834 | 42.5758 | 8.8225 | 15.1073
RICH | Richmond | NQ | 33 | 0.74988 | 42.8614 | 0.87468 | 16.6648 | 8.3816 | 29.1024 | 0.58785 | 12.6622 | 8.3753 | 29.3168
RICH | Richmond | NQ | 66 | 0.57969 | 66.2679 | 0.63145 | 24.0614 | 31.0378 | 71.9434 | 4.406 | 46.7521 | 31.0125 | 72.8011
ROEA | Roma East | SW | 11 | 5.1307 | 97.7523 | 6.1145 | 38.8321 | 0.24705 | 1.3391 | 0.035372 | 0.70743 | 0.24273 | 1.3408
ROEA | Roma East | SW | 33 | 3.4957 | 199.8079 | 3.2016 | 60.9996 | 1.9051 | 5.6849 | 2.2023 | 7.3234 | 1.8662 | 5.7001
ROGL | Rockhampton T023 (TF2) | CA | 11 | 17.3828 | 331.1877 | 18.8807 | 119.9088 | 0.025352 | 0.40109 | 0.013675 | 0.30539 | 0.025401 | 0.40167
ROGL | Rockhampton T023 (TF4) | CA | 11 | 17.3828 | 331.1877 | 18.8807 | 119.9088 | 0.025352 | 0.40109 | 0.013675 | 0.30539 | 0.025401 | 0.40167
ROGL | Rockhampton T023 | CA | 66 | 12.0775 | 1380.6388 | 14.3103 | 545.2954 | 0.42039 | 3.445 | 0.28545 | 1.8038 | 0.42215 | 3.4657
ROLE | Rolleston | CA | 132 | 1.3538 | 309.5228 | 1.5473 | 117.9217 | 13.8823 | 60.4377 | 1.4443 | 39.3088 | 13.8767 | 60.3876
ROLE | Rolleston (TF 1) | CA | 22 | 4.506 | 171.7025 | 5.0128 | 63.671 | 0.38562 | 3.0811 | 0.849 | 2.055 | 0.38546 | 3.0797
ROLE | Rolleston (TF 2) | CA | 22 | 4.506 | 171.7025 | 5.0128 | 63.671 | 0.38562 | 3.0811 | 0.849 | 2.055 | 0.38546 | 3.0797
ROLE | Rolleston | CA | 66 | 2.1233 | 242.7275 | 2.7087 | 103.2145 | 3.617 | 19.4354 | 0.15499 | 7.0434 | 3.6156 | 19.4229
ROLL | Rollingstone | NQ | 11 | 1.7552 | 33.4414 | 1.8584 | 11.8022 | 0.76049 | 3.9182 | 0.24091 | 3.3399 | 0.75938 | 3.9183
ROLL | Rollingstone | NQ | 66 | 1.5018 | 171.6782 | 1.0411 | 39.671 | 18.7051 | 20.8211 | 24.907 | 62.303 | 18.6651 | 20.8238
ROMA | Roma T083 (TF1) | SW | 132 | 3.0917 | 706.8516 | 3.7611 | 286.6359 | 5.2073 | 26.6116 | 0.61841 | 12.6625 | 4.7803 | 26.7488
ROMA | Roma T083 (TF2) | SW | 132 | 3.0917 | 706.8516 | 3.7611 | 286.6359 | 5.2073 | 26.6116 | 0.61841 | 12.6625 | 4.7803 | 26.7488
ROMA | Roma T083 | SW | 33 | 5.7037 | 326.0125 | 7.2634 | 138.3861 | 0.3855 | 3.6543 | 0.023141 | 1.3053 | 0.35881 | 3.6629
ROMA | Roma T083 | SW | 66 | 2.931 | 335.0638 | 3.7559 | 143.1202 | 1.4853 | 14.2238 | 0.33143 | 4.8461 | 1.3785 | 14.2581
ROPL | Ross Plains (TF1) | NQ | 11 | 13.368 | 254.6948 | 14.3088 | 90.8729 | 0.043873 | 0.52074 | 0.020815 | 0.41961 | 0.043489 | 0.52033
ROPL | Ross Plains (TF2) | NQ | 11 | 13.368 | 254.6948 | 14.3088 | 90.8729 | 0.043873 | 0.52074 | 0.020815 | 0.41961 | 0.043489 | 0.52033
ROPL | Ross Plains | NQ | 66 | 11.2247 | 1283.1576 | 8.3256 | 317.2498 | 0.83007 | 3.6408 | 1.6845 | 7.4648 | 0.81625 | 3.6261
ROSE | ROSE Rosella (TF1) | MK | 11 | 5.8471 | 111.4023 | 6.5307 | 41.4757 | 0.19265 | 1.1804 | 0.041154 | 0.82247 | 0.19235 | 1.1816
ROSE | ROSE Rosella (TF2) | MK | 11 | 5.8471 | 111.4023 | 6.5307 | 41.4757 | 0.19265 | 1.1804 | 0.041154 | 0.82247 | 0.19235 | 1.1816
ROSE | ROSE Rosella (TF1) | MK | 33 | 5.9972 | 342.7881 | 3.8204 | 72.7877 | 1.3635 | 3.2217 | 2.2858 | 9.2428 | 1.3608 | 3.2323
ROSE | ROSE Rosella (TF2) | MK | 33 | 5.9972 | 342.7881 | 3.8204 | 72.7877 | 1.3635 | 3.2217 | 2.2858 | 9.2428 | 1.3608 | 3.2323
ROSO | Rockhampton South (TF1) | CA | 11 | 18.0911 | 344.6823 | 20.0776 | 127.5097 | 0.0374 | 0.3845 | 0.0141 | 0.2709 | 0.0375 | 0.3851
ROSO | Rockhampton South (TF2) | CA | 11 | 18.0911 | 344.6823 | 20.0776 | 127.5097 | 0.0374 | 0.3845 | 0.0141 | 0.2709 | 0.0375 | 0.3851
ROSO | Rockhampton South | CA | 66 | 10.0429 | 1148.0522 | 9.9805 | 380.3066 | 0.8393 | 4.0901 | 0.9919 | 4.1158 | 0.8413 | 4.1117
ROST | Rocky Street | WB | 11 | 11.2825 | 214.9606 | 12.5896 | 79.9547 | 0.055659 | 0.61838 | 0.017965 | 0.42476 | 0.054643 | 0.6187
ROST | Rocky Street | WB | 66 | 5.9189 | 676.6222 | 5.8843 | 224.2216 | 1.357 | 6.9702 | 1.3948 | 7.0537 | 1.3204 | 6.9819
ROWE | Roma West (TF1) | SW | 11 | 3.2125 | 61.2058 | 3.7503 | 23.8178 | 0.5557 | 2.1026 | 0.1127 | 1.247 | 0.5514 | 2.1042
ROWE | Roma West (TF2) | SW | 11 | 3.2125 | 61.2058 | 3.7503 | 23.8178 | 0.5557 | 2.1026 | 0.1127 | 1.247 | 0.5514 | 2.1042
ROWE | Roma West | SW | 33 | 2.4171 | 138.1578 | 1.8786 | 35.7913 | 3.9872 | 7.6999 | 5.2133 | 15.3648 | 3.9483 | 7.7151
RYWU | Rywung (Regulated) | SW | 33 | 1.038 | 59.3325 | 0.79788 | 15.2017 | 16.5137 | 11.6537 | 19.2796 | 35.7571 | 16.4886 | 11.6615
RYWU | Rywung (Unregulated) | SW | 33 | 1.0097 | 57.714 | 0.77692 | 14.8022 | 16.5586 | 12.5522 | 19.3265 | 36.6588 | 16.5335 | 12.56
SAGE | St. George (TF1) | SW | 33 | 0.75319 | 43.0508 | 1.0795 | 20.5671 | 10.0247 | 25.9584 | 0.14883 | 2.7149 | 9.9858 | 25.9735
SAGE | St. George (TF2) | SW | 33 | 0.75319 | 43.0508 | 1.0795 | 20.5671 | 10.0247 | 25.9584 | 0.14883 | 2.7149 | 9.9858 | 25.9735
SAGE | St. George | SW | 66 | 0.41214 | 47.1143 | 0.57393 | 21.8697 | 39.599 | 93.682 | 0.97351 | 16.5522 | 39.4434 | 93.7426
SAGT | St. George Town (TF1) | SW | 11 | 1.3115 | 24.9866 | 1.6779 | 10.6564 | 1.6792 | 5.0556 | 0.094622 | 1.8924 | 1.6749 | 5.0573
SAGT | St. George Town (TF2) | SW | 11 | 1.2765 | 24.3203 | 1.6205 | 10.2919 | 1.6867 | 5.2067 | 0.10218 | 2.0436 | 1.6824 | 5.2084
SAGT | St. George Town (TF3) | SW | 11 | 1.3115 | 24.9866 | 1.6779 | 10.6564 | 1.6792 | 5.0556 | 0.094622 | 1.8924 | 1.6749 | 5.0573
SAGT | St. George Town | SW | 33 | 0.65825 | 37.6238 | 0.81416 | 15.5118 | 14.261 | 28.4685 | 5.3416 | 12.4761 | 14.2221 | 28.4836
SARI | Sarina (TF1) | MK | 11 | 11.1063 | 211.6031 | 11.034 | 70.0756 | 0.122 | 0.6174 | 0.0279 | 0.5658 | 0.12 | 0.6982
SARI | Sarina (TF2) | MK | 11 | 11.1063 | 211.6031 | 11.034 | 70.0756 | 0.122 | 0.6174 | 0.0279 | 0.5658 | 0.12 | 0.6982
SARI | Sarina | MK | 33 | 5.3608 | 306.413 | 3.1193 | 59.43 | 1.368 | 3.6659 | 3.0209 | 11.8279 | 1.4265 | 3.8257
SARS | Sarsfield | NQ | 66 | 2.1157 | 241.852 | 1.4 | 53.3472 | 10.6839 | 16.8868 | 15.3067 | 48.6893 | 10.6134 | 16.8582
SAUN | Saunders | NQ | 11 | 3.7613 | 71.6623 | 3.9171 | 24.8768 | 0.22282 | 1.8492 | 0.10015 | 1.6416 | 0.22171 | 1.8493
SAUN | Saunders | NQ | 66 | 4.8417 | 553.4847 | 3.5171 | 134.021 | 4.4161 | 7.4745 | 5.7902 | 17.8189 | 4.3761 | 7.4773
SHUT | Shutehaven | MK | 22 | 3.068 | 116.9058 | 3.8136 | 48.4393 | 1.3075 | 4.3712 | 0.00839 | 1.9507 | 1.2994 | 4.3576
SHUT | Shutehaven | MK | 66 | 1.7199 | 196.6145 | 1.1736 | 44.7186 | 11.0127 | 21.7911 | 15.4176 | 57.1933 | 10.9402 | 21.6684
SKIA | Skid 'A' (Mt Bassett) | MK | 11 | 3.3517 | 63.8581 | 3.5074 | 22.2752 | 0.22395 | 2.0745 | 0.0024208 | 1.8156 | 0.22364 | 2.0753
SKIA | Skid 'A' (Mt Bassett) | MK | 33 | 7.9803 | 456.138 | 6.4348 | 122.5991 | 0.92616 | 2.4604 | 1.2731 | 4.3428 | 0.9234 | 2.4674
SKIE | Skid 'E' (Chinchilla) | SW | 11 | 3.2267 | 61.4767 | 3.4146 | 21.6858 | 0.22482 | 2.1557 | 0.0012104 | 1.8156 | 0.22203 | 2.1566
SKIE | Skid 'E' (Chinchilla) | SW | 33 | 6.3091 | 360.614 | 5.9895 | 114.1151 | 0.93402 | 3.1916 | 0.50057 | 3.853 | 0.9089 | 3.1994
SKIF | Skid 'F' (Broxburn) | SW | 33 | 2.9267 | 167.2826 | 1.7458 | 33.2627 | 3.5077 | 6.2656 | 9.1178 | 19.7983 | 3.5074 | 6.2661
SKIF | Skid 'F' (Broxburn) | SW | 11 | 3.9231 | 74.7443 | 4.6376 | 29.4529 | 0.492 | 1.7165 | 0.1023 | 0.9688 | 0.492 | 1.7166
SKIJ | Skid J | MK | 11 | 6.0009 | 114.3319 | 6.2747 | 39.8495 | 0.081736 | 1.1645 | 0.057791 | 1.0077 | 0.08072 | 1.1648
SKIJ | Skid J | MK | 66 | 7.3633 | 841.7372 | 9.2058 | 350.7878 | 0.86201 | 5.6426 | 0.12419 | 2.2592 | 0.82545 | 5.6544
SOBL | South Blackwater | CA | 22 | 1.8318 | 69.8025 | 1.9759 | 25.0968 | 1.1291 | 7.5552 | 0.55518 | 5.9556 | 1.1302 | 7.5498
SOBL | South Blackwater (ex 6014) | CA | 66 | 2.7446 | 313.7528 | 1.8753 | 71.457 | 5.1653 | 14.3972 | 9.9176 | 35.2898 | 5.175 | 14.348
SOBL | South Blackwater (ex 6061) | CA | 66 | 2.7446 | 313.7528 | 1.8753 | 71.457 | 5.1653 | 14.3972 | 9.9176 | 35.2898 | 5.175 | 14.348
SOBU | South Bundaberg | WB | 11 | 10.217 | 194.6603 | 11.5315 | 73.2351 | 0.084993 | 0.6793 | 0.023248 | 0.44753 | 0.08448 | 0.68147
SOBU | South Bundaberg | WB | 66 | 4.8603 | 555.6061 | 4.0538 | 154.4689 | 2.2228 | 8.3437 | 3.4679 | 13.2522 | 2.2044 | 8.4219
SOKO | South Kolan | WB | 11 | 7.8214 | 149.0182 | 8.607 | 54.6616 | 0.0919 | 0.8896 | 0.0422 | 0.6454 | 0.0914 | 0.8911
SOKO | South Kolan | WB | 66 | 4.6789 | 534.8727 | 3.8556 | 146.9182 | 1.7892 | 8.7893 | 3.0919 | 14.3163 | 1.7691 | 8.8438
SOMA | South Mackay (TF1) | MK | 11 | 9.6556 | 183.9647 | 11.3476 | 72.0671 | 0.1174 | 0.7146 | 0.0201 | 0.4014 | 0.1162 | 0.7153
SOMA | South Mackay (TF2) | MK | 11 | 9.6556 | 183.9647 | 11.3476 | 72.0671 | 0.1174 | 0.7146 | 0.0201 | 0.4014 | 0.1162 | 0.7153
SOMA | South Mackay | MK | 33 | 6.6373 | 379.3752 | 4.6641 | 88.8627 | 0.91783 | 3.0247 | 1.7927 | 6.9436 | 0.91569 | 3.0316
SOTO | South Toowoomba T043 (TF1) | SW | 110 | 16.8878 | 3217.5509 | 14.7871 | 939.1046 | 0.39924 | 4.1207 | 0.72611 | 5.9066 | 0.39896 | 4.0747
SOTO | South Toowoomba T043 (TF2) | SW | 110 | 16.8878 | 3217.5509 | 14.7871 | 939.1046 | 0.39924 | 4.1207 | 0.72611 | 5.9066 | 0.39896 | 4.0747
SOTO | South Toowoomba T043 | SW | 11 | 13.006 | 247.7977 | 2.281 | 14.4866 | 0.028772 | 0.53679 | 9.0197 | 0.39392 | 0.028769 | 0.53633
SOTO | South Toowoomba T043 | SW | 33 | 16.279 | 930.4683 | 1.1584 | 22.07 | 0.081681 | 1.2859 | 54.1128 | -0.38874 | 0.081656 | 1.2817
SOWC | South Walker Switching | MK | 66 | 1.9547 | 223.4532 | 1.2886 | 49.1034 | 4.6547 | 20.9576 | 13.3629 | 53.1089 | 4.6552 | 20.9724
STAM | Stamford | NQ | 33 | 0.16255 | 9.2908 | 0.15766 | 3.0038 | 15.0059 | 138.9079 | 8.9372 | 126.0276 | 14.9996 | 139.1223
STAM | Stamford | NQ | 66 | 0.79751 | 91.1673 | 0.56313 | 21.458 | 24.2747 | 51.5212 | 33.8766 | 107.9312 | 24.2494 | 52.3788
STAN | Stanthorpe | SW | 110 | 1.2674 | 241.4771 | 1.7875 | 113.5242 | 29.5584 | 46.6641 | 0.6184 | 7.8382 | 29.4747 | 46.6754
STAN | Stanthorpe | SW | 33 | 2.7563 | 157.5418 | 1.0101 | 19.2452 | 3.3081 | 6.8664 | 54.0557 | 0.7424 | 3.299 | 6.8676
STTO | Stanthorpe Town | SW | 11 | 4.4437 | 84.6643 | 5.626 | 35.7301 | 0.4961 | 1.4957 | 0.029927 | 0.59855 | 0.49509 | 1.4958
STTO | Stanthorpe Town | SW | 33 | 2.3087 | 131.9597 | 0.93083 | 17.7347 | 4.1956 | 8.0743 | 55.7221 | 5.553 | 4.1864 | 8.0756
STUA | Stuart | NQ | 11 | 18.4596 | 351.7022 | 19.5666 | 124.2649 | 0.020547 | 0.37917 | 0.010101 | 0.31598 | 0.020149 | 0.37872
STUA | Stuart | NQ | 66 | 18.2406 | 2085.1809 | 20.0928 | 765.6376 | 0.37606 | 2.2748 | 0.25563 | 1.6689 | 0.36174 | 2.2587
T076 | Barcaldine Power Station | CA | 132 | 1.8046 | 412.5812 | 1.6277 | 124.0439 | 6.1882 | 46.6074 | 5.1732 | 53.014 | 7.6626 | 55.9233
TANB | Tanby | CA | 22 | 4.3919 | 167.3553 | 5.1811 | 65.8094 | 0.72492 | 3.0988 | 0.070146 | 1.7491 | 0.72516 | 3.1012
TANB | Tanby | CA | 66 | 3.1057 | 355.0261 | 2.0339 | 77.5017 | 5.8929 | 12.1478 | 10.1549 | 33.5093 | 5.8951 | 12.1692
TARA | Tara (TF1) | SW | 11 | 0.54353 | 10.3557 | 0.63206 | 4.0141 | 4.9364 | 11.8798 | 0.38978 | 7.7956 | 4.9364 | 11.8799
TARA | Tara (TF2) | SW | 11 | 0.70898 | 13.5079 | 0.87765 | 5.5738 | 4.7739 | 8.6301 | 0.22729 | 4.5459 | 4.7739 | 8.6302
TARA | Tara | SW | 33 | 0.38136 | 21.7978 | 0.28121 | 5.3578 | 40.9198 | 36.7577 | 49.5172 | 107.6093 | 40.9197 | 36.7587
TARE | Tara Regulator (Regulated) | SW | 33 | 0.42619 | 24.3599 | 0.31694 | 6.0385 | 36.108 | 33.4486 | 43.0842 | 94.71 | 36.108 | 33.4495
TARE | Tara Regulator (Unregulated) | SW | 33 | 0.42619 | 24.3599 | 0.31694 | 6.0385 | 36.108 | 33.4486 | 43.0842 | 94.71 | 36.108 | 33.4495
THAL | Thalanga | NQ | 11 | 2.9509 | 56.2226 | 3.1802 | 20.1971 | 0.40022 | 2.416 | 0.084051 | 1.765 | 0.39404 | 2.4173
THAL | Thalanga | NQ | 66 | 1.6939 | 193.6338 | 1.3733 | 52.3308 | 11.3196 | 22.9595 | 12.0219 | 39.8706 | 11.097 | 23.0063
THEO | Theodore (TF1) | CA | 22 | 2.526 | 96.2547 | 3.1933 | 40.5602 | 0.96708 | 5.4484 | 0.16431 | 2.0553 | 0.96764 | 5.4592
THEO | Theodore (TF2) | CA | 22 | 2.526 | 96.2547 | 3.1933 | 40.5602 | 0.96708 | 5.4484 | 0.16431 | 2.0553 | 0.96764 | 5.4592
THEO | Theodore (TF3) | CA | 22 | 2.526 | 96.2547 | 3.1933 | 40.5602 | 0.96708 | 5.4484 | 0.16431 | 2.0553 | 0.96764 | 5.4592
THEO | Theodore | CA | 66 | 1.3398 | 153.1622 | 0.80287 | 30.5933 | 7.223 | 30.4529 | 20.6112 | 91.7117 | 7.228 | 30.551
TIDH | Tinaroo Dam Hydro | FN | 22 | 0.85075 | 32.4179 | 0.99938 | 12.6938 | 12.8861 | 10.2202 | 2.0457 | 11.0321 | 12.8794 | 10.2358
TIER | Tieri | CA | 22 | 3.269 | 124.5645 | 3.5728 | 45.3811 | 0.7687 | 4.2114 | 0.23833 | 3.1945 | 0.76557 | 4.2108
TIER | Tieri | CA | 66 | 4.0673 | 464.9577 | 2.8098 | 107.0691 | 4.7733 | 9.1521 | 8.0386 | 22.9468 | 4.7451 | 9.1463
TOMA | Townsville Marina SS MF07 (BUSA) | NQ | 11 | 22.6005 | 430.5975 | 25.2924 | 160.6281 | 0.082952 | 0.29881 | 0.087251 | 0.19514 | 0.082554 | 0.29839
TOMA | Townsville Marina SS TOPO08 (BUSB) | NQ | 11 | 22.6005 | 430.5975 | 25.2924 | 160.6281 | 0.082952 | 0.29881 | 0.087251 | 0.19514 | 0.082554 | 0.29839
TOPO | Townsville Port (TF1) | NQ | 11 | 20.7241 | 394.8477 | 22.7279 | 144.3417 | 0.0496 | 0.3345 | 0.0404 | 0.2463 | 0.0492 | 0.3341
TOPO | Townsville Port (TF2) | NQ | 11 | 20.7241 | 394.8477 | 22.7279 | 144.3417 | 0.0496 | 0.3345 | 0.0404 | 0.2463 | 0.0492 | 0.3341
TOPO | Townsville Port | NQ | 66 | 13.5179 | 1545.3041 | 14.2648 | 543.5614 | 0.71932 | 3.0265 | 0.41552 | 2.6162 | 0.70497 | 3.0116
TOPS | Townsville Power Station | NQ | 66 | 8.8201 | 1008.2726 | 8.9118 | 339.5854 | 0.87687 | 4.6834 | 0.37579 | 4.6242 | 0.8192 | 4.6927
TORQ | Torquay | WB | 11 | 13.7349 | 261.6856 | 17.1282 | 108.7788 | 0.076438 | 0.5045 | 0.010925 | 0.20511 | 0.074923 | 0.50497
TORQ | Torquay | WB | 66 | 3.8112 | 435.6819 | 2.5917 | 98.7566 | 2.3585 | 10.7782 | 5.7969 | 25.8778 | 2.3039 | 10.7952
TORR | Torrington T116 (TF1) | SW | 110 | 8.5485 | 1628.711 | 8.0361 | 510.3637 | 1.2571 | 8.0815 | 0.64306 | 9.7913 | 1.2568 | 8.0355
TORR | Torrington T116 (TF2) | SW | 110 | 8.5387 | 1626.8416 | 7.6641 | 486.7368 | 1.2588 | 8.0907 | 0.81639 | 11.0275 | 1.2585 | 8.0447
TORR | Torrington T116 (TF3) | SW | 11 | 13.1585 | 250.7035 | 2.2762 | 14.4555 | 0.038085 | 0.52997 | 9.0266 | 0.37294 | 0.038082 | 0.52951
TORR | Torrington T116 (TF4) | SW | 11 | 13.1585 | 250.7035 | 2.2762 | 14.4555 | 0.038085 | 0.52997 | 9.0266 | 0.37294 | 0.038082 | 0.52951
TORR | Torrington T116 | SW | 33 | 14.8023 | 846.0624 | 1.17 | 22.2918 | 0.10351 | 1.4132 | 53.5474 | -4.4604 | 0.10349 | 1.4091
TULL | Tully T048 | FN | 22 | 7.6375 | 291.0286 | 6.3669 | 80.8699 | 0.1389 | 1.8387 | 0.1805 | 2.9376 | 0.1269 | 1.8365
TUNG | Tungamull | CA | 22 | 0.59079 | 22.512 | 0.60138 | 7.6385 | 3.0326 | 23.4636 | 2.4827 | 22.2707 | 3.0328 | 23.466
TUNG | Tungamull | CA | 66 | 3.5468 | 405.4547 | 2.3661 | 90.1589 | 4.9492 | 10.7366 | 8.7036 | 28.3109 | 4.9514 | 10.758
TURK | Turkinje T055 (TF1) | FN | 66 | 5.1313 | 586.5826 | 6.2695 | 238.9017 | 1.1778 | 8.0954 | 0.37886 | 3.5805 | 1.1167 | 8.2356
TURK | Turkinje T055 (TF2) | FN | 66 | 5.1313 | 586.5826 | 6.2695 | 238.9017 | 1.1778 | 8.0954 | 0.37886 | 3.5805 | 1.1167 | 8.2356
TWCE | Toowoomba Central | SW | 110 | 16.2143 | 3089.2314 | 14.3261 | 909.8292 | 0.56724 | 4.2745 | 0.87455 | 5.9991 | 0.56697 | 4.2285
TWCE | Toowoomba Central | SW | 11 | 18.6817 | 355.9335 | 4.5289 | 28.7623 | 0.013015 | 0.37402 | 1.1106e-07 | 3.8836 | 0.013013 | 0.37356
VERM | Vermont | CA | 22 | 4.2222 | 160.8892 | 4.8346 | 61.4071 | 0.40859 | 3.2878 | 0.10344 | 2.0555 | 0.40853 | 3.2888
VERM | Vermont | CA | 66 | 3.6731 | 419.8894 | 2.9624 | 112.8814 | 2.7463 | 11.0902 | 4.3249 | 19.1632 | 2.7458 | 11.0991
WAEA | Warwick East (TF1) | SW | 11 | 9.8899 | 188.4287 | 5.5145 | 35.0219 | 0.092241 | 0.70266 | 3.1955 | 0.35895 | 0.089451 | 0.70312
WAEA | Warwick East (TF2) | SW | 11 | 9.8899 | 188.4287 | 5.5145 | 35.0219 | 0.092241 | 0.70266 | 3.1955 | 0.35895 | 0.089451 | 0.70312
WAEA | Warwick East | SW | 33 | 6.6338 | 379.1728 | 6.8633 | 130.7629 | 0.69141 | 3.0933 | 0.48922 | 2.8065 | 0.66629 | 3.0974
WAGG | Waggamba T156 | SW | 132 | 1.3982 | 319.6718 | 1.5798 | 120.3972 | 11.3275 | 58.8852 | 3.9797 | 39.2296 | 11.3257 | 58.8552
WAGG | Waggamba T156 | SW | 33 | 2.8418 | 162.4305 | 2.4541 | 46.7574 | 0.72154 | 7.3405 | 3.23e-08 | 10.903 | 0.72142 | 7.3386
WAGG | Waggamba T156 | SW | 66 | 1.9396 | 221.7299 | 2.6802 | 102.128 | 2.8876 | 21.4193 | 0.21865 | 3.7081 | 2.8871 | 21.4118
WALK | Walkers | WB | 11 | 10.8226 | 206.1991 | 3.5338 | 22.4427 | 0.07785 | 0.64256 | 0.46126 | 4.6207 | 0.076835 | 0.64289
WALK | Walkers | WB | 66 | 5.7115 | 652.911 | 5.544 | 211.2562 | 1.4507 | 7.2145 | 1.6205 | 7.822 | 1.4141 | 7.2262
WALL | Wallaville | WB | 11 | 6.0648 | 115.5494 | 7.5387 | 47.877 | 0.43094 | 1.0683 | 0.031935 | 0.49469 | 0.43033 | 1.0698
WALL | Wallaville | WB | 66 | 1.6643 | 190.2592 | 1.1487 | 43.7698 | 14.3775 | 20.7154 | 19.8008 | 56.7151 | 14.3574 | 20.7699
WAND | Wandoan (TF1) | SW | 22 | 0.62825 | 23.9396 | 0.84008 | 10.6705 | 7.5261 | 20.93 | 0.28126 | 5.6252 | 7.5261 | 20.931
WAND | Wandoan (TF2) | SW | 22 | 0.62723 | 23.9008 | 0.83824 | 10.6471 | 7.528 | 20.9678 | 0.28315 | 5.6629 | 7.528 | 20.9687
WAND | Wandoan | SW | 33 | 0.55015 | 31.4455 | 0.30529 | 5.8166 | 16.3008 | 34.4359 | 29.5386 | 127.4972 | 16.3009 | 34.438
WARW | Warwick (CCT 735) | SW | 110 | 3.7671 | 717.738 | 4.5832 | 291.075 | 5.6342 | 17.7097 | 0.77511 | 8.7891 | 5.5506 | 17.721
WARW | Warwick (CCT 736) | SW | 110 | 3.7671 | 717.738 | 4.5832 | 291.075 | 5.6342 | 17.7097 | 0.77511 | 8.7891 | 5.5506 | 17.721
WARW | Warwick | SW | 11 | 3.3867 | 64.5246 | 3.5558 | 22.5824 | 0.20304 | 2.0596 | 0.14826 | 1.764 | 0.20025 | 2.06
WARW | Warwick | SW | 33 | 7.9209 | 452.7397 | 10.424 | 198.6044 | 0.49306 | 2.6084 | 0.022109 | 0.746 | 0.46794 | 2.6125
WEBU | West Bundaberg | WB | 11 | 14.6392 | 278.914 | 16.8152 | 106.7911 | 0.042617 | 0.47589 | 0.016488 | 0.28913 | 0.041981 | 0.478
WEBU | West Bundaberg | WB | 66 | 6.1817 | 706.6672 | 5.9868 | 228.1279 | 0.94064 | 6.7234 | 1.3086 | 7.2542 | 0.91774 | 6.7992
WEDA | West Dalby (TF1) | SW | 11 | 5.9716 | 113.7734 | 6.8356 | 43.4116 | 0.21648 | 1.1507 | 0.055635 | 0.72749 | 0.21648 | 1.1509
WEDA | West Dalby (TF2) | SW | 11 | 5.9716 | 113.7734 | 6.8356 | 43.4116 | 0.21648 | 1.1507 | 0.055635 | 0.72749 | 0.21648 | 1.1509
WEDA | West Dalby (TF3) | SW | 11 | 5.9716 | 113.7734 | 6.8356 | 43.4116 | 0.21648 | 1.1507 | 0.055635 | 0.72749 | 0.21648 | 1.1509
WEDA | West Dalby | SW | 33 | 5.1475 | 294.2194 | 4.7008 | 89.5626 | 1.4476 | 3.8094 | 1.2236 | 5.1156 | 1.4476 | 3.8103
WEMA | West Mackay (TF1) | MK | 11 | 12.4065 | 236.3751 | 13.6655 | 86.7876 | 0.047189 | 0.56171 | 0.020369 | 0.40697 | 0.046882 | 0.56248
WEMA | West Mackay (TF2) | MK | 11 | 12.4065 | 236.3751 | 13.6655 | 86.7876 | 0.047189 | 0.56171 | 0.020369 | 0.40697 | 0.046882 | 0.56248
WEMA | West Mackay (TF1) | MK | 33 | 13.5183 | 772.6769 | 16.9504 | 322.948 | 0.2544 | 1.531 | 0.1196 | 0.5916 | 0.2523 | 1.5379
WEMA | West Mackay (TF2) | MK | 33 | 14.086 | 805.1211 | 19.1035 | 363.9707 | 0.229 | 1.4717 | 0.07 | 0.3025 | 0.2269 | 1.4786
WETO | West Toowoomba | SW | 11 | 11.285 | 215.008 | 2.2622 | 14.3667 | 0.054261 | 0.61716 | 9.0196 | 0.39172 | 0.054258 | 0.6167
WETO | West Toowoomba | SW | 33 | 10.2173 | 583.9967 | 1.147 | 21.8531 | 0.31207 | 2.029 | 54.1936 | -1.926 | 0.31205 | 2.0249
WEWA | West Warwick | SW | 11 | 5.6441 | 107.5346 | 6.7058 | 42.5876 | 0.205 | 1.2248 | 0.035799 | 0.65204 | 0.20221 | 1.2252
WEWA | West Warwick | SW | 33 | 3.8614 | 220.7065 | 2.7393 | 52.1901 | 1.5506 | 5.2199 | 2.8909 | 11.7816 | 1.5255 | 5.2241
WIHI | Windy Hill | FN | 22 | 1.789 | 68.1683 | 1.8988 | 24.1182 | 2.2044 | 7.5044 | 0.56411 | 6.5219 | 2.1976 | 7.52
WIIS | Wiggins Island (TF1) | CA | 132 | 16.5215 | 3777.3148 | 14.5897 | 1111.8819 | 0.58816 | 5.0411 | 0.87058 | 7.0055 | 0.58837 | 5.0723
WIIS | Wiggins Island (TF2) | CA | 132 | 16.4565 | 3762.4639 | 14.5169 | 1106.3394 | 0.59242 | 5.0608 | 0.87584 | 7.0515 | 0.59262 | 5.092
WIIS | Wiggins Island | CA | 22 | 21.1161 | 804.6305 | 4.4605 | 56.6559 | 0.027591 | 0.66125 | 0.17654 | 8.0725 | 0.027597 | 0.66212
WINT | Winton | NQ | 11 | 1.6657 | 31.7358 | 2.2354 | 14.1966 | 1.5946 | 4.2558 | 0.013553 | 0.4544 | 1.5939 | 4.2796
WINT | Winton | NQ | 33 | 0.30197 | 17.2598 | 0.34459 | 6.5654 | 19.8135 | 72.5509 | 0.126 | 36.1043 | 19.8066 | 72.7653
WINT | Winton | NQ | 66 | 0.35781 | 40.9029 | 0.20819 | 7.9331 | 54.6722 | 114.5654 | 108.184 | 345.0533 | 54.6469 | 115.423
WIRR | Wirralie | NQ | 33 | 0.17557 | 10.0352 | 0.18172 | 3.4622 | 15.3564 | 118.5604 | 5.4868 | 107.5407 | 15.3567 | 118.5597
WIRR | Wirralie | NQ | 66 | 0.70943 | 81.0984 | 0.49486 | 18.8569 | 39.4784 | 44.0785 | 51.9016 | 130.1496 | 39.4798 | 44.0756
WOOD | Woodhouse Station | NQ | 11 | 0.27679 | 5.2735 | 0.27723 | 1.7606 | 3.9424 | 25.036 | 3.8485 | 24.8366 | 3.9397 | 25.035
WOOD | Woodhouse Station | NQ | 66 | 5.3031 | 606.2282 | 4.3646 | 166.3126 | 3.3813 | 7.1806 | 4.7012 | 12.2425 | 3.282 | 7.1438
WOOG | Woodgate | WB | 11 | 2.8405 | 54.1183 | 3.0865 | 19.6019 | 0.36014 | 2.4397 | 0.09425 | 1.8705 | 0.35927 | 2.4397
WOOG | Woodgate | WB | 66 | 1.8583 | 212.4352 | 1.2202 | 46.4974 | 9.5719 | 20.492 | 17.07 | 55.6464 | 9.5409 | 20.4909
WOOL | Woolooga | WB | 11 | 3.3847 | 64.4867 | 4.3339 | 27.5242 | 0.9394 | 1.8442 | 0.0531 | 0.7515 | 0.9384 | 1.8445
WOOL | Woolooga | WB | 66 | 0.82974 | 94.8518 | 0.55562 | 21.1721 | 31.9108 | 39.3399 | 43.2876 | 121.0172 | 31.8742 | 39.3516
WOON | Woongarra | WB | 3.3 | 13.3433 | 76.267 | 13.9088 | 26.4998 | 0.017583 | 0.15608 | 0.013172 | 0.13717 | 0.017528 | 0.15622
WOON | Woongarra | WB | 66 | 5.3548 | 612.1348 | 4.7856 | 182.3551 | 1.7776 | 7.6332 | 2.1467 | 10.3503 | 1.7575 | 7.6877
WOSO | Woodstock South (TF1) | NQ | 11 | 3.0736 | 58.5601 | 3.2809 | 20.8368 | 0.45336 | 2.244 | 0.088391 | 1.8514 | 0.45284 | 2.2436
WOSO | Woodstock South | NQ | 66 | 2.1878 | 250.0979 | 1.5584 | 59.3838 | 13.139 | 14.1343 | 17.2056 | 40.1611 | 13.1203 | 14.1188
WOWA | Wowan | CA | 22 | 2.6145 | 99.6271 | 3.0989 | 39.3608 | 1.9265 | 4.9867 | 0.19644 | 2.9356 | 1.9265 | 4.9886
WOWA | Wowan | CA | 66 | 1.7363 | 198.4852 | 1.1738 | 44.7285 | 15.5701 | 18.4599 | 21.821 | 56.2253 | 15.5707 | 18.4772
YALK | Yalkula | FN | 132 | 1.8852 | 431.0139 | 1.5598 | 118.8726 | 12.0231 | 42.8857 | 18.8099 | 69.6055 | 11.7349 | 43.3201
YANO | Yarranlea North | SW | 110 | 5.1662 | 984.2997 | 8.1158 | 515.4235 | 5.9977 | 12.1481 | 0 | 0 | 4.8465 | 11.362
YARA | Yarranlea T010 (TF1) | SW | 110 | 5.139 | 979.1131 | 7.6987 | 488.9304 | 6.05 | 12.2022 | 0.25208 | 1.2363 | 4.9204 | 11.4404
YARA | Yarranlea T010 (TF2) | SW | 110 | 5.1389 | 979.0845 | 7.6978 | 488.876 | 6.0507 | 12.2023 | 0.25268 | 1.2386 | 4.9211 | 11.4405
YARA | Yarranlea T010 | SW | 33 | 6.7346 | 384.9316 | 9.9725 | 190.0014 | 0.58991 | 3.0648 | 0.025659 | 0.15847 | 0.4846 | 3.0075
YARR | Yarraman (TF1) | WB | 11 | 3.8154 | 72.6932 | 4.7177 | 29.9617 | 0.8604 | 1.6165 | 0.0783 | 0.829 | 0.8605 | 1.6167
YARR | Yarraman (TF2) | WB | 11 | 3.8154 | 72.6932 | 4.7177 | 29.9617 | 0.8604 | 1.6165 | 0.0783 | 0.829 | 0.8605 | 1.6167
YARR | Yarraman | WB | 66 | 1.0492 | 119.9429 | 0.71148 | 27.1111 | 28.1554 | 28.3488 | 37.5287 | 93.0897 | 28.1568 | 28.355
YARW | Yarwun Switching Station | CA | 66 | 2.7237 | 311.3574 | 1.8305 | 69.7508 | 8.6811 | 12.7116 | 12.2553 | 36.5656 | 8.6807 | 12.7199
YASO | Yarranlea South (TF1) | SW | 11 | 2.1745 | 41.4295 | 2.3013 | 14.6153 | 0.43568 | 3.1925 | 0.26891 | 2.6908 | 0.42398 | 3.1861
YASO | Yarranlea South (TF2) | SW | 11 | 2.1745 | 41.4295 | 2.3013 | 14.6153 | 0.43568 | 3.1925 | 0.26891 | 2.6908 | 0.42398 | 3.1861
YASO | Yarranlea South | SW | 33 | 4.4174 | 252.4897 | 4.0184 | 76.56 | 1.5009 | 4.5153 | 1.87 | 5.9881 | 1.3956 | 4.4579
YEPP | Yeppoon | CA | 11 | 11.375 | 216.7231 | 14.2093 | 90.2413 | 0.17941 | 0.58761 | 0.012599 | 0.25217 | 0.17947 | 0.5882
YEPP | Yeppoon | CA | 22 | 2.1103 | 80.4123 | 1.0133 | 12.8702 | 0.91584 | 6.5598 | 0.050776 | 28.216 | 0.916 | 6.5618
YEPP | Yeppoon | CA | 66 | 3.1106 | 355.5911 | 2.0447 | 77.9142 | 6.0044 | 12.0691 | 10.108 | 33.2488 | 6.0066 | 12.0905
The following sites are not reported (future subs; de-commisioned sites; unused tertiary voltage, and sites being investigated)
INVI | Invicta | NQ | 66
DIRR | Dirranbandi | SW | 33
WASO | Wandoan South | SW | 66
GRAC | Gracemere | CA | 11
OORA | Ooralea (Future) | MK | 11
GRAC | Gracemere | CA | 66
OORA | Ooralea (Future) | MK | 66
EALE | East Leichhardt | NQ | 11
EALE | East Leichhardt | NQ | 66
THAO | Thallon | SW | 33
INJU | Injune | SW | 33
LIEN | Linc Energy | SW | 33
KARD | Kagara Red Dome | FN | 66
KUMB | Kumbia | WB | 11
KUMB | Kumbia | WB | 66
TOFO | Toowoomba Foundry | SW | 33
MASM | Maryborough Sugar Mill |  | 11
MARI | Marian (MARIAN 11kV) | MK | 11
HUGH | Hughenden | NQ | 6.6
KILK | Kilkivan T012 (TF3 Tert) | WB | 11
MARY | Maryborough T059 (TF2) | WB | 11
MARY | Maryborough T059 (TF3*O1225*ON) | WB | 11
MILC | Millchester T095 (TF2) | NQ | 11
MILC | Millchester T095 (TF1) | NQ | 11
PIVA | Pioneer Valley T141 | MK | 11
CAIR | Capricorn Resort | CA | 66
CADO | Cameby Downs | SW | 33
CLUT | Clutha | CA | 66
DRCM | Drake Coal Mine | NQ | 33
WICC | Wilkie Creek Coal | SW | 33

## 2023 - Regional Norm Fault
Sub Code | Substation | Region | Voltage (kV) | 2023 3-Ph Fault Level (kA) (Power Factory) | 2023 3-Ph Fault Level (MVA) (Power Factory) | 2023 1-Ph-G Fault Level (kA) (Power Factory) | 2023 1-Ph-G Fault Level (MVA) (Power Factory) | R1 (Ohms) | X1 (Ohms) | R0 (Ohms) | X0 (Ohms) | R2 (Ohms) | X2 (Ohms)
ABPO | Abbot Point | NQ | 66 | 1.9238 | 219.9144 | 1.5023 | 57.2443 | 7.6844 | 20.4339 | 10.1684 | 39.0554 | 7.6882 | 20.4099
AGWA | Agnes Water | CA | 22 | 2.0995 | 80 | 2.6662 | 33.8647 | 1.0075 | 6.5832 | 0.11824 | 2.4151 | 1.0073 | 6.584
AGWA | Agnes Water | CA | 66 | 1.0945 | 125.1171 | 0.82063 | 31.2701 | 8.0158 | 37.4773 | 12.0591 | 75.7363 | 8.0139 | 37.4844
AITK | Aitkenvale (TF1) | NQ | 11 | 10.2082 | 194.4914 | 10.6898 | 67.8891 | 0.05462 | 0.68444 | 0.033496 | 0.59424 | 0.054234 | 0.68418
AITK | Aitkenvale (TF2) | NQ | 11 | 10.2082 | 194.4914 | 10.6898 | 67.8891 | 0.05462 | 0.68444 | 0.033496 | 0.59424 | 0.054234 | 0.68418
AITK | Aitkenvale | NQ | 66 | 12.6099 | 1441.5067 | 10.004 | 381.2033 | 0.76043 | 3.2472 | 1.1573 | 5.8481 | 0.74656 | 3.2377
ALCR | Alligator Creek T065 | MK | 33 | 12.0539 | 688.9714 | 14.9293 | 284.4416 | 0.22744 | 1.7256 | 0.040375 | 0.71583 | 0.22431 | 1.7461
ALLO | Allora (TF1) | SW | 11 | 1.9239 | 36.6549 | 2.318 | 14.7215 | 1.9051 | 3.1074 | 0.29465 | 1.8723 | 1.9011 | 3.1083
ALLO | Allora (TF2) | SW | 11 | 1.9239 | 36.6549 | 2.318 | 14.7215 | 1.9051 | 3.1074 | 0.29465 | 1.8723 | 1.9011 | 3.1083
ALLO | Allora | SW | 33 | 1.1517 | 65.8302 | 0.87157 | 16.6055 | 14.494 | 11.1155 | 17.172 | 33.5069 | 14.458 | 11.1238
ALLO | Allora (Reg) | SW | 33 | 1.1517 | 65.8302 | 0.87157 | 16.6055 | 14.494 | 11.1155 | 17.172 | 33.5069 | 14.458 | 11.1238
ALSH | Alan Sherriff (TF1) | NQ | 11 | 9.138 | 174.1024 | 8.1127 | 51.5228 | 0.043308 | 0.76597 | 3.3946e-09 | 1.0608 | 0.043091 | 0.76581
ALSH | Alan Sherriff (TF2) | NQ | 11 | 9.138 | 174.1024 | 8.1034 | 51.4633 | 0.043308 | 0.76597 | 3.4131e-09 | 1.0638 | 0.043091 | 0.76581
ALST | Alfred Street | MK | 11 | 12.6375 | 240.7764 | 14.0658 | 89.33 | 0.039657 | 0.55196 | 0.0097889 | 0.3844 | 0.03942 | 0.55272
ALST | Alfred Street | MK | 33 | 13.6958 | 782.8211 | 18.4267 | 351.0763 | 0.26882 | 1.5081 | 0.11212 | 0.33107 | 0.26668 | 1.515
ARAM | Aramara T173 | WB | 132 | 8.0796 | 1847.2435 | 7.8984 | 601.9369 | 1.4444 | 10.2918 | 1.839 | 10.9069 | 1.405 | 10.3208
ATHE | Atherton (TF1) | FN | 22 | 6.3473 | 241.865 | 8.1755 | 103.8422 | 0.37513 | 2.1723 | 0.0038827 | 0.7205 | 0.36863 | 2.188
ATHE | Atherton (TF2) | FN | 22 | 6.3473 | 241.865 | 8.1755 | 103.8422 | 0.37513 | 2.1723 | 0.0038827 | 0.7205 | 0.36863 | 2.188
ATHE | Atherton | FN | 66 | 3.0948 | 353.7837 | 2.4605 | 93.7585 | 3.1275 | 13.1983 | 4.3476 | 23.5552 | 3.0689 | 13.3399
AWOO | Awoonga | CA | 11 | 10.099 | 192.4126 | 11.195 | 71.0979 | 0.12463 | 0.68058 | 0.031304 | 0.4849 | 0.12293 | 0.68601
AWOO | Awoonga | CA | 66 | 4.7179 | 539.3288 | 3.1678 | 120.7079 | 3.3532 | 8.2295 | 5.9726 | 21.1328 | 3.3559 | 8.2604
AYRZ | Ayr (TF2) | NQ | 11 | 5.0392 | 96.0102 | 5.3358 | 33.8867 | 0.14064 | 1.3819 | 0.074101 | 1.1545 | 0.13579 | 1.3825
AYRZ | Ayr (TF3) | NQ | 11 | 5.3442 | 101.8208 | 5.6782 | 36.0616 | 0.12053 | 1.3042 | 0.053993 | 1.0769 | 0.11568 | 1.3048
AYRZ | Ayr | NQ | 66 | 6.1613 | 704.332 | 5.2333 | 199.4152 | 2.0321 | 6.508 | 2.1352 | 10.2804 | 1.8935 | 6.5109
BABI | Babinda | FN | 22 | 1.2457 | 47.4672 | 0.79164 | 10.0552 | 7.7466 | 8.1382 | 10.86 | 29.7595 | 7.7389 | 8.1534
BALB | Balberra (1 Regulator) | MK | 11 | 3.481 | 66.3229 | 3.793 | 24.0889 | 0.29863 | 1.9866 | 0.088027 | 1.5054 | 0.2917 | 1.9838
BALB | Balberra (2 Regulator) | MK | 11 | 3.481 | 66.3229 | 3.793 | 24.0889 | 0.29863 | 1.9866 | 0.088027 | 1.5054 | 0.2917 | 1.9838
BALB | Balberra (Unregulated) | MK | 11 | 3.5187 | 67.0403 | 3.8369 | 24.3674 | 0.27855 | 1.9678 | 0.074643 | 1.4929 | 0.27832 | 1.9712
BALB | Balberra | MK | 33 | 4.5099 | 257.7727 | 2.9588 | 56.3732 | 1.8352 | 4.2747 | 2.7934 | 11.689 | 1.8331 | 4.3052
BAMB | Bambaroo | NQ | 11 | 1.2438 | 23.6977 | 1.294 | 8.2183 | 0.92273 | 5.552 | 0.51738 | 4.9397 | 0.90787 | 5.5426
BAMB | Bambaroo | NQ | 66 | 1.6287 | 186.1862 | 1.2826 | 48.8719 | 14.1245 | 21.5765 | 20.5845 | 42.0487 | 14.0575 | 21.703
BARC | Barcaldine T072 (TF1) | CA | 11 | 6.1396 | 116.9747 | 0 | 0 | 0.080913 | 1.1462 | 523809515.5297 | -17.0511 | 0.08143 | 1.1985
BARC | Barcaldine T072 (TF2) | CA | 11 | 6.2378 | 118.8467 | 0 | 0 | 0.08668 | 1.1416 | 523809515.0923 | 67.2733 | 0.086673 | 1.186
BARC | Barcaldine T072 | CA | 132 | 2.2582 | 516.2863 | 1.8685 | 142.3961 | 4.1656 | 37.2462 | 5.5466 | 54.5964 | 4.841 | 43.4847
BARC | Barcaldine T072 (TF5) | CA | 22 | 2.6566 | 101.2287 | 2.7866 | 35.3948 | 0.35153 | 5.3618 | 0.21438 | 4.2866 | 0.29036 | 5.753
BARC | Barcaldine T072 (TF6) | CA | 22 | 2.4271 | 92.4864 | 2.5911 | 32.912 | 0.39019 | 5.803 | 0.2144 | 4.2868 | 0.32447 | 6.2498
BARC | Barcaldine T072 | CA | 66 | 1.5472 | 176.8636 | 1.89 | 72.02 | 2.1425 | 27.2745 | 1.5847 | 10.5693 | 2.172 | 29.1859
BARG | Bargara | WB | 11 | 9.732 | 185.4187 | 11.5887 | 73.5982 | 0.10519 | 0.71097 | 0.01704 | 0.37116 | 0.10468 | 0.71315
BARG | Bargara | WB | 66 | 3.3206 | 379.5977 | 2.3091 | 87.9867 | 3.1734 | 12.2334 | 6.1323 | 28.5023 | 3.1549 | 12.3117
BARR | Barratta | NQ | 11 | 3.385 | 64.4938 | 3.6802 | 23.3724 | 0.44739 | 2.0188 | 0.16328 | 1.5683 | 0.44255 | 2.0195
BARR | Barratta | NQ | 66 | 2.0682 | 236.4224 | 1.4551 | 55.4462 | 10.228 | 17.5427 | 14.949 | 43.9664 | 10.0537 | 17.5661
BEEC | Beecher Switching | CA | 66 | 5.1932 | 593.6631 | 3.6014 | 137.2302 | 3.2116 | 7.4069 | 4.9898 | 18.1832 | 3.2112 | 7.4151
BEGA | Belgian Gardens | NQ | 11 | 16.7926 | 319.9415 | 17.7445 | 112.6927 | 0.025125 | 0.41662 | 0.011212 | 0.35099 | 0.024732 | 0.41636
BEGA | Belgian Gardens (TF1) | NQ | 66 | 16.6115 | 1898.9532 | 18.4258 | 702.1176 | 0.604 | 2.4585 | 0.44321 | 1.7443 | 0.58985 | 2.449
BEGA | Belgian Gardens (TF2) | NQ | 66 | 16.6214 | 1900.0767 | 18.4371 | 702.548 | 0.60269 | 2.4573 | 0.44172 | 1.7434 | 0.58854 | 2.4478
BENA | Benarkin (TF1) | WB | 11 | 3.4987 | 66.6594 | 3.7775 | 23.9902 | 0.40076 | 1.9564 | 0.19625 | 1.5454 | 0.40081 | 1.9565
BENA | Benarkin | WB | 66 | 2.5362 | 289.9316 | 1.5523 | 59.1512 | 7.3633 | 14.7983 | 11.7567 | 46.9613 | 7.3647 | 14.8045
BERS | Berserker | CA | 11 | 14.6721 | 279.541 | 16.0987 | 102.2406 | 0.040246 | 0.47462 | 0.011216 | 0.34925 | 0.040303 | 0.47522
BERS | Berserker | CA | 66 | 9.0516 | 1034.7365 | 8.433 | 321.3387 | 1.0451 | 4.5131 | 1.4202 | 5.4497 | 1.0471 | 4.5348
BEWE | Bedford Weir | CA | 22 | 4.1124 | 156.7021 | 4.8457 | 61.5486 | 0.82547 | 3.3009 | 0.13699 | 1.8801 | 0.82659 | 3.2953
BEWE | Bedford Weir | CA | 66 | 2.9543 | 337.7179 | 2.1203 | 80.7947 | 6.1963 | 12.787 | 9.9737 | 29.4956 | 6.2064 | 12.7365
BILO | Biloela T026 (Regulated) | CA | 11 | 15.8206 | 301.4235 | 17.7411 | 112.671 | 0.030996 | 0.44062 | 0.015371 | 0.2974 | 0.030985 | 0.44112
BILO | Biloela T026 | CA | 66 | 8.0844 | 924.1654 | 10.0107 | 381.459 | 0.56248 | 5.1558 | 0.29992 | 2.1546 | 0.56211 | 5.1737
BING | Bingegang | CA | 22 | 1.8573 | 70.7734 | 2.35 | 29.8493 | 2.7654 | 7.0079 | 0.26352 | 2.8868 | 2.7665 | 7.0023
BING | Bingegang | CA | 66 | 0.96746 | 110.5958 | 0.60643 | 23.1082 | 22.517 | 37.0897 | 40.393 | 115.1495 | 22.527 | 37.0392
BLAC | Blackwater T032 (TF4) | CA | 11 | 19.3034 | 367.7787 | 8.3591 | 53.0874 | 0.040751 | 0.36014 | 2.2166e-05 | 1.7907 | 0.04104 | 0.35879
BLAC | Blackwater T032 (TF5) | CA | 11 | 25.2709 | 481.475 | 14.6627 | 93.1206 | 0.03162 | 0.27504 | 5.4388e-06 | 0.88154 | 0.031964 | 0.27351
BLAC | Blackwater T032 | CA | 22 | 6.3346 | 241.3825 | 5.2446 | 66.6153 | 0.23403 | 2.1965 | 0.00025452 | 3.6033 | 0.2353 | 2.1907
BLAC | Blackwater T032 | CA | 66 | 8.5038 | 972.1191 | 11.1164 | 423.592 | 0.88163 | 4.857 | 0.098346 | 1.5098 | 0.89169 | 4.8064
BLAK | Blackall (TF1) | CA | 22 | 0.97191 | 37.0348 | 1.2079 | 15.3429 | 3.7908 | 14.0134 | 0.52711 | 5.9056 | 3.7941 | 14.2258
BLAK | Blackall (TF2) | CA | 22 | 0.97191 | 37.0348 | 1.2079 | 15.3429 | 3.7908 | 14.0134 | 0.52711 | 5.9056 | 3.7941 | 14.2258
BLAK | Blackall | CA | 66 | 0.53811 | 61.5141 | 0.38207 | 14.5588 | 29.3736 | 72.9704 | 49.6859 | 166.8477 | 29.403 | 74.8818
BLOO | Bloomfield SS | FN | 22 | 0.48186 | 18.3614 | 0.34764 | 4.4156 | 11.4992 | 26.6703 | 14.6759 | 61.4005 | 11.3971 | 26.7124
BLRI | Black River (TF1) | NQ | 11 | 7.8402 | 149.3766 | 8.1909 | 52.019 | 0.055917 | 0.8918 | 0.033372 | 0.77926 | 0.05481 | 0.89188
BLRI | Black River (TF2) | NQ | 11 | 7.0834 | 134.9569 | 7.3685 | 46.7963 | 0.057329 | 0.98737 | 0.034784 | 0.87482 | 0.056222 | 0.98744
BLRI | Black River | NQ | 66 | 10.1726 | 1162.8898 | 8.8447 | 337.0294 | 0.81161 | 4.0516 | 0.93259 | 5.9338 | 0.77176 | 4.0543
BLUE | Bluewater | NQ | 11 | 3.7119 | 70.7215 | 3.9152 | 24.8652 | 0.26889 | 1.8681 | 0.079924 | 1.5985 | 0.26778 | 1.8682
BLUE | Bluewater | NQ | 66 | 3.5463 | 405.3985 | 2.5607 | 97.577 | 6.8028 | 9.7064 | 9.148 | 24.3014 | 6.7629 | 9.7091
BLVA | Blue Valley T183 | NQ | 11 | 8.2344 | 156.8863 | 5.6854 | 36.1069 | 0.089634 | 0.84554 | 4.9091e-09 | 2 | 0.088933 | 0.84499
BLVA | Blue Valley T183 | NQ | 132 | 3.5638 | 814.7888 | 2.3594 | 179.8085 | 7.6687 | 22.2935 | 17.0354 | 57.3423 | 7.5677 | 22.2151
BOCR | Boat Creek T130 (TF1) | CA | 11 | 22.7718 | 433.8614 | 0 | 0 | 0.016794 | 0.30639 | 135802467.1961 | 4.0433 | 0.016582 | 0.30652
BOCR | Boat Creek T130 (TF2) | CA | 11 | 23.0658 | 439.4624 | 0 | 0 | 0.016892 | 0.30247 | 135802469.4569 | -2.6722 | 0.016679 | 0.30259
BOCR | Boat Creek T130 (TF1) | CA | 132 | 12.4941 | 2856.5242 | 13.7094 | 1044.7971 | 0.40453 | 6.6991 | 0.59134 | 4.8764 | 0.39998 | 6.7194
BOCR | Boat Creek T130 (TF2) | CA | 132 | 12.5577 | 2871.0724 | 13.8092 | 1052.404 | 0.39707 | 6.6655 | 0.57541 | 4.813 | 0.39255 | 6.6858
BOCR | Boat Creek T130 | CA | 66 | 10.439 | 1193.3364 | 12.6076 | 480.4122 | 0.15349 | 4.0133 | 0.17915 | 1.933 | 0.14521 | 4.018
BODA | Boondooma Dam (TF1) | WB | 11 | 2.8944 | 55.1461 | 3.4275 | 21.7677 | 0.6293 | 2.3305 | 0.14664 | 1.2905 | 0.62934 | 2.3306
BODA | Boondooma Dam (TF2) | WB | 11 | 2.8944 | 55.1461 | 3.4275 | 21.7677 | 0.6293 | 2.3305 | 0.14664 | 1.2905 | 0.62934 | 2.3306
BODA | Boondooma Dam | WB | 66 | 1.0157 | 116.1114 | 0.57757 | 22.0085 | 17.3758 | 37.4373 | 30.4763 | 132.8604 | 17.3772 | 37.4435
BOHL | Bohle (TF1) | NQ | 11 | 10.9792 | 209.1824 | 11.5305 | 73.2285 | 0.045575 | 0.63659 | 0.026604 | 0.54709 | 0.044871 | 0.63651
BOHL | Bohle (TF2) | NQ | 11 | 10.941 | 208.4541 | 11.4884 | 72.9611 | 0.045922 | 0.6388 | 0.026951 | 0.5493 | 0.045218 | 0.63872
BOHL | Bohle | NQ | 66 | 12.765 | 1459.2299 | 10.7115 | 408.1636 | 0.68298 | 3.222 | 1.0017 | 5.1042 | 0.65763 | 3.219
BOPU | Bocoolima Pumps | CA | 11 | 3.7633 | 71.7007 | 4.3837 | 27.84 | 0.45359 | 1.8005 | 0.054128 | 1.0826 | 0.45355 | 1.801
BOPU | Bocoolima Pumps | CA | 66 | 1.4175 | 162.0421 | 0.85887 | 32.7272 | 14.3807 | 25.8456 | 25.4302 | 84.3301 | 14.379 | 25.864
BORE | Boyne Residential | CA | 11 | 8.7185 | 166.1104 | 9.8287 | 62.4206 | 0.16402 | 0.7845 | 0.038651 | 0.53138 | 0.16402 | 0.78503
BORE | Boyne Residential | CA | 66 | 4.123 | 471.3213 | 2.8219 | 107.5302 | 4.5133 | 9.1122 | 7.4104 | 23.1828 | 4.5134 | 9.1314
BOWE | Bowen | NQ | 11 | 8.0492 | 153.3578 | 9.6767 | 61.4555 | 0.19986 | 0.84632 | 0.018473 | 0.43772 | 0.19996 | 0.84566
BOWE | Bowen | NQ | 66 | 2.6096 | 298.3121 | 2.5088 | 95.5977 | 6.5298 | 14.7095 | 6.0149 | 17.0696 | 6.5336 | 14.6856
BROD | Broadlea | MK | 132 | 3.911 | 894.1851 | 4.299 | 327.6261 | 5.0217 | 20.8614 | 1.7575 | 15.6429 | 5.0074 | 20.8656
BROD | Broadlea | MK | 66 | 5.1604 | 589.9119 | 6.479 | 246.8843 | 1.3302 | 8.0217 | 0.17096 | 3.1794 | 1.3267 | 8.0227
BROX | Broxburn | SW | 11 | 3.7002 | 70.4987 | 4.6742 | 29.6854 | 0.59063 | 1.799 | 0.037158 | 0.74315 | 0.57893 | 1.7926
BROX | Broxburn | SW | 33 | 1.9336 | 110.5189 | 1.2896 | 24.5705 | 5.2937 | 9.4945 | 7.9852 | 26.3765 | 5.1884 | 9.4371
BUCE | Bundaberg Central | WB | 11 | 15.2038 | 289.6709 | 16.3561 | 103.875 | 0.054134 | 0.45678 | 0.011314 | 0.34674 | 0.048613 | 0.47342
BUCE | Bundaberg Central | WB | 66 | 5.5686 | 636.5809 | 4.9203 | 187.4886 | 1.4694 | 7.3916 | 2.3597 | 10.1361 | 1.4535 | 7.4928
BUDA | Burdekin Dam (TF1) | NQ | 11 | 0.56815 | 10.8247 | 0.64645 | 4.1055 | 3.6473 | 11.7917 | 1.4754 | 7.7703 | 3.6699 | 11.7767
BUDA | Burdekin Dam (TF2) | NQ | 11 | 0.84365 | 16.0736 | 1.0289 | 6.5345 | 2.5653 | 7.9065 | 0.39343 | 3.8852 | 2.5879 | 7.8915
BUDA | Burdekin Dam | NQ | 33 | 0.51145 | 29.2335 | 0.2925 | 5.5729 | 19.5469 | 36.1921 | 31.5805 | 131.5814 | 19.7504 | 36.0574
BUDG | Burnett Dam Generator | WB | 11 | 0.59095 | 11.2592 | 0.35781 | 2.2724 | 3.2208 | 11.4057 | 5.6718 | 34.5663 | 3.219 | 11.4058
BULL | Bullyard | WB | 11 | 3.1771 | 60.531 | 3.3902 | 21.5307 | 0.34176 | 2.1749 | 0.13321 | 1.7802 | 0.3412 | 2.1764
BULL | Bullyard | WB | 66 | 2.6116 | 298.5414 | 1.8727 | 71.358 | 7.5076 | 14.2084 | 10.6624 | 33.6268 | 7.4875 | 14.2629
BUND | Bundaberg T020 | WB | 11 | 14.3408 | 273.2292 | 0 | 0 | 0.030674 | 0.48678 | 154929577.3869 | 1.1069 | 0.03011 | 0.48826
BUND | Bundaberg T020 | WB | 132 | 7.1236 | 1628.6657 | 7.1112 | 541.9457 | 2.2268 | 11.5709 | 1.5854 | 11.6646 | 2.2006 | 11.6382
BUND | Bundaberg T020 | WB | 66 | 7.3946 | 845.3175 | 8.7418 | 333.1075 | 0.63851 | 5.6394 | 0.23754 | 2.9823 | 0.61838 | 5.6939
CABO | Caboonbah | WB | 11 | 3.2602 | 62.1151 | 3.9478 | 25.0719 | 0.64672 | 2.0432 | 0.090686 | 1.0392 | 0.64676 | 2.0434
CABO | Caboonbah | WB | 66 | 1.0146 | 115.9899 | 0.59753 | 22.7688 | 20.0173 | 36.1434 | 32.2717 | 125.3668 | 20.0188 | 36.1496
CACI | Cairns City (TF1) | FN | 132 | 6.1684 | 1410.2932 | 7.2229 | 550.4627 | 2.1904 | 13.4378 | 1.4892 | 7.6044 | 2.1498 | 13.36
CACI | Cairns City (TF2) | FN | 132 | 6.1693 | 1410.4827 | 7.215 | 549.854 | 2.188 | 13.4364 | 1.3183 | 7.6758 | 2.1473 | 13.3585
CACI | Cairns City | FN | 22 | 12.536 | 477.6872 | 9.0865 | 115.4145 | 0.063062 | 1.1148 | 2.0964e-08 | 2.3936 | 0.061933 | 1.1126
CAFE | Cape Ferguson | NQ | 11 | 1.5211 | 28.9803 | 1.6164 | 10.2655 | 1.3828 | 4.396 | 0.3033 | 3.8554 | 1.3824 | 4.3955
CAFE | Cape Ferguson | NQ | 66 | 0.96769 | 110.6217 | 0.80388 | 30.6318 | 38.8615 | 19.4604 | 44.6309 | 59.5013 | 38.8473 | 19.4443
CALE | Calen | MK | 11 | 2.3732 | 45.2151 | 2.8264 | 17.9499 | 1.1345 | 2.7223 | 0.099179 | 1.6009 | 1.1335 | 2.7199
CALE | Calen | MK | 66 | 0.76429 | 87.3706 | 0.5351 | 20.3899 | 37.2704 | 40.3728 | 47.4751 | 120.7657 | 37.2348 | 40.2862
CALL | Calliope | CA | 11 | 9.3537 | 178.2122 | 10.3629 | 65.8131 | 0.097551 | 0.74064 | 0.03648 | 0.52766 | 0.097504 | 0.74115
CALL | Calliope | CA | 66 | 5.2562 | 600.8632 | 3.5175 | 134.0357 | 2.1986 | 7.6674 | 4.2034 | 19.3523 | 2.1969 | 7.6857
CANN | Cannonvale (TF1) | MK | 11 | 4.8026 | 91.5012 | 5.4906 | 34.8703 | 0.29021 | 1.4282 | 0.046087 | 0.91937 | 0.28922 | 1.4258
CANN | Cannonvale (TF2) | MK | 11 | 4.8427 | 92.2654 | 5.5434 | 35.2051 | 0.28943 | 1.416 | 0.045301 | 0.90721 | 0.28844 | 1.4136
CANN | Cannonvale (FDR P6/3) | MK | 66 | 2.067 | 236.2914 | 1.4816 | 56.4558 | 8.7885 | 18.3174 | 11.0872 | 43.536 | 8.7529 | 18.2309
CANN | Cannonvale (FDR P6/8) | MK | 66 | 2.067 | 236.2914 | 1.4816 | 56.4558 | 8.7885 | 18.3174 | 11.0872 | 43.536 | 8.7529 | 18.2309
CANO | Cairns North T093 (TF1) | FN | 132 | 6.4178 | 1467.3136 | 7.9973 | 609.4756 | 1.8864 | 12.9494 | 1.717 | 5.2185 | 1.8457 | 12.8715
CANO | Cairns North T093 (TF2) | FN | 132 | 6.4451 | 1473.5542 | 8.0614 | 614.36 | 1.8627 | 12.8969 | 1.669 | 5.0859 | 1.8221 | 12.819
CANO | Cairns North T093 | FN | 22 | 11.9623 | 455.8258 | 8.5765 | 108.9356 | 0.064425 | 1.1683 | 1.8938e-08 | 2.5615 | 0.063297 | 1.1662
CARD | Cardwell T134 | FN | 22 | 6.4889 | 247.2607 | 6.4477 | 81.8967 | 0.15477 | 2.1524 | 0.1095 | 2.1975 | 0.153 | 2.1543
CARI | Cape River | NQ | 11 | 1.0361 | 19.7404 | 1.0308 | 6.5468 | 0.63593 | 7.0177 | 0.41671 | 6.4713 | 0.62538 | 7.0211
CARI | Cape River | NQ | 66 | 2.0666 | 236.2492 | 2.7183 | 103.5818 | 7.8917 | 19.6724 | 0.14247 | 4.7024 | 7.5119 | 19.7924
CARM | Carmila | MK | 11 | 0.55875 | 10.6457 | 0.68041 | 4.3212 | 7.5513 | 9.9797 | 0.65307 | 6.5307 | 7.5561 | 9.9917
CARM | Carmila | MK | 33 | 0.30222 | 17.2744 | 0.23403 | 4.4589 | 62.0837 | 31.0413 | 76.2803 | 117.0555 | 62.1277 | 31.149
CAST | Canning Street | CA | 11 | 18.0825 | 344.5174 | 20.1481 | 127.9574 | 0.038744 | 0.38454 | 0.013357 | 0.26693 | 0.0388 | 0.38514
CAST | Canning Street | CA | 66 | 9.679 | 1106.4561 | 9.7286 | 370.7107 | 0.91401 | 4.2347 | 1.2748 | 4.0609 | 0.91606 | 4.2565
CATE | Cairns Terminal T051 | FN | 22 | 11.8782 | 452.6217 | 10.6159 | 134.84 | 0.058734 | 1.1769 | 1.075e-08 | 1.6033 | 0.057606 | 1.1748
CAWD | Cawdor | SW | 11 | 4.3785 | 83.4219 | 4.9728 | 31.5818 | 0.23197 | 1.5798 | 0.10227 | 1.0203 | 0.23197 | 1.5794
CAWD | Cawdor | SW | 33 | 4.0577 | 231.9286 | 1.0037 | 19.1234 | 1.1673 | 5.0356 | 56.6057 | 11.2876 | 1.1672 | 5.0314
CEPL | Cecil Plains (TF1) | SW | 11 | 1.8044 | 34.3792 | 2.2849 | 14.5109 | 1.3875 | 3.6264 | 0.075493 | 1.5099 | 1.3758 | 3.6201
CEPL | Cecil Plains (TF3) | SW | 11 | 1.7941 | 34.1825 | 2.2681 | 14.4044 | 1.3887 | 3.6499 | 0.076667 | 1.5333 | 1.377 | 3.6435
CEPL | Cecil Plains | SW | 33 | 0.93783 | 53.6044 | 0.56222 | 10.7118 | 11.8085 | 19.0492 | 18.7897 | 65.9097 | 11.7032 | 18.9918
CHAL | Charlton | SW | 11 | 4.8252 | 91.932 | 5.3267 | 33.8292 | 0.24495 | 1.4281 | 0.052178 | 1.0443 | 0.24495 | 1.4277
CHAL | Charlton | SW | 33 | 5.4793 | 313.182 | 1.0466 | 19.941 | 1.6381 | 3.4598 | 55.8935 | 3.728 | 1.638 | 3.4557
CHAR | Charleville | SW | 11 | 1.4933 | 28.4507 | 2.1091 | 13.3949 | 1.2259 | 4.515 | 0.016458 | 0.59544 | 1.223 | 4.5159
CHAR | Charleville | SW | 22 | 0.74325 | 28.3217 | 1.0003 | 12.7061 | 4.9081 | 18.1471 | 0.21941 | 4.3883 | 4.8963 | 18.1509
CHAR | Charleville | SW | 66 | 0.32042 | 36.6284 | 0.13871 | 5.2854 | 42.1983 | 123.8294 | 190.0372 | 616.4204 | 42.0916 | 123.8635
CHIA | Chillagoe | FN | 22 | 0.94706 | 36.0878 | 1.1281 | 14.3287 | 3.1286 | 14.4369 | 0.35557 | 7.7096 | 3.1269 | 14.4723
CHIA | Chillagoe | FN | 66 | 0.64088 | 73.2627 | 0.36249 | 13.8127 | 24.9574 | 60.5454 | 50.7755 | 211.0911 | 24.9417 | 60.8646
CHIL | Childers | WB | 11 | 7.858 | 149.7147 | 8.5953 | 54.5872 | 0.10636 | 0.88488 | 0.041492 | 0.65795 | 0.10415 | 0.88525
CHIL | Childers | WB | 66 | 4.9456 | 565.3566 | 4.5156 | 172.0682 | 2.3352 | 8.1693 | 2.4607 | 10.6207 | 2.2558 | 8.1827
CHIN | Chinchilla T013 | SW | 110 | 2.2166 | 422.3136 | 2.2399 | 142.2543 | 3.4031 | 31.3406 | 3.217 | 30.3497 | 3.3959 | 31.3595
CHIN | Chinchilla T013 | SW | 33 | 6.5341 | 373.4767 | 6.3706 | 121.3768 | 0.86674 | 3.0917 | 0.36868 | 3.4678 | 0.84176 | 3.0995
CHIN | Chinchilla T013 (TF3) | SW | 33 | 6.5341 | 373.4767 | 6.3706 | 121.3768 | 0.86674 | 3.0917 | 0.36868 | 3.4678 | 0.84176 | 3.0995
CHIN | Chinchilla T013 | SW | 132 | 8.6505 | 1977.7627 | 7.408 | 564.564 | 3.1039 | 9.183 | 4.0772 | 13.9721 | 3.0936 | 9.2103
CHTO | Charters Towers (TF1) | NQ | 11 | 4.7303 | 90.1234 | 5.0713 | 32.2069 | 0.20292 | 1.4887 | 0.052579 | 1.1579 | 0.20118 | 1.4883
CHTO | Charters Towers (TF2) | NQ | 11 | 4.7622 | 90.7316 | 5.1085 | 32.4433 | 0.20294 | 1.4786 | 0.052606 | 1.1478 | 0.2012 | 1.4782
CHTO | Charters Towers | NQ | 66 | 3.2599 | 372.6555 | 3.2363 | 123.321 | 5.4122 | 11.9091 | 2.784 | 12.8893 | 5.3496 | 11.8941
CHTW | Chinchilla Town (TF1) | SW | 11 | 6.0024 | 114.3604 | 6.7768 | 43.0386 | 0.1662 | 1.1532 | 0.038333 | 0.76667 | 0.16342 | 1.1541
CHTW | Chinchilla Town (TF2) | SW | 11 | 6.0024 | 114.3604 | 6.7768 | 43.0386 | 0.1662 | 1.1532 | 0.038333 | 0.76667 | 0.16342 | 1.1541
CHTW | Chinchilla Town | SW | 33 | 5.7256 | 327.2614 | 5.0771 | 96.7325 | 1.1508 | 3.479 | 0.90092 | 5.0171 | 1.1258 | 3.4868
CHUM | Chumvale | NQ - MI | 220 | 1.4476 | 551.5976 | 1.8443 | 234.2575 | 8.832 | 96.1147 | 3.2978 | 32.2693 | 7.7353 | 98.0174
CHUM | Chumvale | NQ - MI | 66 | 2.2527 | 257.5237 | 2.6613 | 101.411 | 1.127 | 18.5723 | 0.059209 | 9.8816 | 1.0283 | 18.7435
CLER | Clermont T071 (TF1) | CA | 11 | 9.7218 | 185.2258 | 6.5522 | 41.6119 | 0.075165 | 0.71738 | 0.01974 | 1.7231 | 0.083717 | 0.76419
CLER | Clermont T071 (TF2) | CA | 11 | 9.7165 | 185.1236 | 6.5531 | 41.6177 | 0.075297 | 0.71777 | 0.018491 | 1.7221 | 0.08383 | 0.76447
CLER | Clermont T071 | CA | 132 | 2.7308 | 624.347 | 2.4645 | 187.8229 | 6.9675 | 30.0115 | 4.3441 | 37.0861 | 8.0199 | 33.4683
CLER | Clermont T071 | CA | 22 | 3.9407 | 150.1612 | 3.9701 | 50.427 | 0.3522 | 3.5415 | 0.057203 | 3.2944 | 0.38637 | 3.7285
CLER | Clermont T071 | CA | 66 | 4.1114 | 470.0008 | 4.1449 | 157.9404 | 1.6832 | 10.0943 | 1.0305 | 8.1064 | 2.0491 | 11.8672
CLIF | Clifton (TF1) | SW | 11 | 1.4951 | 28.486 | 1.9047 | 12.0965 | 1.9536 | 4.2486 | 0.088232 | 1.7646 | 1.9536 | 4.2481
CLIF | Clifton (TF2) | SW | 11 | 1.5059 | 28.6913 | 1.9226 | 12.2103 | 1.9518 | 4.2126 | 0.086431 | 1.7286 | 1.9518 | 4.2121
CLIF | Clifton | SW | 33 | 0.75024 | 42.8818 | 0.36636 | 6.9801 | 16.7882 | 22.3556 | 80.9313 | 83.3031 | 16.7881 | 22.3514
CLIN | Clinton | CA | 11 | 14.6726 | 279.5509 | 15.6197 | 99.1984 | 0.030968 | 0.47523 | 0.019411 | 0.38884 | 0.030956 | 0.47546
CLIN | Clinton | CA | 66 | 13.3626 | 1527.548 | 13.8819 | 528.9724 | 0.41604 | 3.1098 | 0.49552 | 2.7342 | 0.41559 | 3.1181
CLON | Cloncurry (TF1) | NQ - MI | 11 | 1.1491 | 21.8929 | 1.1907 | 7.5619 | 0.58369 | 6.0515 | 0.42998 | 5.4213 | 0.58095 | 6.0563
CLON | Cloncurry (TF2) | NQ - MI | 11 | 2.3619 | 45.0011 | 2.5456 | 16.1668 | 0.38395 | 2.9327 | 0.23024 | 2.3024 | 0.38121 | 2.9374
CLON | Cloncurry | NQ - MI | 66 | 1.7948 | 205.1751 | 1.7575 | 66.971 | 5.5336 | 22.6887 | 5.816 | 24.0022 | 5.4349 | 22.8599
CLSO | Clare South T193 | NQ | 11 | 3.5096 | 66.8672 | 3.5699 | 22.6721 | 0.21109 | 1.9851 | 0.18852 | 1.8852 | 0.20802 | 1.984
CLSO | Clare South T193 | NQ | 66 | 11.4023 | 1303.4587 | 13.8932 | 529.4019 | 0.81238 | 3.5962 | 0.22345 | 1.7535 | 0.70177 | 3.5568
COCO | Cook Colliery | CA | 66 | 2.0761 | 237.3299 | 1.4016 | 53.4068 | 9.5951 | 17.7979 | 16.1988 | 47.0421 | 9.6051 | 17.7474
COCR | Cooby Creek | SW | 0.415 | 25.8448 | 17.8329 | 32.3204 | 7.4337 | 0.0017219 | 0.009192 | 0.00031578 | 0.0037331 | 0.0017219 | 0.0091915
COCR | Cooby Creek | SW | 33 | 2.1156 | 120.9212 | 0.84038 | 16.0114 | 4.8041 | 8.6721 | 8.4055 | 55.3289 | 4.8041 | 8.669
COLL | Collinsville | NQ | 33 | 7.2535 | 414.5914 | 8.7068 | 165.8863 | 0.39005 | 2.874 | 0.188 | 1.5412 | 0.59364 | 2.7393
COLU | Columboola T194 | SW | 132 | 18.4831 | 4225.7942 | 24.5591 | 1871.6548 | 0.70094 | 4.4816 | 0.16929 | 1.1237 | 0.704 | 4.5145
COLU | Columboola T194 | SW | 33 | 4.1902 | 239.5031 | 5.6844 | 108.3022 | 0.23361 | 4.9967 | 0.014529 | 1.0559 | 0.2338 | 4.9988
COME | Comet (TF1) | CA | 22 | 1.8467 | 70.3691 | 1.9805 | 25.1564 | 1.207 | 7.4887 | 0.53811 | 6.1219 | 1.1735 | 7.4064
COME | Comet (TF2) | CA | 22 | 0.61076 | 23.2732 | 0.62477 | 7.9356 | 3.6561 | 22.6418 | 2.9872 | 21.2751 | 3.6226 | 22.5595
COME | Comet | CA | 66 | 3.0685 | 350.7813 | 2.0651 | 78.6925 | 6.0201 | 12.3009 | 10.3354 | 33.057 | 5.7188 | 11.56
COOK | Cooktown (TF1) | FN | 22 | 1.8175 | 69.2576 | 2.369 | 30.0906 | 1.5738 | 7.5351 | 0.0070327 | 2.3353 | 1.2803 | 7.6147
COOK | Cooktown (TF2) | FN | 22 | 1.4172 | 54.0022 | 1.777 | 22.5703 | 1.9995 | 9.67 | 0.00053014 | 3.9042 | 1.8658 | 9.734
COOK | Cooktown | FN | 66 | 0.78276 | 89.482 | 0.47761 | 18.1993 | 15.7267 | 51.2756 | 37.9177 | 151.6204 | 14.5236 | 51.8521
COOM | Coominglah (TF1) | CA | 22 | 0.77556 | 29.5527 | 0.82703 | 10.5046 | 4.1459 | 17.5376 | 1.6013 | 14.6461 | 4.1458 | 17.5396
COOM | Coominglah (TF2) | CA | 22 | 0.77557 | 29.5532 | 0.82704 | 10.5048 | 4.1456 | 17.5373 | 1.6013 | 14.6461 | 4.1456 | 17.5393
COOM | Coominglah | CA | 66 | 1.2097 | 138.2839 | 0.85402 | 32.5424 | 22.8987 | 26.0204 | 31.5136 | 73.3071 | 22.8983 | 26.0382
COPP | Coppabella Dragline | MK | 66 | 1.6649 | 190.3234 | 1.2023 | 45.8154 | 9.8887 | 23.1819 | 20.0595 | 50.4676 | 9.8852 | 23.1829
CORF | Corfield | NQ | 66 | 0.51888 | 59.3162 | 0.32155 | 12.2527 | 37.5572 | 79.0693 | 67.1841 | 212.766 | 37.5319 | 79.9269
CORI | Corella River | NQ - MI | 11 | 0.13457 | 2.564 | 0.1377 | 0.87452 | 17.6161 | 48.8314 | 16.3425 | 45.5265 | 17.6134 | 48.8361
CORI | Corella River | NQ - MI | 66 | 0.32874 | 37.5804 | 0.26999 | 10.288 | 45.8495 | 118.9739 | 59.6562 | 202.383 | 45.7508 | 119.1451
CRAI | Craiglie (TF1) | FN | 132 | 1.4383 | 328.8418 | 0.98887 | 75.3621 | 16.9486 | 55.8613 | 40.0857 | 131.714 | 16.7869 | 56.2706
CRAI | Craiglie (TF2) | FN | 132 | 1.4822 | 338.8757 | 1.0763 | 82.0286 | 16.188 | 54.2871 | 34.5565 | 115.373 | 15.9263 | 54.7157
CRAI | Craiglie (TF1) | FN | 22 | 5.7824 | 220.3399 | 7.5697 | 96.1476 | 0.39663 | 2.3874 | 4.7661e-05 | 0.70467 | 0.39089 | 2.3989
CRAI | Craiglie (TF2) | FN | 22 | 5.7824 | 220.3399 | 7.5697 | 96.1476 | 0.39663 | 2.3874 | 4.7661e-05 | 0.70467 | 0.39089 | 2.3989
CRAN | Cranbrook (TF1) | NQ | 11 | 7.183 | 136.8545 | 7.4263 | 47.1634 | 0.058114 | 0.97407 | 0.036234 | 0.88094 | 0.057734 | 0.97381
CRAN | Cranbrook (TF2) | NQ | 11 | 7.183 | 136.8545 | 7.4263 | 47.1634 | 0.058114 | 0.97407 | 0.036234 | 0.88094 | 0.057734 | 0.97381
CRAN | Cranbrook | NQ | 66 | 12.2108 | 1395.8847 | 9.7396 | 371.1293 | 0.7877 | 3.3528 | 1.3228 | 5.939 | 0.774 | 3.3434
CRED | Crediton | MK | 11 | 0.63243 | 12.0493 | 0.65185 | 4.1398 | 1.6667 | 10.9304 | 0.71493 | 10.0662 | 1.6665 | 10.9328
CRED | Crediton | MK | 66 | 0.90657 | 103.6352 | 0.64867 | 24.7175 | 34.2635 | 31.1088 | 44.498 | 95.4435 | 34.2565 | 31.1975
CRNA | Cressbrook No. 1 | SW | 3.3 | 6.1813 | 35.3308 | 7.1815 | 13.6825 | 0.090833 | 0.32692 | 0.010054 | 0.20108 | 0.090833 | 0.32689
CRNA | Cressbrook No. 1 | SW | 33 | 1.4026 | 80.1688 | 0.62492 | 11.9062 | 8.0779 | 12.5838 | 13.9341 | 70.918 | 8.0779 | 12.5807
CRNB | Cressbrook No. 2 | SW | 3.3 | 6.9124 | 39.5096 | 7.794 | 14.8495 | 0.067174 | 0.29589 | 0.010125 | 0.20249 | 0.067174 | 0.29586
CRNB | Cressbrook No. 2 | SW | 33 | 1.9164 | 109.539 | 0.79323 | 15.1131 | 5.7049 | 9.3394 | 9.6733 | 57.7906 | 5.7049 | 9.3364
CRNE | Crows Nest (TF1) | SW | 11 | 2.6561 | 50.606 | 3.1978 | 20.3085 | 0.79375 | 2.5096 | 0.06642 | 1.3279 | 0.79375 | 2.5092
CRNE | Crows Nest | SW | 33 | 1.6795 | 95.9963 | 0.71597 | 13.6411 | 6.5459 | 10.6348 | 11.062 | 63.2279 | 6.546 | 10.6317
CROY | Croydon | FN | 22 | 0.65539 | 24.9738 | 0.77843 | 9.8874 | 4.0793 | 25.3865 | 0.0053536 | 15.7153 | 3.9535 | 25.4425
CROY | Croydon | FN | 66 | 0.56836 | 64.9721 | 0.51725 | 19.7098 | 25.1062 | 85.3317 | 23.2666 | 122.6793 | 23.9741 | 85.8362
CUNN | Cunnamulla | SW | 11 | 0.88826 | 16.9237 | 1.2196 | 7.7454 | 2.8399 | 7.3345 | 0.07618 | 1.5236 | 2.8369 | 7.3354
CUNN | Cunnamulla | SW | 22 | 0.444 | 16.9189 | 0.6337 | 8.0491 | 11.36 | 29.3472 | 0.094364 | 3.3943 | 11.3482 | 29.351
CUNN | Cunnamulla | SW | 66 | 0.18084 | 20.673 | 0.083349 | 3.176 | 99.5014 | 209.3473 | 323.5612 | 996.6597 | 99.3947 | 209.3814
DAAN | Daandine T188 | SW | 110 | 1.6175 | 308.1793 | 1.269 | 80.5942 | 22.5773 | 36.8641 | 19.3231 | 78.4338 | 22.5768 | 36.8747
DAAN | Daandine T188 | SW | 33 | 2.653 | 151.6376 | 2.3784 | 45.3143 | 2.251 | 7.5798 | 1.8277 | 10.5258 | 2.251 | 7.5807
DABA | Dalrymple Bay | MK | 33 | 7.0503 | 402.9766 | 5.7402 | 109.3653 | 0.39493 | 2.9496 | 0.65211 | 4.9611 | 0.39422 | 2.9606
DACE | Dalby Central (TF1) | SW | 11 | 5.8138 | 110.7668 | 6.574 | 41.7503 | 0.18801 | 1.1879 | 0.042121 | 0.78684 | 0.18801 | 1.188
DACE | Dalby Central (TF1) | SW | 11 | 5.8138 | 110.7668 | 6.574 | 41.7503 | 0.18801 | 1.1879 | 0.042121 | 0.78684 | 0.18801 | 1.188
DACE | Dalby Central | SW | 33 | 5.4611 | 312.1431 | 5.1718 | 98.5351 | 1.313 | 3.6098 | 0.93122 | 4.4138 | 1.313 | 3.6107
DACG | Dalby Cotton Gin | SW | 33 | 2.3496 | 134.3002 | 1.5915 | 30.3223 | 4.4823 | 7.7209 | 5.8957 | 21.1925 | 4.4823 | 7.7219
DAEA | Dalby East | SW | 110 | 3.5659 | 679.4019 | 3.8082 | 241.8538 | 9.9397 | 16.9026 | 2.0528 | 16.7023 | 9.9392 | 16.9132
DAEA | Dalby East | SW | 33 | 7.0777 | 404.543 | 8.926 | 170.0634 | 0.9352 | 2.8124 | 0.061573 | 1.1533 | 0.93516 | 2.8134
DAGL | Dan Gleeson T092 (TF1) | NQ | 11 | 10.947 | 208.5683 | 11.3486 | 72.0733 | 0.039938 | 0.63905 | 0.030005 | 0.57277 | 0.039562 | 0.63879
DAGL | Dan Gleeson T092 (TF2) | NQ | 11 | 10.8724 | 207.1474 | 11.2685 | 71.5646 | 0.040086 | 0.64344 | 0.030154 | 0.57716 | 0.03971 | 0.64318
DAGL | Dan Gleeson T092 | NQ | 66 | 17.4297 | 1992.4845 | 19.8588 | 756.7215 | 0.35757 | 2.3863 | 0.18696 | 1.5309 | 0.34402 | 2.3769
DEGI | Degilbo | WB | 11 | 1.5256 | 29.0671 | 1.6002 | 10.1625 | 0.46368 | 4.5673 | 0.012408 | 3.9444 | 0.46189 | 4.5674
DEGI | Degilbo | WB | 66 | 1.5175 | 173.4757 | 1.0573 | 40.287 | 16.2458 | 22.4257 | 22.7303 | 60.6754 | 16.1813 | 22.4312
DIMB | Dimbulah (TF1) | FN | 22 | 3.1981 | 121.865 | 4.0909 | 51.9619 | 1.3621 | 4.157 | 0.1063 | 1.514 | 1.3604 | 4.1924
DIMB | Dimbulah (TF2) | FN | 22 | 3.1981 | 121.865 | 4.0909 | 51.9619 | 1.3621 | 4.157 | 0.1063 | 1.514 | 1.3604 | 4.1924
DIMB | Dimbulah | FN | 66 | 1.5937 | 182.1843 | 1.0117 | 38.5526 | 11.3022 | 23.7862 | 19.4847 | 69.2517 | 11.2865 | 24.1054
DIRE | Dirranbandi Regulator (Regulated) | SW | 33 | 0.37009 | 21.1536 | 0.26216 | 4.9948 | 20.9065 | 52.6308 | 24.3191 | 125.2808 | 20.8798 | 52.6393
DIRE | Dirranbandi Regulator (Unregulated) | SW | 33 | 0.37009 | 21.1536 | 0.26216 | 4.9948 | 20.9065 | 52.6308 | 24.3191 | 125.2808 | 20.8798 | 52.6393
DISR | Disraeli | NQ | 11 | 3.4984 | 66.6539 | 3.9269 | 24.9394 | 0.54888 | 1.9497 | 0.0036958 | 1.3551 | 0.54727 | 1.9492
DISR | Disraeli | NQ | 66 | 1.4598 | 166.8721 | 1.0882 | 41.466 | 19.7515 | 21.4051 | 22.774 | 55.3774 | 19.6934 | 21.3857
DURI | Dugald River (TF1) | NQ - MI | 11 | 11.6788 | 222.5116 | 0.07675 | 0.48743 | 0.032781 | 0.59727 | 272.9997 | 0.1338 | 0.030039 | 0.60203
DURI | Dugald River (TF2) | NQ - MI | 11 | 11.6788 | 222.5116 | 0.07675 | 0.48743 | 0.032781 | 0.59727 | 272.9997 | 0.1338 | 0.030039 | 0.60203
DURI | Dugald River | NQ - MI | 220 | 1.1359 | 432.8363 | 1.4547 | 184.7693 | 12.7961 | 122.3352 | 1.7304 | 40.3741 | 11.6995 | 124.2379
DURO | Duchess Road (TF1) | NQ - MI | 11 | 22.0266 | 419.663 | 3.1332 | 19.8987 | 0.020309 | 0.31651 | 2.0304e-07 | 6.051 | 0.017568 | 0.32127
DURO | Duchess Road (TF2) | NQ - MI | 11 | 22.6206 | 430.9797 | 3.1411 | 19.9487 | 0.021034 | 0.30811 | 2.1969e-07 | 6.051 | 0.018293 | 0.31287
DURO | Duchess Road (TF1) | NQ - MI | 132 | 5.879 | 1344.1176 | 6.3388 | 483.0836 | 1.7172 | 14.1557 | 1.2855 | 10.4423 | 1.3224 | 14.8407
DURO | Duchess Road (TF2) | NQ - MI | 132 | 6.4118 | 1465.9444 | 7.1524 | 545.0834 | 1.8216 | 12.9469 | 1.3578 | 8.2805 | 1.4268 | 13.6319
DURO | Duchess Road | NQ - MI | 66 | 0.51214 | 58.5457 | 0.53416 | 20.3541 | 5.8789 | 81.6323 | 5.2467 | 71.3689 | 5.7802 | 81.8035
DYSA | Dysart T035 (R01) | CA | 22 | 5.5383 | 211.0361 | 1.3487 | 17.1303 | 0.18829 | 2.5187 | 0.035995 | 26.0763 | 0.18828 | 2.5196
DYSA | Dysart T035 (R02) | CA | 22 | 5.5383 | 211.0361 | 1.3487 | 17.1303 | 0.18829 | 2.5187 | 0.035995 | 26.0763 | 0.18828 | 2.5196
DYSA | Dysart T035 | CA | 66 | 6.2204 | 711.0826 | 7.8715 | 299.9434 | 1.3778 | 6.604 | 0.2141 | 2.5 | 1.3777 | 6.6124
EAAY | East Ayr (TF1) | NQ | 11 | 8.3724 | 159.5162 | 9.32 | 59.19 | 0.11381 | 0.82834 | 0.030255 | 0.58155 | 0.10939 | 0.82862
EAAY | East Ayr (TF2) | NQ | 11 | 8.4096 | 160.2236 | 9.3662 | 59.4833 | 0.11382 | 0.82461 | 0.030269 | 0.57782 | 0.1094 | 0.82489
EAAY | East Ayr | NQ | 66 | 5.5186 | 630.8639 | 4.2701 | 162.7126 | 2.6079 | 7.1521 | 3.5009 | 13.9349 | 2.4794 | 7.1438
EABU | East Bundaberg | WB | 11 | 10.1581 | 193.5378 | 11.3941 | 72.3621 | 0.07261 | 0.68472 | 0.01797 | 0.46124 | 0.072131 | 0.6873
EABU | East Bundaberg | WB | 66 | 5.0671 | 579.2506 | 4.283 | 163.2037 | 1.967 | 8.0452 | 3.1421 | 12.3334 | 1.9498 | 8.1381
EATO | East Toowoomba | SW | 11 | 9.8556 | 187.7748 | 2.2437 | 14.2495 | 0.063106 | 0.70659 | 9.0248 | 0.49615 | 0.063104 | 0.70612
EATO | East Toowoomba (TF1) | SW | 33 | 8.5627 | 489.4242 | 1.1028 | 21.0108 | 0.5215 | 2.3934 | 55.2927 | 4.2694 | 0.52147 | 2.3892
EATO | East Toowoomba (TF2) | SW | 33 | 8.2295 | 470.377 | 1.0954 | 20.8692 | 0.58073 | 2.4817 | 55.4785 | 4.6261 | 0.58071 | 2.4775
EDMO | Edmonton | FN | 22 | 8.4602 | 322.3766 | 7.6049 | 96.5957 | 0.074239 | 1.6528 | 0.016973 | 2.2171 | 0.073071 | 1.651
EGHI | Egans Hill T127 | CA | 66 | 10.1643 | 1161.9361 | 11.4226 | 435.2609 | 0.70798 | 4.0642 | 0.47568 | 2.6986 | 0.71003 | 4.0859
EIDS | Eidsvold | WB | 11 | 1.2706 | 24.2073 | 1.3295 | 8.4436 | 1.7719 | 5.2203 | 0.49985 | 4.8156 | 1.7706 | 5.2202
EIDS | Eidsvold | WB | 66 | 0.59806 | 68.3674 | 0.41061 | 15.6464 | 47.2678 | 51.9969 | 74.6343 | 151.7645 | 47.2191 | 51.9956
ELAR | El Arish | FN | 22 | 10.9051 | 415.5399 | 8.2874 | 105.2637 | 0.1054 | 1.2795 | 1.4689e-08 | 2.505 | 0.1037 | 1.281
ELRO | Ellwoods Road (TF1) | WB | 11 | 3.4485 | 65.7027 | 3.7384 | 23.7418 | 0.34726 | 1.9961 | 0.1944 | 1.5435 | 0.3473 | 1.9963
ELRO | Ellwoods Road (TF2) | WB | 11 | 3.4932 | 66.5539 | 3.791 | 24.0761 | 0.34589 | 1.97 | 0.19303 | 1.5175 | 0.34593 | 1.9702
ELRO | Ellwoods Road | WB | 66 | 2.4377 | 278.671 | 1.4037 | 53.4899 | 5.5031 | 16.2926 | 10.6983 | 54.3293 | 5.5045 | 16.2988
EMER | Emerald | CA | 22 | 6.9117 | 263.3728 | 9.5066 | 120.7502 | 0.38582 | 1.9929 | 0.035524 | 0.71002 | 0.21941 | 1.678
EMER | Emerald | CA | 66 | 3.5167 | 402.0182 | 2.6231 | 99.9523 | 3.1527 | 11.5459 | 13.2146 | 24.3807 | 1.6549 | 8.7121
EMWE | Emerald West | CA | 66 | 3.7069 | 423.7604 | 2.8769 | 109.6236 | 2.7793 | 11.0105 | 13.35 | 21.3807 | 1.2218 | 7.9319
ERHE | Ernest Henry (TF1) | NQ - MI | 11 | 13.5689 | 258.5224 | 0.10994 | 0.69821 | 0.041374 | 0.51318 | 190.4998 | 3.3501 | 0.038633 | 0.51794
ERHE | Ernest Henry (TF1) | NQ - MI | 11 | 13.5689 | 258.5224 | 0.10994 | 0.69821 | 0.041374 | 0.51318 | 190.4998 | 3.3501 | 0.038633 | 0.51794
ERHE | Ernest Henry | NQ - MI | 220 | 1.1757 | 447.9959 | 1.5451 | 196.2599 | 12.1848 | 118.2141 | 2.6254 | 31.7031 | 11.0882 | 120.1167
ETON | Eton (TF1) | MK | 11 | 2.1662 | 41.2719 | 2.6291 | 16.6972 | 1.0319 | 3.059 | 0.078324 | 1.5665 | 1.0317 | 3.0623
ETON | Eton (TF1) | MK | 11 | 2.1662 | 41.2719 | 2.6291 | 16.6972 | 1.0319 | 3.059 | 0.078324 | 1.5665 | 1.0317 | 3.0623
ETON | Eton | MK | 33 | 1.3162 | 75.2288 | 0.76447 | 14.5651 | 8.5825 | 13.4324 | 13.1041 | 49.6796 | 8.5804 | 13.4628
EUDA | Eungella Dam (TF1) | MK | 11 | 0.62905 | 11.985 | 0.65559 | 4.1635 | 2.0592 | 10.9236 | 0.59614 | 9.8025 | 2.0591 | 10.9261
EUDA | Eungella Dam (TF2) | MK | 11 | 2.0216 | 38.5175 | 2.405 | 15.2735 | 1.6647 | 3.0319 | 0.20155 | 1.9108 | 1.6645 | 3.0344
EUDA | Eungella Dam | MK | 66 | 0.63227 | 72.2779 | 0.46797 | 17.832 | 52.672 | 40.3596 | 68.2098 | 124.7074 | 52.665 | 40.4482
EUMA | Eumamurrin Regulator (Regulated) | SW | 33 | 0.52154 | 29.81 | 0.38287 | 7.2946 | 32.7059 | 23.3506 | 40.5397 | 78.7876 | 32.6792 | 23.3592
EUMA | Eumamurrin Regulator (Unregulated) | SW | 33 | 0.52154 | 29.81 | 0.38287 | 7.2946 | 32.7059 | 23.3506 | 40.5397 | 78.7876 | 32.6792 | 23.3592
EVEL | Evelyn | FN | 22 | 1.5556 | 59.2775 | 1.7544 | 22.2841 | 1.7671 | 8.8194 | 0.45383 | 5.9433 | 1.7606 | 8.8351
EVEL | Evelyn | FN | 66 | 1.4752 | 168.6376 | 0.96525 | 36.7809 | 11.8191 | 25.8846 | 17.7972 | 71.8465 | 11.7606 | 26.0262
FARB | Farnborough | CA | 66 | 2.4581 | 280.9997 | 1.5787 | 60.1554 | 7.971 | 15.0816 | 13.2383 | 43.963 | 7.973 | 15.1034
FARL | Farleigh | MK | 11 | 7.9617 | 151.6905 | 9.1212 | 57.9273 | 0.14032 | 0.86647 | 0.028428 | 0.54248 | 0.10544 | 0.87325
FARL | Farleigh | MK | 33 | 2.5567 | 146.1368 | 1.2747 | 24.2854 | 3.7096 | 7.317 | 9.9803 | 31.534 | 3.6581 | 7.3695
FARN | Farnsfield | WB | 11 | 6.9497 | 132.4096 | 8.1422 | 51.7097 | 0.22597 | 0.98206 | 0.031705 | 0.56709 | 0.22377 | 0.98243
FARN | Farnsfield | WB | 66 | 2.5475 | 291.2154 | 1.8096 | 68.9547 | 6.9937 | 14.9389 | 9.8859 | 35.4828 | 6.9144 | 14.9523
FILA | Fisherman's Landing | CA | 11 | 15.8448 | 301.8839 | 18.2478 | 115.8894 | 0.039462 | 0.43923 | 0.016466 | 0.26618 | 0.039232 | 0.43936
FILA | Fisherman's Landing | CA | 66 | 6.6875 | 764.4889 | 5.7289 | 218.2986 | 0.80387 | 6.2174 | 1.9861 | 9.2195 | 0.79559 | 6.2221
FILA | Fisherman's Landing | CA | 66 | 6.6711 | 762.6066 | 5.7074 | 217.4824 | 0.82787 | 6.2299 | 2.0119 | 9.2657 | 0.81959 | 6.2346
FITR | Fig Tree T185 | NQ | 11 | 7.7553 | 147.7584 | 5.5316 | 35.1304 | 0.1221 | 0.89403 | 4.9091e-09 | 2 | 0.1222 | 0.89383
FITR | Fig Tree T185 | NQ | 132 | 2.811 | 642.692 | 1.908 | 145.4092 | 12.3482 | 27.2012 | 23.7004 | 68.4846 | 12.3635 | 27.1731
FOXL | Foxleigh | CA | 22 | 1.6416 | 62.5527 | 1.8003 | 22.8674 | 1.3983 | 8.4171 | 0.31407 | 6.2815 | 1.3779 | 8.4366
FOXL | Foxleigh | CA | 66 | 1.9493 | 222.84 | 1.0721 | 40.8536 | 9.7581 | 19.221 | 20.3555 | 72.0648 | 9.5742 | 19.3964
FREN | Frenchville | CA | 11 | 14.4748 | 275.7827 | 15.9264 | 101.1464 | 0.04881 | 0.48034 | 0.017529 | 0.35009 | 0.048867 | 0.48094
FREN | Frenchville | CA | 66 | 8.6952 | 993.9987 | 8.234 | 313.7565 | 1.1261 | 4.689 | 1.7836 | 5.3344 | 1.1282 | 4.7108
GARB | Garbutt T046 (TF3) | NQ | 11 | 10.1505 | 193.3921 | 10.4778 | 66.5433 | 0.035608 | 0.68958 | 0.024583 | 0.62659 | 0.035214 | 0.68932
GARB | Garbutt T046 (TF5) | NQ | 11 | 10.1505 | 193.3921 | 10.4778 | 66.5433 | 0.035608 | 0.68958 | 0.024583 | 0.62659 | 0.035214 | 0.68932
GARB | Garbutt T046 | NQ | 66 | 18.2658 | 2088.0664 | 20.3139 | 774.0643 | 0.39688 | 2.2678 | 0.21101 | 1.6079 | 0.38273 | 2.2584
GAVI | Gavial 66kV Switching Station | CA | 66 | 5.5218 | 631.2243 | 4.6008 | 175.3153 | 1.944 | 7.3408 | 3.3527 | 11.6616 | 1.946 | 7.3626
GAYN | Gayndah | WB | 11 | 5.1048 | 97.2594 | 6.4502 | 40.9642 | 0.46623 | 1.2905 | 0.026439 | 0.52812 | 0.46487 | 1.2904
GAYN | Gayndah (Regulated) | WB | 66 | 1.3402 | 153.2046 | 0.87077 | 33.1807 | 15.7473 | 27.1174 | 27.5028 | 77.7886 | 15.6985 | 27.1161
GAYN | Gayndah (Unregulated) | WB | 66 | 1.3402 | 153.2046 | 0.87077 | 33.1807 | 15.7473 | 27.1174 | 27.5028 | 77.7886 | 15.6985 | 27.1161
GEOR | Georgetown | FN | 132 | 0.6715 | 153.525 | 0.87903 | 66.9907 | 48.1599 | 128.9207 | 5.3287 | 53.5866 | 46.3343 | 129.998
GEOR | Georgetown | FN | 22 | 1.2272 | 46.7635 | 1.4636 | 18.5898 | 1.9937 | 12.5922 | 0.0026787 | 7.8633 | 1.9355 | 12.6221
GEOR | Georgetown | FN | 6.6 | 8.2714 | 94.5547 | 0 | 0 | 0.12835 | 0.55242 | 116470583.9317 | 9.7992 | 0.12314 | 0.55509
GEOR | Georgetown | FN | 66 | 1.0491 | 119.9275 | 1.4724 | 56.1055 | 12.135 | 43.0642 | 0.4114 | 9.9523 | 11.6119 | 43.3336
GIRU | Giru (TF1) | NQ | 11 | 2.4772 | 47.197 | 2.7425 | 17.4173 | 0.841 | 2.6975 | 0.15803 | 2.0361 | 0.83615 | 2.6982
GIRU | Giru (TF1) | NQ | 11 | 2.4555 | 46.784 | 2.7179 | 17.261 | 0.87741 | 2.7121 | 0.19444 | 2.0507 | 0.87257 | 2.7128
GIRU | Giru | NQ | 66 | 1.227 | 140.2662 | 0.90964 | 34.6618 | 24.587 | 23.8115 | 31.4627 | 65.0561 | 24.4126 | 23.8349
GIVE | Givelda | WB | 11 | 4.6426 | 88.4526 | 5.0305 | 31.9482 | 0.15745 | 1.4984 | 0.049002 | 1.1545 | 0.15689 | 1.4999
GIVE | Givelda | WB | 66 | 3.2335 | 369.6331 | 2.3202 | 88.4113 | 3.9043 | 12.3781 | 7.2198 | 27.3012 | 3.8841 | 12.4326
GLEE | Glenelg | NQ | 33 | 0.15917 | 9.0975 | 0.15628 | 2.9776 | 23.9776 | 140.6548 | 15.6085 | 123.0127 | 23.9713 | 140.8692
GLEE | Glenelg | NQ | 66 | 0.58153 | 66.4776 | 0.37063 | 14.123 | 33.4763 | 70.5681 | 56.9055 | 180.3815 | 33.4509 | 71.4257
GLEL | Glenella | MK | 11 | 12.6532 | 241.0752 | 14.4345 | 91.6717 | 0.042854 | 0.55095 | 0.011223 | 0.34723 | 0.041503 | 0.55205
GLEL | Glenella (TF5) | MK | 33 | 4.7182 | 269.683 | 5.7435 | 109.4277 | 0.3408 | 4.4328 | 0.10523 | 2.0549 | 0.32864 | 4.4428
GLEL | Glenella (TF6) | MK | 33 | 4.7214 | 269.867 | 5.6891 | 108.3922 | 0.34079 | 4.4298 | 0.10622 | 2.1658 | 0.32863 | 4.4397
GLEL | Glenella | MK | 66 | 5.6528 | 646.205 | 5.8627 | 223.3998 | 1.1387 | 7.3338 | 0.71713 | 6.5595 | 1.0901 | 7.3736
GLEN | Glenden | MK | 11 | 4.0118 | 76.4343 | 4.4804 | 28.4542 | 0.39276 | 1.6992 | 0.0605 | 1.21 | 0.3928 | 1.6991
GLEN | Glenden | MK | 66 | 1.9719 | 225.4186 | 1.5641 | 59.6013 | 11.9613 | 17.6102 | 12.9978 | 36.3437 | 11.963 | 17.6073
GLFS | Gladstone Friend Street | CA | 11 | 18.0015 | 342.975 | 19.596 | 124.4513 | 0.036104 | 0.38648 | 0.016363 | 0.29279 | 0.036084 | 0.38674
GLFS | Gladstone Friend Street | CA | 66 | 12.1627 | 1390.3869 | 11.1153 | 423.551 | 0.71069 | 3.373 | 1.2396 | 4.2427 | 0.70995 | 3.3821
GLFS | Gladstone Friend Street | CA | 66 | 12.1627 | 1390.3869 | 11.1153 | 423.551 | 0.71069 | 3.373 | 1.2396 | 4.2427 | 0.70995 | 3.3821
GLNO | Gladstone North T074 (TF1) | CA | 11 | 21.6914 | 413.2764 | 0 | 0 | 0.025658 | 0.32111 | 135802465.6733 | 5.0553 | 0.025649 | 0.32134
GLNO | Gladstone North T074 (TF2) | CA | 11 | 21.5179 | 409.9705 | 0 | 0 | 0.025368 | 0.32374 | 135802465.5596 | -9.6543 | 0.025359 | 0.32397
GLNO | Gladstone North T074 (TF1) | CA | 132 | 27.7373 | 6341.5921 | 33.2392 | 2533.1638 | 0.13901 | 3.0199 | 0.055432 | 1.4893 | 0.13922 | 3.051
GLNO | Gladstone North T074 (TF2) | CA | 132 | 27.7373 | 6341.5921 | 33.2392 | 2533.1638 | 0.13901 | 3.0199 | 0.055432 | 1.4893 | 0.13922 | 3.051
GLNO | Gladstone North T074 | CA | 66 | 14.6478 | 1674.4681 | 17.5557 | 668.9618 | 0.26042 | 2.8504 | 0.063066 | 1.4313 | 0.26008 | 2.8585
GLSO | Gladstone South T152 (TF 1) | CA | 11 | 13.445 | 256.1611 | 14.1953 | 90.1521 | 0.026384 | 0.51905 | 0.017395 | 0.43661 | 0.026356 | 0.51932
GLSO | Gladstone South T152 (TF 2) | CA | 11 | 13.445 | 256.1611 | 14.1953 | 90.1521 | 0.026384 | 0.51905 | 0.017395 | 0.43661 | 0.026356 | 0.51932
GLSO | Gladstone South T152 | CA | 66 | 14.0442 | 1605.464 | 16.3697 | 623.7692 | 0.32359 | 2.9677 | 0.19188 | 1.6919 | 0.32261 | 2.9776
GOOB | Gooburrum | WB | 11 | 4.6988 | 89.524 | 5.4564 | 34.6525 | 0.51208 | 1.3977 | 0.07874 | 0.88432 | 0.51145 | 1.3998
GOOB | Gooburrum | WB | 3.3 | 6.7464 | 38.5607 | 7.1234 | 13.5719 | 0.039001 | 0.30858 | 1.3614e-10 | 0.26237 | 0.038944 | 0.30877
GOOB | Gooburrum | WB | 66 | 1.7352 | 198.355 | 1.2648 | 48.1959 | 15.6003 | 18.4826 | 20.756 | 47.8062 | 15.5774 | 18.5584
GOOT | Gootchie (TF1) | WB | 11 | 1.2434 | 23.6897 | 1.3074 | 8.3028 | 1.0352 | 5.5379 | 0.49496 | 4.7685 | 1.0342 | 5.5382
GOOT | Gootchie (TF2) | WB | 11 | 3.0686 | 58.4655 | 3.4708 | 22.0423 | 0.62942 | 2.1943 | 0.00013316 | 1.5247 | 0.6284 | 2.1946
GOOT | Gootchie | WB | 66 | 1.2419 | 141.9701 | 0.83272 | 31.7307 | 19.4475 | 27.6975 | 26.76 | 80.8103 | 19.411 | 27.7092
GORD | Gordonvale SS | FN | 22 | 4.0339 | 153.713 | 3.0686 | 38.977 | 1.7403 | 3.002 | 2.2867 | 6.4126 | 1.7391 | 3.0001
GRCR | Granite Creek T166 | CA | 132 | 2.4347 | 556.6377 | 2.312 | 176.2004 | 12.596 | 32.0729 | 4.6059 | 40.4882 | 12.5887 | 32.1012
GRCR | Granite Creek T166 | CA | 22 | 3.3075 | 126.0344 | 3.5612 | 45.2327 | 0.48377 | 4.1996 | 0.333 | 3.303 | 0.48357 | 4.2003
GRCR | Granite Creek T166 | CA | 66 | 1.9781 | 226.1325 | 2.3682 | 90.241 | 3.4918 | 20.9154 | 0.97774 | 10.6814 | 3.49 | 20.9225
GREN | Greenvale | NQ | 11 | 0.49467 | 9.4248 | 0.52119 | 3.31 | 2.4431 | 13.9389 | 1.1966 | 11.9661 | 2.4412 | 13.9424
GREN | Greenvale | NQ | 66 | 0.49997 | 57.1546 | 0.31448 | 11.9831 | 44.8722 | 71.0202 | 80.743 | 220.627 | 44.8052 | 71.1467
GUML | Gumlu (TF1) | NQ | 11 | 0.54984 | 10.4758 | 0.5635 | 3.5787 | 3.0517 | 12.3696 | 2.5335 | 11.5316 | 3.0484 | 12.3688
GUML | Gumlu (TF2) | NQ | 11 | 0.79201 | 15.0899 | 0.81907 | 5.2018 | 0.91658 | 8.7972 | 0.39847 | 7.9594 | 0.91323 | 8.7964
GUML | Gumlu (TF1) | NQ | 66 | 1.1849 | 135.4514 | 0.72572 | 27.6535 | 18.6567 | 30.1703 | 29.5583 | 100.0505 | 18.5363 | 30.1385
GUML | Gumlu (TF2) | NQ | 66 | 1.1849 | 135.4514 | 0.72572 | 27.6535 | 18.6567 | 30.1703 | 29.5583 | 100.0505 | 18.5363 | 30.1385
GUNP | Gunpowder (TF2) | NQ - MI | 11 | 16.5472 | 315.2657 | 0.009556 | 0.060689 | 0.031704 | 0.42099 | 0.027526 | 2192.3 | 0.028962 | 0.42575
GUNP | Gunpowder (TF1) | NQ - MI | 11 | 16.4932 | 314.2373 | 0.0095766 | 0.060819 | 0.031653 | 0.42238 | 0.027408 | 2187.6 | 0.028911 | 0.42714
GUNP | Gunpowder | NQ - MI | 220 | 1.2859 | 490.0082 | 1.7504 | 222.325 | 10.6483 | 108.1282 | 0.54814 | 20.4096 | 9.5516 | 110.0309
GUTH | Guthalungra | NQ | 11 | 0.39542 | 7.5338 | 0.40343 | 2.5621 | 1.4724 | 17.6545 | 0.83189 | 16.6314 | 1.4691 | 17.6536
GUTH | Guthalungra | NQ | 66 | 0.96726 | 110.5726 | 0.58947 | 22.462 | 23.0595 | 36.831 | 37.8062 | 123.1077 | 22.9391 | 36.7993
HAIS | Hayman Island | MK | 11 | 1.8628 | 35.4903 | 2.2884 | 14.5333 | 1.5584 | 3.4189 | 0.17532 | 1.7324 | 1.5564 | 3.4154
HAIS | Hayman Island | MK | 22 | 1.6045 | 61.1381 | 1.0039 | 12.7512 | 5.5324 | 6.7458 | 26.5679 | 4.8173 | 5.5244 | 6.7322
HAUG | Haughton (TF1) | NQ | 11 | 2.4697 | 47.0546 | 2.5957 | 16.4849 | 0.59202 | 2.7738 | 0.32346 | 2.3956 | 0.57999 | 2.7645
HAUG | Haughton (TF2) | NQ | 11 | 3.4697 | 66.1068 | 3.7221 | 23.6387 | 0.40023 | 1.9788 | 0.1406 | 1.6089 | 0.39713 | 1.9779
HAUG | Haughton | NQ | 66 | 2.5836 | 295.3451 | 1.7954 | 68.4142 | 9.3464 | 13.3143 | 13.912 | 35.636 | 9.2351 | 13.2826
HAVI | Havilah T184 | NQ | 11 | 7.8582 | 149.7193 | 5.5665 | 35.352 | 0.12198 | 0.88211 | 4.9091e-09 | 2 | 0.12209 | 0.88192
HAVI | Havilah T184 | NQ | 132 | 2.8155 | 643.7092 | 1.9115 | 145.6757 | 12.328 | 27.1585 | 23.6559 | 68.3437 | 12.3432 | 27.1305
HELE | Helenvale | FN | 22 | 1.0317 | 39.3115 | 1.2768 | 16.2178 | 2.0941 | 13.403 | 0.0053571 | 5.7799 | 1.9919 | 13.4452
HELE | Helenvale | FN | 66 | 0.90529 | 103.4882 | 0.60078 | 22.8928 | 12.7294 | 44.5966 | 27.8389 | 113.4382 | 11.8098 | 44.9764
HEPA | Hermit Park (TF1) | NQ | 11 | 7.6638 | 146.0151 | 7.9084 | 50.2249 | 0.058267 | 0.9127 | 0.035678 | 0.83061 | 0.057882 | 0.91241
HEPA | Hermit Park (TF2) | NQ | 11 | 7.6638 | 146.0151 | 7.9084 | 50.2249 | 0.058267 | 0.9127 | 0.035678 | 0.83061 | 0.057882 | 0.91241
HEPA | Hermit Park | NQ | 66 | 13.7204 | 1568.4576 | 11.6513 | 443.976 | 0.81321 | 2.9552 | 1.0675 | 4.5966 | 0.79934 | 2.9445
HIGH | Highfields (Unregulated) | SW | 0.415 | 23.4941 | 16.211 | 24.4214 | 5.6169 | 0.0010009 | 0.010239 | 0.0005 | 0.0091 | 0.001 | 0.0102
HIGH | Highfields | SW | 11 | 2.9784 | 56.7453 | 3.3861 | 21.5049 | 0.45883 | 2.302 | 0.075588 | 1.5099 | 0.45883 | 2.3017
HIGH | Highfields | SW | 33 | 2.6481 | 151.3609 | 0.97134 | 18.5064 | 3.4492 | 7.1296 | 6.195 | 49.1824 | 3.4492 | 7.1265
HILL | Hillsborough | NQ | 66 | 2.7987 | 319.9344 | 1.8924 | 72.1106 | 7.5113 | 13.0786 | 11.0502 | 35.2973 | 7.4325 | 13.0471
HOHI | Home Hill (TF1) | NQ | 11 | 10.8889 | 207.4609 | 11.2613 | 71.5192 | 0.1173 | 0.6321 | 0.0292 | 0.5842 | 0.1111 | 0.6303
HOHI | Home Hill (TF2) | NQ | 11 | 9.025 | 171.9496 | 9.8588 | 62.6212 | 0.1044 | 0.7689 | 0.0301 | 0.5801 | 0.1011 | 0.7683
HOHI | Home Hill | NQ | 66 | 5.7532 | 657.6783 | 4.2035 | 160.1745 | 2.6748 | 6.796 | 3.9486 | 14.9693 | 2.5557 | 6.7749
HOWA | Howard | WB | 11 | 4.6163 | 87.9518 | 5.1707 | 32.8382 | 0.1741 | 1.5089 | 0.0549 | 1.0223 | 0.1733 | 1.5089
HOWA | Howard | WB | 66 | 2.6049 | 297.7821 | 1.7215 | 65.5968 | 4.2909 | 15.57 | 7.9963 | 40.1351 | 4.2599 | 15.5689
HPCT | Hay Point | MK | 33 | 5.077 | 290.1903 | 3.7019 | 70.5298 | 1.2516 | 3.9384 | 1.963 | 8.5201 | 1.2509 | 3.9495
HUGH | Hughenden | NQ | 33 | 1.6998 | 97.1551 | 2.0583 | 39.2157 | 2.7334 | 13.5857 | 0.038682 | 2.6004 | 2.9147 | 14.5282
HUGH | Hughenden | NQ | 66 | 1.6813 | 192.2003 | 1.8852 | 71.8367 | 8.6836 | 25.5814 | 1.3599 | 13.2466 | 8.6583 | 26.439
ILBI | Ilbilbie | MK | 11 | 0.77949 | 14.8512 | 0.86056 | 5.4653 | 2.368 | 8.6526 | 0.64594 | 6.4594 | 2.3728 | 8.6645
ILBI | Ilbilbie | MK | 33 | 0.83591 | 47.7785 | 0.49191 | 9.3722 | 15.4981 | 19.7385 | 25.6682 | 75.1106 | 15.5421 | 19.8463
ILRE | Ilbilbie Regulator (Primary) | MK | 33 | 0.81854 | 46.7856 | 0.48146 | 9.173 | 15.7886 | 20.1875 | 26.3386 | 76.6924 | 15.8325 | 20.2953
ILRE | Ilbilbie Regulator (Secondary) | MK | 33 | 0.81854 | 46.7856 | 0.48146 | 9.173 | 15.7886 | 20.1875 | 26.3386 | 76.6924 | 15.8325 | 20.2953
INGH | Ingham T047 | NQ | 11 | 8.6585 | 164.967 | 9.6727 | 61.4298 | 0.060359 | 0.80623 | 0.028761 | 0.55093 | 0.058497 | 0.80975
INGH | Ingham T047 | NQ | 66 | 4.5353 | 518.457 | 5.0499 | 192.4289 | 1.1375 | 9.1909 | 0.53414 | 6.3013 | 1.0705 | 9.3174
INNI | Innisfail T050 | FN | 22 | 11.4539 | 436.4509 | 8.6612 | 110.0116 | 0.1383 | 1.2135 | 0.569 | 2.3315 | 0.1307 | 1.2292
ISIS | Isis T131 | WB | 132 | 7.0678 | 1615.9104 | 6.9973 | 533.2626 | 2.2074 | 11.675 | 1.7799 | 12.0542 | 2.1613 | 11.7133
ISIS | Isis T131 | WB | 66 | 7.8906 | 902.0129 | 9.1491 | 348.6268 | 0.7754 | 5.2693 | 0.3368 | 3.095 | 0.7459 | 5.2706
ISPL | Isaac Plains | MK | 66 | 2.8504 | 325.8409 | 2.3611 | 89.9696 | 4.4527 | 14.0314 | 7.5998 | 22.6376 | 4.4492 | 14.0325
JAND | Jandowae (TF1) | SW | 11 | 0.55019 | 10.4825 | 0.61793 | 3.9244 | 4.6847 | 11.8165 | 0.44354 | 8.8709 | 4.6819 | 11.8174
JAND | Jandowae (TF2) | SW | 11 | 1.0004 | 19.0606 | 1.3037 | 8.2796 | 4.3553 | 5.468 | 0.1142 | 2.5224 | 4.3526 | 5.4689
JAND | Jandowae | SW | 33 | 0.45145 | 25.8041 | 0.32854 | 6.2595 | 38.1702 | 26.5108 | 46.4419 | 94.0521 | 38.1452 | 26.5186
JARV | Jarvisfield (TF1) | NQ | 11 | 6.7958 | 129.4767 | 7.3074 | 46.408 | 0.1581 | 1.0181 | 0.0737 | 0.8118 | 0.1546 | 1.0179
JARV | Jarvisfield (TF2) | NQ | 11 | 6.7958 | 129.4767 | 7.3074 | 46.408 | 0.1581 | 1.0181 | 0.0737 | 0.8118 | 0.1546 | 1.0179
JARV | Jarvisfield | NQ | 66 | 5.2337 | 598.2886 | 3.976 | 151.5071 | 3.0407 | 7.4291 | 4.0194 | 15.2318 | 2.9129 | 7.4198
JUCR | Julia Creek | NQ | 33 | 0.4674 | 26.7156 | 0.55205 | 10.518 | 18.6978 | 44.8469 | 1.2816 | 19.3782 | 18.6915 | 45.0613
JUCR | Julia Creek | NQ | 66 | 0.29649 | 33.8937 | 0.31892 | 12.1526 | 72.3054 | 135.0562 | 10.9238 | 99.0112 | 72.2801 | 135.9139
JUPO | Jubilee Pocket | MK | 11 | 5.5379 | 105.511 | 6.5383 | 41.5235 | 0.28493 | 1.2313 | 0.022269 | 0.69804 | 0.28292 | 1.2279
JUPO | Jubilee Pocket | MK | 66 | 1.9624 | 224.3291 | 1.3739 | 52.3538 | 9.4557 | 19.1969 | 12.9073 | 47.7668 | 9.3834 | 19.0742
KAIM | Kaimkillenbun | SW | 11 | 0.72479 | 13.8091 | 0.77609 | 4.9288 | 2.3861 | 9.3476 | 0.28207 | 7.8518 | 2.3861 | 9.3477
KAIM | Kaimkillenbun | SW | 33 | 0.90286 | 51.6054 | 0.68316 | 13.0159 | 18.9364 | 13.4618 | 22.0284 | 43.0351 | 18.9364 | 13.4628
KALA | Kalamia | NQ | 11 | 7.8559 | 149.6741 | 7.3027 | 46.3786 | 0.15269 | 0.87716 | 0.072446 | 1.0923 | 0.10599 | 0.88432
KALA | Kalamia | NQ | 66 | 2.8435 | 325.0501 | 1.9891 | 75.7952 | 6.8177 | 13.1005 | 10.6951 | 32.2442 | 6.5939 | 13.2084
KAME | Kamerunga T053 | FN | 22 | 12.8838 | 490.9401 | 9.2037 | 116.9022 | 0.092992 | 1.0824 | 0.57342 | 2.3394 | 0.090855 | 1.0785
KEBE | Kewerra Beach | CA | 22 | 4.9361 | 188.0922 | 4.0339 | 51.2375 | 2.2683 | 1.7015 | 3.2937 | 3.4664 | 2.2662 | 1.6976
KECE | Kelsey Creek East (TF1) | MK | 11 | 5.5541 | 105.82 | 5.8706 | 37.2833 | 0.066795 | 1.2584 | 0.0070622 | 1.0602 | 0.065807 | 1.256
KECE | Kelsey Creek East (TF2) | MK | 11 | 9.4414 | 179.883 | 10.4072 | 66.0949 | 0.092211 | 0.73557 | 0.032638 | 0.53757 | 0.091223 | 0.73316
KECE | Kelsey Creek East (TF1) | MK | 66 | 5.6343 | 644.084 | 7.2023 | 274.4463 | 2.1504 | 7.1365 | 0.41312 | 2.6714 | 2.1148 | 7.0499
KECE | Kelsey Creek East (TF2) | MK | 66 | 5.6419 | 644.9564 | 7.2233 | 275.2433 | 2.1446 | 7.1277 | 0.40234 | 2.6426 | 2.109 | 7.0411
KEMM | Kemmis T067 | MK | 66 | 5.3259 | 608.8289 | 6.6953 | 255.1269 | 0.89813 | 7.8279 | 0.98783 | 2.927 | 0.89891 | 7.8426
KESP | Kearneys Spring T167 (TF1) | SW | 110 | 19.1999 | 3658.0798 | 17.2173 | 1093.4432 | 0.31324 | 3.6279 | 0.65226 | 4.9049 | 0.31296 | 3.5819
KESP | Kearneys Spring T167 (TF2) | SW | 110 | 19.1785 | 3653.9874 | 17.1821 | 1091.2129 | 0.31394 | 3.632 | 0.65478 | 4.9215 | 0.31366 | 3.586
KESP | Kearneys Spring T167 | SW | 11 | 18.5766 | 353.931 | 4.0751 | 25.8802 | 0.011697 | 0.37618 | 1.4224e-07 | 4.395 | 0.011695 | 0.37572
KIDS | Kidston T077 | FN | 132 | 0.8554 | 195.5618 | 1.2813 | 97.6469 | 34.3442 | 96.9387 | 0.1828 | 9.5025 | 32.7317 | 97.9891
KIDS | Kidston T077 | FN | 6.6 | 12.764 | 145.9125 | 0.0242 | 0.0921 | 0.0911 | 0.3323 | 569.999 | 0.0881 | 0.0871 | 0.335
KILK | Kilkivan T012 | WB | 132 | 7.9403 | 1815.3885 | 7.1574 | 545.4661 | 2.3207 | 10.3053 | 2.0187 | 13.878 | 2.3215 | 10.3281
KILK | Kilkivan T012 | WB | 66 | 1.6499 | 188.6118 | 2.1258 | 81.0028 | 1.5255 | 25.3722 | 0.074706 | 8.3386 | 1.5257 | 25.3779
KILL | Killarney (TF1) | SW | 11 | 1.3229 | 25.2047 | 1.611 | 10.2315 | 2.1957 | 4.8248 | 0.12954 | 2.5907 | 2.1916 | 4.8259
KILL | Killarney (TF2) | SW | 11 | 1.3229 | 25.2047 | 1.611 | 10.2315 | 2.1957 | 4.8248 | 0.12954 | 2.5907 | 2.1916 | 4.8259
KILL | Killarney | SW | 33 | 0.76815 | 43.9058 | 0.49279 | 9.3889 | 18.5954 | 20.1071 | 24.9182 | 71.6873 | 18.5583 | 20.1163
KING | Kingaroy | WB | 11 | 10.8081 | 205.9216 | 12.3629 | 78.5152 | 0.081873 | 0.64125 | 0.016867 | 0.40309 | 0.081914 | 0.64142
KING | Kingaroy | WB | 66 | 4.717 | 539.2285 | 2.9151 | 111.0813 | 2.3402 | 8.5736 | 4.5679 | 24.9843 | 2.3417 | 8.5798
KIRK | Kirknie | NQ | 11 | 5.1891 | 98.866 | 5.6231 | 35.7118 | 0.263 | 1.3243 | 0.051676 | 1.0447 | 0.25993 | 1.3232
KIRK | Kirknie | NQ | 66 | 3.3315 | 380.843 | 2.6169 | 99.7175 | 7.6077 | 10.067 | 10.3831 | 20.7871 | 7.4971 | 10.0276
KITO | Kilkivan Town (TF1) | WB | 11 | 0.72691 | 13.8494 | 0.76539 | 4.8609 | 1.6385 | 9.4752 | 1.4595 | 8.0275 | 1.6385 | 9.4753
KITO | Kilkivan Town (TF1) | WB | 11 | 0.7178 | 13.6759 | 0.75863 | 4.818 | 1.6385 | 9.5989 | 1.4595 | 8.0275 | 1.6385 | 9.5991
KITO | Kilkivan Town | WB | 66 | 1.6105 | 184.1019 | 2.0263 | 77.2111 | 1.9194 | 25.9698 | 0.79917 | 9.9583 | 1.9196 | 25.9755
KOCR | Kogan Creek | SW | 11 | 1.9142 | 36.4709 | 2.1695 | 13.7779 | 0.78761 | 3.5676 | 0.11929 | 2.3858 | 0.78484 | 3.5684
KOCR | Kogan Creek | SW | 33 | 1.717 | 98.1414 | 1.1076 | 21.1033 | 6.0149 | 10.6362 | 8.269 | 31.8051 | 5.9899 | 10.644
KOGA | Kogan Regulator (Regulated) | SW | 33 | 1.1032 | 63.0556 | 0.91964 | 17.5215 | 8.5244 | 16.997 | 7.8328 | 29.7376 | 8.5244 | 16.9979
KOGA | Kogan Regulator (Unregulated) | SW | 33 | 1.1826 | 67.5973 | 0.9684 | 18.4505 | 8.4542 | 15.5928 | 7.9299 | 28.8508 | 8.4542 | 15.5938
KOUM | Koumala (1 Regulator) | MK | 11 | 1.8424 | 35.1027 | 2.1778 | 13.8312 | 1.3863 | 3.5331 | 0.20603 | 2.0815 | 1.3912 | 3.5451
KOUM | Koumala (2 Regulator) | MK | 11 | 1.8424 | 35.1027 | 2.1778 | 13.8312 | 1.3863 | 3.5331 | 0.20603 | 2.0815 | 1.3912 | 3.5451
KOUM | Koumala | MK | 33 | 1.2458 | 71.2095 | 0.75316 | 14.3497 | 10.6228 | 13.0645 | 15.9442 | 48.5765 | 10.6667 | 13.1723
KUNW | Kunwarara | CA | 11 | 3.7159 | 70.7966 | 4.4256 | 28.1065 | 0.49118 | 1.8155 | 0.013414 | 0.99995 | 0.49124 | 1.8161
KUNW | Kunwarara | CA | 66 | 1.2323 | 140.8746 | 0.76878 | 29.2946 | 17.1997 | 29.359 | 25.9598 | 93.3477 | 17.2018 | 29.3808
LACR | Lakes Creek | CA | 11 | 16.6519 | 317.2604 | 18.9048 | 120.0618 | 0.061206 | 0.4152 | 0.017172 | 0.26918 | 0.061263 | 0.41581
LACR | Lakes Creek | CA | 66 | 7.4453 | 851.1068 | 6.1489 | 234.3053 | 1.5852 | 5.4043 | 2.291 | 8.8846 | 1.5873 | 5.426
LAKE | Lakeland | FN | 132 | 0.9063 | 207.2078 | 0.89979 | 68.5736 | 23.485 | 89.6324 | 22.134 | 91.695 | 22.4336 | 90.2865
LAKE | Lakeland | FN | 22 | 1.6951 | 64.5905 | 2.1138 | 26.8489 | 0.89357 | 8.2082 | 1.0472e-08 | 3.3523 | 0.87328 | 8.2262
LAKE | Lakeland (TF1) | FN | 66 | 1.4168 | 161.9665 | 1.3527 | 51.545 | 5.7009 | 29.0838 | 8.6396 | 32.7192 | 5.2074 | 29.2527
LAKE | Lakeland (TF2) | FN | 66 | 1.4168 | 161.9665 | 1.3527 | 51.545 | 5.7009 | 29.0838 | 8.6396 | 32.7192 | 5.2074 | 29.2527
LANN | Lannercost | NQ | 11 | 3.5497 | 67.6311 | 3.9277 | 24.9442 | 0.41305 | 1.9283 | 0.1038 | 1.4075 | 0.41119 | 1.9319
LANN | Lannercost | NQ | 66 | 1.9261 | 220.1779 | 1.4745 | 56.1868 | 11.133 | 18.7512 | 14.1234 | 39.7561 | 11.066 | 18.8777
LAQU | Laguna Quays (TF1) | MK | 11 | 3.282 | 62.5312 | 3.6835 | 23.3936 | 0.54822 | 2.0609 | 0.073037 | 1.4609 | 0.54723 | 2.0585
LAQU | Laguna Quays (TF1) | MK | 11 | 3.2825 | 62.5402 | 3.6839 | 23.396 | 0.54796 | 2.0606 | 0.073001 | 1.4609 | 0.54697 | 2.0582
LAQU | Laguna Quays (TF1) | MK | 66 | 1.5241 | 174.2265 | 1.1301 | 43.0629 | 17.1066 | 21.6007 | 20.505 | 54.0532 | 17.0711 | 21.5141
LAQU | Laguna Quays (TF2) | MK | 66 | 1.5248 | 174.303 | 1.1307 | 43.0849 | 17.0985 | 21.5918 | 20.4937 | 54.0213 | 17.0629 | 21.5052
LARO | Landing Road | CA | 11 | 6.0235 | 114.7628 | 6.2783 | 39.8725 | 0.070735 | 1.1579 | 0.057765 | 1.0169 | 0.070505 | 1.158
LARO | Landing Road | CA | 66 | 8.2253 | 940.2837 | 7.7718 | 296.1448 | 0.46693 | 5.0757 | 0.91477 | 5.9219 | 0.45865 | 5.0804
LEIC | Leichhardt | CA | 66 | 3.1988 | 365.6761 | 2.3443 | 89.3301 | 5.6018 | 11.8672 | 8.8114 | 26.1645 | 5.6118 | 11.8166
LILY | Lilyvale | CA | 66 | 14.5588 | 1664.2995 | 17.0732 | 650.5771 | 0.3692 | 2.859 | 0.1087 | 1.6435 | 0.3394 | 2.8269
LITT | Littlemore | CA | 11 | 1.554 | 29.6067 | 1.7008 | 10.8015 | 1.202 | 4.333 | 0.49233 | 3.3128 | 1.2019 | 4.3335
LITT | Littlemore | CA | 66 | 0.9371 | 107.1247 | 0.57704 | 21.9882 | 25.5476 | 36.7282 | 39.7811 | 124.6317 | 25.5459 | 36.7465
LOCR | Louisa Creek | MK | 11 | 3.1352 | 59.7345 | 3.2548 | 20.671 | 0.15366 | 2.2253 | 0.099226 | 1.982 | 0.15359 | 2.2266
LOCR | Louisa Creek (TF1) | MK | 132 | 3.8943 | 890.3647 | 4.384 | 334.1029 | 4.3899 | 21.0982 | 2.1573 | 14.014 | 4.3786 | 21.2752
LOCR | Louisa Creek (TF2) | MK | 132 | 3.8943 | 890.3647 | 4.384 | 334.1029 | 4.3899 | 21.0982 | 2.1573 | 14.014 | 4.3786 | 21.2752
LOCR | Louisa Creek | MK | 33 | 9.4538 | 540.3562 | 10.2723 | 195.7138 | 0.28142 | 2.2014 | 0.11362 | 1.6769 | 0.28071 | 2.2124
LONG | Longreach | CA | 22 | 1.7104 | 65.1752 | 2.3198 | 29.4655 | 2.1026 | 8.4302 | 0.15016 | 1.9454 | 2.0214 | 8.6057
LONG | Longreach | CA | 66 | 0.73144 | 83.6154 | 0.60686 | 23.1245 | 17.5717 | 58.3634 | 48.8081 | 88.7202 | 16.8409 | 59.9425
LUCI | Lucinda | NQ | 11 | 2.2116 | 42.1372 | 2.3528 | 14.9424 | 0.50616 | 3.1235 | 0.20141 | 2.5829 | 0.5115 | 3.1357
LUCI | Lucinda | NQ | 66 | 1.8795 | 214.8545 | 1.2484 | 47.5709 | 10.971 | 19.4609 | 20.9091 | 51.9307 | 11.1633 | 19.9002
LYLA | Lyndley Lane | SW | 22 | 0.14443 | 5.5034 | 0.14811 | 1.8812 | 8.935 | 96.4152 | 4.4749 | 89.4979 | 8.935 | 96.4156
LYLA | Lyndley Lane | SW | 33 | 1.1327 | 64.7448 | 0.68582 | 13.0667 | 10.0353 | 15.5639 | 15.079 | 53.6136 | 10.0353 | 15.5648
MACI | Maryborough City | WB | 11 | 10.7694 | 205.1838 | 11.9982 | 76.1986 | 0.063337 | 0.64737 | 0.023248 | 0.44753 | 0.062321 | 0.6477
MACI | Maryborough City | WB | 66 | 5.7281 | 654.8064 | 5.5694 | 212.2208 | 1.4432 | 7.1943 | 1.6001 | 7.7642 | 1.4066 | 7.206
MACK | Mackay T038 | MK | 33 | 14.3218 | 818.6009 | 19.5003 | 371.5312 | 0.20754 | 1.4501 | 0.040742 | 0.28883 | 0.20541 | 1.457
MACN | Macknade | NQ | 11 | 8.611 | 164.0613 | 6.7736 | 43.018 | 0.0997 | 0.8058 | 0.1188 | 1.1879 | 0.15 | 1.0814
MACN | Macknade | NQ | 66 | 2.547 | 291.1613 | 1.7884 | 68.1457 | 6.0265 | 15.3375 | 13.1078 | 34.0729 | 6.5659 | 16.1676
MACT | Mackay City | MK | 11 | 13.4596 | 256.4402 | 15.0515 | 95.5898 | 0.045351 | 0.5176 | 0.012463 | 0.35428 | 0.045114 | 0.51836
MACT | Mackay City | MK | 33 | 13.3727 | 764.3551 | 17.8565 | 340.2114 | 0.29599 | 1.5407 | 0.15485 | 0.35736 | 0.29385 | 1.5476
MAFU | Max Fulton (TF1) | NQ | 11 | 9.6238 | 183.3571 | 10.1046 | 64.173 | 0.050749 | 0.72649 | 0.022662 | 0.62547 | 0.050356 | 0.72608
MAFU | Max Fulton (TF2) | NQ | 11 | 9.6165 | 183.2194 | 10.0839 | 64.0413 | 0.049491 | 0.72713 | 0.02267 | 0.62864 | 0.049098 | 0.72671
MAFU | Max Fulton (TF1) | NQ | 66 | 11.1405 | 1273.53 | 10.1618 | 387.2169 | 1.0111 | 3.6367 | 1.0048 | 4.7905 | 0.99699 | 3.6218
MAFU | Max Fulton (TF2) | NQ | 66 | 11.4188 | 1305.3452 | 10.5884 | 403.4736 | 0.96628 | 3.5536 | 0.88792 | 4.4922 | 0.95214 | 3.5387
MAKA | Mary Kathleen | NQ - MI | 11 | 0.27606 | 5.2597 | 0.28781 | 1.8278 | 3.4613 | 25.0677 | 2.512 | 22.0658 | 3.4586 | 25.0724
MAKA | Mary Kathleen | NQ - MI | 66 | 0.36981 | 42.2753 | 0.317 | 12.0795 | 34.177 | 108.0671 | 43.8158 | 164.2072 | 34.0783 | 108.2384
MALC | Malchi | CA | 11 | 8.7034 | 165.8229 | 10.0787 | 64.008 | 0.15698 | 0.78748 | 0.030848 | 0.47588 | 0.15703 | 0.78808
MALC | Malchi | CA | 66 | 3.4649 | 396.0927 | 2.4683 | 94.0554 | 4.5407 | 11.2176 | 7.5504 | 25.7158 | 4.5427 | 11.2394
MARE | Mareeba (TF1) | FN | 22 | 6.0013 | 228.6792 | 7.1136 | 90.355 | 0.30469 | 2.3116 | 0.052119 | 1.2268 | 0.29818 | 2.3273
MARE | Mareeba (TF2) | FN | 22 | 6.0013 | 228.6792 | 7.1136 | 90.355 | 0.30469 | 2.3116 | 0.052119 | 1.2268 | 0.29818 | 2.3273
MARE | Mareeba (TF1) | FN | 66 | 3.6487 | 417.0995 | 3.3041 | 125.9034 | 3.3009 | 11.0211 | 4.1886 | 14.3957 | 3.2424 | 11.1626
MARE | Mareeba (TF2) | FN | 66 | 3.7017 | 423.1655 | 3.3588 | 127.987 | 2.9375 | 10.9528 | 3.4239 | 14.2972 | 2.879 | 11.0944
MARY | Maryborough T059 | WB | 132 | 5.012 | 1145.8985 | 5.5861 | 425.7207 | 3.4126 | 16.4115 | 0.81334 | 11.5622 | 3.3331 | 16.4548
MARY | Maryborough T059 | WB | 66 | 7.3633 | 841.7365 | 9.2058 | 350.7874 | 0.86201 | 5.6426 | 0.12419 | 2.2592 | 0.82545 | 5.6543
MASO | Marian South | MK | 11 | 10.7605 | 205.0154 | 8.2304 | 52.27 | 0.10863 | 0.64037 | 0.059667 | 1.1931 | 0.08747 | 0.70138
MASO | Marian South | MK | 66 | 4.2998 | 491.5361 | 3.1278 | 119.1845 | 3.3409 | 9.1675 | 5.8803 | 19.7845 | 3.3443 | 9.2805
MCCR | McKinley Creek (TF1) | MK | 11 | 3.1143 | 59.3353 | 3.2925 | 20.9101 | 0.22586 | 2.234 | 0.083296 | 1.8807 | 0.22523 | 2.2351
MCCR | McKinley Creek (TF1) | MK | 11 | 3.1362 | 59.7529 | 3.317 | 21.066 | 0.2259 | 2.2182 | 0.083338 | 1.865 | 0.22527 | 2.2193
MCCR | McKinley Creek | MK | 66 | 3.0592 | 349.7189 | 2.2464 | 85.5992 | 5.1323 | 12.7184 | 10.6831 | 26.509 | 5.1095 | 12.7577
MEAD | Meadowvale | WB | 11 | 5.1274 | 97.6909 | 5.6459 | 35.8565 | 0.19173 | 1.3506 | 0.048932 | 0.98581 | 0.1911 | 1.3527
MEAD | Meadowvale | WB | 66 | 2.9759 | 340.186 | 2.114 | 80.556 | 5.1408 | 13.1321 | 8.2188 | 30.2367 | 5.1179 | 13.208
MEAN | Meandarra | SW | 22 | 0.2691 | 10.254 | 0.31401 | 3.9885 | 14.1048 | 49.9753 | 1.5099 | 30.1973 | 14.1049 | 49.9762
MEAN | Meandarra | SW | 33 | 0.3973 | 22.7085 | 0.22846 | 4.3528 | 28.3385 | 44.5004 | 45.4959 | 166.5632 | 28.3387 | 44.5025
MELR | Melrose | WB | 11 | 2.9607 | 56.4091 | 3.3411 | 21.2187 | 0.493 | 2.3078 | 0.19623 | 1.5453 | 0.49304 | 2.308
MELR | Melrose | WB | 66 | 1.4232 | 162.693 | 0.80197 | 30.5593 | 10.6837 | 27.4502 | 20.1458 | 96.3137 | 10.6851 | 27.4564
MEMO | Memooloo T236 | CA | 132 | 1.9575 | 447.5509 | 1.7755 | 135.3142 | 9.6552 | 41.7823 | 7.3005 | 55.813 | 9.651 | 41.7267
MERI | Merinda | NQ | 11 | 6.7638 | 128.8678 | 7.5057 | 47.6678 | 0.1009 | 1.0299 | 0.036578 | 0.7288 | 0.10101 | 1.0293
MERI | Merinda | NQ | 66 | 3.8303 | 437.8579 | 5.0342 | 191.8282 | 2.3153 | 10.7174 | 0.32175 | 3.1252 | 2.3191 | 10.6934
MERN | Meringandan (TF1) | SW | 11 | 3.1413 | 59.8489 | 3.5841 | 22.7618 | 0.26751 | 2.2096 | 0.0701 | 1.402 | 0.26751 | 2.2091
MERN | Meringandan (TF3) | SW | 11 | 3.1464 | 59.9479 | 3.5908 | 22.8049 | 0.26733 | 2.2059 | 0.069916 | 1.3983 | 0.26733 | 2.2054
MERN | Meringandan (Highfields) | SW | 33 | 2.8032 | 160.226 | 0.88071 | 16.7798 | 1.7767 | 7.2683 | 58.3593 | 21.1217 | 1.7767 | 7.2642
MERN | Meringandan (T116) | SW | 33 | 2.8032 | 160.226 | 0.88071 | 16.7798 | 1.7767 | 7.2683 | 58.3593 | 21.1217 | 1.7767 | 7.2642
MICB | Mica Creek B Yard | NQ - MI | 132 | 7.9766 | 1823.6861 | 10.3121 | 785.8841 | 0.65605 | 10.4892 | 0.15319 | 2.7014 | 0.26125 | 11.1742
MICC | Mica Creek C Yard (TF1) | NQ - MI | 132 | 7.9223 | 1811.2888 | 10.1699 | 775.0522 | 0.66755 | 10.5606 | 0.19167 | 2.8972 | 0.27274 | 11.2455
MICC | Mica Creek C Yard (TF2) | NQ - MI | 132 | 7.9268 | 1812.3028 | 10.1814 | 775.928 | 0.6666 | 10.5547 | 0.18856 | 2.8812 | 0.2718 | 11.2397
MICC | Mica Creek C Yard | NQ - MI | 220 | 2.574 | 980.8399 | 3.4547 | 438.8107 | 2.4985 | 54.2225 | 0.35525 | 10.9056 | 1.4018 | 56.1252
MICO | Miles-Condamine | SW | 22 | 0.37125 | 14.1467 | 0.39599 | 5.0297 | 4.6075 | 37.3558 | 1.5301 | 30.6029 | 4.6075 | 37.3567
MICO | Miles-Condamine | SW | 33 | 1.2553 | 71.7515 | 0.8039 | 15.3163 | 6.9239 | 15.1938 | 11.8869 | 43.4749 | 6.9241 | 15.1959
MIDD | Middlemount | CA | 22 | 2.4851 | 94.6968 | 2.9243 | 37.144 | 1.4352 | 5.4513 | 0.26644 | 3.103 | 1.4101 | 5.4765
MIDD | Middlemount | CA | 66 | 1.7802 | 203.5077 | 0.95942 | 36.5587 | 10.5187 | 21.1346 | 22.993 | 81.4054 | 10.2926 | 21.3613
MILC | Millchester T095 (TF3) | NQ | 11 | 5.128 | 97.7006 | 5.5223 | 35.0716 | 0.18713 | 1.3732 | 0.059351 | 1.0501 | 0.18546 | 1.3728
MILC | Millchester T095 | NQ | 132 | 2.2691 | 518.7866 | 2.13 | 162.3283 | 14.6787 | 34.335 | 4.166 | 45.2925 | 14.5847 | 34.3107
MILC | Millchester T095 | NQ | 66 | 3.4086 | 389.6578 | 4.1159 | 156.8375 | 4.6001 | 11.6333 | 0.4602 | 5.9683 | 4.54 | 11.6181
MILE | Miles | SW | 11 | 2.8951 | 55.1597 | 3.3355 | 21.1832 | 0.32876 | 2.3908 | 0.11127 | 1.455 | 0.32879 | 2.391
MILE | Miles (Columboola) | SW | 33 | 2.4241 | 138.5537 | 1.9065 | 36.3246 | 1.9575 | 8.4223 | 4.06 | 15.1559 | 1.9576 | 8.4244
MILE | Miles (Rywung) | SW | 33 | 2.4241 | 138.5537 | 1.9065 | 36.3246 | 1.9575 | 8.4223 | 4.06 | 15.1559 | 1.9576 | 8.4244
MILL | Millaroo | NQ | 11 | 2.9515 | 56.2333 | 3.2312 | 20.521 | 0.56381 | 2.3059 | 0.088896 | 1.7779 | 0.56073 | 2.3048
MILL | Millaroo | NQ | 66 | 1.6443 | 187.9712 | 1.2496 | 47.6149 | 17.0968 | 19.0078 | 25.467 | 43.4682 | 16.9862 | 18.9684
MILM | Millmerran Town | SW | 11 | 1.6833 | 32.0712 | 2.1773 | 13.8279 | 1.5675 | 3.8558 | 0.07056 | 1.4112 | 1.5558 | 3.8495
MILM | Millmerran Town | SW | 33 | 0.81473 | 46.568 | 0.3169 | 6.0377 | 13.4723 | 22.0017 | 14.3154 | 150.8644 | 13.367 | 21.9444
MILN | Millennium Substation | MK | 11 | 5.2349 | 99.7384 | 0.0097126 | 0.061684 | 0.10678 | 1.3316 | 2160.0511 | 1.0341 | 0.10668 | 1.3317
MILN | Millennium Substation | MK | 66 | 3.8515 | 440.2892 | 3.5635 | 135.7882 | 1.9828 | 10.7125 | 2.4976 | 13.3063 | 1.9793 | 10.7135
MING | Mingela | NQ | 11 | 0.30839 | 5.8757 | 0.30892 | 1.9619 | 3.019 | 22.7345 | 2.5608 | 22.2097 | 3.018 | 22.734
MING | Mingela | NQ | 66 | 1.692 | 193.4199 | 1.2281 | 46.7979 | 16.4965 | 18.8921 | 20.2498 | 50.3809 | 16.4613 | 18.877
MIRA | Mirani (Reg 1) | MK | 11 | 3.443 | 65.5986 | 3.6761 | 23.3465 | 0.29566 | 2.0093 | 0.12364 | 1.641 | 0.29546 | 2.0118
MIRA | Mirani (Reg 2) | MK | 11 | 3.443 | 65.5986 | 3.6761 | 23.3465 | 0.29566 | 2.0093 | 0.12364 | 1.641 | 0.29546 | 2.0118
MIRA | Mirani (Unregulated) | MK | 11 | 3.7814 | 72.0454 | 4.063 | 25.8033 | 0.24525 | 1.8329 | 0.073231 | 1.4646 | 0.24506 | 1.8353
MIRA | Mirani | MK | 66 | 2.8674 | 327.7849 | 1.9433 | 74.0491 | 6.1927 | 13.2568 | 9.8619 | 34.2358 | 6.1857 | 13.3455
MITC | Mitchell | SW | 11 | 0.74544 | 14.2025 | 0.98405 | 6.2495 | 5.0551 | 7.8918 | 0.14423 | 2.8845 | 5.0521 | 7.8927
MITC | Mitchell | SW | 33 | 0.33204 | 18.9785 | 0.23988 | 4.5704 | 44.1979 | 45.0651 | 42.6803 | 136.8569 | 44.1712 | 45.0737
MIVA | Miriam Vale | CA | 22 | 1.1941 | 45.5001 | 1.457 | 18.5069 | 4.4531 | 10.8236 | 0.3761 | 5.5852 | 4.4529 | 10.8256
MIVA | Miriam Vale | CA | 66 | 0.70178 | 80.2247 | 0.44119 | 16.8115 | 36.6928 | 47.1451 | 55.0342 | 160.1971 | 36.6911 | 47.1634
MOBA | Mt Bassett (TF1) | MK | 11 | 5.4862 | 104.526 | 5.9376 | 37.709 | 0.14801 | 1.2661 | 0.049198 | 0.98396 | 0.14778 | 1.2669
MOBA | Mt Bassett (TF2) | MK | 11 | 5.4862 | 104.526 | 5.9376 | 37.709 | 0.14801 | 1.2661 | 0.049198 | 0.98396 | 0.14778 | 1.2669
MOBA | Mt Bassett | MK | 33 | 7.7977 | 445.6996 | 6.3573 | 121.1223 | 0.88935 | 2.5393 | 1.2508 | 4.342 | 0.88721 | 2.5462
MODA | Monduran Dam | WB | 11 | 1.4295 | 27.2364 | 1.5106 | 9.5933 | 0.58484 | 4.8578 | 2.2976e-09 | 4.1163 | 0.58428 | 4.8593
MODA | Monduran Dam | WB | 3.3 | 5.8392 | 33.3757 | 6.2563 | 11.9199 | 0.051727 | 0.35562 | 5.9233e-10 | 0.28888 | 0.051677 | 0.35575
MODA | Monduran Dam | WB | 66 | 1.2426 | 142.0443 | 0.84641 | 32.2524 | 20.6909 | 26.6952 | 28.1998 | 77.9322 | 20.6708 | 26.7497
MOFO | Mt Fox | NQ | 33 | 0.17969 | 10.2706 | 0.18461 | 3.5173 | 10.7034 | 116.3832 | 5.4868 | 107.5407 | 10.6867 | 116.4148
MOFO | Mt Fox | NQ | 66 | 1.0228 | 116.9198 | 0.68632 | 26.1522 | 20.8665 | 35.3698 | 34.0889 | 96.4442 | 20.7995 | 35.4963
MOGA | Mt Garnet | FN | 22 | 1.3218 | 50.3682 | 1.6821 | 21.3657 | 3.8499 | 9.8608 | 0.44582 | 3.8584 | 3.8434 | 9.8765
MOGA | Mt Garnet | FN | 66 | 0.67591 | 77.2673 | 0.42049 | 16.0228 | 30.637 | 54.0214 | 49.1018 | 170.3082 | 30.5785 | 54.163
MOLE | Mt Leyshon | NQ | 11 | 4.0847 | 77.8239 | 4.6222 | 29.3547 | 0.34658 | 1.705 | 0.028526 | 1.0979 | 0.34491 | 1.7046
MOLE | Mt Leyshon | NQ | 66 | 1.7282 | 197.5619 | 1.3557 | 51.6584 | 11.4499 | 21.8558 | 11.0103 | 43.3301 | 11.3899 | 21.8406
MOMG | Mt Morgan | CA | 11 | 5.5575 | 105.8845 | 6.4452 | 40.9325 | 0.38477 | 1.1972 | 0.072579 | 0.74702 | 0.38483 | 1.1978
MOMG | Mt Morgan | CA | 66 | 2.1262 | 243.0565 | 1.4947 | 56.9558 | 11.2379 | 16.2063 | 16.9436 | 41.9223 | 11.24 | 16.2281
MOMO | Mt Molloy (TF2) | FN | 22 | 0.553 | 21.0722 | 0.57863 | 7.3496 | 4.1956 | 24.9523 | 2.1291 | 21.8742 | 4.1891 | 24.968
MOMO | Mt Molloy | FN | 66 | 1.258 | 143.8133 | 0.87564 | 33.3663 | 18.5987 | 27.7029 | 25.9343 | 73.7323 | 18.5402 | 27.8445
MOMO | Mt Molloy (TF1) | FN | 22 | 2.0989 | 79.9782 | 2.5538 | 32.4378 | 2.2655 | 6.2698 | 0.199 | 3.1917 | 2.259 | 6.2856
MOMW | Mt Mowbullan | SW | 11 | 0.62911 | 11.9862 | 0.71871 | 4.5644 | 4.6241 | 10.107 | 0.36689 | 7.3378 | 4.6241 | 10.1071
MOMW | Mt Mowbullan | SW | 33 | 0.45894 | 26.2318 | 0.34128 | 6.5022 | 38.3147 | 24.9232 | 45.9441 | 87.8686 | 38.3146 | 24.9241
MONT | Monto | CA | 11 | 2.8654 | 54.593 | 3.8188 | 24.2527 | 1.3495 | 2.0314 | 0.057037 | 0.68448 | 1.3495 | 2.0319
MONT | Monto | CA | 66 | 0.62661 | 71.6307 | 0.4321 | 16.4652 | 46.5291 | 48.0889 | 64.8945 | 148.3282 | 46.5287 | 48.1068
MOOE | Moore | WB | 11 | 3.279 | 62.4737 | 3.6051 | 22.8954 | 0.47272 | 2.0777 | 0.19623 | 1.5453 | 0.47276 | 2.0779
MOOE | Moore | WB | 66 | 1.9411 | 221.8995 | 1.1694 | 44.5618 | 9.9535 | 19.1661 | 15.9716 | 63.039 | 9.955 | 19.1723
MOOR | Moorvale | MK | 11 | 4.8705 | 92.7949 | 5.3522 | 33.9908 | 0.15809 | 1.4271 | 0.069875 | 1.0469 | 0.15799 | 1.4272
MOOR | Moorvale | MK | 66 | 2.9861 | 341.3561 | 2.3734 | 90.4373 | 3.1758 | 13.6883 | 4.2765 | 24.5909 | 3.1722 | 13.6894
MOPA | Mona Park (TF1) | NQ | 11 | 3.039 | 57.9014 | 3.1509 | 20.0112 | 0.26498 | 2.2891 | 0.17317 | 2.0513 | 0.2616 | 2.2885
MOPA | Mona Park (TF2) | NQ | 11 | 2.9563 | 56.3257 | 3.0627 | 19.4506 | 0.31584 | 2.3477 | 0.22403 | 2.1099 | 0.31246 | 2.3471
MOPA | Mona Park | NQ | 66 | 4.5788 | 523.4315 | 3.2657 | 124.4407 | 3.3052 | 8.5608 | 4.8283 | 19.7904 | 3.1836 | 8.5409
MORA | Moranbah T034 (TF1) | MK | 11 | 17.5861 | 335.0599 | 0.804 | 5.1063 | 0.0294 | 0.3964 | 5.4658e-06 | 25.29 | 0.0279 | 0.3964
MORA | Moranbah T034 (TF3) | MK | 11 | 24.4174 | 465.2141 | 0.9867 | 6.2663 | 0.0259 | 0.2851 | 13.9625 | 15.4114 | 0.0213 | 0.285
MORA | Moranbah T034 | MK | 66 | 13.7865 | 1576.0048 | 16.1078 | 613.7911 | 0.5154 | 2.9982 | 0.1663 | 1.7272 | 0.4699 | 3.0011
MORO | Mt Rooper | MK | 11 | 3.2539 | 61.9955 | 3.6187 | 22.9817 | 0.38136 | 2.1168 | 0.075667 | 1.5124 | 0.37935 | 2.1134
MORO | Mt Rooper | MK | 66 | 1.7204 | 196.6705 | 1.174 | 44.7372 | 11.0079 | 21.7857 | 15.4001 | 57.1663 | 10.9356 | 21.663
MORW | Mt Rawdon | WB | 66 | 1.0235 | 117.0041 | 0.62838 | 23.9444 | 19.178 | 36.3077 | 34.4227 | 114.0775 | 19.1352 | 36.306
MOSI | Mt Sibley (TF1) | SW | 11 | 2.2967 | 43.7585 | 2.7729 | 17.6103 | 0.87816 | 2.9147 | 0.075493 | 1.5099 | 0.87816 | 2.9143
MOSI | Mt Sibley (TF3) | SW | 11 | 2.2967 | 43.7585 | 2.7729 | 17.6103 | 0.87816 | 2.9147 | 0.075493 | 1.5099 | 0.87816 | 2.9143
MOSI | Mt Sibley | SW | 33 | 1.4404 | 82.3286 | 0.58024 | 11.0551 | 7.224 | 12.6437 | 66.5811 | 46.7865 | 7.224 | 12.6396
MOSS | Mossman (TF2) | FN | 22 | 1.5491 | 59.0269 | 1.88 | 23.8788 | 2.9725 | 8.5298 | 0.20518 | 4.3961 | 2.966 | 8.5455
MOSS | Mossman | FN | 66 | 0.93762 | 107.1847 | 0.62331 | 23.7514 | 24.9054 | 37.2028 | 35.694 | 108.5744 | 24.8469 | 37.3444
MOTY | Mt Tyson | SW | 33 | 1.1525 | 65.8718 | 0.8102 | 15.4364 | 12.4584 | 13.3202 | 15.9676 | 39.7656 | 12.3531 | 13.2628
MOUR | Moura T027 (TF1) | CA | 11 | 14.9312 | 284.478 | 12.7455 | 80.9447 | 0.05384 | 0.46496 | 0.0013925 | 0.70867 | 0.053922 | 0.46774
MOUR | Moura T027 (TF2) | CA | 11 | 14.8867 | 283.6296 | 12.7183 | 80.7723 | 0.053853 | 0.46637 | 0.0013937 | 0.70937 | 0.053933 | 0.46915
MOUR | Moura T027 | CA | 22 | 5.1306 | 195.5036 | 4.7672 | 60.551 | 0.29976 | 2.7078 | 0.0025289 | 3.3488 | 0.30009 | 2.7189
MOUR | Moura T027 | CA | 66 | 5.8659 | 670.5642 | 7.2708 | 277.0534 | 1.5137 | 6.9864 | 0.12802 | 2.9395 | 1.5185 | 7.0849
MUCK | Muckadilla Regulator (Regulated) | SW | 33 | 0.59051 | 33.7524 | 0.46965 | 8.948 | 24.6868 | 25.5004 | 16.6638 | 65.4653 | 24.6601 | 25.5089
MUCK | Muckadilla Regulator (Unregulated) | SW | 33 | 0.56304 | 32.182 | 0.45311 | 8.6329 | 24.7998 | 27.76 | 16.4163 | 66.5412 | 24.7731 | 27.7686
MURG | Murgon (TF1) | WB | 11 | 3.4403 | 65.5464 | 4.0882 | 25.9638 | 0.25301 | 2.0159 | 0.04738 | 1.066 | 0.25302 | 2.016
MURG | Murgon (TF2) | WB | 11 | 3.4403 | 65.5464 | 4.0882 | 25.9638 | 0.25301 | 2.0159 | 0.04738 | 1.066 | 0.25302 | 2.016
MURG | Murgon | WB | 66 | 1.1987 | 137.0293 | 1.172 | 44.6578 | 7.4027 | 34.1941 | 11.1283 | 35.7541 | 7.4029 | 34.1998
MUTA | Mutarnee | NQ | 11 | 0.94692 | 18.0412 | 0.98713 | 6.2691 | 1.7372 | 7.1857 | 1.1464 | 6.4 | 1.7353 | 7.1892
MUTA | Mutarnee | NQ | 66 | 1.1868 | 135.6682 | 0.88987 | 33.9084 | 21.2692 | 28.2871 | 30.6629 | 64.6103 | 21.2022 | 28.4135
MUTO | Mundubbera Town | WB | 11 | 3.9728 | 75.6926 | 5.4113 | 34.3664 | 0.86389 | 1.5369 | 0.019458 | 0.38866 | 0.86254 | 1.5369
MUTO | Mundubbera Town | WB | 66 | 0.81991 | 93.728 | 0.55079 | 20.9878 | 30.4978 | 41.1964 | 50.9672 | 116.9188 | 30.4491 | 41.1951
NANA | Nanango | WB | 11 | 4.9881 | 95.0363 | 5.8426 | 37.1052 | 0.46836 | 1.3201 | 0.096385 | 0.79518 | 0.4684 | 1.3203
NANA | Nanango | WB | 66 | 1.81 | 206.9138 | 1.159 | 44.1637 | 13.3912 | 18.897 | 19.107 | 60.5271 | 13.3926 | 18.9032
NAND | Nandi | SW | 11 | 1.947 | 37.0944 | 2.1785 | 13.8355 | 1.0546 | 3.4331 | 0.10091 | 2.5038 | 1.0546 | 3.4332
NAND | Nandi | SW | 33 | 1.7504 | 100.049 | 1.3047 | 24.8577 | 8.5831 | 8.3634 | 10.035 | 23.0942 | 8.5831 | 8.3644
NEBO | Nebo H011 (TF3) | MK | 11 | 3.2545 | 62.0062 | 1.8319 | 11.6338 | 0.11818 | 2.1459 | 3.2633e-08 | 7.161 | 0.11823 | 2.1465
NEBO | Nebo H011 (TF4) | MK | 11 | 3.258 | 62.0728 | 1.8326 | 11.6385 | 0.1177 | 2.1436 | 3.2633e-08 | 7.161 | 0.11776 | 2.1442
NESM | Neil Smith (TF1) | NQ | 11 | 10.2152 | 194.6251 | 10.9357 | 69.4512 | 0.082041 | 0.68121 | 0.025996 | 0.55217 | 0.081648 | 0.68094
NESM | Neil Smith (TF2) | NQ | 11 | 10.2152 | 194.6251 | 10.9357 | 69.4512 | 0.082041 | 0.68121 | 0.025996 | 0.55217 | 0.081648 | 0.68094
NESM | Neil Smith (TF1) | NQ | 66 | 8.3037 | 949.2385 | 6.1686 | 235.0544 | 2.0176 | 4.6452 | 2.9463 | 9.9585 | 2.0035 | 4.6357
NESM | Neil Smith (TF2) | NQ | 66 | 10.0322 | 1146.8321 | 8.7373 | 332.9355 | 1.2717 | 3.9941 | 1.4321 | 5.9179 | 1.2576 | 3.9792
NEWL | Newlands T069 | MK | 66 | 4.8118 | 550.0645 | 6.0145 | 229.1845 | 2.4388 | 8.3762 | 0.28884 | 3.5439 | 2.4405 | 8.3732
NOCL | North Cloncurry (TF1) | NQ - MI | 11 | 3.1342 | 59.7138 | 3.4923 | 22.1792 | 0.27406 | 2.2121 | 0.077115 | 1.5399 | 0.27132 | 2.2168
NOCL | North Cloncurry (TF2) | NQ - MI | 11 | 3.1342 | 59.7138 | 3.4923 | 22.1792 | 0.27406 | 2.2121 | 0.077115 | 1.5399 | 0.27132 | 2.2168
NOCL | North Cloncurry | NQ - MI | 66 | 1.6623 | 190.0236 | 1.553 | 59.176 | 7.09 | 24.1985 | 7.892 | 29.3653 | 6.9913 | 24.3698
NOMA | North Mackay (TF1) | MK | 11 | 6.1574 | 117.3151 | 7.2734 | 46.1921 | 0.090183 | 1.132 | 0.03061 | 0.61161 | 0.088832 | 1.1331
NOMA | North Mackay (TF2) | MK | 11 | 6.1888 | 117.9119 | 7.3111 | 46.4314 | 0.089437 | 1.1263 | 0.030382 | 0.60824 | 0.088087 | 1.1274
NOMA | North Mackay (TF1) | MK | 33 | 4.4498 | 254.3424 | 5.3481 | 101.8951 | 0.53615 | 4.6835 | 0.38769 | 2.3017 | 0.524 | 4.6934
NOMA | North Mackay (TF2) | MK | 33 | 4.4702 | 255.5051 | 5.3625 | 102.1696 | 0.5315 | 4.6624 | 0.3755 | 2.3146 | 0.51934 | 4.6724
NORM | Normanton | FN | 22 | 1.2491 | 47.5972 | 1.7985 | 22.8444 | 3.3173 | 14.6685 | 0.0070855 | 1.9736 | 2.9564 | 14.7999
NORM | Normanton | FN | 6.6 | 3.6537 | 41.7669 | 0 | 0 | 0.30604 | 1.5118 | 329999990.0687 | 69.656 | 0.27343 | 1.5232
NORM | Normanton | FN | 66 | 0.43846 | 50.1223 | 0.61504 | 23.436 | 32.041 | 120.1895 | 0.24539 | 24.3569 | 29.6591 | 121.2468
NORW | Norwin (TF1) | SW | 11 | 1.6078 | 30.6322 | 1.977 | 12.5555 | 1.7279 | 4.0006 | 0.10178 | 2.0356 | 1.7162 | 3.9942
NORW | Norwin (TF3) | SW | 11 | 1.6023 | 30.5279 | 1.9685 | 12.5018 | 1.7287 | 4.0164 | 0.10257 | 2.0515 | 1.717 | 4.0101
NORW | Norwin | SW | 33 | 0.91566 | 52.3368 | 0.59615 | 11.3583 | 14.6354 | 17.6845 | 21.6329 | 57.5417 | 14.5301 | 17.6272
NOST | North Street | SW | 11 | 9.8074 | 186.8558 | 2.2331 | 14.1819 | 0.097048 | 0.70625 | 9.0204 | 0.40809 | 0.097045 | 0.70579
NOST | North Street | SW | 33 | 7.5702 | 432.6954 | 1.1083 | 21.1165 | 0.68979 | 2.6834 | 55.2246 | -0.99167 | 0.68977 | 2.6793
OAKE | Oakey | SW | 11 | 14.9154 | 284.1768 | 17.0515 | 108.2918 | 0.024478 | 0.46885 | 0.014889 | 0.29151 | 0.023289 | 0.46895
OAKE | Oakey | SW | 33 | 13.1433 | 751.2393 | 1.4425 | 27.4829 | 0.086298 | 1.596 | 32.4143 | 25.8635 | 0.075604 | 1.597
OAKY | Oakey T189 (TF1) | SW | 110 | 10.1037 | 1925.0078 | 10.3443 | 656.9493 | 0.65644 | 6.8898 | 0.79739 | 6.3653 | 0.65391 | 6.9106
OAKY | Oakey T189 (TF2) | SW | 110 | 10.1036 | 1924.9955 | 10.3426 | 656.8445 | 0.65648 | 6.8899 | 0.79934 | 6.3682 | 0.65394 | 6.9106
OAKY | Oakey T189 (TF1) | SW | 33 | 13.1433 | 751.2393 | 1.4425 | 27.4829 | 0.086298 | 1.596 | 32.4143 | 25.8635 | 0.075604 | 1.597
OAKY | Oakey T189 (TF2) | SW | 33 | 13.1433 | 751.2393 | 1.4425 | 27.4829 | 0.086298 | 1.596 | 32.4143 | 25.8635 | 0.075604 | 1.597
OONN | Oonoonba | NQ | 11 | 15.7039 | 299.2 | 16.9244 | 107.4843 | 0.043363 | 0.44423 | 0.011183 | 0.35103 | 0.04298 | 0.44386
OONN | Oonoonba | NQ | 66 | 11.8485 | 1354.4627 | 9.5254 | 362.9659 | 1.1585 | 3.3551 | 1.794 | 5.9044 | 1.1447 | 3.3418
OWAN | Owanyilla | WB | 11 | 4.1622 | 79.2998 | 4.4811 | 28.4587 | 0.19709 | 1.6715 | 0.097632 | 1.3138 | 0.19608 | 1.6718
OWAN | Owanyilla | WB | 66 | 3.1451 | 359.5319 | 2.2162 | 84.4504 | 3.5805 | 12.8752 | 5.7182 | 29.5771 | 3.544 | 12.8869
PACO | Pacific Coal | WB | 66 | 12.0678 | 1379.5292 | 10.5439 | 401.7769 | 0.92969 | 3.3471 | 1.1153 | 4.8497 | 0.93114 | 3.3533
PAJI | Pajingo | NQ | 11 | 3.2643 | 62.1938 | 3.9482 | 25.0742 | 0.78789 | 2.0296 | 0.059052 | 1.0295 | 0.78622 | 2.0291
PAJI | Pajingo | NQ | 66 | 0.95718 | 109.4198 | 0.68294 | 26.0237 | 26.2382 | 36.0022 | 30.7727 | 93.655 | 26.1782 | 35.987
PAMP | Pampas | SW | 11 | 3.277 | 62.4357 | 4.1797 | 26.5446 | 0.45741 | 2.0885 | 0.038624 | 0.77248 | 0.44571 | 2.0821
PAMP | Pampas | SW | 33 | 1.6911 | 96.6566 | 0.47325 | 9.0165 | 3.7691 | 11.8443 | 0.0057617 | 109.49 | 3.6638 | 11.787
PAND | Pandoin | CA | 22 | 5.291 | 201.6131 | 5.6654 | 71.9607 | 0.19437 | 2.6345 | 0.1192 | 2.1123 | 0.1946 | 2.637
PAND | Pandoin | CA | 66 | 8.8304 | 1009.4479 | 9.8429 | 375.0665 | 0.67649 | 4.7001 | 0.49704 | 3.2233 | 0.67853 | 4.7219
PAPS | Pajingo Pumps | NQ | 66 | 1.9146 | 218.8664 | 1.5615 | 59.5027 | 10.1043 | 19.8477 | 8.9369 | 35.9902 | 10.0443 | 19.8325
PARK | Parkhurst | CA | 11 | 18.1873 | 346.5148 | 20.2076 | 128.3357 | 0.034338 | 0.38272 | 0.013411 | 0.26822 | 0.034395 | 0.38332
PARK | Parkhurst | CA | 66 | 10.0066 | 1143.9135 | 10.1314 | 386.057 | 0.75337 | 4.1221 | 1.0622 | 3.8813 | 0.75542 | 4.1438
PEAR | Peter Arlett | NQ | 11 | 11.0537 | 210.6009 | 11.8496 | 75.2549 | 0.041479 | 0.63256 | 0.021883 | 0.50698 | 0.036586 | 0.63237
PEAR | Peter Arlett | NQ | 66 | 11.9083 | 1361.2995 | 9.0422 | 344.5558 | 0.74325 | 3.4525 | 1.4471 | 6.7562 | 0.72786 | 3.442
PECR | Perseverance Creek (TF2) | SW | 11 | 2.9067 | 55.3805 | 3.8372 | 24.3695 | 0.66855 | 2.3104 | 1.2043 | 0.2185 | 0.66855 | 2.31
PECR | Perseverance Creek | SW | 33 | 2.0259 | 115.7945 | 0.82595 | 15.7366 | 5.3567 | 8.8592 | 9.0164 | 55.8624 | 5.3567 | 8.8562
PERA | Peranga (TF1) | SW | 11 | 1.6472 | 31.3843 | 2.0219 | 12.8405 | 1.6006 | 3.9383 | 0.098324 | 1.9665 | 1.5994 | 3.9384
PERA | Peranga (TF3) | SW | 11 | 0.64301 | 12.251 | 0.68852 | 4.3727 | 1.9395 | 10.7163 | 0.43722 | 8.7445 | 1.9383 | 10.7164
PERA | Peranga | SW | 33 | 0.94165 | 53.8224 | 0.41787 | 7.9615 | 13.5201 | 17.7462 | 55.2362 | 90.7536 | 13.5094 | 17.7471
PIAL | Pialba | WB | 11 | 5.3439 | 101.8157 | 5.7976 | 36.8196 | 0.11394 | 1.3064 | 0.046512 | 0.99652 | 0.1125 | 1.3069
PIAL | Pialba | WB | 66 | 3.6829 | 421.0071 | 2.5286 | 96.3508 | 2.4273 | 11.156 | 5.9876 | 26.291 | 2.3755 | 11.1718
PINN | Pinnacle | MK | 11 | 3.122 | 59.4814 | 3.4013 | 21.6011 | 0.39756 | 2.2042 | 0.12599 | 1.6881 | 0.39736 | 2.2067
PINN | Pinnacle | MK | 66 | 1.9983 | 228.4403 | 1.2903 | 49.1677 | 9.7763 | 18.5801 | 15.4677 | 53.8073 | 9.7693 | 18.6687
PIRR | Pirrinuan (TF1) | SW | 11 | 0.82886 | 15.7919 | 0.87116 | 5.5326 | 1.0601 | 8.3692 | 0.36041 | 7.2083 | 1.0601 | 8.3693
PIRR | Pirrinuan (TF2) | SW | 11 | 1.8584 | 35.4073 | 2.1049 | 13.3681 | 0.92509 | 3.647 | 5.6654e-10 | 2.4964 | 0.92509 | 3.6471
PIRR | Pirrinuan | SW | 33 | 1.7196 | 98.2888 | 1.0948 | 20.8585 | 6.2969 | 10.4477 | 9.2821 | 32.2491 | 6.2969 | 10.4487
PIVA | Pioneer Valley T141 | MK | 66 | 8.8001 | 1005.9921 | 10.9404 | 416.8852 | 0.52846 | 4.7384 | 0.20822 | 1.923 | 0.5056 | 4.7777
PLAN | Planella (TF1) | MK | 11 | 4.2633 | 81.2271 | 5.1078 | 32.4391 | 0.28922 | 1.6144 | 0.041521 | 0.83042 | 0.28787 | 1.6155
PLAN | Planella (TF2) | MK | 11 | 4.2674 | 81.3046 | 5.1137 | 32.4763 | 0.2891 | 1.6128 | 0.041407 | 0.82885 | 0.28775 | 1.6139
PLAN | Planella | MK | 33 | 2.8349 | 162.0337 | 2.3263 | 44.3213 | 2.2293 | 7.0558 | 3.1218 | 11.853 | 2.2171 | 7.0658
PLEY | Pleystowe | MK | 11 | 6.5809 | 125.3826 | 7.8358 | 49.7637 | 0.2597 | 1.0303 | 0.027955 | 0.55909 | 0.25798 | 1.0318
PLEY | Pleystowe | MK | 33 | 4.4386 | 253.6977 | 2.6304 | 50.1167 | 2.0857 | 4.2411 | 3.9164 | 14.0287 | 2.0702 | 4.2545
POCU | Port Curtis | CA | 11 | 25.3768 | 483.4931 | 2.183 | 13.8637 | 0.021058 | 0.27455 | 9.5326 | 0.17789 | 0.021047 | 0.27477
POCU | Port Curtis | CA | 66 | 11.9335 | 1364.1879 | 11.915 | 454.0216 | 0.48483 | 3.4796 | 0.65669 | 3.4621 | 0.48443 | 3.4878
POVE | Point Vernon | WB | 11 | 12.4033 | 236.3145 | 16.0109 | 101.6829 | 0.098983 | 0.55626 | 0.0075568 | 0.18189 | 0.097545 | 0.5567
POVE | Point Vernon | WB | 66 | 3.0308 | 346.4649 | 1.9814 | 75.4998 | 3.2913 | 13.4774 | 8.1345 | 34.8702 | 3.2396 | 13.4932
POZI | Pozieres | SW | 11 | 2.3542 | 44.8541 | 3.0501 | 19.3706 | 1.1177 | 2.7565 | 0.049101 | 0.98195 | 1.1166 | 2.7566
POZI | Pozieres | SW | 33 | 1.1269 | 64.4083 | 0.57677 | 10.989 | 9.617 | 15.9706 | 65.0341 | 37.5559 | 9.6079 | 15.9719
PROS | Proserpine T039 | MK | 66 | 5.7028 | 651.917 | 7.3908 | 281.6263 | 2.0992 | 7.0584 | 0.31658 | 2.4198 | 2.0636 | 6.9718
PROT | Proston | WB | 11 | 1.2884 | 24.548 | 1.4367 | 9.1241 | 1.6266 | 5.1753 | 0.52439 | 3.7439 | 1.6266 | 5.1755
PROT | Proston | WB | 66 | 0.64483 | 73.7145 | 0.53106 | 20.2361 | 39.68 | 51.5291 | 49.5155 | 95.6614 | 39.6802 | 51.5348
PURR | Purrawunda (TF1) | SW | 11 | 2.3347 | 44.4812 | 2.8054 | 17.817 | 0.76015 | 2.8966 | 0.075561 | 1.5112 | 0.76014 | 2.8961
PURR | Purrawunda (TF2) | SW | 11 | 2.3375 | 44.535 | 2.8095 | 17.843 | 0.75996 | 2.8929 | 0.075377 | 1.5075 | 0.75996 | 2.8925
PURR | Purrawunda | SW | 33 | 1.5081 | 86.2017 | 0.61621 | 11.7404 | 6.1613 | 12.4684 | 64.4388 | 42.4065 | 6.1612 | 12.4643
QUIL | Quilpie (TF1) | SW | 11 | 0.75941 | 14.4687 | 1.0262 | 6.5173 | 4.0206 | 8.2744 | 0.10891 | 2.1782 | 4.0176 | 8.2754
QUIL | Quilpie (TF2) | SW | 11 | 0.76062 | 14.4917 | 1.0284 | 6.5315 | 4.0198 | 8.2586 | 0.10812 | 2.1624 | 4.0168 | 8.2596
QUIL | Quilpie | SW | 66 | 0.16075 | 18.3764 | 0.077803 | 2.9647 | 140.8202 | 219.464 | 387.2655 | 1032.4612 | 140.7135 | 219.4981
RAGL | Raglan | CA | 22 | 2.0995 | 80.0011 | 2.5562 | 32.4685 | 2.5844 | 6.1353 | 0.24239 | 3.2122 | 2.5846 | 6.1378
RAGL | Raglan | CA | 66 | 1.2439 | 142.1942 | 0.84531 | 32.2105 | 21.0782 | 26.3079 | 31.4462 | 76.7009 | 21.0802 | 26.3296
RASM | Rasmussen | NQ | 11 | 14.7717 | 281.4391 | 16.2128 | 102.965 | 0.042827 | 0.47258 | 0.011128 | 0.34917 | 0.042452 | 0.47227
RASM | Rasmussen | NQ | 66 | 9.1688 | 1048.134 | 6.5213 | 248.4961 | 1.1412 | 4.4427 | 2.2382 | 9.9497 | 1.1276 | 4.4316
RAVE | Ravenshoe | FN | 22 | 1.9655 | 74.8966 | 2.3626 | 30.0096 | 1.9144 | 6.8567 | 0.00054415 | 3.6254 | 1.9079 | 6.8724
RAVE | Ravenshoe | FN | 66 | 1.2063 | 137.8961 | 0.77214 | 29.4224 | 15.3648 | 31.2231 | 23.3093 | 91.3486 | 15.3063 | 31.3647
RAVN | Ravenswood | NQ | 11 | 2.0722 | 39.4803 | 2.1597 | 13.7159 | 0.57663 | 3.3509 | 0.32962 | 2.9304 | 0.57466 | 3.3501
RAVN | Ravenswood | NQ | 66 | 2.4077 | 275.2342 | 1.5993 | 60.9414 | 8.8924 | 15.14 | 12.7834 | 42.5758 | 8.8217 | 15.1112
RICH | Richmond | NQ | 33 | 0.74988 | 42.8614 | 0.87467 | 16.6648 | 8.3816 | 29.1025 | 0.58785 | 12.6622 | 8.3753 | 29.3169
RICH | Richmond | NQ | 66 | 0.57969 | 66.2678 | 0.63145 | 24.0614 | 31.0377 | 71.9435 | 4.406 | 46.7521 | 31.0124 | 72.8011
ROEA | Roma East | SW | 11 | 5.3174 | 101.3103 | 6.29 | 39.9469 | 0.2303 | 1.2935 | 0.035372 | 0.70743 | 0.22734 | 1.2945
ROEA | Roma East | SW | 33 | 3.7704 | 215.5087 | 3.3534 | 63.8915 | 1.7544 | 5.2746 | 2.2017 | 7.3097 | 1.7277 | 5.2832
ROGL | Rockhampton T023 (TF2) | CA | 11 | 9.7169 | 185.1321 | 10.1656 | 64.56 | 0.039451 | 0.71814 | 0.027887 | 0.62278 | 0.039508 | 0.71874
ROGL | Rockhampton T023 (TF4) | CA | 11 | 10.0459 | 191.3997 | 10.5262 | 66.8503 | 0.038396 | 0.69461 | 0.026832 | 0.59925 | 0.038453 | 0.69521
ROGL | Rockhampton T023 | CA | 66 | 12.126 | 1386.1823 | 14.534 | 553.8206 | 0.4163 | 3.4329 | 0.26105 | 1.6981 | 0.41835 | 3.4546
ROLE | Rolleston | CA | 132 | 1.3538 | 309.5258 | 1.5473 | 117.9226 | 13.8839 | 60.4317 | 1.4443 | 39.3088 | 13.8797 | 60.3762
ROLE | Rolleston (TF 1) | CA | 22 | 4.5059 | 171.6978 | 5.0126 | 63.6685 | 0.38567 | 3.081 | 0.849 | 2.055 | 0.38555 | 3.0794
ROLE | Rolleston (TF 2) | CA | 22 | 4.5059 | 171.6978 | 5.0126 | 63.6685 | 0.38567 | 3.081 | 0.849 | 2.055 | 0.38555 | 3.0794
ROLE | Rolleston | CA | 66 | 2.1233 | 242.7256 | 2.7087 | 103.2141 | 3.6174 | 19.4339 | 0.15499 | 7.0434 | 3.6163 | 19.42
ROLL | Rollingstone | NQ | 11 | 1.7552 | 33.441 | 1.8583 | 11.8021 | 0.76049 | 3.9183 | 0.24091 | 3.3399 | 0.75938 | 3.9183
ROLL | Rollingstone | NQ | 66 | 1.5017 | 171.6714 | 1.0411 | 39.6701 | 18.705 | 20.8226 | 24.907 | 62.303 | 18.6652 | 20.8254
ROMA | Roma T083 (TF1) | SW | 132 | 3.0917 | 706.8516 | 3.7611 | 286.6359 | 5.2073 | 26.6116 | 0.61841 | 12.6625 | 4.7803 | 26.7488
ROMA | Roma T083 (TF2) | SW | 132 | 3.0917 | 706.8516 | 3.7611 | 286.6359 | 5.2073 | 26.6116 | 0.61841 | 12.6625 | 4.7803 | 26.7488
ROMA | Roma T083 | SW | 33 | 5.7037 | 326.0125 | 7.2634 | 138.3861 | 0.3855 | 3.6543 | 0.023141 | 1.3053 | 0.35881 | 3.6629
ROMA | Roma T083 | SW | 66 | 2.931 | 335.0638 | 3.7559 | 143.1202 | 1.4853 | 14.2238 | 0.33143 | 4.8461 | 1.3785 | 14.2581
ROPL | Ross Plains (TF1) | NQ | 11 | 7.5813 | 144.4425 | 7.8728 | 49.999 | 0.064539 | 0.92231 | 0.041665 | 0.82235 | 0.064121 | 0.92196
ROPL | Ross Plains (TF2) | NQ | 11 | 7.3098 | 139.2696 | 7.5804 | 48.1421 | 0.064431 | 0.95674 | 0.041557 | 0.85678 | 0.064012 | 0.95639
ROPL | Ross Plains | NQ | 66 | 11.393 | 1302.3905 | 8.41 | 320.4645 | 0.82347 | 3.5984 | 1.6803 | 7.4539 | 0.80839 | 3.5859
ROSE | ROSE Rosella (TF1) | MK | 11 | 3.0941 | 58.9514 | 3.4061 | 21.6319 | 0.31237 | 2.2385 | 0.082147 | 1.6417 | 0.31213 | 2.2393
ROSE | ROSE Rosella (TF2) | MK | 11 | 2.8882 | 55.0277 | 3.2369 | 20.5568 | 0.46699 | 2.3759 | 0.082469 | 1.6482 | 0.46664 | 2.3782
ROSE | ROSE Rosella (TF1) | MK | 33 | 3.6444 | 208.307 | 2.1946 | 41.813 | 2.072 | 5.371 | 4.0297 | 16.7452 | 2.0698 | 5.3778
ROSE | ROSE Rosella (TF2) | MK | 33 | 2.8322 | 161.8799 | 1.7552 | 33.4415 | 3.4607 | 6.5498 | 5.2738 | 20.6069 | 3.4576 | 6.5703
ROSO | Rockhampton South (TF1) | CA | 11 | 11.0816 | 211.1322 | 11.7954 | 74.9112 | 0.052335 | 0.62848 | 0.029018 | 0.51485 | 0.052391 | 0.62908
ROSO | Rockhampton South (TF2) | CA | 11 | 10.1719 | 193.8 | 10.7694 | 68.3948 | 0.050343 | 0.68521 | 0.027026 | 0.57158 | 0.0504 | 0.68581
ROSO | Rockhampton South | CA | 66 | 10.0417 | 1147.9208 | 9.9796 | 380.274 | 0.83939 | 4.0905 | 0.99191 | 4.1158 | 0.84144 | 4.1123
ROST | Rocky Street | WB | 11 | 11.2825 | 214.9602 | 12.5896 | 79.9545 | 0.055659 | 0.61838 | 0.017965 | 0.42476 | 0.054643 | 0.6187
ROST | Rocky Street | WB | 66 | 5.9189 | 676.6215 | 5.8843 | 224.2212 | 1.357 | 6.9702 | 1.3948 | 7.0537 | 1.3204 | 6.9819
ROWE | Roma West (TF1) | SW | 11 | 2.0745 | 39.525 | 2.2707 | 14.4211 | 0.65168 | 3.304 | 0.2254 | 2.494 | 0.64871 | 3.3049
ROWE | Roma West (TF2) | SW | 11 | 2.0745 | 39.525 | 2.2707 | 14.4211 | 0.65168 | 3.304 | 0.2254 | 2.494 | 0.64871 | 3.3049
ROWE | Roma West | SW | 33 | 2.5443 | 145.4253 | 1.9297 | 36.7652 | 3.8365 | 7.2896 | 5.2128 | 15.3512 | 3.8098 | 7.2982
RYWU | Rywung (Regulated) | SW | 33 | 1.038 | 59.3314 | 0.7979 | 15.202 | 16.5167 | 11.6501 | 19.2796 | 35.757 | 16.4917 | 11.6579
RYWU | Rywung (Unregulated) | SW | 33 | 1.0097 | 57.7134 | 0.77693 | 14.8025 | 16.5616 | 12.5486 | 19.3265 | 36.6587 | 16.5366 | 12.5564
SAGE | St. George (TF1) | SW | 33 | 0.7652 | 43.7371 | 1.096 | 20.8809 | 9.874 | 25.5481 | 0.14883 | 2.7149 | 9.8473 | 25.5566
SAGE | St. George (TF2) | SW | 33 | 0.7652 | 43.7371 | 1.096 | 20.8809 | 9.874 | 25.5481 | 0.14883 | 2.7149 | 9.8473 | 25.5566
SAGE | St. George | SW | 66 | 0.41934 | 47.9367 | 0.58325 | 22.2247 | 38.9962 | 92.0409 | 0.97355 | 16.552 | 38.8894 | 92.0748
SAGT | St. George Town (TF1) | SW | 11 | 1.3235 | 25.216 | 1.6911 | 10.7398 | 1.6624 | 5.01 | 0.094622 | 1.8924 | 1.6595 | 5.0109
SAGT | St. George Town (TF2) | SW | 11 | 1.2879 | 24.5375 | 1.6328 | 10.3696 | 1.67 | 5.1611 | 0.10218 | 2.0436 | 1.667 | 5.1621
SAGT | St. George Town (TF3) | SW | 11 | 1.3235 | 25.216 | 1.6911 | 10.7398 | 1.6624 | 5.01 | 0.094622 | 1.8924 | 1.6595 | 5.0109
SAGT | St. George Town | SW | 33 | 0.66734 | 38.1435 | 0.82342 | 15.6883 | 14.1103 | 28.0582 | 5.3416 | 12.4761 | 14.0836 | 28.0667
SARI | Sarina (TF1) | MK | 11 | 8.9635 | 170.7782 | 7.656 | 48.6222 | 0.12485 | 0.76971 | 0.051456 | 1.0577 | 0.11163 | 0.89641
SARI | Sarina (TF2) | MK | 11 | 4.208 | 80.1727 | 4.6103 | 29.2792 | 0.22519 | 1.6464 | 0.060824 | 1.2165 | 0.23008 | 1.6584
SARI | Sarina | MK | 33 | 5.064 | 289.4456 | 3.0589 | 58.2795 | 1.4793 | 3.8694 | 3.0209 | 11.8279 | 1.5233 | 3.9772
SARS | Sarsfield | NQ | 66 | 2.1154 | 241.8179 | 1.3999 | 53.3434 | 10.683 | 16.8907 | 15.3067 | 48.6893 | 10.6125 | 16.862
SAUN | Saunders | NQ | 11 | 3.7612 | 71.6607 | 3.917 | 24.8764 | 0.22282 | 1.8492 | 0.10015 | 1.6416 | 0.22171 | 1.8493
SAUN | Saunders | NQ | 66 | 4.841 | 553.4018 | 3.5169 | 134.0103 | 4.4161 | 7.4761 | 5.7902 | 17.8189 | 4.3762 | 7.4788
SHUT | Shutehaven | MK | 22 | 3.0677 | 116.8938 | 3.8133 | 48.4352 | 1.3076 | 4.3717 | 0.083947 | 1.9507 | 1.2996 | 4.358
SHUT | Shutehaven | MK | 66 | 1.7196 | 196.5817 | 1.1735 | 44.715 | 11.0136 | 21.7952 | 15.4176 | 57.1933 | 10.9412 | 21.6725
SKIA | Skid 'A' (Mt Bassett) | MK | 11 | 3.3373 | 63.5844 | 3.4968 | 22.2078 | 0.22208 | 2.0837 | 0.0024208 | 1.8156 | 0.22185 | 2.0845
SKIA | Skid 'A' (Mt Bassett) | MK | 33 | 7.7671 | 443.9491 | 6.3381 | 120.7572 | 0.90937 | 2.5435 | 1.2732 | 4.3449 | 0.90723 | 2.5504
SKIE | Skid 'E' (Chinchilla) | SW | 11 | 3.2272 | 61.4869 | 3.415 | 21.6884 | 0.22515 | 2.1553 | 0.0012104 | 1.8156 | 0.22237 | 2.1562
SKIE | Skid 'E' (Chinchilla) | SW | 33 | 6.3141 | 360.8993 | 5.9927 | 114.1772 | 0.93697 | 3.188 | 0.5006 | 3.853 | 0.912 | 3.1958
SKIF | Skid 'F' (Broxburn) | SW | 33 | 2.2895 | 130.8643 | 1.449 | 27.6066 | 5.44 | 6.2973 | 12.1158 | 19.4566 | 5.4396 | 6.2976
SKIF | Skid 'F' (Broxburn) | SW | 11 | 3.4051 | 64.8764 | 4.0722 | 25.8618 | 0.7073 | 1.7258 | 0.1029 | 0.9742 | 0.7072 | 1.7258
SKIJ | Skid J | MK | 11 | 6.0009 | 114.3317 | 6.2747 | 39.8494 | 0.081736 | 1.1645 | 0.057791 | 1.0077 | 0.080721 | 1.1648
SKIJ | Skid J | MK | 66 | 7.3633 | 841.7365 | 9.2058 | 350.7874 | 0.86201 | 5.6426 | 0.12419 | 2.2592 | 0.82545 | 5.6543
SOBL | South Blackwater | CA | 22 | 1.5724 | 59.9161 | 1.7693 | 22.4728 | 2.1026 | 8.647 | 0.55518 | 5.9556 | 2.1037 | 8.6414
SOBL | South Blackwater (ex 6014) | CA | 66 | 1.7894 | 204.5531 | 1.0808 | 41.1835 | 6.128 | 22.645 | 16.277 | 67.7336 | 6.1381 | 22.5945
SOBL | South Blackwater (ex 6061) | CA | 66 | 1.5024 | 171.7441 | 0.97478 | 37.1442 | 13.9267 | 24.2229 | 23.5225 | 70.1403 | 13.9367 | 24.1724
SOBU | South Bundaberg | WB | 11 | 10.217 | 194.6599 | 11.5315 | 73.2349 | 0.084993 | 0.6793 | 0.023248 | 0.44753 | 0.084481 | 0.68147
SOBU | South Bundaberg | WB | 66 | 4.8603 | 555.6051 | 4.0537 | 154.4686 | 2.2228 | 8.3437 | 3.4679 | 13.2522 | 2.2044 | 8.4219
SOKO | South Kolan | WB | 11 | 4.5396 | 86.4904 | 4.7917 | 30.4316 | 0.13415 | 1.535 | 0.084445 | 1.2908 | 0.13359 | 1.5365
SOKO | South Kolan | WB | 66 | 4.6789 | 534.8716 | 3.8556 | 146.9178 | 1.7892 | 8.7893 | 3.0919 | 14.3163 | 1.7691 | 8.8438
SOMA | South Mackay (TF1) | MK | 11 | 6.0936 | 116.0987 | 6.7725 | 43.0114 | 0.14208 | 1.1388 | 0.040101 | 0.80275 | 0.14185 | 1.1396
SOMA | South Mackay (TF2) | MK | 11 | 6.0936 | 116.0987 | 6.7725 | 43.0114 | 0.14208 | 1.1388 | 0.040101 | 0.80275 | 0.14185 | 1.1396
SOMA | South Mackay | MK | 33 | 6.6373 | 379.3752 | 4.6641 | 88.8627 | 0.91783 | 3.0247 | 1.7927 | 6.9436 | 0.91569 | 3.0316
SOTO | South Toowoomba T043 (TF1) | SW | 110 | 16.8883 | 3217.6463 | 14.7873 | 939.1204 | 0.39933 | 4.1206 | 0.72611 | 5.9066 | 0.39906 | 4.0746
SOTO | South Toowoomba T043 (TF2) | SW | 110 | 16.8883 | 3217.6463 | 14.7873 | 939.1204 | 0.39933 | 4.1206 | 0.72611 | 5.9066 | 0.39906 | 4.0746
SOTO | South Toowoomba T043 | SW | 11 | 13.006 | 247.7982 | 2.281 | 14.4866 | 0.028773 | 0.53679 | 9.0197 | 0.39392 | 0.02877 | 0.53633
SOTO | South Toowoomba T043 | SW | 33 | 16.2791 | 930.4762 | 1.1584 | 22.07 | 0.08169 | 1.2858 | 54.1128 | -0.38874 | 0.081665 | 1.2817
SOWC | South Walker Switching | MK | 66 | 1.9543 | 223.4111 | 1.2885 | 49.0988 | 4.6549 | 20.9614 | 13.3629 | 53.1089 | 4.6556 | 20.9761
STAM | Stamford | NQ | 33 | 0.16255 | 9.2908 | 0.15766 | 3.0038 | 15.0059 | 138.9079 | 8.9372 | 126.0276 | 14.9995 | 139.1223
STAM | Stamford | NQ | 66 | 0.79751 | 91.1672 | 0.56312 | 21.4579 | 24.2746 | 51.5213 | 33.8766 | 107.9312 | 24.2493 | 52.3789
STAN | Stanthorpe | SW | 110 | 1.2674 | 241.4772 | 1.7875 | 113.5242 | 29.5585 | 46.664 | 0.6184 | 7.8382 | 29.4748 | 46.6753
STAN | Stanthorpe | SW | 33 | 2.7563 | 157.5418 | 1.0101 | 19.2452 | 3.3081 | 6.8664 | 54.0557 | 0.7424 | 3.299 | 6.8676
STTO | Stanthorpe Town | SW | 11 | 4.4437 | 84.6643 | 5.626 | 35.7301 | 0.4961 | 1.4957 | 0.029927 | 0.59855 | 0.49509 | 1.4958
STTO | Stanthorpe Town | SW | 33 | 2.3087 | 131.9598 | 0.93083 | 17.7347 | 4.1956 | 8.0743 | 55.7221 | 5.553 | 4.1865 | 8.0755
STUA | Stuart | NQ | 11 | 18.4575 | 351.6635 | 19.5651 | 124.2552 | 0.020543 | 0.37921 | 0.010101 | 0.31598 | 0.02015 | 0.37876
STUA | Stuart | NQ | 66 | 18.229 | 2083.858 | 20.0834 | 765.2791 | 0.37593 | 2.2763 | 0.25563 | 1.6689 | 0.36178 | 2.2602
T076 | Barcaldine Power Station | CA | 132 | 2.2582 | 516.2863 | 1.8685 | 142.3961 | 4.1656 | 37.2462 | 5.5466 | 54.5964 | 4.841 | 43.4847
TANB | Tanby | CA | 22 | 4.3819 | 166.9741 | 5.1715 | 65.6863 | 0.71946 | 3.1075 | 0.070146 | 1.7491 | 0.71969 | 3.11
TANB | Tanby | CA | 66 | 3.0944 | 353.7319 | 2.03 | 77.355 | 5.8438 | 12.2262 | 10.1541 | 33.5146 | 5.8459 | 12.248
TARA | Tara (TF1) | SW | 11 | 0.54353 | 10.3557 | 0.63206 | 4.0141 | 4.9364 | 11.8798 | 0.38978 | 7.7956 | 4.9364 | 11.8799
TARA | Tara (TF2) | SW | 11 | 0.70898 | 13.5079 | 0.87765 | 5.5738 | 4.7739 | 8.6301 | 0.22729 | 4.5459 | 4.7739 | 8.6302
TARA | Tara | SW | 33 | 0.38136 | 21.7978 | 0.28121 | 5.3578 | 40.9198 | 36.7577 | 49.5172 | 107.6093 | 40.9197 | 36.7587
TARE | Tara Regulator (Regulated) | SW | 33 | 0.42619 | 24.3599 | 0.31694 | 6.0385 | 36.108 | 33.4486 | 43.0842 | 94.71 | 36.108 | 33.4495
TARE | Tara Regulator (Unregulated) | SW | 33 | 0.42619 | 24.3599 | 0.31694 | 6.0385 | 36.108 | 33.4486 | 43.0842 | 94.71 | 36.108 | 33.4495
THAL | Thalanga | NQ | 11 | 2.9509 | 56.2222 | 3.1802 | 20.197 | 0.40022 | 2.416 | 0.084051 | 1.765 | 0.39403 | 2.4173
THAL | Thalanga | NQ | 66 | 1.6938 | 193.631 | 1.3733 | 52.3303 | 11.3194 | 22.96 | 12.0219 | 39.8706 | 11.0968 | 23.0068
THEO | Theodore (TF1) | CA | 22 | 2.5248 | 96.2095 | 3.192 | 40.5436 | 0.96576 | 5.4511 | 0.16431 | 2.0553 | 0.96629 | 5.4621
THEO | Theodore (TF2) | CA | 22 | 2.5248 | 96.2095 | 3.192 | 40.5436 | 0.96576 | 5.4511 | 0.16431 | 2.0553 | 0.96629 | 5.4621
THEO | Theodore (TF3) | CA | 22 | 2.5248 | 96.2095 | 3.192 | 40.5436 | 0.96576 | 5.4511 | 0.16431 | 2.0553 | 0.96629 | 5.4621
THEO | Theodore | CA | 66 | 1.3389 | 153.0543 | 0.80263 | 30.5842 | 7.2111 | 30.4778 | 20.6111 | 91.7118 | 7.2159 | 30.5763
TIDH | Tinaroo Dam Hydro | FN | 22 | 0.87414 | 33.3092 | 1.0259 | 13.0303 | 12.864 | 9.5259 | 2.0964 | 10.952 | 12.8575 | 9.5416
TIER | Tieri | CA | 22 | 3.2689 | 124.5605 | 3.5727 | 45.379 | 0.76877 | 4.2112 | 0.23833 | 3.1945 | 0.76567 | 4.2104
TIER | Tieri | CA | 66 | 4.0675 | 464.9812 | 2.8098 | 107.0688 | 4.774 | 9.1504 | 8.0386 | 22.9468 | 4.746 | 9.1433
TOMA | Townsville Marina SS MF07 (BUSA) | NQ | 11 | 8.51 | 162.1369 | 8.9604 | 56.9063 | 0.17679 | 0.80438 | 0.21528 | 0.66934 | 0.1764 | 0.80396
TOMA | Townsville Marina SS TOPO08 (BUSB) | NQ | 11 | 7.7067 | 146.8326 | 8.0671 | 51.2327 | 0.14112 | 0.8984 | 0.15279 | 0.77466 | 0.14073 | 0.89799
TOPO | Townsville Port (TF1) | NQ | 11 | 8.8531 | 168.6748 | 9.1886 | 58.3553 | 0.055256 | 0.78972 | 0.03528 | 0.70561 | 0.054864 | 0.78931
TOPO | Townsville Port (TF2) | NQ | 11 | 8.8531 | 168.6748 | 9.188 | 58.3516 | 0.055256 | 0.78972 | 0.035298 | 0.70575 | 0.054864 | 0.78931
TOPO | Townsville Port | NQ | 66 | 13.5113 | 1544.5474 | 14.2598 | 543.3703 | 0.71913 | 3.0281 | 0.41552 | 2.6162 | 0.70499 | 3.0132
TOPS | Townsville Power Station | NQ | 66 | 8.8177 | 1007.9971 | 8.9101 | 339.5217 | 0.87677 | 4.6847 | 0.37579 | 4.6242 | 0.81926 | 4.6941
TORQ | Torquay | WB | 11 | 13.7349 | 261.6853 | 17.1282 | 108.7786 | 0.076438 | 0.5045 | 0.010925 | 0.20511 | 0.074923 | 0.50497
TORQ | Torquay | WB | 66 | 3.8112 | 435.6814 | 2.5917 | 98.7564 | 2.3585 | 10.7782 | 5.7969 | 25.8778 | 2.3039 | 10.7951
TORR | Torrington T116 (TF1) | SW | 110 | 8.5486 | 1628.7339 | 8.0362 | 510.3682 | 1.2572 | 8.0814 | 0.64306 | 9.7913 | 1.2569 | 8.0354
TORR | Torrington T116 (TF2) | SW | 110 | 8.5388 | 1626.8644 | 7.6642 | 486.7409 | 1.2588 | 8.0906 | 0.81639 | 11.0275 | 1.2586 | 8.0446
TORR | Torrington T116 (TF3) | SW | 11 | 13.1585 | 250.704 | 2.2762 | 14.4555 | 0.038086 | 0.52997 | 9.0266 | 0.37294 | 0.038083 | 0.5295
TORR | Torrington T116 (TF4) | SW | 11 | 13.1585 | 250.704 | 2.2762 | 14.4555 | 0.038086 | 0.52997 | 9.0266 | 0.37294 | 0.038083 | 0.5295
TORR | Torrington T116 | SW | 33 | 14.8024 | 846.0689 | 1.17 | 22.2918 | 0.10352 | 1.4132 | 53.5474 | -4.4604 | 0.10349 | 1.4091
TULL | Tully T048 | FN | 22 | 7.6375 | 291.0286 | 6.3669 | 80.8699 | 0.1389 | 1.8387 | 0.1805 | 2.9376 | 0.1269 | 1.8365
TUNG | Tungamull | CA | 22 | 0.59057 | 22.5037 | 0.60122 | 7.6366 | 3.027 | 23.473 | 2.4827 | 22.2707 | 3.0272 | 23.4755
TUNG | Tungamull | CA | 66 | 3.5301 | 403.543 | 2.3603 | 89.9391 | 4.8988 | 10.8212 | 8.7027 | 28.3175 | 4.9008 | 10.8429
TURK | Turkinje T055 (TF1) | FN | 66 | 5.1072 | 583.8297 | 6.245 | 237.9681 | 1.1843 | 8.1335 | 0.37886 | 3.5805 | 1.1258 | 8.275
TURK | Turkinje T055 (TF2) | FN | 66 | 5.1072 | 583.8297 | 6.245 | 237.9681 | 1.1843 | 8.1335 | 0.37886 | 3.5805 | 1.1258 | 8.275
TWCE | Toowoomba Central | SW | 110 | 16.2146 | 3089.2975 | 14.3263 | 909.8401 | 0.56773 | 4.2743 | 0.87455 | 5.9991 | 0.56745 | 4.2283
TWCE | Toowoomba Central | SW | 11 | 9.8953 | 188.5315 | 2.2475 | 14.2738 | 0.02205 | 0.70621 | 2.338e-07 | 7.92 | 0.022047 | 0.70575
VERM | Vermont | CA | 22 | 4.2216 | 160.8644 | 4.8339 | 61.3991 | 0.40871 | 3.2881 | 0.10344 | 2.0555 | 0.4087 | 3.2891
VERM | Vermont | CA | 66 | 3.6718 | 419.7478 | 2.9618 | 112.859 | 2.7474 | 11.0934 | 4.3249 | 19.1632 | 2.7473 | 11.1018
WAEA | Warwick East (TF1) | SW | 11 | 9.89 | 188.4289 | 5.5145 | 35.0219 | 0.092242 | 0.70266 | 3.1955 | 0.35895 | 0.089451 | 0.70312
WAEA | Warwick East (TF2) | SW | 11 | 9.89 | 188.4289 | 5.5145 | 35.0219 | 0.092242 | 0.70266 | 3.1955 | 0.35895 | 0.089451 | 0.70312
WAEA | Warwick East | SW | 33 | 6.6338 | 379.1736 | 6.8633 | 130.763 | 0.69141 | 3.0933 | 0.48922 | 2.8065 | 0.6663 | 3.0974
WAGG | Waggamba T156 | SW | 132 | 1.3982 | 319.6741 | 1.5798 | 120.3978 | 11.3278 | 58.8847 | 3.9797 | 39.2296 | 11.326 | 58.8547
WAGG | Waggamba T156 | SW | 33 | 2.8418 | 162.4311 | 2.4541 | 46.7574 | 0.72156 | 7.3405 | 3.23e-08 | 10.903 | 0.72144 | 7.3386
WAGG | Waggamba T156 | SW | 66 | 1.9396 | 221.731 | 2.6802 | 102.1285 | 2.8877 | 21.4192 | 0.21865 | 3.7081 | 2.8872 | 21.4117
WALK | Walkers | WB | 11 | 10.8226 | 206.1988 | 3.5338 | 22.4426 | 0.07785 | 0.64256 | 0.46126 | 4.6207 | 0.076835 | 0.64289
WALK | Walkers | WB | 66 | 5.7115 | 652.9103 | 5.544 | 211.2558 | 1.4507 | 7.2145 | 1.6205 | 7.822 | 1.4141 | 7.2262
WALL | Wallaville | WB | 11 | 4.2861 | 81.6608 | 4.9486 | 31.4277 | 0.46325 | 1.5648 | 0.06387 | 0.98938 | 0.46269 | 1.5663
WALL | Wallaville | WB | 66 | 1.6643 | 190.2588 | 1.1487 | 43.7697 | 14.3775 | 20.7154 | 19.8008 | 56.7151 | 14.3574 | 20.7699
WAND | Wandoan (TF1) | SW | 22 | 0.62832 | 23.9421 | 0.84016 | 10.6715 | 7.5281 | 20.9267 | 0.28126 | 5.6252 | 7.5282 | 20.9277
WAND | Wandoan (TF2) | SW | 22 | 0.6273 | 23.9032 | 0.83832 | 10.6481 | 7.53 | 20.9645 | 0.28315 | 5.6629 | 7.5301 | 20.9654
WAND | Wandoan | SW | 33 | 0.55022 | 31.4492 | 0.30531 | 5.8169 | 16.3055 | 34.4286 | 29.5386 | 127.4972 | 16.3057 | 34.4306
WARW | Warwick (CCT 735) | SW | 110 | 3.7672 | 717.7408 | 4.5833 | 291.076 | 5.6343 | 17.7096 | 0.77511 | 8.7891 | 5.5507 | 17.7209
WARW | Warwick (CCT 736) | SW | 110 | 3.7672 | 717.7408 | 4.5833 | 291.076 | 5.6343 | 17.7096 | 0.77511 | 8.7891 | 5.5507 | 17.7209
WARW | Warwick | SW | 11 | 3.3867 | 64.5246 | 3.5558 | 22.5824 | 0.20304 | 2.0596 | 0.14826 | 1.764 | 0.20025 | 2.06
WARW | Warwick | SW | 33 | 7.9209 | 452.7408 | 10.4241 | 198.6048 | 0.49306 | 2.6084 | 0.022109 | 0.746 | 0.46795 | 2.6125
WEBU | West Bundaberg | WB | 11 | 14.6392 | 278.9135 | 16.8152 | 106.7909 | 0.042617 | 0.47589 | 0.016488 | 0.28913 | 0.041981 | 0.478
WEBU | West Bundaberg | WB | 66 | 6.1817 | 706.6659 | 5.9868 | 228.1273 | 0.94064 | 6.7234 | 1.3086 | 7.2542 | 0.91775 | 6.7992
WEDA | West Dalby (TF1) | SW | 11 | 3.6843 | 70.1961 | 3.9929 | 25.3583 | 0.27212 | 1.8782 | 0.11127 | 1.455 | 0.27211 | 1.8783
WEDA | West Dalby (TF2) | SW | 11 | 3.6843 | 70.1961 | 3.9929 | 25.3583 | 0.27212 | 1.8782 | 0.11127 | 1.455 | 0.27211 | 1.8783
WEDA | West Dalby (TF3) | SW | 11 | 3.6843 | 70.1961 | 3.9929 | 25.3583 | 0.27212 | 1.8782 | 0.11127 | 1.455 | 0.27211 | 1.8783
WEDA | West Dalby | SW | 33 | 5.1475 | 294.2196 | 4.7008 | 89.5627 | 1.4477 | 3.8094 | 1.2236 | 5.1156 | 1.4476 | 3.8103
WEMA | West Mackay (TF1) | MK | 11 | 7.0893 | 135.0694 | 7.5245 | 47.7873 | 0.069005 | 0.98405 | 0.040739 | 0.81394 | 0.068768 | 0.98482
WEMA | West Mackay (TF2) | MK | 11 | 7.1382 | 136.0018 | 7.5611 | 48.0197 | 0.066188 | 0.97747 | 0.040739 | 0.81394 | 0.065951 | 0.97823
WEMA | West Mackay (TF1) | MK | 33 | 13.5183 | 772.677 | 16.9504 | 322.9481 | 0.25439 | 1.531 | 0.11963 | 0.59159 | 0.25226 | 1.5379
WEMA | West Mackay (TF2) | MK | 33 | 14.086 | 805.1212 | 19.1035 | 363.9707 | 0.22904 | 1.4717 | 0.069996 | 0.30251 | 0.22691 | 1.4786
WETO | West Toowoomba | SW | 11 | 11.285 | 215.0083 | 2.2622 | 14.3667 | 0.054262 | 0.61716 | 9.0196 | 0.39172 | 0.054259 | 0.6167
WETO | West Toowoomba | SW | 33 | 10.2173 | 583.9995 | 1.147 | 21.8531 | 0.31208 | 2.029 | 54.1936 | -1.926 | 0.31206 | 2.0248
WEWA | West Warwick | SW | 11 | 5.6441 | 107.5347 | 6.7058 | 42.5876 | 0.205 | 1.2248 | 0.035799 | 0.65204 | 0.20221 | 1.2252
WEWA | West Warwick | SW | 33 | 3.8614 | 220.7067 | 2.7393 | 52.1901 | 1.5506 | 5.2199 | 2.8909 | 11.7816 | 1.5255 | 5.2241
WIHI | Windy Hill | FN | 22 | 1.788 | 68.1315 | 1.8981 | 24.1087 | 2.2051 | 7.5087 | 0.56411 | 6.5219 | 2.1986 | 7.5244
WIIS | Wiggins Island (TF1) | CA | 132 | 16.5213 | 3777.27 | 14.5895 | 1111.8724 | 0.58814 | 5.0412 | 0.87058 | 7.0055 | 0.58834 | 5.0723
WIIS | Wiggins Island (TF2) | CA | 132 | 16.4563 | 3762.4194 | 14.5168 | 1106.3299 | 0.59239 | 5.0608 | 0.87584 | 7.0515 | 0.5926 | 5.092
WIIS | Wiggins Island | CA | 22 | 21.116 | 804.6268 | 4.4605 | 56.6557 | 0.027591 | 0.66126 | 0.17654 | 8.0725 | 0.027596 | 0.66212
WINT | Winton | NQ | 11 | 1.6657 | 31.7357 | 2.2354 | 14.1966 | 1.5946 | 4.2558 | 0.013553 | 0.4544 | 1.5939 | 4.2796
WINT | Winton | NQ | 33 | 0.30197 | 17.2598 | 0.34459 | 6.5654 | 19.8135 | 72.551 | 0.126 | 36.1043 | 19.8066 | 72.7653
WINT | Winton | NQ | 66 | 0.35781 | 40.9028 | 0.20819 | 7.9331 | 54.6721 | 114.5655 | 108.184 | 345.0533 | 54.6468 | 115.4231
WIRR | Wirralie | NQ | 33 | 0.17557 | 10.035 | 0.18172 | 3.4622 | 15.3567 | 118.5612 | 5.4868 | 107.5407 | 15.3571 | 118.5605
WIRR | Wirralie | NQ | 66 | 0.70938 | 81.0928 | 0.49484 | 18.856 | 39.4795 | 44.0819 | 51.9016 | 130.1496 | 39.4812 | 44.0789
WOOD | Woodhouse Station | NQ | 11 | 0.27679 | 5.2735 | 0.27723 | 1.7606 | 3.9424 | 25.0362 | 3.8485 | 24.8366 | 3.9396 | 25.0352
WOOD | Woodhouse Station | NQ | 66 | 5.2997 | 605.8355 | 4.363 | 166.2521 | 3.38 | 7.1869 | 4.7012 | 12.2425 | 3.2808 | 7.15
WOOG | Woodgate | WB | 11 | 2.8405 | 54.1182 | 3.0865 | 19.6018 | 0.36014 | 2.4397 | 0.09425 | 1.8705 | 0.35927 | 2.4397
WOOG | Woodgate | WB | 66 | 1.8583 | 212.4349 | 1.2202 | 46.4973 | 9.5719 | 20.492 | 17.07 | 55.6464 | 9.5409 | 20.4909
WOOL | Woolooga | WB | 11 | 2.5166 | 47.9469 | 2.9861 | 18.9643 | 0.99324 | 2.6003 | 0.10683 | 1.5076 | 0.99222 | 2.6007
WOOL | Woolooga | WB | 66 | 0.82974 | 94.8517 | 0.55562 | 21.1721 | 31.9108 | 39.3399 | 43.2876 | 121.0172 | 31.8742 | 39.3516
WOON | Woongarra | WB | 3.3 | 7.1125 | 40.6533 | 7.2666 | 13.8447 | 0.030789 | 0.29342 | 0.026345 | 0.27433 | 0.030738 | 0.29355
WOON | Woongarra | WB | 66 | 5.3548 | 612.1336 | 4.7856 | 182.3546 | 1.7776 | 7.6332 | 2.1467 | 10.3503 | 1.7575 | 7.6877
WOSO | Woodstock South (TF1) | NQ | 11 | 3.0736 | 58.5592 | 3.2809 | 20.8366 | 0.45336 | 2.2441 | 0.088391 | 1.8514 | 0.45284 | 2.2436
WOSO | Woodstock South | NQ | 66 | 2.1877 | 250.0868 | 1.5584 | 59.3822 | 13.1389 | 14.1356 | 17.2056 | 40.1611 | 13.1203 | 14.12
WOWA | Wowan | CA | 22 | 1.7662 | 67.3004 | 2.2566 | 28.6626 | 3.5115 | 7.0915 | 0.19644 | 2.9356 | 3.5115 | 7.0935
WOWA | Wowan | CA | 66 | 0.87634 | 100.1787 | 0.58431 | 22.2652 | 29.836 | 37.4034 | 41.9381 | 114.9579 | 29.8356 | 37.4212
YALK | Yalkula | FN | 132 | 1.8786 | 429.5143 | 1.5567 | 118.6403 | 12.0634 | 43.0362 | 18.8099 | 69.6055 | 11.7906 | 43.4723
YANO | Yarranlea North | SW | 110 | 5.1662 | 984.3014 | 8.1158 | 515.4242 | 5.9978 | 12.1481 | 0 | 0 | 4.8465 | 11.3619
YARA | Yarranlea T010 (TF1) | SW | 110 | 5.139 | 979.1148 | 7.6987 | 488.9311 | 6.05 | 12.2022 | 0.25208 | 1.2363 | 4.9205 | 11.4403
YARA | Yarranlea T010 (TF2) | SW | 110 | 5.1389 | 979.0863 | 7.6978 | 488.8767 | 6.0508 | 12.2022 | 0.25268 | 1.2386 | 4.9212 | 11.4404
YARA | Yarranlea T010 | SW | 33 | 6.7346 | 384.932 | 9.9725 | 190.0016 | 0.58991 | 3.0648 | 0.025659 | 0.15847 | 0.4846 | 3.0075
YARR | Yarraman (TF1) | WB | 11 | 2.6672 | 50.8176 | 3.0563 | 19.4103 | 0.93879 | 2.4455 | 0.1567 | 1.6581 | 0.93883 | 2.4457
YARR | Yarraman (TF2) | WB | 11 | 2.6672 | 50.8176 | 3.0563 | 19.4103 | 0.93879 | 2.4455 | 0.1567 | 1.6581 | 0.93883 | 2.4457
YARR | Yarraman | WB | 66 | 1.0492 | 119.9429 | 0.71148 | 27.1111 | 28.1555 | 28.3486 | 37.5287 | 93.0897 | 28.1569 | 28.3548
YARW | Yarwun Switching Station | CA | 66 | 2.7237 | 311.3565 | 1.8305 | 69.7506 | 8.6811 | 12.7116 | 12.2553 | 36.5656 | 8.6807 | 12.7199
YASO | Yarranlea South (TF1) | SW | 11 | 2.1745 | 41.4294 | 2.3013 | 14.6153 | 0.43568 | 3.1925 | 0.26891 | 2.6908 | 0.42398 | 3.1861
YASO | Yarranlea South (TF2) | SW | 11 | 2.1745 | 41.4294 | 2.3013 | 14.6153 | 0.43568 | 3.1925 | 0.26891 | 2.6908 | 0.42398 | 3.1861
YASO | Yarranlea South | SW | 33 | 4.4174 | 252.4898 | 4.0184 | 76.56 | 1.5009 | 4.5153 | 1.87 | 5.9881 | 1.3956 | 4.4579
YEPP | Yeppoon | CA | 11 | 11.347 | 216.1898 | 14.1786 | 90.0464 | 0.17808 | 0.58959 | 0.012599 | 0.25217 | 0.17814 | 0.59019
YEPP | Yeppoon | CA | 22 | 2.108 | 80.3255 | 1.0129 | 12.8659 | 0.91055 | 6.5677 | 0.050777 | 28.216 | 0.91078 | 6.5702
YEPP | Yeppoon | CA | 66 | 3.1007 | 354.462 | 2.0413 | 77.7837 | 5.9568 | 12.1405 | 10.1073 | 33.2527 | 5.9588 | 12.1622
The following sites are not reported (future subs; de-commisioned sites; unused tertiary voltage, and sites being investigated)
INVI | Invicta | NQ | 66
DIRR | Dirranbandi | SW | 33
WASO | Wandoan South | SW | 66
GRAC | Gracemere | CA | 11
OORA | Ooralea (Future) | MK | 11
GRAC | Gracemere | CA | 66
OORA | Ooralea (Future) | MK | 66
EALE | East Leichhardt | NQ | 11
EALE | East Leichhardt | NQ | 66
THAO | Thallon | SW | 33
INJU | Injune | SW | 33
LIEN | Linc Energy | SW | 33
KARD | Kagara Red Dome | FN | 66
KUMB | Kumbia | WB | 11
KUMB | Kumbia | WB | 66
TOFO | Toowoomba Foundry | SW | 33
MASM | Maryborough Sugar Mill |  | 11
MARI | Marian (MARIAN 11kV) | MK | 11
HUGH | Hughenden | NQ | 6.6
KILK | Kilkivan T012 (TF3 Tert) | WB | 11
MARY | Maryborough T059 (TF2) | WB | 11
MARY | Maryborough T059 (TF3*O1225*ON) | WB | 11
MILC | Millchester T095 (TF2) | NQ | 11
MILC | Millchester T095 (TF1) | NQ | 11
PIVA | Pioneer Valley T141 | MK | 11
CAIR | Capricorn Resort | CA | 66
CADO | Cameby Downs | SW | 33
CLUT | Clutha | CA | 66
DRCM | Drake Coal Mine | NQ | 33
WICC | Wilkie Creek Coal | SW | 33