## Compendium Guide
1. Version Control |  |  | 4.2. Fault Calculation Methodology
Version | Description | Date | Based on the IEC60909 standard, the fault calculation performed in the Power Factory assumes:
1 | First 2025 report version release | 2025-06-26 | • Transformers being set to nominal taps,
1.1 | Minor change on MaxMax report for PEAR_11kV_BUS 1 and PEAR_11kV_BUS 2 values | 2025-07-17 | • Conductor temperature of
o Maximum Fault: 20°C
o Minimum Fault: Individual Annealing Temperature
2. Known Limitations |  |  | • Voltage factor value set as Cmax = 1.1 under Max Fault Levels and Cmin = 1.0 under Min Fault Levels, for voltages above 1kV.
This section outlines any report shortfalls that users should be aware of. |  |  | 4.3. Study Cases Modelled
• BARC, SOJM and BOCR 11kV and NORM 6.6kV buses are not presented in this version of the report to allow for further investigations. |  |  |  | Scenario | Voltage factor (C) | Generation1 | Switch Status2 | Model Version | Study Case | Study Case Date
3. Disclaimer |  |  | Regional | Max (Max Fault Normal Config) | 1.1 | Max Dispatch | System Normal | V-3-3-88 Transmission_2025 | Transmission_2025_Max_FL | 2026-01-01 17:00
The Ergon Energy Fault Level Report is prepared and made available solely for information purposes. Whilst care was taken in the preparation of the information in this report, and it is provided with the best intentions and good faith, Ergon Energy accepts no responsibility or liability (including without limitation, liability to any person by reason of negligence or negligent mis-statement) for any loss or damage that may be incurred by any person acting in reliance on this information or assumptions drawn from it, except to the extent that liability under any applicable Queensland or Commonwealth of Australia statute cannot be excluded.. |  |  |  | MaxMax (Max Fault Max Config) | 1.1 | Max Dispatch | Considering alternate scenarios that may increase fault levels as defined by the Planning Group3 | V-3-3-88 Transmission_2026 | Transmission_2025_Max_FL | 2026-01-01 17:00
Ergon Energy makes no representation or warranty as to the accuracy, reliability, completeness or suitability for any particular purpose of the information in this document. All information should be independently investigated, reviewed, analysed, and verified, and must not be relied upon in connection with any investment proposal or decision. The information contained in this report is subject to annual review. Ergon Energy is obligated to publish future editions of this report on an annual basis in accordance with the National Electricity Rules. |  |  | 1Generation scenario considered for each study is clarified the next section. 2Switch status attempts to reflect the 'system normal’ conditions of the network where network elements being ‘intact’ and normally open switches, circuit breakers and isolators remain per their normal state when performing the fault level study. 3MaxMax scenario (Maximum Fault Maximum Configuration) has been provided for further assessment to planning teams incorporating the zone substation switches closed status
This work is copyright. Material contained in this document may be reproduced for personal, in-house or non-commercial use, without formal permission or charge, provided there is due acknowledgement of Ergon Energy as the source. Request and enquiries concerning reproduction and rights for a purpose other than personal, in-house or non-commercial use, should be addressed to the Group Manager Renewables and Distributed Energy. |  |  | This report assumes that all existing and known commissioned and de-commissioned plants have been taken into consideration with normal network operating conditions applied within the model. Due to the dynamic nature of the network, and the model being a snapshot at a given point of time, it is possible that further deviation of network could occur as compared to what was modelled. All reasonable efforts have also been placed to identify the system normal state of all network switches and generation connections. No future projects or network models have been included in the sub-transmission models.
Users of the Report must acknowledge and accept that:
• The information obtained from the Report is intended as general in nature, may be based on assumptions that change with time and may not necessarily be complete. Information contained in, or obtained from, the Report should not be relied upon, and use of the information contained in the Report is at your own risk. |  |  | 4.4. Generation Generation considered for both Powerlink and Ergon Energy networks (transmission, subtransmission and distribution) are as follows:
• Ergon Energy makes no representation or warranty as to the quality, accuracy, completeness, merchantability, suitability or fitness for purpose of any information contained in the Report. The Report is not a substitute for independent advice and research. The information contained in this report is subject to annual review.
• Ergon Energy does not accept any responsibility or liability for any loss or damage, however caused, which any person or entity may suffer in connection with the information contained in, or obtained from, the Report. |  |  | Generation Scenario |  | Powerlink (Transmission) |  |  |  | Ergon (Subtransmission and Distribution)
Use of the Report constitutes acceptance of the terms of this Disclaimer. |  |  | Max Dispatch |  | All modelled generating units in service |  |  |  | All modelled embedded generation in service
4. Introduction and Methodology |  |  | · Fault Level contributions of Non-Synchronous generators (e.g. PV and BESS elements) have been modelled as per the prescribed levels in their respective Generator Performance Standards (GPS) information.
This Fault Level Summary Report is prepared to provide a reference for designers, asset managers, planners, customer representatives and network operators. Engineers should carry out their own due diligence on the information provided by this report prior to applying it to engineering activities. Whenever possible, these activities should be undertaken with an awareness of fault levels and actions to manage fault levels. |  |  | · Distribution Embedded Generators are modelled at the upstream supplying subtransmission substation to account for their impact on Fault Levels.
The fault levels contained in this Report are indicative values under certain network configurations as per the methodology described below. Most Fault levels reported are under normal network conditions. Changes to Network Configuration can result in fault levels above or below the levels reported. Note that in the MaxMax report, only Terminals associated with an alternate configuration are reported. Any other variations of fault level studies would require the user to source or modify the data to meet their specific requirements.
In preparing the Report:
• The sub-transmission network model was developed and prepared using Power Factory 2024 SP5. This network modelling software program was used to produce the Fault Level Summary Report.
• A transmission network model was obtained from Powerlink in PSSE V32 format. This model was then converted to PowerFactory and merged with the sub-transmission model at all of Ergon Energy's respective common coupling points.
• Conversion of the transmission network from PSSE to PowerFactory was done using PowerFactory 2024 to leverage off the newer version updates and features.
• Using Python automation, the following fault level results were obtained at different nodes and buses across the entire network:
o 3-Phase fault levels (kA and MVA);
o 2-Phase - G fault levels (kA and MVA);
o 1-Phase - G fault levels (kA and MVA);
o Positive sequence resistance and reactance (ohms);
o Zero sequence resistance and reactance (ohms); and
o Negative sequence resistance and reactance (ohms)
4.1. Fault Calculation Data
The following data has been used to prepare the Fault Level Summary:
· Powerlink’s PSS/E data model source impedances;
· Network topology and connectivity from Ergon Energy's SCADA and GIS systems; and
· Where applicable and available:
o Connection agreements for generator data;
o Transformer test certificates; and
o Nameplate information.

## Max Fault Level Report
Sub Code | Substation | Region | Reported on Bus in PowerFactory | Voltage (kV) | 2025 3-Ph Fault Level (kA) | 2025 3-Ph Fault Level (MVA) | 2025 1-Ph-G Fault Level (kA) | 2025 1-Ph-G Fault Level (MVA) | 2025 3*I0 Fault Level (kA) | 2025 B 2-Ph-G Fault Level (kA) | 2025 B 2-Ph-G Fault Level (MVA) | 2025 C 2-Ph-G Fault Level (kA) | 2025 C 2-Ph-G Fault Level (MVA) | R1 (Ohms) | X1 (Ohms) | R0 (Ohms) | X0 (Ohms) | R2 (Ohms) | X2 (Ohms)
ABPO | Abbot Point | NQ | ABPO_66kV_TEF T1 | 66 | 1.9042 | 217.6761 | 1.4921 | 56.8576 | 1.2247 | 1.7115 | 65.2183 | 1.8058 | 68.8112 | 7.7193 | 20.6148 | 10.1669 | 39.0707 | 7.7336 | 20.5999
ABPO | Abbot Point | NQ | ABPO_66kV_TEF T2 | 66 | 1.9042 | 217.6761 | 1.4921 | 56.8576 | 1.2247 | 1.7115 | 65.2183 | 1.8058 | 68.8112 | 7.7193 | 20.6148 | 10.1669 | 39.0707 | 7.7336 | 20.5999
ABPO | Abbot Point | NQ | ABPO_11kV_BUS 1 | 11 | 9.535 | 181.6656 | 0.01464 | 0.09298 | 0.00732 | 8.2626 | 52.4743 | 8.2556 | 52.43 | 0.22073 | 0.69863 | 1431.006 | 0.126 | 0.22113 | 0.69822
ABPO | Abbot Point | NQ | ABPO_11kV_BUS 2 | 11 | 9.535 | 181.6656 | 0.01464 | 0.09298 | 0.00732 | 8.2626 | 52.4743 | 8.2556 | 52.43 | 0.22073 | 0.69863 | 1431.006 | 0.126 | 0.22113 | 0.69822
AGWA | Agnes Water | CA | AGWA_66kV_BUS 1 | 66 | 1.0951 | 125.1828 | 0.82081 | 31.277 | 0.65641 | 0.99022 | 37.7324 | 1.0164 | 38.7298 | 8.0125 | 37.4319 | 12.0581 | 75.7347 | 8.0069 | 37.4495
AGWA | Agnes Water | CA | AGWA_66kV_BUS 2 | 66 | 1.0951 | 125.1828 | 0.82081 | 31.277 | 0.65641 | 0.99022 | 37.7324 | 1.0164 | 38.7298 | 8.0125 | 37.4319 | 12.0581 | 75.7347 | 8.0069 | 37.4495
AGWA | Agnes Water | CA | AGWA_22kV_BUS 1 | 22 | 2.5653 | 97.752 | 3.467 | 44.0365 | 5.346 | 3.4094 | 43.3048 | 3.5407 | 44.9729 | 0.94914 | 5.3635 | 0.05954 | 1.2025 | 0.94852 | 5.3655
AGWA | Agnes Water | CA | AGWA_22kV_BUS 2 | 22 | 2.5653 | 97.752 | 3.467 | 44.0365 | 5.346 | 3.4094 | 43.3048 | 3.5407 | 44.9729 | 0.94914 | 5.3635 | 0.05954 | 1.2025 | 0.94852 | 5.3655
AITK | Aitkenvale | NQ | AITK_66kV_BUS 1 | 66 | 12.7978 | 1462.9799 | 10.0208 | 381.8441 | 8.2353 | 11.7309 | 447.0068 | 11.9128 | 453.9377 | 0.75296 | 3.1875 | 1.17 | 5.8835 | 0.73511 | 3.1928
AITK | Aitkenvale | NQ | AITK_66kV_BUS 2 | 66 | 12.7978 | 1462.9799 | 10.0208 | 381.8441 | 8.2353 | 11.7309 | 447.0068 | 11.9128 | 453.9377 | 0.75296 | 3.1875 | 1.17 | 5.8835 | 0.73511 | 3.1928
AITK | Aitkenvale (TF1) | NQ | AITK_11kV_BUS 1 | 11 | 10.1993 | 194.3224 | 10.6652 | 67.733 | 11.1769 | 10.3843 | 65.9493 | 10.5191 | 66.805 | 0.05441 | 0.68278 | 0.0335 | 0.59424 | 0.05392 | 0.68293
AITK | Aitkenvale (TF2) | NQ | AITK_11kV_BUS 2 | 11 | 10.1993 | 194.3224 | 10.6652 | 67.733 | 11.1769 | 10.3843 | 65.9493 | 10.5191 | 66.805 | 0.05441 | 0.68278 | 0.0335 | 0.59424 | 0.05392 | 0.68293
ALCR | Alligator Creek T065 | MK | ALCR_33kV_BUS 1 | 33 | 11.8943 | 679.8504 | 14.718 | 280.4155 | 19.6544 | 13.9886 | 266.5192 | 14.4345 | 275.0134 | 0.22788 | 1.7472 | 0.04088 | 0.72339 | 0.22558 | 1.7726
ALCR | Alligator Creek T065 | MK | ALCR_33kV_BUS 2 | 33 | 11.8943 | 679.8504 | 14.718 | 280.4155 | 19.6544 | 13.9886 | 266.5192 | 14.4345 | 275.0134 | 0.22788 | 1.7472 | 0.04088 | 0.72339 | 0.22558 | 1.7726
ALLO | Allora | SW | ALLO_11kV_BUS 3 | 11 | 1.9442 | 37.0426 | 2.3383 | 14.8501 | 2.8947 | 1.9861 | 12.6131 | 2.4324 | 15.4477 | 1.8882 | 3.0575 | 0.29275 | 1.8726 | 1.8822 | 3.0589
ALLO | Allora (Reg) | SW | ALLO_33kV_BUS | 33 | 1.1719 | 66.9824 | 0.87077 | 16.5903 | 0.67397 | 0.94588 | 18.0214 | 1.1814 | 22.5084 | 14.3586 | 10.6644 | 17.4007 | 34.2609 | 14.3054 | 10.6764
ALLO | Allora (TF1) | SW | ALLO_11kV_BUS 2 | 11 | 1.9442 | 37.0426 | 2.3383 | 14.8501 | 2.8947 | 1.9861 | 12.6131 | 2.4324 | 15.4477 | 1.8882 | 3.0575 | 0.29275 | 1.8726 | 1.8822 | 3.0589
ALLO | Allora (TF2) | SW | ALLO_11kV_BUS 1 | 11 | 1.9438 | 37.0348 | 2.3378 | 14.8471 | 2.8942 | 1.986 | 12.613 | 2.4316 | 15.443 | 1.8901 | 3.0572 | 0.29465 | 1.8723 | 1.8841 | 3.0586
ALSH | Alan Sherriff (TF1) | NQ | ALSH_11kV_BUS 1 | 11 | 9.123 | 173.8168 | 8.0871 | 51.3603 | 7.2614 | 8.5579 | 54.35 | 8.8288 | 56.0707 | 0.04308 | 0.76454 | 0 | 1.0608 | 0.04279 | 0.76474
ALSH | Alan Sherriff (TF2) | NQ | ALSH_11kV_BUS B | 11 | 9.123 | 173.8168 | 8.0778 | 51.3009 | 7.2463 | 8.5549 | 54.3308 | 8.8256 | 56.0499 | 0.04308 | 0.76454 | 0 | 1.0638 | 0.04279 | 0.76474
ALST | Alfred Street | MK | ALST_33kV_BUS 1 | 33 | 13.162 | 752.3108 | 17.7028 | 337.2844 | 27.3125 | 18.1917 | 346.5995 | 17.358 | 330.7144 | 0.26743 | 1.5697 | 0.11341 | 0.3407 | 0.26664 | 1.5817
ALST | Alfred Street | MK | ALST_33kV_BUS 2 | 33 | 13.162 | 752.3108 | 17.7028 | 337.2844 | 27.3125 | 18.1917 | 346.5995 | 17.358 | 330.7144 | 0.26743 | 1.5697 | 0.11341 | 0.3407 | 0.26664 | 1.5817
ALST | Alfred Street | MK | ALST_11kV_BUS 1 | 11 | 12.4705 | 237.5957 | 13.9167 | 88.3829 | 15.7816 | 13.2035 | 83.8534 | 13.5333 | 85.9479 | 0.0395 | 0.5588 | 0.00979 | 0.3844 | 0.03942 | 0.56014
ALST | Alfred Street | MK | ALST_11kV_BUS 2 | 11 | 12.4705 | 237.5957 | 13.9167 | 88.3829 | 15.7816 | 13.2035 | 83.8534 | 13.5333 | 85.9479 | 0.0395 | 0.5588 | 0.00979 | 0.3844 | 0.03942 | 0.56014
ALST | Alfred Street | MK | ALST_11kV_BUS 3 | 11 | 12.4705 | 237.5957 | 13.9167 | 88.3829 | 15.7816 | 13.2035 | 83.8534 | 13.5333 | 85.9479 | 0.0395 | 0.5588 | 0.00979 | 0.3844 | 0.03942 | 0.56014
ARAM | Aramara T173 | WB | ARAM_132kV_BUS 1 | 132 | 8.7308 | 1996.1217 | 8.4879 | 646.8629 | 8.376 | 8.689 | 662.1879 | 8.5313 | 650.1722 | 1.4023 | 9.4997 | 1.7428 | 10.14 | 1.3449 | 9.6506
ARAM | Aramara T173 | WB | ARAM_132kV_BUS 2 | 132 | 8.7308 | 1996.1217 | 8.4879 | 646.8629 | 8.376 | 8.689 | 662.1879 | 8.5313 | 650.1722 | 1.4023 | 9.4997 | 1.7428 | 10.14 | 1.3449 | 9.6506
ATHE | Atherton | FN | ATHE_66kV_BUS 1 | 66 | 3.285 | 375.5249 | 2.5656 | 97.7641 | 2.116 | 3.0023 | 114.405 | 3.0541 | 116.3752 | 2.832 | 12.4415 | 4.2228 | 23.0314 | 2.7352 | 12.5512
ATHE | Atherton | FN | ATHE_66kV_BUS 2 | 66 | 3.285 | 375.5249 | 2.5656 | 97.7641 | 2.116 | 3.0023 | 114.405 | 3.0541 | 116.3752 | 2.832 | 12.4415 | 4.2228 | 23.0314 | 2.7352 | 12.5512
ATHE | Atherton (TF1) | FN | ATHE_22kV_BUS 1 | 22 | 6.6027 | 251.5964 | 8.4413 | 107.2194 | 11.7627 | 7.9346 | 100.7831 | 8.4558 | 107.4035 | 0.34231 | 2.0882 | 0.00026 | 0.73092 | 0.33155 | 2.1004
ATHE | Atherton (TF2) | FN | ATHE_22kV_BUS 2 | 22 | 6.6027 | 251.5964 | 8.4413 | 107.2194 | 11.7627 | 7.9346 | 100.7831 | 8.4558 | 107.4035 | 0.34231 | 2.0882 | 0.00026 | 0.73092 | 0.33155 | 2.1004
AWOO | Awoonga | CA | AWOO_66kV_TEF T1 | 66 | 4.6752 | 534.4485 | 3.1587 | 120.3626 | 2.3898 | 4.1094 | 156.5882 | 4.3166 | 164.4847 | 3.3722 | 8.3074 | 5.9562 | 21.0724 | 3.3788 | 8.3484
AWOO | Awoonga | CA | AWOO_66kV_TEF T2 | 66 | 4.6752 | 534.4485 | 3.1587 | 120.3626 | 2.3898 | 4.1094 | 156.5882 | 4.3166 | 164.4847 | 3.3722 | 8.3074 | 5.9562 | 21.0724 | 3.3788 | 8.3484
AWOO | Awoonga | CA | AWOO_11kV_TEF T1 | 11 | 9.9563 | 189.6932 | 11.0706 | 70.3076 | 12.5741 | 10.3271 | 65.5857 | 10.971 | 69.6752 | 0.12374 | 0.69068 | 0.0313 | 0.4849 | 0.12261 | 0.6971
AWOO | Awoonga | CA | AWOO_11kV_TEF T2 | 11 | 9.9563 | 189.6932 | 11.0706 | 70.3076 | 12.5741 | 10.3271 | 65.5857 | 10.971 | 69.6752 | 0.12374 | 0.69068 | 0.0313 | 0.4849 | 0.12261 | 0.6971
AYRZ | Ayr | NQ | AYRZ_66kV_BUS 1 | 66 | 6.1093 | 698.3865 | 5.1991 | 198.1122 | 4.5069 | 5.6473 | 215.1922 | 5.867 | 223.5618 | 1.9847 | 6.5676 | 2.1767 | 10.2805 | 1.8813 | 6.5712
AYRZ | Ayr | NQ | AYRZ_66kV_BUS 2 | 66 | 6.1093 | 698.3865 | 5.1991 | 198.1122 | 4.5069 | 5.6473 | 215.1922 | 5.867 | 223.5618 | 1.9847 | 6.5676 | 2.1767 | 10.2805 | 1.8813 | 6.5712
AYRZ | Ayr | NQ | AYRZ_66kV_BUS 3 | 66 | 6.1093 | 698.3865 | 5.1991 | 198.1122 | 4.5069 | 5.6473 | 215.1922 | 5.867 | 223.5618 | 1.9847 | 6.5676 | 2.1767 | 10.2805 | 1.8813 | 6.5712
AYRZ | Ayr (TF2) | NQ | AYRZ_11kV_BUS 2 | 11 | 5.2009 | 99.0914 | 5.4539 | 34.6366 | 5.7312 | 5.2923 | 33.611 | 5.3845 | 34.1964 | 0.12923 | 1.337 | 0.0741 | 1.1545 | 0.12636 | 1.3371
AYRZ | Ayr (TF3) | NQ | AYRZ_11kV_BUS 3 | 11 | 5.5268 | 105.3001 | 5.8126 | 36.9148 | 6.1279 | 5.6275 | 35.7397 | 5.7384 | 36.4438 | 0.10912 | 1.2593 | 0.05399 | 1.0769 | 0.10625 | 1.2594
BABI | Babinda | FN | BABI_22kV_BUS 1 | 22 | 1.2442 | 47.4102 | 0.79119 | 10.0495 | 0.56916 | 1.0158 | 12.9029 | 1.2046 | 15.301 | 7.7432 | 8.1332 | 10.832 | 29.7007 | 7.7356 | 8.1489
BALB | Balberra | MK | BALB_33kV_TEF T1 | 33 | 4.4867 | 256.4464 | 2.9482 | 56.1714 | 2.1995 | 3.8783 | 73.8909 | 4.1717 | 79.4808 | 1.8354 | 4.2955 | 2.794 | 11.6966 | 1.8341 | 4.3308
BALB | Balberra | MK | BALB_11kV_TEF T1 | 11 | 3.511 | 66.8935 | 3.8289 | 24.3167 | 4.2157 | 3.6035 | 22.8851 | 3.7908 | 24.0749 | 0.27858 | 1.9701 | 0.07464 | 1.4929 | 0.27843 | 1.9741
BALB | Balberra (with MACK G1) | MK | BALB_1MB REG | 11 | 3.4735 | 66.1786 | 3.7852 | 24.039 | 4.221 | 3.6087 | 22.9184 | 3.7474 | 23.7991 | 0.29865 | 1.9889 | 0.08803 | 1.5054 | 0.29181 | 1.9866
BALB | Balberra (with MACK G1) | MK | MOUNT ALICE | 11 | 3.4735 | 66.1786 | 3.7852 | 24.039 | 4.221 | 3.6087 | 22.9184 | 3.7474 | 23.7991 | 0.29865 | 1.9889 | 0.08803 | 1.5054 | 0.29181 | 1.9866
BAMB | Bambaroo | NQ | BAMB_66kV_TEF T1 | 66 | 1.6 | 182.9021 | 1.2784 | 48.7118 | 1.0696 | 1.4439 | 55.0184 | 1.5186 | 57.8645 | 14.0937 | 22.0836 | 20.5254 | 41.0589 | 14.018 | 22.3583
BAMB | Bambaroo | NQ | BAMB_11kV_BUS | 11 | 1.2382 | 23.5914 | 1.2884 | 8.1826 | 1.3566 | 1.2545 | 7.9673 | 1.286 | 8.1673 | 0.92188 | 5.5661 | 0.51738 | 4.9397 | 0.90677 | 5.5608
BARC | Barcaldine T072 | CA | BARC_132kV_BUS 1 | 132 | 1.7837 | 407.803 | 1.5782 | 120.2777 | 1.685 | 1.6547 | 126.1058 | 1.6943 | 129.119 | 6.1521 | 46.5949 | 5.2674 | 55.5994 | 7.6282 | 56.0148
BARC | Barcaldine T072 | CA | BARC_132kV_BUS 2 | 132 | 1.7837 | 407.803 | 1.5782 | 120.2777 | 1.685 | 1.6547 | 126.1058 | 1.6943 | 129.119 | 6.1521 | 46.5949 | 5.2674 | 55.5994 | 7.6282 | 56.0148
BARC | Barcaldine T072 | CA | BARC_66kV_BUS 1 | 66 | 1.672 | 191.1311 | 1.8634 | 71.0051 | 2.3643 | 1.862 | 70.9503 | 1.8182 | 69.2813 | 2.1781 | 24.975 | 1.9744 | 14.6253 | 2.4139 | 27.5622
BARC | Barcaldine T072 | CA | BARC_66kV_BUS 2 | 66 | 1.5354 | 175.5188 | 1.8578 | 70.7897 | 2.626 | 1.8758 | 71.478 | 1.8275 | 69.6351 | 2.4705 | 27.1877 | 1.5779 | 10.6158 | 2.5288 | 29.564
BARC | Barcaldine T072 | CA | BARC_66kV_BUS 3 | 66 | 1.5354 | 175.5188 | 1.8578 | 70.7897 | 2.626 | 1.8758 | 71.478 | 1.8275 | 69.6351 | 2.4705 | 27.1877 | 1.5779 | 10.6158 | 2.5288 | 29.564
BARC | Barcaldine T072 (TF1) | CA | BARC_11kV_BUS 1 | 11 | 5.6684 | 107.9966 | 0.31323 | 1.9893 | 0.16571 | 4.7666 | 30.2721 | 4.7797 | 30.3555 | 0.09792 | 1.2286 | 1e-05 | 64.3808 | 0.10432 | 1.2995
BARC | Barcaldine T072 (TF2) | CA | BARC_11kV_BUS 2 | 11 | 6.0727 | 115.6997 | 0.30757 | 1.9533 | 0.16225 | 5.1094 | 32.4494 | 5.122 | 32.5287 | 0.09275 | 1.1466 | 1e-05 | 65.7811 | 0.09453 | 1.2121
BARC | Barcaldine T072 (TF5) | CA | BARC_22kV_BUS LH | 22 | 2.405 | 91.6415 | 2.5569 | 32.4772 | 2.9804 | 2.5171 | 31.9718 | 2.526 | 32.084 | 0.41554 | 5.7947 | 0.21436 | 4.2866 | 0.35424 | 6.2821
BARC | Barcaldine T072 (TF6) | CA | BARC_22kV_BUS RH | 22 | 3.025 | 115.2664 | 3.457 | 43.9102 | 4.4575 | 3.3875 | 43.0267 | 3.4084 | 43.2923 | 0.25159 | 4.612 | 0.08331 | 2.4895 | 0.23023 | 5.0101
BARG | Bargara | WB | BARG_66kV_BUS 1 | 66 | 3.4055 | 389.3071 | 2.5074 | 95.5447 | 1.9957 | 3.1275 | 119.1727 | 3.0827 | 117.4651 | 3.0591 | 11.9228 | 6.932 | 24.4868 | 3.0245 | 12.0263
BARG | Bargara | WB | BARG_11kV_BUS 1 | 11 | 9.8316 | 187.3177 | 11.5647 | 73.4459 | 14.0922 | 10.7807 | 68.4668 | 11.3048 | 71.7948 | 0.10046 | 0.70347 | 0.01788 | 0.38947 | 0.09835 | 0.70641
BARG | Bargara | WB | BARG_11kV_BUS 2 | 11 | 9.8316 | 187.3177 | 11.5647 | 73.4459 | 14.0922 | 10.7807 | 68.4668 | 11.3048 | 71.7948 | 0.10046 | 0.70347 | 0.01788 | 0.38947 | 0.09835 | 0.70641
BARR | Barratta | NQ | BARR_66kV_TEF T1 | 66 | 2.2404 | 256.111 | 1.549 | 59.0249 | 1.175 | 1.9304 | 73.5563 | 2.124 | 80.9345 | 9.8175 | 15.9263 | 14.7006 | 41.7526 | 9.7142 | 15.9298
BARR | Barratta | NQ | BARR_11kV_TEF T1 | 11 | 3.4558 | 65.8428 | 3.7345 | 23.7172 | 4.0557 | 3.4987 | 22.22 | 3.7284 | 23.6785 | 0.43599 | 1.9739 | 0.16328 | 1.5683 | 0.43312 | 1.974
BEEC | Beecher Switching | CA | BEEC_66kV_pole2112125_tr_line_33766 | 66 | 5.1857 | 592.8007 | 3.6002 | 137.1843 | 2.7548 | 4.541 | 173.0354 | 4.8424 | 184.5211 | 3.2089 | 7.4189 | 4.9899 | 18.1593 | 3.2088 | 7.4354
BEGA | Belgian Gardens | NQ | BEGA_11kV_BUS 1 | 11 | 16.7995 | 320.0732 | 17.718 | 112.5246 | 18.7457 | 17.1724 | 109.0595 | 17.4381 | 110.747 | 0.02495 | 0.41509 | 0.01121 | 0.35099 | 0.02444 | 0.41522
BEGA | Belgian Gardens (TF1) | NQ | BEGA_66kV_TEF T1 | 66 | 16.925 | 1934.7869 | 18.428 | 702.2029 | 20.2225 | 17.8825 | 681.4133 | 17.7309 | 675.636 | 0.59765 | 2.4034 | 0.46501 | 1.8121 | 0.57916 | 2.4078
BEGA | Belgian Gardens (TF2) | NQ | BEGA_66kV_TEF T2 | 66 | 16.9352 | 1935.9592 | 18.4394 | 702.6355 | 20.2353 | 17.8922 | 681.7835 | 17.743 | 676.0993 | 0.59634 | 2.4021 | 0.46352 | 1.8112 | 0.57785 | 2.4065
BENA | Benarkin | WB | BENA_66kV_BUS 1 | 66 | 2.5458 | 291.0211 | 1.5554 | 59.2672 | 1.1141 | 2.1711 | 82.7307 | 2.3714 | 90.3606 | 7.365 | 14.728 | 11.7588 | 46.9224 | 7.3621 | 14.7354
BENA | Benarkin | WB | BENA_11kV_TEF T1 | 11 | 3.502 | 66.722 | 3.7796 | 24.0039 | 4.1037 | 3.5819 | 22.7478 | 3.7391 | 23.7465 | 0.40081 | 1.9544 | 0.19625 | 1.5454 | 0.40073 | 1.9546
BERS | Berserker | CA | BERS_66kV_BUS 1 | 66 | 9.0382 | 1033.2041 | 8.3662 | 318.7953 | 7.8236 | 8.8115 | 335.763 | 8.6631 | 330.109 | 1.0408 | 4.5194 | 1.4459 | 5.5476 | 1.0406 | 4.5438
BERS | Berserker | CA | BERS_66kV_BUS 2 | 66 | 9.0382 | 1033.2041 | 8.3662 | 318.7953 | 7.8236 | 8.8115 | 335.763 | 8.6631 | 330.109 | 1.0408 | 4.5194 | 1.4459 | 5.5476 | 1.0406 | 4.5438
BERS | Berserker | CA | BERS_11kV_BUS 1 | 11 | 14.6617 | 279.3423 | 16.0879 | 102.1718 | 17.8448 | 15.2869 | 97.0846 | 15.7387 | 99.954 | 0.04013 | 0.47479 | 0.01122 | 0.34925 | 0.04012 | 0.47547
BERS | Berserker | CA | BERS_11kV_BUS 2 | 11 | 14.6617 | 279.3423 | 16.0879 | 102.1718 | 17.8448 | 15.2869 | 97.0846 | 15.7387 | 99.954 | 0.04013 | 0.47479 | 0.01122 | 0.34925 | 0.04012 | 0.47547
BERS | Berserker | CA | BERS_11kV_BUS 3 | 11 | 14.6617 | 279.3423 | 16.0879 | 102.1718 | 17.8448 | 15.2869 | 97.0846 | 15.7387 | 99.954 | 0.04013 | 0.47479 | 0.01122 | 0.34925 | 0.04012 | 0.47547
BEWE | Bedford Weir | CA | BEWE_66kV_BUS 1 | 66 | 2.9505 | 337.2841 | 2.1176 | 80.6903 | 1.6461 | 2.6049 | 99.2592 | 2.765 | 105.362 | 6.1945 | 12.7849 | 10.0124 | 29.4546 | 6.2106 | 12.7492
BEWE | Bedford Weir | CA | BEWE_66kV_BUS 2 | 66 | 2.9505 | 337.2841 | 2.1176 | 80.6903 | 1.6461 | 2.6049 | 99.2592 | 2.765 | 105.362 | 6.1945 | 12.7849 | 10.0124 | 29.4546 | 6.2106 | 12.7492
BEWE | Bedford Weir | CA | BEWE_66kV_BUS TRANSFER | 66 | 2.9505 | 337.2841 | 2.1176 | 80.6903 | 1.6461 | 2.6049 | 99.2592 | 2.765 | 105.362 | 6.1945 | 12.7849 | 10.0124 | 29.4546 | 6.2106 | 12.7492
BEWE | Bedford Weir | CA | BEWE_22kV_BUS 1 | 22 | 4.1066 | 156.484 | 4.8377 | 61.4474 | 5.8641 | 4.3994 | 55.8805 | 4.8112 | 61.1105 | 0.82527 | 3.3007 | 0.13699 | 1.8801 | 0.82706 | 3.2967
BEWE | Bedford Weir | CA | BEWE_22kV_BUS 2 | 22 | 4.1066 | 156.484 | 4.8377 | 61.4474 | 5.8641 | 4.3994 | 55.8805 | 4.8112 | 61.1105 | 0.82527 | 3.3007 | 0.13699 | 1.8801 | 0.82706 | 3.2967
BILO | Biloela T026 | CA | BILO_66KV TRANSFER BUS | 66 | 8.078 | 923.4379 | 9.8929 | 376.9704 | 12.8226 | 9.5517 | 363.9694 | 9.4168 | 358.8298 | 0.57906 | 5.1566 | 0.32724 | 2.2907 | 0.57989 | 5.1766
BILO | Biloela T026 | CA | BILO_66kV_BUS NORTH | 66 | 8.078 | 923.4379 | 9.8929 | 376.9704 | 12.8226 | 9.5517 | 363.9694 | 9.4168 | 358.8298 | 0.57906 | 5.1566 | 0.32724 | 2.2907 | 0.57989 | 5.1766
BILO | Biloela T026 | CA | BILO_66kV_BUS SOUTH | 66 | 8.078 | 923.4379 | 9.8929 | 376.9704 | 12.8226 | 9.5517 | 363.9694 | 9.4168 | 358.8298 | 0.57906 | 5.1566 | 0.32724 | 2.2907 | 0.57989 | 5.1766
BILO | Biloela T026 (TF1) | CA | BILO_11kV_BUS 1 | 11 | 15.8141 | 301.2987 | 17.7335 | 112.6231 | 20.2116 | 16.9247 | 107.4862 | 17.1075 | 108.6471 | 0.03146 | 0.44064 | 0.01537 | 0.2974 | 0.03148 | 0.4412
BILO | Biloela T026 (TF2) | CA | BILO_11kV_BUS 2 | 11 | 15.8141 | 301.2987 | 17.7335 | 112.6231 | 20.2116 | 16.9247 | 107.4862 | 17.1075 | 108.6471 | 0.03146 | 0.44064 | 0.01537 | 0.2974 | 0.03148 | 0.4412
BING | Bingegang | CA | BING_66kV_BUS 3 | 66 | 0.9661 | 110.4399 | 0.60555 | 23.0747 | 0.43867 | 0.82685 | 31.5071 | 0.90173 | 34.3605 | 22.5152 | 37.0876 | 40.4319 | 115.108 | 22.5313 | 37.0518
BING | Bingegang | CA | BING_22kV_BUS 1 | 22 | 1.8547 | 70.6719 | 2.3463 | 29.8024 | 3.1756 | 2.1144 | 26.8562 | 2.3941 | 30.4094 | 2.7652 | 7.0076 | 0.26352 | 2.8868 | 2.767 | 7.0037
BLAC | Blackwater T032 | CA | BLAC_66kV_BUS EAST | 66 | 8.4954 | 971.1568 | 11.1221 | 423.8078 | 15.9428 | 10.6672 | 406.4741 | 11.0368 | 420.5569 | 0.87983 | 4.8549 | 0.13687 | 1.4691 | 0.89593 | 4.8191
BLAC | Blackwater T032 | CA | BLAC_66kV_BUS TRANSFER | 66 | 8.4954 | 971.1568 | 11.1221 | 423.8078 | 15.9428 | 10.6672 | 406.4741 | 11.0368 | 420.5569 | 0.87983 | 4.8549 | 0.13687 | 1.4691 | 0.89593 | 4.8191
BLAC | Blackwater T032 | CA | BLAC_66kV_BUS WEST | 66 | 8.4954 | 971.1568 | 11.1221 | 423.8078 | 15.9428 | 10.6672 | 406.4741 | 11.0368 | 420.5569 | 0.87983 | 4.8549 | 0.13687 | 1.4691 | 0.89593 | 4.8191
BLAC | Blackwater T032 | CA | BLAC_22kV_BUS 1 | 22 | 6.3293 | 241.1787 | 5.2375 | 66.5257 | 4.454 | 5.7476 | 73.0042 | 6.0873 | 77.3195 | 0.23475 | 2.195 | 0.00025 | 3.6033 | 0.23669 | 2.1908
BLAC | Blackwater T032 | CA | BLAC_22kV_BUS 2 | 22 | 6.3293 | 241.1787 | 5.2375 | 66.5257 | 4.454 | 5.7476 | 73.0042 | 6.0873 | 77.3195 | 0.23475 | 2.195 | 0.00025 | 3.6033 | 0.23669 | 2.1908
BLAC | Blackwater T032 (TF4) | CA | BLAC_11kV_TEF T4 | 11 | 19.2602 | 366.9557 | 8.3437 | 52.9896 | 5.3104 | 16.6327 | 105.6317 | 17.1806 | 109.1113 | 0.04112 | 0.36038 | 2e-05 | 1.7907 | 0.04159 | 0.35938
BLAC | Blackwater T032 (TF5) | CA | BLAC_11kV_TEF T5 | 11 | 25.4972 | 485.786 | 14.6948 | 93.3248 | 10.2796 | 22.1907 | 140.93 | 23.2098 | 147.4018 | 0.03155 | 0.27217 | 1e-05 | 0.88154 | 0.03205 | 0.27108
BLAK | Blackall | CA | BLAK_66kV_BUS | 66 | 0.54759 | 62.5979 | 0.37724 | 14.3748 | 0.29447 | 0.4791 | 18.2563 | 0.50195 | 19.1269 | 29.4092 | 70.6709 | 50.1209 | 171.0203 | 29.645 | 73.2581
BLAK | Blackall (TF1) | CA | BLAK_22kV_BUS 1 | 22 | 0.979 | 37.3048 | 1.2087 | 15.3525 | 1.6177 | 1.1219 | 14.25 | 1.2144 | 15.4255 | 3.7948 | 13.7579 | 0.52711 | 5.9056 | 3.821 | 14.0453
BLAK | Blackall (TF2) | CA | BLAK_22kV_BUS 2 | 22 | 0.979 | 37.3048 | 1.2087 | 15.3525 | 1.6177 | 1.1219 | 14.25 | 1.2144 | 15.4255 | 3.7948 | 13.7579 | 0.52711 | 5.9056 | 3.821 | 14.0453
BLOO | Bloomfield SS | FN | BLOO_22kV_BUS | 22 | 0.46664 | 17.7815 | 0.3424 | 4.349 | 0.26852 | 0.40819 | 5.1848 | 0.44405 | 5.6402 | 11.9264 | 27.4634 | 14.6759 | 61.4005 | 11.8537 | 27.3581
BLRI | Black River | NQ | BLRI_66kV_BUS 1 | 66 | 10.3325 | 1181.1585 | 8.9048 | 339.3176 | 7.8181 | 9.6859 | 369.0816 | 9.8477 | 375.2464 | 0.79816 | 3.9774 | 0.93464 | 5.9398 | 0.75079 | 3.984
BLRI | Black River | NQ | BLRI_66kV_BUS 2 | 66 | 10.3325 | 1181.1585 | 8.9048 | 339.3176 | 7.8181 | 9.6859 | 369.0816 | 9.8477 | 375.2464 | 0.79816 | 3.9774 | 0.93464 | 5.9398 | 0.75079 | 3.984
BLRI | Black River | NQ | BLRI_11kV_BUS 3 | 11 | 7.1223 | 135.6976 | 7.328 | 46.5389 | 7.425 | 7.199 | 45.7198 | 7.2536 | 46.0668 | 0.05671 | 0.97922 | 0.0363 | 0.91294 | 0.051 | 0.96419
BLRI | Black River (TF1) | NQ | BLRI_11kV_BUS 1 | 11 | 7.8364 | 149.3033 | 8.1773 | 51.9328 | 8.5499 | 7.9789 | 50.6726 | 8.062 | 51.2005 | 0.05554 | 0.88974 | 0.03337 | 0.77926 | 0.05423 | 0.88993
BLRI | Black River (TF2) | NQ | BLRI_11kV_BUS 2 | 11 | 7.1223 | 135.6976 | 7.328 | 46.5389 | 7.425 | 7.199 | 45.7198 | 7.2536 | 46.0668 | 0.05671 | 0.97922 | 0.0363 | 0.91294 | 0.051 | 0.96419
BLUE | Bluewater | NQ | BLUE_66kV_TEF T1 | 66 | 3.5569 | 406.6035 | 2.5596 | 97.5339 | 1.9811 | 3.0407 | 115.8661 | 3.4242 | 130.4778 | 6.7893 | 9.6322 | 9.1501 | 24.3074 | 6.742 | 9.6388
BLUE | Bluewater | NQ | BLUE_11kV_BUS 1 | 11 | 3.7056 | 70.6006 | 3.9056 | 24.8036 | 4.1246 | 3.7126 | 23.5784 | 3.9141 | 24.8577 | 0.26852 | 1.866 | 0.07992 | 1.5985 | 0.2672 | 1.8662
BLVA | Blue Valley T183 | NQ | BLVA_132kV_TEF T1 | 132 | 3.5677 | 815.6951 | 2.3551 | 179.4833 | 1.7572 | 3.1842 | 242.6714 | 3.2403 | 246.941 | 7.5549 | 22.2494 | 17.0235 | 57.3418 | 7.5744 | 22.2403
BLVA | Blue Valley T183 | NQ | BLVA_11kV_BUS 1 | 11 | 8.2198 | 156.6092 | 5.6724 | 36.0249 | 4.3246 | 7.2589 | 46.1003 | 7.6166 | 48.3721 | 0.08884 | 0.84523 | 0 | 2 | 0.08898 | 0.84517
BOCR | Boat Creek T130 | CA | BOCR_66kV_BUS 1 | 66 | 10.2039 | 1166.4662 | 12.3468 | 470.4775 | 15.7592 | 11.9759 | 456.3425 | 11.6802 | 445.076 | 0.15109 | 4.1051 | 0.17039 | 1.9361 | 0.14829 | 4.1327
BOCR | Boat Creek T130 | CA | BOCR_66kV_BUS 2 | 66 | 10.2039 | 1166.4662 | 12.3468 | 470.4775 | 15.7592 | 11.9759 | 456.3425 | 11.6802 | 445.076 | 0.15109 | 4.1051 | 0.17039 | 1.9361 | 0.14829 | 4.1327
BOCR | Boat Creek T130 | CA | BOCR_66kV_BUS 3 | 66 | 10.2039 | 1166.4662 | 12.3468 | 470.4775 | 15.7592 | 11.9759 | 456.3425 | 11.6802 | 445.076 | 0.15109 | 4.1051 | 0.17039 | 1.9361 | 0.14829 | 4.1327
BOCR | Boat Creek T130 (TF1) | CA | BOCR_132kV_TEF T1 | 132 | 12.2906 | 2810.0201 | 13.4636 | 1026.0671 | 15.1603 | 13.184 | 1004.7585 | 12.8635 | 980.3284 | 0.39193 | 6.8096 | 0.50248 | 4.9013 | 0.40108 | 6.924
BOCR | Boat Creek T130 (TF1) | CA | BOCR_11kV_TEF T1 | 11 | 22.5918 | 430.4314 | 0 | 0 | 0 | 19.541 | 124.1023 | 19.541 | 124.1023 | 0.01666 | 0.30878 | 135802466.7808 | -9.306 | 0.0166 | 0.30955
BOCR | Boat Creek T130 (TF2) | CA | BOCR_132kV_TEF T2 | 132 | 12.3526 | 2824.1866 | 13.56 | 1033.4121 | 15.3102 | 13.2675 | 1011.1183 | 12.9542 | 987.2386 | 0.38443 | 6.7758 | 0.4862 | 4.838 | 0.39359 | 6.8902
BOCR | Boat Creek T130 (TF2) | CA | BOCR_11kV_TEF T2 | 11 | 22.8803 | 435.9287 | 0 | 0 | 0 | 19.7903 | 125.6854 | 19.7903 | 125.6854 | 0.01676 | 0.30487 | 135802469.4643 | -0.39741 | 0.0167 | 0.30564
BODA | Boondooma Dam | WB | BODA_66kV_BUS OVERHEAD | 66 | 1.0349 | 118.3024 | 0.58164 | 22.1634 | 0.40268 | 0.88237 | 33.6229 | 0.95311 | 36.3184 | 17.0505 | 36.7446 | 30.4786 | 132.8214 | 17.007 | 36.771
BODA | Boondooma Dam (TF1) | WB | BODA_11kV_BUS 1 | 11 | 2.9197 | 55.6272 | 3.4504 | 21.9133 | 4.2112 | 3.1627 | 20.0861 | 3.4128 | 21.6739 | 0.62026 | 2.3112 | 0.14664 | 1.2906 | 0.61905 | 2.3119
BODA | Boondooma Dam (TF2) | WB | BODA_11kV_BUS 2 | 11 | 2.9197 | 55.6272 | 3.4504 | 21.9133 | 4.2112 | 3.1627 | 20.0861 | 3.4128 | 21.6739 | 0.62026 | 2.3112 | 0.14664 | 1.2906 | 0.61905 | 2.3119
BOHL | Bohle | NQ | BOHL_66kV_BUS 1 | 66 | 13.012 | 1487.4717 | 10.7869 | 411.0368 | 9.211 | 12.1557 | 463.1936 | 12.1923 | 464.5874 | 0.67083 | 3.1507 | 1.0066 | 5.1172 | 0.63943 | 3.157
BOHL | Bohle | NQ | BOHL_66kV_BUS 2 | 66 | 13.012 | 1487.4717 | 10.7869 | 411.0368 | 9.211 | 12.1557 | 463.1936 | 12.1923 | 464.5874 | 0.67083 | 3.1507 | 1.0066 | 5.1172 | 0.63943 | 3.157
BOHL | Bohle | NQ | BOHL_66kV_BUS 3 | 66 | 13.012 | 1487.4717 | 10.7869 | 411.0368 | 9.211 | 12.1557 | 463.1936 | 12.1923 | 464.5874 | 0.67083 | 3.1507 | 1.0066 | 5.1172 | 0.63943 | 3.157
BOHL | Bohle (TF1) | NQ | BOHL_11kV_BUS 1 | 11 | 10.9804 | 209.2048 | 11.5141 | 73.1241 | 12.1039 | 11.2027 | 71.1468 | 11.3396 | 72.016 | 0.04524 | 0.63461 | 0.0266 | 0.54709 | 0.04437 | 0.63478
BOHL | Bohle (TF2) | NQ | BOHL_11kV_BUS 2 | 11 | 11.0108 | 209.7832 | 11.4433 | 72.6746 | 11.9038 | 11.1761 | 70.9778 | 11.3078 | 71.8142 | 0.04589 | 0.6328 | 0.02759 | 0.56229 | 0.04398 | 0.63259
BOPU | Bocoolima Pumps | CA | BOPU_66kV_TEF T1 | 66 | 1.4145 | 161.7042 | 0.85837 | 32.7084 | 0.61336 | 1.2071 | 45.9958 | 1.3155 | 50.1253 | 14.3887 | 25.9048 | 25.4135 | 84.2692 | 14.3886 | 25.9325
BOPU | Bocoolima Pumps | CA | BOPU_66kV_TEF T2 | 66 | 1.4145 | 161.7042 | 0.85837 | 32.7084 | 0.61336 | 1.2071 | 45.9958 | 1.3155 | 50.1253 | 14.3887 | 25.9048 | 25.4135 | 84.2692 | 14.3886 | 25.9325
BOPU | Bocoolima Pumps | CA | BOPU_11kV_TEF T1 | 11 | 3.7592 | 71.6221 | 4.3797 | 27.8151 | 5.2311 | 3.9545 | 25.1144 | 4.386 | 27.8548 | 0.45381 | 1.8021 | 0.05413 | 1.0826 | 0.45381 | 1.8029
BOPU | Bocoolima Pumps | CA | BOPU_11kV_TEF T2 | 11 | 3.7592 | 71.6221 | 4.3797 | 27.8151 | 5.2311 | 3.9545 | 25.1144 | 4.386 | 27.8548 | 0.45381 | 1.8021 | 0.05413 | 1.0826 | 0.45381 | 1.8029
BORE | Boyne Residential | CA | BORE_66kV_TEF T1 | 66 | 4.0984 | 468.5153 | 2.8173 | 107.3523 | 2.145 | 3.5772 | 136.3076 | 3.8272 | 145.8342 | 4.5244 | 9.1722 | 7.394 | 23.1225 | 4.5265 | 9.2008
BORE | Boyne Residential | CA | BORE_66kV_TEF T2 | 66 | 4.0984 | 468.5153 | 2.8173 | 107.3523 | 2.145 | 3.5772 | 136.3076 | 3.8272 | 145.8342 | 4.5244 | 9.1722 | 7.394 | 23.1225 | 4.5265 | 9.2008
BORE | Boyne Residential | CA | BORE_11kV_BUS LH | 11 | 8.6983 | 165.7248 | 9.8104 | 62.3045 | 11.2429 | 9.0491 | 57.4693 | 9.7336 | 61.8168 | 0.16433 | 0.78617 | 0.03865 | 0.53138 | 0.16439 | 0.78696
BORE | Boyne Residential | CA | BORE_11kV_BUS RH | 11 | 8.6983 | 165.7248 | 9.8104 | 62.3045 | 11.2429 | 9.0491 | 57.4693 | 9.7336 | 61.8168 | 0.16433 | 0.78617 | 0.03865 | 0.53138 | 0.16439 | 0.78696
BOWE | Bowen | NQ | BOWE_66kV_BUS 1 | 66 | 2.5758 | 294.4475 | 2.4843 | 94.6657 | 2.3964 | 2.475 | 94.3092 | 2.5886 | 98.6381 | 6.5647 | 14.8904 | 6.0134 | 17.085 | 6.579 | 14.8755
BOWE | Bowen | NQ | BOWE_66kV_BUS 2 | 66 | 2.5758 | 294.4475 | 2.4843 | 94.6657 | 2.3964 | 2.475 | 94.3092 | 2.5886 | 98.6381 | 6.5647 | 14.8904 | 6.0134 | 17.085 | 6.579 | 14.8755
BOWE | Bowen | NQ | BOWE_11kV_BUS 1 | 11 | 7.9866 | 152.165 | 9.6096 | 61.0293 | 12.0225 | 8.7226 | 55.396 | 9.5854 | 60.8754 | 0.20083 | 0.85135 | 0.01847 | 0.43772 | 0.20122 | 0.85093
BOWE | Bowen | NQ | BOWE_11kV_BUS 2 | 11 | 7.9866 | 152.165 | 9.6096 | 61.0293 | 12.0225 | 8.7226 | 55.396 | 9.5854 | 60.8754 | 0.20083 | 0.85135 | 0.01847 | 0.43772 | 0.20122 | 0.85093
BROD | Broadlea | MK | BROD_132kV_BUS 1 | 132 | 3.7372 | 854.4438 | 4.1485 | 316.1582 | 4.6668 | 3.8416 | 292.7663 | 4.1294 | 314.7053 | 5.3473 | 21.7849 | 1.7426 | 15.7079 | 5.3598 | 21.8383
BROD | Broadlea | MK | BROD_132kV_BUS 2 | 132 | 3.7372 | 854.4438 | 4.1485 | 316.1582 | 4.6668 | 3.8416 | 292.7663 | 4.1294 | 314.7053 | 5.3473 | 21.7849 | 1.7426 | 15.7079 | 5.3598 | 21.8383
BROD | Broadlea | MK | BROD_66kV_BUS 1 | 66 | 5.0064 | 572.3124 | 6.3093 | 240.4174 | 8.541 | 5.9298 | 225.9546 | 6.2355 | 237.6056 | 1.4116 | 8.2525 | 0.16953 | 3.1856 | 1.4148 | 8.2659
BROD | Broadlea | MK | BROD_66kV_BUS 2 | 66 | 5.0064 | 572.3124 | 6.3093 | 240.4174 | 8.541 | 5.9298 | 225.9546 | 6.2355 | 237.6056 | 1.4116 | 8.2525 | 0.16953 | 3.1856 | 1.4148 | 8.2659
BROD | Broadlea | MK | BROD_66kV_BUS TRANSFER | 66 | 5.0064 | 572.3124 | 6.3093 | 240.4174 | 8.541 | 5.9298 | 225.9546 | 6.2355 | 237.6056 | 1.4116 | 8.2525 | 0.16953 | 3.1856 | 1.4148 | 8.2659
BROD | Broadlea | MK | BROD_11kV_TEF T1 | 11 | 14.9881 | 285.5617 | 0 | 0 | 0 | 12.9748 | 82.4011 | 12.9748 | 82.4011 | 0.04903 | 0.46352 | 108910890.0557 | -5.4146 | 0.04912 | 0.46389
BROD | Broadlea | SW | BROD_11kV_TEF T2 | 11 | 14.9646 | 285.1143 | 0 | 0 | 0 | 12.9545 | 82.2721 | 12.9545 | 82.2721 | 0.04912 | 0.46424 | 108910893.0158 | -5.3941 | 0.04921 | 0.46461
BROX | Broxburn | SW | BROX_33kV_BUS | 33 | 1.9363 | 110.6742 | 1.289 | 24.5592 | 0.94735 | 1.6733 | 31.8799 | 1.834 | 34.9417 | 5.2738 | 9.4534 | 7.9985 | 26.4215 | 5.1347 | 9.2945
BROX | Broxburn | SW | BROX_11kV_BUS T1 | 11 | 3.6997 | 70.4888 | 4.6804 | 29.7245 | 6.2448 | 4.2124 | 26.7521 | 4.732 | 30.0525 | 0.58842 | 1.7945 | 0.03716 | 0.74315 | 0.57296 | 1.7768
BROX | Broxburn | SW | BROX_11kV_BUS T3 | 11 | 3.6997 | 70.4888 | 4.6804 | 29.7245 | 6.2448 | 4.2124 | 26.7521 | 4.732 | 30.0525 | 0.58842 | 1.7945 | 0.03716 | 0.74315 | 0.57296 | 1.7768
BUCE | Bundaberg Central | WB | BUCE_66kV_BUS 1 | 66 | 5.7112 | 652.8813 | 5.0037 | 190.6647 | 4.5138 | 5.4721 | 208.5155 | 5.3486 | 203.8079 | 1.4341 | 7.1982 | 2.373 | 10.0665 | 1.4119 | 7.3204
BUCE | Bundaberg Central | WB | BUCE_66kV_BUS 2 | 66 | 5.7112 | 652.8813 | 5.0037 | 190.6647 | 4.5138 | 5.4721 | 208.5155 | 5.3486 | 203.8079 | 1.4341 | 7.1982 | 2.373 | 10.0665 | 1.4119 | 7.3204
BUCE | Bundaberg Central | WB | BUCE_11kV_BUS 1 | 11 | 15.3263 | 292.0048 | 16.4509 | 104.4772 | 18.4344 | 15.7371 | 99.9438 | 16.3516 | 103.8466 | 0.05321 | 0.45273 | 0.01131 | 0.34674 | 0.04762 | 0.46964
BUCE | Bundaberg Central | WB | BUCE_11kV_BUS 2 | 11 | 15.3263 | 292.0048 | 16.4509 | 104.4772 | 18.4344 | 15.7371 | 99.9438 | 16.3516 | 103.8466 | 0.05321 | 0.45273 | 0.01131 | 0.34674 | 0.04762 | 0.46964
BUCE | Bundaberg Central | WB | BUCE_11kV_BUS 3 | 11 | 15.3263 | 292.0048 | 16.4509 | 104.4772 | 18.4344 | 15.7371 | 99.9438 | 16.3516 | 103.8466 | 0.05321 | 0.45273 | 0.01131 | 0.34674 | 0.04762 | 0.46964
BUCR | BULLI CREEK | SW | BUCR_132kV_BUS 1 | 132 | 4.2201 | 964.8415 | 4.6343 | 353.1835 | 5.1273 | 4.536 | 345.6897 | 4.3943 | 334.8875 | 0.84427 | 19.8481 | 1.3853 | 14.5235 | 0.76104 | 19.8168
BUDA | Burdekin Dam | NQ | BUDA_33kV_BUS | 33 | 0.52817 | 30.1892 | 0.29564 | 5.6328 | 0.20365 | 0.44436 | 8.4663 | 0.49163 | 9.3668 | 19.3198 | 34.6589 | 31.5099 | 131.4546 | 19.3677 | 34.634
BUDA | Burdekin Dam | NQ | BUDA_11kV_TEF T1 | 11 | 0.57391 | 10.9344 | 0.65058 | 4.1317 | 0.74993 | 0.60285 | 3.8286 | 0.64175 | 4.0756 | 3.622 | 11.6213 | 1.4754 | 7.7703 | 3.6273 | 11.6186
BUDA | Burdekin Dam | NQ | BUDA_11kV_TEF T2 | 11 | 0.85796 | 16.3464 | 1.0419 | 6.6169 | 1.3215 | 0.94049 | 5.9729 | 1.0454 | 6.639 | 2.5401 | 7.7362 | 0.39343 | 3.8852 | 2.5454 | 7.7334
BUDG | Burnett Dam Generator | WB | BUDG_11kV_GEN BUDG G1 | 11 | 1.4376 | 27.3894 | 0.4697 | 2.983 | 0.2766 | 1.2749 | 8.0968 | 1.2593 | 7.9976 | 0.70735 | 4.8079 | 5.6719 | 34.5661 | 0.4828 | 4.7165
BULL | Bullyard | WB | BULL_66kV_BUS | 66 | 2.6374 | 301.492 | 1.8829 | 71.7487 | 1.4625 | 2.2921 | 87.3399 | 2.494 | 95.035 | 7.4785 | 14.0249 | 10.6755 | 33.5569 | 7.4536 | 14.1023
BULL | Bullyard | WB | BULL_11kV_BUS | 11 | 3.1808 | 60.6028 | 3.3937 | 21.553 | 3.6383 | 3.2238 | 20.474 | 3.3754 | 21.4369 | 0.34095 | 2.1698 | 0.13321 | 1.7802 | 0.34026 | 2.172
BUND | Bundaberg T020 | WB | BUND_132kV_BUS 1 | 132 | 7.5305 | 1721.6935 | 7.4967 | 571.3273 | 7.571 | 7.4486 | 567.6592 | 7.5782 | 577.5375 | 2.1217 | 10.9291 | 1.7225 | 10.9915 | 2.0814 | 11.1018
BUND | Bundaberg T020 | WB | BUND_132kV_BUS 2 | 132 | 7.5305 | 1721.6935 | 7.4967 | 571.3273 | 7.571 | 7.4486 | 567.6592 | 7.5782 | 577.5375 | 2.1217 | 10.9291 | 1.7225 | 10.9915 | 2.0814 | 11.1018
BUND | Bundaberg T020 | WB | BUND_66kV_BUS | 66 | 7.6358 | 872.8853 | 8.9976 | 342.8544 | 11.132 | 8.5838 | 327.0861 | 8.6681 | 330.2995 | 0.60939 | 5.4559 | 0.25077 | 2.9127 | 0.58446 | 5.5333
BUND | Bundaberg T020 | WB | BUND_66kV_TEF T1 | 66 | 7.6358 | 872.8853 | 8.9976 | 342.8544 | 11.132 | 8.5838 | 327.0861 | 8.6681 | 330.2995 | 0.60939 | 5.4559 | 0.25077 | 2.9127 | 0.58446 | 5.5333
BUND | Bundaberg T020 | WB | BUND_66kV_TEF T2 | 66 | 7.6358 | 872.8853 | 8.9976 | 342.8544 | 11.132 | 8.5838 | 327.0861 | 8.6681 | 330.2995 | 0.60939 | 5.4559 | 0.25077 | 2.9127 | 0.58446 | 5.5333
BUND | Bundaberg T020 | WB | BUND_66kV_TEF T3 | 66 | 7.6358 | 872.8853 | 8.9976 | 342.8544 | 11.132 | 8.5838 | 327.0861 | 8.6681 | 330.2995 | 0.60939 | 5.4559 | 0.25077 | 2.9127 | 0.58446 | 5.5333
BUND | Bundaberg T020 | WB | BUND_11kV_TEF T3 | 11 | 14.4761 | 275.8064 | 0 | 0 | 0 | 12.5098 | 79.448 | 12.5098 | 79.448 | 0.02988 | 0.4817 | 154929579.7161 | -5.9869 | 0.02918 | 0.48381
CABO | Caboonbah | WB | CABO_66kV_BUS 1 | 66 | 1.0161 | 116.1587 | 0.59793 | 22.7843 | 0.42066 | 0.85889 | 32.7279 | 0.94816 | 36.1298 | 20.0191 | 36.0731 | 32.2738 | 125.3276 | 20.0162 | 36.0805
CABO | Caboonbah | WB | CABO_11kV_TEF T1 | 11 | 3.263 | 62.1678 | 3.9501 | 25.0866 | 4.9876 | 3.5605 | 22.612 | 3.9657 | 25.1857 | 0.64677 | 2.0412 | 0.09069 | 1.0392 | 0.64669 | 2.0414
CACI | Cairns City | FN | CACI_22kV_BUS 1 | 22 | 12.6822 | 483.2553 | 9.1252 | 115.9057 | 7.1138 | 11.4092 | 144.9166 | 11.6943 | 148.5372 | 0.05818 | 1.1002 | 0 | 2.3936 | 0.05694 | 1.0982
CACI | Cairns City | FN | CACI_22kV_BUS 2 | 22 | 12.6822 | 483.2553 | 9.1252 | 115.9057 | 7.1138 | 11.4092 | 144.9166 | 11.6943 | 148.5372 | 0.05818 | 1.1002 | 0 | 2.3936 | 0.05694 | 1.0982
CACI | Cairns City | FN | CACI_22kV_BUS 3 | 22 | 12.6822 | 483.2553 | 9.1252 | 115.9057 | 7.1138 | 11.4092 | 144.9166 | 11.6943 | 148.5372 | 0.05818 | 1.1002 | 0 | 2.3936 | 0.05694 | 1.0982
CACI | Cairns City | FN | CACI_22kV_BUS 4 | 22 | 12.6822 | 483.2553 | 9.1252 | 115.9057 | 7.1138 | 11.4092 | 144.9166 | 11.6943 | 148.5372 | 0.05818 | 1.1002 | 0 | 2.3936 | 0.05694 | 1.0982
CACI | Cairns City (TF1) | FN | CACI_132kV_TEF T1 | 132 | 6.4124 | 1466.0789 | 7.6189 | 580.6384 | 9.3143 | 7.3502 | 560.1646 | 7.1567 | 545.4156 | 2.0166 | 12.9168 | 1.4128 | 6.8023 | 1.972 | 12.8453
CACI | Cairns City (TF2) | FN | CACI_132kV_TEF T2 | 132 | 6.4246 | 1468.8571 | 7.6607 | 583.8268 | 9.4159 | 7.3467 | 559.8948 | 7.2427 | 551.9639 | 2.0061 | 12.8934 | 1.2198 | 6.7013 | 1.9615 | 12.8219
CAFE | Cape Ferguson | NQ | CAFE_66kV_TEF T1 | 66 | 0.96486 | 110.2989 | 0.80114 | 30.5276 | 0.66658 | 0.78295 | 29.8346 | 1.003 | 38.2195 | 38.8616 | 19.4161 | 44.6317 | 59.5027 | 38.8427 | 19.4192
CAFE | Cape Ferguson | NQ | CAFE_66kV_TEF T2 | 66 | 0.96486 | 110.2989 | 0.80114 | 30.5276 | 0.66658 | 0.78295 | 29.8346 | 1.003 | 38.2195 | 38.8616 | 19.4161 | 44.6317 | 59.5027 | 38.8427 | 19.4192
CAFE | Cape Ferguson | NQ | CAFE_11kV_BUS 1 | 11 | 1.5163 | 28.89 | 1.6107 | 10.2291 | 1.7083 | 1.4618 | 9.2836 | 1.6647 | 10.5724 | 1.3828 | 4.3947 | 0.3033 | 3.8554 | 1.3823 | 4.3948
CAFE | Cape Ferguson | NQ | CAFE_11kV_TEF 1 | 11 | 1.3092 | 24.9438 | 1.379 | 8.7576 | 1.4509 | 1.2702 | 8.067 | 1.4178 | 9.0045 | 1.5795 | 5.0969 | 0.50005 | 4.5575 | 1.579 | 5.0969
CAFE | Cape Ferguson | NQ | CAFE_11kV_TEF 2 | 11 | 1.5163 | 28.89 | 1.6107 | 10.2291 | 1.7083 | 1.4618 | 9.2836 | 1.6647 | 10.5724 | 1.3828 | 4.3947 | 0.3033 | 3.8554 | 1.3823 | 4.3948
CALE | Calen | MK | CALE_66kV_BUS 1 | 66 | 0.76279 | 87.1992 | 0.53385 | 20.3426 | 0.4035 | 0.62996 | 24.0048 | 0.7472 | 28.472 | 37.2651 | 40.3837 | 47.4666 | 120.8178 | 37.2391 | 40.3055
CALE | Calen | MK | CALE_66kV_BUS 2 | 66 | 0.76279 | 87.1992 | 0.53385 | 20.3426 | 0.4035 | 0.62996 | 24.0048 | 0.7472 | 28.472 | 37.2651 | 40.3837 | 47.4666 | 120.8178 | 37.2391 | 40.3055
CALE | Calen | MK | CALE_66kV_BUS 3 | 66 | 0.76279 | 87.1992 | 0.53385 | 20.3426 | 0.4035 | 0.62996 | 24.0048 | 0.7472 | 28.472 | 37.2651 | 40.3837 | 47.4666 | 120.8178 | 37.2391 | 40.3055
CALE | Calen | MK | CALE_11kV_BUS 1 | 11 | 2.3685 | 45.1266 | 2.8203 | 17.9113 | 3.4506 | 2.4419 | 15.5085 | 2.8998 | 18.4159 | 1.1343 | 2.7226 | 0.09918 | 1.6009 | 1.1336 | 2.7205
CALE | Calen | MK | CALE_11kV_BUS 2 | 11 | 2.3685 | 45.1266 | 2.8203 | 17.9113 | 3.4506 | 2.4419 | 15.5085 | 2.8998 | 18.4159 | 1.1343 | 2.7226 | 0.09918 | 1.6009 | 1.1336 | 2.7205
CALE | Calen | MK | CALE_11kV_BUS 3 | 11 | 2.3685 | 45.1266 | 2.8203 | 17.9113 | 3.4506 | 2.4419 | 15.5085 | 2.8998 | 18.4159 | 1.1343 | 2.7226 | 0.09918 | 1.6009 | 1.1336 | 2.7205
CALL | Calliope | CA | CALL_66kV_TEF T1 | 66 | 5.2165 | 596.3234 | 3.5106 | 133.7712 | 2.6508 | 4.6345 | 176.5998 | 4.7686 | 181.7091 | 2.2065 | 7.7265 | 4.1869 | 19.2917 | 2.2065 | 7.7543
CALL | Calliope | CA | CALL_66kV_TEF T2 | 66 | 5.2165 | 596.3234 | 3.5106 | 133.7712 | 2.6508 | 4.6345 | 176.5998 | 4.7686 | 181.7091 | 2.2065 | 7.7265 | 4.1869 | 19.2917 | 2.2065 | 7.7543
CALL | Calliope | CA | CALL_11kV_BUS LH | 11 | 9.331 | 177.7802 | 10.343 | 65.687 | 11.6103 | 9.776 | 62.0858 | 10.117 | 64.2518 | 0.09777 | 0.74228 | 0.03648 | 0.52766 | 0.09777 | 0.74306
CALL | Calliope | CA | CALL_11kV_BUS RH | 11 | 9.331 | 177.7802 | 10.343 | 65.687 | 11.6103 | 9.776 | 62.0858 | 10.117 | 64.2518 | 0.09777 | 0.74228 | 0.03648 | 0.52766 | 0.09777 | 0.74306
CANN | Cannonvale (FDR P6/3) | MK | CANN_66kV_TEF T1 | 66 | 3.1009 | 354.4794 | 2.5027 | 95.3675 | 2.0785 | 2.7711 | 105.594 | 2.9988 | 114.2682 | 5.2923 | 12.4383 | 5.8258 | 22.723 | 5.2485 | 12.3421
CANN | Cannonvale (FDR P6/8) | MK | CANN_66kV_TEF T2 | 66 | 3.1009 | 354.4794 | 2.5027 | 95.3675 | 2.0785 | 2.7711 | 105.594 | 2.9988 | 114.2682 | 5.2923 | 12.4383 | 5.8258 | 22.723 | 5.2485 | 12.3421
CANN | Cannonvale (TF1) | MK | CANN_11kV_BUS 1 | 11 | 5.4598 | 104.0231 | 6.034 | 38.3211 | 6.72 | 5.6378 | 35.8049 | 5.9638 | 37.8754 | 0.19309 | 1.2649 | 0.04609 | 0.91937 | 0.19188 | 1.2622
CANN | Cannonvale (TF2) | MK | CANN_11kV_BUS 2 | 11 | 5.5121 | 105.0194 | 6.0981 | 38.7279 | 6.7996 | 5.6945 | 36.1652 | 6.027 | 38.2768 | 0.19231 | 1.2527 | 0.0453 | 0.90721 | 0.19109 | 1.25
CANO | Cairns North T093 | FN | CANO_22kV_BUS 1 | 22 | 12.0926 | 460.7884 | 8.6093 | 109.3528 | 6.6727 | 10.8662 | 138.0196 | 11.1289 | 141.3559 | 0.0596 | 1.1539 | 0 | 2.5615 | 0.05836 | 1.1519
CANO | Cairns North T093 | FN | CANO_22kV_BUS 2 | 22 | 12.0926 | 460.7884 | 8.6093 | 109.3528 | 6.6727 | 10.8662 | 138.0196 | 11.1289 | 141.3559 | 0.0596 | 1.1539 | 0 | 2.5615 | 0.05836 | 1.1519
CANO | Cairns North T093 | FN | CANO_22kV_BUS 3 | 22 | 12.0926 | 460.7884 | 8.6093 | 109.3528 | 6.6727 | 10.8662 | 138.0196 | 11.1289 | 141.3559 | 0.0596 | 1.1539 | 0 | 2.5615 | 0.05836 | 1.1519
CANO | Cairns North T093 (TF1) | FN | CANO_132kV_TEF T1 | 132 | 6.682 | 1527.7152 | 8.482 | 646.4176 | 11.4762 | 8.5541 | 651.9121 | 7.7343 | 589.4327 | 1.7126 | 12.4284 | 1.7023 | 4.4261 | 1.668 | 12.3568
CANO | Cairns North T093 (TF2) | FN | CANO_132kV_TEF T2 | 132 | 6.7116 | 1534.4784 | 8.5546 | 651.9472 | 11.6568 | 8.6377 | 658.2819 | 7.8144 | 595.5376 | 1.6889 | 12.3758 | 1.6548 | 4.2924 | 1.6443 | 12.3043
CARD | Cardwell T134 | FN | CARD_22kV_BUS 1 | 22 | 6.4558 | 245.9975 | 6.0837 | 77.273 | 5.7575 | 6.4594 | 82.0457 | 6.1048 | 77.5416 | 0.15285 | 2.1589 | 0.42988 | 2.5281 | 0.15131 | 2.1637
CARD | Cardwell T134 | FN | CARD_22kV_BUS 2 | 22 | 6.4558 | 245.9975 | 6.0837 | 77.273 | 5.7575 | 6.4594 | 82.0457 | 6.1048 | 77.5416 | 0.15285 | 2.1589 | 0.42988 | 2.5281 | 0.15131 | 2.1637
CARI | Cape River | NQ | CARI_66kV_BUS 1 | 66 | 1.8962 | 216.7652 | 2.5396 | 96.7738 | 4.0633 | 2.4806 | 94.525 | 2.7281 | 103.9548 | 8.303 | 20.4864 | 0.151 | 4.6989 | 8.273 | 21.4171
CARI | Cape River | NQ | CARI_66kV_BUS 2 | 66 | 1.8962 | 216.7652 | 2.5396 | 96.7738 | 4.0633 | 2.4806 | 94.525 | 2.7281 | 103.9548 | 8.303 | 20.4864 | 0.151 | 4.6989 | 8.273 | 21.4171
CARI | Cape River | NQ | CARI_66kV_BUS 3 | 66 | 1.8962 | 216.7652 | 2.5396 | 96.7738 | 4.0633 | 2.4806 | 94.525 | 2.7281 | 103.9548 | 8.303 | 20.4864 | 0.151 | 4.6989 | 8.273 | 21.4171
CARI | Cape River | NQ | CARI_11kV_TEF T1 | 11 | 0.9881 | 18.8259 | 1.015 | 6.4459 | 1.0471 | 0.99453 | 6.3161 | 1.0101 | 6.4149 | 0.64735 | 7.0404 | 0.41671 | 6.4713 | 0.64652 | 7.0662
CARM | Carmila | MK | CARM_33kV_TEF T1 | 33 | 0.30191 | 17.2565 | 0.23376 | 4.4538 | 0.18438 | 0.23856 | 4.5451 | 0.31094 | 5.9242 | 62.0821 | 31.0583 | 76.2809 | 117.0632 | 62.1264 | 31.1708
CARM | Carmila | MK | CARM_11kV_TEF T1 | 11 | 0.55816 | 10.6344 | 0.67962 | 4.3162 | 0.84917 | 0.54796 | 3.48 | 0.72621 | 4.612 | 7.5511 | 9.9816 | 0.65307 | 6.5307 | 7.556 | 9.9941
CAST | Canning Street | CA | CAST_66kV TRANSFER BUSBAR | 66 | 9.6578 | 1104.0294 | 9.6427 | 367.4382 | 9.6749 | 9.9031 | 377.3568 | 9.3858 | 357.6488 | 0.91183 | 4.2433 | 1.2994 | 4.1487 | 0.91308 | 4.269
CAST | Canning Street | CA | CAST_66kV_BUS | 66 | 9.6578 | 1104.0294 | 9.6427 | 367.4382 | 9.6749 | 9.9031 | 377.3568 | 9.3858 | 357.6488 | 0.91183 | 4.2433 | 1.2994 | 4.1487 | 0.91308 | 4.269
CAST | Canning Street | CA | CAST_11kV_BUS LH | 11 | 18.065 | 344.1855 | 20.1297 | 127.8407 | 22.7691 | 19.0726 | 121.1275 | 19.6073 | 124.5234 | 0.03868 | 0.38478 | 0.01336 | 0.26693 | 0.03872 | 0.38549
CAST | Canning Street | CA | CAST_11kV_BUS RH | 11 | 18.065 | 344.1855 | 20.1297 | 127.8407 | 22.7691 | 19.0726 | 121.1275 | 19.6073 | 124.5234 | 0.03868 | 0.38478 | 0.01336 | 0.26693 | 0.03872 | 0.38549
CATE | Cairns Terminal T051 | FN | CATE_22kV_BUS 1 | 22 | 12.1911 | 464.542 | 11.1974 | 142.226 | 10.2908 | 12.3769 | 157.2072 | 11.0894 | 140.854 | 0.05147 | 1.1449 | 0.34572 | 1.4287 | 0.05023 | 1.1429
CATE | Cairns Terminal T051 | FN | CATE_22kV_BUS 2 | 22 | 12.1911 | 464.542 | 11.1974 | 142.226 | 10.2908 | 12.3769 | 157.2072 | 11.0894 | 140.854 | 0.05147 | 1.1449 | 0.34572 | 1.4287 | 0.05023 | 1.1429
CATE | Cairns Terminal T051 | FN | CATE_22kV_BUS 3 | 22 | 12.1911 | 464.542 | 11.1974 | 142.226 | 10.2908 | 12.3769 | 157.2072 | 11.0894 | 140.854 | 0.05147 | 1.1449 | 0.34572 | 1.4287 | 0.05023 | 1.1429
CATE | Cairns Terminal T051 | FN | CATE_22kV_BUS 4 | 22 | 12.1911 | 464.542 | 11.1974 | 142.226 | 10.2908 | 12.3769 | 157.2072 | 11.0894 | 140.854 | 0.05147 | 1.1449 | 0.34572 | 1.4287 | 0.05023 | 1.1429
CAWD | Cawdor | SW | CAWD_33kV_TEF T1 | 33 | 4.1677 | 238.2186 | 1.0033 | 19.1156 | 0.53338 | 3.8507 | 73.3661 | 3.3742 | 64.2862 | 1.122 | 4.9026 | 56.6656 | 11.614 | 1.1146 | 4.9009
CAWD | Cawdor | SW | CAWD_11kV_BUS | 11 | 4.4181 | 84.1764 | 5.0059 | 31.7915 | 5.7717 | 4.7356 | 30.0751 | 4.8491 | 30.7956 | 0.22694 | 1.5651 | 0.10227 | 1.0203 | 0.22612 | 1.5649
CEPL | Cecil Plains | SW | CEPL_33kV_BUS | 33 | 0.93711 | 53.5631 | 0.56098 | 10.6882 | 0.39433 | 0.79186 | 15.0869 | 0.88227 | 16.8095 | 11.7886 | 19.008 | 18.8031 | 65.9549 | 11.6495 | 18.8492
CEPL | Cecil Plains | SW | CEPL_33kV_BUS T1 | 33 | 0.93711 | 53.5631 | 0.56098 | 10.6882 | 0.39433 | 0.79186 | 15.0869 | 0.88227 | 16.8095 | 11.7886 | 19.008 | 18.8031 | 65.9549 | 11.6495 | 18.8492
CEPL | Cecil Plains | SW | CEPL_33kV_BUS T3 | 33 | 0.93711 | 53.5631 | 0.56098 | 10.6882 | 0.39433 | 0.79186 | 15.0869 | 0.88227 | 16.8095 | 11.7886 | 19.008 | 18.8031 | 65.9549 | 11.6495 | 18.8492
CEPL | Cecil Plains (TF1) | SW | CEPL_11kV_BUS T1 | 11 | 1.8017 | 34.3278 | 2.2822 | 14.494 | 3.0703 | 2.0346 | 12.9216 | 2.3356 | 14.8328 | 1.3853 | 3.6219 | 0.07549 | 1.5099 | 1.3699 | 3.6042
CEPL | Cecil Plains (TF3) | SW | CEPL_11kV_BUS T3 | 11 | 1.7914 | 34.1311 | 2.2654 | 14.3873 | 3.0394 | 2.0187 | 12.8206 | 2.3171 | 14.7156 | 1.3865 | 3.6453 | 0.07667 | 1.5333 | 1.3711 | 3.6277
CHAL | Charlton | SW | CHAL_33kV_BUS | 33 | 5.5084 | 314.85 | 1.0442 | 19.8942 | 0.55069 | 5.0104 | 95.4607 | 4.54 | 86.4987 | 1.6362 | 3.4355 | 55.9525 | 4.052 | 1.6357 | 3.4311
CHAL | Charlton | SW | CHAL_11kV_TEF_T1 | 11 | 4.831 | 92.0434 | 5.3307 | 33.8546 | 5.9352 | 4.9549 | 31.4681 | 5.2988 | 33.6517 | 0.24474 | 1.4254 | 0.05218 | 1.0443 | 0.24469 | 1.4249
CHAR | Charleville | SW | CHAR_66kV_BUS 1 | 66 | 0.32252 | 36.8693 | 0.13896 | 5.2952 | 0.08859 | 0.28142 | 10.7234 | 0.28401 | 10.8224 | 42.4299 | 122.8431 | 190.0704 | 616.362 | 42.3659 | 122.9589
CHAR | Charleville | SW | CHAR_66kV_BUS 2 | 66 | 0.32252 | 36.8693 | 0.13896 | 5.2952 | 0.08859 | 0.28142 | 10.7234 | 0.28401 | 10.8224 | 42.4299 | 122.8431 | 190.0704 | 616.362 | 42.3659 | 122.9589
CHAR | Charleville | SW | CHAR_22kV_BUS 1 | 22 | 0.74717 | 28.471 | 1.0049 | 12.7639 | 1.5329 | 0.96832 | 12.2993 | 1.0366 | 13.1663 | 4.9338 | 18.0375 | 0.21941 | 4.3883 | 4.9267 | 18.0504
CHAR | Charleville | SW | CHAR_11kV_BUS 1 | 11 | 1.5012 | 28.6013 | 2.1192 | 13.4588 | 3.6027 | 2.1696 | 13.7787 | 2.2721 | 14.4298 | 1.2324 | 4.4876 | 0.01646 | 0.59544 | 1.2306 | 4.4908
CHAR | Charleville | SW | CHAR_11kV_BUS 2 | 11 | 1.5012 | 28.6013 | 2.1192 | 13.4588 | 3.6027 | 2.1696 | 13.7787 | 2.2721 | 14.4298 | 1.2324 | 4.4876 | 0.01646 | 0.59544 | 1.2306 | 4.4908
CHIA | Chillagoe | FN | CHIA_66kV_BUS 1 | 66 | 0.64222 | 73.4152 | 0.37782 | 14.3969 | 0.26761 | 0.55278 | 21.0637 | 0.58892 | 22.4409 | 24.9205 | 60.3223 | 45.9097 | 197.8259 | 24.8959 | 60.6112
CHIA | Chillagoe | FN | CHIA_22kV_BUS 1 | 22 | 0.94745 | 36.1026 | 1.1281 | 14.3284 | 1.3943 | 1.0302 | 13.0851 | 1.1207 | 14.2344 | 3.1245 | 14.4121 | 0.35557 | 7.7096 | 3.1218 | 14.4442
CHIL | Childers | WB | CHIL_66kV_BUS 1 | 66 | 5.2092 | 595.489 | 4.6505 | 177.2083 | 4.2015 | 4.8918 | 186.4016 | 5.0576 | 192.7193 | 2.3881 | 7.6845 | 2.4892 | 10.6672 | 2.294 | 7.7212
CHIL | Childers | WB | CHIL_66kV_BUS 2 | 66 | 5.2092 | 595.489 | 4.6505 | 177.2083 | 4.2015 | 4.8918 | 186.4016 | 5.0576 | 192.7193 | 2.3881 | 7.6845 | 2.4892 | 10.6672 | 2.294 | 7.7212
CHIL | Childers | WB | CHIL_11kV_BUS A | 11 | 7.9567 | 151.5949 | 8.6779 | 55.112 | 9.548 | 8.2463 | 52.3708 | 8.5149 | 54.0767 | 0.10783 | 0.87141 | 0.04149 | 0.65795 | 0.10521 | 0.87243
CHIL | Childers | WB | CHIL_11kV_BUS B | 11 | 7.9567 | 151.5949 | 8.6779 | 55.112 | 9.548 | 8.2463 | 52.3708 | 8.5149 | 54.0767 | 0.10783 | 0.87141 | 0.04149 | 0.65795 | 0.10521 | 0.87243
CHIN | Chinchilla T013 | SW | CHIN_110kV_BUS 3 | 110 | 2.0798 | 396.2594 | 2.0385 | 129.4655 | 2.003 | 2.0498 | 130.1824 | 2.0696 | 131.4381 | 4.4619 | 33.2925 | 4.1073 | 35.3239 | 4.4437 | 33.3673
CHIN | Chinchilla T013 | SW | CHIN_110kV_BUS 4 | 110 | 2.0798 | 396.2594 | 2.0385 | 129.4655 | 2.003 | 2.0498 | 130.1824 | 2.0696 | 131.4381 | 4.4619 | 33.2925 | 4.1073 | 35.3239 | 4.4437 | 33.3673
CHIN | Chinchilla T013 (TF1) | SW | CHIN_33kV_BUS 1 | 33 | 6.1878 | 353.6788 | 5.7019 | 108.6362 | 5.2729 | 5.6572 | 107.784 | 6.2678 | 119.4179 | 0.95168 | 3.2506 | 0.40942 | 4.2728 | 0.92356 | 3.264
CHIN | Chinchilla T013 (TF2) | SW | CHIN_33kV_BUS 2 | 33 | 6.1878 | 353.6788 | 5.7019 | 108.6362 | 5.2729 | 5.6572 | 107.784 | 6.2678 | 119.4179 | 0.95168 | 3.2506 | 0.40942 | 4.2728 | 0.92356 | 3.264
CHTO | Charters Towers | NQ | CHTO_66kV_BUS 1 | 66 | 3.1871 | 364.329 | 3.1935 | 121.6877 | 3.2027 | 2.9931 | 114.0507 | 3.3695 | 128.3946 | 5.4085 | 11.9883 | 2.785 | 12.8898 | 5.3573 | 12.093
CHTO | Charters Towers | NQ | CHTO_66kV_BUS 2 | 66 | 3.1871 | 364.329 | 3.1935 | 121.6877 | 3.2027 | 2.9931 | 114.0507 | 3.3695 | 128.3946 | 5.4085 | 11.9883 | 2.785 | 12.8898 | 5.3573 | 12.093
CHTO | Charters Towers (TF1) | NQ | CHTO_11kV_BUS 1 | 11 | 4.6428 | 88.4581 | 5.0285 | 31.9352 | 5.4904 | 4.7435 | 30.1256 | 4.987 | 31.6719 | 0.20281 | 1.4909 | 0.05258 | 1.1579 | 0.20139 | 1.4938
CHTO | Charters Towers (TF2) | NQ | CHTO_11kV_BUS 2 | 11 | 4.6741 | 89.0542 | 5.0653 | 32.1692 | 5.5344 | 4.7768 | 30.3367 | 5.0233 | 31.9023 | 0.20284 | 1.4808 | 0.05261 | 1.1478 | 0.20142 | 1.4837
CHTW | Chinchilla Town | SW | CHTW_33kV_BUS MAIN | 33 | 5.4551 | 311.7984 | 4.6431 | 88.4621 | 4.032 | 4.9082 | 93.5138 | 5.3526 | 101.9802 | 1.2357 | 3.6379 | 0.94177 | 5.8223 | 1.2076 | 3.6513
CHTW | Chinchilla Town | SW | CHTW_33kV_BUS RESERVE | 33 | 5.4551 | 311.7984 | 4.6431 | 88.4621 | 4.032 | 4.9082 | 93.5138 | 5.3526 | 101.9802 | 1.2357 | 3.6379 | 0.94177 | 5.8223 | 1.2076 | 3.6513
CHTW | Chinchilla Town (TF1) | SW | CHTW_11kV_BUS CHINCHILLA NORTH | 11 | 5.9006 | 112.4214 | 6.6876 | 42.4721 | 7.7182 | 6.2333 | 39.5869 | 6.5675 | 41.709 | 0.17564 | 1.1709 | 0.03833 | 0.76667 | 0.17251 | 1.1724
CHTW | Chinchilla Town (TF2) | SW | CHTW_11kV_BUS CHINCHILLA SOUTH | 11 | 5.9006 | 112.4214 | 6.6876 | 42.4721 | 7.7182 | 6.2333 | 39.5869 | 6.5675 | 41.709 | 0.17564 | 1.1709 | 0.03833 | 0.76667 | 0.17251 | 1.1724
CHUM | Chumvale | NQ - MI | CHUM_220kV_BUS 1 and 2 no switch here | 220 | 1.4476 | 551.5976 | 1.8443 | 234.2575 | 2.6068 | 1.8135 | 230.341 | 1.7969 | 228.2386 | 8.832 | 96.1147 | 3.2978 | 32.2693 | 7.7353 | 98.0174
CHUM | Chumvale | NQ - MI | CHUM_66kV_TEF T1 | 66 | 2.2527 | 257.5237 | 2.6614 | 101.411 | 3.2858 | 2.5156 | 95.8563 | 2.5784 | 98.2519 | 1.1271 | 18.5723 | 0.05921 | 9.8816 | 1.0284 | 18.7435
CLER | Clermont T071 | CA | CLER_132kV_BUS 1 | 132 | 2.6553 | 607.0715 | 2.3374 | 178.133 | 2.3394 | 2.3934 | 182.4002 | 2.5816 | 196.7484 | 6.903 | 30.8082 | 3.9477 | 40.247 | 8.136 | 34.8529
CLER | Clermont T071 | CA | CLER_132kV_BUS 2 | 132 | 2.6553 | 607.0715 | 2.3374 | 178.133 | 2.3394 | 2.3934 | 182.4002 | 2.5816 | 196.7484 | 6.903 | 30.8082 | 3.9477 | 40.247 | 8.136 | 34.8529
CLER | Clermont T071 | CA | CLER_66kV_BUS A | 66 | 4.0234 | 459.9316 | 4.0874 | 155.7514 | 5.0494 | 4.1377 | 157.6683 | 4.1778 | 159.1964 | 1.6696 | 10.2835 | 1.1993 | 7.7971 | 2.1139 | 12.2776
CLER | Clermont T071 | CA | CLER_66kV_BUS B | 66 | 4.0234 | 459.9316 | 4.0874 | 155.7514 | 5.0494 | 4.1377 | 157.6683 | 4.1778 | 159.1964 | 1.6696 | 10.2835 | 1.1993 | 7.7971 | 2.1139 | 12.2776
CLER | Clermont T071 | CA | CLER_22kV_BUS LH | 22 | 3.7502 | 142.8999 | 3.8167 | 48.4791 | 4.1456 | 3.7272 | 47.3423 | 3.8691 | 49.1439 | 0.29463 | 3.714 | 0.0572 | 3.2944 | 0.32789 | 3.9526
CLER | Clermont T071 | CA | CLER_22kV_BUS RH | 22 | 3.7502 | 142.8999 | 3.8167 | 48.4791 | 4.1456 | 3.7272 | 47.3423 | 3.8691 | 49.1439 | 0.29463 | 3.714 | 0.0572 | 3.2944 | 0.32789 | 3.9526
CLER | Clermont T071 (TF1) | CA | CLER_11kV_TEF T1 | 11 | 9.1529 | 174.3866 | 6.336 | 40.2387 | 5.1339 | 7.9526 | 50.5059 | 8.2438 | 52.355 | 0.06204 | 0.76073 | 0.01974 | 1.7231 | 0.07037 | 0.8204
CLER | Clermont T071 (TF2) | CA | CLER_11kV_TEF T2 | 11 | 9.1427 | 174.1918 | 6.335 | 40.2327 | 5.1351 | 7.9438 | 50.45 | 8.2379 | 52.3178 | 0.06217 | 0.76157 | 0.01849 | 1.7221 | 0.07047 | 0.82116
CLIF | Clifton | SW | CLIF_33kV_BUS | 33 | 0.75008 | 42.8727 | 0.36641 | 6.981 | 0.24201 | 0.67412 | 12.8437 | 0.6472 | 12.3308 | 16.787 | 22.3412 | 80.9024 | 83.1846 | 16.7871 | 22.3367
CLIF | Clifton (TF1) | SW | CLIF_11kV_BUS 1 | 11 | 1.4946 | 28.4766 | 1.904 | 12.0923 | 2.5997 | 1.6782 | 10.6581 | 1.9783 | 12.5642 | 1.9534 | 4.247 | 0.08823 | 1.7647 | 1.9535 | 4.2465
CLIF | Clifton (TF2) | SW | CLIF_11kV_BUS 2 | 11 | 1.5054 | 28.682 | 1.922 | 12.2061 | 2.6342 | 1.6955 | 10.7677 | 1.9986 | 12.6928 | 1.9517 | 4.211 | 0.08643 | 1.7286 | 1.9517 | 4.2105
CLIN | Clinton | CA | CLIN_66kV_BUS 1 | 66 | 13.3104 | 1521.5814 | 13.862 | 528.2143 | 14.5358 | 13.8067 | 526.1046 | 13.4125 | 511.0853 | 0.41333 | 3.1219 | 0.49777 | 2.714 | 0.41325 | 3.1384
CLIN | Clinton | CA | CLIN_66kV_BUS 2 | 66 | 13.3104 | 1521.5814 | 13.862 | 528.2143 | 14.5358 | 13.8067 | 526.1046 | 13.4125 | 511.0853 | 0.41333 | 3.1219 | 0.49777 | 2.714 | 0.41325 | 3.1384
CLIN | Clinton | CA | CLIN_11kV_BUS LH | 11 | 14.6593 | 279.2976 | 15.607 | 99.1178 | 16.7024 | 15.128 | 96.0758 | 15.2571 | 96.8958 | 0.03089 | 0.47556 | 0.01941 | 0.38884 | 0.03089 | 0.47602
CLIN | Clinton | CA | CLIN_11kV_BUS RH | 11 | 14.6593 | 279.2976 | 15.607 | 99.1178 | 16.7024 | 15.128 | 96.0758 | 15.2571 | 96.8958 | 0.03089 | 0.47556 | 0.01941 | 0.38884 | 0.03089 | 0.47602
CLON | Cloncurry | NQ - MI | CLON_66kV_BUS 1 | 66 | 1.7948 | 205.1751 | 1.7575 | 66.971 | 1.7321 | 1.7788 | 67.7794 | 1.7743 | 67.6108 | 5.5336 | 22.6887 | 5.816 | 24.0022 | 5.4349 | 22.8599
CLON | Cloncurry (TF1) | NQ - MI | CLON_11kV_BUS 1 | 11 | 1.1491 | 21.8929 | 1.1907 | 7.5619 | 1.2363 | 1.1657 | 7.4034 | 1.1768 | 7.474 | 0.58369 | 6.0515 | 0.42998 | 5.4213 | 0.58095 | 6.0563
CLON | Cloncurry (TF2) | NQ - MI | CLON_11kV_BUS 2 | 11 | 2.362 | 45.0011 | 2.5456 | 16.1668 | 2.7644 | 2.4474 | 15.5428 | 2.4884 | 15.8034 | 0.38395 | 2.9327 | 0.23024 | 2.3024 | 0.38121 | 2.9374
CLSO | Clare South T193 | NQ | CLSO_66kV_BUS 1 | 66 | 11.3768 | 1300.5428 | 13.7009 | 522.0744 | 17.115 | 12.8487 | 489.5997 | 13.2657 | 505.4906 | 0.70842 | 3.6156 | 0.22459 | 1.8156 | 0.68429 | 3.6033
CLSO | Clare South T193 | NQ | CLSO_66kV_BUS 2 | 66 | 11.3768 | 1300.5428 | 13.7009 | 522.0744 | 17.115 | 12.8487 | 489.5997 | 13.2657 | 505.4906 | 0.70842 | 3.6156 | 0.22459 | 1.8156 | 0.68429 | 3.6033
CLSO | Clare South T193 | NQ | CLSO_11kV_BUS 1 | 11 | 3.499 | 66.665 | 3.5598 | 22.6079 | 3.622 | 3.5258 | 22.3916 | 3.5349 | 22.4496 | 0.2082 | 1.9857 | 0.18852 | 1.8852 | 0.20753 | 1.9853
COCO | Cook Colliery | CA | COCO_66kV_BUS | 66 | 2.0733 | 237.0121 | 1.3996 | 53.3333 | 1.0522 | 1.8022 | 68.6719 | 1.939 | 73.8858 | 9.5933 | 17.7958 | 16.2374 | 47.0012 | 9.6094 | 17.7601
COCR | Cooby Creek | SW | COCR_33kV_BUS 1 | 33 | 2.1155 | 120.9144 | 0.84024 | 16.0086 | 0.51861 | 1.7661 | 33.6485 | 1.9314 | 36.7976 | 4.807 | 8.6646 | 8.4077 | 55.3134 | 4.8069 | 8.6607
COLL | Collinsville | NQ | COLL_33kV_BUS 1 | 33 | 15.5169 | 886.9082 | 15.3261 | 292.002 | 14.9353 | 15.0872 | 287.4502 | 15.7559 | 300.1902 | 0.16304 | 1.3408 | 0.11881 | 1.416 | 0.21085 | 1.3159
COLL | Collinsville | NQ | COLL_33kV_BUS 2 | 33 | 15.5169 | 886.9082 | 15.3261 | 292.002 | 14.9353 | 15.0872 | 287.4502 | 15.7559 | 300.1902 | 0.16304 | 1.3408 | 0.11881 | 1.416 | 0.21085 | 1.3159
COLU | Columboola T194 | SW | COLU_33kV_BUS | 33 | 4.1747 | 238.6173 | 5.6591 | 107.8199 | 8.7998 | 5.6685 | 107.9991 | 5.72 | 108.9802 | 0.22363 | 5.0154 | 0.01424 | 1.0634 | 0.22311 | 5.0223
COME | Comet | CA | COME_66kV_BUS | 66 | 3.0509 | 348.7647 | 1.8975 | 72.3042 | 1.3129 | 2.6821 | 102.2 | 2.8917 | 110.1889 | 6.0176 | 12.3509 | 10.4928 | 38.4787 | 5.7161 | 11.6019
COME | Comet | CA | COME_22kV_BUS LURLINE | 22 | 1.8406 | 70.1382 | 1.9745 | 25.0793 | 2.1019 | 1.8759 | 23.8276 | 1.9516 | 24.7882 | 1.2067 | 7.4943 | 0.53811 | 6.1219 | 1.1732 | 7.411
COME | Comet | CA | COME_22kV_TEF T01 | 22 | 1.8406 | 70.1382 | 1.9745 | 25.0793 | 2.1019 | 1.8759 | 23.8276 | 1.9516 | 24.7882 | 1.2067 | 7.4943 | 0.53811 | 6.1219 | 1.1732 | 7.411
COME | Comet | CA | COME_22kV_TEF T02 | 22 | 0.60905 | 23.208 | 0.62305 | 7.9139 | 0.63521 | 0.61275 | 7.783 | 0.61974 | 7.8718 | 3.6558 | 22.6474 | 2.9872 | 21.2751 | 3.6223 | 22.5642
COOK | Cooktown | FN | COOK_66kV_BUS | 66 | 0.63416 | 72.4946 | 0.4292 | 16.3548 | 0.31946 | 0.55734 | 21.2374 | 0.59353 | 22.6165 | 22.7099 | 62.072 | 33.0493 | 159.2588 | 22.0558 | 61.1246
COOK | Cooktown (G1,G2) | FN | COOK_22kV_BUS RMU 4 | 22 | 1.243 | 47.3636 | 1.6002 | 20.3249 | 2.2048 | 1.4623 | 18.5736 | 1.6188 | 20.5616 | 2.7744 | 10.893 | 0.00053 | 3.9349 | 2.7017 | 10.7877
COOK | Cooktown (G3,G4) | FN | COOK_22kV_BUS RMU 3 | 22 | 1.243 | 47.3636 | 1.6002 | 20.3249 | 2.2048 | 1.4623 | 18.5736 | 1.6188 | 20.5616 | 2.7744 | 10.893 | 0.00053 | 3.9349 | 2.7017 | 10.7877
COOK | Cooktown (TF1) | FN | COOK_22kV_BUS RMU 1 | 22 | 1.243 | 47.3636 | 1.6002 | 20.3249 | 2.2048 | 1.4623 | 18.5736 | 1.6188 | 20.5616 | 2.7744 | 10.893 | 0.00053 | 3.9349 | 2.7017 | 10.7877
COOK | Cooktown (TF2) | FN | COOK_22kV_BUS RMU 2 | 22 | 1.2455 | 47.4583 | 1.6048 | 20.3836 | 2.2146 | 1.4671 | 18.6349 | 1.624 | 20.6273 | 2.7754 | 10.8696 | 0.00053 | 3.9042 | 2.7027 | 10.7643
COOM | Coominglah | CA | COOM_66kV_TEF T2 | 66 | 1.2089 | 138.1974 | 0.85288 | 32.4991 | 0.65127 | 1.0131 | 38.6046 | 1.1735 | 44.7166 | 22.9153 | 26.0211 | 31.5423 | 73.4452 | 22.9161 | 26.0411
COOM | Coominglah (TF1) | CA | COOM_22kV_TEF T1 | 22 | 0.77531 | 29.5432 | 0.82677 | 10.5014 | 0.88429 | 0.77517 | 9.846 | 0.83167 | 10.5636 | 4.1477 | 17.5377 | 1.6013 | 14.6461 | 4.1478 | 17.5399
COOM | Coominglah (TF2) | CA | COOM_22kV_TEF T2 | 22 | 0.77532 | 29.5437 | 0.82678 | 10.5015 | 0.88429 | 0.77518 | 9.8462 | 0.83168 | 10.5638 | 4.1475 | 17.5374 | 1.6013 | 14.6461 | 4.1475 | 17.5396
COPP | Coppabella Dragline | MK | Coppabella Dragline 66 kV | 66 | 1.6472 | 188.2969 | 1.1952 | 45.542 | 0.93814 | 1.4926 | 56.8746 | 1.5101 | 57.5412 | 9.9701 | 23.4127 | 20.0581 | 50.4738 | 9.9733 | 23.4261
CORF | Corfield | NQ | CORF_66kV_BUS | 66 | 0.4704 | 53.7741 | 0.31237 | 11.9029 | 0.23745 | 0.40832 | 15.559 | 0.43249 | 16.4801 | 38.0757 | 80.5614 | 67.1847 | 212.7658 | 38.3335 | 82.751
CPRE | Cape River East | NQ | CPRE_132kV_BUS_1 | 132 | 0.92853 | 212.2897 | 1.2516 | 95.3867 | 2.0469 | 1.2493 | 95.2082 | 1.3471 | 102.659 | 29.6858 | 85.2643 | 0.39884 | 17.1981 | 29.1287 | 89.5486
CPRE | Cape River East (TF1&2) | NQ | CPRE_66kV_BUS_1 | 66 | 1.8953 | 216.66 | 2.5451 | 96.9798 | 4.0952 | 2.4919 | 94.9545 | 2.7409 | 104.4408 | 8.2998 | 20.4993 | 0.10978 | 4.5773 | 8.2694 | 21.4314
CPRE | Cape River East (TF1&2) | NQ | CPRE_33kV_STATCOM_BUS 1 | 33 | 3.4004 | 194.3582 | 1.5459 | 29.4531 | 1.0142 | 2.7956 | 53.2628 | 3.0791 | 58.6639 | 2.0264 | 5.8207 | 0 | 28.5793 | 2.0058 | 6.0711
CRAI | Craiglie (TF1) | FN | CRAIGLIE NO 1 | 132 | 1.709 | 390.7323 | 1.7019 | 129.7016 | 1.6939 | 1.6604 | 126.5369 | 1.7488 | 133.2777 | 14.1714 | 46.9609 | 9.6682 | 48.8442 | 13.8087 | 47.0918
CRAI | Craiglie (TF2) | FN | CRAIGLIE NO 2 | 132 | 1.688 | 385.9211 | 1.3927 | 106.136 | 1.1858 | 1.5716 | 119.7706 | 1.5829 | 120.6324 | 14.474 | 47.5082 | 22.0603 | 78.186 | 14.1343 | 47.6354
CRAI | Craiglie (TF2) | FN | CRAI_22kV_BUS 2 | 22 | 5.8651 | 223.4907 | 7.6723 | 97.4509 | 11.0896 | 7.2976 | 92.6918 | 7.7348 | 98.2448 | 0.38322 | 2.3512 | 5e-05 | 0.70467 | 0.37349 | 2.3548
CRAN | Cranbrook | NQ | CRAN_66kV_BUS 1 | 66 | 12.4015 | 1417.6861 | 9.7741 | 372.4439 | 8.0694 | 11.4495 | 436.2842 | 11.4916 | 437.8874 | 0.77909 | 3.2889 | 1.3325 | 5.9564 | 0.76176 | 3.295
CRAN | Cranbrook | NQ | CRAN_66kV_BUS 2 | 66 | 12.4015 | 1417.6861 | 9.7741 | 372.4439 | 8.0694 | 11.4495 | 436.2842 | 11.4916 | 437.8874 | 0.77909 | 3.2889 | 1.3325 | 5.9564 | 0.76176 | 3.295
CRAN | Cranbrook (TF1) | NQ | CRAN_11kV_BUS 1 | 11 | 7.1723 | 136.6511 | 7.4062 | 47.0359 | 7.6568 | 7.2587 | 46.0987 | 7.3336 | 46.5745 | 0.05788 | 0.97229 | 0.03623 | 0.88094 | 0.05739 | 0.97247
CRAN | Cranbrook (TF2) | NQ | CRAN_11kV_BUS 2 | 11 | 7.1723 | 136.6511 | 7.4062 | 47.0359 | 7.6568 | 7.2587 | 46.0987 | 7.3336 | 46.5745 | 0.05788 | 0.97229 | 0.03623 | 0.88094 | 0.05739 | 0.97247
CRED | Crediton | MK | CRED_66kV_TEF T1 | 66 | 0.90284 | 103.2086 | 0.64616 | 24.6221 | 0.4944 | 0.74115 | 28.2418 | 0.89121 | 33.9595 | 34.2629 | 31.3286 | 44.5379 | 95.6333 | 34.2563 | 31.4359
CRED | Crediton | MK | CRED_11kV_TEF R1 | 11 | 0.63149 | 12.0314 | 0.65091 | 4.1339 | 0.67129 | 0.62663 | 3.9796 | 0.65629 | 4.168 | 1.6667 | 10.9365 | 0.71493 | 10.0663 | 1.6665 | 10.9395
CRNA | Cressbrook No. 1 | SW | CRNA_33kV_TEF T1 | 33 | 1.4026 | 80.1708 | 0.62488 | 11.9055 | 0.39675 | 1.1633 | 22.1642 | 1.295 | 24.6729 | 8.078 | 12.5729 | 13.9316 | 70.8891 | 8.078 | 12.5691
CRNA | Cressbrook No. 1 | SW | CRNA_3.3kV_BUS | 3.3 | 6.1796 | 35.3212 | 7.1792 | 13.6783 | 8.5278 | 6.4308 | 12.2524 | 7.2313 | 13.7774 | 0.09083 | 0.32681 | 0.01005 | 0.20108 | 0.09083 | 0.32677
CRNB | Cressbrook No. 2 | SW | CRNB_33kV_TEF T1 | 33 | 1.9169 | 109.5673 | 0.79329 | 15.1142 | 0.49376 | 1.5924 | 30.3392 | 1.7606 | 33.5433 | 5.7051 | 9.3286 | 9.6708 | 57.7617 | 5.7051 | 9.3247
CRNB | Cressbrook No. 2 | SW | CRNB_3.3kV_BUS | 3.3 | 6.9108 | 39.5005 | 7.7918 | 14.8453 | 8.9042 | 7.0967 | 13.5211 | 7.8053 | 14.8711 | 0.06718 | 0.29578 | 0.01012 | 0.20249 | 0.06718 | 0.29574
CRNE | Crows Nest | SW | CRNE_33kV_BUS 1 | 33 | 1.6796 | 96.0026 | 0.71593 | 13.6404 | 0.44913 | 1.3947 | 26.5718 | 1.5454 | 29.4448 | 6.5468 | 10.6248 | 11.0607 | 63.2025 | 6.5468 | 10.621
CRNE | Crows Nest | SW | CRNE_33kV_BUS 2 | 33 | 1.6796 | 96.0026 | 0.71593 | 13.6404 | 0.44913 | 1.3947 | 26.5718 | 1.5454 | 29.4448 | 6.5468 | 10.6248 | 11.0607 | 63.2025 | 6.5468 | 10.621
CRNE | Crows Nest (TF1) | SW | CRNE_11kV_BUS 1 | 11 | 2.6556 | 50.5964 | 3.197 | 20.304 | 3.995 | 2.8457 | 18.0724 | 3.2344 | 20.5412 | 0.79384 | 2.5084 | 0.06642 | 1.3279 | 0.79384 | 2.508
CRNE | Crows Nest (TF1) | SW | CRNE_11kV_BUS 2 | 11 | 2.6556 | 50.5964 | 3.197 | 20.304 | 3.995 | 2.8457 | 18.0724 | 3.2344 | 20.5412 | 0.79384 | 2.5084 | 0.06642 | 1.3279 | 0.79384 | 2.508
CRNE | Crows Nest (TF1) | SW | CRNE_11kV_BUS 3 | 11 | 2.6556 | 50.5964 | 3.197 | 20.304 | 3.995 | 2.8457 | 18.0724 | 3.2344 | 20.5412 | 0.79384 | 2.5084 | 0.06642 | 1.3279 | 0.79384 | 2.508
CROY | Croydon | FN | CROY_66kV_BUS 1 | 66 | 0.4871 | 55.6825 | 0.43101 | 16.4238 | 0.38974 | 0.45496 | 17.3364 | 0.47152 | 17.9673 | 24.3129 | 82.5462 | 24.9401 | 116.3178 | 23.6123 | 83.6389
CROY | Croydon | FN | CROY_66kV_BUS 2 | 66 | 0.4871 | 55.6825 | 0.43101 | 16.4238 | 0.38974 | 0.45496 | 17.3364 | 0.47152 | 17.9673 | 24.3129 | 82.5462 | 24.9401 | 116.3178 | 23.6123 | 83.6389
CROY | Croydon | FN | CROY_NORM 66KV BUS IS | 66 | 0.4871 | 55.6825 | 0.43101 | 16.4238 | 0.38974 | 0.45496 | 17.3364 | 0.47152 | 17.9673 | 24.3129 | 82.5462 | 24.9401 | 116.3178 | 23.6123 | 83.6389
CROY | Croydon | FN | CROY_22kV_BUS 1 | 22 | 0.55024 | 20.9668 | 0.63066 | 8.0105 | 0.74073 | 0.5778 | 7.339 | 0.6274 | 7.9691 | 3.9912 | 25.077 | 0.00535 | 15.7153 | 3.9133 | 25.1984
CROY | Croydon | FN | CROY_22kV_BUS 2 | 22 | 0.55221 | 21.0421 | 0.63237 | 8.0322 | 0.74185 | 0.57923 | 7.3571 | 0.62934 | 7.9937 | 4.0012 | 24.9833 | 0.00535 | 15.719 | 3.9234 | 25.1047
CUNN | Cunnamulla | SW | CUNN_66kV_BUS 1 | 66 | 0.18146 | 20.7433 | 0.08344 | 3.1794 | 0.0541 | 0.15624 | 5.9535 | 0.16257 | 6.1946 | 99.733 | 208.361 | 323.596 | 996.5942 | 99.669 | 208.4768
CUNN | Cunnamulla | SW | CUNN_66kV_BUS 2 | 66 | 0.18146 | 20.7433 | 0.08344 | 3.1794 | 0.0541 | 0.15624 | 5.9535 | 0.16257 | 6.1946 | 99.733 | 208.361 | 323.596 | 996.5942 | 99.669 | 208.4768
CUNN | Cunnamulla | SW | CUNN_22kV_BUS | 22 | 0.44531 | 16.9685 | 0.63539 | 8.0706 | 1.1078 | 0.65552 | 8.3262 | 0.69375 | 8.8118 | 11.3858 | 29.2376 | 0.09436 | 3.3943 | 11.3787 | 29.2505
CUNN | Cunnamulla | SW | CUNN_11kV_BUS BROAD ST | 11 | 0.89087 | 16.9734 | 1.2228 | 7.7655 | 1.9443 | 1.1859 | 7.5313 | 1.2939 | 8.2175 | 2.8463 | 7.3071 | 0.07618 | 1.5236 | 2.8445 | 7.3103
CUNN | Cunnamulla | SW | CUNN_11kV_BUS WICKS ST | 11 | 0.89087 | 16.9734 | 1.2228 | 7.7655 | 1.9443 | 1.1859 | 7.5313 | 1.2939 | 8.2175 | 2.8463 | 7.3071 | 0.07618 | 1.5236 | 2.8445 | 7.3103
DAAN | Daandine T188 | SW | DAAN_110kV_BUS 1 | 110 | 1.6296 | 310.479 | 1.2727 | 80.8253 | 1.0317 | 1.3784 | 87.5409 | 1.6171 | 102.6978 | 22.5341 | 36.4744 | 19.2927 | 78.6415 | 22.5481 | 36.4755
DAAN | Daandine T188 | SW | DAAN_33kV_BUS 1 | 33 | 2.6625 | 152.1845 | 2.3818 | 45.3788 | 2.1511 | 2.4587 | 46.8443 | 2.6271 | 50.0528 | 2.2471 | 7.5447 | 1.8252 | 10.5434 | 2.2484 | 7.5448
DAAN | Daandine T188 | SW | DAAN_33kV_BUS 2 | 33 | 2.6625 | 152.1845 | 2.3818 | 45.3788 | 2.1511 | 2.4587 | 46.8443 | 2.6271 | 50.0528 | 2.2471 | 7.5447 | 1.8252 | 10.5434 | 2.2484 | 7.5448
DABA | Dalrymple Bay (with MACK G1) | MK | DABA_33kV_BUS | 33 | 6.9894 | 399.4983 | 5.6735 | 108.0947 | 4.7959 | 6.4978 | 123.7997 | 6.5006 | 123.8533 | 0.39524 | 2.9724 | 0.66083 | 5.0258 | 0.39543 | 2.9884
DACE | Dalby Central | SW | DACE_33kV_BUS 1 | 33 | 5.5058 | 314.7017 | 5.1957 | 98.991 | 4.9074 | 5.1369 | 97.8715 | 5.5785 | 106.2852 | 1.3091 | 3.5747 | 0.93038 | 4.4206 | 1.3104 | 3.5748
DACE | Dalby Central | SW | DACE_33kV_BUS 2 | 33 | 5.5058 | 314.7017 | 5.1957 | 98.991 | 4.9074 | 5.1369 | 97.8715 | 5.5785 | 106.2852 | 1.3091 | 3.5747 | 0.93038 | 4.4206 | 1.3104 | 3.5748
DACE | Dalby Central | SW | DACE_11kV_BUS 3 | 11 | 5.8281 | 111.0397 | 6.5862 | 41.8281 | 7.5639 | 6.1261 | 38.9059 | 6.4828 | 41.171 | 0.18758 | 1.184 | 0.04212 | 0.78684 | 0.18772 | 1.184
DACE | Dalby Central (TF1) | SW | DACE_11kV_BUS 1 | 11 | 5.8281 | 111.0397 | 6.5862 | 41.8281 | 7.5639 | 6.1261 | 38.9059 | 6.4828 | 41.171 | 0.18758 | 1.184 | 0.04212 | 0.78684 | 0.18772 | 1.184
DACE | Dalby Central (TF2) | SW | DACE_11kV_BUS 2 | 11 | 5.8281 | 111.0397 | 6.5862 | 41.8281 | 7.5639 | 6.1261 | 38.9059 | 6.4828 | 41.171 | 0.18758 | 1.184 | 0.04212 | 0.78684 | 0.18772 | 1.184
DACG | Dalby Cotton Gin | SW | SS596009_tr_cable_132 | 33 | 2.3563 | 134.6795 | 1.593 | 30.3512 | 1.1941 | 2.0009 | 38.1225 | 2.2443 | 42.7593 | 4.4784 | 7.6858 | 5.8949 | 21.1993 | 4.4797 | 7.6859
DAEA | Dalby East | SW | DAEA_110kV_BUS 3 | 110 | 3.6292 | 691.4522 | 3.8446 | 244.1626 | 4.0108 | 3.2454 | 206.11 | 4.1546 | 263.8527 | 9.8966 | 16.5129 | 2.0244 | 16.9299 | 9.9106 | 16.514
DAEA | Dalby East | SW | DAEA_110kV_BUS 4 | 110 | 3.6292 | 691.4522 | 3.8446 | 244.1626 | 4.0108 | 3.2454 | 206.11 | 4.1546 | 263.8527 | 9.8966 | 16.5129 | 2.0244 | 16.9299 | 9.9106 | 16.514
DAEA | Dalby East | SW | DAEA_33kV_BUS 1 | 33 | 7.1553 | 408.9795 | 9.0019 | 171.5099 | 12.0813 | 8.1191 | 154.6888 | 9.1569 | 174.4623 | 0.93132 | 2.7773 | 0.06073 | 1.1601 | 0.93258 | 2.7774
DAEA | Dalby East | SW | DAEA_33kV_BUS 2 | 33 | 7.1553 | 408.9795 | 9.0019 | 171.5099 | 12.0813 | 8.1191 | 154.6888 | 9.1569 | 174.4623 | 0.93132 | 2.7773 | 0.06073 | 1.1601 | 0.93258 | 2.7774
DAGL | Dan Gleeson T092 | NQ | DAGL_66kV_BUS 1 | 66 | 17.9013 | 2046.3921 | 20.1587 | 768.1491 | 23.1248 | 19.2663 | 734.1454 | 19.3981 | 739.1682 | 0.34698 | 2.3156 | 0.19902 | 1.5371 | 0.33037 | 2.3232
DAGL | Dan Gleeson T092 | NQ | DAGL_66kV_BUS 2 | 66 | 17.9013 | 2046.3921 | 20.1587 | 768.1491 | 23.1248 | 19.2663 | 734.1454 | 19.3981 | 739.1682 | 0.34698 | 2.3156 | 0.19902 | 1.5371 | 0.33037 | 2.3232
DAGL | Dan Gleeson T092 (TF1) | NQ | DAGL_11kV_BUS 1 | 11 | 10.9442 | 208.5154 | 11.3263 | 71.9319 | 11.7395 | 11.1185 | 70.6121 | 11.1766 | 70.9812 | 0.03964 | 0.63709 | 0.03001 | 0.57277 | 0.03918 | 0.6373
DAGL | Dan Gleeson T092 (TF2) | NQ | DAGL_11kV_BUS 2 | 11 | 10.8694 | 207.0904 | 11.2462 | 71.4232 | 11.6534 | 11.0412 | 70.1208 | 11.0986 | 70.4855 | 0.03979 | 0.64148 | 0.03015 | 0.57716 | 0.03933 | 0.64169
DEGI | Degilbo | WB | DEGI_66kV_BUS | 66 | 2.1188 | 242.2143 | 1.4323 | 54.5784 | 1.082 | 1.9203 | 73.1715 | 1.9054 | 72.6068 | 5.9214 | 18.8769 | 15.0325 | 45.8265 | 5.8434 | 18.9063
DEGI | Degilbo | WB | DEGI_11kV_BUS 1 | 11 | 1.5622 | 29.7636 | 1.6263 | 10.3284 | 1.6959 | 1.5801 | 10.0347 | 1.613 | 10.2439 | 0.17689 | 4.4687 | 0.01241 | 3.9444 | 0.17472 | 4.4695
DEGI | Degilbo | WB | DEGI_11kV_BUS 2 | 11 | 2.0041 | 38.1828 | 1.9258 | 12.2305 | 1.8384 | 1.9278 | 12.2433 | 2.0078 | 12.7512 | 0.28087 | 3.4747 | 0.01242 | 3.9451 | 0.25542 | 3.4495
DIMB | Dimbulah | FN | DIMB_66kV_BUS | 66 | 1.6049 | 183.4633 | 1.1404 | 43.4569 | 0.88742 | 1.3897 | 52.9538 | 1.5154 | 57.7462 | 11.2652 | 23.5631 | 14.8347 | 56.3306 | 11.2406 | 23.8521
DIMB | Dimbulah (TF1) | FN | DIMB_22kV_BUS 1 | 22 | 3.18 | 121.174 | 4.0532 | 51.4822 | 5.6212 | 3.7295 | 47.3715 | 4.1253 | 52.3987 | 1.358 | 4.1786 | 0.1063 | 1.5604 | 1.3553 | 4.2107
DIMB | Dimbulah (TF1) | FN | DIMB_22kV_BUS 2 | 22 | 3.18 | 121.174 | 4.0532 | 51.4822 | 5.6212 | 3.7295 | 47.3715 | 4.1253 | 52.3987 | 1.358 | 4.1786 | 0.1063 | 1.5604 | 1.3553 | 4.2107
DIRE | Dirranbandi Regulator (Regulated) | SW | DIRE_33kV_BUS R1 Upstream | 33 | 0.37145 | 21.2309 | 0.26266 | 5.0044 | 0.20237 | 0.32199 | 6.1348 | 0.3517 | 6.7008 | 20.9643 | 52.3842 | 24.3213 | 125.2303 | 20.9483 | 52.4131
DIRE | Dirranbandi Regulator (UnRegulated) | SW | DIRE_33kV_BUS R1 Downstream | 33 | 0.37145 | 21.2309 | 0.26266 | 5.0044 | 0.20237 | 0.32199 | 6.1348 | 0.3517 | 6.7008 | 20.9643 | 52.3842 | 24.3213 | 125.2303 | 20.9483 | 52.4131
DISR | Disraeli | NQ | DISR_66kV_TEF T1 | 66 | 1.4381 | 164.402 | 1.0806 | 41.1773 | 0.85302 | 1.1983 | 45.6594 | 1.4244 | 54.2772 | 19.7317 | 21.4507 | 22.7737 | 55.3805 | 19.6928 | 21.5164
DISR | Disraeli | NQ | DISR_11kV_TEF T1 | 11 | 3.4472 | 65.6778 | 3.9009 | 24.7741 | 4.4654 | 3.4407 | 21.8515 | 3.9937 | 25.3634 | 0.54833 | 1.951 | 0.0037 | 1.3551 | 0.54725 | 1.9528
DRILL | Drillham Switching Station | SW | DRILL_132kV_BUS_7174 | 132 | 7.2813 | 1664.7211 | 5.7877 | 441.0861 | 5.0143 | 6.7263 | 512.6107 | 6.6124 | 503.9292 | 3.1283 | 11.0805 | 5.9793 | 18.8989 | 3.2852 | 11.6699
DRILL | Drillham Switching Station | SW | DRILL_132kV_BUS_7491 | 132 | 7.2813 | 1664.7211 | 5.7877 | 441.0861 | 5.0143 | 6.7263 | 512.6107 | 6.6124 | 503.9292 | 3.1283 | 11.0805 | 5.9793 | 18.8989 | 3.2852 | 11.6699
DRILL | Drillham Switching Station | SW | DRILL_132kV_BUS_7492 | 132 | 7.2813 | 1664.7211 | 5.7877 | 441.0861 | 5.0143 | 6.7263 | 512.6107 | 6.6124 | 503.9292 | 3.1283 | 11.0805 | 5.9793 | 18.8989 | 3.2852 | 11.6699
DRILL | Drillham Switching Station | SW | DRILL_132kV_BUS_7164 | 132 | 7.2813 | 1664.7211 | 5.7877 | 441.0861 | 5.0143 | 6.7263 | 512.6107 | 6.6124 | 503.9292 | 3.1283 | 11.0805 | 5.9793 | 18.8989 | 3.2852 | 11.6699
DRILL | Drillham Switching Station | SW | DRILL_132kV_BUS_7490 | 132 | 7.2813 | 1664.7211 | 5.7877 | 441.0861 | 5.0143 | 6.7263 | 512.6107 | 6.6124 | 503.9292 | 3.1283 | 11.0805 | 5.9793 | 18.8989 | 3.2852 | 11.6699
DURI | Dugald River | NQ-MI | DURI_220kV_BUS | 220 | 1.1359 | 432.8363 | 1.4547 | 184.7693 | 2.0631 | 1.4092 | 178.9912 | 1.4377 | 182.6154 | 12.7962 | 122.3352 | 1.7304 | 40.3741 | 11.6995 | 124.2379
DURI | Dugald River | NQ-MI | DURI_11kV_TEF_T1 | 11 | 11.6788 | 222.5116 | 0.07675 | 0.48743 | 0.03853 | 10.0946 | 64.1094 | 10.0561 | 63.865 | 0.03278 | 0.59727 | 272.9997 | 0.1338 | 0.03004 | 0.60203
DURI | Dugald River | NQ-MI | DURI_11kV_TEF_T2 | 11 | 11.6788 | 222.5116 | 0.07675 | 0.48743 | 0.03853 | 10.0946 | 64.1094 | 10.0561 | 63.865 | 0.03278 | 0.59727 | 272.9997 | 0.1338 | 0.03004 | 0.60203
DURO | Duchess Road | NQ - MI | DURO_66kV_BUS | 66 | 0.51214 | 58.5457 | 0.53416 | 20.3542 | 0.55932 | 0.52452 | 19.987 | 0.52367 | 19.9545 | 5.8789 | 81.6323 | 5.2465 | 71.3675 | 5.7802 | 81.8035
DURO | Duchess Road (TF1) | NQ - MI | DURO_132kV_TEF T1 | 132 | 5.879 | 1344.1176 | 6.3388 | 483.0836 | 7.2173 | 6.2441 | 475.8648 | 6.1287 | 467.0708 | 1.7172 | 14.1557 | 1.2855 | 10.4423 | 1.3224 | 14.8407
DURO | Duchess Road (TF2) | NQ - MI | DURO_132kV_TEF T2 | 132 | 6.4118 | 1465.9444 | 7.1524 | 545.0834 | 8.5364 | 7.0525 | 537.475 | 6.8367 | 521.0235 | 1.8216 | 12.9469 | 1.3578 | 8.2805 | 1.4268 | 13.6319
DURO | Duchess Road (TF1) | NQ - MI | DURO_11kV_BUS A | 11 | 22.0266 | 419.663 | 3.1332 | 19.8987 | 1.6994 | 18.9164 | 120.1351 | 19.0067 | 120.7086 | 0.02031 | 0.31651 | 0 | 6.051 | 0.01757 | 0.32127
DURO | Duchess Road (TF2) | NQ - MI | DURO_11kV_BUS B | 11 | 22.6206 | 430.9797 | 3.1411 | 19.9487 | 1.7009 | 19.4201 | 123.3345 | 19.5168 | 123.9485 | 0.02103 | 0.30811 | 0 | 6.051 | 0.01829 | 0.31287
DYSA | Dysart T035 | CA | DYSA_66kV_BUS A | 66 | 6.0744 | 694.3936 | 7.6698 | 292.2595 | 10.4417 | 7.2057 | 274.5734 | 7.6064 | 289.8413 | 1.4084 | 6.7552 | 0.20483 | 2.5794 | 1.4146 | 6.7785
DYSA | Dysart T035 | CA | DYSA_22kV_BUS 1 | 22 | 5.4949 | 209.385 | 1.3455 | 17.0902 | 0.76683 | 4.7447 | 60.2658 | 4.7988 | 60.9528 | 0.19169 | 2.5355 | 0.03599 | 26.0763 | 0.19239 | 2.5381
DYSA | Dysart T035 | CA | DYSA_22kV_BUS 2 | 22 | 5.4949 | 209.385 | 1.3455 | 17.0902 | 0.76683 | 4.7447 | 60.2658 | 4.7988 | 60.9528 | 0.19169 | 2.5355 | 0.03599 | 26.0763 | 0.19239 | 2.5381
EAAY | East Ayr | NQ | EAAY_66kV_BUS 1 | 66 | 5.4776 | 626.1754 | 4.2467 | 161.8215 | 3.4539 | 4.9578 | 188.9186 | 5.1512 | 196.2874 | 2.5541 | 7.2134 | 3.6161 | 13.8969 | 2.4699 | 7.2116
EAAY | East Ayr | NQ | EAAY_66kV_BUS 2 | 66 | 5.4776 | 626.1754 | 4.2467 | 161.8215 | 3.4539 | 4.9578 | 188.9186 | 5.1512 | 196.2874 | 2.5541 | 7.2134 | 3.6161 | 13.8969 | 2.4699 | 7.2116
EAAY | East Ayr (TF2) | NQ | EAAY_11kV_BUS 2 | 11 | 8.9022 | 169.6099 | 9.7635 | 62.0068 | 10.7981 | 9.2158 | 58.5284 | 9.6062 | 61.0077 | 0.10122 | 0.77819 | 0.03027 | 0.57782 | 0.09888 | 0.77814
EABU | East Bundaberg | WB | EABU_66kV_BUS 1 | 66 | 5.193 | 593.641 | 4.3496 | 165.741 | 3.7839 | 4.8819 | 186.0233 | 4.8353 | 184.2497 | 1.9218 | 7.84 | 3.1554 | 12.2638 | 1.8975 | 7.9546
EABU | East Bundaberg | WB | EABU_66kV_BUS 2 | 66 | 5.193 | 593.641 | 4.3496 | 165.741 | 3.7839 | 4.8819 | 186.0233 | 4.8353 | 184.2497 | 1.9218 | 7.84 | 3.1554 | 12.2638 | 1.8975 | 7.9546
EABU | East Bundaberg | WB | EABU_11kV_BUS 1 | 11 | 13.359 | 254.5241 | 15.706 | 99.7467 | 19.1797 | 14.7067 | 93.3998 | 15.3146 | 97.2605 | 0.06685 | 0.51869 | 0.01346 | 0.28586 | 0.06617 | 0.52187
EABU | East Bundaberg | WB | EABU_11kV_BUS 2 | 11 | 13.359 | 254.5241 | 15.706 | 99.7467 | 19.1797 | 14.7067 | 93.3998 | 15.3146 | 97.2605 | 0.06685 | 0.51869 | 0.01346 | 0.28586 | 0.06617 | 0.52187
EATO | East Toowoomba | SW | EATO_11kV_BUS 1 | 11 | 9.8716 | 188.0785 | 2.2425 | 14.2419 | 1.1518 | 9.1189 | 57.913 | 7.9863 | 50.7201 | 0.06297 | 0.70498 | 9.0248 | 0.49615 | 0.06299 | 0.70449
EATO | East Toowoomba | SW | EATO_11kV_BUS 2 | 11 | 9.8716 | 188.0785 | 2.2425 | 14.2419 | 1.1518 | 9.1189 | 57.913 | 7.9863 | 50.7201 | 0.06297 | 0.70498 | 9.0248 | 0.49615 | 0.06299 | 0.70449
EATO | East Toowoomba (TF1) | SW | EATO_33kV_TEF T1 | 33 | 8.6075 | 491.9845 | 1.1031 | 21.017 | 0.56316 | 7.7294 | 147.2656 | 7.1935 | 137.0536 | 0.52031 | 2.379 | 55.2647 | 4.1524 | 0.52046 | 2.3745
EATO | East Toowoomba (TF2) | SW | EATO_33kV_TEF T2 | 33 | 8.2705 | 472.7237 | 1.0957 | 20.8757 | 0.56062 | 7.434 | 141.6364 | 6.9043 | 131.5455 | 0.57954 | 2.4673 | 55.4504 | 4.5091 | 0.5797 | 2.4628
EDMO | Edmonton | FN | EDMO_22kV_BUS 1 | 22 | 8.5174 | 324.5579 | 7.1783 | 91.1762 | 6.1786 | 8.3351 | 105.8701 | 7.6497 | 97.1641 | 0.06952 | 1.6389 | 0.51298 | 2.5267 | 0.06825 | 1.6373
EDMO | Edmonton | FN | EDMO_22kV_BUS 2 | 22 | 8.5174 | 324.5579 | 7.1783 | 91.1762 | 6.1786 | 8.3351 | 105.8701 | 7.6497 | 97.1641 | 0.06952 | 1.6389 | 0.51298 | 2.5267 | 0.06825 | 1.6373
EDMO | Edmonton | FN | EDMO_22kV_BUS 3 | 22 | 8.5174 | 324.5579 | 7.1783 | 91.1762 | 6.1786 | 8.3351 | 105.8701 | 7.6497 | 97.1641 | 0.06952 | 1.6389 | 0.51298 | 2.5267 | 0.06825 | 1.6373
EGHI | Egans Hill T127 | CA | EGHI_66kV_BUS EAST | 66 | 10.147 | 1159.9565 | 11.4301 | 435.5466 | 13.1781 | 10.9715 | 418.0685 | 10.9708 | 418.0445 | 0.70516 | 4.0703 | 0.46165 | 2.6745 | 0.70659 | 4.0961
EGHI | Egans Hill T127 | CA | EGHI_66kV_BUS WEST | 66 | 10.147 | 1159.9565 | 11.4301 | 435.5466 | 13.1781 | 10.9715 | 418.0685 | 10.9708 | 418.0445 | 0.70516 | 4.0703 | 0.46165 | 2.6745 | 0.70659 | 4.0961
EIDS | Eidsvold | WB | EIDS_66kV_BUS | 66 | 0.68052 | 77.7939 | 0.45404 | 17.3012 | 0.33877 | 0.58218 | 22.1841 | 0.64261 | 24.4869 | 38.6969 | 47.9252 | 68.0125 | 139.823 | 38.5519 | 48.0726
EIDS | Eidsvold | WB | EIDS_11kV_BUS | 11 | 1.3101 | 24.9617 | 1.3565 | 8.6151 | 1.4017 | 1.2595 | 7.9991 | 1.4036 | 8.9138 | 1.5338 | 5.1072 | 0.49985 | 4.8156 | 1.5298 | 5.1113
ELAR | El Arish | FN | ELAR_22kV_BUS 1 | 22 | 11.0152 | 419.7359 | 8.5213 | 108.2353 | 6.9386 | 10.5301 | 133.7503 | 9.7434 | 123.758 | 0.1018 | 1.2643 | 0.54995 | 2.3301 | 0.10018 | 1.2667
ELAR | El Arish | FN | ELAR_22kV_BUS 2 | 22 | 11.0152 | 419.7359 | 8.5213 | 108.2353 | 6.9386 | 10.5301 | 133.7503 | 9.7434 | 123.758 | 0.1018 | 1.2643 | 0.54995 | 2.3301 | 0.10018 | 1.2667
ELAR | El Arish | FN | ELAR_22kV_BUS 3 | 22 | 11.0152 | 419.7359 | 8.5213 | 108.2353 | 6.9386 | 10.5301 | 133.7503 | 9.7434 | 123.758 | 0.1018 | 1.2643 | 0.54995 | 2.3301 | 0.10018 | 1.2667
ELRO | Ellwoods Road | WB | ELRO_66kV_BUS OVERHEAD | 66 | 2.5504 | 291.5524 | 1.428 | 54.4126 | 0.99046 | 2.2105 | 84.2317 | 2.3137 | 88.1649 | 5.1778 | 15.5999 | 10.7006 | 54.2906 | 5.1343 | 15.6263
ELRO | Ellwoods Road (TF1) | WB | ELRO_11kV_BUS 1 | 11 | 3.4837 | 66.3728 | 3.7651 | 23.9117 | 4.097 | 3.6011 | 22.8699 | 3.6907 | 23.4394 | 0.33822 | 1.9768 | 0.1944 | 1.5435 | 0.33702 | 1.9776
ELRO | Ellwoods Road (TF2) | WB | ELRO_11kV_BUS 2 | 11 | 3.5293 | 67.2419 | 3.8185 | 24.251 | 4.1604 | 3.6507 | 23.1849 | 3.7421 | 23.7657 | 0.33685 | 1.9508 | 0.19303 | 1.5175 | 0.33564 | 1.9515
EMER | Emerald | CA | EMER_66kV_BUS 1 | 66 | 3.4763 | 397.3938 | 1.6151 | 61.5435 | 0.8625 | 3.4796 | 132.5896 | 3.4264 | 130.5624 | 3.1408 | 11.6414 | 14.1851 | 55.1053 | 1.6392 | 8.7653
EMER | Emerald | CA | EMER_66kV_BUS 3 | 66 | 3.4763 | 397.3938 | 1.6151 | 61.5435 | 0.8625 | 3.4796 | 132.5896 | 3.4264 | 130.5624 | 3.1408 | 11.6414 | 14.1851 | 55.1053 | 1.6392 | 8.7653
EMER | Emerald | CA | EMER_22kV_BUS 1 | 22 | 6.8488 | 260.9731 | 9.4331 | 119.8166 | 11.6452 | 8.332 | 105.831 | 8.6352 | 109.6823 | 0.38451 | 2.0035 | 0.03552 | 0.71002 | 0.21765 | 1.6839
EMER | Emerald | CA | EMER_22kV_BUS 2 | 22 | 6.8488 | 260.9731 | 9.4331 | 119.8166 | 11.6452 | 8.332 | 105.831 | 8.6352 | 109.6823 | 0.38451 | 2.0035 | 0.03552 | 0.71002 | 0.21765 | 1.6839
EMER | Emerald | CA | EMER_22kV_BUS 3 | 22 | 6.8488 | 260.9731 | 9.4331 | 119.8166 | 11.6452 | 8.332 | 105.831 | 8.6352 | 109.6823 | 0.38451 | 2.0035 | 0.03552 | 0.71002 | 0.21765 | 1.6839
EMWE | Emerald West | CA | EMWE_66kV_BUS | 66 | 3.6623 | 418.6566 | 1.64 | 62.4915 | 0.84084 | 3.7431 | 142.633 | 3.6656 | 139.6788 | 2.7663 | 11.1059 | 14.1142 | 55.4236 | 1.2055 | 7.9829
ERHE | Ernest Henry | NQ - MI | ERHE_220kV_BUS | 220 | 1.1757 | 447.9959 | 1.5452 | 196.2599 | 2.3032 | 1.533 | 194.7113 | 1.5379 | 195.3412 | 12.1849 | 118.2141 | 2.6254 | 31.7031 | 11.0882 | 120.1167
ERHE | Ernest Henry (TF1) | NQ - MI | ERHE_11kV_TEF T1 | 11 | 13.5689 | 258.5224 | 0.10994 | 0.69821 | 0.05523 | 11.7271 | 74.4768 | 11.6721 | 74.1275 | 0.04137 | 0.51318 | 190.4998 | 3.3501 | 0.03863 | 0.51794
ERHE | Ernest Henry (TF2) | NQ - MI | ERHE_11kV_TEF T2 | 11 | 13.5689 | 258.5224 | 0.10994 | 0.69821 | 0.05523 | 11.7271 | 74.4768 | 11.6721 | 74.1275 | 0.04137 | 0.51318 | 190.4998 | 3.3501 | 0.03863 | 0.51794
ETON | Eton | MK | ETON_33kV_BUS 1 | 33 | 1.3133 | 75.0675 | 0.76312 | 14.5394 | 0.53292 | 1.0966 | 20.8928 | 1.234 | 23.5113 | 8.5827 | 13.4531 | 13.1046 | 49.6872 | 8.5814 | 13.4885
ETON | Eton | MK | ETON_33kV_BUS 2 | 33 | 1.3133 | 75.0675 | 0.76312 | 14.5394 | 0.53292 | 1.0966 | 20.8928 | 1.234 | 23.5113 | 8.5827 | 13.4531 | 13.1046 | 49.6872 | 8.5814 | 13.4885
ETON | Eton | MK | ETON_33kV_BUS 3 | 33 | 1.3133 | 75.0675 | 0.76312 | 14.5394 | 0.53292 | 1.0966 | 20.8928 | 1.234 | 23.5113 | 8.5827 | 13.4531 | 13.1046 | 49.6872 | 8.5814 | 13.4885
ETON | Eton | MK | ETON_11kV_BUS 3 | 11 | 2.1875 | 41.678 | 2.662 | 16.9057 | 3.385 | 2.3628 | 15.0058 | 2.7056 | 17.1831 | 1.03 | 3.0229 | 0.0764 | 1.5281 | 1.0299 | 3.0268
ETON | Eton | MK | ETON_11kV_BUS 4 | 11 | 2.1875 | 41.678 | 2.662 | 16.9057 | 3.385 | 2.3628 | 15.0058 | 2.7056 | 17.1831 | 1.03 | 3.0229 | 0.0764 | 1.5281 | 1.0299 | 3.0268
ETON | Eton (TF1) | MK | ETON_11kV_BUS 1 | 11 | 2.1625 | 41.201 | 2.6245 | 16.6676 | 3.3237 | 2.3298 | 14.7963 | 2.6658 | 16.93 | 1.032 | 3.0613 | 0.07832 | 1.5665 | 1.0318 | 3.0652
ETON | Eton (TF2) | MK | ETON_11kV_BUS 2 | 11 | 2.1625 | 41.201 | 2.6245 | 16.6676 | 3.3237 | 2.3298 | 14.7963 | 2.6658 | 16.93 | 1.032 | 3.0613 | 0.07832 | 1.5665 | 1.0318 | 3.0652
EUDA | Eungella Dam | MK | EUDA_66kV_BUS | 66 | 0.63041 | 72.065 | 0.46658 | 17.7791 | 0.36297 | 0.51529 | 19.6352 | 0.62934 | 23.9812 | 52.6715 | 40.5794 | 68.2499 | 124.8974 | 52.6648 | 40.6866
EUDA | Eungella Dam (TF1) | MK | EUDA_11kV_TEF R1 | 11 | 0.62812 | 11.9673 | 0.65465 | 4.1576 | 0.68256 | 0.61857 | 3.9284 | 0.66485 | 4.2224 | 2.0592 | 10.9297 | 0.59614 | 9.8025 | 2.0591 | 10.9327
EUDA | Eungella Dam (TF2) | MK | EUDA_11kV_TEF R2 | 11 | 2.0166 | 38.422 | 2.3993 | 15.2374 | 2.9257 | 2.033 | 12.9115 | 2.499 | 15.8706 | 1.6646 | 3.038 | 0.20155 | 1.9108 | 1.6645 | 3.041
EUMA | Eumamurrin Regulator (Regulated) | SW | GW00024_tr_line_22769 | 33 | 0.52277 | 29.8804 | 0.38351 | 7.3069 | 0.29443 | 0.41894 | 7.9819 | 0.52703 | 10.0412 | 32.7638 | 23.1041 | 40.5443 | 78.7831 | 32.7478 | 23.1331
EUMA | Eumamurrin Regulator (Un-Regulated) | SW | GW00024_AB9545 | 33 | 0.52277 | 29.8804 | 0.38351 | 7.3069 | 0.29443 | 0.41894 | 7.9819 | 0.52703 | 10.0412 | 32.7638 | 23.1041 | 40.5443 | 78.7831 | 32.7478 | 23.1331
EVEL | Evelyn | FN | EVEL_66kV_BUS MAIN | 66 | 1.6834 | 192.435 | 1.0215 | 38.9239 | 0.73381 | 1.4609 | 55.6669 | 1.5401 | 58.6867 | 9.3218 | 23.0891 | 17.6709 | 71.3201 | 9.1191 | 23.2769
EVEL | Evelyn | FN | EVEL_66kV_BUS RESERVE | 66 | 1.6834 | 192.435 | 1.0215 | 38.9239 | 0.73381 | 1.4609 | 55.6669 | 1.5401 | 58.6867 | 9.3218 | 23.0891 | 17.6709 | 71.3201 | 9.1191 | 23.2769
EVEL | Evelyn | FN | EVEL_22kV_BUS 1 | 22 | 1.6175 | 61.6335 | 1.8041 | 22.9153 | 2.0422 | 1.6873 | 21.4311 | 1.7772 | 22.5738 | 1.4896 | 8.5088 | 0.45383 | 5.9433 | 1.4671 | 8.5296
EVEL | Evelyn | FN | EVEL_22kV_BUS 2 | 22 | 1.6175 | 61.6335 | 1.8041 | 22.9153 | 2.0422 | 1.6873 | 21.4311 | 1.7772 | 22.5738 | 1.4896 | 8.5088 | 0.45383 | 5.9433 | 1.4671 | 8.5296
FARB | Farnborough | CA | FARB_66kV_TEF Upstream | 66 | 2.4697 | 282.3288 | 1.5801 | 60.2097 | 1.1563 | 2.1255 | 80.9921 | 2.3034 | 87.7729 | 7.8927 | 15.0251 | 13.2606 | 44.0513 | 7.8581 | 15.0303
FARL | Farleigh | MK | FARL_33kV_BUS 1 | 33 | 2.1059 | 120.3667 | 1.1943 | 22.7539 | 0.82939 | 1.7831 | 33.9725 | 1.9509 | 37.1694 | 5.2007 | 8.4852 | 9.9817 | 31.5438 | 5.1821 | 8.5191
FARL | Farleigh | MK | FARL_33kV_BUS 2 | 33 | 2.1059 | 120.3667 | 1.1943 | 22.7539 | 0.82939 | 1.7831 | 33.9725 | 1.9509 | 37.1694 | 5.2007 | 8.4852 | 9.9817 | 31.5438 | 5.1821 | 8.5191
FARL | Farleigh | MK | FARL_33kV_BUS 3 | 33 | 2.1059 | 120.3667 | 1.1943 | 22.7539 | 0.82939 | 1.7831 | 33.9725 | 1.9509 | 37.1694 | 5.2007 | 8.4852 | 9.9817 | 31.5438 | 5.1821 | 8.5191
FARL | Farleigh | MK | FARL_11kV_BUS 1 | 11 | 3.8153 | 72.6916 | 4.019 | 25.5239 | 4.2434 | 3.7686 | 23.9339 | 4.0769 | 25.892 | 0.44781 | 1.7754 | 0.15833 | 1.5528 | 0.43362 | 1.7818
FARL | Farleigh | MK | FARL_11kV_BUS 2 | 11 | 3.8153 | 72.6916 | 4.019 | 25.5239 | 4.2434 | 3.7686 | 23.9339 | 4.0769 | 25.892 | 0.44781 | 1.7754 | 0.15833 | 1.5528 | 0.43362 | 1.7818
FARL | Farleigh | MK | FARL_11kV_BUS 3 | 11 | 3.8153 | 72.6916 | 4.019 | 25.5239 | 4.2434 | 3.7686 | 23.9339 | 4.0769 | 25.892 | 0.44781 | 1.7754 | 0.15833 | 1.5528 | 0.43362 | 1.7818
FARN | Farnsfield | WB | FARN_66kV_TEF T1 | 66 | 2.6068 | 298 | 1.8287 | 69.6843 | 1.4025 | 2.2665 | 86.3649 | 2.4588 | 93.6933 | 7.0466 | 14.454 | 9.9145 | 35.5293 | 6.9525 | 14.4908
FARN | Farnsfield | WB | FARN_66kV_TEF T2 | 66 | 2.6068 | 298 | 1.8287 | 69.6843 | 1.4025 | 2.2665 | 86.3649 | 2.4588 | 93.6933 | 7.0466 | 14.454 | 9.9145 | 35.5293 | 6.9525 | 14.4908
FARN | Farnsfield | WB | FARN_11kV_BUS 1 | 11 | 7.0219 | 133.7856 | 8.2141 | 52.1663 | 9.8738 | 7.4735 | 47.4629 | 8.176 | 51.9248 | 0.22744 | 0.96859 | 0.0317 | 0.56709 | 0.22483 | 0.96961
FARN | Farnsfield | WB | FARN_11kV_BUS 2 | 11 | 7.0219 | 133.7856 | 8.2141 | 52.1663 | 9.8738 | 7.4735 | 47.4629 | 8.176 | 51.9248 | 0.22744 | 0.96859 | 0.0317 | 0.56709 | 0.22483 | 0.96961
FILA | Fisherman's Landing (TF1) | CA | 6103_FILA - BOCR TR_LINE_22202_1 | 66 | 6.5748 | 751.5979 | 5.6538 | 215.4387 | 4.9734 | 6.3463 | 241.8277 | 6.0603 | 230.927 | 0.82547 | 6.3217 | 2.0032 | 9.2688 | 0.82267 | 6.3493
FILA | Fisherman's Landing (TF1) | CA | FILA_11kV_BUS 1 | 11 | 15.7509 | 300.0957 | 18.1545 | 115.2964 | 21.4656 | 17.228 | 109.4127 | 17.4749 | 110.9805 | 0.0394 | 0.44178 | 0.01647 | 0.26618 | 0.03932 | 0.44255
FILA | Fisherman's Landing (TF2) | CA | 6103_FILA - BOCR TR_LINE_22203_1 | 66 | 6.5907 | 753.4207 | 5.6748 | 216.2386 | 4.9966 | 6.3671 | 242.621 | 6.0738 | 231.4431 | 0.80147 | 6.3092 | 1.9773 | 9.2225 | 0.79867 | 6.3369
FILA | Fisherman's Landing (TF2) | CA | FILA_11kV_BUS 2 | 11 | 15.7509 | 300.0957 | 18.1545 | 115.2964 | 21.4656 | 17.228 | 109.4127 | 17.4749 | 110.9805 | 0.0394 | 0.44178 | 0.01647 | 0.26618 | 0.03932 | 0.44255
FITR | Fig Tree T185 | NQ | FITR_132kV_TEF T1 | 132 | 2.7914 | 638.1984 | 1.9617 | 149.4991 | 1.5118 | 2.4764 | 188.7271 | 2.5861 | 197.0901 | 12.2708 | 27.4109 | 22.0785 | 64.5753 | 12.3216 | 27.4218
FITR | Fig Tree T185 | NQ | FITR_11kV_BUS 1 | 11 | 7.7304 | 147.2844 | 5.5169 | 35.037 | 4.28 | 6.7998 | 43.1845 | 7.2492 | 46.0385 | 0.12156 | 0.89548 | 0 | 2 | 0.12191 | 0.89556
FOXL | Foxleigh | CA | FOXL_66kV_TEF T1 | 66 | 1.9236 | 219.8934 | 1.0633 | 40.5152 | 0.73415 | 1.6476 | 62.7831 | 1.757 | 66.9513 | 9.707 | 19.5092 | 20.3733 | 72.2334 | 9.5205 | 19.697
FOXL | Foxleigh | CA | FOXL_22kV_TEF T1 | 22 | 1.6316 | 62.1737 | 1.791 | 22.7482 | 1.9868 | 1.6724 | 21.242 | 1.7792 | 22.5992 | 1.3926 | 8.4492 | 0.31407 | 6.2815 | 1.3719 | 8.47
FREN | Frenchville | CA | FREN_66kV_BUS 1 | 66 | 8.6647 | 990.5072 | 8.1652 | 311.1363 | 7.7508 | 8.6409 | 329.2629 | 8.2208 | 313.2561 | 1.1267 | 4.7046 | 1.8031 | 5.4221 | 1.1276 | 4.7298
FREN | Frenchville | CA | FREN_66kV_BUS 2 | 66 | 8.6647 | 990.5072 | 8.1652 | 311.1363 | 7.7508 | 8.6409 | 329.2629 | 8.2208 | 313.2561 | 1.1267 | 4.7046 | 1.8031 | 5.4221 | 1.1276 | 4.7298
FREN | Frenchville | CA | FREN_11kV_BUS LH | 11 | 14.4567 | 275.4363 | 15.9091 | 101.0363 | 17.71 | 15.1104 | 95.9641 | 15.5474 | 98.7391 | 0.04883 | 0.48077 | 0.01753 | 0.35009 | 0.04885 | 0.48147
FREN | Frenchville | CA | FREN_11kV_BUS RH | 11 | 14.4567 | 275.4363 | 15.9091 | 101.0363 | 17.71 | 15.1104 | 95.9641 | 15.5474 | 98.7391 | 0.04883 | 0.48077 | 0.01753 | 0.35009 | 0.04885 | 0.48147
GARB | Garbutt T046 | NQ | GARB_11kV_BUS 3 | 11 | 11.6282 | 221.5465 | 11.4683 | 72.8336 | 11.2892 | 11.5109 | 73.1039 | 11.5907 | 73.6107 | 0.03945 | 0.59948 | 0.0246 | 0.62676 | 0.03069 | 0.59876
GARB | Garbutt T046 (TF3) | NQ | GARB_11kV_BUS 1 | 11 | 10.1398 | 193.1887 | 10.4525 | 66.382 | 10.7864 | 10.2708 | 65.2283 | 10.3389 | 65.6609 | 0.03543 | 0.68805 | 0.02458 | 0.62659 | 0.03492 | 0.68818
GARB | Garbutt T046 (TF5) | NQ | GARB_11kV_BUS 2 | 11 | 10.1398 | 193.1887 | 10.4525 | 66.382 | 10.7864 | 10.2708 | 65.2283 | 10.3389 | 65.6609 | 0.03543 | 0.68805 | 0.02458 | 0.62659 | 0.03492 | 0.68818
GARB | Garbutt T047 | NQ | GARB_66kV_BUS 1 | 66 | 18.6547 | 2132.5126 | 20.3272 | 774.5712 | 22.3398 | 19.4829 | 742.3997 | 19.7943 | 754.2627 | 0.39051 | 2.2127 | 0.2328 | 1.6757 | 0.37202 | 2.2171
GAVI | Gavial 66kV Switching Station | CA | GAVI_66kV_BUS pole10464283 | 66 | 5.5202 | 631.0394 | 4.6044 | 175.4492 | 3.9602 | 5.2 | 198.1465 | 5.1375 | 195.7662 | 1.9258 | 7.345 | 3.323 | 11.6354 | 1.9272 | 7.3708
GAYN | Gayndah | WB | GAYN_11kV_BUS 1 | 11 | 5.7053 | 108.7005 | 7.0517 | 44.7844 | 9.2195 | 6.4849 | 41.1844 | 7.0187 | 44.5747 | 0.27137 | 1.1941 | 0.02644 | 0.52812 | 0.26866 | 1.1955
GAYN | Gayndah | WB | GAYN_11kV_BUS 2 | 11 | 5.7053 | 108.7005 | 7.0517 | 44.7844 | 9.2195 | 6.4849 | 41.1844 | 7.0187 | 44.5747 | 0.27137 | 1.1941 | 0.02644 | 0.52812 | 0.26866 | 1.1955
GAYN | Gayndah (Regulated) | WB | GAYN_66kV_BUS 2 | 66 | 1.6628 | 190.0878 | 1.0518 | 40.0809 | 0.76937 | 1.4772 | 56.2888 | 1.5032 | 57.2786 | 8.7323 | 23.6483 | 20.9683 | 65.8963 | 8.6347 | 23.6992
GAYN | Gayndah (Unregulated) | WB | GAYN_66kV_BUS 1 | 66 | 1.6628 | 190.0878 | 1.0518 | 40.0809 | 0.76937 | 1.4772 | 56.2888 | 1.5032 | 57.2786 | 8.7323 | 23.6483 | 20.9683 | 65.8963 | 8.6347 | 23.6992
GEOR | Georgetown | FN | GEOR_132kV_BUS 1 | 132 | 0.6191 | 141.5446 | 0.76559 | 58.3461 | 1.0374 | 0.69992 | 53.3408 | 0.78496 | 59.8222 | 46.9728 | 127.0007 | 4.8594 | 55.1109 | 47.3553 | 131.0513
GEOR | Georgetown | FN | GEOR_132kV_BUS 2 | 132 | 0.6191 | 141.5446 | 0.76559 | 58.3461 | 1.0374 | 0.69992 | 53.3408 | 0.78496 | 59.8222 | 46.9728 | 127.0007 | 4.8594 | 55.1109 | 47.3553 | 131.0513
GEOR | Georgetown | FN | GEOR_66kV_BUS 1 | 66 | 0.9483 | 108.4055 | 1.2681 | 48.3206 | 1.9728 | 1.2372 | 47.1423 | 1.3252 | 50.4948 | 11.8409 | 42.5852 | 0.38551 | 10.0481 | 11.8456 | 43.5633
GEOR | Georgetown | FN | GEOR_66kV_BUS 2 | 66 | 0.9483 | 108.4055 | 1.2681 | 48.3206 | 1.9728 | 1.2372 | 47.1423 | 1.3252 | 50.4948 | 11.8409 | 42.5852 | 0.38551 | 10.0481 | 11.8456 | 43.5633
GEOR | Georgetown | FN | GEOR_22kV_BUS 1 | 22 | 1.1009 | 41.9497 | 1.2594 | 15.9965 | 1.4828 | 1.1555 | 14.6768 | 1.2545 | 15.9339 | 1.961 | 12.539 | 0.00268 | 7.8633 | 1.9615 | 12.6477
GEOR | Georgetown | FN | GEOR_22kV_BUS 2 | 22 | 1.1009 | 41.9497 | 1.2594 | 15.9965 | 1.4828 | 1.1555 | 14.6768 | 1.2545 | 15.9339 | 1.961 | 12.539 | 0.00268 | 7.8633 | 1.9615 | 12.6477
GEOR | Georgetown | FN | GEOR_6.6kV_BUS 1 | 6.6 | 7.4609 | 85.2896 | 0 | 0 | 0 | 6.407 | 24.4137 | 6.407 | 24.4137 | 0.12541 | 0.54763 | 116470585.5392 | 0.79705 | 0.1255 | 0.55739
GEOR | Georgetown | FN | GEOR_6.6kV_BUS 2 | 6.6 | 7.4609 | 85.2896 | 0 | 0 | 0 | 6.407 | 24.4137 | 6.407 | 24.4137 | 0.12541 | 0.54763 | 116470585.5392 | 0.79705 | 0.1255 | 0.55739
GEOR | Georgetown | FN | GEOR_6.6kV_BUS 3 | 6.6 | 7.4609 | 85.2896 | 0 | 0 | 0 | 6.407 | 24.4137 | 6.407 | 24.4137 | 0.12541 | 0.54763 | 116470585.5392 | 0.79705 | 0.1255 | 0.55739
GIRU | Giru | NQ | GIRU_66kV_BUS 1 | 66 | 1.2772 | 145.9983 | 0.94218 | 35.9019 | 0.73309 | 1.0596 | 40.378 | 1.2639 | 48.1594 | 24.1765 | 22.1952 | 31.2103 | 62.8383 | 24.0731 | 22.1987
GIRU | Giru | NQ | GIRU_66kV_BUS 2 | 66 | 1.2772 | 145.9983 | 0.94218 | 35.9019 | 0.73309 | 1.0596 | 40.378 | 1.2639 | 48.1594 | 24.1765 | 22.1952 | 31.2103 | 62.8383 | 24.0731 | 22.1987
GIRU | Giru (TF2) | NQ | GIRU_11kV_TEF 1 | 11 | 2.5135 | 47.8892 | 2.7713 | 17.6004 | 3.0719 | 2.4913 | 15.8218 | 2.8268 | 17.9523 | 0.82959 | 2.6526 | 0.15803 | 2.0361 | 0.82672 | 2.6527
GIRU | Giru (TF2) | NQ | GIRU_11kV_TEF 2 | 11 | 2.4912 | 47.4628 | 2.7462 | 17.4405 | 3.0441 | 2.4739 | 15.7114 | 2.7971 | 17.7641 | 0.86601 | 2.6672 | 0.19444 | 2.0507 | 0.86314 | 2.6673
GIVE | Givelda | WB | GIVE_66kV_BUS | 66 | 3.2761 | 374.5059 | 2.3367 | 89.0394 | 1.8228 | 2.9428 | 112.1354 | 3.0055 | 114.525 | 3.8751 | 12.1945 | 7.233 | 27.2314 | 3.8502 | 12.272
GIVE | Givelda | WB | GIVE_11kV_BUS 1 | 11 | 4.6531 | 88.6531 | 5.0395 | 32.0053 | 5.5022 | 4.7925 | 30.4364 | 4.9618 | 31.5114 | 0.15664 | 1.4933 | 0.049 | 1.1545 | 0.15595 | 1.4954
GIVE | Givelda | WB | GIVE_11kV_BUS 2 | 11 | 4.6531 | 88.6531 | 5.0395 | 32.0053 | 5.5022 | 4.7925 | 30.4364 | 4.9618 | 31.5114 | 0.15664 | 1.4933 | 0.049 | 1.1545 | 0.15595 | 1.4954
GLEE | Glenelg | NQ | GLEE_66kV_TEF T1 | 66 | 0.52607 | 60.1383 | 0.35944 | 13.6964 | 0.27786 | 0.45767 | 17.4397 | 0.48529 | 18.4921 | 33.9948 | 72.0602 | 56.9061 | 180.3813 | 34.2526 | 74.2498
GLEE | Glenelg | NQ | GLEE_33kV_TEF T1 | 33 | 0.14648 | 8.3726 | 0.15312 | 2.9173 | 0.161 | 0.14826 | 2.8247 | 0.15195 | 2.895 | 24.1072 | 141.0278 | 15.6085 | 123.0127 | 24.1717 | 141.5752
GLEL | Glenella | MK | GLEL_66kV_BUS 1 | 66 | 5.4207 | 619.6706 | 5.6718 | 216.1251 | 5.9853 | 5.5002 | 209.5845 | 5.6184 | 214.0889 | 1.1736 | 7.643 | 0.71705 | 6.6225 | 1.1241 | 7.6992
GLEL | Glenella | MK | GLEL_66kV_BUS 2 | 66 | 5.4207 | 619.6706 | 5.6718 | 216.1251 | 5.9853 | 5.5002 | 209.5845 | 5.6184 | 214.0889 | 1.1736 | 7.643 | 0.71705 | 6.6225 | 1.1241 | 7.6992
GLEL | Glenella | MK | GLEL_11kV_BUS 1 | 11 | 12.4473 | 237.1519 | 14.2465 | 90.4775 | 16.7014 | 13.4714 | 85.5548 | 13.7864 | 87.5556 | 0.04382 | 0.55953 | 0.01122 | 0.34723 | 0.04245 | 0.5611
GLEL | Glenella | MK | GLEL_11kV_BUS 2 | 11 | 12.4473 | 237.1519 | 14.2465 | 90.4775 | 16.7014 | 13.4714 | 85.5548 | 13.7864 | 87.5556 | 0.04382 | 0.55953 | 0.01122 | 0.34723 | 0.04245 | 0.5611
GLEL | Glenella | MK | GLEL_11kV_BUS 3 | 11 | 12.4473 | 237.1519 | 14.2465 | 90.4775 | 16.7014 | 13.4714 | 85.5548 | 13.7864 | 87.5556 | 0.04382 | 0.55953 | 0.01122 | 0.34723 | 0.04245 | 0.5611
GLEL | Glenella (TF5) | MK | GLEL_33kV_TEF T5 | 33 | 4.633 | 264.8107 | 5.6524 | 107.6919 | 7.2735 | 5.3831 | 102.5614 | 5.4431 | 103.7047 | 0.34951 | 4.5101 | 0.1052 | 2.061 | 0.33714 | 4.5242
GLEL | Glenella (TF6) | MK | GLEL_33kV_TEF T6 | 33 | 4.6361 | 264.9883 | 5.5996 | 106.6872 | 7.0942 | 5.3219 | 101.3965 | 5.3885 | 102.6649 | 0.3495 | 4.5071 | 0.10618 | 2.172 | 0.33713 | 4.5211
GLEN | Glenden | MK | GLEN_66kV_BUS 1 | 66 | 1.9527 | 223.2296 | 1.5532 | 59.1839 | 1.2804 | 1.689 | 64.3598 | 1.9195 | 73.142 | 11.9331 | 17.8423 | 12.9933 | 36.3876 | 11.9426 | 17.8496
GLEN | Glenden | MK | GLEN_66kV_BUS 2 | 66 | 1.9527 | 223.2296 | 1.5532 | 59.1839 | 1.2804 | 1.689 | 64.3598 | 1.9195 | 73.142 | 11.9331 | 17.8423 | 12.9933 | 36.3876 | 11.9426 | 17.8496
GLEN | Glenden | MK | GLEN_11kV_BUS 1 | 11 | 3.9918 | 76.054 | 4.461 | 28.3313 | 5.0414 | 4.0651 | 25.8166 | 4.4813 | 28.4604 | 0.39198 | 1.7056 | 0.0605 | 1.21 | 0.39224 | 1.7058
GLEN | Glenden | MK | GLEN_11kV_BUS 2 | 11 | 3.9918 | 76.054 | 4.461 | 28.3313 | 5.0414 | 4.0651 | 25.8166 | 4.4813 | 28.4604 | 0.39198 | 1.7056 | 0.0605 | 1.21 | 0.39224 | 1.7058
GLFS | Gladstone Friend Street | CA | GLFS_11kV_BUS 1 | 11 | 17.9622 | 342.2253 | 19.5607 | 124.2272 | 21.4978 | 18.7056 | 118.7963 | 19.0992 | 121.2964 | 0.03612 | 0.38725 | 0.01636 | 0.29279 | 0.03611 | 0.38774
GLFS | Gladstone Friend Street | CA | GLFS_11kV_BUS 2 | 11 | 17.9622 | 342.2253 | 19.5607 | 124.2272 | 21.4978 | 18.7056 | 118.7963 | 19.0992 | 121.2964 | 0.03612 | 0.38725 | 0.01636 | 0.29279 | 0.03611 | 0.38774
GLFS | Gladstone Friend Street | CA | GLFS_11kV_BUS 3 | 11 | 17.9622 | 342.2253 | 19.5607 | 124.2272 | 21.4978 | 18.7056 | 118.7963 | 19.0992 | 121.2964 | 0.03612 | 0.38725 | 0.01636 | 0.29279 | 0.03611 | 0.38774
GLFS | Gladstone Friend Street (TF1) | CA | GLFS_66kV_TEF T1 | 66 | 12.0648 | 1379.1963 | 11.1007 | 422.9942 | 10.318 | 11.9002 | 453.4577 | 11.3663 | 433.1135 | 0.7113 | 3.4007 | 1.2327 | 4.1938 | 0.71101 | 3.4181
GLFS | Gladstone Friend Street (TF5) | CA | GLFS_66kV_TEF T5 | 66 | 12.0648 | 1379.1963 | 11.1007 | 422.9942 | 10.318 | 11.9002 | 453.4577 | 11.3663 | 433.1135 | 0.7113 | 3.4007 | 1.2327 | 4.1938 | 0.71101 | 3.4181
GLNO | Gladstone North T074 | CA | GLNO_66kV_BUS 1 | 66 | 14.5986 | 1668.8473 | 17.5167 | 667.4772 | 22.045 | 16.5838 | 631.929 | 16.9338 | 645.2653 | 0.25819 | 2.8596 | 0.06685 | 1.4196 | 0.25821 | 2.8759
GLNO | Gladstone North T074 | CA | GLNO_66kV_BUS 2 | 66 | 14.5986 | 1668.8473 | 17.5167 | 667.4772 | 22.045 | 16.5838 | 631.929 | 16.9338 | 645.2653 | 0.25819 | 2.8596 | 0.06685 | 1.4196 | 0.25821 | 2.8759
GLNO | Gladstone North T074 | CA | GLNO_66kV_BUS 3 | 66 | 14.5986 | 1668.8473 | 17.5167 | 667.4772 | 22.045 | 16.5838 | 631.929 | 16.9338 | 645.2653 | 0.25819 | 2.8596 | 0.06685 | 1.4196 | 0.25821 | 2.8759
GLNO | Gladstone North T074 (TF1) | CA | GLNO_132kV_BUS 1 | 132 | 27.5779 | 6305.1543 | 33.1677 | 2527.722 | 42.7032 | 32.0646 | 2443.6514 | 31.8289 | 2425.6868 | 0.14002 | 3.0366 | 0.08789 | 1.4369 | 0.14168 | 3.1001
GLNO | Gladstone North T074 (TF1) | CA | GLNO_11kV_TEF T1 | 11 | 21.6705 | 412.8777 | 0 | 0 | 0 | 18.7541 | 119.1044 | 18.7541 | 119.1044 | 0.02559 | 0.32136 | 135802470.2909 | -2.3367 | 0.02559 | 0.32181
GLNO | Gladstone North T074 (TF2) | CA | GLNO_132kV_BUS 2 | 132 | 27.5779 | 6305.1543 | 33.1677 | 2527.722 | 42.7032 | 32.0646 | 2443.6514 | 31.8289 | 2425.6868 | 0.14002 | 3.0366 | 0.08789 | 1.4369 | 0.14168 | 3.1001
GLNO | Gladstone North T074 (TF2) | CA | GLNO_11kV_TEF T2 | 11 | 21.4972 | 409.5765 | 0 | 0 | 0 | 18.6042 | 118.1527 | 18.6042 | 118.1527 | 0.0253 | 0.32399 | 135802470.6018 | -4.1575 | 0.0253 | 0.32444
GLSO | Gladstone South T152 | CA | GLSO_66kV_BUS EAST | 66 | 13.828 | 1580.7559 | 16.2842 | 620.5093 | 19.9468 | 15.5661 | 593.149 | 15.5744 | 593.4635 | 0.3301 | 3.0133 | 0.17574 | 1.632 | 0.32966 | 3.0317
GLSO | Gladstone South T152 | CA | GLSO_66kV_BUS TRANSFER | 66 | 13.828 | 1580.7559 | 16.2842 | 620.5093 | 19.9468 | 15.5661 | 593.149 | 15.5744 | 593.4635 | 0.3301 | 3.0133 | 0.17574 | 1.632 | 0.32966 | 3.0317
GLSO | Gladstone South T152 | CA | GLSO_66kV_BUS WEST | 66 | 13.828 | 1580.7559 | 16.2842 | 620.5093 | 19.9468 | 15.5661 | 593.149 | 15.5744 | 593.4635 | 0.3301 | 3.0133 | 0.17574 | 1.632 | 0.32966 | 3.0317
GLSO | Gladstone South T152 (TF 1) | CA | GLSO_11kV_BUS 1 | 11 | 13.4093 | 255.4805 | 14.1664 | 89.9691 | 15.0297 | 13.7852 | 87.5477 | 13.873 | 88.1056 | 0.02656 | 0.52031 | 0.01739 | 0.43661 | 0.02655 | 0.52083
GLSO | Gladstone South T152 (TF 2) | CA | GLSO_11kV_BUS 2 | 11 | 13.4093 | 255.4805 | 14.1664 | 89.9691 | 15.0297 | 13.7852 | 87.5477 | 13.873 | 88.1056 | 0.02656 | 0.52031 | 0.01739 | 0.43661 | 0.02655 | 0.52083
GLSO | Gladstone South T152 (TF 3) | CA | GLSO_11kV_BUS 3 | 11 | 13.4093 | 255.4805 | 14.1664 | 89.9691 | 15.0297 | 13.7852 | 87.5477 | 13.873 | 88.1056 | 0.02656 | 0.52031 | 0.01739 | 0.43661 | 0.02655 | 0.52083
GOOB | Gooburrum | WB | GOOB_66kV_BUS 1 | 66 | 1.745 | 199.4785 | 1.2691 | 48.3602 | 0.98877 | 1.4744 | 56.181 | 1.6954 | 64.6052 | 15.5694 | 18.2941 | 20.7692 | 47.7364 | 15.5412 | 18.3917
GOOB | Gooburrum | WB | GOOB_66kV_BUS 2 | 66 | 1.745 | 199.4785 | 1.2691 | 48.3602 | 0.98877 | 1.4744 | 56.181 | 1.6954 | 64.6052 | 15.5694 | 18.2941 | 20.7692 | 47.7364 | 15.5412 | 18.3917
GOOB | Gooburrum | WB | GOOB_11kV_BUS 1 | 11 | 4.7099 | 89.7354 | 5.4677 | 34.7244 | 6.4893 | 4.8363 | 30.7149 | 5.5601 | 35.3113 | 0.51122 | 1.3925 | 0.07874 | 0.88432 | 0.51044 | 1.3952
GOOB | Gooburrum | WB | GOOB_11kV_BUS 2 | 11 | 4.7099 | 89.7354 | 5.4677 | 34.7244 | 6.4893 | 4.8363 | 30.7149 | 5.5601 | 35.3113 | 0.51122 | 1.3925 | 0.07874 | 0.88432 | 0.51044 | 1.3952
GOOB | Gooburrum | WB | GOOB_3.3kV_BUS | 3.3 | 6.749 | 38.5756 | 7.1269 | 13.5785 | 7.5432 | 6.701 | 12.7672 | 7.1998 | 13.7176 | 0.03892 | 0.30811 | 0 | 0.26237 | 0.03885 | 0.30835
GOOT | Gootchie | WB | GOOT_66kV_BUS | 66 | 2.3077 | 263.8104 | 1.6461 | 62.7253 | 1.2696 | 1.9658 | 74.9082 | 2.2198 | 84.5859 | 10.2447 | 15.0003 | 13.5474 | 38.3813 | 10.2191 | 15.0281
GOOT | Gootchie (TF1) | WB | GOOT_11kV_BUS A | 11 | 3.718 | 70.8372 | 3.9833 | 25.2972 | 4.2733 | 3.6379 | 23.1038 | 4.0777 | 25.8967 | 0.37378 | 1.8416 | 0.00013 | 1.5247 | 0.37307 | 1.8424
GOOT | Gootchie (TF1) | WB | GOOT_11kV_TEF T01 | 11 | 1.3324 | 25.3864 | 1.3719 | 8.7125 | 1.4136 | 1.3352 | 8.4799 | 1.3708 | 8.7058 | 0.77954 | 5.1852 | 0.49496 | 4.7686 | 0.77883 | 5.186
GOOT | Gootchie (TF2) | WB | GOOT_11kV_BUS B | 11 | 3.718 | 70.8372 | 3.9833 | 25.2972 | 4.2733 | 3.6379 | 23.1038 | 4.0777 | 25.8967 | 0.37378 | 1.8416 | 0.00013 | 1.5247 | 0.37307 | 1.8424
GOOT | Gootchie (TF2) | WB | GOOT_11kV_TEF T02 | 11 | 3.718 | 70.8372 | 3.9833 | 25.2972 | 4.2733 | 3.6379 | 23.1038 | 4.0777 | 25.8967 | 0.37378 | 1.8416 | 0.00013 | 1.5247 | 0.37307 | 1.8424
GORD | Gordonvale SS | NQ | GORD_22KV BUS 1 | 22 | 4.0433 | 154.0719 | 2.9674 | 37.6907 | 2.3374 | 3.5684 | 45.3244 | 3.8123 | 48.422 | 1.7356 | 2.9881 | 2.7548 | 6.7056 | 1.7343 | 2.9864
GRAC | Gracemere | CA | GRAC_66kV_TEF T1 | 66 | 6.402 | 731.8427 | 5.2146 | 198.7019 | 4.4129 | 5.9408 | 226.3763 | 5.9782 | 227.8017 | 1.771 | 6.3034 | 2.8394 | 10.6224 | 1.7724 | 6.3292
GRAC | Gracemere | CA | GRAC_11kV_TEF T1 | 11 | 6.4815 | 123.4891 | 6.9615 | 44.2115 | 7.5227 | 6.6861 | 42.4625 | 6.825 | 43.3445 | 0.09969 | 1.0732 | 0.04813 | 0.85322 | 0.09973 | 1.0739
GRCR | Granite Creek T166 | CA | GRCR_132kV_BUS 1 | 132 | 2.4454 | 559.0978 | 2.3186 | 176.7004 | 2.19 | 2.1978 | 167.4959 | 2.555 | 194.7147 | 12.583 | 31.891 | 4.5943 | 40.4684 | 12.5606 | 31.9616
GRCR | Granite Creek T166 | CA | GRCR_66kV_BUS 1 | 66 | 1.9811 | 226.4695 | 2.3712 | 90.3528 | 2.9541 | 2.2216 | 84.653 | 2.3049 | 87.8302 | 3.4885 | 20.8699 | 0.97672 | 10.6798 | 3.4829 | 20.8876
GRCR | Granite Creek T166 | CA | GRCR_22kV_BUS 1 | 22 | 3.3093 | 126.103 | 3.5627 | 45.2528 | 3.8599 | 3.4411 | 43.7081 | 3.4686 | 44.0576 | 0.48341 | 4.1945 | 0.333 | 3.303 | 0.48279 | 4.1965
GREN | Greenvale | NQ | GREN_66kV_TEF T1 | 66 | 0.49651 | 56.7585 | 0.31367 | 11.9525 | 0.22853 | 0.42496 | 16.1933 | 0.46326 | 17.6525 | 44.8414 | 71.5273 | 80.6674 | 219.5981 | 44.7657 | 71.8021
GREN | Greenvale | NQ | GREN_11kV_TEF T1 | 11 | 0.92799 | 17.6806 | 1.039 | 6.5982 | 1.1783 | 0.94974 | 6.0316 | 1.0408 | 6.6098 | 1.2456 | 7.4243 | 0 | 5.1619 | 1.2435 | 7.4319
GUEA | Gumlu Rebuild (TF1) | NQ | GUEA_66kV_BUS 1 | 66 | 1.3164 | 150.4851 | 0.82094 | 31.2821 | 0.59127 | 1.1129 | 42.4075 | 1.2403 | 47.2632 | 16.7083 | 27.1051 | 25.7752 | 87.0978 | 16.6456 | 27.0984
GUEA | Gumlu Rebuild (TF1) | NQ | GUEA_11kV_BUS 1 | 11 | 2.5705 | 48.9756 | 2.865 | 18.1952 | 3.2286 | 2.6396 | 16.7638 | 2.8561 | 18.1388 | 0.65264 | 2.6382 | 0.18852 | 1.8852 | 0.6509 | 2.638
GUNP | Gunpowder | NQ - MI | GUNP_220kV_BUS | 220 | 1.2859 | 490.0082 | 1.7504 | 222.325 | 2.8114 | 1.7778 | 225.8117 | 1.8059 | 229.382 | 10.6483 | 108.1282 | 0.54814 | 20.4096 | 9.5516 | 110.0309
GUNP | Gunpowder (TF1) | NQ - MI | GUNP_11kV_TEF T1 | 11 | 16.4932 | 314.2373 | 0.00958 | 0.06082 | 0.00482 | 14.2072 | 90.2275 | 14.2075 | 90.2296 | 0.03165 | 0.42238 | 0.02741 | 2187.6 | 0.02891 | 0.42714
GUNP | Gunpowder (TF2) | NQ - MI | GUNP_11kV_TEF T2 | 11 | 16.5472 | 315.2658 | 0.00956 | 0.06069 | 0.00481 | 14.2534 | 90.5213 | 14.2537 | 90.5234 | 0.0317 | 0.42099 | 0.02753 | 2192.3 | 0.02896 | 0.42575
GUTH | Guthalungra | NQ | GUTH_66kV_TEF T1 | 66 | 1.0524 | 120.3105 | 0.65058 | 24.7906 | 0.46696 | 0.89044 | 33.9304 | 0.98947 | 37.7038 | 21.1176 | 33.7674 | 34.0008 | 110.1122 | 21.0549 | 33.7608
GUTH | Guthalungra | NQ | GUTH_11kV_TEF T1 | 11 | 0.39633 | 7.5511 | 0.40382 | 2.5646 | 0.41154 | 0.39666 | 2.5191 | 0.40369 | 2.5638 | 1.4185 | 17.5694 | 0.83189 | 16.6314 | 1.4167 | 17.5692
HAIS | Hayman Island | MK | HAIS_22kV_TEF T1 | 22 | 1.7326 | 66.0216 | 1.0294 | 13.0748 | 0.69326 | 1.7231 | 21.8866 | 1.3341 | 16.9456 | 5.1807 | 6.1797 | 26.5679 | 4.8173 | 5.1759 | 6.169
HAIS | Hayman Island | MK | HAIS_11kV_TEF T1 | 11 | 1.9448 | 37.0536 | 2.3679 | 15.0384 | 3.0004 | 2.072 | 13.1588 | 2.4256 | 15.4049 | 1.4705 | 3.2773 | 0.17532 | 1.7324 | 1.4693 | 3.2746
HAUG | Haughton | NQ | HAUG_66kV_TEF T1 | 66 | 2.5783 | 294.7454 | 1.7894 | 68.1868 | 1.3594 | 2.2074 | 84.1136 | 2.4574 | 93.6392 | 9.2732 | 13.3525 | 13.9003 | 35.657 | 9.2366 | 13.3419
HAUG | Haughton | NQ | HAUG_66kV_TEF T2 | 66 | 2.5783 | 294.7454 | 1.7894 | 68.1868 | 1.3594 | 2.2074 | 84.1136 | 2.4574 | 93.6392 | 9.2732 | 13.3525 | 13.9003 | 35.657 | 9.2366 | 13.3419
HAUG | Haughton (TF1) | NQ | HAUG_11kV_BUS 1 | 11 | 2.4626 | 46.9184 | 2.5888 | 16.4411 | 2.7601 | 2.5061 | 15.9161 | 2.5839 | 16.41 | 0.58998 | 2.7748 | 0.32346 | 2.3956 | 0.58003 | 2.7662
HAUG | Haughton (TF2) | NQ | HAUG_11kV_BUS 2 | 11 | 3.4593 | 65.9088 | 3.7117 | 23.5728 | 3.9979 | 3.4865 | 22.1424 | 3.7133 | 23.5828 | 0.39819 | 1.9798 | 0.1406 | 1.6089 | 0.39718 | 1.9795
HAVI | Havilah T184 | NQ | HAVI_132kV_TEF T1 | 132 | 2.7958 | 639.2031 | 1.9654 | 149.7814 | 1.515 | 2.4804 | 189.0349 | 2.5903 | 197.4063 | 12.2505 | 27.3683 | 22.0341 | 64.4344 | 12.3013 | 27.3791
HAVI | Havilah T184 | NQ | HAVI_11kV_BUS 1 | 11 | 7.8329 | 149.2363 | 5.5517 | 35.2579 | 4.2904 | 6.8817 | 43.7048 | 7.3393 | 46.611 | 0.12145 | 0.88357 | 0 | 2 | 0.1218 | 0.88365
HELE | Helenvale | FN | HELE_66kV_TEF T1 | 66 | 0.77158 | 88.2032 | 0.54591 | 20.8018 | 0.41505 | 0.68592 | 26.1369 | 0.72377 | 27.5792 | 16.5737 | 51.7347 | 22.9806 | 121.0443 | 15.9195 | 50.7872
HELE | Helenvale | FN | HELE_22kV_BUS RMU 1 | 22 | 0.96904 | 36.9255 | 1.2175 | 15.4641 | 1.6166 | 1.1209 | 14.2374 | 1.21 | 15.369 | 2.5212 | 14.1961 | 0.00536 | 5.7799 | 2.4486 | 14.0908
HEPA | Hermit Park | NQ | HEPA_66kV_BUS 1 | 66 | 13.9171 | 1590.9418 | 11.6601 | 444.3114 | 10.0285 | 12.9289 | 492.6578 | 13.1811 | 502.2685 | 0.80747 | 2.9015 | 1.0829 | 4.639 | 0.78911 | 2.9056
HEPA | Hermit Park | NQ | HEPA_66kV_BUS 2 | 66 | 13.9171 | 1590.9418 | 11.6601 | 444.3114 | 10.0285 | 12.9289 | 492.6578 | 13.1811 | 502.2685 | 0.80747 | 2.9015 | 1.0829 | 4.639 | 0.78911 | 2.9056
HEPA | Hermit Park (TF1) | NQ | HEPA_11kV_BUS 1 | 11 | 7.6511 | 145.7732 | 7.8864 | 50.0853 | 8.137 | 7.7299 | 49.0918 | 7.8203 | 49.6658 | 0.05811 | 0.91121 | 0.03568 | 0.83061 | 0.0576 | 0.91133
HEPA | Hermit Park (TF2) | NQ | HEPA_11kV_BUS 2 | 11 | 7.6511 | 145.7732 | 7.8864 | 50.0853 | 8.137 | 7.7299 | 49.0918 | 7.8203 | 49.6658 | 0.05811 | 0.91121 | 0.03568 | 0.83061 | 0.0576 | 0.91133
HIGH | Highfields | SW | HIGH_33kV_BUS | 33 | 2.6503 | 151.482 | 0.97164 | 18.5123 | 0.58979 | 2.2257 | 42.4057 | 2.4 | 45.7263 | 3.4484 | 7.1178 | 6.1909 | 49.1503 | 3.4484 | 7.114
HIGH | Highfields | SW | HIGH_11kV_TEF T3 | 11 | 2.9783 | 56.7438 | 3.3857 | 21.5023 | 3.9139 | 3.1063 | 19.7276 | 3.3641 | 21.3647 | 0.45875 | 2.3007 | 0.07559 | 1.5099 | 0.45874 | 2.3003
HIGH | Highfields (Unregulated) | SW | HIGH_T1 | 0.415 | 23.4836 | 16.2036 | 35.2264 | 8.1021 | 70.4514 | 40.6752 | 9.3553 | 40.6748 | 9.3552 | 0.001 | 0.01024 | 0 | 0 | 0.001 | 0.01024
HILL | Hillsborough | NQ | HILL_66kV_TEF T1 | 66 | 2.7839 | 318.2362 | 1.8841 | 71.7919 | 1.4157 | 2.3909 | 91.1049 | 2.6299 | 100.2139 | 7.4421 | 13.089 | 11.0474 | 35.328 | 7.4184 | 13.0924
HOHI | Home Hill | NQ | HOHI_66kV_BUS 1 | 66 | 5.7211 | 654.0133 | 4.1772 | 159.1724 | 3.2753 | 5.1006 | 194.3605 | 5.3484 | 203.8014 | 2.6144 | 6.8441 | 3.9704 | 15.0017 | 2.5516 | 6.8375
HOHI | Home Hill | NQ | HOHI_66kV_BUS 2 | 66 | 5.7211 | 654.0133 | 4.1772 | 159.1724 | 3.2753 | 5.1006 | 194.3605 | 5.3484 | 203.8014 | 2.6144 | 6.8441 | 3.9704 | 15.0017 | 2.5516 | 6.8375
HOHI | Home Hill | NQ | HOHI_66kV_BUS 3 | 66 | 5.7211 | 654.0133 | 4.1772 | 159.1724 | 3.2753 | 5.1006 | 194.3605 | 5.3484 | 203.8014 | 2.6144 | 6.8441 | 3.9704 | 15.0017 | 2.5516 | 6.8375
HOHI | Home Hill (TF1) | NQ | HOHI_11kV_BUS 1 | 11 | 8.9902 | 171.2868 | 9.8243 | 62.3925 | 10.8158 | 9.2694 | 58.8689 | 9.6875 | 61.5242 | 0.10276 | 0.77024 | 0.03014 | 0.58012 | 0.10102 | 0.77005
HOHI | Home Hill (TF2) | NQ | HOHI_11kV_BUS 2 | 11 | 10.8513 | 206.745 | 11.2271 | 71.3019 | 11.5628 | 10.6421 | 67.5863 | 11.4326 | 72.6067 | 0.11618 | 0.63322 | 0.02919 | 0.5842 | 0.11113 | 0.63159
HOWA | Howard | WB | HOWA_66kV_BUS 1 | 66 | 2.886 | 329.9144 | 1.8103 | 68.9809 | 1.3121 | 2.5596 | 97.5321 | 2.6213 | 99.8847 | 3.7766 | 14.0252 | 7.9092 | 39.7631 | 3.622 | 13.9715
HOWA | Howard | WB | HOWA_66kV_BUS 2 | 66 | 2.886 | 329.9144 | 1.8103 | 68.9809 | 1.3121 | 2.5596 | 97.5321 | 2.6213 | 99.8847 | 3.7766 | 14.0252 | 7.9092 | 39.7631 | 3.622 | 13.9715
HOWA | Howard | WB | HOWA_11kV_BUS 1 | 11 | 5.2257 | 99.5621 | 5.7409 | 36.4595 | 6.1277 | 5.4399 | 34.5478 | 5.5701 | 35.3747 | 0.14301 | 1.3293 | 0.05493 | 1.0223 | 0.12292 | 1.2849
HOWA | Howard | WB | HOWA_11kV_BUS 2 | 11 | 5.2257 | 99.5621 | 5.7409 | 36.4595 | 6.1277 | 5.4399 | 34.5478 | 5.5701 | 35.3747 | 0.14301 | 1.3293 | 0.05493 | 1.0223 | 0.12292 | 1.2849
HPCT | Hay Point | MK | HPCT_33kV_BUS 1 | 33 | 5.0448 | 288.3512 | 3.6728 | 69.9765 | 2.8937 | 4.5074 | 85.8767 | 4.6833 | 89.2278 | 1.2519 | 3.9612 | 1.9717 | 8.5848 | 1.2521 | 3.9773
HUGH | Hughenden | NQ | HUGH_66kV_BUS 1 | 66 | 1.4659 | 167.5702 | 1.7367 | 66.1765 | 2.33 | 1.6223 | 61.8167 | 1.7884 | 68.1475 | 9.2021 | 27.0735 | 1.3605 | 13.2465 | 9.4599 | 29.2631
HUGH | Hughenden | NQ | HUGH_66kV_BUS 2 | 66 | 1.4659 | 167.5702 | 1.7367 | 66.1765 | 2.33 | 1.6223 | 61.8167 | 1.7884 | 68.1475 | 9.2021 | 27.0735 | 1.3605 | 13.2465 | 9.4599 | 29.2631
HUGH | Hughenden | NQ | HUGH_33kV_TEF T1 | 33 | 1.4742 | 84.2588 | 1.9593 | 37.3304 | 3.2801 | 2.0236 | 38.554 | 2.1172 | 40.3371 | 2.8512 | 13.9281 | 0.03869 | 2.6004 | 3.036 | 15.0088
HUGH | Hughenden | NQ | HUGH_33kV_TEF T2 | 33 | 1.4742 | 84.2588 | 1.9593 | 37.3304 | 3.2801 | 2.0236 | 38.5539 | 2.1171 | 40.337 | 2.8512 | 13.9281 | 0.03869 | 2.6004 | 3.036 | 15.0088
ICIZ | ICIZ (TF2) | CA | ICIZ_11kV_TEF T2 | 11 | 6.0076 | 114.4602 | 6.2172 | 39.4845 | 6.4463 | 6.1245 | 38.8958 | 6.1141 | 38.8296 | 0.08153 | 1.16 | 0.0762 | 1.0417 | 0.08146 | 1.1608
ILBI | Ilbilbie | MK | ILBI_33kV_TEF T1 | 33 | 0.8347 | 47.7098 | 0.49124 | 9.3594 | 0.34489 | 0.69229 | 13.1899 | 0.78816 | 15.0164 | 15.4965 | 19.7555 | 25.6688 | 75.1182 | 15.5408 | 19.868
ILBI | Ilbilbie | MK | ILBI_11kV_TEF T1 | 11 | 0.7786 | 14.8343 | 0.85952 | 5.4587 | 0.95822 | 0.78736 | 5.0004 | 0.86468 | 5.4915 | 2.3678 | 8.6545 | 0.64594 | 6.4594 | 2.3727 | 8.667
ILRE | Ilbilbie Regulator (Primary) | MK | ILRE_33kV_TEF Primary | 33 | 0.81737 | 46.7187 | 0.48081 | 9.1606 | 0.33756 | 0.67843 | 12.9259 | 0.77134 | 14.696 | 15.787 | 20.2045 | 26.3391 | 76.7001 | 15.8313 | 20.317
ILRE | Ilbilbie Regulator (Secondary) | MK | ILRE_33kV_TEF Secondary | 33 | 0.81737 | 46.7187 | 0.48081 | 9.1606 | 0.33756 | 0.67843 | 12.9259 | 0.77134 | 14.696 | 15.787 | 20.2045 | 26.3391 | 76.7001 | 15.8313 | 20.317
INGH | Ingham T047 | NQ | INGH_66kV_BUS A | 66 | 4.2942 | 490.8927 | 5.0037 | 190.6653 | 6.1918 | 4.8035 | 183.0382 | 4.8346 | 184.224 | 1.1067 | 9.6981 | 0.48203 | 5.3232 | 1.031 | 9.9728
INGH | Ingham T047 | NQ | INGH_66kV_BUS B | 66 | 4.2942 | 490.8927 | 5.0037 | 190.6653 | 6.1918 | 4.8035 | 183.0382 | 4.8346 | 184.224 | 1.1067 | 9.6981 | 0.48203 | 5.3232 | 1.031 | 9.9728
INGH | Ingham T047 | NQ | INGH_66kV_BUS C | 66 | 4.2942 | 490.8927 | 5.0037 | 190.6653 | 6.1918 | 4.8035 | 183.0382 | 4.8346 | 184.224 | 1.1067 | 9.6981 | 0.48203 | 5.3232 | 1.031 | 9.9728
INGH | Ingham T047 | NQ | INGH_11kV_BUS A | 11 | 8.4938 | 161.829 | 9.5089 | 60.3899 | 10.9111 | 9.1002 | 57.7941 | 9.1855 | 58.3355 | 0.0595 | 0.82032 | 0.02876 | 0.55093 | 0.0574 | 0.82795
INGH | Ingham T047 | NQ | INGH_11kV_BUS B | 11 | 8.4938 | 161.829 | 9.5089 | 60.3899 | 10.9111 | 9.1002 | 57.7941 | 9.1855 | 58.3355 | 0.0595 | 0.82032 | 0.02876 | 0.55093 | 0.0574 | 0.82795
INNI | Innisfail T050 | FN | INNI_22kV_BUS 1 | 22 | 11.5674 | 440.7764 | 8.8097 | 111.8984 | 7.1705 | 10.9344 | 138.8854 | 10.2415 | 130.0839 | 0.13475 | 1.2003 | 0.54158 | 2.2732 | 0.12718 | 1.216
INNI | Innisfail T050 | FN | INNI_22kV_BUS 2 | 22 | 11.5674 | 440.7764 | 8.8097 | 111.8984 | 7.1705 | 10.9344 | 138.8854 | 10.2415 | 130.0839 | 0.13475 | 1.2003 | 0.54158 | 2.2732 | 0.12718 | 1.216
ISIS | Isis T131 | WB | ISIS_132kV_BUS 1 | 132 | 7.8516 | 1795.1216 | 8.5681 | 652.9766 | 9.6528 | 8.1718 | 622.7778 | 8.4334 | 642.7102 | 1.9373 | 10.5006 | 0.91568 | 7.7237 | 1.8958 | 10.7439
ISIS | Isis T131 | WB | ISIS_132kV_BUS 2 | 132 | 7.8516 | 1795.1216 | 8.5681 | 652.9766 | 9.6528 | 8.1718 | 622.7778 | 8.4334 | 642.7102 | 1.9373 | 10.5006 | 0.91568 | 7.7237 | 1.8958 | 10.7439
ISIS | Isis T131 | WB | ISIS_66kV_BUS 1 | 66 | 8.3065 | 949.5654 | 9.7006 | 369.6443 | 11.7256 | 9.2469 | 352.3547 | 9.2991 | 354.3453 | 0.52954 | 5.0186 | 0.23909 | 2.8363 | 0.48089 | 5.0484
ISIS | Isis T131 | WB | ISIS_66kV_BUS 2 | 66 | 8.3065 | 949.5654 | 9.7006 | 369.6443 | 11.7256 | 9.2469 | 352.3547 | 9.2991 | 354.3453 | 0.52954 | 5.0186 | 0.23909 | 2.8363 | 0.48089 | 5.0484
ISPL | Isaac Plains | MK | ISPL_66kV_BUS | 66 | 2.8008 | 320.1746 | 2.3361 | 89.0174 | 2.0052 | 2.6351 | 100.4106 | 2.6125 | 99.5498 | 4.5342 | 14.2623 | 7.5983 | 22.6438 | 4.5373 | 14.2756
JAND | Jandowae | SW | JAND_33kV_BUS | 33 | 0.44942 | 25.6881 | 0.32646 | 6.22 | 0.24839 | 0.35755 | 6.8122 | 0.45394 | 8.6486 | 38.2551 | 26.6697 | 46.4875 | 94.8663 | 38.227 | 26.6831
JAND | Jandowae | SW | JAND_11kV_BUS 1 | 11 | 0.99656 | 18.987 | 1.2991 | 8.2501 | 1.8241 | 1.0822 | 6.8727 | 1.408 | 8.9419 | 4.3648 | 5.4857 | 0.1142 | 2.5224 | 4.3616 | 5.4872
JAND | Jandowae | SW | JAND_11kV_TEF T01 | 11 | 0.54875 | 10.455 | 0.61654 | 3.9156 | 0.69632 | 0.53314 | 3.3859 | 0.64019 | 4.0658 | 4.6941 | 11.8342 | 0.44354 | 8.8709 | 4.691 | 11.8356
JAND | Jandowae | SW | JAND_11kV_TEF T02 | 11 | 0.99656 | 18.987 | 1.2991 | 8.2501 | 1.8241 | 1.0822 | 6.8727 | 1.408 | 8.9419 | 4.3648 | 5.4857 | 0.1142 | 2.5224 | 4.3616 | 5.4872
JARV | Jarvisfield | NQ | JARV_66kV_BUS 1 | 66 | 5.1966 | 594.0553 | 3.9531 | 150.6352 | 3.1748 | 4.65 | 177.189 | 4.9052 | 186.915 | 2.9868 | 7.4925 | 4.0946 | 15.2184 | 2.9041 | 7.4905
JARV | Jarvisfield | NQ | JARV_66kV_BUS 2 | 66 | 5.1966 | 594.0553 | 3.9531 | 150.6352 | 3.1748 | 4.65 | 177.189 | 4.9052 | 186.915 | 2.9868 | 7.4925 | 4.0946 | 15.2184 | 2.9041 | 7.4905
JARV | Jarvisfield (TF1) | NQ | JARV_11kV_BUS 1 | 11 | 6.7702 | 128.9906 | 7.2837 | 46.258 | 7.8752 | 6.9429 | 44.0931 | 7.1819 | 45.6111 | 0.15664 | 1.0199 | 0.07367 | 0.81178 | 0.15434 | 1.0198
JARV | Jarvisfield (TF2) | NQ | JARV_11kV_BUS 2 | 11 | 6.7702 | 128.9906 | 7.2837 | 46.258 | 7.8752 | 6.9429 | 44.0931 | 7.1819 | 45.6111 | 0.15664 | 1.0199 | 0.07367 | 0.81178 | 0.15434 | 1.0198
JUCR | Julia Creek | NQ | JUCR_66kV_BUS 1 | 66 | 0.27085 | 30.9627 | 0.30986 | 11.8071 | 0.3629 | 0.26434 | 10.0727 | 0.32443 | 12.3624 | 72.8239 | 136.5483 | 10.9238 | 99.0112 | 73.0817 | 138.738
JUCR | Julia Creek | NQ | JUCR_33kV_BUS 1 | 33 | 0.42786 | 24.4556 | 0.53713 | 10.2338 | 0.72716 | 0.4802 | 9.149 | 0.55422 | 10.5593 | 18.8275 | 45.2199 | 1.2816 | 19.3782 | 18.8919 | 45.7673
JUCR | Julia Creek | NQ | JUCR_33kV_BUS 2 | 33 | 0.42786 | 24.4556 | 0.53713 | 10.2338 | 0.72716 | 0.4802 | 9.149 | 0.55422 | 10.5593 | 18.8275 | 45.2199 | 1.2816 | 19.3782 | 18.8919 | 45.7673
JUPO | Jubilee Pocket | MK | JUPO_66kV_BUS 1 | 66 | 2.712 | 310.0255 | 2.0827 | 79.3616 | 1.6755 | 2.3937 | 91.2103 | 2.6014 | 99.1246 | 6.3031 | 14.1119 | 7.4912 | 28.8218 | 6.2593 | 14.0157
JUPO | Jubilee Pocket | MK | JUPO_66kV_BUS 2 | 66 | 2.712 | 310.0255 | 2.0827 | 79.3616 | 1.6755 | 2.3937 | 91.2103 | 2.6014 | 99.1246 | 6.3031 | 14.1119 | 7.4912 | 28.8218 | 6.2593 | 14.0157
JUPO | Jubilee Pocket | MK | JUPO_11kV_BUS 1 | 11 | 6.3064 | 120.1531 | 7.2136 | 45.8124 | 8.3842 | 6.6105 | 41.9825 | 7.1549 | 45.4394 | 0.19735 | 1.09 | 0.02227 | 0.69804 | 0.19614 | 1.0874
JUPO | Jubilee Pocket | MK | JUPO_11kV_BUS 2 | 11 | 6.3064 | 120.1531 | 7.2136 | 45.8124 | 8.3842 | 6.6105 | 41.9825 | 7.1549 | 45.4394 | 0.19735 | 1.09 | 0.02227 | 0.69804 | 0.19614 | 1.0874
JUPO | Jubilee Pocket | MK | JUPO_11kV_BUS 3 | 11 | 6.3064 | 120.1531 | 7.2136 | 45.8124 | 8.3842 | 6.6105 | 41.9825 | 7.1549 | 45.4394 | 0.19735 | 1.09 | 0.02227 | 0.69804 | 0.19614 | 1.0874
KAIM | Kaimkillenbun | SW | KAIM_33kV_BUS | 33 | 0.90305 | 51.6162 | 0.68313 | 13.0154 | 0.53393 | 0.72406 | 13.7951 | 0.91732 | 17.4774 | 18.9325 | 13.4268 | 22.0276 | 43.0419 | 18.9338 | 13.4269
KAIM | Kaimkillenbun | SW | KAIM_11kV_BUS | 11 | 0.7245 | 13.8036 | 0.77584 | 4.9272 | 0.83107 | 0.70521 | 4.4787 | 0.7971 | 5.0623 | 2.3857 | 9.3437 | 0.28207 | 7.8518 | 2.3858 | 9.3437
KALA | Kalamia | NQ | KALA_66kV_TEF T1 | 66 | 3.1212 | 356.8048 | 2.1548 | 82.1093 | 1.6316 | 2.7213 | 103.6969 | 2.9363 | 111.8872 | 6.6434 | 11.6708 | 10.4513 | 30.0393 | 6.4161 | 11.7006
KALA | Kalamia | NQ | KALA_11kV_BUS 1 | 11 | 7.6928 | 146.568 | 7.3076 | 46.4094 | 6.6617 | 7.4329 | 47.2053 | 7.662 | 48.6601 | 0.15187 | 0.89532 | 0.07245 | 1.0923 | 0.10364 | 0.86147
KAME | Kamerunga T053 | FN | KAME_22kV_BUS 1 | 22 | 13.5231 | 515.3003 | 9.6082 | 122.041 | 7.3357 | 12.8119 | 162.7332 | 11.8608 | 150.6525 | 0.08524 | 1.0297 | 0.56154 | 2.2584 | 0.07918 | 1.0136
KAME | Kamerunga T053 | FN | KAME_22kV_BUS 2 | 22 | 13.5231 | 515.3003 | 9.6082 | 122.041 | 7.3357 | 12.8119 | 162.7332 | 11.8608 | 150.6525 | 0.08524 | 1.0297 | 0.56154 | 2.2584 | 0.07918 | 1.0136
KEBE | Kewarra Beach | FN | KEBE_22kV_BUS 1 | 22 | 9.0512 | 344.8981 | 6.3207 | 80.2835 | 4.7763 | 8.3916 | 106.5875 | 8.1234 | 103.1807 | 0.48735 | 1.4647 | 1.3323 | 3.3226 | 0.46156 | 1.4396
KEBE | Kewarra Beach | FN | KEBE_22kV_BUS 2 | 22 | 9.0512 | 344.8981 | 6.3207 | 80.2835 | 4.7763 | 8.3916 | 106.5875 | 8.1234 | 103.1807 | 0.48735 | 1.4647 | 1.3323 | 3.3226 | 0.46156 | 1.4396
KECE | Kelsey Creek East (TF1) | MK | KECE_66kV_TEF T1 | 66 | 5.6169 | 642.099 | 7.1565 | 272.6996 | 9.6986 | 6.6625 | 253.8739 | 7.0846 | 269.961 | 2.1451 | 7.1475 | 0.40448 | 2.7227 | 2.1191 | 7.0693
KECE | Kelsey Creek East (TF1) | MK | KECE_11kV_BUS 1 | 11 | 5.5424 | 105.5961 | 5.8572 | 37.1984 | 6.1971 | 5.6401 | 35.8192 | 5.7896 | 36.7689 | 0.06665 | 1.2587 | 0.00706 | 1.0602 | 0.06593 | 1.2565
KECE | Kelsey Creek East (TF2) | MK | KECE_66kV_TEF T2 | 66 | 5.6245 | 642.9673 | 7.1772 | 273.4879 | 9.7521 | 6.6835 | 254.6757 | 7.1105 | 270.9475 | 2.1394 | 7.1387 | 0.3937 | 2.6939 | 2.1133 | 7.0605
KECE | Kelsey Creek East (TF2) | MK | KECE_11kV_BUS 2 | 11 | 9.42 | 179.4759 | 10.3817 | 65.9326 | 11.5186 | 9.8141 | 62.3282 | 10.167 | 64.5691 | 0.09207 | 0.73587 | 0.03264 | 0.53757 | 0.09134 | 0.7337
KECE | Kelsey Creek East (TF3) | MK | KECE_11kV_BUS 3 | 11 | 9.42 | 179.4759 | 10.3817 | 65.9326 | 11.5186 | 9.8141 | 62.3282 | 10.167 | 64.5691 | 0.09207 | 0.73587 | 0.03264 | 0.53757 | 0.09134 | 0.7337
KEMM | Kemmis T067 | MK | KEMM_66kV_BUS 1 | 66 | 5.2402 | 599.0344 | 6.681 | 254.5785 | 9.2449 | 6.7505 | 257.2276 | 6.1875 | 235.7743 | 0.91245 | 7.9467 | 0.90687 | 2.6955 | 0.9181 | 7.9795
KEMM | Kemmis T067 | MK | KEMM_66kV_BUS 2 | 66 | 5.2402 | 599.0344 | 6.681 | 254.5785 | 9.2449 | 6.7505 | 257.2276 | 6.1875 | 235.7743 | 0.91245 | 7.9467 | 0.90687 | 2.6955 | 0.9181 | 7.9795
KESP | Kearneys Spring T167 | SW | KESP_11kV_BUS 1 | 11 | 18.644 | 355.215 | 4.0751 | 25.8802 | 2.2857 | 16.1629 | 102.6481 | 16.2306 | 103.078 | 0.01156 | 0.37458 | 0 | 4.395 | 0.01158 | 0.37408
KESP | Kearneys Spring T167 | SW | KESP_11kV_BUS 2 | 11 | 18.644 | 355.215 | 4.0751 | 25.8802 | 2.2857 | 16.1629 | 102.6481 | 16.2306 | 103.078 | 0.01156 | 0.37458 | 0 | 4.395 | 0.01158 | 0.37408
KESP | Kearneys Spring T167 | SW | KESP_11kV_BUS 3 | 11 | 18.644 | 355.215 | 4.0751 | 25.8802 | 2.2857 | 16.1629 | 102.6481 | 16.2306 | 103.078 | 0.01156 | 0.37458 | 0 | 4.395 | 0.01158 | 0.37408
KESP | Kearneys Spring T167 (TF1) | SW | KESP_110kV_TEF T1 | 110 | 20.0733 | 3824.4834 | 20.4267 | 1297.2692 | 20.4933 | 20.3529 | 1292.5836 | 20.1461 | 1279.4523 | 0.29993 | 3.4678 | 0.3535 | 3.3311 | 0.30169 | 3.4181
KESP | Kearneys Spring T167 (TF2) | SW | KESP_110kV_TEF T2 | 110 | 20.0498 | 3820.0075 | 20.3789 | 1294.2316 | 20.4212 | 20.3174 | 1290.3295 | 20.1099 | 1277.1514 | 0.30063 | 3.4718 | 0.35582 | 3.3469 | 0.30239 | 3.4221
KIDS | Kidston T077 | FN | KIDS_132kV_BUS 1 | 132 | 0.87085 | 199.1034 | 1.1638 | 88.6969 | 1.866 | 1.1491 | 87.5736 | 1.243 | 94.7287 | 30.8855 | 91.1745 | 0.79 | 20.2173 | 31.5334 | 95.2458
KIDS | Kidston T077 | FN | KIDS_132kV_BUS 2 | 132 | 0.87085 | 199.1034 | 1.1638 | 88.6969 | 1.866 | 1.1491 | 87.5736 | 1.243 | 94.7287 | 30.8855 | 91.1745 | 0.79 | 20.2173 | 31.5334 | 95.2458
KIDS | Kidston T077 | FN | KIDS_6.6kV_BUS 1 | 6.6 | 10.0586 | 114.9857 | 0.02205 | 0.08404 | 0.01116 | 8.6102 | 32.8094 | 8.5993 | 32.7678 | 0.08767 | 0.40739 | 569.9998 | 0.17689 | 0.08929 | 0.41757
KIEA | Kilkivan East | WB | KIEA 132kV_BUS 1 | 132 | 6.2077 | 1419.2632 | 4.7987 | 365.7115 | 3.9002 | 5.5745 | 424.832 | 5.8671 | 447.1351 | 3.4587 | 13.0557 | 3.7972 | 25.2148 | 3.3413 | 13.0619
KIEA | Kilkivan East | WB | KIEA 132kV_BUS 2 | 132 | 6.2074 | 1419.2088 | 4.7985 | 365.6958 | 3.9001 | 5.5743 | 424.815 | 5.8669 | 447.1179 | 3.4588 | 13.0562 | 3.7974 | 25.216 | 3.3415 | 13.0624
KIEA | Kilkivan East | WB | KIEA 66kV_BUS 1 | 66 | 3.9166 | 447.7325 | 4.5411 | 173.0387 | 5.3986 | 4.2134 | 160.5513 | 4.453 | 169.6811 | 1.5763 | 10.5865 | 0.25355 | 6.308 | 1.5468 | 10.5931
KIEA | Kilkivan East | WB | KIEA 11kV_BUS 1 | 11 | 6.7157 | 127.9505 | 4.5767 | 29.0659 | 3.4707 | 6.0084 | 38.1588 | 6.1289 | 38.9239 | 0.04635 | 1.0393 | 0 | 2.5 | 0.04553 | 1.0395
KIEA | Kilkivan East | WB | KIEA 11kV_BUS 2 | 11 | 6.7157 | 127.9505 | 4.5767 | 29.0659 | 3.4707 | 6.0084 | 38.1588 | 6.1289 | 38.9239 | 0.04635 | 1.0393 | 0 | 2.5 | 0.04553 | 1.0395
KILL | Killarney | SW | KILL_33kV_BUS | 33 | 0.7778 | 44.4574 | 0.49171 | 9.3683 | 0.3521 | 0.6342 | 12.0832 | 0.75362 | 14.3583 | 18.4498 | 19.6415 | 25.1857 | 72.5177 | 18.395 | 19.6546
KILL | Killarney (TF1) | SW | KILL_11kV_BUS 1 | 11 | 1.3315 | 25.3688 | 1.6197 | 10.2863 | 2.0447 | 1.3911 | 8.8349 | 1.6776 | 10.6544 | 2.1795 | 4.7731 | 0.12954 | 2.5907 | 2.1734 | 4.7746
KILL | Killarney (TF2) | SW | KILL_11kV_BUS 2 | 11 | 1.3315 | 25.3688 | 1.6197 | 10.2863 | 2.0447 | 1.3911 | 8.8349 | 1.6776 | 10.6544 | 2.1795 | 4.7731 | 0.12954 | 2.5907 | 2.1734 | 4.7746
KILL | Killarney (TF3) | SW | KILL_11kV_BUS 3 | 11 | 1.3315 | 25.3688 | 1.6197 | 10.2863 | 2.0447 | 1.3911 | 8.8349 | 1.6776 | 10.6544 | 2.1795 | 4.7731 | 0.12954 | 2.5907 | 2.1734 | 4.7746
KING | Kingaroy | WB | KING_66kV_BUS 1 | 66 | 5.1535 | 589.1228 | 3.0211 | 115.119 | 2.1388 | 4.5287 | 172.5649 | 4.6418 | 176.8743 | 2.0149 | 7.8809 | 4.5703 | 24.9458 | 1.9714 | 7.9073
KING | Kingaroy | WB | KING_66kV_BUS 2 | 66 | 5.1535 | 589.1228 | 3.0211 | 115.119 | 2.1388 | 4.5287 | 172.5649 | 4.6418 | 176.8743 | 2.0149 | 7.8809 | 4.5703 | 24.9458 | 1.9714 | 7.9073
KING | Kingaroy | WB | KING_66kV_BUS 3 | 66 | 5.1535 | 589.1228 | 3.0211 | 115.119 | 2.1388 | 4.5287 | 172.5649 | 4.6418 | 176.8743 | 2.0149 | 7.8809 | 4.5703 | 24.9458 | 1.9714 | 7.9073
KING | Kingaroy | WB | KING_11kV_BUS A | 11 | 11.1564 | 212.5582 | 12.6579 | 80.3882 | 14.6373 | 11.8769 | 75.4285 | 12.3542 | 78.4598 | 0.07284 | 0.62201 | 0.01687 | 0.40309 | 0.07163 | 0.62274
KING | Kingaroy | WB | KING_11kV_BUS B | 11 | 11.1564 | 212.5582 | 12.6579 | 80.3882 | 14.6373 | 11.8769 | 75.4285 | 12.3542 | 78.4598 | 0.07284 | 0.62201 | 0.01687 | 0.40309 | 0.07163 | 0.62274
KIRK | Kirknie | NQ | KIRK_66kV_BUS 1 | 66 | 3.3342 | 381.1505 | 2.6077 | 99.3667 | 2.1296 | 2.9378 | 111.9454 | 3.2153 | 122.5202 | 7.5038 | 10.0863 | 10.3843 | 20.8492 | 7.4796 | 10.0741
KIRK | Kirknie | NQ | KIRK_11kV_BUS 1 | 11 | 5.1741 | 98.5807 | 5.6067 | 35.6073 | 6.1031 | 5.1965 | 33.0023 | 5.638 | 35.8061 | 0.26011 | 1.3249 | 0.05168 | 1.0447 | 0.25944 | 1.3245
KIRK | Kirknie | NQ | KIRK_11kV_BUS 2 | 11 | 5.1741 | 98.5807 | 5.6067 | 35.6073 | 6.1031 | 5.1965 | 33.0023 | 5.638 | 35.8061 | 0.26011 | 1.3249 | 0.05168 | 1.0447 | 0.25944 | 1.3245
KITO | Kilkivan Town | WB | KITO_66kV_BUS | 66 | 3.6914 | 421.9816 | 4.0974 | 156.1302 | 4.6032 | 3.8853 | 148.049 | 3.9922 | 152.1247 | 1.9702 | 11.1841 | 0.97771 | 7.9267 | 1.9407 | 11.1907
KITO | Kilkivan Town (TF1) | WB | KITO_11kV_BUS 1 | 11 | 0.76125 | 14.5037 | 0.7905 | 5.0203 | 0.8221 | 0.77697 | 4.9344 | 0.77684 | 4.9336 | 1.64 | 9.0304 | 1.4595 | 8.0275 | 1.6391 | 9.0306
KITO | Kilkivan Town (TF2) | WB | KITO_11kV_BUS 2 | 11 | 0.75128 | 14.3137 | 0.7833 | 4.9746 | 0.81819 | 0.76914 | 4.8847 | 0.76796 | 4.8772 | 1.64 | 9.1541 | 1.4595 | 8.0275 | 1.6391 | 9.1543
KOCR | Kogan Creek | SW | KOCR_33kV_TEF T1 | 33 | 1.6903 | 96.6133 | 1.0848 | 20.6683 | 0.79229 | 1.43 | 27.2457 | 1.5985 | 30.4558 | 6.0998 | 10.7951 | 8.3113 | 32.6147 | 6.0717 | 10.8085
KOCR | Kogan Creek | SW | KOCR_11kV_TEF T1 | 11 | 1.9022 | 36.2411 | 2.1585 | 13.7083 | 2.489 | 1.9681 | 12.4991 | 2.1565 | 13.6958 | 0.79705 | 3.5852 | 0.11929 | 2.3857 | 0.79393 | 3.5867
KOGA | Kogan Regulator (Regulated) | SW | KOGA_33kV_BUS R1 Downstream | 33 | 1.1042 | 63.1149 | 0.91985 | 17.5256 | 0.78412 | 0.97429 | 18.5627 | 1.0895 | 20.7585 | 8.5205 | 16.9619 | 7.8294 | 29.7498 | 8.5218 | 16.962
KOGA | Kogan Regulator (Unregulated) | SW | KOGA_33kV_BUS R1 Upstream | 33 | 1.1839 | 67.6678 | 0.96866 | 18.4554 | 0.81443 | 1.0342 | 19.7046 | 1.168 | 22.2542 | 8.4503 | 15.5577 | 7.9265 | 28.8633 | 8.4516 | 15.5578
KOUM | Koumala | MK | KOUM_33kV_TEF T1 | 33 | 1.2438 | 71.0906 | 0.75202 | 14.3278 | 0.53364 | 1.0241 | 19.5126 | 1.1834 | 22.5474 | 10.6212 | 13.0816 | 15.9447 | 48.5841 | 10.6655 | 13.194
KOUM | Koumala (1 Regulator) | MK | KOUM_11kV_TEF R1 | 11 | 1.8398 | 35.0539 | 2.1747 | 13.811 | 2.6536 | 1.9205 | 12.197 | 2.2137 | 14.0591 | 1.3862 | 3.535 | 0.20603 | 2.0815 | 1.3911 | 3.5475
KOUM | Koumala (2 Regulator) | MK | KOUM_11kV_TEF R2 | 11 | 1.8398 | 35.0539 | 2.1747 | 13.811 | 2.6536 | 1.9205 | 12.197 | 2.2137 | 14.0591 | 1.3862 | 3.535 | 0.20603 | 2.0815 | 1.3911 | 3.5475
KUNW | Kunwarara | CA | KUNW_66kV_TEF T1 | 66 | 1.2294 | 140.541 | 0.76655 | 29.2095 | 0.55301 | 1.0399 | 39.6242 | 1.1565 | 44.0683 | 17.2166 | 29.4283 | 26.0509 | 93.6045 | 17.2182 | 29.4545
KUNW | Kunwarara | CA | KUNW_11kV_TEF T1 | 11 | 3.7106 | 70.6963 | 4.4202 | 28.0721 | 5.4409 | 3.9337 | 24.9822 | 4.4695 | 28.3852 | 0.49165 | 1.8174 | 0.01341 | 0.99995 | 0.4917 | 1.8181
LACR | Lakes Creek | CA | LACR_66kV_BUS VERT_1 | 66 | 7.4434 | 850.8934 | 6.1191 | 233.1679 | 5.2103 | 6.8896 | 262.5298 | 6.9988 | 266.6883 | 1.5767 | 5.4061 | 2.3173 | 8.9752 | 1.5736 | 5.4283
LACR | Lakes Creek | CA | LACR_66kV_BUS VERT_2 | 66 | 7.4434 | 850.8934 | 6.1191 | 233.1679 | 5.2103 | 6.8896 | 262.5298 | 6.9988 | 266.6883 | 1.5767 | 5.4061 | 2.3173 | 8.9752 | 1.5736 | 5.4283
LACR | Lakes Creek | CA | LACR_66kV_BUS VERT_3 | 66 | 7.4434 | 850.8934 | 6.1191 | 233.1679 | 5.2103 | 6.8896 | 262.5298 | 6.9988 | 266.6883 | 1.5767 | 5.4061 | 2.3173 | 8.9752 | 1.5736 | 5.4283
LACR | Lakes Creek | CA | LACR_66kV_BUS VERT_4 | 66 | 7.4434 | 850.8934 | 6.1191 | 233.1679 | 5.2103 | 6.8896 | 262.5298 | 6.9988 | 266.6883 | 1.5767 | 5.4061 | 2.3173 | 8.9752 | 1.5736 | 5.4283
LACR | Lakes Creek | CA | LACR_11kV_BUS LH | 11 | 16.6451 | 317.1325 | 18.8973 | 120.0143 | 21.8772 | 17.6867 | 112.3256 | 18.4865 | 117.4049 | 0.06097 | 0.41525 | 0.01717 | 0.26918 | 0.06088 | 0.41587
LACR | Lakes Creek | CA | LACR_11kV_BUS RH | 11 | 16.6451 | 317.1325 | 18.8973 | 120.0143 | 21.8772 | 17.6867 | 112.3256 | 18.4865 | 117.4049 | 0.06097 | 0.41525 | 0.01717 | 0.26918 | 0.06088 | 0.41587
LAKE | Lakeland | FN | LAKE_132kV_BUS 1 | 132 | 0.92592 | 211.6949 | 0.88895 | 67.7474 | 0.83644 | 0.87773 | 66.892 | 0.94056 | 71.6807 | 23.0698 | 87.5495 | 12.8336 | 103.4404 | 21.4277 | 86.0504
LAKE | Lakeland | FN | LAKE_132kV_BUS 2 | 132 | 0.92592 | 211.6949 | 0.88895 | 67.7474 | 0.83644 | 0.87773 | 66.892 | 0.94056 | 71.6807 | 23.0698 | 87.5495 | 12.8336 | 103.4404 | 21.4277 | 86.0504
LAKE | Lakeland | FN | LAKE_22kV_BUS 1 | 22 | 1.7209 | 65.5769 | 2.144 | 27.232 | 2.8297 | 2.0071 | 25.4935 | 2.1033 | 26.716 | 0.87254 | 8.0717 | 0 | 3.3523 | 0.83641 | 8.0517
LAKE | Lakeland | FN | LAKE_22kV_BUS 2 | 22 | 1.7209 | 65.5769 | 2.144 | 27.232 | 2.8297 | 2.0071 | 25.4935 | 2.1033 | 26.716 | 0.87254 | 8.0717 | 0 | 3.3523 | 0.83641 | 8.0517
LAKE | Lakeland (TF1) | FN | LAKE_66kV_BUS 1 | 66 | 1.349 | 154.2065 | 1.2406 | 47.2715 | 1.1117 | 1.2783 | 48.7077 | 1.3352 | 50.8788 | 5.8171 | 30.5233 | 3.8331 | 40.1761 | 5.1629 | 29.5759
LAKE | Lakeland (TF2) | FN | LAKE_66kV_BUS 2 | 66 | 1.349 | 154.2065 | 1.2406 | 47.2715 | 1.1117 | 1.2783 | 48.7077 | 1.3352 | 50.8788 | 5.8171 | 30.5233 | 3.8331 | 40.1761 | 5.1629 | 29.5759
LANN | Lannercost | NQ | LANN_66kV_BUS 1 | 66 | 1.8856 | 215.5533 | 1.469 | 55.9771 | 1.2079 | 1.6606 | 63.2761 | 1.808 | 68.8941 | 11.1022 | 19.2584 | 14.0708 | 38.777 | 11.0265 | 19.5331
LANN | Lannercost | NQ | LANN_66kV_BUS 2 | 66 | 1.8856 | 215.5533 | 1.469 | 55.9771 | 1.2079 | 1.6606 | 63.2761 | 1.808 | 68.8941 | 11.1022 | 19.2584 | 14.0708 | 38.777 | 11.0265 | 19.5331
LANN | Lannercost | NQ | LANN_11kV_BUS | 11 | 3.5182 | 67.0301 | 3.8953 | 24.7386 | 4.3728 | 3.6059 | 22.9009 | 3.8842 | 24.6678 | 0.4122 | 1.9424 | 0.1038 | 1.4075 | 0.41009 | 1.9501
LAQU | Laguna Quays (TF1) | MK | LAQU_11kV_TEF T1 | 11 | 3.2755 | 62.406 | 3.6755 | 23.3424 | 4.1644 | 3.3098 | 21.0203 | 3.7174 | 23.6088 | 0.54808 | 2.0612 | 0.07304 | 1.4609 | 0.54735 | 2.059
LAQU | Laguna Quays (TF2) | MK | LAQU_66kV_TEF T1 | 66 | 1.5209 | 173.8651 | 1.1271 | 42.9492 | 0.88314 | 1.283 | 48.8891 | 1.4905 | 56.794 | 17.1014 | 21.6117 | 20.4964 | 54.105 | 17.0753 | 21.5334
LAQU | Laguna Quays (TF2) | MK | LAQU_66kV_TEF T2 | 66 | 1.5216 | 173.9414 | 1.1277 | 42.9711 | 0.88363 | 1.2836 | 48.9115 | 1.4911 | 56.8193 | 17.0932 | 21.6027 | 20.4852 | 54.0731 | 17.0672 | 21.5245
LAQU | Laguna Quays (TF2) | MK | LAQU_11kV_TEF T2 | 11 | 3.2759 | 62.415 | 3.6759 | 23.3449 | 4.1646 | 3.3103 | 21.0231 | 3.7178 | 23.6111 | 0.54781 | 2.0609 | 0.073 | 1.4609 | 0.54709 | 2.0588
LARO | LARO HV | CA | LARO_66kV_TEF T1 | 66 | 8.079 | 923.5587 | 7.6722 | 292.3505 | 7.3377 | 8.0304 | 305.9975 | 7.7448 | 295.1154 | 0.46453 | 5.1675 | 0.90601 | 5.9249 | 0.46172 | 5.1951
LARO | LARO LV | CA | LARO_11kV_BUS | 11 | 6.0091 | 114.4877 | 6.2665 | 39.7976 | 6.5515 | 6.1412 | 39.0019 | 6.1552 | 39.091 | 0.07067 | 1.1604 | 0.05776 | 1.0169 | 0.07059 | 1.1612
LEIC | Leichhardt | CA | LEIC_66kV_BUS TRANSFER | 66 | 3.1948 | 365.2119 | 2.3413 | 89.2168 | 1.842 | 2.8346 | 108.0108 | 2.9991 | 114.2824 | 5.5999 | 11.8651 | 8.85 | 26.1237 | 5.6161 | 11.8293
LILY | Lilyvale | CA | LILY_66kV_BUS NORTH | 66 | 14.7623 | 1687.5615 | 17.9867 | 685.3862 | 22.9822 | 17.0369 | 649.1932 | 17.3461 | 660.9733 | 0.31437 | 2.8219 | 0.09152 | 1.3128 | 0.30346 | 2.8203
LILY | Lilyvale | CA | LILY_66kV_BUS SOUTH | 66 | 14.7623 | 1687.5615 | 17.9867 | 685.3862 | 22.9822 | 17.0369 | 649.1932 | 17.3461 | 660.9733 | 0.31437 | 2.8219 | 0.09152 | 1.3128 | 0.30346 | 2.8203
LITT | Littlemore | CA | LITT_66kV_BUS TRANSFER | 66 | 0.93579 | 106.9752 | 0.5768 | 21.979 | 0.41289 | 0.78412 | 29.8791 | 0.88509 | 33.7265 | 25.5555 | 36.7873 | 39.7632 | 124.569 | 25.5555 | 36.8151
LITT | Littlemore | CA | LITT_66kV_TEF T2 | 66 | 0.93579 | 106.9752 | 0.5768 | 21.979 | 0.41289 | 0.78412 | 29.8791 | 0.88509 | 33.7265 | 25.5555 | 36.7873 | 39.7632 | 124.569 | 25.5555 | 36.8151
LITT | Littlemore | CA | LITT_11kV_TEF T1 | 11 | 1.5531 | 29.5897 | 1.7001 | 10.7967 | 1.8753 | 1.582 | 10.0469 | 1.6951 | 10.7654 | 1.2022 | 4.3347 | 0.49233 | 3.3128 | 1.2022 | 4.3354
LITT | Littlemore | CA | LITT_11kV_TEF T2 | 11 | 1.5508 | 29.5457 | 1.6973 | 10.7794 | 1.872 | 1.5797 | 10.0322 | 1.6923 | 10.7475 | 1.2059 | 4.3406 | 0.49597 | 3.3187 | 1.2059 | 4.3414
LOCR | Louisa Creek | MK | LOCR_33kV_BUS 1 | 33 | 9.3481 | 534.3127 | 10.0699 | 191.8577 | 10.9935 | 9.6179 | 183.2454 | 9.9218 | 189.035 | 0.28173 | 2.2242 | 0.12233 | 1.7415 | 0.28192 | 2.2402
LOCR | Louisa Creek | MK | LOCR_33kV_BUS 2 | 33 | 9.3481 | 534.3127 | 10.0699 | 191.8577 | 10.9935 | 9.6179 | 183.2454 | 9.9218 | 189.035 | 0.28173 | 2.2242 | 0.12233 | 1.7415 | 0.28192 | 2.2402
LOCR | Louisa Creek | MK | LOCR_11kV_BUS 1 | 11 | 3.1283 | 59.6019 | 3.2481 | 20.6282 | 3.3801 | 3.1752 | 20.1653 | 3.2097 | 20.3845 | 0.1537 | 2.2279 | 0.09923 | 1.982 | 0.15372 | 2.2296
LOCR | Louisa Creek (TF1) | MK | LOCR_132kV_TEF T1 | 132 | 3.8265 | 874.8498 | 4.3459 | 331.2006 | 5.0947 | 4.1179 | 313.8265 | 4.2243 | 321.9351 | 4.3948 | 21.463 | 2.0951 | 13.6539 | 4.3979 | 21.7195
LOCR | Louisa Creek (TF2) | MK | LOCR_132kV_TEF T2 | 132 | 3.8265 | 874.8498 | 4.3459 | 331.2006 | 5.0947 | 4.1179 | 313.8265 | 4.2243 | 321.9351 | 4.3948 | 21.463 | 2.0951 | 13.6539 | 4.3979 | 21.7195
LONG | Longreach | CA | LONG_66kV_BUS 1 | 66 | 0.64456 | 73.6833 | 0.39842 | 15.1819 | 0.29437 | 0.57536 | 21.9241 | 0.56602 | 21.5683 | 17.7347 | 62.5648 | 53.2846 | 175.7982 | 16.9133 | 64.7539
LONG | Longreach | CA | LONG_22kV_BUS LH | 22 | 1.5276 | 58.2094 | 2.0506 | 26.0467 | 3.2309 | 2.0425 | 25.9426 | 2.1274 | 27.0213 | 2.1207 | 8.8971 | 0.15016 | 1.9454 | 2.0294 | 9.1403
LONG | Longreach | CA | LONG_22kV_BUS RH | 22 | 1.5276 | 58.2094 | 2.0506 | 26.0467 | 3.2309 | 2.0425 | 25.9426 | 2.1274 | 27.0213 | 2.1207 | 8.8971 | 0.15016 | 1.9454 | 2.0294 | 9.1403
LUCI | Lucinda | NQ | LUCI_66kV_TEF T1 | 66 | 1.7876 | 204.3465 | 1.293 | 49.2694 | 1.0428 | 1.5542 | 59.2237 | 1.6637 | 63.395 | 11.4208 | 20.4791 | 18.0535 | 46.2311 | 11.9279 | 21.29
LUCI | Lucinda | NQ | LUCI_11kV_BUS | 11 | 2.1871 | 41.6701 | 2.3295 | 14.7945 | 2.5104 | 2.2107 | 14.0399 | 2.3248 | 14.7645 | 0.51866 | 3.1517 | 0.20141 | 2.5829 | 0.53274 | 3.1743
LYLA | Lyndley Lane | SW | LYLA_33kV_TEF T1 | 33 | 1.1338 | 64.8034 | 0.68586 | 13.0674 | 0.48677 | 0.94956 | 18.0916 | 1.07 | 20.3859 | 10.0315 | 15.5288 | 15.0782 | 53.6205 | 10.0327 | 15.5289
LYLA | Lyndley Lane | SW | LYLA_33kV_TEF T2 | 33 | 1.1338 | 64.8034 | 0.68586 | 13.0674 | 0.48677 | 0.94956 | 18.0916 | 1.07 | 20.3859 | 10.0315 | 15.5288 | 15.0782 | 53.6205 | 10.0327 | 15.5289
LYLA | Lyndley Lane | SW | LYLA_22kV_TEF T1 | 22 | 0.36797 | 14.0214 | 0.39378 | 5.0016 | 0.42297 | 0.37049 | 4.7058 | 0.39407 | 5.0054 | 5.9883 | 37.4994 | 1.5299 | 30.5977 | 5.9889 | 37.4994
LYLA | Lyndley Lane | SW | LYLA_22kV_TEF T2 | 22 | 0.14433 | 5.4999 | 0.14803 | 1.8803 | 0.1519 | 0.14446 | 1.8349 | 0.14804 | 1.8804 | 8.9333 | 96.3996 | 4.4749 | 89.4979 | 8.9339 | 96.3996
MACI | Maryborough City | WB | MACI_66kV_BUS MACI | 66 | 6.1562 | 703.7485 | 5.8316 | 222.2137 | 5.5857 | 5.9831 | 227.9868 | 6.0254 | 229.5997 | 1.5173 | 6.6381 | 1.6088 | 7.7214 | 1.4836 | 6.707
MACI | Maryborough City | WB | MACI_66kV_BUS MACI_TUAN | 66 | 6.1562 | 703.7485 | 5.8316 | 222.2137 | 5.5857 | 5.9831 | 227.9868 | 6.0254 | 229.5997 | 1.5173 | 6.6381 | 1.6088 | 7.7214 | 1.4836 | 6.707
MACI | Maryborough City | WB | MACI_66kV_BUS WALKERS | 66 | 6.1562 | 703.7485 | 5.8316 | 222.2137 | 5.5857 | 5.9831 | 227.9868 | 6.0254 | 229.5997 | 1.5173 | 6.6381 | 1.6088 | 7.7214 | 1.4836 | 6.707
MACI | Maryborough City | WB | MACI_11kV_BUS 1 | 11 | 10.9973 | 209.5271 | 12.185 | 77.3853 | 13.7007 | 11.5636 | 73.4386 | 11.885 | 75.4796 | 0.0654 | 0.63192 | 0.02325 | 0.44753 | 0.06446 | 0.63384
MACI | Maryborough City | WB | MACI_11kV_BUS 2 | 11 | 10.9973 | 209.5271 | 12.185 | 77.3853 | 13.7007 | 11.5636 | 73.4386 | 11.885 | 75.4796 | 0.0654 | 0.63192 | 0.02325 | 0.44753 | 0.06446 | 0.63384
MACK | Mackay T038 | MK | MACK_33kV_BUS A | 33 | 13.7364 | 785.1426 | 18.6866 | 356.027 | 29.5712 | 18.9844 | 361.7021 | 18.9535 | 361.1134 | 0.20615 | 1.5117 | 0.04202 | 0.29845 | 0.20536 | 1.5238
MACK | Mackay T038 | MK | MACK_33kV_BUS B | 33 | 13.7364 | 785.1426 | 18.6866 | 356.027 | 29.5712 | 18.9844 | 361.7021 | 18.9535 | 361.1134 | 0.20615 | 1.5117 | 0.04202 | 0.29845 | 0.20536 | 1.5238
MACK | Mackay T038 | MK | MACK_33kV_BUS C | 33 | 13.7364 | 785.1426 | 18.6866 | 356.027 | 29.5712 | 18.9844 | 361.7021 | 18.9535 | 361.1134 | 0.20615 | 1.5117 | 0.04202 | 0.29845 | 0.20536 | 1.5238
MACN | Macknade | NQ | MACN_66kV_TEF T1 | 66 | 2.5493 | 291.4291 | 1.9644 | 74.8521 | 1.6745 | 2.2908 | 87.2918 | 2.339 | 89.1285 | 6.0271 | 15.2973 | 10.2541 | 28.3749 | 6.5643 | 16.1268
MACN | Macknade | NQ | MACN_11kV_BUS 1 | 11 | 8.6082 | 164.0076 | 6.7691 | 42.9895 | 7.2446 | 7.5029 | 47.65 | 7.6698 | 48.71 | 0.09969 | 0.8054 | 0.1188 | 1.1879 | 0.14998 | 1.0808
MACN | Macknade | NQ | MACN_11kV_BUS 2 | 11 | 8.6082 | 164.0076 | 6.7691 | 42.9895 | 7.2446 | 7.5029 | 47.65 | 7.6698 | 48.71 | 0.09969 | 0.8054 | 0.1188 | 1.1879 | 0.14998 | 1.0808
MACT | Mackay City | MK | MACT_33kV_BUS 1 | 33 | 12.8643 | 735.2965 | 17.178 | 327.2859 | 26.0795 | 17.7451 | 338.0889 | 16.5172 | 314.6951 | 0.2946 | 1.6023 | 0.15613 | 0.36698 | 0.29381 | 1.6143
MACT | Mackay City | MK | MACT_33kV_BUS 2 | 33 | 12.8643 | 735.2965 | 17.178 | 327.2859 | 26.0795 | 17.7451 | 338.0889 | 16.5172 | 314.6951 | 0.2946 | 1.6023 | 0.15613 | 0.36698 | 0.29381 | 1.6143
MACT | Mackay City | MK | MACT_11kV_BUS 1 | 11 | 13.2716 | 252.8576 | 14.8822 | 94.5149 | 16.9824 | 14.0846 | 89.4489 | 14.4793 | 91.9557 | 0.0452 | 0.52444 | 0.01246 | 0.35428 | 0.04511 | 0.52578
MACT | Mackay City | MK | MACT_11kV_BUS 2 | 11 | 13.2716 | 252.8576 | 14.8822 | 94.5149 | 16.9824 | 14.0846 | 89.4489 | 14.4793 | 91.9557 | 0.0452 | 0.52444 | 0.01246 | 0.35428 | 0.04511 | 0.52578
MAFU | Max Fulton (TF1) | NQ | MAFU_66kV_TEF T1 | 66 | 11.2521 | 1286.2904 | 10.143 | 386.5016 | 9.2211 | 10.603 | 404.0276 | 10.9611 | 417.6736 | 1.0082 | 3.5861 | 1.0327 | 4.8474 | 0.98909 | 3.5879
MAFU | Max Fulton (TF1) | NQ | MAFU_11kV_BUS 1 | 11 | 9.6112 | 183.1183 | 10.079 | 64.0101 | 10.5936 | 9.7728 | 62.0653 | 9.9583 | 63.2437 | 0.05067 | 0.72509 | 0.02266 | 0.62547 | 0.05014 | 0.72514
MAFU | Max Fulton (TF2) | NQ | MAFU_66kV_TEF T2 | 66 | 11.5373 | 1318.8846 | 10.5698 | 402.765 | 9.7388 | 10.9134 | 415.8565 | 11.3193 | 431.3232 | 0.96337 | 3.503 | 0.91581 | 4.5491 | 0.94424 | 3.5048
MAFU | Max Fulton (TF2) | NQ | MAFU_11kV_BUS 2 | 11 | 9.604 | 182.9806 | 10.0583 | 63.8786 | 10.5567 | 9.7623 | 61.999 | 9.9385 | 63.118 | 0.04941 | 0.72572 | 0.02267 | 0.62864 | 0.04888 | 0.72577
MAKA | Mary Kathleen | NQ - MI | MAKA_66kV_TEF T1 | 66 | 0.36981 | 42.2753 | 0.31701 | 12.0797 | 0.27762 | 0.34467 | 13.1339 | 0.35313 | 13.456 | 34.177 | 108.0671 | 43.812 | 164.2006 | 34.0783 | 108.2383
MAKA | Mary Kathleen | NQ - MI | MAKA_11kV_TEF T1 | 11 | 0.27606 | 5.2597 | 0.28781 | 1.8278 | 0.30063 | 0.28046 | 1.7812 | 0.28431 | 1.8056 | 3.4613 | 25.0677 | 2.512 | 22.0658 | 3.4586 | 25.0724
MALC | Malchi | CA | MALC_66kV_TEF T1 | 66 | 3.4645 | 396.0427 | 2.4691 | 94.0852 | 1.9189 | 3.0741 | 117.1401 | 3.2195 | 122.6791 | 4.5225 | 11.2219 | 7.5208 | 25.6896 | 4.5239 | 11.2477
MALC | Malchi | CA | MALC_66kV_TEF T2 | 66 | 3.4645 | 396.0427 | 2.4691 | 94.0852 | 1.9189 | 3.0741 | 117.1401 | 3.2195 | 122.6791 | 4.5225 | 11.2219 | 7.5208 | 25.6896 | 4.5239 | 11.2477
MALC | Malchi | CA | MALC_11kV_BUS 1 | 11 | 8.7001 | 165.7589 | 10.0741 | 63.9795 | 11.9586 | 9.278 | 58.9234 | 9.9451 | 63.1601 | 0.15647 | 0.78759 | 0.03085 | 0.47588 | 0.15651 | 0.78831
MALC | Malchi | CA | MALC_11kV_BUS 2 | 11 | 8.7001 | 165.7589 | 10.0741 | 63.9795 | 11.9586 | 9.278 | 58.9234 | 9.9451 | 63.1601 | 0.15647 | 0.78759 | 0.03085 | 0.47588 | 0.15651 | 0.78831
MARE | Mareeba (TF1) | FN | MARE_66kV_BUS 1 | 66 | 3.2458 | 371.0422 | 2.6936 | 102.6392 | 2.3139 | 3.0189 | 115.0342 | 3.0485 | 116.1627 | 4.0816 | 12.2519 | 6.05 | 19.8799 | 4.0081 | 12.3593
MARE | Mareeba (TF1) | FN | MARE_22kV_BUS 1 | 22 | 5.9414 | 226.3971 | 7.0595 | 89.6684 | 8.7389 | 6.5864 | 83.6581 | 6.9019 | 87.6665 | 0.32718 | 2.3287 | 0.05212 | 1.2268 | 0.31902 | 2.3407
MARE | Mareeba (TF2) | FN | MARE_66kV_BUS 2 | 66 | 3.783 | 432.4514 | 3.4535 | 131.5941 | 3.199 | 3.6184 | 137.8801 | 3.657 | 139.3496 | 2.8778 | 10.6999 | 3.3017 | 13.7792 | 2.8044 | 10.8073
MARE | Mareeba (TF2) | FN | MARE_22kV_BUS 2 | 22 | 5.9414 | 226.3971 | 7.0595 | 89.6684 | 8.7389 | 6.5864 | 83.6581 | 6.9019 | 87.6665 | 0.32718 | 2.3287 | 0.05212 | 1.2268 | 0.31902 | 2.3407
MARE | Mareeba (TF3) | FN | MARE_66kV_BUS 3 | 66 | 3.783 | 432.4514 | 3.4535 | 131.5941 | 3.199 | 3.6184 | 137.8801 | 3.657 | 139.3496 | 2.8778 | 10.6999 | 3.3017 | 13.7792 | 2.8044 | 10.8073
MARE | Mareeba (TF3) | FN | MARE_22kV_BUS 3 | 22 | 5.9414 | 226.3971 | 7.0595 | 89.6684 | 8.7389 | 6.5864 | 83.6581 | 6.9019 | 87.6665 | 0.32718 | 2.3287 | 0.05212 | 1.2268 | 0.31902 | 2.3407
MARY | Maryborough T059 | WB | MARY_132kV_BUS 1 | 132 | 5.4264 | 1240.6521 | 5.9337 | 452.2055 | 6.6169 | 5.5066 | 419.6563 | 5.9537 | 453.7337 | 3.3949 | 15.0724 | 0.84622 | 11.362 | 3.317 | 15.2743
MARY | Maryborough T059 | WB | MARY_132kV_BUS 2 | 132 | 5.4264 | 1240.6521 | 5.9337 | 452.2055 | 6.6169 | 5.5066 | 419.6563 | 5.9537 | 453.7337 | 3.3949 | 15.0724 | 0.84622 | 11.362 | 3.317 | 15.2743
MARY | Maryborough T059 | WB | MARY_132kV_BUS 3 | 132 | 5.4264 | 1240.6521 | 5.9337 | 452.2055 | 6.6169 | 5.5066 | 419.6563 | 5.9537 | 453.7337 | 3.3949 | 15.0724 | 0.84622 | 11.362 | 3.317 | 15.2743
MARY | Maryborough T059 | WB | MARY_66kV_BUS 1 | 66 | 8.1053 | 926.5579 | 9.9703 | 379.9198 | 13.1411 | 9.3488 | 356.2364 | 9.8476 | 375.2422 | 0.93616 | 5.0864 | 0.13286 | 2.2164 | 0.90247 | 5.1554
MARY | Maryborough T059 | WB | MARY_66kV_BUS 2 | 66 | 8.1053 | 926.5579 | 9.9703 | 379.9198 | 13.1411 | 9.3488 | 356.2364 | 9.8476 | 375.2422 | 0.93616 | 5.0864 | 0.13286 | 2.2164 | 0.90247 | 5.1554
MARY | Maryborough T059 | WB | MARY_66kV_BUS 3 | 66 | 8.1053 | 926.5579 | 9.9703 | 379.9198 | 13.1411 | 9.3488 | 356.2364 | 9.8476 | 375.2422 | 0.93616 | 5.0864 | 0.13286 | 2.2164 | 0.90247 | 5.1554
MASO | Marian South | MK | MASO_66kV_TEF T1 | 66 | 4.2103 | 481.3007 | 3.0781 | 117.2894 | 2.449 | 3.7823 | 144.1264 | 3.875 | 147.6593 | 3.3367 | 9.3798 | 5.9185 | 19.9717 | 3.3403 | 9.5114
MASO | Marian South | MK | MASO_11kV_BUS 1 | 11 | 10.732 | 204.472 | 8.2158 | 52.1775 | 7.1288 | 9.4817 | 60.2172 | 9.8596 | 62.6166 | 0.10884 | 0.64178 | 0.05967 | 1.1931 | 0.08758 | 0.70318
MCCR | McKinley Creek | MK | MCCR_66kV_TEF T1 | 66 | 3.0062 | 343.6564 | 2.2178 | 84.5097 | 1.7615 | 2.7499 | 104.7862 | 2.7404 | 104.4243 | 5.1428 | 12.96 | 10.7209 | 26.6956 | 5.1211 | 13.0174
MCCR | McKinley Creek | MK | MCCR_11kV_BUS 3 | 11 | 3.1237 | 59.515 | 3.3061 | 20.9968 | 3.5126 | 3.1726 | 20.1486 | 3.2763 | 20.8073 | 0.22619 | 2.225 | 0.08334 | 1.865 | 0.22559 | 2.2266
MCCR | McKinley Creek (TF1) | MK | MCCR_11kV_BUS 1 | 11 | 3.102 | 59.1004 | 3.2817 | 20.8418 | 3.485 | 3.1499 | 20.0048 | 3.2523 | 20.6551 | 0.22615 | 2.2407 | 0.0833 | 1.8807 | 0.22555 | 2.2423
MCCR | McKinley Creek (TF2) | MK | MCCR_11kV_BUS 2 | 11 | 3.1237 | 59.515 | 3.3061 | 20.9968 | 3.5126 | 3.1726 | 20.1486 | 3.2763 | 20.8073 | 0.22619 | 2.225 | 0.08334 | 1.865 | 0.22559 | 2.2266
MEAD | Meadowvale | WB | MEAD_66kV_BUS 1 | 66 | 3.0123 | 344.3562 | 2.128 | 81.0865 | 1.6501 | 2.662 | 101.4346 | 2.797 | 106.5817 | 5.1099 | 12.9436 | 8.232 | 30.167 | 5.0816 | 13.0412
MEAD | Meadowvale | WB | MEAD_11kV_BUS 1 | 11 | 5.1415 | 97.9597 | 5.6582 | 35.9344 | 6.2985 | 5.3124 | 33.7385 | 5.5878 | 35.4871 | 0.19087 | 1.3454 | 0.04893 | 0.98581 | 0.19009 | 1.3481
MEAD | Meadowvale | WB | MEAD_11kV_BUS 2 | 11 | 5.1415 | 97.9597 | 5.6582 | 35.9344 | 6.2985 | 5.3124 | 33.7385 | 5.5878 | 35.4871 | 0.19087 | 1.3454 | 0.04893 | 0.98581 | 0.19009 | 1.3481
MEAN | Meandarra | SW | MEAN_33kV_BUS | 33 | 0.39712 | 22.6982 | 0.22839 | 4.3515 | 0.15875 | 0.33241 | 6.3333 | 0.37234 | 7.094 | 28.3374 | 44.524 | 45.5089 | 166.5727 | 28.3368 | 44.5309
MEAN | Meandarra | SW | MEAN_22kV_BUS | 22 | 0.26902 | 10.2511 | 0.31394 | 3.9875 | 0.37527 | 0.28093 | 3.5683 | 0.3163 | 4.0175 | 14.1043 | 49.9858 | 1.5099 | 30.1973 | 14.104 | 49.9888
MELR | Melrose | WB | MELR_66kV_BUS | 66 | 1.461 | 167.0184 | 0.80982 | 30.8582 | 0.55874 | 1.2566 | 47.8827 | 1.3332 | 50.8022 | 10.3584 | 26.7575 | 20.1481 | 96.2748 | 10.3149 | 26.7838
MELR | Melrose | WB | MELR_11kV_BUS 1 | 11 | 2.9868 | 56.907 | 3.3626 | 21.3553 | 3.8456 | 3.1501 | 20.0055 | 3.2937 | 20.918 | 0.48396 | 2.2886 | 0.19623 | 1.5453 | 0.48275 | 2.2893
MELR | Melrose | WB | MELR_11kV_BUS 2 | 11 | 2.9868 | 56.907 | 3.3626 | 21.3553 | 3.8456 | 3.1501 | 20.0055 | 3.2937 | 20.918 | 0.48396 | 2.2886 | 0.19623 | 1.5453 | 0.48275 | 2.2893
MEMO | Memooloo T236 | CA | MEMO_132kV_BUS 1 | 132 | 1.9355 | 442.512 | 1.7581 | 133.9848 | 1.609 | 1.8082 | 137.8071 | 1.9087 | 145.461 | 9.6834 | 42.2168 | 7.3412 | 56.0937 | 9.7035 | 42.2208
MEMO | Memooloo T236 | CA | MEMO_132kV_BUS 2 | 132 | 1.9355 | 442.512 | 1.7581 | 133.9848 | 1.609 | 1.8082 | 137.8071 | 1.9087 | 145.461 | 9.6834 | 42.2168 | 7.3412 | 56.0937 | 9.7035 | 42.2208
MERI | Merinda | NQ | MERI_66kV_BUS 1 | 66 | 3.7597 | 429.7882 | 4.9457 | 188.4555 | 7.21 | 4.7589 | 181.3404 | 4.9552 | 188.82 | 2.3502 | 10.8983 | 0.32026 | 3.1405 | 2.3645 | 10.8834
MERI | Merinda | NQ | MERI_66kV_BUS 2 | 66 | 3.7597 | 429.7882 | 4.9457 | 188.4555 | 7.21 | 4.7589 | 181.3404 | 4.9552 | 188.82 | 2.3502 | 10.8983 | 0.32026 | 3.1405 | 2.3645 | 10.8834
MERI | Merinda | NQ | MERI_11kV_BUS 1 | 11 | 6.7176 | 127.9871 | 7.462 | 47.3899 | 8.3867 | 7.0751 | 44.9328 | 7.2674 | 46.1538 | 0.10187 | 1.035 | 0.03658 | 0.7288 | 0.10227 | 1.0345
MERI | Merinda | NQ | MERI_11kV_BUS 2 | 11 | 6.7176 | 127.9871 | 7.462 | 47.3899 | 8.3867 | 7.0751 | 44.9328 | 7.2674 | 46.1538 | 0.10187 | 1.035 | 0.03658 | 0.7288 | 0.10227 | 1.0345
MERI | Merinda | NQ | MERI_11kV_BUS 3 | 11 | 6.7176 | 127.9871 | 7.462 | 47.3899 | 8.3867 | 7.0751 | 44.9328 | 7.2674 | 46.1538 | 0.10187 | 1.035 | 0.03658 | 0.7288 | 0.10227 | 1.0345
MERN | Meringandan (Highfields) | SW | MERN_33kV_BUS 1 | 33 | 2.9192 | 166.8524 | 0.8836 | 16.8348 | 0.48907 | 2.7296 | 52.0064 | 2.335 | 44.4872 | 1.6611 | 6.9857 | 58.4193 | 21.4483 | 1.6443 | 6.9882
MERN | Meringandan (TF1) | SW | MERN_11kV_BUS 1 | 11 | 3.1913 | 60.8034 | 3.6286 | 23.045 | 4.2033 | 3.4099 | 21.6557 | 3.5332 | 22.4389 | 0.25449 | 2.1745 | 0.06992 | 1.3983 | 0.25261 | 2.1748
MERN | Meringandan (TF2) | SW | MERN_11kV_BUS 2 | 11 | 3.1913 | 60.8034 | 3.6286 | 23.045 | 4.2033 | 3.4099 | 21.6557 | 3.5332 | 22.4389 | 0.25449 | 2.1745 | 0.06992 | 1.3983 | 0.25261 | 2.1748
MERN | Meringandan (TF3) | SW | MERN_11kV_BUS 3 | 11 | 3.4546 | 65.8186 | 3.8496 | 24.4485 | 4.3448 | 3.6357 | 23.0897 | 3.7582 | 23.8676 | 0.23445 | 2.0089 | 0.07002 | 1.4003 | 0.22187 | 2.0102
MERN | Meringandan (TF4) | SW | MERN_11kV_BUS 4 | 11 | 3.4546 | 65.8186 | 3.8496 | 24.4485 | 4.3448 | 3.6357 | 23.0897 | 3.7582 | 23.8676 | 0.23445 | 2.0089 | 0.07002 | 1.4003 | 0.22187 | 2.0102
MICB | Mica Creek B Yard | NQ - MI | MICB_132kV_BUS MAIN B | 132 | 7.9766 | 1823.6861 | 10.312 | 785.8841 | 15.9594 | 10.5642 | 805.097 | 10.4515 | 796.5087 | 0.65605 | 10.4892 | 0.15319 | 2.7014 | 0.26125 | 11.1742
MICC | Mica Creek C Yard | NQ - MI | MICC_220kV_BUS 1 | 220 | 2.574 | 980.8399 | 3.4547 | 438.8107 | 5.5342 | 3.5503 | 450.9524 | 3.543 | 450.0179 | 2.4985 | 54.2225 | 0.35525 | 10.9056 | 1.4018 | 56.1252
MICC | Mica Creek C Yard (TF1) | NQ - MI | GENERATOR 2 | 132 | 7.9223 | 1811.2888 | 10.1699 | 775.0522 | 15.5104 | 10.3785 | 790.9468 | 10.2331 | 779.8648 | 0.66755 | 10.5606 | 0.19167 | 2.8972 | 0.27274 | 11.2455
MICC | Mica Creek C Yard (TF2) | NQ - MI | GENERATOR 1 | 132 | 7.9268 | 1812.3028 | 10.1814 | 775.928 | 15.5462 | 10.3933 | 792.0787 | 10.2504 | 781.1874 | 0.6666 | 10.5547 | 0.18856 | 2.8812 | 0.2718 | 11.2396
MICO | Miles-Condamine | SW | MICO_33kV_BUS 1 | 33 | 1.2536 | 71.6553 | 0.80321 | 15.3032 | 0.58934 | 1.0859 | 20.69 | 1.1624 | 22.1462 | 6.9228 | 15.2174 | 11.8996 | 43.4843 | 6.9222 | 15.2243
MICO | Miles-Condamine | SW | MICO_22kV_TEF T1 | 22 | 0.37112 | 14.1416 | 0.39587 | 5.0283 | 0.42397 | 0.37696 | 4.788 | 0.39289 | 4.9904 | 4.6069 | 37.3662 | 1.5301 | 30.6029 | 4.6067 | 37.3693
MICO | Miles-Condamine | SW | MICO_22kV_TEF T2 | 22 | 0.37112 | 14.1416 | 0.39587 | 5.0283 | 0.42397 | 0.37696 | 4.788 | 0.39289 | 4.9904 | 4.6069 | 37.3662 | 1.5301 | 30.6029 | 4.6067 | 37.3693
MIDD | Middlemount | CA | MIDD_66kV_BUS 1 | 66 | 1.759 | 201.0851 | 0.9521 | 36.28 | 0.65283 | 1.5078 | 57.4553 | 1.6008 | 60.9973 | 10.4629 | 21.4089 | 23.0106 | 81.5746 | 10.2332 | 21.6477
MIDD | Middlemount | CA | MIDD_66kV_BUS 2 | 66 | 1.759 | 201.0851 | 0.9521 | 36.28 | 0.65283 | 1.5078 | 57.4553 | 1.6008 | 60.9973 | 10.4629 | 21.4089 | 23.0106 | 81.5746 | 10.2332 | 21.6477
MIDD | Middlemount | CA | MIDD_66kV_BUS 3 | 66 | 1.759 | 201.0851 | 0.9521 | 36.28 | 0.65283 | 1.5078 | 57.4553 | 1.6008 | 60.9973 | 10.4629 | 21.4089 | 23.0106 | 81.5746 | 10.2332 | 21.6477
MIDD | Middlemount | CA | MIDD_22kV_BUS 1 | 22 | 2.4664 | 93.9814 | 2.9048 | 36.8958 | 3.5395 | 2.6534 | 33.7034 | 2.8868 | 36.6671 | 1.429 | 5.4818 | 0.26644 | 3.103 | 1.4035 | 5.5083
MIDD | Middlemount | CA | MIDD_22kV_BUS 3 | 22 | 2.4664 | 93.9814 | 2.9048 | 36.8958 | 3.5395 | 2.6534 | 33.7034 | 2.8868 | 36.6671 | 1.429 | 5.4818 | 0.26644 | 3.103 | 1.4035 | 5.5083
MILC | Millchester T095 | NQ | MILC_132kV_TEF T1 | 132 | 2.248 | 513.9683 | 2.1165 | 161.297 | 1.982 | 1.9802 | 150.913 | 2.3683 | 180.486 | 14.6959 | 34.2733 | 4.1714 | 45.3168 | 14.6506 | 34.4117
MILC | Millchester T095 | NQ | MILC_132kV_TEF T2 | 132 | 2.248 | 513.9683 | 2.1165 | 161.297 | 1.982 | 1.9802 | 150.913 | 2.3683 | 180.486 | 14.6959 | 34.2733 | 4.1714 | 45.3168 | 14.6506 | 34.4117
MILC | Millchester T095 | NQ | MILC_66kV_BUS 1 | 66 | 3.3322 | 380.9245 | 4.0545 | 154.4986 | 5.1848 | 3.5955 | 137.0086 | 4.1386 | 157.6998 | 4.5951 | 11.7096 | 0.46111 | 5.9692 | 4.5427 | 11.8123
MILC | Millchester T095 | NQ | MILC_66kV_BUS 2 | 66 | 3.3322 | 380.9245 | 4.0545 | 154.4986 | 5.1848 | 3.5955 | 137.0086 | 4.1386 | 157.6998 | 4.5951 | 11.7096 | 0.46111 | 5.9692 | 4.5427 | 11.8123
MILC | Millchester T095 (TF1) | NQ | MILC_11kV_BUS 1 | 11 | 5.0332 | 95.8947 | 5.4749 | 34.77 | 6.0104 | 5.176 | 32.8717 | 5.4063 | 34.335 | 0.18699 | 1.3753 | 0.05935 | 1.0501 | 0.18554 | 1.3782
MILC | Millchester T095 (TF2) | NQ | MILC_11kV_BUS 2 | 11 | 5.0332 | 95.8947 | 5.4749 | 34.77 | 6.0104 | 5.176 | 32.8717 | 5.4063 | 34.335 | 0.18699 | 1.3753 | 0.05935 | 1.0501 | 0.18554 | 1.3782
MILE | Miles | SW | MILE_33kV_BUS 1 | 33 | 2.4175 | 138.1789 | 1.9028 | 36.2538 | 1.5696 | 2.2553 | 42.97 | 2.2151 | 42.2026 | 1.9563 | 8.4459 | 4.0726 | 15.1653 | 1.9558 | 8.4528
MILE | Miles | SW | MILE_33kV_BUS 2 | 33 | 2.4175 | 138.1789 | 1.9028 | 36.2538 | 1.5696 | 2.2553 | 42.97 | 2.2151 | 42.2026 | 1.9563 | 8.4459 | 4.0726 | 15.1653 | 1.9558 | 8.4528
MILE | Miles | SW | MILE_33kV_BUS 3 | 33 | 2.4175 | 138.1789 | 1.9028 | 36.2538 | 1.5696 | 2.2553 | 42.97 | 2.2151 | 42.2026 | 1.9563 | 8.4459 | 4.0726 | 15.1653 | 1.9558 | 8.4528
MILE | Miles | SW | MILE_33kV_BUS 5 | 33 | 2.4175 | 138.1789 | 1.9028 | 36.2538 | 1.5696 | 2.2553 | 42.97 | 2.2151 | 42.2026 | 1.9563 | 8.4459 | 4.0726 | 15.1653 | 1.9558 | 8.4528
MILE | Miles | SW | MILE_11kV_BUS 1 | 11 | 2.8918 | 55.0961 | 3.3322 | 21.1624 | 3.9311 | 3.1322 | 19.8923 | 3.2338 | 20.5375 | 0.32863 | 2.3934 | 0.11127 | 1.455 | 0.32858 | 2.3942
MILE | Miles | SW | MILE_11kV_BUS 2 | 11 | 2.8918 | 55.0961 | 3.3322 | 21.1624 | 3.9311 | 3.1322 | 19.8923 | 3.2338 | 20.5375 | 0.32863 | 2.3934 | 0.11127 | 1.455 | 0.32858 | 2.3942
MILL | Millaroo | NQ | MILL_66kV_BUS 1 | 66 | 1.6431 | 187.8282 | 1.2459 | 47.4767 | 0.99781 | 1.4318 | 54.5604 | 1.5813 | 60.2546 | 16.9929 | 19.0272 | 25.4682 | 43.5304 | 16.9687 | 19.0149
MILL | Millaroo | NQ | MILL_66kV_BUS 2 | 66 | 1.6431 | 187.8282 | 1.2459 | 47.4767 | 0.99781 | 1.4318 | 54.5604 | 1.5813 | 60.2546 | 16.9929 | 19.0272 | 25.4682 | 43.5304 | 16.9687 | 19.0149
MILL | Millaroo | NQ | MILL_11kV_BUS 1 | 11 | 2.9431 | 56.0735 | 3.2223 | 20.4643 | 3.5467 | 2.9363 | 18.6481 | 3.2653 | 20.7375 | 0.56092 | 2.3064 | 0.0889 | 1.7779 | 0.56025 | 2.3061
MILL | Millaroo | NQ | MILL_11kV_BUS 2 | 11 | 2.9431 | 56.0735 | 3.2223 | 20.4643 | 3.5467 | 2.9363 | 18.6481 | 3.2653 | 20.7375 | 0.56092 | 2.3064 | 0.0889 | 1.7779 | 0.56025 | 2.3061
MILM | Millmerran Town | SW | MILM_33kV_BUS | 33 | 0.81388 | 46.5197 | 0.31608 | 6.0222 | 0.19189 | 0.67409 | 12.8432 | 0.75162 | 14.3202 | 13.4524 | 21.9606 | 14.3154 | 150.8644 | 13.3133 | 21.8018
MILM | Millmerran Town | SW | MILM_11kV_BUS BRINGALILY | 11 | 1.6806 | 32.0205 | 2.1745 | 13.8102 | 3.039 | 1.9581 | 12.4353 | 2.2426 | 14.2426 | 1.5653 | 3.8513 | 0.07056 | 1.4112 | 1.5498 | 3.8336
MILM | Millmerran Town | SW | MILM_11kV_BUS MILMERRAN TOWN | 11 | 1.6806 | 32.0205 | 2.1745 | 13.8102 | 3.039 | 1.9581 | 12.4353 | 2.2426 | 14.2426 | 1.5653 | 3.8513 | 0.07056 | 1.4112 | 1.5498 | 3.8336
MILM | Millmerran Town | SW | MILM_11kV_BUS ROCKY STREET | 11 | 1.6806 | 32.0205 | 2.1745 | 13.8102 | 3.039 | 1.9581 | 12.4353 | 2.2426 | 14.2426 | 1.5653 | 3.8513 | 0.07056 | 1.4112 | 1.5498 | 3.8336
MILN | Millennium Substation | MK | MILN_66kV_BUS | 66 | 3.7639 | 430.2701 | 3.5095 | 133.7289 | 3.2911 | 3.649 | 139.0446 | 3.6513 | 139.1349 | 2.0642 | 10.9433 | 2.4962 | 13.3125 | 2.0674 | 10.9567
MILN | Millennium Substation | MK | MILN_11kV_BUS 1 | 11 | 5.2038 | 99.1449 | 0.0097 | 0.06161 | 0.00485 | 4.5084 | 28.632 | 4.5035 | 28.6013 | 0.10904 | 1.338 | 2160.0511 | 1.0341 | 0.10913 | 1.3384
MING | Mingela | NQ | MING_66kV_TEF T1 | 66 | 1.6709 | 191.0093 | 1.2205 | 46.5058 | 0.94891 | 1.3967 | 53.2209 | 1.6388 | 62.4478 | 16.4902 | 18.9042 | 20.2503 | 50.38 | 16.4586 | 18.9516
MING | Mingela | NQ | MING_11kV_TEF T1 | 11 | 1.1329 | 21.5853 | 1.2185 | 7.7385 | 1.3176 | 1.1566 | 7.3457 | 1.2064 | 7.6614 | 0.45806 | 6.1492 | 0 | 4.8756 | 0.45718 | 6.1505
MIRA | Mirani | MK | MIRA_66kV_TEF T1 | 66 | 2.8262 | 323.0786 | 1.9229 | 73.2707 | 1.4604 | 2.4615 | 93.7963 | 2.6318 | 100.2835 | 6.1922 | 13.4767 | 9.9006 | 34.4241 | 6.1856 | 13.5839
MIRA | Mirani (Reg 1) | MK | MIRA_11kV_TEF R1 | 11 | 3.4296 | 65.3427 | 3.6642 | 23.2708 | 3.9373 | 3.4905 | 22.1674 | 3.6326 | 23.07 | 0.29564 | 2.0154 | 0.12364 | 1.641 | 0.29546 | 2.0184
MIRA | Mirani (Reg 2) | MK | MIRA_11kV_TEF R2 | 11 | 3.4296 | 65.3427 | 3.6642 | 23.2708 | 3.9373 | 3.4905 | 22.1674 | 3.6326 | 23.07 | 0.29564 | 2.0154 | 0.12364 | 1.641 | 0.29546 | 2.0184
MIRA | Mirani (Unregulated) | MK | MIRA_1T | 11 | 3.7655 | 71.743 | 4.0488 | 25.7136 | 4.3827 | 3.8349 | 24.3551 | 4.0182 | 25.5189 | 0.24524 | 1.839 | 0.07323 | 1.4646 | 0.24505 | 1.8419
MITC | Mitchell | SW | MITC_33kV_BUS 1 | 33 | 0.33274 | 19.0188 | 0.2402 | 4.5764 | 0.18284 | 0.26693 | 5.0857 | 0.33395 | 6.3627 | 44.2558 | 44.8185 | 42.683 | 136.855 | 44.2398 | 44.8475
MITC | Mitchell | SW | MITC_11kV_BUS 3 | 11 | 0.77748 | 14.813 | 1.0589 | 6.7252 | 1.6462 | 0.97774 | 6.2095 | 1.1426 | 7.2567 | 5.1108 | 7.3905 | 0.19347 | 2.0465 | 5.109 | 7.3937
MIVA | Miriam Vale | CA | MIVA_66kV_TEF T5 | 66 | 0.70103 | 80.1386 | 0.44103 | 16.8056 | 0.31785 | 0.58334 | 22.2281 | 0.66871 | 25.4815 | 36.7007 | 47.2042 | 55.0162 | 160.1342 | 36.7007 | 47.232
MIVA | Miriam Vale | CA | MIVA_tr_line_22276 | 66 | 0.70103 | 80.1386 | 0.44103 | 16.8056 | 0.31785 | 0.58334 | 22.2281 | 0.66871 | 25.4815 | 36.7007 | 47.2042 | 55.0162 | 160.1342 | 36.7007 | 47.232
MIVA | Miriam Vale | CA | MIVA_22kV_TEF T5 | 22 | 1.1932 | 45.4656 | 1.4561 | 18.4951 | 1.8541 | 1.2752 | 16.1972 | 1.4927 | 18.9593 | 4.454 | 10.8301 | 0.3761 | 5.5852 | 4.454 | 10.8332
MOBA | Mt Bassett | MK | MOBA_33kV_BUS 1 | 33 | 7.6258 | 435.8712 | 6.2667 | 119.3964 | 5.3356 | 7.0232 | 133.8098 | 7.202 | 137.2159 | 0.88796 | 2.6009 | 1.2521 | 4.3516 | 0.88717 | 2.613
MOBA | Mt Bassett | MK | MOBA_33kV_BUS 2 | 33 | 7.6258 | 435.8712 | 6.2667 | 119.3964 | 5.3356 | 7.0232 | 133.8098 | 7.202 | 137.2159 | 0.88796 | 2.6009 | 1.2521 | 4.3516 | 0.88717 | 2.613
MOBA | Mt Bassett | MK | MOBA_33kV_BUS 3 | 33 | 7.6258 | 435.8712 | 6.2667 | 119.3964 | 5.3356 | 7.0232 | 133.8098 | 7.202 | 137.2159 | 0.88796 | 2.6009 | 1.2521 | 4.3516 | 0.88717 | 2.613
MOBA | Mt Bassett | MK | MOBA_11kV_BUS 3 | 11 | 5.4514 | 103.8631 | 5.907 | 37.5145 | 6.4502 | 5.6097 | 35.6262 | 5.8209 | 36.9678 | 0.14786 | 1.273 | 0.0492 | 0.98396 | 0.14777 | 1.2743
MOBA | Mt Bassett | MK | MOBA_11kV_BUS 4 | 11 | 5.4438 | 103.718 | 5.8981 | 37.4577 | 6.4395 | 5.6015 | 35.5745 | 5.8122 | 36.9123 | 0.14795 | 1.2747 | 0.04929 | 0.98575 | 0.14786 | 1.2761
MOBA | Mt Bassett | MK | MOBA_11kV_BUS 5 | 11 | 5.4438 | 103.718 | 5.8981 | 37.4577 | 6.4395 | 5.6015 | 35.5745 | 5.8122 | 36.9123 | 0.14795 | 1.2747 | 0.04929 | 0.98575 | 0.14786 | 1.2761
MOBA | Mt Bassett (TF1) | MK | MOBA_11kV_BUS 1 | 11 | 5.4514 | 103.8631 | 5.907 | 37.5145 | 6.4502 | 5.6097 | 35.6262 | 5.8209 | 36.9678 | 0.14786 | 1.273 | 0.0492 | 0.98396 | 0.14777 | 1.2743
MOBA | Mt Bassett (TF2) | MK | MOBA_11kV_BUS 2 | 11 | 5.4514 | 103.8631 | 5.907 | 37.5145 | 6.4502 | 5.6097 | 35.6262 | 5.8209 | 36.9678 | 0.14786 | 1.273 | 0.0492 | 0.98396 | 0.14777 | 1.2743
MODA | Monduran Dam | WB | MODA_66kV_BUS | 66 | 1.2471 | 142.5664 | 0.84818 | 32.3198 | 0.63589 | 1.0439 | 39.7798 | 1.2012 | 45.7722 | 20.6618 | 26.5117 | 28.213 | 77.8621 | 20.6368 | 26.5891
MODA | Monduran Dam | WB | MODA_11kV_BUS 1 | 11 | 1.4294 | 27.2334 | 1.5108 | 9.5948 | 1.6004 | 1.4226 | 9.0346 | 1.5234 | 9.6749 | 0.58404 | 4.8527 | 0 | 4.1163 | 0.58334 | 4.8549
MODA | Monduran Dam | WB | MODA_11kV_BUS 2 | 11 | 1.3473 | 25.6703 | 1.419 | 9.0117 | 1.4973 | 1.3416 | 8.5203 | 1.4295 | 9.0786 | 0.57394 | 5.1535 | 0 | 4.4171 | 0.57325 | 5.1557
MODA | Monduran Dam | WB | MODA_3.3kV_BUS | 3.3 | 5.84 | 33.3801 | 6.2584 | 11.9238 | 6.7307 | 5.8201 | 11.0888 | 6.3183 | 12.0379 | 0.05165 | 0.35516 | 0 | 0.28888 | 0.05159 | 0.35535
MOFO | Mt Fox | NQ | MOFO_66kV_TEF T1 | 66 | 1.0103 | 115.4929 | 0.68437 | 26.0781 | 0.51734 | 0.87332 | 33.2779 | 0.94672 | 36.0748 | 20.8357 | 35.877 | 34.0211 | 95.4314 | 20.76 | 36.1517
MOFO | Mt Fox | NQ | MOFO_33kV_TEF T1 | 33 | 0.17913 | 10.2385 | 0.18401 | 3.5059 | 0.18924 | 0.17956 | 3.4211 | 0.18378 | 3.5015 | 10.6957 | 116.51 | 5.4868 | 107.5408 | 10.6768 | 116.5787
MOGA | Mt Garnet | FN | MOGA_66kV_BUS | 66 | 0.68378 | 78.166 | 0.42292 | 16.1154 | 0.3044 | 0.58119 | 22.1464 | 0.63988 | 24.3828 | 30.3416 | 53.2647 | 48.9699 | 169.7726 | 30.2448 | 53.3744
MOGA | Mt Garnet | FN | MOGA_22kV_BUS 1 | 22 | 1.3312 | 50.727 | 1.6919 | 21.4896 | 2.314 | 1.5421 | 19.5879 | 1.7195 | 21.8409 | 3.8171 | 9.7767 | 0.44582 | 3.8584 | 3.8064 | 9.7889
MOGA | Mt Garnet | FN | MOGA_22kV_BUS 2 | 22 | 1.3312 | 50.727 | 1.6919 | 21.4896 | 2.314 | 1.5421 | 19.5879 | 1.7195 | 21.8409 | 3.8171 | 9.7767 | 0.44582 | 3.8584 | 3.8064 | 9.7889
MOLE | Mt Leyshon | NQ | MOLE_66kV_TEF T1 | 66 | 1.6943 | 193.6889 | 1.343 | 51.1757 | 1.1077 | 1.4719 | 56.0882 | 1.6567 | 63.1278 | 11.4449 | 21.9321 | 11.0112 | 43.3311 | 11.3926 | 22.0348
MOLE | Mt Leyshon | NQ | MOLE_11kV_TEF T1 | 11 | 4.0105 | 76.4101 | 4.5839 | 29.1118 | 5.3433 | 4.1718 | 26.4947 | 4.5803 | 29.0889 | 0.34644 | 1.7071 | 0.02853 | 1.0979 | 0.34499 | 1.71
MOMG | Mt Morgan | CA | MOMG_66kV_TEF T1 | 66 | 2.1262 | 243.0525 | 1.495 | 56.9662 | 1.1471 | 1.8262 | 69.5878 | 2.0242 | 77.1344 | 11.2197 | 16.2106 | 16.9119 | 41.8941 | 11.2211 | 16.2364
MOMG | Mt Morgan | CA | MOMG_66kV_TEF T2 | 66 | 2.1262 | 243.0525 | 1.495 | 56.9662 | 1.1471 | 1.8262 | 69.5878 | 2.0242 | 77.1344 | 11.2197 | 16.2106 | 16.9119 | 41.8941 | 11.2211 | 16.2364
MOMG | Mt Morgan | CA | MOMG_11kV_BUS LH | 11 | 5.5556 | 105.8494 | 6.4427 | 40.9167 | 7.6419 | 5.7861 | 36.7468 | 6.4811 | 41.1604 | 0.38426 | 1.1973 | 0.07258 | 0.74702 | 0.3843 | 1.198
MOMG | Mt Morgan | CA | MOMG_11kV_BUS RH | 11 | 5.5556 | 105.8494 | 6.4427 | 40.9167 | 7.6419 | 5.7861 | 36.7468 | 6.4811 | 41.1604 | 0.38426 | 1.1973 | 0.07258 | 0.74702 | 0.3843 | 1.198
MOMO | Mt Molloy | FN | MOMO_66kV_BUS 1 | 66 | 1.9493 | 222.8391 | 1.4323 | 54.5762 | 1.1302 | 1.7016 | 64.8399 | 1.8523 | 70.5828 | 10.1554 | 18.9533 | 13.8346 | 42.9017 | 10.082 | 19.0607
MOMO | Mt Molloy (TF1) | FN | MOMO_22kV_BUS | 22 | 2.5583 | 97.4842 | 2.975 | 37.7876 | 3.5513 | 2.7 | 34.2951 | 2.9707 | 37.7323 | 1.3274 | 5.2976 | 0.199 | 3.1917 | 1.3192 | 5.3096
MOMO | Mt Molloy (TF2) | FN | MOMO_22kV_BUS GMS 2 | 22 | 0.57734 | 21.9997 | 0.59558 | 7.5648 | 0.61519 | 0.58059 | 7.3745 | 0.59329 | 7.5358 | 3.2575 | 23.9801 | 2.1291 | 21.8742 | 3.2493 | 23.992
MOMW | Mt Mowbullan | SW | MOMW_33kV_TEF T1 | 33 | 0.45879 | 26.2236 | 0.34116 | 6.5 | 0.2629 | 0.3642 | 6.9389 | 0.46653 | 8.8886 | 38.3108 | 24.8881 | 45.9433 | 87.8754 | 38.312 | 24.8882
MOMW | Mt Mowbullan | SW | MOMW_11kV_TEF T1 | 11 | 0.62882 | 11.9806 | 0.71846 | 4.5628 | 0.82679 | 0.60896 | 3.8674 | 0.75104 | 4.7698 | 4.6236 | 10.1031 | 0.36689 | 7.3378 | 4.6238 | 10.1031
MONT | Monto | CA | MONT_66KV BUS 2 | 66 | 0.62631 | 71.5967 | 0.43175 | 16.4518 | 0.32454 | 0.51873 | 19.7664 | 0.60981 | 23.237 | 46.5457 | 48.0897 | 64.9237 | 148.467 | 46.5465 | 48.1097
MONT | Monto | CA | MONT_66kV_TEF T1 | 66 | 0.62631 | 71.5967 | 0.43175 | 16.4518 | 0.32454 | 0.51873 | 19.7664 | 0.60981 | 23.237 | 46.5457 | 48.0897 | 64.9237 | 148.467 | 46.5465 | 48.1097
MONT | Monto | CA | MONT_66kV_TEF T2 | 66 | 0.62631 | 71.5967 | 0.43175 | 16.4518 | 0.32454 | 0.51873 | 19.7664 | 0.60981 | 23.237 | 46.5457 | 48.0897 | 64.9237 | 148.467 | 46.5465 | 48.1097
MONT | Monto | CA | MONT_11kV_BUS LH | 11 | 2.8642 | 54.5709 | 3.8173 | 24.2432 | 5.6612 | 3.4135 | 21.6789 | 4.0838 | 25.9357 | 1.35 | 2.0314 | 0.05704 | 0.68448 | 1.35 | 2.032
MONT | Monto | CA | MONT_11kV_BUS RH | 11 | 2.8642 | 54.5709 | 3.8173 | 24.2432 | 5.6612 | 3.4135 | 21.6789 | 4.0838 | 25.9357 | 1.35 | 2.0314 | 0.05704 | 0.68448 | 1.35 | 2.032
MOOE | Moore | WB | MOOE_66kV_BUS 1 | 66 | 1.9466 | 222.5304 | 1.1711 | 44.6262 | 0.8327 | 1.6542 | 63.0338 | 1.8143 | 69.1354 | 9.9553 | 19.0958 | 15.9737 | 62.9999 | 9.9524 | 19.1032
MOOE | Moore | WB | MOOE_11kV_BUS | 11 | 3.2819 | 62.5283 | 3.607 | 22.9077 | 4.001 | 3.3792 | 21.4607 | 3.5688 | 22.6649 | 0.47277 | 2.0758 | 0.19623 | 1.5453 | 0.47268 | 2.076
MOOR | Moorvale | MK | MOOR_66kV_TEF T1 | 66 | 2.9322 | 335.191 | 2.3483 | 89.4833 | 1.9592 | 2.6795 | 102.102 | 2.7616 | 105.2299 | 3.2572 | 13.9192 | 4.2751 | 24.5971 | 3.2603 | 13.9325
MOOR | Moorvale | MK | MOOR_11kV_BUS 1 | 11 | 4.843 | 92.2712 | 5.3276 | 33.8348 | 5.9206 | 5.0688 | 32.1911 | 5.1971 | 33.0062 | 0.16035 | 1.4336 | 0.06988 | 1.0469 | 0.16044 | 1.4339
MOOR | Moorvale | MK | MOOR_11kV_BUS 2 | 11 | 4.843 | 92.2712 | 5.3276 | 33.8348 | 5.9206 | 5.0688 | 32.1911 | 5.1971 | 33.0062 | 0.16035 | 1.4336 | 0.06988 | 1.0469 | 0.16044 | 1.4339
MOPA | Mona Park | NQ | MOPA_66kV_BUS 1 | 66 | 4.6803 | 535.0307 | 3.3224 | 126.6 | 2.5647 | 4.1344 | 157.543 | 4.3746 | 166.6926 | 3.2068 | 8.362 | 4.7776 | 19.4568 | 3.1536 | 8.3537
MOPA | Mona Park | NQ | MOPA_66kV_BUS 2 | 66 | 4.6803 | 535.0307 | 3.3224 | 126.6 | 2.5647 | 4.1344 | 157.543 | 4.3746 | 166.6926 | 3.2068 | 8.362 | 4.7776 | 19.4568 | 3.1536 | 8.3537
MOPA | Mona Park (TF1) | NQ | MOPA_11kV_BUS 1 | 11 | 4.7422 | 90.3518 | 5.0899 | 32.3255 | 5.4898 | 4.8716 | 30.9391 | 5.0075 | 31.802 | 0.15336 | 1.4651 | 0.06429 | 1.1709 | 0.15188 | 1.4649
MOPA | Mona Park (TF2) | NQ | MOPA_11kV_BUS 2 | 11 | 4.7422 | 90.3518 | 5.0899 | 32.3255 | 5.4898 | 4.8716 | 30.9391 | 5.0075 | 31.802 | 0.15336 | 1.4651 | 0.06429 | 1.1709 | 0.15188 | 1.4649
MOPS | Moranbah Power Station | MK | MOPS_11kV_BUS 1 | 11 | 22.1673 | 422.3433 | 0.8056 | 5.1163 | 0.41016 | 19.1781 | 121.7973 | 19.2252 | 122.0965 | 0.04172 | 0.31237 | 0.03692 | 25.3896 | 0.03686 | 0.3129
MORA | Moranbah T034 | MK | MORA_66kV_BUS A | 66 | 11.3797 | 1300.8769 | 13.2645 | 505.4463 | 15.9177 | 12.4564 | 474.6508 | 12.8708 | 490.4436 | 0.59127 | 3.6356 | 0.19057 | 2.1033 | 0.56235 | 3.6453
MORA | Moranbah T034 | MK | MORA_66kV_BUS B | 66 | 11.3797 | 1300.8769 | 13.2645 | 505.4463 | 15.9177 | 12.4564 | 474.6508 | 12.8708 | 490.4436 | 0.59127 | 3.6356 | 0.19057 | 2.1033 | 0.56235 | 3.6453
MORA | Moranbah T034 (TF1) | MK | MORA_11kV_BUS A | 11 | 16.7881 | 319.8562 | 0.97866 | 6.2153 | 0.5011 | 14.69 | 93.2941 | 14.3847 | 91.3548 | 0.03113 | 0.41496 | 13.9019 | 15.4065 | 0.0302 | 0.41519
MORA | Moranbah T034 (TF2*O0518*ON) | MK | MORA_11kV_BUS B | 11 | 23.1964 | 441.9508 | 0.80668 | 5.1231 | 0.41028 | 20.0836 | 127.5479 | 20.1149 | 127.7467 | 0.02752 | 0.29991 | 0.00182 | 25.3804 | 0.02311 | 0.30001
MORO | Mt Rooper | MK | MORO_66kV_TEF T1 | 66 | 2.2729 | 259.829 | 1.6556 | 63.0877 | 1.2909 | 1.9824 | 75.5396 | 2.1654 | 82.511 | 7.8429 | 16.6906 | 9.972 | 38.2173 | 7.7991 | 16.5944
MORO | Mt Rooper | MK | MORO_11kV_TEF T1 | 11 | 3.4983 | 66.6506 | 3.8104 | 24.1991 | 4.1733 | 3.5777 | 22.7217 | 3.7789 | 23.9994 | 0.29344 | 1.9753 | 0.07567 | 1.5124 | 0.29223 | 1.9726
MORW | Mt Rawdon | WB | MORW_66kV_TEF T1 | 66 | 1.1131 | 127.2432 | 0.67132 | 25.5808 | 0.47937 | 0.96255 | 36.678 | 1.0231 | 38.9862 | 15.8359 | 34.1683 | 31.0373 | 108.1684 | 15.7598 | 34.2074
MOSI | Mt Sibley | SW | MOSI_33kV_BUS 1 | 33 | 1.4407 | 82.3491 | 0.58052 | 11.0604 | 0.35757 | 1.3284 | 25.3097 | 1.1889 | 22.6524 | 7.2228 | 12.6293 | 66.5525 | 46.6683 | 7.2229 | 12.6248
MOSI | Mt Sibley | SW | MOSI_33kV_BUS 2 | 33 | 1.4407 | 82.3491 | 0.58052 | 11.0604 | 0.35757 | 1.3284 | 25.3097 | 1.1889 | 22.6524 | 7.2228 | 12.6293 | 66.5525 | 46.6683 | 7.2229 | 12.6248
MOSI | Mt Sibley | SW | MOSI_33kV_BUS 3 | 33 | 1.4407 | 82.3491 | 0.58052 | 11.0604 | 0.35757 | 1.3284 | 25.3097 | 1.1889 | 22.6524 | 7.2228 | 12.6293 | 66.5525 | 46.6683 | 7.2229 | 12.6248
MOSI | Mt Sibley (TF1) | SW | MOSI_11kV_BUS 1 | 11 | 2.2964 | 43.7526 | 2.7723 | 17.6066 | 3.4809 | 2.4797 | 15.748 | 2.7965 | 17.7604 | 0.87803 | 2.9131 | 0.07549 | 1.5099 | 0.87804 | 2.9126
MOSI | Mt Sibley (TF2) | SW | MOSI_11kV_BUS 2 | 11 | 2.2964 | 43.7526 | 2.7723 | 17.6066 | 3.4809 | 2.4797 | 15.748 | 2.7965 | 17.7604 | 0.87803 | 2.9131 | 0.07549 | 1.5099 | 0.87804 | 2.9126
MOSI | Mt Sibley (TF3) | SW | MOSI_11kV_BUS 3 | 11 | 2.0959 | 39.9316 | 2.4826 | 15.7669 | 3.032 | 2.2271 | 14.1442 | 2.4952 | 15.8463 | 0.89296 | 3.2119 | 0.09043 | 1.8086 | 0.89298 | 3.2114
MOSS | Mossman (TF1) | FN | MOSS_22kV_BUS 1 | 22 | 4.8214 | 183.7195 | 4.269 | 54.2229 | 3.8246 | 4.4679 | 56.7502 | 4.715 | 59.8892 | 0.40986 | 2.8688 | 0.1553 | 4.0326 | 0.3902 | 2.8707
MOSS | Mossman (TF2) | FN | MOSS_22kV_BUS 2 | 22 | 4.8214 | 183.7195 | 4.269 | 54.2229 | 3.8246 | 4.4679 | 56.7502 | 4.715 | 59.8892 | 0.40986 | 2.8688 | 0.1553 | 4.0326 | 0.3902 | 2.8707
MOTY | Mt Tyson | SW | pole6065148_tr_line_47122 | 33 | 1.152 | 65.8451 | 0.80888 | 15.4112 | 0.60767 | 0.95525 | 18.2 | 1.1321 | 21.5691 | 12.4385 | 13.279 | 15.981 | 39.8108 | 12.2994 | 13.1202
MOUR | Moura T027 | CA | MOUR_66kV_BUS EAST | 66 | 6.0142 | 687.5207 | 7.4061 | 282.2098 | 9.7952 | 6.8466 | 260.8893 | 7.4169 | 282.621 | 1.5156 | 6.8027 | 0.1253 | 2.9771 | 1.5226 | 6.902
MOUR | Moura T027 | CA | MOUR_66kV_BUS TRANSFER | 66 | 6.0142 | 687.5207 | 7.4061 | 282.2098 | 9.7952 | 6.8466 | 260.8893 | 7.4169 | 282.621 | 1.5156 | 6.8027 | 0.1253 | 2.9771 | 1.5226 | 6.902
MOUR | Moura T027 | CA | MOUR_66kV_BUS WEST | 66 | 6.0142 | 687.5207 | 7.4061 | 282.2098 | 9.7952 | 6.8466 | 260.8893 | 7.4169 | 282.621 | 1.5156 | 6.8027 | 0.1253 | 2.9771 | 1.5226 | 6.902
MOUR | Moura T027 | CA | MOUR_22kV_TEF T5 | 22 | 5.1825 | 197.4786 | 4.7963 | 60.9208 | 4.4744 | 4.8493 | 61.5938 | 5.1637 | 65.5876 | 0.29951 | 2.6793 | 0.00253 | 3.3488 | 0.30008 | 2.6905
MOUR | Moura T027 | CA | MOUR_22kV_TEF T6 | 22 | 5.1825 | 197.4786 | 4.7963 | 60.9208 | 4.4744 | 4.8493 | 61.5938 | 5.1637 | 65.5876 | 0.29951 | 2.6793 | 0.00253 | 3.3488 | 0.30008 | 2.6905
MOUR | Moura T027 (TF1) | CA | MOUR_11kV_TEF T5 | 11 | 15.1541 | 288.7241 | 12.8513 | 81.6169 | 11.1967 | 13.7899 | 87.5776 | 14.6777 | 93.2157 | 0.05375 | 0.45786 | 0.00139 | 0.70867 | 0.05389 | 0.46064
MOUR | Moura T027 (TF2) | CA | MOUR_11kV_TEF T6 | 11 | 15.107 | 287.8275 | 12.8232 | 81.4379 | 11.1798 | 13.7515 | 87.3341 | 14.6348 | 92.9431 | 0.05377 | 0.4593 | 0.00139 | 0.70937 | 0.05391 | 0.46209
MUCK | Muckadilla Regulator (Regulated) | SW | MUCK_33kV_R1 Upstream | 33 | 0.59278 | 33.8817 | 0.47086 | 8.9711 | 0.37736 | 0.46946 | 8.9443 | 0.61466 | 11.7109 | 24.7447 | 25.2538 | 16.6665 | 65.4634 | 24.7287 | 25.2828
MUCK | Muckadilla Regulator (Un-Regulated) | SW | MUCK_33kV_R1 Downstream | 33 | 0.56522 | 32.3069 | 0.45427 | 8.655 | 0.36849 | 0.45287 | 8.6283 | 0.58476 | 11.1411 | 24.8576 | 27.5134 | 16.4191 | 66.5394 | 24.8417 | 27.5424
MUNG | Mungar QR T123 | WB | MUNG_132kV_TEF T1 | 132 | 2.996 | 684.972 | 1.719 | 131.0051 | 1.2046 | 2.6408 | 201.2534 | 2.6872 | 204.7894 | 7.665 | 26.9139 | 20.0767 | 88.145 | 7.451 | 26.9631
MUNG | Mungar QR T123 | WB | MUNG_132kV_TEF T2 | 132 | 2.996 | 684.972 | 1.719 | 131.0051 | 1.2046 | 2.6408 | 201.2534 | 2.6872 | 204.7894 | 7.665 | 26.9139 | 20.0767 | 88.145 | 7.451 | 26.9631
MURG | Murgon | WB | MURG_66kV_BUS LOWER_1 | 66 | 2.0163 | 230.4989 | 1.631 | 62.1501 | 1.3688 | 1.855 | 70.6851 | 1.8961 | 72.252 | 7.4535 | 19.4084 | 11.3008 | 33.7028 | 7.424 | 19.415
MURG | Murgon | WB | MURG_66kV_BUS LOWER_2 | 66 | 2.0163 | 230.4989 | 1.631 | 62.1501 | 1.3688 | 1.855 | 70.6851 | 1.8961 | 72.252 | 7.4535 | 19.4084 | 11.3008 | 33.7028 | 7.424 | 19.415
MURG | Murgon | WB | MURG_66kV_BUS UPPER_1 | 66 | 2.0163 | 230.4989 | 1.631 | 62.1501 | 1.3688 | 1.855 | 70.6851 | 1.8961 | 72.252 | 7.4535 | 19.4084 | 11.3008 | 33.7028 | 7.424 | 19.415
MURG | Murgon | WB | MURG_66kV_BUS UPPER_2 | 66 | 2.0163 | 230.4989 | 1.631 | 62.1501 | 1.3688 | 1.855 | 70.6851 | 1.8961 | 72.252 | 7.4535 | 19.4084 | 11.3008 | 33.7028 | 7.424 | 19.415
MURG | Murgon (TF1) | WB | MURG_11kV_BUS 1 | 11 | 4.299 | 81.9068 | 4.8604 | 30.8675 | 5.5841 | 4.5091 | 28.6369 | 4.7938 | 30.4449 | 0.25442 | 1.6052 | 0.04738 | 1.066 | 0.2536 | 1.6054
MURG | Murgon (TF2) | WB | MURG_11kV_BUS 2 | 11 | 4.299 | 81.9068 | 4.8604 | 30.8675 | 5.5841 | 4.5091 | 28.6369 | 4.7938 | 30.4449 | 0.25442 | 1.6052 | 0.04738 | 1.066 | 0.2536 | 1.6054
MUTA | Mutarnee | NQ | MUTA_66kV_TEF T1 | 66 | 1.1715 | 133.9204 | 0.88723 | 33.8079 | 0.71389 | 1.0242 | 39.0259 | 1.1211 | 42.7188 | 21.2384 | 28.7942 | 30.603 | 63.6189 | 21.1627 | 29.0689
MUTA | Mutarnee | NQ | MUTA_11kV_TEF T1 | 11 | 0.94325 | 17.9714 | 0.98332 | 6.2449 | 1.0276 | 0.94837 | 6.023 | 0.98099 | 6.2301 | 1.7363 | 7.1998 | 1.1464 | 6.4 | 1.7342 | 7.2074
MUTO | Mundubbera Town | WB | MUTO_66kV_BUS 1 | 66 | 0.97221 | 111.1389 | 0.62928 | 23.9789 | 0.4647 | 0.84843 | 32.3297 | 0.89698 | 34.1795 | 21.9269 | 37.1247 | 44.3649 | 104.987 | 21.7819 | 37.2721
MUTO | Mundubbera Town | WB | MUTO_66kV_BUS 2 | 66 | 0.97221 | 111.1389 | 0.62928 | 23.9789 | 0.4647 | 0.84843 | 32.3297 | 0.89698 | 34.1795 | 21.9269 | 37.1247 | 44.3649 | 104.987 | 21.7819 | 37.2721
MUTO | Mundubbera Town | WB | MUTO_11kV_BUS 1 | 11 | 4.5472 | 86.6358 | 6.0685 | 38.54 | 9.0879 | 5.6364 | 35.7956 | 6.3673 | 40.4378 | 0.61836 | 1.4065 | 0.02012 | 0.40187 | 0.61227 | 1.411
MUTO | Mundubbera Town | WB | MUTO_11kV_BUS 2 | 11 | 4.5472 | 86.6358 | 6.0685 | 38.54 | 9.0879 | 5.6364 | 35.7956 | 6.3673 | 40.4378 | 0.61836 | 1.4065 | 0.02012 | 0.40187 | 0.61227 | 1.411
MUTO | Mundubbera Town | WB | MUTO_11kV_BUS 3 | 11 | 4.5472 | 86.6358 | 6.0685 | 38.54 | 9.0879 | 5.6364 | 35.7956 | 6.3673 | 40.4378 | 0.61836 | 1.4065 | 0.02012 | 0.40187 | 0.61227 | 1.411
NANA | Nanango | WB | NANA_66kV_BUS | 66 | 1.9246 | 220.0175 | 1.2029 | 45.8362 | 0.86595 | 1.6132 | 61.4711 | 1.8245 | 69.5227 | 12.3615 | 17.9332 | 18.519 | 59.3016 | 12.3178 | 17.9596
NANA | Nanango | WB | NANA_11kV_BUS 1 | 11 | 5.1146 | 97.4466 | 5.9536 | 37.8106 | 7.0992 | 5.3593 | 34.0361 | 5.9753 | 37.9484 | 0.43976 | 1.2933 | 0.09638 | 0.79518 | 0.43855 | 1.294
NANA | Nanango | WB | NANA_11kV_BUS 2 | 11 | 5.1146 | 97.4466 | 5.9536 | 37.8106 | 7.0992 | 5.3593 | 34.0361 | 5.9753 | 37.9484 | 0.43976 | 1.2933 | 0.09638 | 0.79518 | 0.43855 | 1.294
NAND | Nandi | SW | NAND_33kV_BUS | 33 | 1.753 | 100.1966 | 1.3054 | 24.8717 | 1.0209 | 1.4431 | 27.4955 | 1.7457 | 33.2604 | 8.5792 | 8.3284 | 10.0342 | 23.101 | 8.5805 | 8.3285
NAND | Nandi | SW | NAND_11kV_BUS G/DALE | 11 | 1.9475 | 37.1045 | 2.1789 | 13.8382 | 2.4573 | 1.932 | 12.2701 | 2.2306 | 14.1659 | 1.0542 | 3.4292 | 0.10091 | 2.5038 | 1.0543 | 3.4292
NAND | Nandi | SW | NAND_11kV_BUS_LOUDIN | 11 | 1.9475 | 37.1045 | 2.1789 | 13.8382 | 2.4573 | 1.932 | 12.2701 | 2.2306 | 14.1659 | 1.0542 | 3.4292 | 0.10091 | 2.5038 | 1.0543 | 3.4292
NEBO | Nebo H011 (TF3) | MK | NEBO_11kV_TEF T3 | 11 | 3.2474 | 61.8713 | 1.8287 | 11.6137 | 1.2728 | 2.8529 | 18.1186 | 2.9123 | 18.4955 | 0.11816 | 2.148 | 0 | 7.161 | 0.11835 | 2.1492
NESM | Neil Smith | NQ | NESM_66kV_TEF T1 | 66 | 8.3641 | 956.1433 | 6.1529 | 234.4567 | 4.855 | 7.4129 | 282.4705 | 7.8635 | 299.6413 | 2.0113 | 4.5901 | 2.9682 | 10.0264 | 1.9928 | 4.5945
NESM | Neil Smith | NQ | NESM_66kV_TEF T2 | 66 | 10.1182 | 1156.6708 | 8.7184 | 332.2162 | 7.6477 | 9.3864 | 357.6681 | 9.7382 | 371.0745 | 1.2688 | 3.9435 | 1.46 | 5.9748 | 1.2497 | 3.9453
NESM | Neil Smith (TF1) | NQ | NESM_11kV_BUS 1 | 11 | 10.2046 | 194.424 | 10.91 | 69.2875 | 11.7149 | 10.3827 | 65.9392 | 10.8172 | 68.6987 | 0.08186 | 0.67967 | 0.026 | 0.55217 | 0.08135 | 0.6798
NESM | Neil Smith (TF2) | NQ | NESM_11kV_BUS 2 | 11 | 10.4599 | 199.2883 | 11.081 | 70.3735 | 11.7781 | 10.6708 | 67.7689 | 10.9367 | 69.4573 | 0.06513 | 0.66469 | 0.02988 | 0.55515 | 0.0646 | 0.66474
NEWL | Newlands T069 | NQ | NEWL_66kV_BUS 1 | 66 | 4.6889 | 536.0099 | 5.8675 | 223.5836 | 7.8306 | 5.3902 | 205.3959 | 5.8793 | 224.03 | 2.4107 | 8.6083 | 0.28431 | 3.5878 | 2.4201 | 8.6156
NEWL | Newlands T069 | NQ | NEWL_66kV_BUS 2 | 66 | 4.6889 | 536.0099 | 5.8675 | 223.5836 | 7.8306 | 5.3902 | 205.3959 | 5.8793 | 224.03 | 2.4107 | 8.6083 | 0.28431 | 3.5878 | 2.4201 | 8.6156
NOCL | North Cloncurry | NQ - MI | NOCL_66kV_BUS | 66 | 1.6623 | 190.0236 | 1.553 | 59.176 | 1.4645 | 1.6049 | 61.155 | 1.6204 | 61.7456 | 7.09 | 24.1985 | 7.892 | 29.3652 | 6.9913 | 24.3698
NOCL | North Cloncurry (TF1) | NQ - MI | NOCL_11kV_BUS 1 | 11 | 3.1342 | 59.7138 | 3.4923 | 22.1792 | 3.9497 | 3.2884 | 20.8839 | 3.4212 | 21.7277 | 0.27406 | 2.2121 | 0.07712 | 1.5399 | 0.27132 | 2.2168
NOCL | North Cloncurry (TF2) | NQ - MI | NOCL_11kV_BUS 3 | 11 | 3.1342 | 59.7138 | 3.4923 | 22.1792 | 3.9497 | 3.2884 | 20.8839 | 3.4212 | 21.7277 | 0.27406 | 2.2121 | 0.07712 | 1.5399 | 0.27132 | 2.2168
NOMA | North Mackay (TF1) | MK | NOMA_33kV_BUS 1 | 33 | 4.3737 | 249.989 | 5.2686 | 100.3811 | 6.6446 | 5.1041 | 97.2469 | 4.9677 | 94.648 | 0.5449 | 4.7608 | 0.38765 | 2.3077 | 0.53253 | 4.7748
NOMA | North Mackay (TF1) | MK | NOMA_11kV_BUS 1 | 11 | 6.1055 | 116.3247 | 7.2218 | 45.8644 | 8.8507 | 6.8437 | 43.4632 | 6.9434 | 44.0964 | 0.09115 | 1.1406 | 0.03061 | 0.61161 | 0.08978 | 1.1421
NOMA | North Mackay (TF2) | MK | NOMA_33kV_BUS 2 | 33 | 4.3933 | 251.1132 | 5.2826 | 100.6471 | 6.644 | 5.1104 | 97.366 | 4.9869 | 95.0124 | 0.54024 | 4.7397 | 0.37547 | 2.3207 | 0.52787 | 4.7538
NOMA | North Mackay (TF2) | MK | NOMA_11kV_BUS 2 | 11 | 6.1363 | 116.9121 | 7.2589 | 46.1005 | 8.8977 | 6.8792 | 43.689 | 6.9789 | 44.3218 | 0.09041 | 1.1349 | 0.03038 | 0.60824 | 0.08903 | 1.1364
NORM | Normanton | FN | NORM_T01 3MI | 66 | 0.34832 | 39.8181 | 0.47403 | 18.0631 | 0.74971 | 0.46519 | 17.7261 | 0.49637 | 18.9144 | 31.3589 | 116.1795 | 0.2891 | 24.2953 | 29.376 | 117.6814
NORM | Normanton | FN | NORM_T02 3MI | 66 | 0.34832 | 39.8181 | 0.47403 | 18.0631 | 0.74971 | 0.46519 | 17.7261 | 0.49637 | 18.9144 | 31.3589 | 116.1795 | 0.2891 | 24.2953 | 29.376 | 117.6814
NORM | Normanton | FN | NORM_22kV_BUS 1 | 22 | 0.95368 | 36.3402 | 1.3377 | 16.9914 | 2.2641 | 1.3734 | 17.4443 | 1.4284 | 18.1427 | 3.2531 | 14.2847 | 0.00831 | 1.9719 | 2.9337 | 14.4584
NORM | Normanton | FN | NORM_22kV_BUS 2 | 22 | 0.95368 | 36.3402 | 1.3377 | 16.9914 | 2.2641 | 1.3734 | 17.4443 | 1.4284 | 18.1427 | 3.2531 | 14.2847 | 0.00831 | 1.9719 | 2.9337 | 14.4584
NORM | Normanton | FN | NORM_6.6kV_BUS 1 | 6.6 | 2.7805 | 31.7856 | 0 | 0 | 0 | 2.4005 | 9.1473 | 2.4005 | 9.1473 | 0.30006 | 1.4773 | 329999969.002 | -28.6636 | 0.27121 | 1.4926
NORM | Normanton | FN | NORM_6.6kV_BUS 2 | 6.6 | 2.7805 | 31.7856 | 0 | 0 | 0 | 2.4005 | 9.1473 | 2.4005 | 9.1473 | 0.30006 | 1.4773 | 329999969.002 | -28.6636 | 0.27121 | 1.4926
NORW | Norwin | SW | NORW_33kV_BUS 2 | 33 | 0.91486 | 52.2915 | 0.59488 | 11.3341 | 0.43223 | 0.76417 | 14.5594 | 0.88007 | 16.7675 | 14.6156 | 17.6434 | 21.6463 | 57.587 | 14.4764 | 17.4846
NORW | Norwin | SW | NORW_33kV_BUS T1 | 33 | 0.91486 | 52.2915 | 0.59488 | 11.3341 | 0.43223 | 0.76417 | 14.5594 | 0.88007 | 16.7675 | 14.6156 | 17.6434 | 21.6463 | 57.587 | 14.4764 | 17.4846
NORW | Norwin | SW | NORW_33kV_BUS T3 | 33 | 0.91486 | 52.2915 | 0.59488 | 11.3341 | 0.43223 | 0.76417 | 14.5594 | 0.88007 | 16.7675 | 14.6156 | 17.6434 | 21.6463 | 57.587 | 14.4764 | 17.4846
NORW | Norwin (TF1) | SW | NORW_11kV_BUS T1 | 11 | 1.6052 | 30.5821 | 1.974 | 12.5368 | 2.5233 | 1.7105 | 10.8629 | 2.0327 | 12.9094 | 1.7257 | 3.996 | 0.10178 | 2.0356 | 1.7103 | 3.9783
NORW | Norwin (TF2) | SW | NORW_11kV_BUS 2 | 11 | 1.5997 | 30.4779 | 1.9656 | 12.4831 | 2.5091 | 1.7032 | 10.8168 | 2.0235 | 12.8511 | 1.7265 | 4.0119 | 0.10257 | 2.0515 | 1.7111 | 3.9942
NORW | Norwin (TF3) | SW | NORW_11kV_BUS T3 | 11 | 1.5997 | 30.4779 | 1.9656 | 12.4831 | 2.5091 | 1.7032 | 10.8168 | 2.0235 | 12.8511 | 1.7265 | 4.0119 | 0.10257 | 2.0515 | 1.7111 | 3.9942
NOST | North Street | SW | NOST_33kV_BUS 1 | 33 | 7.6314 | 436.1926 | 1.1069 | 21.0897 | 0.56515 | 6.8873 | 131.2205 | 6.342 | 120.8313 | 0.68796 | 2.6591 | 55.2411 | -0.64508 | 0.6875 | 2.6547
NOST | North Street | SW | NOST_33kV_BUS 2 | 33 | 7.6314 | 436.1926 | 1.1069 | 21.0897 | 0.56515 | 6.8873 | 131.2205 | 6.342 | 120.8313 | 0.68796 | 2.6591 | 55.2411 | -0.64508 | 0.6875 | 2.6547
NOST | North Street | SW | NOST_33kV_BUS 3 | 33 | 7.6314 | 436.1926 | 1.1069 | 21.0897 | 0.56515 | 6.8873 | 131.2205 | 6.342 | 120.8313 | 0.68796 | 2.6591 | 55.2411 | -0.64508 | 0.6875 | 2.6547
NOST | North Street | SW | NOST_11kV_BUS 1 | 11 | 9.8383 | 187.445 | 2.232 | 14.1752 | 1.1512 | 9.0857 | 57.702 | 7.9624 | 50.5684 | 0.09684 | 0.70355 | 9.0204 | 0.40809 | 0.09679 | 0.70306
NOST | North Street | SW | NOST_11kV_BUS 2 | 11 | 9.8383 | 187.445 | 2.232 | 14.1752 | 1.1512 | 9.0857 | 57.702 | 7.9624 | 50.5684 | 0.09684 | 0.70355 | 9.0204 | 0.40809 | 0.09679 | 0.70306
NOST | North Street | SW | NOST_11kV_BUS 3 | 11 | 9.8383 | 187.445 | 2.232 | 14.1752 | 1.1512 | 9.0857 | 57.702 | 7.9624 | 50.5684 | 0.09684 | 0.70355 | 9.0204 | 0.40809 | 0.09679 | 0.70306
NOST | North Street | SW | NOST_11kV_BUS 4 | 11 | 9.8383 | 187.445 | 2.232 | 14.1752 | 1.1512 | 9.0857 | 57.702 | 7.9624 | 50.5684 | 0.09684 | 0.70355 | 9.0204 | 0.40809 | 0.09679 | 0.70306
NOST | North Street | SW | NOST_11kV_BUS 5 | 11 | 9.8383 | 187.445 | 2.232 | 14.1752 | 1.1512 | 9.0857 | 57.702 | 7.9624 | 50.5684 | 0.09684 | 0.70355 | 9.0204 | 0.40809 | 0.09679 | 0.70306
NOST | North Street | SW | NOST_11kV_BUS 6 | 11 | 9.8383 | 187.445 | 2.232 | 14.1752 | 1.1512 | 9.0857 | 57.702 | 7.9624 | 50.5684 | 0.09684 | 0.70355 | 9.0204 | 0.40809 | 0.09679 | 0.70306
NOST | North Street | SW | NOST_11kV_BUS 7 | 11 | 9.8383 | 187.445 | 2.232 | 14.1752 | 1.1512 | 9.0857 | 57.702 | 7.9624 | 50.5684 | 0.09684 | 0.70355 | 9.0204 | 0.40809 | 0.09679 | 0.70306
OAKE | Oakey | SW | OAKE_33kV_BUS 1 | 33 | 14.9159 | 852.5569 | 1.1581 | 22.0654 | 0.58113 | 13.2046 | 251.5811 | 12.6249 | 240.5356 | 0.0784 | 1.403 | 54.074 | -0.52275 | 0.09279 | 1.403
OAKE | Oakey | SW | OAKE_33kV_BUS 2 | 33 | 14.9159 | 852.5569 | 1.1581 | 22.0654 | 0.58113 | 13.2046 | 251.5811 | 12.6249 | 240.5356 | 0.0784 | 1.403 | 54.074 | -0.52275 | 0.09279 | 1.403
OAKE | Oakey | SW | OAKE_11kV_BUS 1 | 11 | 15.5941 | 297.108 | 17.6425 | 112.0447 | 20.3146 | 16.8737 | 107.1622 | 16.9218 | 107.4676 | 0.0236 | 0.4474 | 0.01489 | 0.29151 | 0.0252 | 0.4474
OAKE | Oakey | SW | OAKE_11kV_BUS 2 | 11 | 15.5941 | 297.108 | 17.6425 | 112.0447 | 20.3146 | 16.8737 | 107.1622 | 16.9218 | 107.4676 | 0.0236 | 0.4474 | 0.01489 | 0.29151 | 0.0252 | 0.4474
OAKY | Oakey T189 (TF1) | SW | OAKY_33kV_TEF T3 | 33 | 14.9159 | 852.5569 | 1.1581 | 22.0654 | 0.58113 | 13.2046 | 251.5811 | 12.6249 | 240.5356 | 0.0784 | 1.403 | 54.074 | -0.52275 | 0.09279 | 1.403
OAKY | Oakey T189 (TF2) | SW | OAKY_33kV_TEF T4 | 33 | 14.9159 | 852.5569 | 1.1581 | 22.0654 | 0.58113 | 13.2046 | 251.5811 | 12.6249 | 240.5356 | 0.0784 | 1.403 | 54.074 | -0.52275 | 0.09279 | 1.403
OONN | Oonoonba | NQ | OONN_66kV_BUS 1 | 66 | 11.9721 | 1368.6001 | 9.5409 | 363.5568 | 7.9239 | 10.9991 | 419.1219 | 11.205 | 426.966 | 1.155 | 3.3051 | 1.7988 | 5.9153 | 1.1366 | 3.3086
OONN | Oonoonba | NQ | OONN_66kV_BUS 2 | 66 | 11.9721 | 1368.6001 | 9.5409 | 363.5568 | 7.9239 | 10.9991 | 419.1219 | 11.205 | 426.966 | 1.155 | 3.3051 | 1.7988 | 5.9153 | 1.1366 | 3.3086
OONN | Oonoonba | NQ | OONN_11kV_BUS 1 | 11 | 15.7006 | 299.1365 | 16.893 | 107.2851 | 18.2758 | 16.0805 | 102.1249 | 16.6783 | 105.9214 | 0.04327 | 0.44284 | 0.01118 | 0.35103 | 0.04275 | 0.44294
OONN | Oonoonba | NQ | OONN_11kV_BUS 2 | 11 | 15.7006 | 299.1365 | 16.893 | 107.2851 | 18.2758 | 16.0805 | 102.1249 | 16.6783 | 105.9214 | 0.04327 | 0.44284 | 0.01118 | 0.35103 | 0.04275 | 0.44294
OONN | Oonoonba | NQ | OONN_11kV_BUS 3 | 11 | 15.7006 | 299.1365 | 16.893 | 107.2851 | 18.2758 | 16.0805 | 102.1249 | 16.6783 | 105.9214 | 0.04327 | 0.44284 | 0.01118 | 0.35103 | 0.04275 | 0.44294
OWAN | Owanyilla | WB | OWAN_66kV_BUS | 66 | 3.813 | 435.884 | 2.7091 | 103.2289 | 2.1043 | 3.368 | 128.3393 | 3.5506 | 135.2966 | 3.6647 | 10.365 | 5.4373 | 23.8513 | 3.6383 | 10.4226
OWAN | Owanyilla | WB | OWAN_11kV_BUS | 11 | 4.3285 | 82.4686 | 4.6106 | 29.2813 | 4.9357 | 4.4239 | 28.0956 | 4.5494 | 28.8928 | 0.19943 | 1.6017 | 0.09763 | 1.3138 | 0.1987 | 1.6033
OWAN | Owanyilla | WB | OWAN_11kV_TEF T1 | 11 | 4.3285 | 82.4686 | 4.6106 | 29.2813 | 4.9357 | 4.4239 | 28.0956 | 4.5494 | 28.8928 | 0.19943 | 1.6017 | 0.09763 | 1.3138 | 0.1987 | 1.6033
OWAN | Owanyilla | WB | OWAN_11kV_TEF T2 | 11 | 4.8143 | 91.7246 | 5.1645 | 32.799 | 5.5739 | 4.9283 | 31.2992 | 5.098 | 32.3767 | 0.15917 | 1.4425 | 0.05737 | 1.1545 | 0.15843 | 1.4441
PACO | Pacific Coal | WB | PACO_66kV_BUS | 66 | 12.3056 | 1406.7158 | 10.7133 | 408.2314 | 9.5016 | 11.5792 | 441.2278 | 11.7403 | 447.366 | 0.93149 | 3.2768 | 1.2195 | 4.7652 | 0.92859 | 3.2842
PAJI | Pajingo | NQ | PAJI_66kV_TEF T1 | 66 | 0.93965 | 107.4169 | 0.67751 | 25.8165 | 0.52413 | 0.78986 | 30.0978 | 0.91475 | 34.8567 | 26.2332 | 36.0785 | 30.7736 | 93.656 | 26.1809 | 36.1812
PAJI | Pajingo | NQ | PAJI_11kV_TEF T1 | 11 | 3.206 | 61.0818 | 3.9166 | 24.8739 | 5.0031 | 3.4452 | 21.88 | 4.0072 | 25.449 | 0.78775 | 2.0317 | 0.05905 | 1.0295 | 0.7863 | 2.0345
PAMP | Pampas | SW | PAMP_33kV_BUS 1 | 33 | 1.6925 | 96.7382 | 0.47223 | 8.9972 | 0.27035 | 1.4444 | 27.5199 | 1.5201 | 28.9622 | 3.7492 | 11.8032 | 0.00576 | 109.49 | 3.6101 | 11.6444
PAMP | Pampas | SW | PAMP_33kV_BUS 2 | 33 | 1.6925 | 96.7382 | 0.47223 | 8.9972 | 0.27035 | 1.4444 | 27.5199 | 1.5201 | 28.9622 | 3.7492 | 11.8032 | 0.00576 | 109.49 | 3.6101 | 11.6444
PAMP | Pampas | SW | PAMP_33kV_BUS 3 | 33 | 1.6925 | 96.7382 | 0.47223 | 8.9972 | 0.27035 | 1.4444 | 27.5199 | 1.5201 | 28.9622 | 3.7492 | 11.8032 | 0.00576 | 109.49 | 3.6101 | 11.6444
PAMP | Pampas | SW | PAMP_33kV_BUS R1 Downstream | 33 | 1.6925 | 96.7382 | 0.47223 | 8.9972 | 0.27035 | 1.4444 | 27.5199 | 1.5201 | 28.9622 | 3.7492 | 11.8032 | 0.00576 | 109.49 | 3.6101 | 11.6444
PAMP | Pampas | SW | PAMP_33kV_BUS R1 Upstream | 33 | 1.8556 | 106.0612 | 1.205 | 22.9582 | 0.88078 | 1.684 | 32.0847 | 1.6708 | 31.8336 | 3.6928 | 10.6751 | 10.052 | 28.0352 | 3.5537 | 10.5162
PAMP | Pampas | SW | PAMP_11kV_BUS ST RONANS | 11 | 3.2754 | 62.4052 | 4.1828 | 26.5644 | 5.7018 | 3.8876 | 24.6897 | 4.1593 | 26.415 | 0.4552 | 2.084 | 0.03862 | 0.77248 | 0.43975 | 2.0663
PAMP | Pampas | SW | PAMP_11kV_BUS T1 | 11 | 3.2754 | 62.4052 | 4.1828 | 26.5644 | 5.7018 | 3.8876 | 24.6897 | 4.1593 | 26.415 | 0.4552 | 2.084 | 0.03862 | 0.77248 | 0.43975 | 2.0663
PAMP | Pampas | SW | PAMP_11kV_BUS T3 | 11 | 3.2754 | 62.4052 | 4.1828 | 26.5644 | 5.7018 | 3.8876 | 24.6897 | 4.1593 | 26.415 | 0.4552 | 2.084 | 0.03862 | 0.77248 | 0.43975 | 2.0663
PAMP | Pampas | SW | PAMP_11kV_BUS YANDILLA | 11 | 3.2754 | 62.4052 | 4.1828 | 26.5644 | 5.7018 | 3.8876 | 24.6897 | 4.1593 | 26.415 | 0.4552 | 2.084 | 0.03862 | 0.77248 | 0.43975 | 2.0663
PAND | Pandoin | CA | PAND_66kV_BUS 1 | 66 | 8.6972 | 994.2223 | 9.5552 | 364.1008 | 10.6647 | 9.269 | 353.1951 | 9.168 | 349.3469 | 0.6934 | 4.7694 | 0.56918 | 3.4489 | 0.69491 | 4.7956
PAND | Pandoin | CA | PAND_66kV_TEF T1 | 66 | 8.6972 | 994.2223 | 9.5552 | 364.1008 | 10.6647 | 9.269 | 353.1951 | 9.168 | 349.3469 | 0.6934 | 4.7694 | 0.56918 | 3.4489 | 0.69491 | 4.7956
PAND | Pandoin | CA | PAND_66kV_TEF T2 | 66 | 8.6972 | 994.2223 | 9.5552 | 364.1008 | 10.6647 | 9.269 | 353.1951 | 9.168 | 349.3469 | 0.6934 | 4.7694 | 0.56918 | 3.4489 | 0.69491 | 4.7956
PAND | Pandoin | CA | PAND_22kV_BUS 1 | 22 | 5.2734 | 200.9451 | 5.6511 | 71.7783 | 6.094 | 5.4611 | 69.3652 | 5.5164 | 70.0675 | 0.19625 | 2.6422 | 0.1192 | 2.1123 | 0.19642 | 2.6452
PAND | Pandoin | CA | PAND_22kV_BUS 2 | 22 | 5.2734 | 200.9451 | 5.6511 | 71.7783 | 6.094 | 5.4611 | 69.3652 | 5.5164 | 70.0675 | 0.19625 | 2.6422 | 0.1192 | 2.1123 | 0.19642 | 2.6452
PAPS | Pajingo Pumps | NQ | PAPS_66kV_TEF T1 | 66 | 1.8765 | 214.5102 | 1.5463 | 58.9224 | 1.3103 | 1.6443 | 62.6569 | 1.8507 | 70.5199 | 10.0993 | 19.924 | 8.9378 | 35.9912 | 10.047 | 20.0267
PARK | Parkhurst | CA | PARK_66kV_BUS | 66 | 9.9606 | 1138.6477 | 10.0317 | 382.2574 | 10.1549 | 10.2419 | 390.2704 | 9.7422 | 371.2261 | 0.7557 | 4.1398 | 1.0799 | 3.9599 | 0.75625 | 4.1646
PARK | Parkhurst | CA | PARK_11kV_BUS 1 | 11 | 18.1572 | 345.9417 | 20.1794 | 128.1564 | 22.7508 | 19.1884 | 121.8626 | 19.6117 | 124.5512 | 0.0344 | 0.38321 | 0.01341 | 0.26822 | 0.03442 | 0.3839
PARK | Parkhurst | CA | PARK_11kV_BUS 2 | 11 | 18.1572 | 345.9417 | 20.1794 | 128.1564 | 22.7508 | 19.1884 | 121.8626 | 19.6117 | 124.5512 | 0.0344 | 0.38321 | 0.01341 | 0.26822 | 0.03442 | 0.3839
PARK | Parkhurst | CA | PARK_11kV_BUS 3 | 11 | 18.1572 | 345.9417 | 20.1794 | 128.1564 | 22.7508 | 19.1884 | 121.8626 | 19.6117 | 124.5512 | 0.0344 | 0.38321 | 0.01341 | 0.26822 | 0.03442 | 0.3839
PEAR | Peter Arlett | NQ | PEAR_66kV_BUS 1 | 66 | 11.8375 | 1353.2101 | 8.9902 | 342.5711 | 7.2392 | 10.8814 | 414.6371 | 10.8726 | 414.3021 | 0.75569 | 3.4593 | 1.4525 | 6.7557 | 0.73771 | 3.4584
PEAR | Peter Arlett | NQ | PEAR_66kV_BUS 2 | 66 | 11.8375 | 1353.2101 | 8.9902 | 342.5711 | 7.2392 | 10.8814 | 414.6371 | 10.8726 | 414.3021 | 0.75569 | 3.4593 | 1.4525 | 6.7557 | 0.73771 | 3.4584
PEAR | Peter Arlett | NQ | PEAR_11kV_BUS 1 | 11 | 9.8716 | 188.0785 | 10.3434 | 65.6894 | 10.861 | 10.0592 | 63.8844 | 10.1967 | 64.7579 | 0.0444 | 0.70629 | 0.02345 | 0.61057 | 0.0439 | 0.70626
PEAR | Peter Arlett | NQ | PEAR_11kV_BUS 2 | 11 | 9.8716 | 188.0785 | 10.3434 | 65.6894 | 10.861 | 10.0592 | 63.8844 | 10.1967 | 64.7579 | 0.0444 | 0.70629 | 0.02345 | 0.61057 | 0.0439 | 0.70626
PECR | Perseverance Creek | SW | PECR_33kV_BUS 1 | 33 | 2.0265 | 115.8302 | 0.82604 | 15.7382 | 0.51216 | 1.684 | 32.0841 | 1.8594 | 35.4256 | 5.3568 | 8.8484 | 9.0139 | 55.8336 | 5.3568 | 8.8445
PECR | Perseverance Creek (TF2) | SW | PECR_11kV_TEF T2 | 11 | 2.9064 | 55.375 | 3.8366 | 24.3657 | 5.082 | 4.4263 | 28.1109 | 2.4482 | 15.5481 | 0.66857 | 2.3092 | 1.2043 | 0.2185 | 0.66857 | 2.3087
PERA | Peranga | SW | PERA_33kV_BUS | 33 | 0.94619 | 54.0819 | 0.43724 | 8.3306 | 0.28311 | 0.85829 | 16.3527 | 0.80365 | 15.3116 | 13.5122 | 17.5531 | 76.9476 | 64.2285 | 13.5266 | 17.5531
PERA | Peranga | SW | PERA_33kV_BUS T1 | 33 | 0.94619 | 54.0819 | 0.43724 | 8.3306 | 0.28311 | 0.85829 | 16.3527 | 0.80365 | 15.3116 | 13.5122 | 17.5531 | 76.9476 | 64.2285 | 13.5266 | 17.5531
PERA | Peranga | SW | PERA_33kV_BUS T3 | 33 | 0.94619 | 54.0819 | 0.43724 | 8.3306 | 0.28311 | 0.85829 | 16.3527 | 0.80365 | 15.3116 | 13.5122 | 17.5531 | 76.9476 | 64.2285 | 13.5266 | 17.5531
PERA | Peranga | SW | PERA_11kV_BUS QUINALOW | 11 | 1.6513 | 31.4616 | 2.0269 | 12.8727 | 2.6029 | 1.7706 | 11.2447 | 2.0839 | 13.2343 | 1.5997 | 3.9168 | 0.09832 | 1.9665 | 1.6013 | 3.9168
PERA | Peranga (TF1) | SW | PERA_11kV_BUS BRYMAROO | 11 | 1.6513 | 31.4616 | 2.0269 | 12.8727 | 2.6029 | 1.7706 | 11.2447 | 2.0839 | 13.2343 | 1.5997 | 3.9168 | 0.09832 | 1.9665 | 1.6013 | 3.9168
PERA | Peranga (TF3) | SW | PERA_11kV_BUS E/GREEN | 11 | 0.64279 | 12.2468 | 0.68852 | 4.3727 | 0.74001 | 0.64334 | 4.0858 | 0.69258 | 4.3985 | 1.9386 | 10.6948 | 0.43722 | 8.7445 | 1.9402 | 10.6948
PIAL | Pialba | WB | PIAL_66kV_BUS 1 | 66 | 3.884 | 444.0048 | 2.6046 | 99.2465 | 1.9809 | 3.492 | 133.0634 | 3.4816 | 132.6667 | 2.456 | 10.5095 | 6.0916 | 25.8303 | 2.4434 | 10.6763
PIAL | Pialba | WB | PIAL_66kV_BUS 2 | 66 | 3.884 | 444.0048 | 2.6046 | 99.2465 | 1.9809 | 3.492 | 133.0634 | 3.4816 | 132.6667 | 2.456 | 10.5095 | 6.0916 | 25.8303 | 2.4434 | 10.6763
PIAL | Pialba | WB | PIAL_11kV_BUS 1 | 11 | 5.401 | 102.9034 | 5.8405 | 37.0921 | 6.3812 | 5.5911 | 35.5083 | 5.7239 | 36.3515 | 0.11473 | 1.2885 | 0.04651 | 0.99652 | 0.11439 | 1.2931
PIAL | Pialba | WB | PIAL_11kV_BUS 2 | 11 | 5.401 | 102.9034 | 5.8405 | 37.0921 | 6.3812 | 5.5911 | 35.5083 | 5.7239 | 36.3515 | 0.11473 | 1.2885 | 0.04651 | 0.99652 | 0.11439 | 1.2931
PINN | Pinnacle | MK | PINN_66kV_BUS 1 | 66 | 1.9781 | 226.1307 | 1.2809 | 48.8075 | 0.9458 | 1.6973 | 64.6742 | 1.848 | 70.4177 | 9.7758 | 18.7999 | 15.5069 | 53.9965 | 9.7691 | 18.9071
PINN | Pinnacle | MK | PINN_66kV_BUS 2 | 66 | 1.9781 | 226.1307 | 1.2809 | 48.8075 | 0.9458 | 1.6973 | 64.6742 | 1.848 | 70.4177 | 9.7758 | 18.7999 | 15.5069 | 53.9965 | 9.7691 | 18.9071
PINN | Pinnacle | MK | PINN_11kV_BUS 1 | 11 | 3.1107 | 59.2666 | 3.3908 | 21.5348 | 3.7278 | 3.1787 | 20.1874 | 3.3686 | 21.3938 | 0.39754 | 2.2103 | 0.12599 | 1.6881 | 0.39736 | 2.2133
PINN | Pinnacle | MK | PINN_11kV_BUS 2 | 11 | 3.1107 | 59.2666 | 3.3908 | 21.5348 | 3.7278 | 3.1787 | 20.1874 | 3.3686 | 21.3938 | 0.39754 | 2.2103 | 0.12599 | 1.6881 | 0.39736 | 2.2133
PINN | Pinnacle | MK | PINN_11kV_BUS 3 | 11 | 3.1107 | 59.2666 | 3.3908 | 21.5348 | 3.7278 | 3.1787 | 20.1874 | 3.3686 | 21.3938 | 0.39754 | 2.2103 | 0.12599 | 1.6881 | 0.39736 | 2.2133
PIRR | Pirrinuan | SW | PIRR_33kV_BUS 1 | 33 | 1.7228 | 98.4687 | 1.0953 | 20.8681 | 0.79658 | 1.4564 | 27.7486 | 1.6272 | 31.0018 | 6.2931 | 10.4127 | 9.2812 | 32.2559 | 6.2943 | 10.4128
PIRR | Pirrinuan (TF1) | SW | PIRR_11kV_BUS 1 | 11 | 0.82858 | 15.7866 | 0.87091 | 5.531 | 0.91724 | 0.83286 | 5.2893 | 0.86996 | 5.525 | 1.0596 | 8.3652 | 0.36041 | 7.2083 | 1.0598 | 8.3653
PIRR | Pirrinuan (TF2) | SW | PIRR_11kV_BUS 2 | 11 | 1.8588 | 35.4154 | 2.1053 | 13.3703 | 2.4133 | 1.8703 | 11.8779 | 2.144 | 13.6165 | 0.92466 | 3.6431 | 0 | 2.4964 | 0.9248 | 3.6431
PIVA | Pioneer Valley T141 | MK | PIVA_66kV_BUS 1 | 66 | 8.368 | 956.5847 | 10.3101 | 392.8675 | 13.6188 | 9.962 | 379.6021 | 9.8998 | 377.232 | 0.53889 | 4.98 | 0.24594 | 2.1094 | 0.51719 | 5.0374
PIVA | Pioneer Valley T141 | MK | PIVA_66kV_BUS 2 | 66 | 8.368 | 956.5847 | 10.3101 | 392.8675 | 13.6188 | 9.962 | 379.6021 | 9.8998 | 377.232 | 0.53889 | 4.98 | 0.24594 | 2.1094 | 0.51719 | 5.0374
PLAN | Planella | MK | PLAN_33kV_BUS 1 | 33 | 2.8568 | 163.2903 | 2.4064 | 45.8487 | 2.0812 | 2.6951 | 51.349 | 2.6704 | 50.8782 | 1.9138 | 7.082 | 3.1502 | 11.0037 | 1.9014 | 7.0961
PLAN | Planella (TF1) | MK | PLAN_11kV_BUS 1 | 11 | 4.2671 | 81.2998 | 5.1074 | 32.4365 | 6.3609 | 4.746 | 30.1412 | 5.0008 | 31.7594 | 0.25417 | 1.6173 | 0.04152 | 0.83042 | 0.25279 | 1.6189
PLAN | Planella (TF2) | MK | PLAN_11kV_BUS 2 | 11 | 4.2712 | 81.3776 | 5.1133 | 32.4738 | 6.37 | 4.7514 | 30.1755 | 5.0067 | 31.7968 | 0.25405 | 1.6157 | 0.04141 | 0.82885 | 0.25268 | 1.6173
PLEY | Pleystowe | MK | PLEY_33kV_BUS 1 | 33 | 4.0464 | 231.2802 | 2.5325 | 48.2504 | 1.8377 | 3.4694 | 66.1014 | 3.7642 | 71.717 | 2.348 | 4.6167 | 3.9177 | 14.0384 | 2.3418 | 4.632
PLEY | Pleystowe | MK | PLEY_33kV_BUS 2 | 33 | 4.0464 | 231.2802 | 2.5325 | 48.2504 | 1.8377 | 3.4694 | 66.1014 | 3.7642 | 71.717 | 2.348 | 4.6167 | 3.9177 | 14.0384 | 2.3418 | 4.632
PLEY | Pleystowe | MK | PLEY_33kV_BUS 3 | 33 | 4.0464 | 231.2802 | 2.5325 | 48.2504 | 1.8377 | 3.4694 | 66.1014 | 3.7642 | 71.717 | 2.348 | 4.6167 | 3.9177 | 14.0384 | 2.3418 | 4.632
PLEY | Pleystowe | MK | PLEY_33kV_BUS 4 | 33 | 4.0464 | 231.2802 | 2.5325 | 48.2504 | 1.8377 | 3.4694 | 66.1014 | 3.7642 | 71.717 | 2.348 | 4.6167 | 3.9177 | 14.0384 | 2.3418 | 4.632
PLEY | Pleystowe | MK | PLEY_11kV_BUS 1 | 11 | 6.292 | 119.8796 | 7.5613 | 48.0208 | 9.4553 | 6.8228 | 43.3305 | 7.5828 | 48.1575 | 0.28885 | 1.0721 | 0.02795 | 0.55909 | 0.28816 | 1.0738
PLEY | Pleystowe | MK | PLEY_11kV_BUS 2 | 11 | 6.292 | 119.8796 | 7.5613 | 48.0208 | 9.4553 | 6.8228 | 43.3305 | 7.5828 | 48.1575 | 0.28885 | 1.0721 | 0.02795 | 0.55909 | 0.28816 | 1.0738
PLEY | Pleystowe | MK | PLEY_11kV_BUS 3 | 11 | 6.292 | 119.8796 | 7.5613 | 48.0208 | 9.4553 | 6.8228 | 43.3305 | 7.5828 | 48.1575 | 0.28885 | 1.0721 | 0.02795 | 0.55909 | 0.28816 | 1.0738
PLEY | Pleystowe | MK | PLEY_11kV_BUS 4 | 11 | 6.292 | 119.8796 | 7.5613 | 48.0208 | 9.4553 | 6.8228 | 43.3305 | 7.5828 | 48.1575 | 0.28885 | 1.0721 | 0.02795 | 0.55909 | 0.28816 | 1.0738
POCU | Port Curtis | CA | POCU_66kV_BUS 1 | 66 | 11.8967 | 1359.9746 | 11.8986 | 453.396 | 11.9516 | 12.0757 | 460.1447 | 11.7152 | 446.4107 | 0.48235 | 3.4902 | 0.65976 | 3.4461 | 0.48232 | 3.5066
POCU | Port Curtis | CA | POCU_66kV_BUS 2 | 66 | 11.8967 | 1359.9746 | 11.8986 | 453.396 | 11.9516 | 12.0757 | 460.1447 | 11.7152 | 446.4107 | 0.48235 | 3.4902 | 0.65976 | 3.4461 | 0.48232 | 3.5066
POCU | Port Curtis | CA | POCU_11kV_BUS A | 11 | 25.3449 | 482.8856 | 2.1827 | 13.8617 | 1.0984 | 22.4773 | 142.7503 | 21.3855 | 135.8161 | 0.02099 | 0.27484 | 9.5326 | 0.17789 | 0.02099 | 0.2753
POCU | Port Curtis | CA | POCU_11kV_BUS B | 11 | 25.3449 | 482.8856 | 2.1827 | 13.8617 | 1.0984 | 22.4773 | 142.7503 | 21.3855 | 135.8161 | 0.02099 | 0.27484 | 9.5326 | 0.17789 | 0.02099 | 0.2753
POVE | Point Vernon | WB | POVE_66kV_BUS 1 | 66 | 3.163 | 361.5788 | 2.0611 | 78.5374 | 1.5421 | 2.8375 | 108.1215 | 2.8277 | 107.7483 | 3.3205 | 12.8303 | 8.7353 | 33.2221 | 3.308 | 12.9971
POVE | Point Vernon | WB | POVE_11kV_BUS 1 | 11 | 12.7617 | 243.1422 | 16.3756 | 103.9993 | 23.0852 | 15.5198 | 98.5639 | 16.4047 | 104.1837 | 0.09979 | 0.53829 | 0.00756 | 0.18189 | 0.09945 | 0.54292
POVE | Point Vernon | WB | POVE_11kV_BUS 2 | 11 | 12.7617 | 243.1422 | 16.3756 | 103.9993 | 23.0852 | 15.5198 | 98.5639 | 16.4047 | 104.1837 | 0.09979 | 0.53829 | 0.00756 | 0.18189 | 0.09945 | 0.54292
POZI | Pozieres | SW | POZI_33kV_BUS 1 | 33 | 1.1663 | 66.6609 | 0.59083 | 11.2568 | 0.38487 | 1.1104 | 21.1567 | 0.93892 | 17.8889 | 9.2496 | 15.4098 | 64.5071 | 35.8085 | 9.2364 | 15.4131
POZI | Pozieres | SW | POZI_33kV_BUS 2 | 33 | 1.1663 | 66.6609 | 0.59083 | 11.2568 | 0.38487 | 1.1104 | 21.1567 | 0.93892 | 17.8889 | 9.2496 | 15.4098 | 64.5071 | 35.8085 | 9.2364 | 15.4131
POZI | Pozieres | SW | POZI_33kV_BUS 3 | 33 | 1.1663 | 66.6609 | 0.59083 | 11.2568 | 0.38487 | 1.1104 | 21.1567 | 0.93892 | 17.8889 | 9.2496 | 15.4098 | 64.5071 | 35.8085 | 9.2364 | 15.4131
POZI | Pozieres | SW | POZI_11kV_BUS 1 | 11 | 2.4082 | 45.8814 | 3.1098 | 19.75 | 4.3631 | 2.8112 | 17.8534 | 3.2117 | 20.397 | 1.0768 | 2.6942 | 0.0491 | 0.98195 | 1.0754 | 2.6945
POZI | Pozieres | SW | POZI_11kV_BUS 2 | 11 | 2.4082 | 45.8814 | 3.1098 | 19.75 | 4.3631 | 2.8112 | 17.8534 | 3.2117 | 20.397 | 1.0768 | 2.6942 | 0.0491 | 0.98195 | 1.0754 | 2.6945
PROS | Proserpine T039 | MK | PROS_66kV_BUS 1 | 66 | 5.6851 | 649.8958 | 7.3428 | 279.7997 | 10.1889 | 6.8534 | 261.1511 | 7.3239 | 279.0765 | 2.0939 | 7.0693 | 0.30795 | 2.4712 | 2.0679 | 6.9911
PROS | Proserpine T039 | MK | PROS_66kV_BUS 2 | 66 | 5.6851 | 649.8958 | 7.3428 | 279.7997 | 10.1889 | 6.8534 | 261.1511 | 7.3239 | 279.0765 | 2.0939 | 7.0693 | 0.30795 | 2.4712 | 2.0679 | 6.9911
PROT | Proston | WB | PROT_66kV_BUS STRUNG | 66 | 0.77463 | 88.5522 | 0.59555 | 22.6936 | 0.47697 | 0.64978 | 24.7598 | 0.76933 | 29.3155 | 39.7309 | 36.7434 | 49.6842 | 93.6022 | 39.7014 | 36.75
PROT | Proston | WB | PROT_11kV_BUS 1 | 11 | 1.3876 | 26.4378 | 1.5188 | 9.6454 | 1.6713 | 1.3834 | 8.7859 | 1.5398 | 9.7791 | 1.628 | 4.7646 | 0.52439 | 3.7439 | 1.6272 | 4.7648
PROT | Proston | WB | PROT_11kV_BUS 2 | 11 | 1.3876 | 26.4378 | 1.5188 | 9.6454 | 1.6713 | 1.3834 | 8.7859 | 1.5398 | 9.7791 | 1.628 | 4.7646 | 0.52439 | 3.7439 | 1.6272 | 4.7648
PURR | Purrawunda | SW | PURR_33kV_BUS 1 | 33 | 1.5096 | 86.2858 | 0.61447 | 11.7073 | 0.37673 | 1.4051 | 26.7717 | 1.2312 | 23.4576 | 6.1594 | 12.4441 | 64.4983 | 42.7317 | 6.1589 | 12.4397
PURR | Purrawunda | SW | PURR_33kV_BUS 2 | 33 | 1.5096 | 86.2858 | 0.61447 | 11.7073 | 0.37673 | 1.4051 | 26.7717 | 1.2312 | 23.4576 | 6.1594 | 12.4441 | 64.4983 | 42.7317 | 6.1589 | 12.4397
PURR | Purrawunda | SW | PURR_33kV_BUS 3 | 33 | 1.5096 | 86.2858 | 0.61447 | 11.7073 | 0.37673 | 1.4051 | 26.7717 | 1.2312 | 23.4576 | 6.1594 | 12.4441 | 64.4983 | 42.7317 | 6.1589 | 12.4397
PURR | Purrawunda (TF1) | SW | PURR_11kV_BUS 1 | 11 | 2.3352 | 44.4918 | 2.8057 | 17.8186 | 3.5015 | 2.5338 | 16.0916 | 2.809 | 17.8398 | 0.75994 | 2.8939 | 0.07556 | 1.5112 | 0.75989 | 2.8934
PURR | Purrawunda (TF2) | SW | PURR_11kV_BUS 2 | 11 | 2.338 | 44.5456 | 2.8098 | 17.8447 | 3.5079 | 2.5374 | 16.1148 | 2.8133 | 17.8668 | 0.75975 | 2.8902 | 0.07538 | 1.5075 | 0.7597 | 2.8897
QUIL | Quilpie | SW | QUIL_66kV_BUS | 66 | 0.16118 | 18.4258 | 0.07788 | 2.9675 | 0.05112 | 0.13703 | 5.2214 | 0.1466 | 5.5863 | 141.0517 | 218.4776 | 387.2997 | 1032.3941 | 140.9877 | 218.5935
QUIL | Quilpie (TF1) | SW | QUIL_11kV_BUS T1 | 11 | 0.7612 | 14.5028 | 1.0283 | 6.5308 | 1.5759 | 0.95998 | 6.0967 | 1.0906 | 6.9261 | 4.027 | 8.247 | 0.10891 | 2.1782 | 4.0252 | 8.2502
QUIL | Quilpie (TF2) | SW | QUIL_11kV_BUS T2 | 11 | 0.76241 | 14.5259 | 1.0306 | 6.545 | 1.5814 | 0.96273 | 6.1142 | 1.0933 | 6.9437 | 4.0262 | 8.2312 | 0.10812 | 2.1624 | 4.0244 | 8.2344
RAGL | Raglan | CA | RAGL_66kV_TEF T1 | 66 | 1.2433 | 142.1295 | 0.84464 | 32.185 | 0.63377 | 1.0482 | 39.9404 | 1.1915 | 45.4035 | 21.0754 | 26.314 | 31.4905 | 76.736 | 21.0768 | 26.3398
RAGL | Raglan | CA | RAGL_66kV_TEF T2 | 66 | 1.2433 | 142.1295 | 0.84464 | 32.185 | 0.63377 | 1.0482 | 39.9404 | 1.1915 | 45.4035 | 21.0754 | 26.314 | 31.4905 | 76.736 | 21.0768 | 26.3398
RAGL | Raglan | CA | RAGL_22kV_TEF T1 | 22 | 2.0986 | 79.9658 | 2.5551 | 32.4538 | 3.2421 | 2.2357 | 28.3966 | 2.6196 | 33.2729 | 2.5841 | 6.136 | 0.24239 | 3.2123 | 2.5842 | 6.1389
RAGL | Raglan | CA | RAGL_22kV_TEF T2 | 22 | 2.0986 | 79.9658 | 2.5551 | 32.4538 | 3.2421 | 2.2357 | 28.3966 | 2.6196 | 33.2729 | 2.5841 | 6.136 | 0.24239 | 3.2123 | 2.5842 | 6.1389
RAPS | RAAF Power Station | NQ | RAPS_11kV_BUS 1 | 11 | 9.0302 | 172.0476 | 8.8068 | 55.9308 | 8.5471 | 9.5775 | 60.8254 | 8.1706 | 51.89 | 0.19867 | 0.74768 | 0.41697 | 0.7402 | 0.18388 | 0.75353
RASM | Rasmussen | NQ | RASM_66kV_BUS 1 | 66 | 9.3114 | 1064.4339 | 6.5498 | 249.5804 | 5.0484 | 8.4015 | 320.1413 | 8.5022 | 323.9756 | 1.1227 | 4.3593 | 2.2449 | 9.9504 | 1.1016 | 4.3615
RASM | Rasmussen | NQ | RASM_66kV_BUS 2 | 66 | 9.3114 | 1064.4339 | 6.5498 | 249.5804 | 5.0484 | 8.4015 | 320.1413 | 8.5022 | 323.9756 | 1.1227 | 4.3593 | 2.2449 | 9.9504 | 1.1016 | 4.3615
RASM | Rasmussen | NQ | RASM_66kV_BUS 3 | 66 | 9.3114 | 1064.4339 | 6.5498 | 249.5804 | 5.0484 | 8.4015 | 320.1413 | 8.5022 | 323.9756 | 1.1227 | 4.3593 | 2.2449 | 9.9504 | 1.1016 | 4.3615
RASM | Rasmussen | NQ | RASM_11kV_BUS 1 | 11 | 14.3086 | 272.6158 | 15.5492 | 98.7505 | 16.9369 | 14.7986 | 93.9835 | 15.2442 | 96.8134 | 0.04245 | 0.48638 | 0.01191 | 0.37377 | 0.04098 | 0.48431
RASM | Rasmussen | NQ | RASM_11kV_BUS 2 | 11 | 14.3086 | 272.6158 | 15.5492 | 98.7505 | 16.9369 | 14.7986 | 93.9835 | 15.2442 | 96.8134 | 0.04245 | 0.48638 | 0.01191 | 0.37377 | 0.04098 | 0.48431
RAVE | Ravenshoe | FN | RAVE_66kV_BUS 1 | 66 | 1.4196 | 162.2759 | 0.82428 | 31.4092 | 0.58124 | 1.2278 | 46.7863 | 1.2937 | 49.2956 | 11.4012 | 27.2376 | 23.1827 | 90.8217 | 11.136 | 27.4828
RAVE | Ravenshoe | FN | RAVE_22kV_BUS 1 | 22 | 2.7802 | 105.9398 | 3.0741 | 39.0463 | 3.435 | 2.7918 | 35.4605 | 3.1131 | 39.5421 | 1.0775 | 4.9086 | 0.00054 | 3.6254 | 0.97687 | 4.9453
RAVN | Ravenswood | NQ | RAVN_66kV_TEF T1 | 66 | 2.3897 | 273.1835 | 1.5917 | 60.6501 | 1.1854 | 2.0387 | 77.6856 | 2.2613 | 86.1679 | 8.8348 | 15.1524 | 12.7783 | 42.594 | 8.8097 | 15.1653
RAVN | Ravenswood | NQ | RAVN_11kV_TEF T1 | 11 | 2.0545 | 39.1443 | 2.1504 | 13.6567 | 2.255 | 2.0713 | 13.1543 | 2.141 | 13.597 | 0.57503 | 3.3513 | 0.32962 | 2.9304 | 0.57433 | 3.3516
RGSS | Ravenswood Gold | NQ | RGSS_66kV_BUS 1 | 66 | 2.2996 | 262.8826 | 1.5298 | 58.2927 | 1.1382 | 1.9582 | 74.6178 | 2.1787 | 83.0182 | 9.3374 | 15.6539 | 13.4387 | 44.3563 | 9.3122 | 15.6671
RICH | Richmond | NQ | RICH_66kV_BUS 1 | 66 | 0.52441 | 59.9485 | 0.60686 | 23.1243 | 0.73708 | 0.53435 | 20.3615 | 0.62697 | 23.8909 | 31.5562 | 73.4356 | 4.406 | 46.7521 | 31.814 | 75.6252
RICH | Richmond | NQ | RICH_66kV_BUS 2 | 66 | 0.52441 | 59.9485 | 0.60686 | 23.1243 | 0.73708 | 0.53435 | 20.3615 | 0.62697 | 23.8909 | 31.5562 | 73.4356 | 4.406 | 46.7521 | 31.814 | 75.6252
RICH | Richmond | NQ | RICH_33kV_BUS 1 | 33 | 0.68312 | 39.0454 | 0.84628 | 16.1239 | 1.1342 | 0.77434 | 14.7532 | 0.85916 | 16.3692 | 8.5112 | 29.4755 | 0.58786 | 12.6622 | 8.5757 | 30.0229
RICH | Richmond | NQ | RICH_33kV_BUS 2 | 33 | 0.68312 | 39.0454 | 0.84628 | 16.1239 | 1.1342 | 0.77434 | 14.7532 | 0.85916 | 16.3692 | 8.5112 | 29.4755 | 0.58786 | 12.6622 | 8.5757 | 30.0229
RICH | Richmond | NQ | RICH_33kV_BUS 3 | 33 | 0.68312 | 39.0454 | 0.84628 | 16.1239 | 1.1342 | 0.77434 | 14.7532 | 0.85916 | 16.3692 | 8.5112 | 29.4755 | 0.58786 | 12.6622 | 8.5757 | 30.0229
ROEA | Roma East | SW | ROEA_33kV_BUS 1 | 33 | 3.9213 | 224.1355 | 3.4289 | 65.3295 | 3.0565 | 3.6696 | 69.9155 | 3.7685 | 71.8004 | 1.8123 | 5.028 | 2.2063 | 7.3052 | 1.7963 | 5.057
ROEA | Roma East | SW | ROEA_33kV_BUS 2 | 33 | 3.9213 | 224.1355 | 3.4289 | 65.3295 | 3.0565 | 3.6696 | 69.9155 | 3.7685 | 71.8004 | 1.8123 | 5.028 | 2.2063 | 7.3052 | 1.7963 | 5.057
ROEA | Roma East | SW | ROEA_11kV_BUS 1 | 11 | 5.4238 | 103.3373 | 6.3853 | 40.5522 | 7.7708 | 5.8819 | 37.3553 | 6.2987 | 40.002 | 0.23674 | 1.2661 | 0.03537 | 0.70743 | 0.23496 | 1.2693
ROEA | Roma East | SW | ROEA_11kV_BUS 2 | 11 | 5.4238 | 103.3373 | 6.3853 | 40.5522 | 7.7708 | 5.8819 | 37.3553 | 6.2987 | 40.002 | 0.23674 | 1.2661 | 0.03537 | 0.70743 | 0.23496 | 1.2693
ROGL | Rockhampton T023 | CA | ROGL_66kV_BUS 4 | 66 | 12.088 | 1381.8425 | 14.3183 | 545.5992 | 17.7153 | 13.828 | 526.9188 | 13.5667 | 516.9616 | 0.41444 | 3.4427 | 0.28522 | 1.8002 | 0.41563 | 3.4684
ROGL | Rockhampton T023 (TF1) | CA | ROGL_11kV_BUS LH | 11 | 17.3862 | 331.2509 | 18.881 | 119.9107 | 20.6966 | 18.171 | 115.401 | 18.3555 | 116.5731 | 0.02519 | 0.40103 | 0.01367 | 0.30539 | 0.02522 | 0.40174
ROGL | Rockhampton T023 (TF2) | CA | ROGL_11kV_BUS RH | 11 | 17.3862 | 331.2509 | 18.881 | 119.9107 | 20.6966 | 18.171 | 115.401 | 18.3555 | 116.5731 | 0.02519 | 0.40103 | 0.01367 | 0.30539 | 0.02522 | 0.40174
ROLE | Rolleston | CA | ROLE_132kV_TEF T1 | 132 | 1.3427 | 306.9799 | 1.536 | 117.0559 | 1.7889 | 1.3906 | 105.9772 | 1.5396 | 117.3301 | 13.9122 | 60.8662 | 1.442 | 39.3619 | 13.9322 | 60.8702
ROLE | Rolleston | CA | ROLE_66kV_BUS 1 | 66 | 2.1089 | 241.0798 | 2.6912 | 102.5473 | 3.7128 | 2.5154 | 95.8491 | 2.69 | 102.502 | 3.6244 | 19.5425 | 0.15475 | 7.0491 | 3.6295 | 19.5435
ROLE | Rolleston | CA | ROLE_66kV_BUS 2 | 66 | 2.1089 | 241.0798 | 2.6912 | 102.5473 | 3.7128 | 2.5154 | 95.8491 | 2.69 | 102.502 | 3.6244 | 19.5425 | 0.15475 | 7.0491 | 3.6295 | 19.5435
ROLE | Rolleston | CA | ROLE_66kV_BUS 3 | 66 | 2.1089 | 241.0798 | 2.6912 | 102.5473 | 3.7128 | 2.5154 | 95.8491 | 2.69 | 102.502 | 3.6244 | 19.5425 | 0.15475 | 7.0491 | 3.6295 | 19.5435
ROLE | Rolleston (TF 1) | CA | ROLE_22kV_BUS 1 | 22 | 4.4824 | 170.8019 | 4.9904 | 63.3862 | 5.5899 | 5.1263 | 65.1131 | 4.4138 | 56.0624 | 0.38645 | 3.093 | 0.849 | 2.055 | 0.38701 | 3.0932
ROLE | Rolleston (TF 2) | CA | ROLE_22kV_BUS 2 | 22 | 4.4824 | 170.8019 | 4.9904 | 63.3862 | 5.5899 | 5.1263 | 65.1131 | 4.4138 | 56.0624 | 0.38645 | 3.093 | 0.849 | 2.055 | 0.38701 | 3.0932
ROLL | Rollingstone | NQ | ROLL_66kV_TEF T1 | 66 | 1.5009 | 171.581 | 1.0389 | 39.5859 | 0.78215 | 1.2456 | 47.4633 | 1.4617 | 55.6984 | 18.6916 | 20.7484 | 24.9091 | 62.309 | 18.6442 | 20.755
ROLL | Rollingstone | NQ | ROLL_11kV_TEF T1 | 11 | 1.7512 | 33.3644 | 1.853 | 11.7681 | 1.9645 | 1.7442 | 11.0768 | 1.8675 | 11.8601 | 0.76012 | 3.9162 | 0.24091 | 3.3399 | 0.7588 | 3.9164
ROMA | Roma T083 | SW | ROMA_66kV_BUS | 66 | 3.1402 | 358.9736 | 3.9749 | 151.4651 | 5.4727 | 3.8137 | 145.3217 | 3.8954 | 148.4333 | 1.7168 | 13.2375 | 0.35045 | 4.8252 | 1.6528 | 13.3535
ROMA | Roma T083 | SW | ROMA_33kV_BUS 1 | 33 | 6.0989 | 348.5977 | 7.6727 | 146.1843 | 10.4436 | 7.2565 | 138.2558 | 7.5825 | 144.4654 | 0.44339 | 3.4077 | 0.02776 | 1.3008 | 0.42738 | 3.4367
ROMA | Roma T083 | SW | ROMA_33kV_BUS 2 | 33 | 6.0989 | 348.5977 | 7.6727 | 146.1843 | 10.4436 | 7.2565 | 138.2558 | 7.5825 | 144.4654 | 0.44339 | 3.4077 | 0.02776 | 1.3008 | 0.42738 | 3.4367
ROMA | Roma T083 (TF1) | SW | ROMA_132kV_BUS 1 | 132 | 3.5702 | 816.2558 | 4.2197 | 321.5867 | 5.2481 | 3.8618 | 294.3062 | 4.2229 | 321.8292 | 6.1335 | 22.6661 | 0.88811 | 12.3916 | 5.8774 | 23.1304
ROMA | Roma T083 (TF2) | SW | ROMA_132kV_BUS 2 | 132 | 3.5702 | 816.2558 | 4.2197 | 321.5867 | 5.2481 | 3.8618 | 294.3062 | 4.2229 | 321.8292 | 6.1335 | 22.6661 | 0.88811 | 12.3916 | 5.8774 | 23.1304
ROPL | Ross Plains | NQ | ROPL_66kV_BUS 1 | 66 | 11.3614 | 1298.7794 | 8.3758 | 319.1591 | 6.6251 | 10.388 | 395.8376 | 10.3867 | 395.7857 | 0.82905 | 3.595 | 1.6832 | 7.4522 | 0.81067 | 3.5937
ROPL | Ross Plains | NQ | ROPL_66kV_BUS 2 | 66 | 11.3614 | 1298.7794 | 8.3758 | 319.1591 | 6.6251 | 10.388 | 395.8376 | 10.3867 | 395.7857 | 0.82905 | 3.595 | 1.6832 | 7.4522 | 0.81067 | 3.5937
ROPL | Ross Plains (TF1) | NQ | ROPL_11kV_BUS 1 | 11 | 7.5566 | 143.9729 | 7.8429 | 49.8093 | 8.1508 | 7.6677 | 48.6964 | 7.7513 | 49.2273 | 0.06469 | 0.92221 | 0.04167 | 0.82235 | 0.06418 | 0.92218
ROPL | Ross Plains (TF2) | NQ | ROPL_11kV_BUS 2 | 11 | 7.286 | 138.8164 | 7.5517 | 47.9595 | 7.8366 | 7.3882 | 46.9211 | 7.4668 | 47.4206 | 0.06459 | 0.95664 | 0.04156 | 0.85678 | 0.06408 | 0.95661
ROSE | ROSE Rosella (TF1) | MK | ROSE_33kV_BUS 1 | 33 | 3.6049 | 206.0462 | 2.182 | 41.5725 | 1.5638 | 3.1324 | 59.6812 | 3.2973 | 62.8212 | 2.0706 | 5.4326 | 4.0309 | 16.7549 | 2.0698 | 5.4446
ROSE | ROSE Rosella (TF1) | MK | ROSE_11kV_BUS 1 | 11 | 3.0817 | 58.7136 | 3.3944 | 21.5572 | 3.7773 | 3.1878 | 20.2453 | 3.3484 | 21.2654 | 0.31221 | 2.2454 | 0.08215 | 1.6417 | 0.31212 | 2.2467
ROSE | ROSE Rosella (TF2) | MK | ROSE_33kV_BUS 2 | 33 | 2.8218 | 161.2878 | 1.7506 | 33.353 | 1.2638 | 2.3979 | 45.6869 | 2.6389 | 50.2773 | 3.4612 | 6.5714 | 5.2743 | 20.6144 | 3.4588 | 6.5968
ROSE | ROSE Rosella (TF2) | MK | ROSE_11kV_BUS 2 | 11 | 2.8823 | 54.9158 | 3.2304 | 20.516 | 3.6718 | 2.9732 | 18.8823 | 3.2179 | 20.4364 | 0.46704 | 2.3783 | 0.08247 | 1.6482 | 0.46679 | 2.3811
ROSO | Rockhampton South | CA | ROSO_66kV_TEF T1 | 66 | 10.0184 | 1145.2553 | 9.8872 | 376.7523 | 9.8165 | 10.0583 | 383.2735 | 9.8463 | 375.1952 | 0.83725 | 4.0993 | 1.0178 | 4.2056 | 0.83849 | 4.125
ROSO | Rockhampton South | CA | ROSO_66kV_TEF T2 | 66 | 10.0184 | 1145.2553 | 9.8872 | 376.7523 | 9.8165 | 10.0583 | 383.2735 | 9.8463 | 375.1952 | 0.83725 | 4.0993 | 1.0178 | 4.2056 | 0.83849 | 4.125
ROSO | Rockhampton South (TF1) | CA | ROSO_11kV_BUS LH | 11 | 11.0733 | 210.9752 | 11.7873 | 74.8593 | 12.614 | 11.3878 | 72.3222 | 11.5617 | 73.4267 | 0.05228 | 0.62872 | 0.02902 | 0.51485 | 0.05231 | 0.62943
ROSO | Rockhampton South (TF2) | CA | ROSO_11kV_BUS RH | 11 | 10.1646 | 193.6617 | 10.7622 | 68.3493 | 11.4463 | 10.4193 | 66.1713 | 10.5748 | 67.159 | 0.05028 | 0.68545 | 0.02703 | 0.57158 | 0.05032 | 0.68616
ROSS | H013 Ross | NQ | ROSS_132kV_BUS 2 | 132 | 20.2176 | 4622.3692 | 22.5013 | 1714.8308 | 25.4605 | 21.7992 | 1661.3255 | 21.4669 | 1635.996 | 0.56758 | 4.1074 | 0.44209 | 2.8365 | 0.52598 | 4.1269
ROSS | H013 Ross | NQ | ROSS_132kV_BUS 3 | 132 | 20.2176 | 4622.3692 | 22.5013 | 1714.8308 | 25.4605 | 21.7992 | 1661.3255 | 21.4669 | 1635.996 | 0.56758 | 4.1074 | 0.44209 | 2.8365 | 0.52598 | 4.1269
ROSS | H013 Ross | NQ | ROSS_132kV_BUS 4 | 132 | 20.2176 | 4622.3692 | 22.5013 | 1714.8308 | 25.4605 | 21.7992 | 1661.3255 | 21.4669 | 1635.996 | 0.56758 | 4.1074 | 0.44209 | 2.8365 | 0.52598 | 4.1269
ROST | Rocky Street | WB | ROST_66kV_TEF T1 | 66 | 6.3788 | 729.1922 | 6.179 | 235.4499 | 6.0443 | 6.2551 | 238.3509 | 6.3084 | 240.3836 | 1.4311 | 6.4139 | 1.4035 | 7.0109 | 1.3974 | 6.4829
ROST | Rocky Street | WB | ROST_66kV_TEF T2 | 66 | 6.3788 | 729.1922 | 6.179 | 235.4499 | 6.0443 | 6.2551 | 238.3509 | 6.3084 | 240.3836 | 1.4311 | 6.4139 | 1.4035 | 7.0109 | 1.3974 | 6.4829
ROST | Rocky Street | WB | ROST_11kV_BUS 1 | 11 | 11.535 | 219.7703 | 12.7966 | 81.2696 | 14.413 | 12.1345 | 77.0644 | 12.4844 | 79.2865 | 0.05772 | 0.60293 | 0.01796 | 0.42476 | 0.05678 | 0.60484
ROST | Rocky Street | WB | ROST_11kV_BUS 2 | 11 | 11.535 | 219.7703 | 12.7966 | 81.2696 | 14.413 | 12.1345 | 77.0644 | 12.4844 | 79.2865 | 0.05772 | 0.60293 | 0.01796 | 0.42476 | 0.05678 | 0.60484
ROWE | Roma West | SW | ROWE_33kV_BUS 1 | 33 | 2.6041 | 148.8469 | 1.9527 | 37.2044 | 1.5589 | 2.2798 | 43.4355 | 2.4846 | 47.338 | 3.8944 | 7.043 | 5.2174 | 15.3467 | 3.8784 | 7.072
ROWE | Roma West | SW | ROWE_33kV_BUS 2 | 33 | 2.6041 | 148.8469 | 1.9527 | 37.2044 | 1.5589 | 2.2798 | 43.4355 | 2.4846 | 47.338 | 3.8944 | 7.043 | 5.2174 | 15.3467 | 3.8784 | 7.072
ROWE | Roma West (TF1) | SW | ROWE_11kV_BUS 1 | 11 | 2.0904 | 39.8271 | 2.2829 | 14.4985 | 2.514 | 2.1361 | 13.5661 | 2.269 | 14.4102 | 0.65811 | 3.2766 | 0.2254 | 2.494 | 0.65633 | 3.2798
ROWE | Roma West (TF2) | SW | ROWE_11kV_BUS 2 | 11 | 2.0904 | 39.8271 | 2.2829 | 14.4985 | 2.514 | 2.1361 | 13.5661 | 2.269 | 14.4102 | 0.65811 | 3.2766 | 0.2254 | 2.494 | 0.65633 | 3.2798
RYWU | Rywung (Regulated) | SW | RYWU_33kV_BUS R1 Downstream | 33 | 1.0008 | 57.2013 | 0.76656 | 14.6049 | 0.60617 | 0.81315 | 15.4926 | 1.0128 | 19.2956 | 16.6465 | 12.7074 | 19.3757 | 37.4712 | 16.6184 | 12.7208
RYWU | Rywung (Unregulated) | SW | RYWU_33kV_BUS R1 Upstream | 33 | 1.0287 | 58.7997 | 0.7871 | 14.9963 | 0.62021 | 0.8295 | 15.804 | 1.0453 | 19.9161 | 16.6016 | 11.809 | 19.3286 | 36.5692 | 16.5735 | 11.8224
SAGE | St. George | SW | SAGE_66kV_BUS 1 | 66 | 0.42278 | 48.3302 | 0.5879 | 22.4022 | 0.96352 | 0.57969 | 22.089 | 0.62946 | 23.9858 | 39.2277 | 91.0545 | 0.98039 | 16.3977 | 39.1637 | 91.1702
SAGE | St. George | SW | SAGE_66kV_BUS 2 | 66 | 0.42278 | 48.3302 | 0.5879 | 22.4022 | 0.96352 | 0.57969 | 22.089 | 0.62946 | 23.9858 | 39.2277 | 91.0545 | 0.98039 | 16.3977 | 39.1637 | 91.1702
SAGE | St. George | SW | SAGE_66kV_BUS 3 | 66 | 0.42278 | 48.3302 | 0.5879 | 22.4022 | 0.96352 | 0.57969 | 22.089 | 0.62946 | 23.9858 | 39.2277 | 91.0545 | 0.98039 | 16.3977 | 39.1637 | 91.1702
SAGE | St. George (TF1) | SW | SAGE_33kV_BUS 1 | 33 | 0.77106 | 44.072 | 1.1044 | 21.0425 | 1.9465 | 1.1516 | 21.9412 | 1.2083 | 23.0209 | 9.9319 | 25.3015 | 0.1516 | 2.6684 | 9.9159 | 25.3304
SAGE | St. George (TF2) | SW | SAGE_33kV_BUS 2 | 33 | 0.77106 | 44.072 | 1.1044 | 21.0425 | 1.9465 | 1.1516 | 21.9412 | 1.2083 | 23.0209 | 9.9319 | 25.3015 | 0.1516 | 2.6684 | 9.9159 | 25.3304
SAGT | St. George Town | SW | SAGT_33kV_BUS | 33 | 0.67147 | 38.3796 | 0.82784 | 15.7725 | 1.0797 | 0.78153 | 14.8901 | 0.80511 | 15.3395 | 14.1682 | 27.8116 | 5.3444 | 12.4296 | 14.1522 | 27.8405
SAGT | St. George Town (TF1) | SW | SAGT_11kV_BUS ALFRED ST EAST | 11 | 1.3295 | 25.3304 | 1.6974 | 10.7802 | 2.3387 | 1.5448 | 9.8105 | 1.7319 | 10.9989 | 1.6689 | 4.9826 | 0.09462 | 1.8924 | 1.6671 | 4.9858
SAGT | St. George Town (TF2) | SW | SAGT_11kV_BUS ALFRED ST WEST | 11 | 1.2936 | 24.6463 | 1.6387 | 10.4074 | 2.2273 | 1.4869 | 9.4428 | 1.6671 | 10.5875 | 1.6764 | 5.1337 | 0.10218 | 2.0436 | 1.6746 | 5.1369
SAGT | St. George Town (TF3) | SW | SAGT_11kV_BUS SCOTT ST | 11 | 1.3295 | 25.3304 | 1.6974 | 10.7802 | 2.3387 | 1.5448 | 9.8105 | 1.7319 | 10.9989 | 1.6689 | 4.9826 | 0.09462 | 1.8924 | 1.6671 | 4.9858
SARI | Sarina | MK | SARI_33kV_BUS 1 | 33 | 5.0405 | 288.103 | 3.0492 | 58.0955 | 2.228 | 4.3479 | 82.8385 | 4.5564 | 86.8119 | 1.4777 | 3.8864 | 3.0214 | 11.8355 | 1.522 | 3.9989
SARI | Sarina | MK | SARI_33kV_BUS 2 | 33 | 5.0405 | 288.103 | 3.0492 | 58.0955 | 2.228 | 4.3479 | 82.8385 | 4.5564 | 86.8119 | 1.4777 | 3.8864 | 3.0214 | 11.8355 | 1.522 | 3.9989
SARI | Sarina (TF1) | MK | SARI_11kV_BUS 1 | 11 | 8.9529 | 170.5759 | 7.6478 | 48.5703 | 7.6205 | 8.0972 | 51.4242 | 8.4534 | 53.6862 | 0.12486 | 0.77025 | 0.05146 | 1.0577 | 0.11161 | 0.89728
SARI | Sarina (TF2) | MK | SARI_11kV_BUS 2 | 11 | 4.1993 | 80.0078 | 4.6012 | 29.2215 | 5.1287 | 4.333 | 27.5179 | 4.5503 | 28.8982 | 0.22502 | 1.6483 | 0.06082 | 1.2165 | 0.22994 | 1.6608
SAUN | Saunders | NQ | SAUN_66kV_TEF T1 | 66 | 4.867 | 556.3708 | 3.5192 | 134.0987 | 2.7355 | 4.1999 | 160.0393 | 4.6585 | 177.5126 | 4.4026 | 7.4019 | 5.7923 | 17.8249 | 4.3552 | 7.4085
SAUN | Saunders | NQ | SAUN_11kV_TEF T1 | 11 | 3.7548 | 71.5391 | 3.9073 | 24.8148 | 4.0713 | 3.7717 | 23.9536 | 3.9 | 24.7683 | 0.22244 | 1.8472 | 0.10015 | 1.6416 | 0.22113 | 1.8474
SHUT | Shutehaven | MK | SHUT_66kV_TEF T1 | 66 | 2.2716 | 259.6742 | 1.6545 | 63.0438 | 1.2899 | 1.9813 | 75.4977 | 2.1639 | 82.4566 | 7.8485 | 16.7001 | 9.9895 | 38.2443 | 7.8047 | 16.6039
SHUT | Shutehaven | MK | SHUT_22kV_TEF T1 | 22 | 3.5609 | 135.687 | 4.2962 | 54.5698 | 5.3778 | 3.883 | 49.3209 | 4.2931 | 54.5295 | 0.95593 | 3.8055 | 0.08395 | 1.9507 | 0.95106 | 3.7948
SKIA | Skid 'A' (Mt Bassett) | MK | SKIA_33kV_TEF T1 | 33 | 7.5968 | 434.217 | 6.2482 | 119.044 | 5.3228 | 6.9945 | 133.2632 | 7.1795 | 136.7878 | 0.90798 | 2.6051 | 1.2745 | 4.3545 | 0.90719 | 2.6171
SKIA | Skid 'A' (Mt Bassett) | MK | SKIA_11kV_TEF T1 | 11 | 3.323 | 63.3121 | 3.4845 | 22.1295 | 3.6607 | 3.3066 | 20.9995 | 3.5106 | 22.2951 | 0.22193 | 2.0905 | 0.00242 | 1.8156 | 0.22184 | 2.0919
SKIE | Skid 'E' (Chinchilla) | SW | SKIE_33kV_TEF T1 | 33 | 5.9891 | 342.3244 | 5.3972 | 102.8308 | 4.8997 | 5.4509 | 103.8539 | 6.0047 | 114.4045 | 1.0219 | 3.3469 | 0.54136 | 4.658 | 0.9938 | 3.3603
SKIE | Skid 'E' (Chinchilla) | SW | SKIE_11kV_TEF T1 | 11 | 3.1964 | 60.9004 | 3.3908 | 21.5346 | 3.6083 | 3.2029 | 20.3413 | 3.4017 | 21.6038 | 0.23459 | 2.173 | 0.00121 | 1.8156 | 0.23146 | 2.1745
SKIF | Skid 'F' (Broxburn) | SW | BROX_AB13920 | 33 | 1.9363 | 110.6742 | 1.289 | 24.5592 | 0.94735 | 1.6733 | 31.8799 | 1.834 | 34.9417 | 5.2738 | 9.4534 | 7.9985 | 26.4215 | 5.1347 | 9.2945
SKIF | Skid 'F' (Broxburn) | SW | F2620 COPPS HILL | 11 | 3.193 | 60.8355 | 3.9382 | 25.0112 | 5.0535 | 3.5378 | 22.4679 | 3.952 | 25.0987 | 0.64969 | 2.0894 | 0.06371 | 0.98692 | 0.63423 | 2.0718
SKIJ | Skid J | MK | SKIJ_66kV_TEF T1 | 66 | 8.1053 | 926.5579 | 9.9703 | 379.9198 | 13.1411 | 9.3488 | 356.2364 | 9.8476 | 375.2422 | 0.93616 | 5.0864 | 0.13286 | 2.2164 | 0.90247 | 5.1554
SKIJ | Skid J | MK | SKIJ_11kV_BUS 1 | 11 | 6.0643 | 115.5404 | 6.3221 | 40.1505 | 6.6136 | 6.1779 | 39.235 | 6.2298 | 39.5648 | 0.0838 | 1.149 | 0.05779 | 1.0077 | 0.08286 | 1.1509
SOBL | South Blackwater | CA | SOBL_22kV_TEF T1 | 22 | 1.5701 | 59.8297 | 1.7665 | 22.4378 | 2.0143 | 1.6232 | 20.617 | 1.7586 | 22.3368 | 2.1024 | 8.6468 | 0.55518 | 5.9555 | 2.1042 | 8.6428
SOBL | South Blackwater (ex 6014) | CA | SOBL_66kV_BUS 1 | 66 | 1.5003 | 171.5079 | 0.9734 | 37.0916 | 0.71673 | 1.2894 | 49.134 | 1.4045 | 53.5206 | 13.9248 | 24.2208 | 23.5611 | 70.0993 | 13.941 | 24.1851
SOBL | South Blackwater (ex 6014) | CA | SOBL_66kV_BUS 2 | 66 | 1.7869 | 204.2736 | 1.0793 | 41.1283 | 0.77239 | 1.5865 | 60.4555 | 1.605 | 61.159 | 6.1262 | 22.6429 | 16.3157 | 67.6926 | 6.1423 | 22.6071
SOBL | South Blackwater (ex 6061) | CA | SOBL_66kV_BUS 3 | 66 | 1.5003 | 171.5079 | 0.9734 | 37.0916 | 0.71673 | 1.2894 | 49.134 | 1.4045 | 53.5206 | 13.9248 | 24.2208 | 23.5611 | 70.0993 | 13.941 | 24.1851
SOBL | South Blackwater (ex 6061) | CA | SOBL_66kV_BUS 4 | 66 | 1.7869 | 204.2736 | 1.0793 | 41.1283 | 0.77239 | 1.5865 | 60.4555 | 1.605 | 61.159 | 6.1262 | 22.6429 | 16.3157 | 67.6926 | 6.1423 | 22.6071
SOBU | South Bundaberg | WB | SOBU_66kV_BUS 1 | 66 | 4.9931 | 570.7849 | 4.1209 | 157.0275 | 3.5406 | 4.6616 | 177.6312 | 4.6503 | 177.201 | 2.1569 | 8.1136 | 3.4813 | 13.1828 | 2.1297 | 8.2151
SOBU | South Bundaberg | WB | SOBU_66kV_BUS 2 | 66 | 4.9931 | 570.7849 | 4.1209 | 157.0275 | 3.5406 | 4.6616 | 177.6312 | 4.6503 | 177.201 | 2.1569 | 8.1136 | 3.4813 | 13.1828 | 2.1297 | 8.2151
SOBU | South Bundaberg | WB | SOBU_66kV_BUS 3 | 66 | 4.9931 | 570.7849 | 4.1209 | 157.0275 | 3.5406 | 4.6616 | 177.6312 | 4.6503 | 177.201 | 2.1569 | 8.1136 | 3.4813 | 13.1828 | 2.1297 | 8.2151
SOBU | South Bundaberg | WB | SOBU_11kV_BUS 1 | 11 | 10.3041 | 196.3199 | 11.605 | 73.7019 | 13.3367 | 10.9192 | 69.3461 | 11.3407 | 72.0231 | 0.08316 | 0.67291 | 0.02325 | 0.44753 | 0.08241 | 0.67573
SOBU | South Bundaberg | WB | SOBU_11kV_BUS 2 | 11 | 10.3041 | 196.3199 | 11.605 | 73.7019 | 13.3367 | 10.9192 | 69.3461 | 11.3407 | 72.0231 | 0.08316 | 0.67291 | 0.02325 | 0.44753 | 0.08241 | 0.67573
SOKO | South Kolan | WB | SOKO_66kV_BUS LOWER A | 66 | 4.7722 | 545.5413 | 3.9032 | 148.732 | 3.3244 | 4.4633 | 170.073 | 4.4222 | 168.5078 | 1.7601 | 8.6057 | 3.1051 | 14.2466 | 1.7351 | 8.6832
SOKO | South Kolan | WB | SOKO_66kV_BUS LOWER B | 66 | 4.7722 | 545.5413 | 3.9032 | 148.732 | 3.3244 | 4.4633 | 170.073 | 4.4222 | 168.5078 | 1.7601 | 8.6057 | 3.1051 | 14.2466 | 1.7351 | 8.6832
SOKO | South Kolan | WB | SOKO_66kV_BUS UPPER A | 66 | 4.7722 | 545.5413 | 3.9032 | 148.732 | 3.3244 | 4.4633 | 170.073 | 4.4222 | 168.5078 | 1.7601 | 8.6057 | 3.1051 | 14.2466 | 1.7351 | 8.6832
SOKO | South Kolan | WB | SOKO_66kV_BUS UPPER B | 66 | 4.7722 | 545.5413 | 3.9032 | 148.732 | 3.3244 | 4.4633 | 170.073 | 4.4222 | 168.5078 | 1.7601 | 8.6057 | 3.1051 | 14.2466 | 1.7351 | 8.6832
SOKO | South Kolan | WB | SOKO_11kV_BUS 1 | 11 | 4.5495 | 86.6796 | 4.7998 | 30.4826 | 5.0862 | 4.6598 | 29.5935 | 4.7161 | 29.9516 | 0.13334 | 1.5299 | 0.08445 | 1.2908 | 0.13264 | 1.532
SOKO | South Kolan | WB | SOKO_11kV_BUS 2 | 11 | 4.5495 | 86.6796 | 4.7998 | 30.4826 | 5.0862 | 4.6598 | 29.5935 | 4.7161 | 29.9516 | 0.13334 | 1.5299 | 0.08445 | 1.2908 | 0.13264 | 1.532
SOMA | South Mackay | MK | SOMA_33kV_BUS 1 | 33 | 6.5097 | 372.0768 | 4.6132 | 87.8934 | 3.5816 | 5.8587 | 111.6234 | 5.9558 | 113.4731 | 0.91644 | 3.0863 | 1.794 | 6.9532 | 0.91565 | 3.0984
SOMA | South Mackay | MK | SOMA_33kV_BUS 2 | 33 | 6.5097 | 372.0768 | 4.6132 | 87.8934 | 3.5816 | 5.8587 | 111.6234 | 5.9558 | 113.4731 | 0.91644 | 3.0863 | 1.794 | 6.9532 | 0.91565 | 3.0984
SOMA | South Mackay (TF1) | MK | SOMA_11kV_BUS 1 | 11 | 6.0514 | 115.2956 | 6.7338 | 42.7657 | 7.5956 | 6.3386 | 40.2556 | 6.6002 | 41.9169 | 0.14193 | 1.1457 | 0.0401 | 0.80275 | 0.14184 | 1.147
SOMA | South Mackay (TF2) | MK | SOMA_11kV_BUS 2 | 11 | 6.0514 | 115.2956 | 6.7338 | 42.7657 | 7.5956 | 6.3386 | 40.2556 | 6.6002 | 41.9169 | 0.14193 | 1.1457 | 0.0401 | 0.80275 | 0.14184 | 1.147
SOTO | South Toowoomba T043 | SW | SOTO_33kV_BUS 1 | 33 | 16.4532 | 940.4246 | 1.1584 | 22.0706 | 0.57989 | 14.5631 | 277.4651 | 13.9845 | 266.4408 | 0.08049 | 1.2714 | 54.0848 | -0.50571 | 0.08065 | 1.267
SOTO | South Toowoomba T043 | SW | SOTO_33kV_BUS 2 | 33 | 16.4532 | 940.4246 | 1.1584 | 22.0706 | 0.57989 | 14.5631 | 277.4651 | 13.9845 | 266.4408 | 0.08049 | 1.2714 | 54.0848 | -0.50571 | 0.08065 | 1.267
SOTO | South Toowoomba T043 | SW | SOTO_33kV_BUS 3 | 33 | 16.4532 | 940.4246 | 1.1584 | 22.0706 | 0.57989 | 14.5631 | 277.4651 | 13.9845 | 266.4408 | 0.08049 | 1.2714 | 54.0848 | -0.50571 | 0.08065 | 1.267
SOTO | South Toowoomba T043 | SW | SOTO_11kV_BUS 1 | 11 | 13.0365 | 248.3788 | 2.2798 | 14.4786 | 1.1565 | 11.869 | 75.3782 | 10.7218 | 68.0925 | 0.02864 | 0.53519 | 9.0197 | 0.39392 | 0.02866 | 0.53469
SOTO | South Toowoomba T043 | SW | SOTO_11kV_BUS 2 | 11 | 13.0365 | 248.3788 | 2.2798 | 14.4786 | 1.1565 | 11.869 | 75.3782 | 10.7218 | 68.0925 | 0.02864 | 0.53519 | 9.0197 | 0.39392 | 0.02866 | 0.53469
SOTO | South Toowoomba T043 | SW | SOTO_11kV_BUS 3 | 11 | 13.0365 | 248.3788 | 2.2798 | 14.4786 | 1.1565 | 11.869 | 75.3782 | 10.7218 | 68.0925 | 0.02864 | 0.53519 | 9.0197 | 0.39392 | 0.02866 | 0.53469
SOTO | South Toowoomba T043 (TF1) | SW | SOTO_110kV_BUS 1 | 110 | 17.5588 | 3345.405 | 16.7686 | 1064.9459 | 15.8566 | 17.2558 | 1095.8885 | 17.1599 | 1089.7997 | 0.38603 | 3.9604 | 0.49747 | 4.5642 | 0.38779 | 3.9107
SOTO | South Toowoomba T043 (TF2) | SW | SOTO_110kV_BUS 2 | 110 | 17.5588 | 3345.405 | 16.7686 | 1064.9459 | 15.8566 | 17.2558 | 1095.8885 | 17.1599 | 1089.7997 | 0.38603 | 3.9604 | 0.49747 | 4.5642 | 0.38779 | 3.9107
SOWC | South Walker Switching | MK | Dragline | 66 | 1.9413 | 221.9257 | 1.2868 | 49.0318 | 0.9633 | 1.7587 | 67.0156 | 1.7369 | 66.1857 | 4.6692 | 21.0803 | 13.2814 | 52.8766 | 4.6748 | 21.1131
STAM | Stamford | NQ | STAM_66kV_TEF T1 | 66 | 0.71621 | 81.8735 | 0.54249 | 20.6717 | 0.44833 | 0.63094 | 24.0421 | 0.67137 | 25.5826 | 24.7931 | 53.0134 | 33.8772 | 107.931 | 25.0509 | 55.203
STAM | Stamford | NQ | STAM_33kV_TEF T1 | 33 | 0.14959 | 8.5503 | 0.15447 | 2.943 | 0.1603 | 0.15055 | 2.8683 | 0.15383 | 2.9309 | 15.1355 | 139.2809 | 8.9372 | 126.0276 | 15.2 | 139.8283
STAN | Stanthorpe | SW | STAN_110kV_BUS | 110 | 1.2958 | 246.8801 | 1.8257 | 115.9474 | 3.0724 | 1.8023 | 114.463 | 1.9977 | 126.8726 | 28.9425 | 45.4939 | 0.61829 | 7.8385 | 28.8209 | 45.5241
STAN | Stanthorpe | SW | STAN_33kV_BUS 1 | 33 | 2.8031 | 160.217 | 1.0114 | 19.2695 | 0.56311 | 2.6758 | 50.9807 | 2.188 | 41.6876 | 3.2411 | 6.7389 | 54.0555 | 0.74803 | 3.2278 | 6.7422
STAN | Stanthorpe | SW | STAN_33kV_BUS 2 | 33 | 2.8031 | 160.217 | 1.0114 | 19.2695 | 0.56311 | 2.6758 | 50.9807 | 2.188 | 41.6876 | 3.2411 | 6.7389 | 54.0555 | 0.74803 | 3.2278 | 6.7422
STTO | Stanthorpe Town | SW | STTO_33kV_BUS 1 | 33 | 2.3592 | 134.8459 | 0.9357 | 17.8275 | 0.53807 | 2.2655 | 43.163 | 1.8339 | 34.9403 | 4.0862 | 7.8894 | 55.6425 | 5.3286 | 4.073 | 7.8926
STTO | Stanthorpe Town | SW | STTO_33kV_BUS 2 | 33 | 2.3592 | 134.8459 | 0.9357 | 17.8275 | 0.53807 | 2.2655 | 43.163 | 1.8339 | 34.9403 | 4.0862 | 7.8894 | 55.6425 | 5.3286 | 4.073 | 7.8926
STTO | Stanthorpe Town | SW | STTO_11kV_BUS 1 | 11 | 4.5005 | 85.7453 | 5.686 | 36.111 | 7.686 | 5.1477 | 32.6922 | 5.7813 | 36.716 | 0.48395 | 1.4751 | 0.02993 | 0.59855 | 0.48248 | 1.4755
STTO | Stanthorpe Town | SW | STTO_11kV_BUS 2 | 11 | 4.5005 | 85.7453 | 5.686 | 36.111 | 7.686 | 5.1477 | 32.6922 | 5.7813 | 36.716 | 0.48395 | 1.4751 | 0.02993 | 0.59855 | 0.48248 | 1.4755
STUA | Stuart | NQ | STUA_66kV_BUS 1 | 66 | 18.518 | 2116.8935 | 20.2268 | 770.7445 | 22.2826 | 19.4941 | 742.8265 | 19.5608 | 745.3664 | 0.37608 | 2.2321 | 0.25648 | 1.6704 | 0.35712 | 2.2352
STUA | Stuart | NQ | STUA_66kV_BUS 2 | 66 | 18.518 | 2116.8935 | 20.2268 | 770.7445 | 22.2826 | 19.4941 | 742.8265 | 19.5608 | 745.3664 | 0.37608 | 2.2321 | 0.25648 | 1.6704 | 0.35712 | 2.2352
STUA | Stuart | NQ | STUA_11kV_BUS A | 11 | 18.455 | 351.6155 | 19.5279 | 124.019 | 20.7356 | 18.9359 | 120.259 | 19.1638 | 121.7067 | 0.02055 | 0.37798 | 0.0101 | 0.31598 | 0.02002 | 0.37807
STUA | Stuart | NQ | STUA_11kV_BUS B | 11 | 18.455 | 351.6155 | 19.5279 | 124.019 | 20.7356 | 18.9359 | 120.259 | 19.1638 | 121.7067 | 0.02055 | 0.37798 | 0.0101 | 0.31598 | 0.02002 | 0.37807
STUA | Stuart | NQ | STUA_11kV_BUS C | 11 | 18.455 | 351.6155 | 19.5279 | 124.019 | 20.7356 | 18.9359 | 120.259 | 19.1638 | 121.7067 | 0.02055 | 0.37798 | 0.0101 | 0.31598 | 0.02002 | 0.37807
TANB | Tanby | CA | TANB_66kV_BUS 1 | 66 | 3.1352 | 358.4003 | 2.0391 | 77.7009 | 1.504 | 2.7341 | 104.1844 | 2.9049 | 110.693 | 5.6815 | 12.1023 | 10.1816 | 33.6157 | 5.6109 | 12.0905
TANB | Tanby | CA | TANB_66kV_BUS 2 | 66 | 3.1352 | 358.4003 | 2.0391 | 77.7009 | 1.504 | 2.7341 | 104.1844 | 2.9049 | 110.693 | 5.6815 | 12.1023 | 10.1816 | 33.6157 | 5.6109 | 12.0905
TANB | Tanby | CA | TANB_22kV_BUS 1 | 22 | 4.403 | 167.7777 | 5.1608 | 65.5516 | 6.1485 | 4.6766 | 59.401 | 5.1246 | 65.0918 | 0.68812 | 3.0978 | 0.0732 | 1.8252 | 0.66799 | 3.0722
TANB | Tanby | CA | TANB_22kV_BUS 2 | 22 | 4.403 | 167.7777 | 5.1608 | 65.5516 | 6.1485 | 4.6766 | 59.401 | 5.1246 | 65.0918 | 0.68812 | 3.0978 | 0.0732 | 1.8252 | 0.66799 | 3.0722
TANB | Tanby | CA | TANB_22kV_BUS 3 | 22 | 4.403 | 167.7777 | 5.1608 | 65.5516 | 6.1485 | 4.6766 | 59.401 | 5.1246 | 65.0918 | 0.68812 | 3.0978 | 0.0732 | 1.8252 | 0.66799 | 3.0722
TARA | Tara | SW | TARA_33kV_BUS | 33 | 0.38124 | 21.7908 | 0.2811 | 5.3557 | 0.21817 | 0.31209 | 5.9462 | 0.38001 | 7.2402 | 40.9159 | 36.7226 | 49.5139 | 107.6219 | 40.9172 | 36.7227
TARA | Tara (TF1) | SW | TARA_11kV_BUS FRY ST(1) | 11 | 0.70867 | 13.502 | 0.87738 | 5.5721 | 1.1346 | 0.73997 | 4.6994 | 0.92166 | 5.8533 | 4.7735 | 8.6262 | 0.22729 | 4.5459 | 4.7736 | 8.6262
TARA | Tara (TF2) | SW | TARA_11kV_BUS BILTON ST(1) | 11 | 0.54325 | 10.3504 | 0.63181 | 4.0126 | 0.7471 | 0.54308 | 3.449 | 0.65333 | 4.1492 | 4.936 | 11.8759 | 0.38978 | 7.7956 | 4.9361 | 11.8759
TARE | Tara Regulator (Regulated) | SW | TARE_33kV_R Upstream | 33 | 0.42608 | 24.3535 | 0.31683 | 6.0363 | 0.24737 | 0.35006 | 6.6695 | 0.42469 | 8.0915 | 36.1041 | 33.4135 | 43.0808 | 94.7226 | 36.1054 | 33.4136
TARE | Tara Regulator (Unregulated) | SW | TARE_33kV_R Downstream | 33 | 0.42608 | 24.3535 | 0.31683 | 6.0363 | 0.24737 | 0.35006 | 6.6695 | 0.42469 | 8.0915 | 36.1041 | 33.4135 | 43.0808 | 94.7226 | 36.1054 | 33.4136
TARO | Tarong | WB | TARO_66kV_BUS 1 | 66 | 16.9421 | 1936.7421 | 18.1984 | 693.4504 | 19.7185 | 17.4935 | 666.5925 | 17.8344 | 679.5814 | 0.10174 | 2.4723 | 0.01129 | 1.9546 | 0.09883 | 2.4796
TARO | Tarong | WB | TARO_66kV_BUS 2 | 66 | 16.9421 | 1936.7421 | 18.1984 | 693.4504 | 19.7185 | 17.4935 | 666.5925 | 17.8344 | 679.5814 | 0.10174 | 2.4723 | 0.01129 | 1.9546 | 0.09883 | 2.4796
TECR | H063 Teebar Creek | WB | TECR_132kV_BUS 1 | 132 | 10.5588 | 2414.068 | 11.5049 | 876.7909 | 12.7827 | 11.1064 | 846.4177 | 11.1601 | 850.5174 | 0.91113 | 7.8878 | 0.5878 | 5.8695 | 0.8684 | 7.9761
TECR | H063 Teebar Creek | WB | TECR_132kV_BUS 2 | 132 | 10.5588 | 2414.068 | 11.5049 | 876.7909 | 12.7827 | 11.1064 | 846.4177 | 11.1601 | 850.5174 | 0.91113 | 7.8878 | 0.5878 | 5.8695 | 0.8684 | 7.9761
THAL | Thalanga | NQ | THAL_66kV_TEF T1 | 66 | 1.6061 | 183.6065 | 1.3379 | 50.9827 | 1.1598 | 1.4362 | 54.7272 | 1.5592 | 59.4138 | 11.5118 | 23.4209 | 12.0815 | 39.8433 | 11.4535 | 23.9419
THAL | Thalanga | NQ | THAL_11kV_TEF T1 | 11 | 2.837 | 54.0517 | 3.1294 | 19.8745 | 3.5067 | 2.916 | 18.5191 | 3.111 | 19.7575 | 0.40556 | 2.4288 | 0.08405 | 1.765 | 0.40394 | 2.4433
THEO | Theodore | CA | THEO_66kV_TEF T1 | 66 | 1.346 | 153.8707 | 0.80395 | 30.6348 | 0.57442 | 1.1961 | 45.5768 | 1.202 | 45.8005 | 7.213 | 30.2941 | 20.6085 | 91.7498 | 7.22 | 30.3934
THEO | Theodore | CA | THEO_66kV_TEF T2 | 66 | 1.346 | 153.8707 | 0.80395 | 30.6348 | 0.57442 | 1.1961 | 45.5768 | 1.202 | 45.8005 | 7.213 | 30.2941 | 20.6085 | 91.7498 | 7.22 | 30.3934
THEO | Theodore | CA | THEO_66kV_TEF T3 | 66 | 1.346 | 153.8707 | 0.80395 | 30.6348 | 0.57442 | 1.1961 | 45.5768 | 1.202 | 45.8005 | 7.213 | 30.2941 | 20.6085 | 91.7498 | 7.22 | 30.3934
THEO | Theodore (TF1) | CA | THEO_22kV_TEF T1 | 22 | 2.533 | 96.5218 | 3.2005 | 40.652 | 4.3551 | 3.0262 | 38.4383 | 3.153 | 40.0489 | 0.96598 | 5.4307 | 0.16431 | 2.0553 | 0.96675 | 5.4417
THEO | Theodore (TF2) | CA | THEO_22kV_TEF T2 | 22 | 2.533 | 96.5218 | 3.2005 | 40.652 | 4.3551 | 3.0262 | 38.4383 | 3.153 | 40.0489 | 0.96598 | 5.4307 | 0.16431 | 2.0553 | 0.96675 | 5.4417
THEO | Theodore (TF3) | CA | THEO_22kV_TEF T3 | 22 | 2.533 | 96.5218 | 3.2005 | 40.652 | 4.3551 | 3.0262 | 38.4383 | 3.153 | 40.0489 | 0.96598 | 5.4307 | 0.16431 | 2.0553 | 0.96675 | 5.4417
TIDH | Tinaroo Dam Hydro | FN | TIDH_22kV_TEF T1 | 22 | 0.87704 | 33.4198 | 0.66258 | 8.4159 | 0.51861 | 0.70756 | 8.9873 | 0.88759 | 11.2739 | 12.8312 | 9.4418 | 15.135 | 29.4614 | 12.8204 | 9.454
TIER | Tieri | CA | TIER_66kV_BUS 1 | 66 | 3.9349 | 449.8157 | 2.7524 | 104.8817 | 2.1119 | 3.4627 | 131.947 | 3.6704 | 139.8619 | 4.7581 | 9.5308 | 8.0563 | 23.1121 | 4.736 | 9.5373
TIER | Tieri | CA | TIER_66kV_BUS 2 | 66 | 3.9349 | 449.8157 | 2.7524 | 104.8817 | 2.1119 | 3.4627 | 131.947 | 3.6704 | 139.8619 | 4.7581 | 9.5308 | 8.0563 | 23.1121 | 4.736 | 9.5373
TIER | Tieri | CA | TIER_22kV_BUS 1 | 22 | 3.2327 | 123.1819 | 3.5416 | 44.984 | 3.9119 | 3.3148 | 42.1031 | 3.5126 | 44.6166 | 0.767 | 4.2535 | 0.23833 | 3.1945 | 0.76455 | 4.2542
TIER | Tieri | CA | TIER_22kV_BUS 2 | 22 | 3.2327 | 123.1819 | 3.5416 | 44.984 | 3.9119 | 3.3148 | 42.1031 | 3.5126 | 44.6166 | 0.767 | 4.2535 | 0.23833 | 3.1945 | 0.76455 | 4.2542
TOMA | Townsville Marina SS (MF07) | NQ | TOMA_11kV_BUS A | 11 | 8.4968 | 161.8853 | 8.9365 | 56.7541 | 9.4145 | 8.9703 | 56.969 | 8.4939 | 53.9436 | 0.17672 | 0.80297 | 0.21528 | 0.66934 | 0.17619 | 0.80302
TOMA | Townsville Marina SS (TOPO08) | NQ | TOMA_11kV_BUS B | 11 | 7.6937 | 146.584 | 8.0448 | 51.0911 | 8.4278 | 7.9721 | 50.6297 | 7.7942 | 49.4997 | 0.14106 | 0.89699 | 0.15279 | 0.77466 | 0.14053 | 0.89704
TOPO | Townsville Port | NQ | TOPO_66kV_BUS 1A | 66 | 13.6871 | 1564.642 | 14.2453 | 542.8175 | 14.83 | 13.7194 | 522.7785 | 14.2454 | 542.8232 | 0.71622 | 2.9775 | 0.4434 | 2.673 | 0.69708 | 2.9793
TOPO | Townsville Port | NQ | TOPO_66kV_BUS 1B | 66 | 13.6871 | 1564.642 | 14.2453 | 542.8175 | 14.83 | 13.7194 | 522.7785 | 14.2454 | 542.8232 | 0.71622 | 2.9775 | 0.4434 | 2.673 | 0.69708 | 2.9793
TOPO | Townsville Port | CA | TOPO_66kV_BUS 2 | 66 | 13.6871 | 1564.642 | 14.2453 | 542.8175 | 14.83 | 13.7194 | 522.7785 | 14.2454 | 542.8232 | 0.71622 | 2.9775 | 0.4434 | 2.673 | 0.69708 | 2.9793
TOPO | Townsville Port | NQ | TOPO_11kV_BUS 3 | 11 | 8.8402 | 168.429 | 9.1637 | 58.1975 | 9.5116 | 8.9628 | 56.9213 | 9.0624 | 57.5541 | 0.05518 | 0.78832 | 0.0353 | 0.70575 | 0.05464 | 0.78837
TOPO | Townsville Port (TF1) | NQ | TOPO_11kV_BUS 1 | 11 | 8.8402 | 168.429 | 9.1643 | 58.2012 | 9.5128 | 8.9631 | 56.9231 | 9.0628 | 57.5564 | 0.05518 | 0.78832 | 0.03528 | 0.70561 | 0.05464 | 0.78837
TOPO | Townsville Port (TF2) | NQ | TOPO_11kV_BUS 2 | 11 | 8.8402 | 168.429 | 9.1637 | 58.1975 | 9.5116 | 8.9628 | 56.9213 | 9.0624 | 57.5541 | 0.05518 | 0.78832 | 0.0353 | 0.70575 | 0.05464 | 0.78837
TOPS | Townsville Power Station | NQ | TOPS_66kV_TEF T1 | 66 | 8.9166 | 1019.2996 | 8.9634 | 341.5498 | 9.0026 | 8.7021 | 331.5959 | 9.1694 | 349.4022 | 0.86683 | 4.6203 | 0.37611 | 4.6261 | 0.80306 | 4.6326
TORQ | Torquay | WB | TORQ_66kV_BUS 1 | 66 | 4.0363 | 461.414 | 2.6674 | 101.6433 | 2.0182 | 3.6147 | 137.7369 | 3.6129 | 137.6691 | 2.3735 | 10.1106 | 5.9008 | 25.5171 | 2.3699 | 10.3001
TORQ | Torquay | WB | TORQ_66kV_BUS 2 | 66 | 4.0363 | 461.414 | 2.6674 | 101.6433 | 2.0182 | 3.6147 | 137.7369 | 3.6129 | 137.6691 | 2.3735 | 10.1106 | 5.9008 | 25.5171 | 2.3699 | 10.3001
TORQ | Torquay | WB | TORQ_66kV_BUS 3 | 66 | 4.0363 | 461.414 | 2.6674 | 101.6433 | 2.0182 | 3.6147 | 137.7369 | 3.6129 | 137.6691 | 2.3735 | 10.1106 | 5.9008 | 25.5171 | 2.3699 | 10.3001
TORQ | Torquay | WB | TORQ_11kV_BUS 1 | 11 | 14.2312 | 271.1405 | 17.4136 | 110.5913 | 23.1169 | 16.4573 | 104.518 | 17.2298 | 109.4242 | 0.07626 | 0.48497 | 0.01122 | 0.21062 | 0.07706 | 0.49674
TORQ | Torquay | WB | TORQ_11kV_BUS 2 | 11 | 14.2312 | 271.1405 | 17.4136 | 110.5913 | 23.1169 | 16.4573 | 104.518 | 17.2298 | 109.4242 | 0.07626 | 0.48497 | 0.01122 | 0.21062 | 0.07706 | 0.49674
TORR | Torrington T116 | SW | TORR_33kV_BUS 1 | 33 | 15.0518 | 860.3242 | 1.1683 | 22.2582 | 0.58384 | 13.3478 | 254.3102 | 12.764 | 243.187 | 0.10164 | 1.3889 | 53.6064 | -4.1364 | 0.10118 | 1.3845
TORR | Torrington T116 | SW | TORR_33kV_BUS 2 | 33 | 15.0518 | 860.3242 | 1.1683 | 22.2582 | 0.58384 | 13.3478 | 254.3102 | 12.764 | 243.187 | 0.10164 | 1.3889 | 53.6064 | -4.1364 | 0.10118 | 1.3845
TORR | Torrington T116 (TF1) | SW | TORR_11kV_BUS 1 | 11 | 13.2174 | 251.8246 | 2.275 | 14.4484 | 1.1553 | 12.024 | 76.3624 | 10.8804 | 69.0995 | 0.03788 | 0.52726 | 9.0266 | 0.37294 | 0.03783 | 0.52677
TORR | Torrington T116 (TF2) | SW | TORR_110kV_TEF T2 | 110 | 8.7161 | 1660.6425 | 7.9105 | 502.3818 | 7.1954 | 8.1823 | 519.6465 | 8.567 | 544.0788 | 1.2425 | 7.9193 | 0.79052 | 10.5052 | 1.2435 | 7.8699
TORR | Torrington T116 (TF2) | SW | TORR_11kV_BUS 2 | 11 | 13.2174 | 251.8246 | 2.275 | 14.4484 | 1.1553 | 12.024 | 76.3624 | 10.8804 | 69.0995 | 0.03788 | 0.52726 | 9.0266 | 0.37294 | 0.03783 | 0.52677
TULL | Tully T048 | FN | TULL_22kV_BUS 1 | 22 | 8.0739 | 307.6566 | 6.5887 | 83.6881 | 5.5641 | 7.5221 | 95.544 | 7.5296 | 95.6385 | 0.12338 | 1.7261 | 0.18419 | 2.8952 | 0.11307 | 1.7265
TULL | Tully T048 | FN | TULL_22kV_BUS 2 | 22 | 8.0739 | 307.6566 | 6.5887 | 83.6881 | 5.5641 | 7.5221 | 95.544 | 7.5296 | 95.6385 | 0.12338 | 1.7261 | 0.18419 | 2.8952 | 0.11307 | 1.7265
TUNG | Tungamull | CA | TUNG_66kV_TEF T1 | 66 | 3.5553 | 406.4293 | 2.3631 | 90.0477 | 1.7654 | 3.1185 | 118.8287 | 3.288 | 125.2904 | 4.8168 | 10.7608 | 8.734 | 28.4305 | 4.7798 | 10.7643
TUNG | Tungamull | CA | TUNG_22kV_TEF T1 | 22 | 0.59055 | 22.5029 | 0.60116 | 7.6358 | 0.61214 | 0.59314 | 7.5339 | 0.59889 | 7.6069 | 3.0179 | 23.4663 | 2.4827 | 22.2707 | 3.0137 | 23.4667
TURK | Turkinje T055 (TF1) | FN | TURK_66kV_BUS 1 | 66 | 5.2666 | 602.0533 | 6.5892 | 251.0833 | 8.9412 | 6.3144 | 240.6118 | 6.4416 | 245.4579 | 1.1153 | 7.8802 | 0.25669 | 3.0626 | 1.0418 | 7.9877
TURK | Turkinje T055 (TF1) | FN | TURK_66kV_BUS 2 | 66 | 5.2666 | 602.0533 | 6.5892 | 251.0833 | 8.9412 | 6.3144 | 240.6118 | 6.4416 | 245.4579 | 1.1153 | 7.8802 | 0.25669 | 3.0626 | 1.0418 | 7.9877
TWCE | Toowoomba Central | SW | TWCE_110kV_TEF T1 | 110 | 16.8306 | 3206.6576 | 16.1738 | 1027.1724 | 15.39 | 16.5525 | 1051.2253 | 16.5185 | 1049.0627 | 0.55444 | 4.1142 | 0.65479 | 4.6604 | 0.55619 | 4.0645
TWCE | Toowoomba Central | SW | TWCE_110kV_TEF T2 | 110 | 16.8312 | 3206.7642 | 16.1742 | 1027.1985 | 15.3903 | 16.5531 | 1051.2619 | 16.5189 | 1049.0892 | 0.5543 | 4.1141 | 0.65473 | 4.6604 | 0.55606 | 4.0644
TWCE | Toowoomba Central | SW | TWCE_11kV_BUS 1 | 11 | 9.9114 | 188.8375 | 2.2469 | 14.2698 | 1.2665 | 8.5909 | 54.5595 | 8.6285 | 54.7986 | 0.02192 | 0.7046 | 0 | 7.92 | 0.02193 | 0.70411
TWCE | Toowoomba Central | SW | TWCE_11kV_BUS 2 | 11 | 9.9114 | 188.8375 | 2.2469 | 14.2698 | 1.2665 | 8.5909 | 54.5595 | 8.6285 | 54.7986 | 0.02192 | 0.7046 | 0 | 7.92 | 0.02193 | 0.70411
TWCE | Toowoomba Central | SW | TWCE_11kV_BUS 3 | 11 | 9.8938 | 188.5025 | 2.3209 | 14.7398 | 1.3141 | 8.5769 | 54.4703 | 8.6157 | 54.7173 | 0.0219 | 0.70586 | 0 | 7.62 | 0.02191 | 0.70536
VERM | Vermont | CA | VERM_66kV_BUS | 66 | 3.6189 | 413.6898 | 2.9307 | 111.6731 | 2.4666 | 3.3464 | 127.5141 | 3.3847 | 128.9745 | 2.778 | 11.2446 | 4.3157 | 19.2426 | 2.7842 | 11.2679
VERM | Vermont | CA | VERM_22kV_BUS 1 | 22 | 4.1951 | 159.856 | 4.8082 | 61.0727 | 5.6338 | 4.5048 | 57.2185 | 4.6865 | 59.527 | 0.4121 | 3.3049 | 0.10344 | 2.0555 | 0.4128 | 3.3075
VERM | Vermont | CA | VERM_22kV_BUS 2 | 22 | 4.1951 | 159.856 | 4.8082 | 61.0727 | 5.6338 | 4.5048 | 57.2185 | 4.6865 | 59.527 | 0.4121 | 3.3049 | 0.10344 | 2.0555 | 0.4128 | 3.3075
WAEA | Warwick East | SW | WAEA_33kV_BUS 1 | 33 | 7.3763 | 421.6138 | 7.3468 | 139.9762 | 7.3136 | 7.2972 | 139.0309 | 7.4249 | 141.4628 | 0.6046 | 2.7765 | 0.4905 | 2.8355 | 0.56794 | 2.7828
WAEA | Warwick East | SW | WAEA_33kV_BUS 2 | 33 | 7.3763 | 421.6138 | 7.3468 | 139.9762 | 7.3136 | 7.2972 | 139.0309 | 7.4249 | 141.4628 | 0.6046 | 2.7765 | 0.4905 | 2.8355 | 0.56794 | 2.7828
WAEA | Warwick East (TF1*C0516*ON) | CA | WAEA_11kV_BUS 1 | 11 | 10.3885 | 197.9267 | 5.5738 | 35.3983 | 3.1672 | 10.5032 | 66.7046 | 7.5099 | 47.6942 | 0.0826 | 0.66746 | 3.1955 | 0.35895 | 0.07852 | 0.66816
WAEA | Warwick East (TF2*C0516*ON) | SW | WAEA_11kV_BUS 2 | 11 | 10.3885 | 197.9267 | 5.5738 | 35.3983 | 3.1672 | 10.5032 | 66.7046 | 7.5099 | 47.6942 | 0.0826 | 0.66746 | 3.1955 | 0.35895 | 0.07852 | 0.66816
WAGG | Waggamba T156 | SW | WAGG_132kV_TEF T1 | 132 | 1.9575 | 447.5525 | 2.3234 | 177.0678 | 2.8581 | 2.2104 | 168.4572 | 2.224 | 169.4883 | 6.6115 | 42.3135 | 2.9693 | 22.3938 | 6.1424 | 42.3931
WAGG | Waggamba T156 | SW | WAGG_66kV_BUS ESSENTIAL ENERGY | 66 | 2.4145 | 276.016 | 3.3383 | 127.2066 | 5.4112 | 3.4055 | 129.7683 | 3.4332 | 130.8222 | 1.7086 | 17.2764 | 0.17259 | 2.9366 | 1.5913 | 17.2963
WAGG | Waggamba T156 | SW | WAGG_33kV_BUS GOONDIWINDI | 33 | 3.3167 | 189.5743 | 2.672 | 50.9077 | 2.2368 | 3.0307 | 57.7433 | 3.1324 | 59.6797 | 0.42679 | 6.3048 | 0 | 10.903 | 0.39746 | 6.3097
WALK | Walkers | WB | WALK_66kV_TEF T1 | 66 | 6.1369 | 701.5445 | 5.8037 | 221.1521 | 5.5506 | 5.9613 | 227.1576 | 6.0015 | 228.6858 | 1.5249 | 6.6583 | 1.6291 | 7.7791 | 1.4912 | 6.7272
WALK | Walkers | WB | WALK_66kV_TEF T2 | 66 | 6.1369 | 701.5445 | 5.8037 | 221.1521 | 5.5506 | 5.9613 | 227.1576 | 6.0015 | 228.6858 | 1.5249 | 6.6583 | 1.6291 | 7.7791 | 1.4912 | 6.7272
WALK | Walkers | WB | MARYBOROUGH CITY | 11 | 10.6816 | 203.5118 | 11.8085 | 74.994 | 13.2388 | 11.4452 | 72.6869 | 11.2926 | 71.7178 | 0.1277 | 0.64149 | 0.10093 | 0.45413 | 0.12676 | 0.6434
WALK | Walkers | WB | WALK_11kV_BUS | 11 | 11.0515 | 210.5591 | 3.5468 | 22.5253 | 2.1158 | 9.5916 | 60.9149 | 9.6416 | 61.2324 | 0.07991 | 0.62711 | 0.46126 | 4.6207 | 0.07897 | 0.62903
WALK | Walkers | WB | WALK_11kV_BUS FURNACE | 11 | 11.0515 | 210.5591 | 3.5468 | 22.5253 | 2.1158 | 9.5916 | 60.9149 | 9.6416 | 61.2324 | 0.07991 | 0.62711 | 0.46126 | 4.6207 | 0.07897 | 0.62903
WALL | Wallaville | WB | WALL_66kV_BUS | 66 | 1.6735 | 191.3067 | 1.1522 | 43.9039 | 0.87218 | 1.4165 | 53.9753 | 1.6026 | 61.0681 | 14.3484 | 20.5318 | 19.814 | 56.6451 | 14.3235 | 20.6093
WALL | Wallaville | WB | WALL_11kV_BUS 1 | 11 | 4.2946 | 81.8225 | 4.9573 | 31.4829 | 5.8443 | 4.4395 | 28.1943 | 5.0018 | 31.7657 | 0.46244 | 1.5597 | 0.06387 | 0.98938 | 0.46174 | 1.5619
WALL | Wallaville | WB | WALL_11kV_BUS 2 | 11 | 4.2946 | 81.8225 | 4.9573 | 31.4829 | 5.8443 | 4.4395 | 28.1943 | 5.0018 | 31.7657 | 0.46244 | 1.5597 | 0.06387 | 0.98938 | 0.46174 | 1.5619
WAND | Wandoan | SW | WAND_33kV_BUS 1 | 33 | 0.54987 | 31.4293 | 0.30519 | 5.8147 | 0.21021 | 0.46815 | 8.9195 | 0.50636 | 9.6475 | 16.3043 | 34.4522 | 29.5513 | 127.5067 | 16.3038 | 34.4591
WAND | Wandoan | SW | WAND_33kV_BUS 2 | 33 | 0.54987 | 31.4293 | 0.30519 | 5.8147 | 0.21021 | 0.46815 | 8.9195 | 0.50636 | 9.6475 | 16.3043 | 34.4522 | 29.5513 | 127.5067 | 16.3038 | 34.4591
WAND | Wandoan (TF1) | SW | WAND_22kV_BUS 1 | 22 | 0.62799 | 23.9296 | 0.83974 | 10.6661 | 1.263 | 0.79169 | 10.0558 | 0.87314 | 11.0904 | 7.5276 | 20.9372 | 0.28126 | 5.6251 | 7.5274 | 20.9403
WAND | Wandoan (TF1) | SW | WAND_22kV_BUS 2 | 22 | 0.62697 | 23.8908 | 0.8379 | 10.6427 | 1.2588 | 0.78954 | 10.0285 | 0.87094 | 11.0624 | 7.5295 | 20.975 | 0.28315 | 5.6629 | 7.5293 | 20.978
WARW | Warwick | SW | WARW_33kV_BUS 1 | 33 | 9.0062 | 514.7718 | 11.5924 | 220.8654 | 16.2498 | 10.9689 | 208.9858 | 11.5505 | 220.0657 | 0.40625 | 2.2916 | 0.0234 | 0.775 | 0.36959 | 2.2979
WARW | Warwick | SW | WARW_33kV_BUS 2 | 33 | 9.0062 | 514.7718 | 11.5924 | 220.8654 | 16.2498 | 10.9689 | 208.9858 | 11.5505 | 220.0657 | 0.40625 | 2.2916 | 0.0234 | 0.775 | 0.36959 | 2.2979
WARW | Warwick | SW | WARW_11kV_BUS 1 | 11 | 3.4357 | 65.4586 | 3.5901 | 22.8004 | 3.7601 | 3.5097 | 22.2898 | 3.5286 | 22.4099 | 0.1934 | 2.0244 | 0.14826 | 1.764 | 0.18932 | 2.0251
WARW | Warwick (CCT 735) | SW | WARW_110kV_BUS 1 | 110 | 4.0424 | 770.1744 | 4.8409 | 307.4411 | 6.0113 | 4.3805 | 278.2018 | 4.8377 | 307.2328 | 5.0183 | 16.5395 | 0.79414 | 8.8441 | 4.8967 | 16.5697
WARW | Warwick (CCT 736) | SW | WARW_110kV_BUS 2 | 110 | 4.0424 | 770.1744 | 4.8409 | 307.4411 | 6.0113 | 4.3805 | 278.2018 | 4.8377 | 307.2328 | 5.0183 | 16.5395 | 0.79414 | 8.8441 | 4.8967 | 16.5697
WEBU | West Bundaberg | WB | WEBU_66kV_TEF T1 | 66 | 6.3534 | 726.2883 | 6.1081 | 232.7487 | 5.9595 | 6.3227 | 240.9252 | 6.1438 | 234.1099 | 0.9097 | 6.5349 | 1.3218 | 7.1845 | 0.88148 | 6.6325
WEBU | West Bundaberg | WB | WEBU_66kV_TEF T2 | 66 | 6.3534 | 726.2883 | 6.1081 | 232.7487 | 5.9595 | 6.3227 | 240.9252 | 6.1438 | 234.1099 | 0.9097 | 6.5349 | 1.3218 | 7.1845 | 0.88148 | 6.6325
WEBU | West Bundaberg | WB | WEBU_11kV_BUS 1 | 11 | 14.7861 | 281.7138 | 16.942 | 107.596 | 19.9619 | 16.0927 | 102.2023 | 16.3466 | 103.8151 | 0.04176 | 0.47065 | 0.01649 | 0.28913 | 0.04097 | 0.47336
WEBU | West Bundaberg | WB | WEBU_11kV_BUS 2 | 11 | 14.7861 | 281.7138 | 16.942 | 107.596 | 19.9619 | 16.0927 | 102.2023 | 16.3466 | 103.8151 | 0.04176 | 0.47065 | 0.01649 | 0.28913 | 0.04097 | 0.47336
WEDA | West Dalby | SW | WEDA_33kV_BUS 1 | 33 | 5.1869 | 296.4689 | 4.7202 | 89.9327 | 4.3223 | 4.7964 | 91.3843 | 5.1659 | 98.4236 | 1.4438 | 3.7743 | 1.2227 | 5.1224 | 1.445 | 3.7744
WEDA | West Dalby | SW | WEDA_33kV_BUS 2 | 33 | 5.1869 | 296.4689 | 4.7202 | 89.9327 | 4.3223 | 4.7964 | 91.3843 | 5.1659 | 98.4236 | 1.4438 | 3.7743 | 1.2227 | 5.1224 | 1.445 | 3.7744
WEDA | West Dalby (TF1) | SW | WEDA_11kV_BUS DRAYTON ST | 11 | 3.689 | 70.2849 | 3.9964 | 25.3808 | 4.3579 | 3.7925 | 24.0854 | 3.9403 | 25.024 | 0.27169 | 1.8743 | 0.11127 | 1.455 | 0.27183 | 1.8743
WEDA | West Dalby (TF2) | SW | WEDA_11kV_BUS EDWARD ST | 11 | 3.689 | 70.2849 | 3.9964 | 25.3808 | 4.3579 | 3.7925 | 24.0854 | 3.9403 | 25.024 | 0.27169 | 1.8743 | 0.11127 | 1.455 | 0.27183 | 1.8743
WEDA | West Dalby (TF3) | SW | WEDA_11kV_BUS NICHOLSON ST | 11 | 3.689 | 70.2849 | 3.9964 | 25.3808 | 4.3579 | 3.7925 | 24.0854 | 3.9403 | 25.024 | 0.27169 | 1.8743 | 0.11127 | 1.455 | 0.27183 | 1.8743
WEMA | West Mackay (TF1) | MK | WEMA_33kV_TEF T1 | 33 | 12.9968 | 742.8649 | 16.3323 | 311.1717 | 22.1856 | 15.9344 | 303.5901 | 15.6452 | 298.0813 | 0.253 | 1.5926 | 0.12091 | 0.60121 | 0.25221 | 1.6046
WEMA | West Mackay (TF1) | MK | WEMA_11kV_BUS 2 | 11 | 7.0814 | 134.919 | 7.5138 | 47.7191 | 8.0137 | 7.2883 | 46.287 | 7.3585 | 46.7325 | 0.06603 | 0.98431 | 0.04074 | 0.81394 | 0.06595 | 0.98565
WEMA | West Mackay (TF2) | MK | WEMA_33kV_TEF T2 | 33 | 13.5202 | 772.7824 | 18.3235 | 349.1098 | 28.7534 | 18.7397 | 357.0396 | 18.3244 | 349.1265 | 0.22765 | 1.5333 | 0.07128 | 0.31213 | 0.22686 | 1.5454
WEMA | West Mackay (TF2) | MK | WEMA_11kV_BUS 1 | 11 | 7.0332 | 134.0006 | 7.4776 | 47.4893 | 7.9931 | 7.243 | 45.9994 | 7.3226 | 46.5049 | 0.06885 | 0.9909 | 0.04074 | 0.81394 | 0.06876 | 0.99223
WETO | West Toowoomba | SW | WETO_33kV_BUS 1 | 33 | 10.3331 | 590.6147 | 1.1449 | 21.8129 | 0.57722 | 9.2442 | 176.1259 | 8.6729 | 165.2401 | 0.3102 | 2.0047 | 54.2527 | -1.602 | 0.30974 | 2.0003
WETO | West Toowoomba | SW | WETO_33kV_BUS 2 | 33 | 10.3331 | 590.6147 | 1.1449 | 21.8129 | 0.57722 | 9.2442 | 176.1259 | 8.6729 | 165.2401 | 0.3102 | 2.0047 | 54.2527 | -1.602 | 0.30974 | 2.0003
WETO | West Toowoomba | SW | WETO_33kV_BUS 3 | 33 | 10.3331 | 590.6147 | 1.1449 | 21.8129 | 0.57722 | 9.2442 | 176.1259 | 8.6729 | 165.2401 | 0.3102 | 2.0047 | 54.2527 | -1.602 | 0.30974 | 2.0003
WETO | West Toowoomba | SW | WETO_33kV_BUS 4 | 33 | 10.3331 | 590.6147 | 1.1449 | 21.8129 | 0.57722 | 9.2442 | 176.1259 | 8.6729 | 165.2401 | 0.3102 | 2.0047 | 54.2527 | -1.602 | 0.30974 | 2.0003
WETO | West Toowoomba | SW | WETO_11kV_BUS 1 | 11 | 11.3272 | 215.8118 | 2.2611 | 14.3598 | 1.1546 | 10.3834 | 65.9436 | 9.2445 | 58.7106 | 0.05405 | 0.61446 | 9.0196 | 0.39172 | 0.054 | 0.61397
WETO | West Toowoomba | SW | WETO_11kV_BUS 2 | 11 | 11.3272 | 215.8118 | 2.2611 | 14.3598 | 1.1546 | 10.3834 | 65.9436 | 9.2445 | 58.7106 | 0.05405 | 0.61446 | 9.0196 | 0.39172 | 0.054 | 0.61397
WETO | West Toowoomba | SW | WETO_11kV_BUS 3 | 11 | 11.3272 | 215.8118 | 2.2611 | 14.3598 | 1.1546 | 10.3834 | 65.9436 | 9.2445 | 58.7106 | 0.05405 | 0.61446 | 9.0196 | 0.39172 | 0.054 | 0.61397
WETO | West Toowoomba | SW | WETO_11kV_BUS 4 | 11 | 11.3272 | 215.8118 | 2.2611 | 14.3598 | 1.1546 | 10.3834 | 65.9436 | 9.2445 | 58.7106 | 0.05405 | 0.61446 | 9.0196 | 0.39172 | 0.054 | 0.61397
WETO | West Toowoomba | SW | WETO_11kV_BUS 5 | 11 | 11.3272 | 215.8118 | 2.2611 | 14.3598 | 1.1546 | 10.3834 | 65.9436 | 9.2445 | 58.7106 | 0.05405 | 0.61446 | 9.0196 | 0.39172 | 0.054 | 0.61397
WETO | West Toowoomba | SW | WETO_11kV_BUS 6 | 11 | 11.3272 | 215.8118 | 2.2611 | 14.3598 | 1.1546 | 10.3834 | 65.9436 | 9.2445 | 58.7106 | 0.05405 | 0.61446 | 9.0196 | 0.39172 | 0.054 | 0.61397
WEWA | West Warwick | SW | WEWA_33kV_BUS 1 | 33 | 4.0974 | 234.1962 | 2.81 | 53.5376 | 2.1364 | 3.6704 | 69.9298 | 3.7425 | 71.3046 | 1.463 | 4.9019 | 2.8906 | 11.8055 | 1.4263 | 4.9081
WEWA | West Warwick | SW | WEWA_33kV_BUS 2 | 33 | 4.1327 | 236.2162 | 2.8514 | 54.327 | 2.1748 | 3.7059 | 70.6068 | 3.7767 | 71.9563 | 1.4473 | 4.8609 | 2.8419 | 11.5723 | 1.4106 | 4.8672
WEWA | West Warwick | SW | WEWA_11kV_BUS 1 | 11 | 5.7965 | 110.4376 | 6.8471 | 43.4847 | 8.357 | 6.3544 | 40.3556 | 6.7031 | 42.5707 | 0.19526 | 1.1894 | 0.0358 | 0.65204 | 0.19119 | 1.1901
WEWA | West Warwick | SW | WEWA_11kV_BUS 2 | 11 | 5.7965 | 110.4376 | 6.8471 | 43.4847 | 8.357 | 6.3544 | 40.3556 | 6.7031 | 42.5707 | 0.19526 | 1.1894 | 0.0358 | 0.65204 | 0.19119 | 1.1901
WIHI | Windy Hill | FN | WIHI_22kV_GEN G1 | 22 | 2.6345 | 100.3863 | 2.4447 | 31.0518 | 2.285 | 2.4721 | 31.3998 | 2.6245 | 33.3352 | 1.1315 | 5.1814 | 0.56411 | 6.5219 | 1.012 | 5.2271
WIIS | Wiggins Island | CA | WIIS_22kV_TEF T1 | 22 | 21.0966 | 803.8875 | 4.4589 | 56.6361 | 2.4966 | 18.2658 | 232.0067 | 18.3132 | 232.6086 | 0.02762 | 0.66172 | 0.17654 | 8.0725 | 0.02766 | 0.66348
WIIS | Wiggins Island | CA | WIIS_22kV_TEF T2 | 22 | 21.0966 | 803.8875 | 4.4589 | 56.6361 | 2.4966 | 18.2658 | 232.0067 | 18.3132 | 232.6086 | 0.02762 | 0.66172 | 0.17654 | 8.0725 | 0.02766 | 0.66348
WIIS | Wiggins Island (TF1*C0114*ON) | CA | WIIS_132kV_BUS 1 | 132 | 16.4633 | 3764.0072 | 14.5585 | 1109.5095 | 13.1941 | 15.7072 | 1197.0462 | 15.5954 | 1188.5327 | 0.58914 | 5.0579 | 0.89443 | 6.9707 | 0.59081 | 5.1214
WIIS | Wiggins Island (TF1*C0114*ON) | CA | WIIS_132kV_TEF T1 | 132 | 16.4633 | 3764.0072 | 14.5585 | 1109.5095 | 13.1941 | 15.7072 | 1197.0462 | 15.5954 | 1188.5327 | 0.58914 | 5.0579 | 0.89443 | 6.9707 | 0.59081 | 5.1214
WIIS | Wiggins Island (TF2*C0114*ON) | CA | WIIS_132kV_BUS 2 | 132 | 16.3987 | 3749.2577 | 14.486 | 1103.9807 | 13.1166 | 15.6382 | 1191.7911 | 15.5312 | 1183.6404 | 0.5934 | 5.0776 | 0.89961 | 7.0169 | 0.59507 | 5.141
WIIS | Wiggins Island (TF2*C0114*ON) | CA | WIIS_132kV_TEF T2 | 132 | 16.3987 | 3749.2577 | 14.486 | 1103.9807 | 13.1166 | 15.6382 | 1191.7911 | 15.5312 | 1183.6404 | 0.5934 | 5.0776 | 0.89961 | 7.0169 | 0.59507 | 5.141
WINT | Winton | NQ | WINT_66kV_BUS 1 | 66 | 0.32616 | 37.2852 | 0.20305 | 7.7371 | 0.14883 | 0.28194 | 10.7433 | 0.29832 | 11.3676 | 55.1906 | 116.0576 | 108.1846 | 345.0531 | 55.4484 | 118.2472
WINT | Winton | NQ | WINT_33kV_BUS | 33 | 0.27721 | 15.8449 | 0.3365 | 6.4111 | 0.42983 | 0.30084 | 5.7318 | 0.34168 | 6.5099 | 19.9431 | 72.924 | 0.12599 | 36.1035 | 20.0078 | 73.4713
WINT | Winton | NQ | WINT_11kV_BUS 1 | 11 | 1.5225 | 29.0067 | 2.1677 | 13.7665 | 3.8443 | 2.2722 | 14.4305 | 2.3868 | 15.1579 | 1.609 | 4.2972 | 0.01355 | 0.45437 | 1.6162 | 4.3581
WINT | Winton | NQ | WINT_11kV_BUS 4 | 11 | 1.5225 | 29.0067 | 2.1677 | 13.7665 | 3.8443 | 2.2722 | 14.4305 | 2.3868 | 15.1579 | 1.609 | 4.2972 | 0.01355 | 0.45437 | 1.6162 | 4.3581
WIRR | Wirralie | NQ | WIRR_66kV_TEF T1 | 66 | 0.70648 | 80.7612 | 0.49323 | 18.7947 | 0.37351 | 0.58673 | 22.3573 | 0.68851 | 26.2357 | 39.4514 | 44.3139 | 51.8973 | 130.1942 | 39.4608 | 44.3213
WIRR | Wirralie | NQ | WIRR_33kV_BUS | 33 | 0.17522 | 10.0152 | 0.18136 | 3.4554 | 0.18783 | 0.17442 | 3.3232 | 0.1824 | 3.4752 | 15.3496 | 118.6192 | 5.4868 | 107.5408 | 15.352 | 118.6211
WOOD | Woodhouse Station | NQ | WOOD_66kV_TEF T1 | 66 | 5.295 | 605.2992 | 4.3413 | 165.4264 | 3.67 | 4.8625 | 185.2845 | 5.022 | 191.3637 | 3.2873 | 7.2013 | 4.701 | 12.2966 | 3.264 | 7.1923
WOOD | Woodhouse Station | NQ | WOOD_11kV_TEF T1 | 11 | 0.27564 | 5.2516 | 0.27641 | 1.7554 | 0.27718 | 0.27584 | 1.7518 | 0.27621 | 1.7542 | 3.9398 | 25.0366 | 3.8485 | 24.8366 | 3.9392 | 25.0363
WOOG | Woodgate | WB | WOOG_66kV_TEF T1 | 66 | 1.9109 | 218.4487 | 1.2398 | 47.243 | 0.91547 | 1.662 | 63.3317 | 1.7701 | 67.4496 | 9.4748 | 19.7845 | 16.9823 | 55.2737 | 9.4262 | 19.8143
WOOG | Woodgate | WB | WOOG_11kV_TEF T1 | 11 | 2.8559 | 54.412 | 3.1005 | 19.691 | 3.3889 | 2.9159 | 18.5184 | 3.0777 | 19.546 | 0.35744 | 2.4201 | 0.09425 | 1.8705 | 0.35609 | 2.4209
WOON | Woongarra | WB | WOON_66kV_BUS | 66 | 5.4781 | 626.2313 | 4.8597 | 185.178 | 4.4023 | 5.1893 | 197.7405 | 5.2419 | 199.7441 | 1.7485 | 7.4496 | 2.1599 | 10.2806 | 1.7235 | 7.5271
WOON | Woongarra | WB | WOON_3.3kV_BUS | 3.3 | 7.1154 | 40.6701 | 7.27 | 13.8512 | 7.4362 | 7.1783 | 13.6765 | 7.2134 | 13.7433 | 0.03072 | 0.29296 | 0.02634 | 0.27433 | 0.03065 | 0.29315
WOSO | Woodstock South | NQ | WOSO_66kV_BUS 1 | 66 | 2.1748 | 248.6132 | 1.552 | 59.1398 | 1.1892 | 1.8105 | 68.9882 | 2.1274 | 81.0659 | 13.1344 | 14.105 | 17.2061 | 40.1608 | 13.1137 | 14.1174
WOSO | Woodstock South | NQ | WOSO_66kV_BUS 2 | 66 | 2.1748 | 248.6132 | 1.552 | 59.1398 | 1.1892 | 1.8105 | 68.9882 | 2.1274 | 81.0659 | 13.1344 | 14.105 | 17.2061 | 40.1608 | 13.1137 | 14.1174
WOSO | Woodstock South (TF1) | NQ | WOSO_11kV_BUS 1 | 11 | 3.0526 | 58.1591 | 3.2666 | 20.7459 | 3.5051 | 3.0321 | 19.2562 | 3.3054 | 20.9924 | 0.45323 | 2.2432 | 0.08839 | 1.8514 | 0.45266 | 2.2436
WOTO | Woolooga Town | WB | WOTO_66kV_TEF T2 | 66 | 2.781 | 317.9116 | 2.2644 | 86.2863 | 1.9042 | 2.4855 | 94.7099 | 2.6904 | 102.5161 | 6.8561 | 13.4243 | 8.0429 | 24.2501 | 6.8287 | 13.4365
WOTO | Woolooga Town | WB | WOTO_11kV_BUS 1 | 11 | 3.6698 | 69.9198 | 3.9434 | 25.0441 | 4.2584 | 3.7313 | 23.6973 | 3.9172 | 24.8775 | 0.29728 | 1.8805 | 0.10683 | 1.5076 | 0.29651 | 1.8808
WOTO | Woolooga Town | WB | WOTO_11kV_BUS 2 | 11 | 3.6698 | 69.9198 | 3.9434 | 25.0441 | 4.2584 | 3.7313 | 23.6973 | 3.9172 | 24.8775 | 0.29728 | 1.8805 | 0.10683 | 1.5076 | 0.29651 | 1.8808
WOTO | Woolooga Town | WB | WOTO_11kV_BUS 3 | 11 | 3.6698 | 69.9198 | 3.9434 | 25.0441 | 4.2584 | 3.7313 | 23.6973 | 3.9172 | 24.8775 | 0.29728 | 1.8805 | 0.10683 | 1.5076 | 0.29651 | 1.8808
WOWA | Wowan | CA | WOWA_66kV_BUS 1 | 66 | 0.87588 | 100.1264 | 0.58372 | 22.2429 | 0.43251 | 0.7308 | 27.8473 | 0.84255 | 32.1055 | 29.8526 | 37.4041 | 41.9665 | 115.0956 | 29.8534 | 37.4242
WOWA | Wowan | CA | WOWA_66kV_BUS 2 | 66 | 0.87588 | 100.1264 | 0.58372 | 22.2429 | 0.43251 | 0.7308 | 27.8473 | 0.84255 | 32.1055 | 29.8526 | 37.4041 | 41.9665 | 115.0956 | 29.8534 | 37.4242
WOWA | Wowan | CA | WOWA_66kV_BUS 3 | 66 | 0.87588 | 100.1264 | 0.58372 | 22.2429 | 0.43251 | 0.7308 | 27.8473 | 0.84255 | 32.1055 | 29.8526 | 37.4041 | 41.9665 | 115.0956 | 29.8534 | 37.4242
WOWA | Wowan | CA | WOWA_22kV_BUS 1 | 22 | 1.7655 | 67.273 | 2.2557 | 28.6515 | 3.0963 | 1.9865 | 25.232 | 2.3499 | 29.8477 | 3.5134 | 7.0916 | 0.19644 | 2.9356 | 3.5135 | 7.0938
WOWA | Wowan | CA | WOWA_22kV_BUS 2 | 22 | 1.7655 | 67.273 | 2.2557 | 28.6515 | 3.0963 | 1.9865 | 25.232 | 2.3499 | 29.8477 | 3.5134 | 7.0916 | 0.19644 | 2.9356 | 3.5135 | 7.0938
WOWA | Wowan | CA | WOWA_22kV_BUS 3 | 22 | 1.7655 | 67.273 | 2.2557 | 28.6515 | 3.0963 | 1.9865 | 25.232 | 2.3499 | 29.8477 | 3.5134 | 7.0916 | 0.19644 | 2.9356 | 3.5135 | 7.0938
YALK | Yalkula | FN | YALK_132kV_BUS | 132 | 2.3803 | 544.2 | 2.4499 | 186.7114 | 2.5258 | 2.3813 | 181.4796 | 2.4521 | 186.877 | 8.7344 | 34.1192 | 6.0676 | 31.6344 | 8.3942 | 34.2439
YANO | Yarranlea North SF | SW | YANO_110kV | 110 | 5.2076 | 992.1758 | 3.6516 | 231.9078 | 2.5935 | 4.7378 | 300.893 | 5.0206 | 318.8505 | 5.9646 | 12.0179 | 8.4401 | 30.9422 | 4.7296 | 11.1575
YARA | Yarranlea T010 | SW | YARA_33kV_BUS 1 | 33 | 6.812 | 389.3596 | 10.1735 | 193.8305 | 17.9433 | 10.7733 | 205.2586 | 10.7244 | 204.3273 | 0.57003 | 3.0237 | 0.03889 | 0.2035 | 0.43091 | 2.8649
YARA | Yarranlea T010 | SW | YARA_33kV_BUS 2 | 33 | 6.812 | 389.3596 | 10.1735 | 193.8305 | 17.9433 | 10.7733 | 205.2586 | 10.7244 | 204.3273 | 0.57003 | 3.0237 | 0.03889 | 0.2035 | 0.43091 | 2.8649
YARA | Yarranlea T010 (TF1) | SW | YARA_110kV_TEF T1 | 110 | 5.1802 | 986.9577 | 3.6458 | 231.5384 | 2.5996 | 4.706 | 298.8686 | 4.9951 | 317.2335 | 6.0165 | 12.0713 | 8.4188 | 30.8724 | 4.8019 | 11.2346
YARA | Yarranlea T010 (TF2) | SW | YARA_110kV_TEF T2 | 110 | 5.18 | 986.9288 | 3.6385 | 231.0783 | 2.5919 | 4.7054 | 298.8355 | 4.9936 | 317.1335 | 6.0173 | 12.0714 | 8.4564 | 30.9799 | 4.8026 | 11.2346
YARR | Yarraman | WB | YARR_66kV_BUS | 66 | 1.0876 | 124.3258 | 0.72823 | 27.7492 | 0.53722 | 0.89094 | 33.9495 | 1.0606 | 40.4148 | 27.1258 | 27.3848 | 36.9391 | 91.8631 | 27.0821 | 27.4112
YARR | Yarraman | WB | YARR_11kV_BUS 1 | 11 | 2.7035 | 51.5084 | 3.0865 | 19.6018 | 3.574 | 2.7255 | 17.3092 | 3.1494 | 20.0016 | 0.91019 | 2.4188 | 0.1567 | 1.6581 | 0.90898 | 2.4195
YARR | Yarraman | WB | YARR_11kV_BUS 2 | 11 | 2.7035 | 51.5084 | 3.0865 | 19.6018 | 3.574 | 2.7255 | 17.3092 | 3.1494 | 20.0016 | 0.91019 | 2.4188 | 0.1567 | 1.6581 | 0.90898 | 2.4195
YARW | Yarwun Switching Station | CA | YARW_66kV_pole4229800_tr_line_15129 | 66 | 2.7216 | 311.1191 | 1.8304 | 69.7481 | 1.3677 | 2.2994 | 87.6188 | 2.5982 | 99.0052 | 8.6784 | 12.7237 | 12.2467 | 36.531 | 8.6783 | 12.7402
YASO | Yarranlea South | SW | YASO_33kV_BUS | 33 | 4.4474 | 254.2036 | 4.0428 | 77.0264 | 3.5675 | 4.2994 | 81.9142 | 4.2968 | 81.8653 | 1.481 | 4.4741 | 1.8832 | 6.0332 | 1.3419 | 4.3153
YASO | Yarranlea South (TF1) | SW | YASO_11kV_BUS 1 | 11 | 2.1717 | 41.3756 | 2.2985 | 14.5974 | 2.4254 | 2.2204 | 14.1013 | 2.2607 | 14.3576 | 0.43347 | 3.1879 | 0.26891 | 2.6908 | 0.41801 | 3.1703
YASO | Yarranlea South (TF2) | SW | YASO_11kV_BUS 2 | 11 | 2.1717 | 41.3756 | 2.2985 | 14.5974 | 2.4254 | 2.2204 | 14.1013 | 2.2607 | 14.3576 | 0.43347 | 3.1879 | 0.26891 | 2.6908 | 0.41801 | 3.1703
YEPP | Yeppoon | CA | YEPP_66kV_BUS 1 | 66 | 3.1233 | 357.0428 | 2.045 | 77.9268 | 1.5147 | 2.7145 | 103.4348 | 2.9029 | 110.6156 | 5.863 | 12.072 | 10.1306 | 33.3431 | 5.8219 | 12.0743
YEPP | Yeppoon | CA | YEPP_66kV_BUS 2 | 66 | 3.1233 | 357.0428 | 2.045 | 77.9268 | 1.5147 | 2.7145 | 103.4348 | 2.9029 | 110.6156 | 5.863 | 12.072 | 10.1306 | 33.3431 | 5.8219 | 12.0743
YEPP | Yeppoon | CA | YEPP_22kV_BUS 1 | 22 | 2.1101 | 80.4047 | 1.013 | 12.867 | 0.66532 | 1.8179 | 23.0906 | 1.8962 | 24.0848 | 0.90013 | 6.5601 | 0.05078 | 28.216 | 0.89557 | 6.5604
YEPP | Yeppoon | CA | YEPP_22kV_BUS 2 | 22 | 2.1101 | 80.4047 | 1.013 | 12.867 | 0.66532 | 1.8179 | 23.0906 | 1.8962 | 24.0848 | 0.90013 | 6.5601 | 0.05078 | 28.216 | 0.89557 | 6.5604
YEPP | Yeppoon | CA | YEPP_22kV_BUS 3 | 22 | 2.1101 | 80.4047 | 1.013 | 12.867 | 0.66532 | 1.8179 | 23.0906 | 1.8962 | 24.0848 | 0.90013 | 6.5601 | 0.05078 | 28.216 | 0.89557 | 6.5604
YEPP | Yeppoon | CA | YEPP_11kV_BUS 1 | 11 | 11.3904 | 217.0165 | 14.2293 | 90.3679 | 18.8731 | 12.8989 | 81.9189 | 14.3662 | 91.2374 | 0.17548 | 0.58769 | 0.0126 | 0.25217 | 0.17434 | 0.58775
YEPP | Yeppoon | CA | YEPP_11kV_BUS 2 | 11 | 11.3904 | 217.0165 | 14.2293 | 90.3679 | 18.8731 | 12.8989 | 81.9189 | 14.3662 | 91.2374 | 0.17548 | 0.58769 | 0.0126 | 0.25217 | 0.17434 | 0.58775

## Max-Max Fault Level Report
Sub Code | Substation | Region | Reported on Bus in PowerFactory | Voltage (kV) | 2025 3-Ph Fault Level (kA) | 2025 3-Ph Fault Level (MVA) | 2025 1-Ph-G Fault Level (kA) | 2025 1-Ph-G Fault Level (MVA) | 2025 3*I0 Fault Level (kA) | 2025 B 2-Ph-G Fault Level (kA) | 2025 B 2-Ph-G Fault Level (MVA) | 2025 C 2-Ph-G Fault Level (kA) | 2025 C 2-Ph-G Fault Level (MVA) | R1 (Ohms) | X1 (Ohms) | R0 (Ohms) | X0 (Ohms) | R2 (Ohms) | X2 (Ohms)
ABPO | Abbot Point | NQ | ABPO_11kV_BUS 1 | 11 | 9.5345 | 181.6567 | 0.01464 | 0.09298 | 0.00732 | 8.2622 | 52.472 | 8.2552 | 52.4277 | 0.22074 | 0.69866 | 1431.006 | 0.126 | 0.22113 | 0.69824
ABPO | Abbot Point | NQ | ABPO_11kV_BUS 2 | 11 | 9.5345 | 181.6567 | 0.01464 | 0.09298 | 0.00732 | 8.2622 | 52.472 | 8.2552 | 52.4277 | 0.22074 | 0.69866 | 1431.006 | 0.126 | 0.22113 | 0.69824
ABPO | Abbot Point | NQ | ABPO_66kV_TEF T1 | 66 | 1.9041 | 217.6635 | 1.4921 | 56.8561 | 1.2247 | 1.7114 | 65.2151 | 1.8057 | 68.8077 | 7.7196 | 20.616 | 10.1669 | 39.0707 | 7.7338 | 20.6009
ABPO | Abbot Point | NQ | ABPO_66kV_TEF T2 | 66 | 1.9041 | 217.6635 | 1.4921 | 56.8561 | 1.2247 | 1.7114 | 65.2151 | 1.8057 | 68.8077 | 7.7196 | 20.616 | 10.1669 | 39.0707 | 7.7338 | 20.6009
AGWA | Agnes Water | CA | AGWA_22kV_BUS 1 | 22 | 2.5653 | 97.752 | 3.467 | 44.0365 | 5.346 | 3.4094 | 43.3048 | 3.5407 | 44.9729 | 0.94914 | 5.3635 | 0.05954 | 1.2025 | 0.94852 | 5.3655
AGWA | Agnes Water | CA | AGWA_22kV_BUS 2 | 22 | 2.5653 | 97.752 | 3.467 | 44.0365 | 5.346 | 3.4094 | 43.3048 | 3.5407 | 44.9729 | 0.94914 | 5.3635 | 0.05954 | 1.2025 | 0.94852 | 5.3655
AGWA | Agnes Water | CA | AGWA_66kV_BUS 1 | 66 | 1.0951 | 125.1828 | 0.82081 | 31.277 | 0.65641 | 0.99022 | 37.7324 | 1.0164 | 38.7298 | 8.0125 | 37.4319 | 12.0581 | 75.7347 | 8.0069 | 37.4495
AGWA | Agnes Water | CA | AGWA_66kV_BUS 2 | 66 | 1.0951 | 125.1828 | 0.82081 | 31.277 | 0.65641 | 0.99022 | 37.7324 | 1.0164 | 38.7298 | 8.0125 | 37.4319 | 12.0581 | 75.7347 | 8.0069 | 37.4495
AITK | Aitkenvale (TF1) | NQ | AITK_11kV_BUS 1 | 11 | 17.9955 | 342.8599 | 19.5177 | 123.9543 | 21.3153 | 18.668 | 118.558 | 19.0911 | 121.2448 | 0.03773 | 0.38637 | 0.01675 | 0.29712 | 0.03722 | 0.38637
AITK | Aitkenvale (TF2) | NQ | AITK_11kV_BUS 2 | 11 | 17.9955 | 342.8599 | 19.5177 | 123.9543 | 21.3153 | 18.668 | 118.558 | 19.0911 | 121.2448 | 0.03773 | 0.38637 | 0.01675 | 0.29712 | 0.03722 | 0.38637
AITK | Aitkenvale | NQ | AITK_66kV_BUS 1 | 66 | 12.6997 | 1451.7667 | 9.9845 | 380.4597 | 8.2167 | 11.6571 | 444.1949 | 11.8332 | 450.9071 | 0.75527 | 3.213 | 1.17 | 5.8835 | 0.73701 | 3.2132
AITK | Aitkenvale | NQ | AITK_66kV_BUS 2 | 66 | 12.6997 | 1451.7667 | 9.9845 | 380.4597 | 8.2167 | 11.6571 | 444.1949 | 11.8332 | 450.9071 | 0.75527 | 3.213 | 1.17 | 5.8835 | 0.73701 | 3.2132
ALCR | Alligator Creek T065 | MK | ALCR_33kV_BUS 1 | 33 | 11.8939 | 679.826 | 14.7176 | 280.4077 | 19.654 | 13.9882 | 266.5117 | 14.4341 | 275.0058 | 0.2279 | 1.7473 | 0.04088 | 0.72339 | 0.22559 | 1.7727
ALCR | Alligator Creek T065 | MK | ALCR_33kV_BUS 2 | 33 | 11.8939 | 679.826 | 14.7176 | 280.4077 | 19.654 | 13.9882 | 266.5117 | 14.4341 | 275.0058 | 0.2279 | 1.7473 | 0.04088 | 0.72339 | 0.22559 | 1.7727
ALLO | Allora (TF2) | SW | ALLO_11kV_BUS 1 | 11 | 2.5453 | 48.4943 | 3.3151 | 21.0538 | 4.6743 | 2.8496 | 18.0974 | 3.5396 | 22.4792 | 1.7423 | 2.1212 | 0.14685 | 0.93623 | 1.7363 | 2.1225
ALLO | Allora (TF1) | SW | ALLO_11kV_BUS 2 | 11 | 2.5453 | 48.4943 | 3.3151 | 21.0538 | 4.6743 | 2.8496 | 18.0974 | 3.5396 | 22.4792 | 1.7423 | 2.1212 | 0.14685 | 0.93623 | 1.7363 | 2.1225
ALLO | Allora | SW | ALLO_11kV_BUS 3 | 11 | 2.5453 | 48.4943 | 3.3151 | 21.0538 | 4.6743 | 2.8496 | 18.0974 | 3.5396 | 22.4792 | 1.7423 | 2.1212 | 0.14685 | 0.93623 | 1.7363 | 2.1225
ALLO | Allora (Reg) | SW | ALLO_33kV_BUS | 33 | 1.1719 | 66.9824 | 0.87086 | 16.5922 | 0.67404 | 0.94598 | 18.0234 | 1.1815 | 22.5108 | 14.3586 | 10.6644 | 17.4007 | 34.2609 | 14.3054 | 10.6764
ALSH | Alan Sherriff (TF1) | NQ | ALSH_11kV_BUS 1 | 11 | 17.3199 | 329.9883 | 15.671 | 99.5244 | 14.3065 | 16.327 | 103.6905 | 16.9008 | 107.3343 | 0.02503 | 0.40257 | 0 | 0.53115 | 0.02472 | 0.40272
ALSH | Alan Sherriff (TF2) | NQ | ALSH_11kV_BUS B | 11 | 17.3199 | 329.9883 | 15.671 | 99.5244 | 14.3065 | 16.327 | 103.6905 | 16.9008 | 107.3343 | 0.02503 | 0.40257 | 0 | 0.53115 | 0.02472 | 0.40272
ALST | Alfred Street | MK | ALST_11kV_BUS 1 | 11 | 12.4704 | 237.5926 | 13.9166 | 88.3821 | 15.7815 | 13.2034 | 83.8525 | 13.5332 | 85.9471 | 0.0395 | 0.55881 | 0.00979 | 0.3844 | 0.03942 | 0.56015
ALST | Alfred Street | MK | ALST_11kV_BUS 2 | 11 | 12.4704 | 237.5926 | 13.9166 | 88.3821 | 15.7815 | 13.2034 | 83.8525 | 13.5332 | 85.9471 | 0.0395 | 0.55881 | 0.00979 | 0.3844 | 0.03942 | 0.56015
ALST | Alfred Street | MK | ALST_11kV_BUS 3 | 11 | 12.4704 | 237.5926 | 13.9166 | 88.3821 | 15.7815 | 13.2034 | 83.8525 | 13.5332 | 85.9471 | 0.0395 | 0.55881 | 0.00979 | 0.3844 | 0.03942 | 0.56015
ALST | Alfred Street | MK | ALST_33kV_BUS 1 | 33 | 13.1615 | 752.2802 | 17.7022 | 337.2727 | 27.3117 | 18.1911 | 346.5876 | 17.3574 | 330.7037 | 0.26744 | 1.5697 | 0.11341 | 0.3407 | 0.26665 | 1.5818
ALST | Alfred Street | MK | ALST_33kV_BUS 2 | 33 | 13.1615 | 752.2802 | 17.7022 | 337.2727 | 27.3117 | 18.1911 | 346.5876 | 17.3574 | 330.7037 | 0.26744 | 1.5697 | 0.11341 | 0.3407 | 0.26665 | 1.5818
ARAM | Aramara T173 | WB | ARAM_132kV_BUS 1 | 132 | 8.7308 | 1996.1212 | 8.4879 | 646.8628 | 8.376 | 8.689 | 662.1878 | 8.5313 | 650.1721 | 1.4023 | 9.4997 | 1.7428 | 10.14 | 1.3449 | 9.6506
ARAM | Aramara T173 | WB | ARAM_132kV_BUS 2 | 132 | 8.7308 | 1996.1212 | 8.4879 | 646.8628 | 8.376 | 8.689 | 662.1878 | 8.5313 | 650.1721 | 1.4023 | 9.4997 | 1.7428 | 10.14 | 1.3449 | 9.6506
ATHE | Atherton (TF1) | FN | ATHE_22kV_BUS 1 | 22 | 6.6025 | 251.5891 | 8.4412 | 107.217 | 11.7625 | 7.9344 | 100.7808 | 8.4556 | 107.401 | 0.34232 | 2.0883 | 0.00026 | 0.73092 | 0.33156 | 2.1005
ATHE | Atherton (TF2) | FN | ATHE_22kV_BUS 2 | 22 | 6.6025 | 251.5891 | 8.4412 | 107.217 | 11.7625 | 7.9344 | 100.7808 | 8.4556 | 107.401 | 0.34232 | 2.0883 | 0.00026 | 0.73092 | 0.33156 | 2.1005
ATHE | Atherton | FN | ATHE_66kV_BUS 1 | 66 | 3.2849 | 375.5086 | 2.5656 | 97.7621 | 2.116 | 3.0022 | 114.4007 | 3.0539 | 116.3708 | 2.8321 | 12.442 | 4.2228 | 23.0314 | 2.7353 | 12.5517
ATHE | Atherton | FN | ATHE_66kV_BUS 2 | 66 | 3.2849 | 375.5086 | 2.5656 | 97.7621 | 2.116 | 3.0022 | 114.4007 | 3.0539 | 116.3708 | 2.8321 | 12.442 | 4.2228 | 23.0314 | 2.7353 | 12.5517
AWOO | Awoonga | CA | AWOO_11kV_TEF T1 | 11 | 9.9563 | 189.6932 | 11.0706 | 70.3076 | 12.5741 | 10.3271 | 65.5857 | 10.971 | 69.6752 | 0.12374 | 0.69068 | 0.0313 | 0.4849 | 0.12261 | 0.6971
AWOO | Awoonga | CA | AWOO_11kV_TEF T2 | 11 | 9.9563 | 189.6932 | 11.0706 | 70.3076 | 12.5741 | 10.3271 | 65.5857 | 10.971 | 69.6752 | 0.12374 | 0.69068 | 0.0313 | 0.4849 | 0.12261 | 0.6971
AWOO | Awoonga | CA | AWOO_66kV_TEF T1 | 66 | 4.6752 | 534.4484 | 3.1587 | 120.3626 | 2.3898 | 4.1094 | 156.5881 | 4.3166 | 164.4847 | 3.3722 | 8.3074 | 5.9562 | 21.0724 | 3.3788 | 8.3484
AWOO | Awoonga | CA | AWOO_66kV_TEF T2 | 66 | 4.6752 | 534.4484 | 3.1587 | 120.3626 | 2.3898 | 4.1094 | 156.5881 | 4.3166 | 164.4847 | 3.3722 | 8.3074 | 5.9562 | 21.0724 | 3.3788 | 8.3484
AYRZ | Ayr (TF2) | NQ | AYRZ_11kV_BUS 2 | 11 | 9.3802 | 178.7166 | 10.2399 | 65.0321 | 11.2653 | 9.7289 | 61.7866 | 10.0408 | 63.7677 | 0.08684 | 0.73968 | 0.03171 | 0.5572 | 0.08396 | 0.73977
AYRZ | Ayr (TF3) | NQ | AYRZ_11kV_BUS 3 | 11 | 9.3802 | 178.7166 | 10.2399 | 65.0321 | 11.2653 | 9.7289 | 61.7866 | 10.0408 | 63.7677 | 0.08684 | 0.73968 | 0.03171 | 0.5572 | 0.08396 | 0.73977
AYRZ | Ayr | NQ | AYRZ_66kV_BUS 1 | 66 | 6.1081 | 698.2468 | 5.1986 | 198.0919 | 4.5065 | 5.6465 | 215.1608 | 5.8659 | 223.5207 | 1.9845 | 6.5691 | 2.1767 | 10.2805 | 1.8812 | 6.5723
AYRZ | Ayr | NQ | AYRZ_66kV_BUS 2 | 66 | 6.1081 | 698.2468 | 5.1986 | 198.0919 | 4.5065 | 5.6465 | 215.1608 | 5.8659 | 223.5207 | 1.9845 | 6.5691 | 2.1767 | 10.2805 | 1.8812 | 6.5723
AYRZ | Ayr | NQ | AYRZ_66kV_BUS 3 | 66 | 6.1081 | 698.2468 | 5.1986 | 198.0919 | 4.5065 | 5.6465 | 215.1608 | 5.8659 | 223.5207 | 1.9845 | 6.5691 | 2.1767 | 10.2805 | 1.8812 | 6.5723
BABI | Babinda | FN | BABI_22kV_BUS 1 | 22 | 1.2442 | 47.4097 | 0.79119 | 10.0494 | 0.56916 | 1.0158 | 12.9028 | 1.2046 | 15.3008 | 7.7432 | 8.1333 | 10.832 | 29.7007 | 7.7356 | 8.149
BALB | Balberra | MK | BALB_11kV_TEF T1 | 11 | 3.631 | 69.1798 | 3.9232 | 24.9159 | 4.2714 | 3.7067 | 23.5407 | 3.8908 | 24.7101 | 0.26077 | 1.9062 | 0.07464 | 1.4929 | 0.2607 | 1.9095
BALB | Balberra (with MACK G1) | MK | BALB_1MB REG | 11 | 3.591 | 68.4181 | 3.8775 | 24.6254 | 4.2778 | 3.7117 | 23.5724 | 3.8454 | 24.4214 | 0.28084 | 1.925 | 0.08803 | 1.5054 | 0.27408 | 1.9221
BALB | Balberra (with MACK G1) | MK | MOUNT ALICE | 11 | 3.591 | 68.4181 | 3.8775 | 24.6254 | 4.2778 | 3.7117 | 23.5724 | 3.8454 | 24.4214 | 0.28084 | 1.925 | 0.08803 | 1.5054 | 0.27408 | 1.9221
BALB | Balberra | MK | BALB_33kV_TEF T1 | 33 | 5.1368 | 293.605 | 3.3698 | 64.2025 | 2.51 | 4.4252 | 84.311 | 4.7887 | 91.2377 | 1.6751 | 3.7203 | 2.504 | 10.2459 | 1.6745 | 3.7501
BAMB | Bambaroo | NQ | BAMB_11kV_BUS | 11 | 1.2382 | 23.5911 | 1.2884 | 8.1825 | 1.3565 | 1.2545 | 7.9672 | 1.286 | 8.1672 | 0.92189 | 5.5661 | 0.51738 | 4.9397 | 0.90678 | 5.5608
BAMB | Bambaroo | NQ | BAMB_66kV_TEF T1 | 66 | 1.5998 | 182.8838 | 1.2783 | 48.7094 | 1.0695 | 1.4438 | 55.0142 | 1.5184 | 57.8591 | 14.0942 | 22.0864 | 20.5254 | 41.0589 | 14.0183 | 22.3607
BARC | Barcaldine T072 (TF1) | CA | BARC_11kV_BUS 1 | 11 | 9.6633 | 184.1105 | 0.61564 | 3.9098 | 0.33226 | 7.9949 | 50.7744 | 8.0247 | 50.9634 | 0.06608 | 0.71991 | 0 | 32.5367 | 0.07154 | 0.78558
BARC | Barcaldine T072 (TF2) | CA | BARC_11kV_BUS 2 | 11 | 9.6633 | 184.1105 | 0.61564 | 3.9098 | 0.33226 | 7.9949 | 50.7744 | 8.0247 | 50.9634 | 0.06608 | 0.71991 | 0 | 32.5367 | 0.07154 | 0.78558
BARC | Barcaldine T072 | CA | BARC_132kV_BUS 1 | 132 | 1.7872 | 408.6059 | 1.5999 | 121.9308 | 1.7273 | 1.6679 | 127.1117 | 1.7093 | 130.2663 | 6.1346 | 46.504 | 4.9814 | 53.6705 | 7.5943 | 55.8991
BARC | Barcaldine T072 | CA | BARC_132kV_BUS 2 | 132 | 1.7872 | 408.6059 | 1.5999 | 121.9308 | 1.7273 | 1.6679 | 127.1117 | 1.7093 | 130.2663 | 6.1346 | 46.504 | 4.9814 | 53.6705 | 7.5943 | 55.8991
BARC | Barcaldine T072 (TF5) | CA | BARC_22kV_BUS LH | 22 | 4.714 | 179.6267 | 5.3451 | 67.8918 | 7.0397 | 5.2792 | 67.0553 | 5.3348 | 67.7606 | 0.21551 | 2.9561 | 0.06227 | 1.575 | 0.20164 | 3.2962
BARC | Barcaldine T072 (TF6) | CA | BARC_22kV_BUS RH | 22 | 4.714 | 179.6267 | 5.3451 | 67.8918 | 7.0397 | 5.2792 | 67.0553 | 5.3348 | 67.7606 | 0.21551 | 2.9561 | 0.06227 | 1.575 | 0.20164 | 3.2962
BARC | Barcaldine T072 | CA | BARC_66kV_BUS 1 | 66 | 2.3485 | 268.4728 | 2.7355 | 104.2373 | 3.8454 | 2.7866 | 106.1856 | 2.7271 | 103.9176 | 1.8032 | 17.7563 | 1.1645 | 7.8101 | 1.9946 | 20.1331
BARC | Barcaldine T072 | CA | BARC_66kV_BUS 2 | 66 | 2.3485 | 268.4728 | 2.7355 | 104.2373 | 3.8454 | 2.7866 | 106.1856 | 2.7271 | 103.9176 | 1.8032 | 17.7563 | 1.1645 | 7.8101 | 1.9946 | 20.1331
BARC | Barcaldine T072 | CA | BARC_66kV_BUS 3 | 66 | 2.3485 | 268.4728 | 2.7355 | 104.2373 | 3.8454 | 2.7866 | 106.1856 | 2.7271 | 103.9176 | 1.8032 | 17.7563 | 1.1645 | 7.8101 | 1.9946 | 20.1331
BARG | Bargara | WB | BARG_11kV_BUS 1 | 11 | 9.8316 | 187.3177 | 11.5647 | 73.4459 | 14.0922 | 10.7807 | 68.4668 | 11.3047 | 71.7948 | 0.10046 | 0.70347 | 0.01788 | 0.38947 | 0.09835 | 0.70641
BARG | Bargara | WB | BARG_11kV_BUS 2 | 11 | 9.8316 | 187.3177 | 11.5647 | 73.4459 | 14.0922 | 10.7807 | 68.4668 | 11.3047 | 71.7948 | 0.10046 | 0.70347 | 0.01788 | 0.38947 | 0.09835 | 0.70641
BARG | Bargara | WB | BARG_66kV_BUS 1 | 66 | 3.4055 | 389.3071 | 2.5074 | 95.5447 | 1.9957 | 3.1275 | 119.1727 | 3.0827 | 117.465 | 3.0591 | 11.9228 | 6.932 | 24.4868 | 3.0245 | 12.0263
BARR | Barratta | NQ | BARR_11kV_TEF T1 | 11 | 3.4558 | 65.8415 | 3.7344 | 23.717 | 4.0556 | 3.4987 | 22.2197 | 3.7283 | 23.6781 | 0.43598 | 1.974 | 0.16328 | 1.5683 | 0.43311 | 1.974
BARR | Barratta | NQ | BARR_66kV_TEF T1 | 66 | 2.2403 | 256.095 | 1.549 | 59.0233 | 1.175 | 1.9303 | 73.553 | 2.1239 | 80.9295 | 9.8173 | 15.9278 | 14.7006 | 41.7526 | 9.714 | 15.931
BEEC | Beecher Switching | CA | BEEC_66kV_pole2112125_tr_line_33766 | 66 | 5.1857 | 592.8006 | 3.6002 | 137.1843 | 2.7548 | 4.541 | 173.0354 | 4.8424 | 184.5211 | 3.2089 | 7.4189 | 4.9899 | 18.1593 | 3.2088 | 7.4354
BEGA | Belgian Gardens | NQ | BEGA_11kV_BUS 1 | 11 | 16.7776 | 319.6553 | 17.7034 | 112.4316 | 18.7351 | 17.1548 | 108.9476 | 17.42 | 110.6322 | 0.02497 | 0.41564 | 0.01121 | 0.35099 | 0.02445 | 0.41565
BEGA | Belgian Gardens (TF1) | NQ | BEGA_66kV_TEF T1 | 66 | 16.7948 | 1919.9063 | 18.3352 | 698.6639 | 20.1512 | 17.7803 | 677.5205 | 17.6178 | 671.329 | 0.59853 | 2.4229 | 0.46501 | 1.8121 | 0.57984 | 2.4234
BEGA | Belgian Gardens (TF2) | NQ | BEGA_66kV_TEF T2 | 66 | 16.8049 | 1921.0595 | 18.3464 | 699.0918 | 20.1638 | 17.7899 | 677.8856 | 17.6298 | 671.7869 | 0.59722 | 2.4217 | 0.46352 | 1.8112 | 0.57853 | 2.4222
BENA | Benarkin | WB | BENA_11kV_TEF T1 | 11 | 3.502 | 66.722 | 3.7801 | 24.007 | 4.1043 | 3.5823 | 22.7507 | 3.7396 | 23.7495 | 0.40081 | 1.9544 | 0.19625 | 1.5454 | 0.40073 | 1.9546
BENA | Benarkin | WB | BENA_66kV_BUS 1 | 66 | 2.5458 | 291.0211 | 1.5556 | 59.2748 | 1.1143 | 2.1714 | 82.7412 | 2.3716 | 90.372 | 7.365 | 14.728 | 11.7588 | 46.9224 | 7.3621 | 14.7354
BERS | Berserker | CA | BERS_11kV_BUS 1 | 11 | 14.6616 | 279.342 | 16.0879 | 102.1718 | 17.8448 | 15.2868 | 97.0846 | 15.7387 | 99.9539 | 0.04013 | 0.47479 | 0.01122 | 0.34925 | 0.04012 | 0.47547
BERS | Berserker | CA | BERS_11kV_BUS 2 | 11 | 14.6616 | 279.342 | 16.0879 | 102.1718 | 17.8448 | 15.2868 | 97.0846 | 15.7387 | 99.9539 | 0.04013 | 0.47479 | 0.01122 | 0.34925 | 0.04012 | 0.47547
BERS | Berserker | CA | BERS_11kV_BUS 3 | 11 | 14.6616 | 279.342 | 16.0879 | 102.1718 | 17.8448 | 15.2868 | 97.0846 | 15.7387 | 99.9539 | 0.04013 | 0.47479 | 0.01122 | 0.34925 | 0.04012 | 0.47547
BERS | Berserker | CA | BERS_66kV_BUS 1 | 66 | 9.0382 | 1033.2004 | 8.3662 | 318.7945 | 7.8236 | 8.8115 | 335.762 | 8.6631 | 330.108 | 1.0408 | 4.5194 | 1.4459 | 5.5476 | 1.0406 | 4.5438
BERS | Berserker | CA | BERS_66kV_BUS 2 | 66 | 9.0382 | 1033.2004 | 8.3662 | 318.7945 | 7.8236 | 8.8115 | 335.762 | 8.6631 | 330.108 | 1.0408 | 4.5194 | 1.4459 | 5.5476 | 1.0406 | 4.5438
BEWE | Bedford Weir | CA | BEWE_22kV_BUS 1 | 22 | 4.1066 | 156.4837 | 4.8377 | 61.4473 | 5.8641 | 4.3994 | 55.8804 | 4.8112 | 61.1104 | 0.82527 | 3.3007 | 0.13699 | 1.8801 | 0.82706 | 3.2967
BEWE | Bedford Weir | CA | BEWE_22kV_BUS 2 | 22 | 4.1066 | 156.4837 | 4.8377 | 61.4473 | 5.8641 | 4.3994 | 55.8804 | 4.8112 | 61.1104 | 0.82527 | 3.3007 | 0.13699 | 1.8801 | 0.82706 | 3.2967
BEWE | Bedford Weir | CA | BEWE_66kV_BUS 1 | 66 | 2.9505 | 337.2828 | 2.1176 | 80.6901 | 1.6461 | 2.6049 | 99.2588 | 2.765 | 105.3616 | 6.1945 | 12.785 | 10.0124 | 29.4546 | 6.2106 | 12.7492
BEWE | Bedford Weir | CA | BEWE_66kV_BUS 2 | 66 | 2.9505 | 337.2828 | 2.1176 | 80.6901 | 1.6461 | 2.6049 | 99.2588 | 2.765 | 105.3616 | 6.1945 | 12.785 | 10.0124 | 29.4546 | 6.2106 | 12.7492
BEWE | Bedford Weir | CA | BEWE_66kV_BUS TRANSFER | 66 | 2.9505 | 337.2828 | 2.1176 | 80.6901 | 1.6461 | 2.6049 | 99.2588 | 2.765 | 105.3616 | 6.1945 | 12.785 | 10.0124 | 29.4546 | 6.2106 | 12.7492
BILO | Biloela T026 (TF1) | CA | BILO_11kV_BUS 1 | 11 | 15.8141 | 301.2986 | 17.7335 | 112.6231 | 20.2116 | 16.9247 | 107.4861 | 17.1075 | 108.647 | 0.03146 | 0.44064 | 0.01537 | 0.2974 | 0.03148 | 0.4412
BILO | Biloela T026 (TF2) | CA | BILO_11kV_BUS 2 | 11 | 15.8141 | 301.2986 | 17.7335 | 112.6231 | 20.2116 | 16.9247 | 107.4861 | 17.1075 | 108.647 | 0.03146 | 0.44064 | 0.01537 | 0.2974 | 0.03148 | 0.4412
BILO | Biloela T026 | CA | BILO_66KV TRANSFER BUS | 66 | 8.078 | 923.437 | 9.8929 | 376.9701 | 12.8226 | 9.5517 | 363.9691 | 9.4168 | 358.8295 | 0.57906 | 5.1566 | 0.32724 | 2.2907 | 0.57989 | 5.1766
BILO | Biloela T026 | CA | BILO_66kV_BUS NORTH | 66 | 8.078 | 923.437 | 9.8929 | 376.9701 | 12.8226 | 9.5517 | 363.9691 | 9.4168 | 358.8295 | 0.57906 | 5.1566 | 0.32724 | 2.2907 | 0.57989 | 5.1766
BILO | Biloela T026 | CA | BILO_66kV_BUS SOUTH | 66 | 8.078 | 923.437 | 9.8929 | 376.9701 | 12.8226 | 9.5517 | 363.9691 | 9.4168 | 358.8295 | 0.57906 | 5.1566 | 0.32724 | 2.2907 | 0.57989 | 5.1766
BING | Bingegang | CA | BING_22kV_BUS 1 | 22 | 1.8546 | 70.6718 | 2.3463 | 29.8023 | 3.1756 | 2.1144 | 26.8562 | 2.3941 | 30.4094 | 2.7652 | 7.0076 | 0.26352 | 2.8868 | 2.767 | 7.0037
BING | Bingegang | CA | BING_66kV_BUS 3 | 66 | 0.9661 | 110.4397 | 0.60555 | 23.0746 | 0.43867 | 0.82685 | 31.5071 | 0.90173 | 34.3604 | 22.5152 | 37.0877 | 40.4319 | 115.108 | 22.5313 | 37.0519
BLAC | Blackwater T032 (TF4) | CA | BLAC_11kV_TEF T4 | 11 | 19.2601 | 366.9542 | 8.3437 | 52.9895 | 5.3104 | 16.6326 | 105.6312 | 17.1805 | 109.1108 | 0.04112 | 0.36038 | 2e-05 | 1.7907 | 0.04159 | 0.35939
BLAC | Blackwater T032 (TF5) | CA | BLAC_11kV_TEF T5 | 11 | 25.497 | 485.7832 | 14.6948 | 93.3246 | 10.2796 | 22.1906 | 140.9293 | 23.2096 | 147.4011 | 0.03155 | 0.27217 | 1e-05 | 0.88154 | 0.03205 | 0.27108
BLAC | Blackwater T032 | CA | BLAC_22kV_BUS 1 | 22 | 6.3293 | 241.178 | 5.2375 | 66.5256 | 4.454 | 5.7476 | 73.004 | 6.0873 | 77.3193 | 0.23475 | 2.195 | 0.00025 | 3.6033 | 0.23669 | 2.1908
BLAC | Blackwater T032 | CA | BLAC_22kV_BUS 2 | 22 | 6.3293 | 241.178 | 5.2375 | 66.5256 | 4.454 | 5.7476 | 73.004 | 6.0873 | 77.3193 | 0.23475 | 2.195 | 0.00025 | 3.6033 | 0.23669 | 2.1908
BLAC | Blackwater T032 | CA | BLAC_66kV_BUS EAST | 66 | 8.4953 | 971.1458 | 11.122 | 423.8037 | 15.9427 | 10.6671 | 406.4704 | 11.0367 | 420.5531 | 0.87984 | 4.8549 | 0.13687 | 1.4691 | 0.89594 | 4.8192
BLAC | Blackwater T032 | CA | BLAC_66kV_BUS TRANSFER | 66 | 8.4953 | 971.1458 | 11.122 | 423.8037 | 15.9427 | 10.6671 | 406.4704 | 11.0367 | 420.5531 | 0.87984 | 4.8549 | 0.13687 | 1.4691 | 0.89594 | 4.8192
BLAC | Blackwater T032 | CA | BLAC_66kV_BUS WEST | 66 | 8.4953 | 971.1458 | 11.122 | 423.8037 | 15.9427 | 10.6671 | 406.4704 | 11.0367 | 420.5531 | 0.87984 | 4.8549 | 0.13687 | 1.4691 | 0.89594 | 4.8192
BLAK | Blackall (TF1) | CA | BLAK_22kV_BUS 1 | 22 | 1.2291 | 46.8354 | 1.6174 | 20.5439 | 2.4472 | 1.5582 | 19.7921 | 1.6776 | 21.3085 | 3.5312 | 10.8051 | 0.26355 | 2.9528 | 3.5574 | 11.0926
BLAK | Blackall (TF2) | CA | BLAK_22kV_BUS 2 | 22 | 1.2291 | 46.8354 | 1.6174 | 20.5439 | 2.4472 | 1.5582 | 19.7921 | 1.6776 | 21.3085 | 3.5312 | 10.8051 | 0.26355 | 2.9528 | 3.5574 | 11.0926
BLAK | Blackall | CA | BLAK_66kV_BUS | 66 | 0.54759 | 62.5979 | 0.37724 | 14.3748 | 0.29447 | 0.4791 | 18.2563 | 0.50195 | 19.1269 | 29.4092 | 70.6709 | 50.1209 | 171.0203 | 29.6449 | 73.2581
BLOO | Bloomfield SS | FN | BLOO_22kV_BUS | 22 | 0.46664 | 17.7815 | 0.34239 | 4.349 | 0.26852 | 0.40819 | 5.1848 | 0.44405 | 5.6402 | 11.9264 | 27.4634 | 14.6759 | 61.4005 | 11.8537 | 27.3581
BLRI | Black River (TF1) | NQ | BLRI_11kV_BUS 1 | 11 | 13.2234 | 251.9393 | 14.1576 | 89.9128 | 15.0974 | 13.6293 | 86.5577 | 13.8511 | 87.9664 | 0.03914 | 0.52685 | 0.01771 | 0.42786 | 0.03649 | 0.52267
BLRI | Black River (TF2) | NQ | BLRI_11kV_BUS 2 | 11 | 13.2234 | 251.9393 | 14.1576 | 89.9128 | 15.0974 | 13.6293 | 86.5577 | 13.8511 | 87.9664 | 0.03914 | 0.52685 | 0.01771 | 0.42786 | 0.03649 | 0.52267
BLRI | Black River | NQ | BLRI_11kV_BUS 3 | 11 | 13.2234 | 251.9393 | 14.1576 | 89.9128 | 15.0974 | 13.6293 | 86.5577 | 13.8511 | 87.9664 | 0.03914 | 0.52685 | 0.01771 | 0.42786 | 0.03649 | 0.52267
BLRI | Black River | NQ | BLRI_66kV_BUS 1 | 66 | 10.2826 | 1175.4538 | 8.8828 | 338.4796 | 7.8053 | 9.6492 | 367.6823 | 9.8068 | 373.6881 | 0.79878 | 3.9974 | 0.93464 | 5.9398 | 0.75085 | 3.9994
BLRI | Black River | NQ | BLRI_66kV_BUS 2 | 66 | 10.2826 | 1175.4538 | 8.8828 | 338.4796 | 7.8053 | 9.6492 | 367.6823 | 9.8068 | 373.6881 | 0.79878 | 3.9974 | 0.93464 | 5.9398 | 0.75085 | 3.9994
BLUE | Bluewater | NQ | BLUE_11kV_BUS 1 | 11 | 3.7045 | 70.5794 | 3.9048 | 24.7989 | 4.1241 | 3.7118 | 23.573 | 3.9131 | 24.8516 | 0.26854 | 1.8666 | 0.07992 | 1.5985 | 0.26721 | 1.8667
BLUE | Bluewater | NQ | BLUE_66kV_TEF T1 | 66 | 3.5517 | 406.0104 | 2.5579 | 97.4678 | 1.9803 | 3.0374 | 115.7399 | 3.4194 | 130.2969 | 6.7901 | 9.6527 | 9.1501 | 24.3074 | 6.7424 | 9.6552
BLVA | Blue Valley T183 | NQ | BLVA_11kV_BUS 1 | 11 | 8.2194 | 156.5998 | 5.6723 | 36.024 | 4.3246 | 7.2585 | 46.0978 | 7.6162 | 48.3696 | 0.08885 | 0.84528 | 0 | 2 | 0.08899 | 0.84521
BLVA | Blue Valley T183 | NQ | BLVA_132kV_TEF T1 | 132 | 3.5666 | 815.4434 | 2.3548 | 179.4613 | 1.7571 | 3.1834 | 242.6085 | 3.2394 | 246.873 | 7.5561 | 22.2567 | 17.0235 | 57.3418 | 7.5753 | 22.2461
BOCR | Boat Creek T130 (TF1) | CA | BOCR_11kV_TEF T1 | 11 | 22.5918 | 430.4313 | 0 | 0 | 0 | 19.541 | 124.1023 | 19.541 | 124.1023 | 0.01666 | 0.30878 | 135802466.7808 | -9.306 | 0.0166 | 0.30955
BOCR | Boat Creek T130 (TF2) | CA | BOCR_11kV_TEF T2 | 11 | 22.8803 | 435.9286 | 0 | 0 | 0 | 19.7903 | 125.6853 | 19.7903 | 125.6853 | 0.01676 | 0.30487 | 135802469.4643 | -0.39741 | 0.0167 | 0.30564
BOCR | Boat Creek T130 (TF1) | CA | BOCR_132kV_TEF T1 | 132 | 12.2906 | 2810.0166 | 13.4636 | 1026.0661 | 15.1603 | 13.184 | 1004.7575 | 12.8635 | 980.3274 | 0.39193 | 6.8096 | 0.50248 | 4.9013 | 0.40108 | 6.924
BOCR | Boat Creek T130 (TF2) | CA | BOCR_132kV_TEF T2 | 132 | 12.3526 | 2824.183 | 13.56 | 1033.411 | 15.3102 | 13.2675 | 1011.1173 | 12.9541 | 987.2376 | 0.38443 | 6.7758 | 0.4862 | 4.838 | 0.39359 | 6.8902
BOCR | Boat Creek T130 | CA | BOCR_66kV_BUS 1 | 66 | 10.2039 | 1166.4656 | 12.3468 | 470.4773 | 15.7592 | 11.9759 | 456.3423 | 11.6802 | 445.0759 | 0.15109 | 4.1051 | 0.17039 | 1.9361 | 0.14829 | 4.1327
BOCR | Boat Creek T130 | CA | BOCR_66kV_BUS 2 | 66 | 10.2039 | 1166.4656 | 12.3468 | 470.4773 | 15.7592 | 11.9759 | 456.3423 | 11.6802 | 445.0759 | 0.15109 | 4.1051 | 0.17039 | 1.9361 | 0.14829 | 4.1327
BOCR | Boat Creek T130 | CA | BOCR_66kV_BUS 3 | 66 | 10.2039 | 1166.4656 | 12.3468 | 470.4773 | 15.7592 | 11.9759 | 456.3423 | 11.6802 | 445.0759 | 0.15109 | 4.1051 | 0.17039 | 1.9361 | 0.14829 | 4.1327
BODA | Boondooma Dam (TF1) | WB | BODA_11kV_BUS 1 | 11 | 2.9197 | 55.6272 | 3.4508 | 21.9159 | 4.2117 | 3.1631 | 20.0885 | 3.4132 | 21.6765 | 0.62026 | 2.3112 | 0.14664 | 1.2906 | 0.61905 | 2.3119
BODA | Boondooma Dam (TF2) | WB | BODA_11kV_BUS 2 | 11 | 2.9197 | 55.6272 | 3.4508 | 21.9159 | 4.2117 | 3.1631 | 20.0885 | 3.4132 | 21.6765 | 0.62026 | 2.3112 | 0.14664 | 1.2906 | 0.61905 | 2.3119
BODA | Boondooma Dam | WB | BODA_66kV_BUS OVERHEAD | 66 | 1.0349 | 118.3024 | 0.58171 | 22.1661 | 0.40273 | 0.88248 | 33.627 | 0.95322 | 36.3227 | 17.0505 | 36.7446 | 30.4786 | 132.8214 | 17.007 | 36.771
BOHL | Bohle (TF1) | NQ | BOHL_11kV_BUS 1 | 11 | 19.1486 | 364.8293 | 20.746 | 131.7551 | 22.6193 | 19.8687 | 126.1835 | 20.2787 | 128.7872 | 0.03216 | 0.36341 | 0.0137 | 0.28054 | 0.03095 | 0.36334
BOHL | Bohle (TF2) | NQ | BOHL_11kV_BUS 2 | 11 | 19.1486 | 364.8293 | 20.746 | 131.7551 | 22.6193 | 19.8687 | 126.1835 | 20.2787 | 128.7872 | 0.03216 | 0.36341 | 0.0137 | 0.28054 | 0.03095 | 0.36334
BOHL | Bohle | NQ | BOHL_66kV_BUS 1 | 66 | 12.9182 | 1476.7455 | 10.7481 | 409.5568 | 9.1901 | 12.085 | 460.5004 | 12.116 | 461.6835 | 0.6723 | 3.1743 | 1.0066 | 5.1172 | 0.64051 | 3.1758
BOHL | Bohle | NQ | BOHL_66kV_BUS 2 | 66 | 12.9182 | 1476.7455 | 10.7481 | 409.5568 | 9.1901 | 12.085 | 460.5004 | 12.116 | 461.6835 | 0.6723 | 3.1743 | 1.0066 | 5.1172 | 0.64051 | 3.1758
BOHL | Bohle | NQ | BOHL_66kV_BUS 3 | 66 | 12.9182 | 1476.7455 | 10.7481 | 409.5568 | 9.1901 | 12.085 | 460.5004 | 12.116 | 461.6835 | 0.6723 | 3.1743 | 1.0066 | 5.1172 | 0.64051 | 3.1758
BOPU | Bocoolima Pumps | CA | BOPU_11kV_TEF T1 | 11 | 3.7803 | 72.0254 | 4.3993 | 27.9392 | 5.2453 | 3.9688 | 25.2054 | 4.4088 | 27.9993 | 0.4558 | 1.7909 | 0.05413 | 1.0826 | 0.45582 | 1.7916
BOPU | Bocoolima Pumps | CA | BOPU_11kV_TEF T2 | 11 | 3.7803 | 72.0254 | 4.3993 | 27.9392 | 5.2453 | 3.9688 | 25.2054 | 4.4088 | 27.9993 | 0.4558 | 1.7909 | 0.05413 | 1.0826 | 0.45582 | 1.7916
BOPU | Bocoolima Pumps | CA | BOPU_66kV_TEF T1 | 66 | 1.4299 | 163.4568 | 0.86826 | 33.0853 | 0.62041 | 1.2185 | 46.4322 | 1.3313 | 50.7302 | 14.4603 | 25.5002 | 25.3442 | 83.2519 | 14.461 | 25.5264
BOPU | Bocoolima Pumps | CA | BOPU_66kV_TEF T2 | 66 | 1.4299 | 163.4568 | 0.86826 | 33.0853 | 0.62041 | 1.2185 | 46.4322 | 1.3313 | 50.7302 | 14.4603 | 25.5002 | 25.3442 | 83.2519 | 14.461 | 25.5264
BORE | Boyne Residential | CA | BORE_11kV_BUS LH | 11 | 8.6983 | 165.7247 | 9.8104 | 62.3045 | 11.2429 | 9.0491 | 57.4693 | 9.7336 | 61.8168 | 0.16433 | 0.78617 | 0.03865 | 0.53138 | 0.16439 | 0.78696
BORE | Boyne Residential | CA | BORE_11kV_BUS RH | 11 | 8.6983 | 165.7247 | 9.8104 | 62.3045 | 11.2429 | 9.0491 | 57.4693 | 9.7336 | 61.8168 | 0.16433 | 0.78617 | 0.03865 | 0.53138 | 0.16439 | 0.78696
BORE | Boyne Residential | CA | BORE_66kV_TEF T1 | 66 | 4.0984 | 468.5153 | 2.8173 | 107.3523 | 2.145 | 3.5772 | 136.3076 | 3.8272 | 145.8341 | 4.5244 | 9.1722 | 7.394 | 23.1225 | 4.5265 | 9.2008
BORE | Boyne Residential | CA | BORE_66kV_TEF T2 | 66 | 4.0984 | 468.5153 | 2.8173 | 107.3523 | 2.145 | 3.5772 | 136.3076 | 3.8272 | 145.8341 | 4.5244 | 9.1722 | 7.394 | 23.1225 | 4.5265 | 9.2008
BOWE | Bowen | NQ | BOWE_11kV_BUS 1 | 11 | 8.0452 | 153.2814 | 9.6647 | 61.3789 | 12.0636 | 8.7821 | 55.7739 | 9.6303 | 61.1607 | 0.19527 | 0.8461 | 0.01847 | 0.43772 | 0.19566 | 0.84568
BOWE | Bowen | NQ | BOWE_11kV_BUS 2 | 11 | 8.0452 | 153.2814 | 9.6647 | 61.3789 | 12.0636 | 8.7821 | 55.7739 | 9.6303 | 61.1607 | 0.19527 | 0.8461 | 0.01847 | 0.43772 | 0.19566 | 0.84568
BOWE | Bowen | NQ | BOWE_66kV_BUS 1 | 66 | 2.6164 | 299.1002 | 2.5522 | 97.2521 | 2.4888 | 2.5413 | 96.8379 | 2.6289 | 100.1732 | 6.3646 | 14.7016 | 5.9337 | 16.2048 | 6.3788 | 14.6865
BOWE | Bowen | NQ | BOWE_66kV_BUS 2 | 66 | 2.6164 | 299.1002 | 2.5522 | 97.2521 | 2.4888 | 2.5413 | 96.8379 | 2.6289 | 100.1732 | 6.3646 | 14.7016 | 5.9337 | 16.2048 | 6.3788 | 14.6865
BROD | Broadlea | MK | BROD_11kV_TEF T1 | 11 | 14.9879 | 285.5572 | 0 | 0 | 0 | 12.9746 | 82.3999 | 12.9746 | 82.3999 | 0.04903 | 0.46352 | 108910890.0557 | -5.4146 | 0.04912 | 0.46389
BROD | Broadlea | SW | BROD_11kV_TEF T2 | 11 | 14.9644 | 285.1098 | 0 | 0 | 0 | 12.9543 | 82.2709 | 12.9543 | 82.2709 | 0.04913 | 0.46425 | 108910893.0158 | -5.3941 | 0.04921 | 0.46462
BROD | Broadlea | MK | BROD_132kV_BUS 1 | 132 | 3.737 | 854.4037 | 4.1484 | 316.148 | 4.6667 | 3.8414 | 292.756 | 4.1293 | 314.6932 | 5.3474 | 21.7859 | 1.7426 | 15.7079 | 5.36 | 21.8392
BROD | Broadlea | MK | BROD_132kV_BUS 2 | 132 | 3.737 | 854.4037 | 4.1484 | 316.148 | 4.6667 | 3.8414 | 292.756 | 4.1293 | 314.6932 | 5.3474 | 21.7859 | 1.7426 | 15.7079 | 5.36 | 21.8392
BROD | Broadlea | MK | BROD_66kV_BUS 1 | 66 | 5.0063 | 572.2943 | 6.3092 | 240.4115 | 8.5408 | 5.9296 | 225.9491 | 6.2354 | 237.5995 | 1.4117 | 8.2528 | 0.16953 | 3.1856 | 1.4148 | 8.2661
BROD | Broadlea | MK | BROD_66kV_BUS 2 | 66 | 5.0063 | 572.2943 | 6.3092 | 240.4115 | 8.5408 | 5.9296 | 225.9491 | 6.2354 | 237.5995 | 1.4117 | 8.2528 | 0.16953 | 3.1856 | 1.4148 | 8.2661
BROD | Broadlea | MK | BROD_66kV_BUS TRANSFER | 66 | 5.0063 | 572.2943 | 6.3092 | 240.4115 | 8.5408 | 5.9296 | 225.9491 | 6.2354 | 237.5995 | 1.4117 | 8.2528 | 0.16953 | 3.1856 | 1.4148 | 8.2661
BROX | Broxburn | SW | BROX_11kV_BUS T1 | 11 | 3.6997 | 70.4888 | 4.6804 | 29.7245 | 6.2448 | 4.2124 | 26.7521 | 4.732 | 30.0525 | 0.58842 | 1.7945 | 0.03716 | 0.74315 | 0.57296 | 1.7768
BROX | Broxburn | SW | BROX_11kV_BUS T3 | 11 | 3.6997 | 70.4888 | 4.6804 | 29.7245 | 6.2448 | 4.2124 | 26.7521 | 4.732 | 30.0525 | 0.58842 | 1.7945 | 0.03716 | 0.74315 | 0.57296 | 1.7768
BROX | Broxburn | SW | BROX_33kV_BUS | 33 | 1.9363 | 110.6742 | 1.289 | 24.5592 | 0.94735 | 1.6733 | 31.8799 | 1.834 | 34.9417 | 5.2738 | 9.4534 | 7.9985 | 26.4215 | 5.1347 | 9.2945
BUCE | Bundaberg Central | WB | BUCE_11kV_BUS 1 | 11 | 15.3263 | 292.0048 | 16.4509 | 104.4772 | 18.4344 | 15.7371 | 99.9438 | 16.3516 | 103.8466 | 0.05321 | 0.45273 | 0.01131 | 0.34674 | 0.04762 | 0.46964
BUCE | Bundaberg Central | WB | BUCE_11kV_BUS 2 | 11 | 15.3263 | 292.0048 | 16.4509 | 104.4772 | 18.4344 | 15.7371 | 99.9438 | 16.3516 | 103.8466 | 0.05321 | 0.45273 | 0.01131 | 0.34674 | 0.04762 | 0.46964
BUCE | Bundaberg Central | WB | BUCE_11kV_BUS 3 | 11 | 15.3263 | 292.0048 | 16.4509 | 104.4772 | 18.4344 | 15.7371 | 99.9438 | 16.3516 | 103.8466 | 0.05321 | 0.45273 | 0.01131 | 0.34674 | 0.04762 | 0.46964
BUCE | Bundaberg Central | WB | BUCE_66kV_BUS 1 | 66 | 5.7112 | 652.8812 | 5.0037 | 190.6647 | 4.5138 | 5.4721 | 208.5154 | 5.3486 | 203.8079 | 1.4341 | 7.1982 | 2.373 | 10.0665 | 1.4119 | 7.3204
BUCE | Bundaberg Central | WB | BUCE_66kV_BUS 2 | 66 | 5.7112 | 652.8812 | 5.0037 | 190.6647 | 4.5138 | 5.4721 | 208.5154 | 5.3486 | 203.8079 | 1.4341 | 7.1982 | 2.373 | 10.0665 | 1.4119 | 7.3204
BUCR | BULLI CREEK | SW | BUCR_132kV_BUS 1 | 132 | 4.2201 | 964.8415 | 4.6343 | 353.1835 | 5.1273 | 4.536 | 345.6897 | 4.3943 | 334.8875 | 0.84427 | 19.8481 | 1.3853 | 14.5235 | 0.76104 | 19.8168
BUDA | Burdekin Dam | NQ | BUDA_11kV_TEF T1 | 11 | 1.0113 | 19.2679 | 1.2803 | 8.1312 | 1.7383 | 1.1687 | 7.4224 | 1.2958 | 8.2294 | 2.4847 | 6.4455 | 0.33808 | 2.5945 | 2.4901 | 6.4428
BUDA | Burdekin Dam | NQ | BUDA_11kV_TEF T2 | 11 | 1.0113 | 19.2679 | 1.2803 | 8.1312 | 1.7383 | 1.1687 | 7.4224 | 1.2958 | 8.2294 | 2.4847 | 6.4455 | 0.33808 | 2.5945 | 2.4901 | 6.4428
BUDA | Burdekin Dam | NQ | BUDA_33kV_BUS | 33 | 0.52817 | 30.189 | 0.29564 | 5.6328 | 0.20365 | 0.44436 | 8.4662 | 0.49162 | 9.3667 | 19.3199 | 34.6591 | 31.5099 | 131.4546 | 19.3677 | 34.6342
BUDG | Burnett Dam Generator | WB | BUDG_11kV_GEN BUDG G1 | 11 | 1.4376 | 27.3894 | 0.4697 | 2.983 | 0.2766 | 1.2749 | 8.0968 | 1.2593 | 7.9976 | 0.70735 | 4.8079 | 5.6719 | 34.5661 | 0.4828 | 4.7165
BULL | Bullyard | WB | BULL_11kV_BUS | 11 | 5.3382 | 101.7061 | 5.9782 | 37.9669 | 6.7925 | 5.5169 | 35.0369 | 5.9449 | 37.7552 | 0.27434 | 1.2797 | 0.06661 | 0.89012 | 0.27365 | 1.2818
BULL | Bullyard | WB | BULL_66kV_BUS | 66 | 2.6374 | 301.492 | 1.8829 | 71.7487 | 1.4625 | 2.2921 | 87.3399 | 2.494 | 95.035 | 7.4785 | 14.0249 | 10.6755 | 33.5569 | 7.4536 | 14.1023
BUND | Bundaberg T020 | WB | BUND_11kV_TEF T3 | 11 | 14.4761 | 275.8064 | 0 | 0 | 0 | 12.5098 | 79.448 | 12.5098 | 79.448 | 0.02988 | 0.4817 | 154929579.7161 | -5.9869 | 0.02918 | 0.48381
BUND | Bundaberg T020 | WB | BUND_132kV_BUS 1 | 132 | 7.5305 | 1721.6931 | 7.4967 | 571.3271 | 7.571 | 7.4486 | 567.6591 | 7.5782 | 577.5374 | 2.1217 | 10.9291 | 1.7225 | 10.9915 | 2.0814 | 11.1018
BUND | Bundaberg T020 | WB | BUND_132kV_BUS 2 | 132 | 7.5305 | 1721.6931 | 7.4967 | 571.3271 | 7.571 | 7.4486 | 567.6591 | 7.5782 | 577.5374 | 2.1217 | 10.9291 | 1.7225 | 10.9915 | 2.0814 | 11.1018
BUND | Bundaberg T020 | WB | BUND_66kV_BUS | 66 | 7.6358 | 872.8852 | 8.9976 | 342.8544 | 11.1319 | 8.5838 | 327.0861 | 8.6681 | 330.2995 | 0.60939 | 5.4559 | 0.25077 | 2.9127 | 0.58446 | 5.5333
BUND | Bundaberg T020 | WB | BUND_66kV_TEF T1 | 66 | 7.6358 | 872.8852 | 8.9976 | 342.8544 | 11.1319 | 8.5838 | 327.0861 | 8.6681 | 330.2995 | 0.60939 | 5.4559 | 0.25077 | 2.9127 | 0.58446 | 5.5333
BUND | Bundaberg T020 | WB | BUND_66kV_TEF T2 | 66 | 7.6358 | 872.8852 | 8.9976 | 342.8544 | 11.1319 | 8.5838 | 327.0861 | 8.6681 | 330.2995 | 0.60939 | 5.4559 | 0.25077 | 2.9127 | 0.58446 | 5.5333
BUND | Bundaberg T020 | WB | BUND_66kV_TEF T3 | 66 | 7.6358 | 872.8852 | 8.9976 | 342.8544 | 11.1319 | 8.5838 | 327.0861 | 8.6681 | 330.2995 | 0.60939 | 5.4559 | 0.25077 | 2.9127 | 0.58446 | 5.5333
CABO | Caboonbah | WB | CABO_11kV_TEF T1 | 11 | 3.263 | 62.1678 | 3.9506 | 25.0898 | 4.9882 | 3.5609 | 22.6149 | 3.9662 | 25.1889 | 0.64677 | 2.0412 | 0.09069 | 1.0392 | 0.64669 | 2.0414
CABO | Caboonbah | WB | CABO_66kV_BUS 1 | 66 | 1.0161 | 116.1587 | 0.59801 | 22.7871 | 0.42072 | 0.85899 | 32.7321 | 0.94828 | 36.1344 | 20.0191 | 36.0731 | 32.2738 | 125.3276 | 20.0162 | 36.0805
CACI | Cairns City (TF1) | FN | CACI_132kV_TEF T1 | 132 | 6.4101 | 1465.5454 | 7.6169 | 580.4865 | 9.3125 | 7.3481 | 560.0021 | 7.1547 | 545.2644 | 2.0177 | 12.9214 | 1.4128 | 6.8023 | 1.9728 | 12.8491
CACI | Cairns City (TF2) | FN | CACI_132kV_TEF T2 | 132 | 6.4222 | 1468.3216 | 7.6587 | 583.6733 | 9.414 | 7.3446 | 559.7324 | 7.2406 | 551.8102 | 2.0072 | 12.898 | 1.2198 | 6.7013 | 1.9624 | 12.8257
CACI | Cairns City | FN | CACI_22kV_BUS 1 | 22 | 12.6807 | 483.1981 | 9.1247 | 115.8997 | 7.1136 | 11.408 | 144.9011 | 11.6931 | 148.5227 | 0.05821 | 1.1003 | 0 | 2.3936 | 0.05696 | 1.0983
CACI | Cairns City | FN | CACI_22kV_BUS 2 | 22 | 12.6807 | 483.1981 | 9.1247 | 115.8997 | 7.1136 | 11.408 | 144.9011 | 11.6931 | 148.5227 | 0.05821 | 1.1003 | 0 | 2.3936 | 0.05696 | 1.0983
CACI | Cairns City | FN | CACI_22kV_BUS 4 | 22 | 12.6807 | 483.1981 | 9.1247 | 115.8997 | 7.1136 | 11.408 | 144.9011 | 11.6931 | 148.5227 | 0.05821 | 1.1003 | 0 | 2.3936 | 0.05696 | 1.0983
CAFE | Cape Ferguson | NQ | CAFE_11kV_BUS 1 | 11 | 2.3914 | 45.5613 | 2.6726 | 16.9733 | 2.9908 | 2.2857 | 14.5163 | 2.7976 | 17.767 | 1.2735 | 2.6291 | 0.19398 | 2.0891 | 1.273 | 2.6291
CAFE | Cape Ferguson | NQ | CAFE_11kV_TEF 1 | 11 | 2.3914 | 45.5613 | 2.6726 | 16.9733 | 2.9908 | 2.2857 | 14.5163 | 2.7976 | 17.767 | 1.2735 | 2.6291 | 0.19398 | 2.0891 | 1.273 | 2.6291
CAFE | Cape Ferguson | NQ | CAFE_11kV_TEF 2 | 11 | 2.3914 | 45.5613 | 2.6726 | 16.9733 | 2.9908 | 2.2857 | 14.5163 | 2.7976 | 17.767 | 1.2735 | 2.6291 | 0.19398 | 2.0891 | 1.273 | 2.6291
CAFE | Cape Ferguson | NQ | CAFE_66kV_TEF T1 | 66 | 0.96456 | 110.2638 | 0.80097 | 30.5212 | 0.66649 | 0.78284 | 29.8301 | 1.0027 | 38.2061 | 38.864 | 19.4422 | 44.6317 | 59.5027 | 38.8446 | 19.4401
CAFE | Cape Ferguson | NQ | CAFE_66kV_TEF T2 | 66 | 0.96456 | 110.2638 | 0.80097 | 30.5212 | 0.66649 | 0.78284 | 29.8301 | 1.0027 | 38.2061 | 38.864 | 19.4422 | 44.6317 | 59.5027 | 38.8446 | 19.4401
CALE | Calen | MK | CALE_11kV_BUS 1 | 11 | 3.1651 | 60.3033 | 4.0731 | 25.8674 | 5.6377 | 3.5421 | 22.4955 | 4.287 | 27.2258 | 1.0847 | 1.9222 | 0.04959 | 0.80044 | 1.084 | 1.9201
CALE | Calen | MK | CALE_11kV_BUS 2 | 11 | 3.1651 | 60.3033 | 4.0731 | 25.8674 | 5.6377 | 3.5421 | 22.4955 | 4.287 | 27.2258 | 1.0847 | 1.9222 | 0.04959 | 0.80044 | 1.084 | 1.9201
CALE | Calen | MK | CALE_11kV_BUS 3 | 11 | 3.1651 | 60.3033 | 4.0731 | 25.8674 | 5.6377 | 3.5421 | 22.4955 | 4.287 | 27.2258 | 1.0847 | 1.9222 | 0.04959 | 0.80044 | 1.084 | 1.9201
CALE | Calen | MK | CALE_66kV_BUS 1 | 66 | 0.76278 | 87.1976 | 0.53385 | 20.3424 | 0.4035 | 0.62995 | 24.0045 | 0.74718 | 28.4716 | 37.2654 | 40.3848 | 47.4666 | 120.8178 | 37.2393 | 40.3064
CALE | Calen | MK | CALE_66kV_BUS 2 | 66 | 0.76278 | 87.1976 | 0.53385 | 20.3424 | 0.4035 | 0.62995 | 24.0045 | 0.74718 | 28.4716 | 37.2654 | 40.3848 | 47.4666 | 120.8178 | 37.2393 | 40.3064
CALE | Calen | MK | CALE_66kV_BUS 3 | 66 | 0.76278 | 87.1976 | 0.53385 | 20.3424 | 0.4035 | 0.62995 | 24.0045 | 0.74718 | 28.4716 | 37.2654 | 40.3848 | 47.4666 | 120.8178 | 37.2393 | 40.3064
CALL | Calliope | CA | CALL_11kV_BUS LH | 11 | 9.4686 | 180.4002 | 10.456 | 66.4048 | 11.6813 | 9.8775 | 62.7308 | 10.25 | 65.0966 | 0.09976 | 0.73105 | 0.03648 | 0.52766 | 0.09978 | 0.73177
CALL | Calliope | CA | CALL_11kV_BUS RH | 11 | 9.4686 | 180.4002 | 10.456 | 66.4048 | 11.6813 | 9.8775 | 62.7308 | 10.25 | 65.0966 | 0.09976 | 0.73105 | 0.03648 | 0.52766 | 0.09978 | 0.73177
CALL | Calliope | CA | CALL_66kV_TEF T1 | 66 | 5.4663 | 624.8798 | 3.6907 | 140.6329 | 2.7906 | 4.8406 | 184.4516 | 5.0161 | 191.1384 | 2.2782 | 7.322 | 4.1195 | 18.2791 | 2.2789 | 7.3482
CALL | Calliope | CA | CALL_66kV_TEF T2 | 66 | 5.4663 | 624.8798 | 3.6907 | 140.6329 | 2.7906 | 4.8406 | 184.4516 | 5.0161 | 191.1384 | 2.2782 | 7.322 | 4.1195 | 18.2791 | 2.2789 | 7.3482
CANN | Cannonvale (TF1) | MK | CANN_11kV_BUS 1 | 11 | 8.52 | 162.3279 | 10.0289 | 63.6921 | 12.1107 | 9.1522 | 58.124 | 9.9329 | 63.0826 | 0.16986 | 0.80216 | 0.02285 | 0.45662 | 0.16864 | 0.79948
CANN | Cannonvale (TF2) | MK | CANN_11kV_BUS 2 | 11 | 8.52 | 162.3279 | 10.0289 | 63.6921 | 12.1107 | 9.1522 | 58.124 | 9.9329 | 63.0826 | 0.16986 | 0.80216 | 0.02285 | 0.45662 | 0.16864 | 0.79948
CANN | Cannonvale (FDR P6/3) | MK | CANN_66kV_TEF T1 | 66 | 3.1006 | 354.4502 | 2.5027 | 95.3637 | 2.0785 | 2.7709 | 105.5869 | 2.9985 | 114.26 | 5.2925 | 12.4394 | 5.8258 | 22.723 | 5.2487 | 12.343
CANN | Cannonvale (FDR P6/8) | MK | CANN_66kV_TEF T2 | 66 | 3.1006 | 354.4502 | 2.5027 | 95.3637 | 2.0785 | 2.7709 | 105.5869 | 2.9985 | 114.26 | 5.2925 | 12.4394 | 5.8258 | 22.723 | 5.2487 | 12.343
CANO | Cairns North T093 (TF1) | FN | CANO_132kV_TEF T1 | 132 | 6.6795 | 1527.1367 | 8.4796 | 646.2292 | 11.4735 | 8.5515 | 651.7087 | 7.7321 | 589.2658 | 1.7137 | 12.433 | 1.7023 | 4.4261 | 1.6688 | 12.3606
CANO | Cairns North T093 (TF2) | FN | CANO_132kV_TEF T2 | 132 | 6.7091 | 1533.8949 | 8.5521 | 651.7556 | 11.654 | 8.635 | 658.0752 | 7.8122 | 595.368 | 1.69 | 12.3804 | 1.6548 | 4.2924 | 1.6451 | 12.3081
CANO | Cairns North T093 | FN | CANO_22kV_BUS 1 | 22 | 12.0912 | 460.7364 | 8.6089 | 109.3475 | 6.6725 | 10.8651 | 138.0055 | 11.1279 | 141.3427 | 0.05963 | 1.154 | 0 | 2.5615 | 0.05838 | 1.152
CANO | Cairns North T093 | FN | CANO_22kV_BUS 2 | 22 | 12.0912 | 460.7364 | 8.6089 | 109.3475 | 6.6725 | 10.8651 | 138.0055 | 11.1279 | 141.3427 | 0.05963 | 1.154 | 0 | 2.5615 | 0.05838 | 1.152
CANO | Cairns North T093 | FN | CANO_22kV_BUS 3 | 22 | 12.0912 | 460.7364 | 8.6089 | 109.3475 | 6.6725 | 10.8651 | 138.0055 | 11.1279 | 141.3427 | 0.05963 | 1.154 | 0 | 2.5615 | 0.05838 | 1.152
CARD | Cardwell T134 | FN | CARD_22kV_BUS 1 | 22 | 6.4549 | 245.9639 | 6.0832 | 77.2669 | 5.7572 | 6.4587 | 82.0363 | 6.1042 | 77.5332 | 0.1529 | 2.1591 | 0.42988 | 2.5281 | 0.15135 | 2.1639
CARD | Cardwell T134 | FN | CARD_22kV_BUS 2 | 22 | 6.4549 | 245.9639 | 6.0832 | 77.2669 | 5.7572 | 6.4587 | 82.0363 | 6.1042 | 77.5332 | 0.1529 | 2.1591 | 0.42988 | 2.5281 | 0.15135 | 2.1639
CARI | Cape River | NQ | CARI_11kV_TEF T1 | 11 | 0.9881 | 18.8258 | 1.015 | 6.4459 | 1.0471 | 0.99453 | 6.3161 | 1.0101 | 6.4148 | 0.64733 | 7.0404 | 0.41671 | 6.4713 | 0.6465 | 7.0663
CARI | Cape River | NQ | CARI_66kV_BUS 1 | 66 | 1.8961 | 216.7495 | 2.5395 | 96.7679 | 4.0631 | 2.4805 | 94.5201 | 2.7279 | 103.9473 | 8.3023 | 20.4884 | 0.151 | 4.6989 | 8.2723 | 21.4188
CARI | Cape River | NQ | CARI_66kV_BUS 2 | 66 | 1.8961 | 216.7495 | 2.5395 | 96.7679 | 4.0631 | 2.4805 | 94.5201 | 2.7279 | 103.9473 | 8.3023 | 20.4884 | 0.151 | 4.6989 | 8.2723 | 21.4188
CARI | Cape River | NQ | CARI_66kV_BUS 3 | 66 | 1.8961 | 216.7495 | 2.5395 | 96.7679 | 4.0631 | 2.4805 | 94.5201 | 2.7279 | 103.9473 | 8.3023 | 20.4884 | 0.151 | 4.6989 | 8.2723 | 21.4188
CARM | Carmila | MK | CARM_11kV_TEF T1 | 11 | 0.55816 | 10.6344 | 0.67962 | 4.3162 | 0.84917 | 0.54796 | 3.48 | 0.72621 | 4.612 | 7.5511 | 9.9816 | 0.65307 | 6.5307 | 7.556 | 9.9941
CARM | Carmila | MK | CARM_33kV_TEF T1 | 33 | 0.30191 | 17.2565 | 0.23376 | 4.4538 | 0.18438 | 0.23856 | 4.5451 | 0.31094 | 5.9242 | 62.0822 | 31.0584 | 76.2809 | 117.0632 | 62.1264 | 31.1709
CAST | Canning Street | CA | CAST_11kV_BUS LH | 11 | 18.065 | 344.185 | 20.1297 | 127.8406 | 22.7691 | 19.0726 | 121.1274 | 19.6073 | 124.5233 | 0.03868 | 0.38478 | 0.01336 | 0.26693 | 0.03872 | 0.38549
CAST | Canning Street | CA | CAST_11kV_BUS RH | 11 | 18.065 | 344.185 | 20.1297 | 127.8406 | 22.7691 | 19.0726 | 121.1274 | 19.6073 | 124.5233 | 0.03868 | 0.38478 | 0.01336 | 0.26693 | 0.03872 | 0.38549
CAST | Canning Street | CA | CAST_66kV TRANSFER BUSBAR | 66 | 9.6577 | 1104.0252 | 9.6427 | 367.4373 | 9.6749 | 9.903 | 377.3556 | 9.3858 | 357.6476 | 0.91183 | 4.2433 | 1.2994 | 4.1487 | 0.91308 | 4.269
CAST | Canning Street | CA | CAST_66kV_BUS | 66 | 9.6577 | 1104.0252 | 9.6427 | 367.4373 | 9.6749 | 9.903 | 377.3556 | 9.3858 | 357.6476 | 0.91183 | 4.2433 | 1.2994 | 4.1487 | 0.91308 | 4.269
CATE | Cairns Terminal T051 | FN | CATE_22kV_BUS 1 | 22 | 12.1897 | 464.4892 | 11.1967 | 142.2169 | 10.2904 | 12.3757 | 157.192 | 11.0884 | 140.8414 | 0.0515 | 1.145 | 0.34572 | 1.4287 | 0.05025 | 1.143
CATE | Cairns Terminal T051 | FN | CATE_22kV_BUS 2 | 22 | 12.1897 | 464.4892 | 11.1967 | 142.2169 | 10.2904 | 12.3757 | 157.192 | 11.0884 | 140.8414 | 0.0515 | 1.145 | 0.34572 | 1.4287 | 0.05025 | 1.143
CATE | Cairns Terminal T051 | FN | CATE_22kV_BUS 3 | 22 | 12.1897 | 464.4892 | 11.1967 | 142.2169 | 10.2904 | 12.3757 | 157.192 | 11.0884 | 140.8414 | 0.0515 | 1.145 | 0.34572 | 1.4287 | 0.05025 | 1.143
CATE | Cairns Terminal T051 | FN | CATE_22kV_BUS 4 | 22 | 12.1897 | 464.4892 | 11.1967 | 142.2169 | 10.2904 | 12.3757 | 157.192 | 11.0884 | 140.8414 | 0.0515 | 1.145 | 0.34572 | 1.4287 | 0.05025 | 1.143
CAWD | Cawdor | SW | CAWD_11kV_BUS | 11 | 4.4181 | 84.1764 | 5.0059 | 31.7915 | 5.7717 | 4.7356 | 30.0751 | 4.8491 | 30.7956 | 0.22694 | 1.5651 | 0.10227 | 1.0203 | 0.22612 | 1.5649
CAWD | Cawdor | SW | CAWD_33kV_TEF T1 | 33 | 4.1677 | 238.2186 | 1.0033 | 19.1156 | 0.53338 | 3.8507 | 73.3661 | 3.3742 | 64.2862 | 1.122 | 4.9026 | 56.6656 | 11.614 | 1.1146 | 4.9009
CEPL | Cecil Plains (TF1) | SW | CEPL_11kV_BUS T1 | 11 | 2.2018 | 41.9492 | 2.9794 | 18.9218 | 4.532 | 2.7746 | 17.6211 | 3.1402 | 19.9428 | 1.3479 | 2.8728 | 0.03804 | 0.76075 | 1.3324 | 2.8551
CEPL | Cecil Plains (TF3) | SW | CEPL_11kV_BUS T3 | 11 | 2.2018 | 41.9492 | 2.9794 | 18.9218 | 4.532 | 2.7746 | 17.6211 | 3.1402 | 19.9428 | 1.3479 | 2.8728 | 0.03804 | 0.76075 | 1.3324 | 2.8551
CEPL | Cecil Plains | SW | CEPL_33kV_BUS | 33 | 0.93711 | 53.5631 | 0.56105 | 10.6894 | 0.39438 | 0.79195 | 15.0887 | 0.88237 | 16.8115 | 11.7886 | 19.008 | 18.8031 | 65.9549 | 11.6495 | 18.8492
CEPL | Cecil Plains | SW | CEPL_33kV_BUS T1 | 33 | 0.93711 | 53.5631 | 0.56105 | 10.6894 | 0.39438 | 0.79195 | 15.0887 | 0.88237 | 16.8115 | 11.7886 | 19.008 | 18.8031 | 65.9549 | 11.6495 | 18.8492
CEPL | Cecil Plains | SW | CEPL_33kV_BUS T3 | 33 | 0.93711 | 53.5631 | 0.56105 | 10.6894 | 0.39438 | 0.79195 | 15.0887 | 0.88237 | 16.8115 | 11.7886 | 19.008 | 18.8031 | 65.9549 | 11.6495 | 18.8492
CHAL | Charlton | SW | CHAL_11kV_TEF_T1 | 11 | 4.831 | 92.0434 | 5.3307 | 33.8546 | 5.9352 | 4.9549 | 31.4681 | 5.2988 | 33.6517 | 0.24474 | 1.4254 | 0.05218 | 1.0443 | 0.24469 | 1.4249
CHAL | Charlton | SW | CHAL_33kV_BUS | 33 | 5.5084 | 314.85 | 1.0442 | 19.8942 | 0.55069 | 5.0104 | 95.4607 | 4.54 | 86.4987 | 1.6362 | 3.4355 | 55.9525 | 4.052 | 1.6357 | 3.4311
CHAR | Charleville | SW | CHAR_11kV_BUS 1 | 11 | 1.6239 | 30.9399 | 2.3237 | 14.7572 | 4.0847 | 2.4303 | 15.4343 | 2.5281 | 16.0559 | 1.2194 | 4.1255 | 0.01263 | 0.42617 | 1.2176 | 4.1288
CHAR | Charleville | SW | CHAR_11kV_BUS 2 | 11 | 1.6239 | 30.9399 | 2.3237 | 14.7572 | 4.0847 | 2.4303 | 15.4343 | 2.5281 | 16.0559 | 1.2194 | 4.1255 | 0.01263 | 0.42617 | 1.2176 | 4.1288
CHAR | Charleville | SW | CHAR_22kV_BUS 1 | 22 | 0.81067 | 30.8908 | 1.1444 | 14.5363 | 1.9455 | 1.17 | 14.8605 | 1.2286 | 15.6052 | 4.8797 | 16.53 | 0.07275 | 2.2109 | 4.8726 | 16.5429
CHAR | Charleville | SW | CHAR_66kV_BUS 1 | 66 | 0.32252 | 36.8693 | 0.13896 | 5.2952 | 0.08859 | 0.28142 | 10.7234 | 0.28401 | 10.8224 | 42.4299 | 122.8431 | 190.0704 | 616.362 | 42.3659 | 122.9589
CHAR | Charleville | SW | CHAR_66kV_BUS 2 | 66 | 0.32252 | 36.8693 | 0.13896 | 5.2952 | 0.08859 | 0.28142 | 10.7234 | 0.28401 | 10.8224 | 42.4299 | 122.8431 | 190.0704 | 616.362 | 42.3659 | 122.9589
CHIA | Chillagoe | FN | CHIA_22kV_BUS 1 | 22 | 0.94744 | 36.1024 | 1.1281 | 14.3283 | 1.3943 | 1.0302 | 13.0851 | 1.1207 | 14.2344 | 3.1245 | 14.4121 | 0.35557 | 7.7096 | 3.1218 | 14.4442
CHIA | Chillagoe | FN | CHIA_66kV_BUS 1 | 66 | 0.64221 | 73.4147 | 0.37782 | 14.3968 | 0.26761 | 0.55278 | 21.0636 | 0.58892 | 22.4408 | 24.9205 | 60.3227 | 45.9097 | 197.8259 | 24.8959 | 60.6116
CHIL | Childers | WB | CHIL_11kV_BUS A | 11 | 7.9567 | 151.5949 | 8.6779 | 55.112 | 9.548 | 8.2463 | 52.3708 | 8.5149 | 54.0767 | 0.10783 | 0.87141 | 0.04149 | 0.65795 | 0.10521 | 0.87243
CHIL | Childers | WB | CHIL_11kV_BUS B | 11 | 7.9567 | 151.5949 | 8.6779 | 55.112 | 9.548 | 8.2463 | 52.3708 | 8.5149 | 54.0767 | 0.10783 | 0.87141 | 0.04149 | 0.65795 | 0.10521 | 0.87243
CHIL | Childers | WB | CHIL_66kV_BUS 1 | 66 | 5.2092 | 595.489 | 4.6505 | 177.2083 | 4.2015 | 4.8918 | 186.4016 | 5.0576 | 192.7193 | 2.3881 | 7.6845 | 2.4892 | 10.6672 | 2.294 | 7.7212
CHIL | Childers | WB | CHIL_66kV_BUS 2 | 66 | 5.2092 | 595.489 | 4.6505 | 177.2083 | 4.2015 | 4.8918 | 186.4016 | 5.0576 | 192.7193 | 2.3881 | 7.6845 | 2.4892 | 10.6672 | 2.294 | 7.7212
CHIN | Chinchilla T013 | SW | CHIN_110kV_BUS 3 | 110 | 2.0798 | 396.2594 | 2.0385 | 129.4655 | 2.003 | 2.0498 | 130.1824 | 2.0696 | 131.4381 | 4.4619 | 33.2925 | 4.1073 | 35.3239 | 4.4437 | 33.3673
CHIN | Chinchilla T013 | SW | CHIN_110kV_BUS 4 | 110 | 2.0798 | 396.2594 | 2.0385 | 129.4655 | 2.003 | 2.0498 | 130.1824 | 2.0696 | 131.4381 | 4.4619 | 33.2925 | 4.1073 | 35.3239 | 4.4437 | 33.3673
CHIN | Chinchilla T013 (TF1) | SW | CHIN_33kV_BUS 1 | 33 | 7.622 | 435.6527 | 7.1879 | 136.948 | 6.7961 | 7.1263 | 135.7737 | 7.7049 | 146.7977 | 0.6888 | 2.6621 | 0.35637 | 3.2437 | 0.6699 | 2.6718
CHIN | Chinchilla T013 (TF2) | SW | CHIN_33kV_BUS 2 | 33 | 7.622 | 435.6527 | 7.1879 | 136.948 | 6.7961 | 7.1263 | 135.7737 | 7.7049 | 146.7977 | 0.6888 | 2.6621 | 0.35637 | 3.2437 | 0.6699 | 2.6718
CHTO | Charters Towers (TF1) | NQ | CHTO_11kV_BUS 1 | 11 | 7.5398 | 143.6523 | 8.6316 | 54.8182 | 10.1071 | 7.9282 | 50.3506 | 8.5656 | 54.3989 | 0.17654 | 0.90957 | 0.0263 | 0.57641 | 0.17511 | 0.91245
CHTO | Charters Towers (TF2) | NQ | CHTO_11kV_BUS 2 | 11 | 7.5398 | 143.6523 | 8.6316 | 54.8182 | 10.1071 | 7.9282 | 50.3506 | 8.5656 | 54.3989 | 0.17654 | 0.90957 | 0.0263 | 0.57641 | 0.17511 | 0.91245
CHTO | Charters Towers | NQ | CHTO_66kV_BUS 1 | 66 | 3.1858 | 364.1908 | 3.1927 | 121.659 | 3.2022 | 2.9923 | 114.0209 | 3.3683 | 128.351 | 5.4086 | 11.9938 | 2.785 | 12.8898 | 5.3574 | 12.0974
CHTO | Charters Towers | NQ | CHTO_66kV_BUS 2 | 66 | 3.1858 | 364.1908 | 3.1927 | 121.659 | 3.2022 | 2.9923 | 114.0209 | 3.3683 | 128.351 | 5.4086 | 11.9938 | 2.785 | 12.8898 | 5.3574 | 12.0974
CHTW | Chinchilla Town (TF1) | SW | CHTW_11kV_BUS CHINCHILLA NORTH | 11 | 5.9006 | 112.4214 | 6.6876 | 42.4721 | 7.7182 | 6.2333 | 39.5869 | 6.5675 | 41.709 | 0.17564 | 1.1709 | 0.03833 | 0.76667 | 0.17251 | 1.1724
CHTW | Chinchilla Town (TF2) | SW | CHTW_11kV_BUS CHINCHILLA SOUTH | 11 | 5.9006 | 112.4214 | 6.6876 | 42.4721 | 7.7182 | 6.2333 | 39.5869 | 6.5675 | 41.709 | 0.17564 | 1.1709 | 0.03833 | 0.76667 | 0.17251 | 1.1724
CHTW | Chinchilla Town | SW | CHTW_33kV_BUS MAIN | 33 | 5.4551 | 311.7984 | 4.6431 | 88.4621 | 4.032 | 4.9082 | 93.5138 | 5.3526 | 101.9802 | 1.2357 | 3.6379 | 0.94177 | 5.8223 | 1.2076 | 3.6513
CHTW | Chinchilla Town | SW | CHTW_33kV_BUS RESERVE | 33 | 5.4551 | 311.7984 | 4.6431 | 88.4621 | 4.032 | 4.9082 | 93.5138 | 5.3526 | 101.9802 | 1.2357 | 3.6379 | 0.94177 | 5.8223 | 1.2076 | 3.6513
CHUM | Chumvale | NQ - MI | CHUM_220kV_BUS 1 and 2 no switch here | 220 | 1.4476 | 551.5976 | 1.8443 | 234.2575 | 2.6068 | 1.8135 | 230.341 | 1.7969 | 228.2386 | 8.832 | 96.1147 | 3.2978 | 32.2693 | 7.7353 | 98.0174
CHUM | Chumvale | NQ - MI | CHUM_66kV_TEF T1 | 66 | 2.2527 | 257.5237 | 2.6614 | 101.411 | 3.2858 | 2.5156 | 95.8563 | 2.5784 | 98.2519 | 1.1271 | 18.5723 | 0.05921 | 9.8816 | 1.0284 | 18.7435
CLER | Clermont T071 (TF1) | CA | CLER_11kV_TEF T1 | 11 | 9.1529 | 174.3864 | 6.336 | 40.2389 | 5.134 | 7.9527 | 50.5062 | 8.2438 | 52.3553 | 0.06204 | 0.76073 | 0.01974 | 1.7231 | 0.07037 | 0.82041
CLER | Clermont T071 (TF2) | CA | CLER_11kV_TEF T2 | 11 | 9.1427 | 174.1916 | 6.335 | 40.2329 | 5.1352 | 7.9439 | 50.4502 | 8.238 | 52.3181 | 0.06217 | 0.76157 | 0.01849 | 1.7221 | 0.07047 | 0.82116
CLER | Clermont T071 | CA | CLER_132kV_BUS 1 | 132 | 2.6552 | 607.0687 | 2.3374 | 178.1325 | 2.3394 | 2.3934 | 182.3995 | 2.5816 | 196.7476 | 6.903 | 30.8084 | 3.9477 | 40.247 | 8.1361 | 34.8531
CLER | Clermont T071 | CA | CLER_132kV_BUS 2 | 132 | 2.6552 | 607.0687 | 2.3374 | 178.1325 | 2.3394 | 2.3934 | 182.3995 | 2.5816 | 196.7476 | 6.903 | 30.8084 | 3.9477 | 40.247 | 8.1361 | 34.8531
CLER | Clermont T071 | CA | CLER_22kV_BUS LH | 22 | 3.7502 | 142.8998 | 3.8167 | 48.4791 | 4.1456 | 3.7272 | 47.3422 | 3.8691 | 49.1439 | 0.29463 | 3.714 | 0.0572 | 3.2944 | 0.32789 | 3.9526
CLER | Clermont T071 | CA | CLER_22kV_BUS RH | 22 | 3.7502 | 142.8998 | 3.8167 | 48.4791 | 4.1456 | 3.7272 | 47.3422 | 3.8691 | 49.1439 | 0.29463 | 3.714 | 0.0572 | 3.2944 | 0.32789 | 3.9526
CLER | Clermont T071 | CA | CLER_66kV_BUS A | 66 | 4.0233 | 459.9302 | 4.0874 | 155.7519 | 5.0495 | 4.1377 | 157.6688 | 4.1778 | 159.1969 | 1.6696 | 10.2835 | 1.1993 | 7.7971 | 2.1139 | 12.2777
CLER | Clermont T071 | CA | CLER_66kV_BUS B | 66 | 4.0233 | 459.9302 | 4.0874 | 155.7519 | 5.0495 | 4.1377 | 157.6688 | 4.1778 | 159.1969 | 1.6696 | 10.2835 | 1.1993 | 7.7971 | 2.1139 | 12.2777
CLIF | Clifton (TF1) | SW | CLIF_11kV_BUS 1 | 11 | 1.8098 | 34.4823 | 2.463 | 15.6422 | 3.8259 | 2.2921 | 14.5569 | 2.6417 | 16.7769 | 1.9089 | 3.3556 | 0.04366 | 0.87322 | 1.9089 | 3.3551
CLIF | Clifton (TF2) | SW | CLIF_11kV_BUS 2 | 11 | 1.8098 | 34.4823 | 2.463 | 15.6422 | 3.8259 | 2.2921 | 14.5569 | 2.6417 | 16.7769 | 1.9089 | 3.3556 | 0.04366 | 0.87322 | 1.9089 | 3.3551
CLIF | Clifton | SW | CLIF_33kV_BUS | 33 | 0.75008 | 42.8727 | 0.36641 | 6.981 | 0.24201 | 0.67412 | 12.8437 | 0.6472 | 12.3308 | 16.787 | 22.3412 | 80.9024 | 83.1846 | 16.7871 | 22.3367
CLIN | Clinton | CA | CLIN_11kV_BUS LH | 11 | 14.6593 | 279.2976 | 15.607 | 99.1178 | 16.7024 | 15.128 | 96.0758 | 15.2571 | 96.8958 | 0.03089 | 0.47556 | 0.01941 | 0.38884 | 0.03089 | 0.47602
CLIN | Clinton | CA | CLIN_11kV_BUS RH | 11 | 14.6593 | 279.2976 | 15.607 | 99.1178 | 16.7024 | 15.128 | 96.0758 | 15.2571 | 96.8958 | 0.03089 | 0.47556 | 0.01941 | 0.38884 | 0.03089 | 0.47602
CLIN | Clinton | CA | CLIN_66kV_BUS 1 | 66 | 13.3104 | 1521.5807 | 13.862 | 528.2141 | 14.5357 | 13.8067 | 526.1044 | 13.4125 | 511.0851 | 0.41333 | 3.1219 | 0.49777 | 2.714 | 0.41325 | 3.1384
CLIN | Clinton | CA | CLIN_66kV_BUS 2 | 66 | 13.3104 | 1521.5807 | 13.862 | 528.2141 | 14.5357 | 13.8067 | 526.1044 | 13.4125 | 511.0851 | 0.41333 | 3.1219 | 0.49777 | 2.714 | 0.41325 | 3.1384
CLON | Cloncurry (TF1) | NQ - MI | CLON_11kV_BUS 1 | 11 | 3.0814 | 58.7088 | 3.4017 | 21.604 | 3.8039 | 3.2391 | 20.571 | 3.3121 | 21.0347 | 0.30534 | 2.2465 | 0.15163 | 1.6162 | 0.3026 | 2.2512
CLON | Cloncurry (TF2) | NQ - MI | CLON_11kV_BUS 2 | 11 | 3.0814 | 58.7088 | 3.4017 | 21.604 | 3.8039 | 3.2391 | 20.571 | 3.3121 | 21.0347 | 0.30534 | 2.2465 | 0.15163 | 1.6162 | 0.3026 | 2.2512
CLON | Cloncurry | NQ - MI | CLON_66kV_BUS 1 | 66 | 1.7948 | 205.1751 | 1.7575 | 66.971 | 1.7321 | 1.7788 | 67.7794 | 1.7743 | 67.6108 | 5.5336 | 22.6887 | 5.816 | 24.0022 | 5.4349 | 22.8599
CLSO | Clare South T193 | NQ | CLSO_11kV_BUS 1 | 11 | 3.4989 | 66.6625 | 3.5598 | 22.6074 | 3.622 | 3.5257 | 22.391 | 3.5348 | 22.449 | 0.20821 | 1.9857 | 0.18852 | 1.8852 | 0.20754 | 1.9854
CLSO | Clare South T193 | NQ | CLSO_66kV_BUS 1 | 66 | 11.3688 | 1299.6251 | 13.694 | 521.8098 | 17.1083 | 12.8419 | 489.3411 | 13.2581 | 505.202 | 0.70864 | 3.6182 | 0.22459 | 1.8156 | 0.68441 | 3.6053
CLSO | Clare South T193 | NQ | CLSO_66kV_BUS 2 | 66 | 11.3688 | 1299.6251 | 13.694 | 521.8098 | 17.1083 | 12.8419 | 489.3411 | 13.2581 | 505.202 | 0.70864 | 3.6182 | 0.22459 | 1.8156 | 0.68441 | 3.6053
COCO | Cook Colliery | CA | COCO_66kV_BUS | 66 | 2.8576 | 326.6642 | 2.0051 | 76.403 | 1.5403 | 2.5308 | 96.4367 | 2.6547 | 101.1596 | 5.7583 | 13.4909 | 9.9798 | 31.9644 | 5.7744 | 13.4551
COCR | Cooby Creek | SW | COCR_33kV_BUS 1 | 33 | 2.1155 | 120.9144 | 0.84024 | 16.0086 | 0.51861 | 1.7661 | 33.6485 | 1.9314 | 36.7976 | 4.807 | 8.6646 | 8.4077 | 55.3134 | 4.8069 | 8.6607
COLL | Collinsville | NQ | COLL_33kV_BUS 1 | 33 | 15.5135 | 886.7164 | 15.3241 | 291.9638 | 14.934 | 15.0844 | 287.3959 | 15.7532 | 300.1396 | 0.16312 | 1.3411 | 0.11881 | 1.416 | 0.21094 | 1.3161
COLL | Collinsville | NQ | COLL_33kV_BUS 2 | 33 | 15.5135 | 886.7164 | 15.3241 | 291.9638 | 14.934 | 15.0844 | 287.3959 | 15.7532 | 300.1396 | 0.16312 | 1.3411 | 0.11881 | 1.416 | 0.21094 | 1.3161
COLU | Columboola T194 | SW | COLU_33kV_BUS | 33 | 4.1747 | 238.6173 | 5.6591 | 107.8199 | 8.7998 | 5.6685 | 107.9991 | 5.72 | 108.9802 | 0.22363 | 5.0154 | 0.01424 | 1.0634 | 0.22311 | 5.0223
COME | Comet | CA | COME_22kV_BUS LURLINE | 22 | 2.2412 | 85.403 | 2.4444 | 31.048 | 2.6448 | 2.3003 | 29.2172 | 2.4097 | 30.6072 | 1.142 | 6.1285 | 0.47336 | 4.7562 | 1.1085 | 6.0453
COME | Comet | CA | COME_22kV_TEF T01 | 22 | 2.2412 | 85.403 | 2.4444 | 31.048 | 2.6448 | 2.3003 | 29.2172 | 2.4097 | 30.6072 | 1.142 | 6.1285 | 0.47336 | 4.7562 | 1.1085 | 6.0453
COME | Comet | CA | COME_22kV_TEF T02 | 22 | 2.2412 | 85.403 | 2.4444 | 31.048 | 2.6448 | 2.3003 | 29.2172 | 2.4097 | 30.6072 | 1.142 | 6.1285 | 0.47336 | 4.7562 | 1.1085 | 6.0453
COME | Comet | CA | COME_66kV_BUS | 66 | 3.0509 | 348.7637 | 1.8975 | 72.3047 | 1.3129 | 2.6821 | 102.2006 | 2.8917 | 110.1894 | 6.0176 | 12.351 | 10.4928 | 38.4787 | 5.7161 | 11.6019
COOK | Cooktown (TF1) | FN | COOK_22kV_BUS RMU 1 | 22 | 1.5063 | 57.3988 | 2.0631 | 26.2056 | 3.198 | 1.9774 | 25.1158 | 2.1497 | 27.3048 | 2.6491 | 8.8891 | 0.00027 | 1.9598 | 2.5764 | 8.7838
COOK | Cooktown (TF2) | FN | COOK_22kV_BUS RMU 2 | 22 | 1.5063 | 57.3988 | 2.0631 | 26.2056 | 3.198 | 1.9774 | 25.1158 | 2.1497 | 27.3048 | 2.6491 | 8.8891 | 0.00027 | 1.9598 | 2.5764 | 8.7838
COOK | Cooktown (G3,G4) | FN | COOK_22kV_BUS RMU 3 | 22 | 1.5063 | 57.3988 | 2.0631 | 26.2056 | 3.198 | 1.9774 | 25.1158 | 2.1497 | 27.3048 | 2.6491 | 8.8891 | 0.00027 | 1.9598 | 2.5764 | 8.7838
COOK | Cooktown (G1,G2) | FN | COOK_22kV_BUS RMU 4 | 22 | 1.5063 | 57.3988 | 2.0631 | 26.2056 | 3.198 | 1.9774 | 25.1158 | 2.1497 | 27.3048 | 2.6491 | 8.8891 | 0.00027 | 1.9598 | 2.5764 | 8.7838
COOK | Cooktown | FN | COOK_66kV_BUS | 66 | 0.63416 | 72.4941 | 0.4292 | 16.3548 | 0.31946 | 0.55733 | 21.2373 | 0.59353 | 22.6164 | 22.71 | 62.0726 | 33.0493 | 159.2588 | 22.0558 | 61.125
COOM | Coominglah (TF1) | CA | COOM_22kV_TEF T1 | 22 | 1.3002 | 49.5432 | 1.4583 | 18.5228 | 1.6539 | 1.3147 | 16.699 | 1.4746 | 18.7305 | 3.3451 | 10.2125 | 0.80066 | 7.3231 | 3.3453 | 10.2147
COOM | Coominglah (TF2) | CA | COOM_22kV_TEF T2 | 22 | 1.3002 | 49.5432 | 1.4583 | 18.5228 | 1.6539 | 1.3147 | 16.699 | 1.4746 | 18.7305 | 3.3451 | 10.2125 | 0.80066 | 7.3231 | 3.3453 | 10.2147
COOM | Coominglah | CA | COOM_66kV_TEF T2 | 66 | 1.2089 | 138.1974 | 0.85288 | 32.4991 | 0.65127 | 1.0131 | 38.6046 | 1.1735 | 44.7166 | 22.9153 | 26.0211 | 31.5423 | 73.4452 | 22.9161 | 26.0411
COPP | Coppabella Dragline | MK | Coppabella Dragline 66 kV | 66 | 3.25 | 371.5213 | 2.2599 | 86.1147 | 1.7343 | 2.933 | 111.7623 | 2.9537 | 112.5517 | 4.3657 | 12.1359 | 9.6584 | 28.2223 | 4.3679 | 12.1566
CORF | Corfield | NQ | CORF_66kV_BUS | 66 | 0.4704 | 53.7738 | 0.31237 | 11.9028 | 0.23745 | 0.40832 | 15.559 | 0.43249 | 16.48 | 38.0752 | 80.5622 | 67.1847 | 212.7658 | 38.333 | 82.7518
CPRE | Cape River East | NQ | CPRE_132kV_BUS_1 | 132 | 0.92847 | 212.2767 | 1.2516 | 95.3817 | 2.0468 | 1.2492 | 95.2038 | 1.347 | 102.6529 | 29.6836 | 85.2709 | 0.39884 | 17.1981 | 29.1264 | 89.5543
CPRE | Cape River East (TF1&2) | NQ | CPRE_33kV_STATCOM_BUS 1 | 33 | 3.4002 | 194.3462 | 1.5459 | 29.4525 | 1.0142 | 2.7954 | 53.2602 | 3.0789 | 58.6604 | 2.0262 | 5.8212 | 0 | 28.5793 | 2.0056 | 6.0715
CPRE | Cape River East (TF1&2) | NQ | CPRE_66kV_BUS_1 | 66 | 1.8951 | 216.6444 | 2.5449 | 96.9738 | 4.0949 | 2.4918 | 94.9496 | 2.7407 | 104.4333 | 8.299 | 20.5013 | 0.10978 | 4.5773 | 8.2687 | 21.4331
CRAI | Craiglie (TF1) | FN | CRAIGLIE NO 1 | 132 | 1.7089 | 390.7123 | 1.7018 | 129.6975 | 1.6939 | 1.6603 | 126.5319 | 1.7487 | 133.2721 | 14.172 | 46.9634 | 9.6682 | 48.8442 | 13.8091 | 47.0939
CRAI | Craiglie (TF2) | FN | CRAIGLIE NO 2 | 132 | 1.6879 | 385.9013 | 1.3926 | 106.1332 | 1.1857 | 1.5715 | 119.7655 | 1.5828 | 120.627 | 14.4745 | 47.5107 | 22.0603 | 78.186 | 14.1347 | 47.6376
CRAI | Craiglie (TF1) | FN | CRAI_22kV_BUS 1 | 22 | 5.8649 | 223.4841 | 7.6721 | 97.4486 | 11.0894 | 7.2974 | 92.6896 | 7.7346 | 98.2425 | 0.38324 | 2.3512 | 5e-05 | 0.70467 | 0.3735 | 2.3548
CRAI | Craiglie (TF2) | FN | CRAI_22kV_BUS 2 | 22 | 5.8649 | 223.4841 | 7.6721 | 97.4486 | 11.0894 | 7.2974 | 92.6896 | 7.7346 | 98.2425 | 0.38324 | 2.3512 | 5e-05 | 0.70467 | 0.3735 | 2.3548
CRAN | Cranbrook (TF1) | NQ | CRAN_11kV_BUS 1 | 11 | 13.078 | 249.1691 | 13.8887 | 88.2052 | 14.8038 | 13.4038 | 85.1252 | 13.6558 | 86.7257 | 0.03986 | 0.53269 | 0.01812 | 0.44047 | 0.03936 | 0.53269
CRAN | Cranbrook (TF2) | NQ | CRAN_11kV_BUS 2 | 11 | 13.078 | 249.1691 | 13.8887 | 88.2052 | 14.8038 | 13.4038 | 85.1252 | 13.6558 | 86.7257 | 0.03986 | 0.53269 | 0.01812 | 0.44047 | 0.03936 | 0.53269
CRAN | Cranbrook | NQ | CRAN_66kV_BUS 1 | 66 | 12.2887 | 1404.7828 | 9.7318 | 370.8314 | 8.0476 | 11.3635 | 433.0089 | 11.4011 | 434.4393 | 0.78291 | 3.3199 | 1.3325 | 5.9564 | 0.76492 | 3.3198
CRAN | Cranbrook | NQ | CRAN_66kV_BUS 2 | 66 | 12.2887 | 1404.7828 | 9.7318 | 370.8314 | 8.0476 | 11.3635 | 433.0089 | 11.4011 | 434.4393 | 0.78291 | 3.3199 | 1.3325 | 5.9564 | 0.76492 | 3.3198
CRED | Crediton | MK | CRED_11kV_TEF R1 | 11 | 0.63149 | 12.0314 | 0.65091 | 4.1339 | 0.67129 | 0.62663 | 3.9796 | 0.65629 | 4.168 | 1.6667 | 10.9365 | 0.71493 | 10.0663 | 1.6665 | 10.9395
CRED | Crediton | MK | CRED_66kV_TEF T1 | 66 | 0.90284 | 103.2083 | 0.64616 | 24.6221 | 0.4944 | 0.74115 | 28.2417 | 0.8912 | 33.9594 | 34.263 | 31.3288 | 44.5379 | 95.6333 | 34.2563 | 31.436
CRNA | Cressbrook No. 1 | SW | CRNA_3.3kV_BUS | 3.3 | 6.1796 | 35.3212 | 7.1792 | 13.6783 | 8.5278 | 6.4308 | 12.2524 | 7.2313 | 13.7774 | 0.09083 | 0.32681 | 0.01005 | 0.20108 | 0.09083 | 0.32677
CRNA | Cressbrook No. 1 | SW | CRNA_33kV_TEF T1 | 33 | 1.4026 | 80.1708 | 0.62488 | 11.9055 | 0.39675 | 1.1633 | 22.1642 | 1.295 | 24.6729 | 8.078 | 12.5729 | 13.9316 | 70.8891 | 8.078 | 12.5691
CRNB | Cressbrook No. 2 | SW | CRNB_3.3kV_BUS | 3.3 | 6.9108 | 39.5005 | 7.7918 | 14.8453 | 8.9042 | 7.0967 | 13.5211 | 7.8053 | 14.8711 | 0.06718 | 0.29578 | 0.01012 | 0.20249 | 0.06718 | 0.29574
CRNB | Cressbrook No. 2 | SW | CRNB_33kV_TEF T1 | 33 | 1.9169 | 109.5673 | 0.79329 | 15.1142 | 0.49376 | 1.5924 | 30.3392 | 1.7606 | 33.5433 | 5.7051 | 9.3286 | 9.6708 | 57.7617 | 5.7051 | 9.3247
CRNE | Crows Nest (TF1) | SW | CRNE_11kV_BUS 1 | 11 | 2.9815 | 56.8055 | 3.6888 | 23.4271 | 4.8077 | 3.2822 | 20.845 | 3.7575 | 23.8636 | 0.77892 | 2.2102 | 0.0515 | 1.0297 | 0.77892 | 2.2098
CRNE | Crows Nest (TF1) | SW | CRNE_11kV_BUS 2 | 11 | 2.9815 | 56.8055 | 3.6888 | 23.4271 | 4.8077 | 3.2822 | 20.845 | 3.7575 | 23.8636 | 0.77892 | 2.2102 | 0.0515 | 1.0297 | 0.77892 | 2.2098
CRNE | Crows Nest (TF1) | SW | CRNE_11kV_BUS 3 | 11 | 2.9815 | 56.8055 | 3.6888 | 23.4271 | 4.8077 | 3.2822 | 20.845 | 3.7575 | 23.8636 | 0.77892 | 2.2102 | 0.0515 | 1.0297 | 0.77892 | 2.2098
CRNE | Crows Nest | SW | CRNE_33kV_BUS 1 | 33 | 1.6796 | 96.0026 | 0.71593 | 13.6404 | 0.44913 | 1.3947 | 26.5718 | 1.5454 | 29.4448 | 6.5468 | 10.6248 | 11.0607 | 63.2025 | 6.5468 | 10.621
CRNE | Crows Nest | SW | CRNE_33kV_BUS 2 | 33 | 1.6796 | 96.0026 | 0.71593 | 13.6404 | 0.44913 | 1.3947 | 26.5718 | 1.5454 | 29.4448 | 6.5468 | 10.6248 | 11.0607 | 63.2025 | 6.5468 | 10.621
CROY | Croydon | FN | CROY_22kV_BUS 1 | 22 | 0.80179 | 30.5521 | 0.98166 | 12.4687 | 1.2722 | 0.89862 | 11.414 | 0.98161 | 12.4682 | 3.3488 | 17.1012 | 0.00268 | 7.8586 | 3.2709 | 17.2225
CROY | Croydon | FN | CROY_22kV_BUS 2 | 22 | 0.80179 | 30.5521 | 0.98166 | 12.4687 | 1.2722 | 0.89862 | 11.414 | 0.98161 | 12.4682 | 3.3488 | 17.1012 | 0.00268 | 7.8586 | 3.2709 | 17.2225
CROY | Croydon | FN | CROY_66kV_BUS 1 | 66 | 0.48708 | 55.681 | 0.43101 | 16.4235 | 0.38973 | 0.45495 | 17.3361 | 0.47151 | 17.9668 | 24.3126 | 82.5488 | 24.9401 | 116.3178 | 23.6119 | 83.6411
CROY | Croydon | FN | CROY_66kV_BUS 2 | 66 | 0.48708 | 55.681 | 0.43101 | 16.4235 | 0.38973 | 0.45495 | 17.3361 | 0.47151 | 17.9668 | 24.3126 | 82.5488 | 24.9401 | 116.3178 | 23.6119 | 83.6411
CROY | Croydon | FN | CROY_NORM 66KV BUS IS | 66 | 0.48708 | 55.681 | 0.43101 | 16.4235 | 0.38973 | 0.45495 | 17.3361 | 0.47151 | 17.9668 | 24.3126 | 82.5488 | 24.9401 | 116.3178 | 23.6119 | 83.6411
CUNN | Cunnamulla | SW | CUNN_11kV_BUS BROAD ST | 11 | 0.94684 | 18.0398 | 1.4139 | 8.9792 | 2.7917 | 1.6141 | 10.2509 | 1.6236 | 10.3114 | 2.8218 | 6.8174 | 0.00126 | 0.06928 | 2.8201 | 6.8206
CUNN | Cunnamulla | SW | CUNN_11kV_BUS WICKS ST | 11 | 0.94684 | 18.0398 | 1.4139 | 8.9792 | 2.7917 | 1.6141 | 10.2509 | 1.6236 | 10.3114 | 2.8218 | 6.8174 | 0.00126 | 0.06928 | 2.8201 | 6.8206
CUNN | Cunnamulla | SW | CUNN_22kV_BUS | 22 | 0.47337 | 18.0378 | 0.67455 | 8.5679 | 1.1719 | 0.69272 | 8.7987 | 0.73687 | 9.3595 | 11.2875 | 27.2728 | 0.0937 | 3.3019 | 11.2804 | 27.2856
CUNN | Cunnamulla | SW | CUNN_66kV_BUS 1 | 66 | 0.18146 | 20.7433 | 0.08344 | 3.1794 | 0.0541 | 0.15624 | 5.9535 | 0.16257 | 6.1946 | 99.733 | 208.361 | 323.596 | 996.5942 | 99.669 | 208.4768
CUNN | Cunnamulla | SW | CUNN_66kV_BUS 2 | 66 | 0.18146 | 20.7433 | 0.08344 | 3.1794 | 0.0541 | 0.15624 | 5.9535 | 0.16257 | 6.1946 | 99.733 | 208.361 | 323.596 | 996.5942 | 99.669 | 208.4768
DAAN | Daandine T188 | SW | DAAN_110kV_BUS 1 | 110 | 1.6296 | 310.479 | 1.2727 | 80.8253 | 1.0317 | 1.3784 | 87.5409 | 1.6171 | 102.6978 | 22.5341 | 36.4744 | 19.2927 | 78.6415 | 22.5481 | 36.4755
DAAN | Daandine T188 | SW | DAAN_33kV_BUS 1 | 33 | 2.6625 | 152.1845 | 2.3818 | 45.3788 | 2.1511 | 2.4587 | 46.8443 | 2.6271 | 50.0528 | 2.2471 | 7.5447 | 1.8252 | 10.5434 | 2.2484 | 7.5448
DAAN | Daandine T188 | SW | DAAN_33kV_BUS 2 | 33 | 2.6625 | 152.1845 | 2.3818 | 45.3788 | 2.1511 | 2.4587 | 46.8443 | 2.6271 | 50.0528 | 2.2471 | 7.5447 | 1.8252 | 10.5434 | 2.2484 | 7.5448
DABA | Dalrymple Bay (with MACK G1) | MK | DABA_33kV_BUS | 33 | 6.9893 | 399.4894 | 5.6734 | 108.0935 | 4.7959 | 6.4977 | 123.7972 | 6.5005 | 123.851 | 0.39525 | 2.9724 | 0.66083 | 5.0258 | 0.39544 | 2.9885
DACE | Dalby Central (TF1) | SW | DACE_11kV_BUS 1 | 11 | 8.6562 | 164.9229 | 10.4607 | 66.4343 | 13.1933 | 9.6008 | 60.9734 | 10.356 | 65.7696 | 0.16638 | 0.7898 | 0.02092 | 0.39261 | 0.16652 | 0.78981
DACE | Dalby Central (TF2) | SW | DACE_11kV_BUS 2 | 11 | 8.6562 | 164.9229 | 10.4607 | 66.4343 | 13.1933 | 9.6008 | 60.9734 | 10.356 | 65.7696 | 0.16638 | 0.7898 | 0.02092 | 0.39261 | 0.16652 | 0.78981
DACE | Dalby Central | SW | DACE_11kV_BUS 3 | 11 | 8.6562 | 164.9229 | 10.4607 | 66.4343 | 13.1933 | 9.6008 | 60.9734 | 10.356 | 65.7696 | 0.16638 | 0.7898 | 0.02092 | 0.39261 | 0.16652 | 0.78981
DACE | Dalby Central | SW | DACE_33kV_BUS 1 | 33 | 5.5058 | 314.7017 | 5.1957 | 98.991 | 4.9074 | 5.1369 | 97.8715 | 5.5785 | 106.2852 | 1.3091 | 3.5747 | 0.93038 | 4.4206 | 1.3104 | 3.5748
DACE | Dalby Central | SW | DACE_33kV_BUS 2 | 33 | 5.5058 | 314.7017 | 5.1957 | 98.991 | 4.9074 | 5.1369 | 97.8715 | 5.5785 | 106.2852 | 1.3091 | 3.5747 | 0.93038 | 4.4206 | 1.3104 | 3.5748
DACG | Dalby Cotton Gin | SW | SS596009_tr_cable_132 | 33 | 2.3563 | 134.6795 | 1.593 | 30.3512 | 1.1941 | 2.0009 | 38.1225 | 2.2443 | 42.7593 | 4.4784 | 7.6858 | 5.8949 | 21.1993 | 4.4797 | 7.6859
DAEA | Dalby East | SW | DAEA_110kV_BUS 3 | 110 | 3.6292 | 691.4522 | 3.8446 | 244.1626 | 4.0108 | 3.2454 | 206.11 | 4.1546 | 263.8527 | 9.8966 | 16.5129 | 2.0244 | 16.9299 | 9.9106 | 16.514
DAEA | Dalby East | SW | DAEA_110kV_BUS 4 | 110 | 3.6292 | 691.4522 | 3.8446 | 244.1626 | 4.0108 | 3.2454 | 206.11 | 4.1546 | 263.8527 | 9.8966 | 16.5129 | 2.0244 | 16.9299 | 9.9106 | 16.514
DAEA | Dalby East | SW | DAEA_33kV_BUS 1 | 33 | 7.1553 | 408.9795 | 9.0019 | 171.5099 | 12.0813 | 8.1191 | 154.6888 | 9.1569 | 174.4623 | 0.93132 | 2.7773 | 0.06073 | 1.1601 | 0.93258 | 2.7774
DAEA | Dalby East | SW | DAEA_33kV_BUS 2 | 33 | 7.1553 | 408.9795 | 9.0019 | 171.5099 | 12.0813 | 8.1191 | 154.6888 | 9.1569 | 174.4623 | 0.93132 | 2.7773 | 0.06073 | 1.1601 | 0.93258 | 2.7774
DAGL | Dan Gleeson T092 (TF1) | NQ | DAGL_11kV_BUS 1 | 11 | 19.7467 | 376.2247 | 21.0557 | 133.7217 | 22.5469 | 20.3858 | 129.4674 | 20.5802 | 130.7018 | 0.02486 | 0.3529 | 0.01504 | 0.28748 | 0.02437 | 0.35289
DAGL | Dan Gleeson T092 (TF2) | NQ | DAGL_11kV_BUS 2 | 11 | 19.7467 | 376.2247 | 21.0557 | 133.7217 | 22.5469 | 20.3858 | 129.4674 | 20.5802 | 130.7018 | 0.02486 | 0.3529 | 0.01504 | 0.28748 | 0.02437 | 0.35289
DAGL | Dan Gleeson T092 | NQ | DAGL_66kV_BUS 1 | 66 | 17.5989 | 2011.8194 | 19.9273 | 759.3332 | 22.9328 | 19.0103 | 724.3908 | 19.1437 | 729.4728 | 0.35345 | 2.3554 | 0.19902 | 1.5371 | 0.33576 | 2.355
DAGL | Dan Gleeson T092 | NQ | DAGL_66kV_BUS 2 | 66 | 17.5989 | 2011.8194 | 19.9273 | 759.3332 | 22.9328 | 19.0103 | 724.3908 | 19.1437 | 729.4728 | 0.35345 | 2.3554 | 0.19902 | 1.5371 | 0.33576 | 2.355
DEGI | Degilbo | WB | DEGI_11kV_BUS 1 | 11 | 3.2236 | 61.4178 | 3.3309 | 21.1539 | 3.4267 | 3.1994 | 20.3192 | 3.3568 | 21.3186 | 0.19726 | 2.1583 | 0.00621 | 1.9724 | 0.18631 | 2.1492
DEGI | Degilbo | WB | DEGI_11kV_BUS 2 | 11 | 3.2236 | 61.4178 | 3.3309 | 21.1539 | 3.4267 | 3.1994 | 20.3192 | 3.3568 | 21.3186 | 0.19726 | 2.1583 | 0.00621 | 1.9724 | 0.18631 | 2.1492
DEGI | Degilbo | WB | DEGI_66kV_BUS | 66 | 2.1257 | 242.9955 | 1.4344 | 54.6597 | 1.0825 | 1.9261 | 73.3954 | 1.9113 | 72.8308 | 5.9061 | 18.8151 | 15.0325 | 45.8265 | 5.8241 | 18.842
DIMB | Dimbulah (TF1) | FN | DIMB_22kV_BUS 1 | 22 | 3.18 | 121.1727 | 4.0531 | 51.4817 | 5.6212 | 3.7295 | 47.3711 | 4.1253 | 52.3982 | 1.358 | 4.1786 | 0.1063 | 1.5604 | 1.3553 | 4.2107
DIMB | Dimbulah (TF1) | FN | DIMB_22kV_BUS 2 | 22 | 3.18 | 121.1727 | 4.0531 | 51.4817 | 5.6212 | 3.7295 | 47.3711 | 4.1253 | 52.3982 | 1.358 | 4.1786 | 0.1063 | 1.5604 | 1.3553 | 4.2107
DIMB | Dimbulah | FN | DIMB_66kV_BUS | 66 | 1.6049 | 183.4603 | 1.1404 | 43.4566 | 0.88742 | 1.3897 | 52.9531 | 1.5154 | 57.7453 | 11.2653 | 23.5635 | 14.8347 | 56.3306 | 11.2406 | 23.8525
DIRE | Dirranbandi Regulator (UnRegulated) | SW | DIRE_33kV_BUS R1 Downstream | 33 | 0.37145 | 21.2309 | 0.26266 | 5.0044 | 0.20237 | 0.32199 | 6.1348 | 0.3517 | 6.7008 | 20.9643 | 52.3842 | 24.3213 | 125.2303 | 20.9483 | 52.4131
DIRE | Dirranbandi Regulator (Regulated) | SW | DIRE_33kV_BUS R1 Upstream | 33 | 0.37145 | 21.2309 | 0.26266 | 5.0044 | 0.20237 | 0.32199 | 6.1348 | 0.3517 | 6.7008 | 20.9643 | 52.3842 | 24.3213 | 125.2303 | 20.9483 | 52.4131
DISR | Disraeli | NQ | DISR_11kV_TEF T1 | 11 | 3.447 | 65.6736 | 3.9007 | 24.773 | 4.4653 | 3.4406 | 21.8505 | 3.9935 | 25.3621 | 0.54834 | 1.9511 | 0.0037 | 1.3551 | 0.54726 | 1.9529
DISR | Disraeli | NQ | DISR_66kV_TEF T1 | 66 | 1.438 | 164.3817 | 1.0806 | 41.1747 | 0.85299 | 1.1982 | 45.6555 | 1.4242 | 54.2707 | 19.7318 | 21.4554 | 22.7737 | 55.3805 | 19.6929 | 21.5203
DRILL | Drillham Switching Station | SW | DRILL_132kV_BUS_7174 | 132 | 7.2813 | 1664.7211 | 5.7877 | 441.0861 | 5.0143 | 6.7263 | 512.6107 | 6.6124 | 503.9292 | 3.1283 | 11.0805 | 5.9793 | 18.8989 | 3.2852 | 11.6699
DRILL | Drillham Switching Station | SW | DRILL_132kV_BUS_7491 | 132 | 7.2813 | 1664.7211 | 5.7877 | 441.0861 | 5.0143 | 6.7263 | 512.6107 | 6.6124 | 503.9292 | 3.1283 | 11.0805 | 5.9793 | 18.8989 | 3.2852 | 11.6699
DRILL | Drillham Switching Station | SW | DRILL_132kV_BUS_7492 | 132 | 7.2813 | 1664.7211 | 5.7877 | 441.0861 | 5.0143 | 6.7263 | 512.6107 | 6.6124 | 503.9292 | 3.1283 | 11.0805 | 5.9793 | 18.8989 | 3.2852 | 11.6699
DRILL | Drillham Switching Station | SW | DRILL_132kV_BUS_7164 | 132 | 7.2813 | 1664.7211 | 5.7877 | 441.0861 | 5.0143 | 6.7263 | 512.6107 | 6.6124 | 503.9292 | 3.1283 | 11.0805 | 5.9793 | 18.8989 | 3.2852 | 11.6699
DRILL | Drillham Switching Station | SW | DRILL_132kV_BUS_7490 | 132 | 7.2813 | 1664.7211 | 5.7877 | 441.0861 | 5.0143 | 6.7263 | 512.6107 | 6.6124 | 503.9292 | 3.1283 | 11.0805 | 5.9793 | 18.8989 | 3.2852 | 11.6699
DURI | Dugald River | NQ-MI | DURI_11kV_TEF_T1 | 11 | 15.4312 | 294.004 | 0.15346 | 0.97462 | 0.07714 | 13.3354 | 84.6909 | 13.2584 | 84.2021 | 0.03239 | 0.45156 | 136.4998 | 0.0669 | 0.02964 | 0.45631
DURI | Dugald River | NQ-MI | DURI_11kV_TEF_T2 | 11 | 15.4312 | 294.004 | 0.15346 | 0.97462 | 0.07714 | 13.3354 | 84.6909 | 13.2584 | 84.2021 | 0.03239 | 0.45156 | 136.4998 | 0.0669 | 0.02964 | 0.45631
DURI | Dugald River | NQ-MI | DURI_220kV_BUS | 220 | 1.1359 | 432.8363 | 1.4547 | 184.7693 | 2.0631 | 1.4092 | 178.9912 | 1.4377 | 182.6154 | 12.7962 | 122.3352 | 1.7304 | 40.3741 | 11.6995 | 124.2379
DURO | Duchess Road (TF1) | NQ - MI | DURO_11kV_BUS A | 11 | 36.2052 | 689.8022 | 6.1363 | 38.9704 | 3.395 | 30.9631 | 196.6419 | 31.1273 | 197.6848 | 0.01262 | 0.19254 | 0 | 3.0255 | 0.00988 | 0.1973
DURO | Duchess Road (TF2) | NQ - MI | DURO_11kV_BUS B | 11 | 36.2052 | 689.8022 | 6.1363 | 38.9704 | 3.395 | 30.9631 | 196.6419 | 31.1273 | 197.6848 | 0.01262 | 0.19254 | 0 | 3.0255 | 0.00988 | 0.1973
DURO | Duchess Road (TF1) | NQ - MI | DURO_132kV_TEF T1 | 132 | 5.9609 | 1362.8378 | 6.4018 | 487.8799 | 7.2599 | 6.3227 | 481.8512 | 6.1859 | 471.4286 | 1.6168 | 13.9703 | 1.2855 | 10.4423 | 1.222 | 14.6553
DURO | Duchess Road (TF2) | NQ - MI | DURO_132kV_TEF T2 | 132 | 6.4529 | 1475.3265 | 7.1861 | 547.657 | 8.5621 | 7.0975 | 540.8981 | 6.8609 | 522.8699 | 1.7434 | 12.8738 | 1.3578 | 8.2805 | 1.3486 | 13.5587
DURO | Duchess Road | NQ - MI | DURO_66kV_BUS | 66 | 0.53965 | 61.6901 | 0.55379 | 21.1021 | 0.56992 | 0.54756 | 20.865 | 0.54663 | 20.8296 | 5.5761 | 77.4716 | 5.2465 | 71.3675 | 5.4774 | 77.6429
DYSA | Dysart T035 | CA | DYSA_22kV_BUS 1 | 22 | 5.4949 | 209.3834 | 1.3455 | 17.0902 | 0.76683 | 4.7447 | 60.2654 | 4.7988 | 60.9524 | 0.19169 | 2.5355 | 0.03599 | 26.0763 | 0.19239 | 2.5381
DYSA | Dysart T035 | CA | DYSA_22kV_BUS 2 | 22 | 5.4949 | 209.3834 | 1.3455 | 17.0902 | 0.76683 | 4.7447 | 60.2654 | 4.7988 | 60.9524 | 0.19169 | 2.5355 | 0.03599 | 26.0763 | 0.19239 | 2.5381
DYSA | Dysart T035 | CA | DYSA_66kV_BUS A | 66 | 6.0742 | 694.3758 | 7.6697 | 292.2536 | 10.4415 | 7.2055 | 274.5681 | 7.6062 | 289.8352 | 1.4084 | 6.7554 | 0.20483 | 2.5794 | 1.4146 | 6.7787
DYSA | Dysart T035 | CA | DYSA_66kV_BUS B | 66 | 6.0742 | 694.3758 | 7.6697 | 292.2536 | 10.4415 | 7.2055 | 274.5681 | 7.6062 | 289.8352 | 1.4084 | 6.7554 | 0.20483 | 2.5794 | 1.4146 | 6.7787
EAAY | East Ayr (TF1) | NQ | EAAY_11kV_BUS 1 | 11 | 14.035 | 267.4018 | 16.3264 | 103.6864 | 19.4671 | 15.0884 | 95.8244 | 16.0462 | 101.9071 | 0.08608 | 0.49025 | 0.01513 | 0.28984 | 0.08374 | 0.4902
EAAY | East Ayr (TF2) | NQ | EAAY_11kV_BUS 2 | 11 | 14.035 | 267.4018 | 16.3264 | 103.6864 | 19.4671 | 15.0884 | 95.8244 | 16.0462 | 101.9071 | 0.08608 | 0.49025 | 0.01513 | 0.28984 | 0.08374 | 0.4902
EAAY | East Ayr | NQ | EAAY_66kV_BUS 1 | 66 | 5.4765 | 626.0507 | 4.2463 | 161.8064 | 3.4537 | 4.9571 | 188.8903 | 5.1503 | 196.2512 | 2.554 | 7.215 | 3.6161 | 13.8969 | 2.4697 | 7.2129
EAAY | East Ayr | NQ | EAAY_66kV_BUS 2 | 66 | 5.4765 | 626.0507 | 4.2463 | 161.8064 | 3.4537 | 4.9571 | 188.8903 | 5.1503 | 196.2512 | 2.554 | 7.215 | 3.6161 | 13.8969 | 2.4697 | 7.2129
EABU | East Bundaberg | WB | EABU_11kV_BUS 1 | 11 | 13.359 | 254.524 | 15.706 | 99.7467 | 19.1797 | 14.7067 | 93.3998 | 15.3146 | 97.2605 | 0.06685 | 0.51869 | 0.01346 | 0.28586 | 0.06617 | 0.52187
EABU | East Bundaberg | WB | EABU_11kV_BUS 2 | 11 | 13.359 | 254.524 | 15.706 | 99.7467 | 19.1797 | 14.7067 | 93.3998 | 15.3146 | 97.2605 | 0.06685 | 0.51869 | 0.01346 | 0.28586 | 0.06617 | 0.52187
EABU | East Bundaberg | WB | EABU_66kV_BUS 1 | 66 | 5.193 | 593.641 | 4.3496 | 165.741 | 3.7839 | 4.8818 | 186.0233 | 4.8353 | 184.2497 | 1.9218 | 7.84 | 3.1554 | 12.2638 | 1.8975 | 7.9546
EABU | East Bundaberg | WB | EABU_66kV_BUS 2 | 66 | 5.193 | 593.641 | 4.3496 | 165.741 | 3.7839 | 4.8818 | 186.0233 | 4.8353 | 184.2497 | 1.9218 | 7.84 | 3.1554 | 12.2638 | 1.8975 | 7.9546
EATO | East Toowoomba | SW | EATO_11kV_BUS 1 | 11 | 9.8716 | 188.0785 | 2.2425 | 14.2419 | 1.1518 | 9.1189 | 57.913 | 7.9863 | 50.7201 | 0.06297 | 0.70498 | 9.0248 | 0.49615 | 0.06299 | 0.70449
EATO | East Toowoomba | SW | EATO_11kV_BUS 2 | 11 | 9.8716 | 188.0785 | 2.2425 | 14.2419 | 1.1518 | 9.1189 | 57.913 | 7.9863 | 50.7201 | 0.06297 | 0.70498 | 9.0248 | 0.49615 | 0.06299 | 0.70449
EATO | East Toowoomba (TF1) | SW | EATO_33kV_TEF T1 | 33 | 8.6075 | 491.9845 | 1.1031 | 21.017 | 0.56316 | 7.7294 | 147.2656 | 7.1935 | 137.0536 | 0.52031 | 2.379 | 55.2647 | 4.1524 | 0.52046 | 2.3745
EATO | East Toowoomba (TF2) | SW | EATO_33kV_TEF T2 | 33 | 8.2705 | 472.7237 | 1.0957 | 20.8757 | 0.56062 | 7.434 | 141.6364 | 6.9043 | 131.5455 | 0.57954 | 2.4673 | 55.4504 | 4.5091 | 0.5797 | 2.4628
EDMO | Edmonton | FN | EDMO_22kV_BUS 1 | 22 | 8.5168 | 324.5317 | 7.178 | 91.1724 | 6.1784 | 8.3345 | 105.8627 | 7.6492 | 97.1578 | 0.06955 | 1.639 | 0.51298 | 2.5267 | 0.06828 | 1.6374
EDMO | Edmonton | FN | EDMO_22kV_BUS 2 | 22 | 8.5168 | 324.5317 | 7.178 | 91.1724 | 6.1784 | 8.3345 | 105.8627 | 7.6492 | 97.1578 | 0.06955 | 1.639 | 0.51298 | 2.5267 | 0.06828 | 1.6374
EDMO | Edmonton | FN | EDMO_22kV_BUS 3 | 22 | 8.5168 | 324.5317 | 7.178 | 91.1724 | 6.1784 | 8.3345 | 105.8627 | 7.6492 | 97.1578 | 0.06955 | 1.639 | 0.51298 | 2.5267 | 0.06828 | 1.6374
EGHI | Egans Hill T127 | CA | EGHI_66kV_BUS EAST | 66 | 10.147 | 1159.9519 | 11.4301 | 435.5453 | 13.1781 | 10.9714 | 418.0671 | 10.9708 | 418.0431 | 0.70516 | 4.0703 | 0.46165 | 2.6745 | 0.70659 | 4.0961
EGHI | Egans Hill T127 | CA | EGHI_66kV_BUS WEST | 66 | 10.147 | 1159.9519 | 11.4301 | 435.5453 | 13.1781 | 10.9714 | 418.0671 | 10.9708 | 418.0431 | 0.70516 | 4.0703 | 0.46165 | 2.6745 | 0.70659 | 4.0961
EIDS | Eidsvold | WB | EIDS_11kV_BUS | 11 | 1.8978 | 36.1573 | 2.158 | 13.7051 | 2.4873 | 1.9094 | 12.1266 | 2.2018 | 13.9836 | 1.3145 | 3.4387 | 0.2487 | 2.396 | 1.3105 | 3.4428
EIDS | Eidsvold | WB | EIDS_66kV_BUS | 66 | 0.68052 | 77.7939 | 0.45404 | 17.3012 | 0.33877 | 0.58218 | 22.1841 | 0.64261 | 24.4869 | 38.6969 | 47.9252 | 68.0125 | 139.823 | 38.5519 | 48.0726
ELAR | El Arish | FN | ELAR_22kV_BUS 1 | 22 | 11.0136 | 419.6728 | 8.5207 | 108.2276 | 6.9383 | 10.5287 | 133.7329 | 9.7422 | 123.7423 | 0.10184 | 1.2645 | 0.54995 | 2.3301 | 0.10021 | 1.2668
ELAR | El Arish | FN | ELAR_22kV_BUS 2 | 22 | 11.0136 | 419.6728 | 8.5207 | 108.2276 | 6.9383 | 10.5287 | 133.7329 | 9.7422 | 123.7423 | 0.10184 | 1.2645 | 0.54995 | 2.3301 | 0.10021 | 1.2668
ELAR | El Arish | FN | ELAR_22kV_BUS 3 | 22 | 11.0136 | 419.6728 | 8.5207 | 108.2276 | 6.9383 | 10.5287 | 133.7329 | 9.7422 | 123.7423 | 0.10184 | 1.2645 | 0.54995 | 2.3301 | 0.10021 | 1.2668
ELRO | Ellwoods Road (TF1) | WB | ELRO_11kV_BUS 1 | 11 | 5.7154 | 108.8928 | 6.5192 | 41.4025 | 7.5861 | 6.1148 | 38.8344 | 6.3539 | 40.3527 | 0.24068 | 1.1985 | 0.09686 | 0.76519 | 0.23948 | 1.1992
ELRO | Ellwoods Road (TF2) | WB | ELRO_11kV_BUS 2 | 11 | 5.7154 | 108.8928 | 6.5192 | 41.4025 | 7.5861 | 6.1148 | 38.8344 | 6.3539 | 40.3527 | 0.24068 | 1.1985 | 0.09686 | 0.76519 | 0.23948 | 1.1992
ELRO | Ellwoods Road | WB | ELRO_66kV_BUS OVERHEAD | 66 | 2.5504 | 291.5524 | 1.4281 | 54.4191 | 0.99058 | 2.2108 | 84.2417 | 2.314 | 88.1754 | 5.1778 | 15.5999 | 10.7006 | 54.2906 | 5.1343 | 15.6263
EMER | Emerald | CA | EMER_22kV_BUS 1 | 22 | 6.8488 | 260.9728 | 9.4331 | 119.8165 | 11.6452 | 8.332 | 105.8309 | 8.6352 | 109.6821 | 0.38451 | 2.0035 | 0.03552 | 0.71002 | 0.21765 | 1.6839
EMER | Emerald | CA | EMER_22kV_BUS 2 | 22 | 6.8488 | 260.9728 | 9.4331 | 119.8165 | 11.6452 | 8.332 | 105.8309 | 8.6352 | 109.6821 | 0.38451 | 2.0035 | 0.03552 | 0.71002 | 0.21765 | 1.6839
EMER | Emerald | CA | EMER_22kV_BUS 3 | 22 | 6.8488 | 260.9728 | 9.4331 | 119.8165 | 11.6452 | 8.332 | 105.8309 | 8.6352 | 109.6821 | 0.38451 | 2.0035 | 0.03552 | 0.71002 | 0.21765 | 1.6839
EMER | Emerald | CA | EMER_66kV_BUS 1 | 66 | 3.4763 | 397.393 | 1.6151 | 61.5435 | 0.8625 | 3.4796 | 132.5894 | 3.4264 | 130.5622 | 3.1408 | 11.6414 | 14.1851 | 55.1053 | 1.6392 | 8.7653
EMER | Emerald | CA | EMER_66kV_BUS 3 | 66 | 3.4763 | 397.393 | 1.6151 | 61.5435 | 0.8625 | 3.4796 | 132.5894 | 3.4264 | 130.5622 | 3.1408 | 11.6414 | 14.1851 | 55.1053 | 1.6392 | 8.7653
EMWE | Emerald West | CA | EMWE_66kV_BUS | 66 | 3.6623 | 418.6558 | 1.64 | 62.4915 | 0.84084 | 3.7431 | 142.6327 | 3.6656 | 139.6785 | 2.7663 | 11.1059 | 14.1142 | 55.4236 | 1.2055 | 7.9829
ERHE | Ernest Henry (TF1) | NQ - MI | ERHE_11kV_TEF T1 | 11 | 17.2088 | 327.8716 | 0.2198 | 1.3959 | 0.11058 | 14.876 | 94.4752 | 14.766 | 93.7765 | 0.03592 | 0.40436 | 95.2499 | 1.675 | 0.03318 | 0.40912
ERHE | Ernest Henry (TF2) | NQ - MI | ERHE_11kV_TEF T2 | 11 | 17.2088 | 327.8716 | 0.2198 | 1.3959 | 0.11058 | 14.876 | 94.4752 | 14.766 | 93.7765 | 0.03592 | 0.40436 | 95.2499 | 1.675 | 0.03318 | 0.40912
ERHE | Ernest Henry | NQ - MI | ERHE_220kV_BUS | 220 | 1.1757 | 447.9959 | 1.5452 | 196.2599 | 2.3032 | 1.533 | 194.7113 | 1.5379 | 195.3412 | 12.1849 | 118.2141 | 2.6254 | 31.7031 | 11.0882 | 120.1167
ETON | Eton | MK | ETON_33kV_BUS 1 | 33 | 3.1949 | 182.6104 | 1.9189 | 36.5601 | 1.3615 | 2.6851 | 51.1578 | 3 | 57.1579 | 3.4 | 5.61 | 5.1984 | 19.2523 | 3.3975 | 5.6282
ETON | Eton | MK | ETON_33kV_BUS 2 | 33 | 3.1949 | 182.6104 | 1.9189 | 36.5601 | 1.3615 | 2.6851 | 51.1578 | 3 | 57.1579 | 3.4 | 5.61 | 5.1984 | 19.2523 | 3.3975 | 5.6282
ETON | Eton | MK | ETON_33kV_BUS 3 | 33 | 3.1949 | 182.6104 | 1.9189 | 36.5601 | 1.3615 | 2.6851 | 51.1578 | 3 | 57.1579 | 3.4 | 5.61 | 5.1984 | 19.2523 | 3.3975 | 5.6282
ETON | Eton (TF1) | MK | ETON_11kV_BUS 1 | 11 | 4.7927 | 91.3141 | 5.7043 | 36.2271 | 7.0232 | 5.0959 | 32.3631 | 5.7558 | 36.5542 | 0.41646 | 1.3969 | 0.03868 | 0.77352 | 0.41617 | 1.3989
ETON | Eton (TF2) | MK | ETON_11kV_BUS 2 | 11 | 4.7927 | 91.3141 | 5.7043 | 36.2271 | 7.0232 | 5.0959 | 32.3631 | 5.7558 | 36.5542 | 0.41646 | 1.3969 | 0.03868 | 0.77352 | 0.41617 | 1.3989
ETON | Eton | MK | ETON_11kV_BUS 3 | 11 | 4.7927 | 91.3141 | 5.7043 | 36.2271 | 7.0232 | 5.0959 | 32.3631 | 5.7558 | 36.5542 | 0.41646 | 1.3969 | 0.03868 | 0.77352 | 0.41617 | 1.3989
ETON | Eton | MK | ETON_11kV_BUS 4 | 11 | 4.7927 | 91.3141 | 5.7043 | 36.2271 | 7.0232 | 5.0959 | 32.3631 | 5.7558 | 36.5542 | 0.41646 | 1.3969 | 0.03868 | 0.77352 | 0.41617 | 1.3989
EUDA | Eungella Dam (TF1) | MK | EUDA_11kV_TEF R1 | 11 | 0.62812 | 11.9673 | 0.65465 | 4.1576 | 0.68256 | 0.61857 | 3.9284 | 0.66485 | 4.2224 | 2.0592 | 10.9297 | 0.59614 | 9.8025 | 2.0591 | 10.9327
EUDA | Eungella Dam (TF2) | MK | EUDA_11kV_TEF R2 | 11 | 2.0166 | 38.4219 | 2.3993 | 15.2374 | 2.9257 | 2.033 | 12.9115 | 2.499 | 15.8706 | 1.6646 | 3.038 | 0.20155 | 1.9108 | 1.6645 | 3.041
EUDA | Eungella Dam | MK | EUDA_66kV_BUS | 66 | 0.6304 | 72.0649 | 0.46658 | 17.779 | 0.36297 | 0.51529 | 19.6351 | 0.62934 | 23.9812 | 52.6715 | 40.5796 | 68.2499 | 124.8974 | 52.6649 | 40.6868
EUMA | Eumamurrin Regulator (Un-Regulated) | SW | GW00024_AB9545 | 33 | 0.52277 | 29.8804 | 0.38351 | 7.3069 | 0.29443 | 0.41894 | 7.9819 | 0.52703 | 10.0412 | 32.7638 | 23.1041 | 40.5443 | 78.7831 | 32.7478 | 23.1331
EUMA | Eumamurrin Regulator (Regulated) | SW | GW00024_tr_line_22769 | 33 | 0.52277 | 29.8804 | 0.38351 | 7.3069 | 0.29443 | 0.41894 | 7.9819 | 0.52703 | 10.0412 | 32.7638 | 23.1041 | 40.5443 | 78.7831 | 32.7478 | 23.1331
EVEL | Evelyn | FN | EVEL_22kV_BUS 1 | 22 | 1.6175 | 61.6331 | 1.8041 | 22.9152 | 2.0422 | 1.6872 | 21.431 | 1.7772 | 22.5737 | 1.4896 | 8.5088 | 0.45383 | 5.9433 | 1.4671 | 8.5297
EVEL | Evelyn | FN | EVEL_22kV_BUS 2 | 22 | 1.6175 | 61.6331 | 1.8041 | 22.9152 | 2.0422 | 1.6872 | 21.431 | 1.7772 | 22.5737 | 1.4896 | 8.5088 | 0.45383 | 5.9433 | 1.4671 | 8.5297
EVEL | Evelyn | FN | EVEL_66kV_BUS MAIN | 66 | 1.6833 | 192.4314 | 1.0215 | 38.9236 | 0.7338 | 1.4608 | 55.666 | 1.5401 | 58.6857 | 9.3219 | 23.0896 | 17.6709 | 71.3201 | 9.1191 | 23.2773
EVEL | Evelyn | FN | EVEL_66kV_BUS RESERVE | 66 | 1.6833 | 192.4314 | 1.0215 | 38.9236 | 0.7338 | 1.4608 | 55.666 | 1.5401 | 58.6857 | 9.3219 | 23.0896 | 17.6709 | 71.3201 | 9.1191 | 23.2773
FARB | Farnborough | CA | FARB_66kV_TEF Upstream | 66 | 2.4697 | 282.3286 | 1.5801 | 60.2097 | 1.1563 | 2.1255 | 80.992 | 2.3034 | 87.7728 | 7.8927 | 15.0251 | 13.2606 | 44.0513 | 7.8581 | 15.0304
FARL | Farleigh | MK | FARL_11kV_BUS 1 | 11 | 4.7513 | 90.5237 | 5.6828 | 36.0906 | 7.0657 | 5.1522 | 32.7211 | 5.6793 | 36.0681 | 0.50521 | 1.3808 | 0.11281 | 0.7475 | 0.49693 | 1.3871
FARL | Farleigh | MK | FARL_11kV_BUS 2 | 11 | 4.7513 | 90.5237 | 5.6828 | 36.0906 | 7.0657 | 5.1522 | 32.7211 | 5.6793 | 36.0681 | 0.50521 | 1.3808 | 0.11281 | 0.7475 | 0.49693 | 1.3871
FARL | Farleigh | MK | FARL_11kV_BUS 3 | 11 | 4.7513 | 90.5237 | 5.6828 | 36.0906 | 7.0657 | 5.1522 | 32.7211 | 5.6793 | 36.0681 | 0.50521 | 1.3808 | 0.11281 | 0.7475 | 0.49693 | 1.3871
FARL | Farleigh | MK | FARL_33kV_BUS 1 | 33 | 2.1457 | 122.6429 | 1.2019 | 22.8997 | 0.83126 | 1.8199 | 34.6739 | 1.9816 | 37.7556 | 5.0267 | 8.3747 | 9.9817 | 31.5438 | 5.0034 | 8.4136
FARL | Farleigh | MK | FARL_33kV_BUS 2 | 33 | 2.1457 | 122.6429 | 1.2019 | 22.8997 | 0.83126 | 1.8199 | 34.6739 | 1.9816 | 37.7556 | 5.0267 | 8.3747 | 9.9817 | 31.5438 | 5.0034 | 8.4136
FARL | Farleigh | MK | FARL_33kV_BUS 3 | 33 | 2.1457 | 122.6429 | 1.2019 | 22.8997 | 0.83126 | 1.8199 | 34.6739 | 1.9816 | 37.7556 | 5.0267 | 8.3747 | 9.9817 | 31.5438 | 5.0034 | 8.4136
FARN | Farnsfield | WB | FARN_11kV_BUS 2 | 11 | 7.0219 | 133.7856 | 8.2141 | 52.1663 | 9.8738 | 7.4735 | 47.4629 | 8.176 | 51.9248 | 0.22744 | 0.96859 | 0.0317 | 0.56709 | 0.22483 | 0.96961
FARN | Farnsfield | WB | FARN_66kV_TEF T1 | 66 | 2.6068 | 297.9999 | 1.8287 | 69.6843 | 1.4025 | 2.2665 | 86.3649 | 2.4588 | 93.6933 | 7.0466 | 14.454 | 9.9145 | 35.5293 | 6.9525 | 14.4908
FARN | Farnsfield | WB | FARN_66kV_TEF T2 | 66 | 2.6068 | 297.9999 | 1.8287 | 69.6843 | 1.4025 | 2.2665 | 86.3649 | 2.4588 | 93.6933 | 7.0466 | 14.454 | 9.9145 | 35.5293 | 6.9525 | 14.4908
FARN | Farnsfield | WB | FARN_11kV_BUS 1 | 11 | 8.4879 | 161.7173 | 9.4722 | 60.1567 | 10.718 | 8.8202 | 56.0158 | 9.3614 | 59.4531 | 0.13562 | 0.81185 | 0.0317 | 0.56709 | 0.13431 | 0.81311
FILA | Fisherman's Landing (TF1) | CA | FILA_11kV_BUS 1 | 11 | 16.8085 | 320.2446 | 19.0764 | 121.1514 | 22.0973 | 18.1539 | 115.2926 | 18.383 | 116.748 | 0.03542 | 0.41412 | 0.01647 | 0.26618 | 0.03534 | 0.41488
FILA | Fisherman's Landing (TF2) | CA | FILA_11kV_BUS 2 | 11 | 16.8085 | 320.2446 | 19.0764 | 121.1514 | 22.0973 | 18.1539 | 115.2926 | 18.383 | 116.748 | 0.03542 | 0.41412 | 0.01647 | 0.26618 | 0.03534 | 0.41488
FILA | Fisherman's Landing (TF1) | CA | 6103_FILA - BOCR TR_LINE_22202_1 | 66 | 7.7778 | 889.1238 | 7.4822 | 285.1088 | 7.2351 | 7.849 | 299.0854 | 7.4157 | 282.5772 | 0.7058 | 5.3428 | 1.3651 | 5.8628 | 0.703 | 5.3705
FILA | Fisherman's Landing (TF2) | CA | 6103_FILA - BOCR TR_LINE_22203_1 | 66 | 7.8002 | 891.6802 | 7.519 | 286.5118 | 7.2844 | 7.8821 | 300.347 | 7.4398 | 283.4936 | 0.6818 | 5.3304 | 1.3392 | 5.8165 | 0.679 | 5.358
FITR | Fig Tree T185 | NQ | FITR_11kV_BUS 1 | 11 | 7.7302 | 147.2805 | 5.5168 | 35.0366 | 4.28 | 6.7996 | 43.1834 | 7.249 | 46.0375 | 0.12157 | 0.89551 | 0 | 2 | 0.12192 | 0.89558
FITR | Fig Tree T185 | NQ | FITR_132kV_TEF T1 | 132 | 2.7911 | 638.1254 | 1.9616 | 149.4918 | 1.5118 | 2.4762 | 188.7091 | 2.5859 | 197.07 | 12.2715 | 27.4144 | 22.0785 | 64.5753 | 12.3222 | 27.4246
FOXL | Foxleigh | CA | FOXL_22kV_TEF T1 | 22 | 1.6316 | 62.1737 | 1.791 | 22.7482 | 1.9868 | 1.6724 | 21.242 | 1.7792 | 22.5992 | 1.3926 | 8.4492 | 0.31407 | 6.2815 | 1.3719 | 8.47
FOXL | Foxleigh | CA | FOXL_66kV_TEF T1 | 66 | 1.9236 | 219.893 | 1.0633 | 40.5152 | 0.73415 | 1.6476 | 62.783 | 1.757 | 66.9511 | 9.707 | 19.5092 | 20.3733 | 72.2334 | 9.5205 | 19.6971
FREN | Frenchville | CA | FREN_11kV_BUS LH | 11 | 14.4566 | 275.4361 | 15.9091 | 101.0362 | 17.71 | 15.1104 | 95.9641 | 15.5474 | 98.739 | 0.04883 | 0.48077 | 0.01753 | 0.35009 | 0.04885 | 0.48147
FREN | Frenchville | CA | FREN_11kV_BUS RH | 11 | 14.4566 | 275.4361 | 15.9091 | 101.0362 | 17.71 | 15.1104 | 95.9641 | 15.5474 | 98.739 | 0.04883 | 0.48077 | 0.01753 | 0.35009 | 0.04885 | 0.48147
FREN | Frenchville | CA | FREN_66kV_BUS 1 | 66 | 8.6647 | 990.5038 | 8.1652 | 311.1356 | 7.7508 | 8.6409 | 329.2619 | 8.2208 | 313.2552 | 1.1267 | 4.7046 | 1.8031 | 5.4221 | 1.1276 | 4.7298
FREN | Frenchville | CA | FREN_66kV_BUS 2 | 66 | 8.6647 | 990.5038 | 8.1652 | 311.1356 | 7.7508 | 8.6409 | 329.2619 | 8.2208 | 313.2552 | 1.1267 | 4.7046 | 1.8031 | 5.4221 | 1.1276 | 4.7298
GARB | Garbutt T046 (TF3) | NQ | GARB_11kV_BUS 1 | 11 | 20.0419 | 381.8493 | 20.7464 | 131.757 | 21.4722 | 20.2923 | 128.8734 | 20.5377 | 130.4318 | 0.02415 | 0.34773 | 0.0123 | 0.31334 | 0.02092 | 0.3475
GARB | Garbutt T046 (TF5) | NQ | GARB_11kV_BUS 2 | 11 | 20.0419 | 381.8493 | 20.7464 | 131.757 | 21.4722 | 20.2923 | 128.8734 | 20.5377 | 130.4318 | 0.02415 | 0.34773 | 0.0123 | 0.31334 | 0.02092 | 0.3475
GARB | Garbutt T046 | NQ | GARB_11kV_BUS 3 | 11 | 20.0419 | 381.8493 | 20.7464 | 131.757 | 21.4722 | 20.2923 | 128.8734 | 20.5377 | 130.4318 | 0.02415 | 0.34773 | 0.0123 | 0.31334 | 0.02092 | 0.3475
GARB | Garbutt T047 | NQ | GARB_66kV_BUS 1 | 66 | 18.5088 | 2115.843 | 20.224 | 770.6395 | 22.2581 | 19.3689 | 738.0545 | 19.6678 | 749.445 | 0.39124 | 2.2306 | 0.2328 | 1.6757 | 0.37224 | 2.2311
GAVI | Gavial 66kV Switching Station | CA | GAVI_66kV_BUS pole10464283 | 66 | 5.9241 | 677.218 | 4.8995 | 186.6946 | 4.1892 | 5.5241 | 210.498 | 5.5465 | 211.3495 | 2.031 | 6.7778 | 3.2068 | 11.0341 | 2.0328 | 6.8026
GAYN | Gayndah | WB | GAYN_11kV_BUS 1 | 11 | 5.7053 | 108.7005 | 7.0517 | 44.7844 | 9.2195 | 6.4849 | 41.1844 | 7.0187 | 44.5747 | 0.27137 | 1.1941 | 0.02644 | 0.52812 | 0.26866 | 1.1955
GAYN | Gayndah | WB | GAYN_11kV_BUS 2 | 11 | 5.7053 | 108.7005 | 7.0517 | 44.7844 | 9.2195 | 6.4849 | 41.1844 | 7.0187 | 44.5747 | 0.27137 | 1.1941 | 0.02644 | 0.52812 | 0.26866 | 1.1955
GAYN | Gayndah (Unregulated) | WB | GAYN_66kV_BUS 1 | 66 | 1.6628 | 190.0878 | 1.0518 | 40.0809 | 0.76937 | 1.4772 | 56.2888 | 1.5032 | 57.2786 | 8.7323 | 23.6483 | 20.9683 | 65.8963 | 8.6347 | 23.6992
GAYN | Gayndah (Regulated) | WB | GAYN_66kV_BUS 2 | 66 | 1.6628 | 190.0878 | 1.0518 | 40.0809 | 0.76937 | 1.4772 | 56.2888 | 1.5032 | 57.2786 | 8.7323 | 23.6483 | 20.9683 | 65.8963 | 8.6347 | 23.6992
GEOR | Georgetown | FN | GEOR_132kV_BUS 1 | 132 | 0.61904 | 141.5318 | 0.76554 | 58.342 | 1.0374 | 0.69987 | 53.3376 | 0.7849 | 59.8173 | 46.9718 | 127.0142 | 4.8594 | 55.1109 | 47.3541 | 131.063
GEOR | Georgetown | FN | GEOR_132kV_BUS 2 | 132 | 0.61904 | 141.5318 | 0.76554 | 58.342 | 1.0374 | 0.69987 | 53.3376 | 0.7849 | 59.8173 | 46.9718 | 127.0142 | 4.8594 | 55.1109 | 47.3541 | 131.063
GEOR | Georgetown | FN | GEOR_22kV_BUS 1 | 22 | 1.1009 | 41.9486 | 1.2594 | 15.9962 | 1.4827 | 1.1555 | 14.6765 | 1.2544 | 15.9335 | 1.961 | 12.5393 | 0.00268 | 7.8633 | 1.9615 | 12.648
GEOR | Georgetown | FN | GEOR_22kV_BUS 2 | 22 | 1.1009 | 41.9486 | 1.2594 | 15.9962 | 1.4827 | 1.1555 | 14.6765 | 1.2544 | 15.9335 | 1.961 | 12.5393 | 0.00268 | 7.8633 | 1.9615 | 12.648
GEOR | Georgetown | FN | GEOR_6.6kV_BUS 1 | 6.6 | 7.4605 | 85.285 | 0 | 0 | 0 | 6.4066 | 24.4125 | 6.4066 | 24.4125 | 0.1254 | 0.54766 | 116470585.5392 | 0.79705 | 0.12549 | 0.55742
GEOR | Georgetown | FN | GEOR_6.6kV_BUS 2 | 6.6 | 7.4605 | 85.285 | 0 | 0 | 0 | 6.4066 | 24.4125 | 6.4066 | 24.4125 | 0.1254 | 0.54766 | 116470585.5392 | 0.79705 | 0.12549 | 0.55742
GEOR | Georgetown | FN | GEOR_6.6kV_BUS 3 | 6.6 | 7.4605 | 85.285 | 0 | 0 | 0 | 6.4066 | 24.4125 | 6.4066 | 24.4125 | 0.1254 | 0.54766 | 116470585.5392 | 0.79705 | 0.12549 | 0.55742
GEOR | Georgetown | FN | GEOR_66kV_BUS 1 | 66 | 0.94824 | 108.398 | 1.268 | 48.3178 | 1.9728 | 1.2371 | 47.1399 | 1.3251 | 50.4917 | 11.8407 | 42.5885 | 0.38551 | 10.0481 | 11.8454 | 43.5661
GEOR | Georgetown | FN | GEOR_66kV_BUS 2 | 66 | 0.94824 | 108.398 | 1.268 | 48.3178 | 1.9728 | 1.2371 | 47.1399 | 1.3251 | 50.4917 | 11.8407 | 42.5885 | 0.38551 | 10.0481 | 11.8454 | 43.5661
GIRU | Giru (TF2) | NQ | GIRU_11kV_TEF 1 | 11 | 3.8685 | 73.7043 | 4.5678 | 29.0094 | 5.5156 | 3.9297 | 24.9571 | 4.7144 | 29.9407 | 0.75961 | 1.6383 | 0.08805 | 1.0218 | 0.75674 | 1.6384
GIRU | Giru (TF2) | NQ | GIRU_11kV_TEF 2 | 11 | 3.8685 | 73.7043 | 4.5678 | 29.0094 | 5.5156 | 3.9297 | 24.9571 | 4.7144 | 29.9407 | 0.75961 | 1.6383 | 0.08805 | 1.0218 | 0.75674 | 1.6384
GIRU | Giru | NQ | GIRU_66kV_BUS 1 | 66 | 1.2771 | 145.9944 | 0.94217 | 35.9014 | 0.73308 | 1.0596 | 40.3774 | 1.2638 | 48.1581 | 24.1763 | 22.1967 | 31.2103 | 62.8383 | 24.0729 | 22.1999
GIRU | Giru | NQ | GIRU_66kV_BUS 2 | 66 | 1.2771 | 145.9944 | 0.94217 | 35.9014 | 0.73308 | 1.0596 | 40.3774 | 1.2638 | 48.1581 | 24.1763 | 22.1967 | 31.2103 | 62.8383 | 24.0729 | 22.1999
GIVE | Givelda | WB | GIVE_11kV_BUS 1 | 11 | 7.5489 | 143.8267 | 8.6303 | 54.8098 | 10.0901 | 8.0308 | 51.0025 | 8.4729 | 53.8099 | 0.13214 | 0.91601 | 0.0245 | 0.57727 | 0.13145 | 0.91816
GIVE | Givelda | WB | GIVE_11kV_BUS 2 | 11 | 7.5489 | 143.8267 | 8.6303 | 54.8098 | 10.0901 | 8.0308 | 51.0025 | 8.4729 | 53.8099 | 0.13214 | 0.91601 | 0.0245 | 0.57727 | 0.13145 | 0.91816
GIVE | Givelda | WB | GIVE_66kV_BUS | 66 | 3.2761 | 374.5058 | 2.3367 | 89.0394 | 1.8228 | 2.9428 | 112.1354 | 3.0055 | 114.525 | 3.8751 | 12.1945 | 7.233 | 27.2314 | 3.8502 | 12.272
GLEE | Glenelg | NQ | GLEE_33kV_TEF T1 | 33 | 0.14648 | 8.3726 | 0.15312 | 2.9173 | 0.161 | 0.14826 | 2.8247 | 0.15195 | 2.895 | 24.1071 | 141.028 | 15.6085 | 123.0127 | 24.1716 | 141.5754
GLEE | Glenelg | NQ | GLEE_66kV_TEF T1 | 66 | 0.52607 | 60.1379 | 0.35944 | 13.6964 | 0.27786 | 0.45767 | 17.4396 | 0.48529 | 18.4919 | 33.9943 | 72.061 | 56.9061 | 180.3813 | 34.2521 | 74.2506
GLEL | Glenella | MK | GLEL_11kV_BUS 1 | 11 | 12.4471 | 237.1497 | 14.2464 | 90.4769 | 16.7013 | 13.4713 | 85.5542 | 13.7863 | 87.555 | 0.04382 | 0.55954 | 0.01122 | 0.34723 | 0.04245 | 0.5611
GLEL | Glenella | MK | GLEL_11kV_BUS 2 | 11 | 12.4471 | 237.1497 | 14.2464 | 90.4769 | 16.7013 | 13.4713 | 85.5542 | 13.7863 | 87.555 | 0.04382 | 0.55954 | 0.01122 | 0.34723 | 0.04245 | 0.5611
GLEL | Glenella | MK | GLEL_11kV_BUS 3 | 11 | 12.4471 | 237.1497 | 14.2464 | 90.4769 | 16.7013 | 13.4713 | 85.5542 | 13.7863 | 87.555 | 0.04382 | 0.55954 | 0.01122 | 0.34723 | 0.04245 | 0.5611
GLEL | Glenella (TF5) | MK | GLEL_33kV_TEF T5 | 33 | 4.6329 | 264.808 | 5.6523 | 107.6911 | 7.2734 | 5.383 | 102.5605 | 5.443 | 103.7039 | 0.34952 | 4.5102 | 0.1052 | 2.061 | 0.33715 | 4.5242
GLEL | Glenella (TF6) | MK | GLEL_33kV_TEF T6 | 33 | 4.6361 | 264.9856 | 5.5996 | 106.6863 | 7.0942 | 5.3219 | 101.3957 | 5.3885 | 102.6641 | 0.34951 | 4.5071 | 0.10618 | 2.172 | 0.33714 | 4.5212
GLEL | Glenella | MK | GLEL_66kV_BUS 1 | 66 | 5.4206 | 619.6555 | 5.6717 | 216.1216 | 5.9852 | 5.5001 | 209.5804 | 5.6183 | 214.0847 | 1.1736 | 7.6432 | 0.71705 | 6.6225 | 1.1241 | 7.6994
GLEL | Glenella (with MACK GT1) | MK | GLEL_66kV_BUS 2 | 66 | 5.4206 | 619.6555 | 5.6717 | 216.1216 | 5.9852 | 5.5001 | 209.5804 | 5.6183 | 214.0847 | 1.1736 | 7.6432 | 0.71705 | 6.6225 | 1.1241 | 7.6994
GLEL | Glenella (with MACK GT1) | MK | GLEL_66kV_BUS 2 | 66 | 5.4206 | 619.6555 | 5.6717 | 216.1216 | 5.9852 | 5.5001 | 209.5804 | 5.6183 | 214.0847 | 1.1736 | 7.6432 | 0.71705 | 6.6225 | 1.1241 | 7.6994
GLEN | Glenden | MK | GLEN_11kV_BUS 1 | 11 | 6.0299 | 114.8851 | 7.212 | 45.8022 | 8.923 | 6.3886 | 40.5732 | 7.3163 | 46.4648 | 0.36173 | 1.1006 | 0.03025 | 0.605 | 0.36199 | 1.1008
GLEN | Glenden | MK | GLEN_11kV_BUS 2 | 11 | 6.0299 | 114.8851 | 7.212 | 45.8022 | 8.923 | 6.3886 | 40.5732 | 7.3163 | 46.4648 | 0.36173 | 1.1006 | 0.03025 | 0.605 | 0.36199 | 1.1008
GLEN | Glenden | MK | GLEN_66kV_BUS 1 | 66 | 1.9527 | 223.2234 | 1.5532 | 59.1831 | 1.2804 | 1.689 | 64.3584 | 1.9194 | 73.1402 | 11.9332 | 17.8429 | 12.9933 | 36.3876 | 11.9427 | 17.8501
GLEN | Glenden | MK | GLEN_66kV_BUS 2 | 66 | 1.9527 | 223.2234 | 1.5532 | 59.1831 | 1.2804 | 1.689 | 64.3584 | 1.9194 | 73.1402 | 11.9332 | 17.8429 | 12.9933 | 36.3876 | 11.9427 | 17.8501
GLFS | Gladstone Friend Street | CA | GLFS_11kV_BUS 1 | 11 | 17.9622 | 342.2253 | 19.5607 | 124.2272 | 21.4978 | 18.7056 | 118.7963 | 19.0992 | 121.2964 | 0.03612 | 0.38725 | 0.01636 | 0.29279 | 0.03611 | 0.38774
GLFS | Gladstone Friend Street | CA | GLFS_11kV_BUS 2 | 11 | 17.9622 | 342.2253 | 19.5607 | 124.2272 | 21.4978 | 18.7056 | 118.7963 | 19.0992 | 121.2964 | 0.03612 | 0.38725 | 0.01636 | 0.29279 | 0.03611 | 0.38774
GLFS | Gladstone Friend Street | CA | GLFS_11kV_BUS 3 | 11 | 17.9622 | 342.2253 | 19.5607 | 124.2272 | 21.4978 | 18.7056 | 118.7963 | 19.0992 | 121.2964 | 0.03612 | 0.38725 | 0.01636 | 0.29279 | 0.03611 | 0.38774
GLFS | Gladstone Friend Street (TF1) | CA | GLFS_66kV_TEF T1 | 66 | 12.0648 | 1379.1957 | 11.1007 | 422.9941 | 10.318 | 11.9002 | 453.4576 | 11.3663 | 433.1133 | 0.7113 | 3.4007 | 1.2327 | 4.1938 | 0.71101 | 3.4181
GLFS | Gladstone Friend Street (TF5) | CA | GLFS_66kV_TEF T5 | 66 | 12.0648 | 1379.1957 | 11.1007 | 422.9941 | 10.318 | 11.9002 | 453.4576 | 11.3663 | 433.1133 | 0.7113 | 3.4007 | 1.2327 | 4.1938 | 0.71101 | 3.4181
GLNO | Gladstone North T074 (TF1) | CA | GLNO_11kV_TEF T1 | 11 | 21.6705 | 412.8777 | 0 | 0 | 0 | 18.7541 | 119.1044 | 18.7541 | 119.1044 | 0.02559 | 0.32136 | 135802470.2909 | -2.3367 | 0.02559 | 0.32181
GLNO | Gladstone North T074 (TF2) | CA | GLNO_11kV_TEF T2 | 11 | 21.4972 | 409.5765 | 0 | 0 | 0 | 18.6042 | 118.1527 | 18.6042 | 118.1527 | 0.0253 | 0.32399 | 135802470.6018 | -4.1575 | 0.0253 | 0.32444
GLNO | Gladstone North T074 (TF1) | CA | GLNO_132kV_BUS 1 | 132 | 27.5779 | 6305.1425 | 33.1677 | 2527.7178 | 42.7032 | 32.0646 | 2443.6478 | 31.8288 | 2425.6832 | 0.14002 | 3.0366 | 0.08789 | 1.4369 | 0.14168 | 3.1001
GLNO | Gladstone North T074 (TF2) | CA | GLNO_132kV_BUS 2 | 132 | 27.5779 | 6305.1425 | 33.1677 | 2527.7178 | 42.7032 | 32.0646 | 2443.6478 | 31.8288 | 2425.6832 | 0.14002 | 3.0366 | 0.08789 | 1.4369 | 0.14168 | 3.1001
GLNO | Gladstone North T074 | CA | GLNO_66kV_BUS 1 | 66 | 14.5986 | 1668.8465 | 17.5167 | 667.4769 | 22.0449 | 16.5838 | 631.9288 | 16.9338 | 645.2651 | 0.25819 | 2.8596 | 0.06685 | 1.4196 | 0.25821 | 2.8759
GLNO | Gladstone North T074 | CA | GLNO_66kV_BUS 2 | 66 | 14.5986 | 1668.8465 | 17.5167 | 667.4769 | 22.0449 | 16.5838 | 631.9288 | 16.9338 | 645.2651 | 0.25819 | 2.8596 | 0.06685 | 1.4196 | 0.25821 | 2.8759
GLNO | Gladstone North T074 | CA | GLNO_66kV_BUS 3 | 66 | 14.5986 | 1668.8465 | 17.5167 | 667.4769 | 22.0449 | 16.5838 | 631.9288 | 16.9338 | 645.2651 | 0.25819 | 2.8596 | 0.06685 | 1.4196 | 0.25821 | 2.8759
GLSO | Gladstone South T152 (TF 1) | CA | GLSO_11kV_BUS 1 | 11 | 13.4093 | 255.4805 | 14.1664 | 89.9691 | 15.0297 | 13.7852 | 87.5477 | 13.873 | 88.1056 | 0.02656 | 0.52031 | 0.01739 | 0.43661 | 0.02655 | 0.52083
GLSO | Gladstone South T152 (TF 2) | CA | GLSO_11kV_BUS 2 | 11 | 13.4093 | 255.4805 | 14.1664 | 89.9691 | 15.0297 | 13.7852 | 87.5477 | 13.873 | 88.1056 | 0.02656 | 0.52031 | 0.01739 | 0.43661 | 0.02655 | 0.52083
GLSO | Gladstone South T152 (TF 3) | CA | GLSO_11kV_BUS 3 | 11 | 13.4093 | 255.4805 | 14.1664 | 89.9691 | 15.0297 | 13.7852 | 87.5477 | 13.873 | 88.1056 | 0.02656 | 0.52031 | 0.01739 | 0.43661 | 0.02655 | 0.52083
GLSO | Gladstone South T152 | CA | GLSO_66kV_BUS EAST | 66 | 13.828 | 1580.7551 | 16.2841 | 620.5091 | 19.9468 | 15.5661 | 593.1488 | 15.5744 | 593.4633 | 0.3301 | 3.0133 | 0.17574 | 1.632 | 0.32966 | 3.0317
GLSO | Gladstone South T152 | CA | GLSO_66kV_BUS TRANSFER | 66 | 13.828 | 1580.7551 | 16.2841 | 620.5091 | 19.9468 | 15.5661 | 593.1488 | 15.5744 | 593.4633 | 0.3301 | 3.0133 | 0.17574 | 1.632 | 0.32966 | 3.0317
GLSO | Gladstone South T152 | CA | GLSO_66kV_BUS WEST | 66 | 13.828 | 1580.7551 | 16.2841 | 620.5091 | 19.9468 | 15.5661 | 593.1488 | 15.5744 | 593.4633 | 0.3301 | 3.0133 | 0.17574 | 1.632 | 0.32966 | 3.0317
GOOB | Gooburrum | WB | GOOB_11kV_BUS 1 | 11 | 4.7099 | 89.7354 | 5.4677 | 34.7244 | 6.4893 | 4.8363 | 30.7149 | 5.5601 | 35.3113 | 0.51122 | 1.3925 | 0.07874 | 0.88432 | 0.51044 | 1.3952
GOOB | Gooburrum | WB | GOOB_11kV_BUS 2 | 11 | 4.7099 | 89.7354 | 5.4677 | 34.7244 | 6.4893 | 4.8363 | 30.7149 | 5.5601 | 35.3113 | 0.51122 | 1.3925 | 0.07874 | 0.88432 | 0.51044 | 1.3952
GOOB | Gooburrum | WB | GOOB_3.3kV_BUS | 3.3 | 6.749 | 38.5756 | 7.1269 | 13.5785 | 7.5432 | 6.701 | 12.7672 | 7.1998 | 13.7176 | 0.03892 | 0.30811 | 0 | 0.26237 | 0.03885 | 0.30835
GOOB | Gooburrum | WB | GOOB_66kV_BUS 1 | 66 | 1.745 | 199.4785 | 1.2691 | 48.3602 | 0.98877 | 1.4744 | 56.181 | 1.6954 | 64.6052 | 15.5694 | 18.2941 | 20.7692 | 47.7364 | 15.5412 | 18.3917
GOOB | Gooburrum | WB | GOOB_66kV_BUS 2 | 66 | 1.745 | 199.4785 | 1.2691 | 48.3602 | 0.98877 | 1.4744 | 56.181 | 1.6954 | 64.6052 | 15.5694 | 18.2941 | 20.7692 | 47.7364 | 15.5412 | 18.3917
GOOT | Gootchie (TF1) | WB | GOOT_11kV_BUS A | 11 | 4.4868 | 85.4855 | 4.9269 | 31.2901 | 5.4413 | 4.455 | 28.2931 | 5.0148 | 31.8482 | 0.36363 | 1.5141 | 0.02895 | 1.1576 | 0.36291 | 1.5149
GOOT | Gootchie (TF2) | WB | GOOT_11kV_BUS B | 11 | 4.4868 | 85.4855 | 4.9269 | 31.2901 | 5.4413 | 4.455 | 28.2931 | 5.0148 | 31.8482 | 0.36363 | 1.5141 | 0.02895 | 1.1576 | 0.36291 | 1.5149
GOOT | Gootchie (TF1) | WB | GOOT_11kV_TEF T01 | 11 | 4.4868 | 85.4855 | 4.9269 | 31.2901 | 5.4413 | 4.455 | 28.2931 | 5.0148 | 31.8482 | 0.36363 | 1.5141 | 0.02895 | 1.1576 | 0.36291 | 1.5149
GOOT | Gootchie (TF2) | WB | GOOT_11kV_TEF T02 | 11 | 4.4868 | 85.4855 | 4.9269 | 31.2901 | 5.4413 | 4.455 | 28.2931 | 5.0148 | 31.8482 | 0.36363 | 1.5141 | 0.02895 | 1.1576 | 0.36291 | 1.5149
GOOT | Gootchie | WB | GOOT_66kV_BUS | 66 | 2.3077 | 263.8104 | 1.6461 | 62.7253 | 1.2696 | 1.9658 | 74.9082 | 2.2198 | 84.5859 | 10.2447 | 15.0003 | 13.5474 | 38.3813 | 10.2191 | 15.0281
GORD | Gordonvale SS | NQ | GORD_22KV BUS 1 | 22 | 4.0432 | 154.0662 | 2.9673 | 37.69 | 2.3373 | 3.5683 | 45.323 | 3.8121 | 48.4204 | 1.7356 | 2.9882 | 2.7548 | 6.7056 | 1.7343 | 2.9865
GRAC | Gracemere | CA | GRAC_11kV_TEF T1 | 11 | 6.4815 | 123.4891 | 6.9615 | 44.2115 | 7.5227 | 6.6861 | 42.4625 | 6.825 | 43.3445 | 0.09969 | 1.0732 | 0.04813 | 0.85322 | 0.09973 | 1.0739
GRAC | Gracemere | CA | GRAC_66kV_TEF T1 | 66 | 6.402 | 731.8408 | 5.2146 | 198.7016 | 4.4129 | 5.9408 | 226.3758 | 5.9782 | 227.8011 | 1.771 | 6.3034 | 2.8394 | 10.6224 | 1.7724 | 6.3292
GRCR | Granite Creek T166 | CA | GRCR_132kV_BUS 1 | 132 | 2.4454 | 559.0978 | 2.3327 | 177.7786 | 2.2151 | 2.2 | 167.6612 | 2.5639 | 195.3967 | 12.583 | 31.891 | 4.3693 | 39.8484 | 12.5606 | 31.9616
GRCR | Granite Creek T166 | CA | GRCR_22kV_BUS 1 | 22 | 3.7022 | 141.0743 | 3.8568 | 48.9879 | 4.0265 | 3.751 | 47.6446 | 3.8196 | 48.5155 | 0.49769 | 3.7412 | 0.333 | 3.303 | 0.49707 | 3.7432
GRCR | Granite Creek T166 | CA | GRCR_66kV_BUS 1 | 66 | 2.4535 | 280.4717 | 3.0593 | 116.5734 | 4.0627 | 2.8495 | 108.5789 | 3.0264 | 115.3213 | 3.4842 | 16.7264 | 0.49204 | 6.9549 | 3.4785 | 16.744
GREN | Greenvale | NQ | GREN_11kV_TEF T1 | 11 | 0.92798 | 17.6804 | 1.0389 | 6.5982 | 1.1783 | 0.94973 | 6.0316 | 1.0408 | 6.6098 | 1.2456 | 7.4243 | 0 | 5.1619 | 1.2435 | 7.432
GREN | Greenvale | NQ | GREN_66kV_TEF T1 | 66 | 0.49649 | 56.7567 | 0.31367 | 11.9524 | 0.22852 | 0.42495 | 16.1928 | 0.46324 | 17.652 | 44.8419 | 71.5301 | 80.6674 | 219.5981 | 44.7661 | 71.8044
GUEA | Gumlu Rebuild (TF1) | NQ | GUEA_11kV_BUS 1 | 11 | 2.5705 | 48.9747 | 2.865 | 18.1949 | 3.2286 | 2.6396 | 16.7636 | 2.8561 | 18.1385 | 0.65264 | 2.6382 | 0.18852 | 1.8852 | 0.6509 | 2.638
GUEA | Gumlu Rebuild (TF1) | NQ | GUEA_66kV_BUS 1 | 66 | 1.3163 | 150.4776 | 0.82093 | 31.2815 | 0.59126 | 1.1129 | 42.4058 | 1.2403 | 47.261 | 16.7083 | 27.107 | 25.7752 | 87.0978 | 16.6455 | 27.0999
GUNP | Gunpowder (TF1) | NQ - MI | GUNP_11kV_TEF T1 | 11 | 20.1192 | 383.3222 | 0.01913 | 0.12148 | 0.00963 | 17.3108 | 109.9384 | 17.3115 | 109.943 | 0.02915 | 0.346 | 0.01362 | 1094.9737 | 0.02641 | 0.35076
GUNP | Gunpowder (TF2) | NQ - MI | GUNP_11kV_TEF T2 | 11 | 20.1192 | 383.3222 | 0.01913 | 0.12148 | 0.00963 | 17.3108 | 109.9384 | 17.3115 | 109.943 | 0.02915 | 0.346 | 0.01362 | 1094.9737 | 0.02641 | 0.35076
GUNP | Gunpowder | NQ - MI | GUNP_220kV_BUS | 220 | 1.2859 | 490.0082 | 1.7504 | 222.325 | 2.8114 | 1.7778 | 225.8117 | 1.8059 | 229.382 | 10.6483 | 108.1282 | 0.54814 | 20.4096 | 9.5516 | 110.0309
GUTH | Guthalungra | NQ | GUTH_11kV_TEF T1 | 11 | 0.39633 | 7.5511 | 0.40381 | 2.5646 | 0.41154 | 0.39665 | 2.5191 | 0.40369 | 2.5638 | 1.4185 | 17.5694 | 0.83189 | 16.6314 | 1.4167 | 17.5692
GUTH | Guthalungra | NQ | GUTH_66kV_TEF T1 | 66 | 1.0524 | 120.3057 | 0.65057 | 24.7902 | 0.46695 | 0.89042 | 33.9294 | 0.98943 | 37.7024 | 21.1176 | 33.7693 | 34.0008 | 110.1122 | 21.0548 | 33.7622
HAIS | Hayman Island | MK | HAIS_11kV_TEF T1 | 11 | 1.9448 | 37.0533 | 2.3679 | 15.0383 | 3.0003 | 2.072 | 13.1587 | 2.4256 | 15.4047 | 1.4705 | 3.2774 | 0.17532 | 1.7324 | 1.4693 | 3.2747
HAIS | Hayman Island | MK | HAIS_22kV_TEF T1 | 22 | 1.7326 | 66.0207 | 1.0294 | 13.0747 | 0.69326 | 1.7231 | 21.8864 | 1.3341 | 16.9453 | 5.1808 | 6.1799 | 26.5679 | 4.8173 | 5.1759 | 6.1691
HAUG | Haughton (TF1) | NQ | HAUG_11kV_BUS 1 | 11 | 5.0497 | 96.2101 | 5.6225 | 35.7078 | 6.3496 | 5.1792 | 32.8923 | 5.6277 | 35.741 | 0.36142 | 1.3354 | 0.10246 | 0.963 | 0.35903 | 1.3337
HAUG | Haughton (TF2) | NQ | HAUG_11kV_BUS 2 | 11 | 5.0497 | 96.2101 | 5.6225 | 35.7078 | 6.3496 | 5.1792 | 32.8923 | 5.6277 | 35.741 | 0.36142 | 1.3354 | 0.10246 | 0.963 | 0.35903 | 1.3337
HAUG | Haughton | NQ | HAUG_66kV_TEF T1 | 66 | 2.578 | 294.7098 | 1.7893 | 68.1832 | 1.3594 | 2.2072 | 84.106 | 2.4571 | 93.6285 | 9.2733 | 13.3549 | 13.9003 | 35.657 | 9.2367 | 13.3437
HAUG | Haughton | NQ | HAUG_66kV_TEF T2 | 66 | 2.578 | 294.7098 | 1.7893 | 68.1832 | 1.3594 | 2.2072 | 84.106 | 2.4571 | 93.6285 | 9.2733 | 13.3549 | 13.9003 | 35.657 | 9.2367 | 13.3437
HAVI | Havilah T184 | NQ | HAVI_11kV_BUS 1 | 11 | 7.8327 | 149.2322 | 5.5516 | 35.2574 | 4.2904 | 6.8815 | 43.7037 | 7.3392 | 46.6099 | 0.12145 | 0.8836 | 0 | 2 | 0.1218 | 0.88367
HAVI | Havilah T184 | NQ | HAVI_132kV_TEF T1 | 132 | 2.7955 | 639.1298 | 1.9653 | 149.774 | 1.5149 | 2.4802 | 189.0169 | 2.59 | 197.3861 | 12.2513 | 27.3717 | 22.0341 | 64.4344 | 12.3019 | 27.3819
HELE | Helenvale | FN | HELE_22kV_BUS RMU 1 | 22 | 0.96904 | 36.9254 | 1.2175 | 15.4641 | 1.6166 | 1.1209 | 14.2374 | 1.21 | 15.369 | 2.5213 | 14.1961 | 0.00536 | 5.7799 | 2.4486 | 14.0909
HELE | Helenvale | FN | HELE_66kV_TEF T1 | 66 | 0.77157 | 88.2023 | 0.5459 | 20.8017 | 0.41505 | 0.68591 | 26.1367 | 0.72376 | 27.579 | 16.5738 | 51.7352 | 22.9806 | 121.0443 | 15.9196 | 50.7877
HEPA | Hermit Park (TF1) | NQ | HEPA_11kV_BUS 1 | 11 | 14.0248 | 267.2088 | 14.8462 | 94.2859 | 15.766 | 14.3262 | 90.9833 | 14.6324 | 92.9281 | 0.0403 | 0.49648 | 0.01784 | 0.41531 | 0.03978 | 0.49648
HEPA | Hermit Park (TF2) | NQ | HEPA_11kV_BUS 2 | 11 | 14.0248 | 267.2088 | 14.8462 | 94.2859 | 15.766 | 14.3262 | 90.9833 | 14.6324 | 92.9281 | 0.0403 | 0.49648 | 0.01784 | 0.41531 | 0.03978 | 0.49648
HEPA | Hermit Park | NQ | HEPA_66kV_BUS 1 | 66 | 13.8244 | 1580.3349 | 11.6208 | 442.8107 | 10.0073 | 12.8608 | 490.0633 | 13.1038 | 499.3218 | 0.8085 | 2.9222 | 1.0829 | 4.639 | 0.78992 | 2.9222
HEPA | Hermit Park | NQ | HEPA_66kV_BUS 2 | 66 | 13.8244 | 1580.3349 | 11.6208 | 442.8107 | 10.0073 | 12.8608 | 490.0633 | 13.1038 | 499.3218 | 0.8085 | 2.9222 | 1.0829 | 4.639 | 0.78992 | 2.9222
HIGH | Highfields (Unregulated) | SW | HIGH_T1 | 0.415 | 23.4836 | 16.2036 | 35.2264 | 8.1021 | 70.4514 | 40.6752 | 9.3553 | 40.6748 | 9.3552 | 0.001 | 0.01024 | 0 | 0 | 0.001 | 0.01024
HIGH | Highfields | SW | HIGH_11kV_TEF T3 | 11 | 2.9783 | 56.7438 | 3.3857 | 21.5023 | 3.9139 | 3.1063 | 19.7276 | 3.3641 | 21.3647 | 0.45875 | 2.3007 | 0.07559 | 1.5099 | 0.45874 | 2.3003
HIGH | Highfields | SW | HIGH_33kV_BUS | 33 | 2.6503 | 151.482 | 0.97164 | 18.5123 | 0.58979 | 2.2257 | 42.4057 | 2.4 | 45.7263 | 3.4484 | 7.1178 | 6.1909 | 49.1503 | 3.4484 | 7.114
HILL | Hillsborough | NQ | HILL_66kV_TEF T1 | 66 | 2.7833 | 318.1733 | 1.8839 | 71.7859 | 1.4156 | 2.3905 | 91.0908 | 2.6294 | 100.1955 | 7.4423 | 13.0923 | 11.0474 | 35.328 | 7.4185 | 13.0951
HOHI | Home Hill (TF1) | NQ | HOHI_11kV_BUS 1 | 11 | 16.0151 | 305.1291 | 18.0693 | 114.7555 | 20.6075 | 16.5514 | 105.1156 | 17.9972 | 114.2974 | 0.09097 | 0.42662 | 0.01483 | 0.29108 | 0.08788 | 0.42588
HOHI | Home Hill (TF2) | NQ | HOHI_11kV_BUS 2 | 11 | 16.0151 | 305.1291 | 18.0693 | 114.7555 | 20.6075 | 16.5514 | 105.1156 | 17.9972 | 114.2974 | 0.09097 | 0.42662 | 0.01483 | 0.29108 | 0.08788 | 0.42588
HOHI | Home Hill | NQ | HOHI_66kV_BUS 1 | 66 | 5.7428 | 656.4948 | 4.1851 | 159.4753 | 3.2775 | 5.1179 | 195.0173 | 5.3682 | 204.5577 | 2.6116 | 6.8155 | 3.9704 | 15.0017 | 2.5475 | 6.8083
HOHI | Home Hill | NQ | HOHI_66kV_BUS 2 | 66 | 5.7428 | 656.4948 | 4.1851 | 159.4753 | 3.2775 | 5.1179 | 195.0173 | 5.3682 | 204.5577 | 2.6116 | 6.8155 | 3.9704 | 15.0017 | 2.5475 | 6.8083
HOHI | Home Hill | NQ | HOHI_66kV_BUS 3 | 66 | 5.7428 | 656.4948 | 4.1851 | 159.4753 | 3.2775 | 5.1179 | 195.0173 | 5.3682 | 204.5577 | 2.6116 | 6.8155 | 3.9704 | 15.0017 | 2.5475 | 6.8083
HOWA | Howard | WB | HOWA_11kV_BUS 1 | 11 | 5.2257 | 99.5621 | 5.7409 | 36.4595 | 6.1277 | 5.4399 | 34.5478 | 5.5701 | 35.3747 | 0.14301 | 1.3293 | 0.05493 | 1.0223 | 0.12292 | 1.2849
HOWA | Howard | WB | HOWA_11kV_BUS 2 | 11 | 5.2257 | 99.5621 | 5.7409 | 36.4595 | 6.1277 | 5.4399 | 34.5478 | 5.5701 | 35.3747 | 0.14301 | 1.3293 | 0.05493 | 1.0223 | 0.12292 | 1.2849
HOWA | Howard | WB | HOWA_66kV_BUS 1 | 66 | 2.886 | 329.9144 | 1.8103 | 68.9809 | 1.3121 | 2.5596 | 97.5321 | 2.6213 | 99.8847 | 3.7766 | 14.0252 | 7.9092 | 39.7631 | 3.622 | 13.9715
HOWA | Howard | WB | HOWA_66kV_BUS 2 | 66 | 2.886 | 329.9144 | 1.8103 | 68.9809 | 1.3121 | 2.5596 | 97.5321 | 2.6213 | 99.8847 | 3.7766 | 14.0252 | 7.9092 | 39.7631 | 3.622 | 13.9715
HPCT | Hay Point | MK | HPCT_33kV_BUS 1 | 33 | 6.7356 | 384.9894 | 5.5978 | 106.6519 | 4.808 | 6.2161 | 118.4335 | 6.3806 | 121.5658 | 0.75769 | 3.0179 | 0.97416 | 4.9008 | 0.75788 | 3.0339
HUGH | Hughenden | NQ | HUGH_33kV_TEF T1 | 33 | 2.0238 | 115.6773 | 2.7157 | 51.7402 | 4.7843 | 2.8942 | 55.1412 | 3.0158 | 57.4581 | 2.4675 | 10.0573 | 0.03801 | 1.4823 | 2.644 | 11.0327
HUGH | Hughenden | NQ | HUGH_33kV_TEF T2 | 33 | 2.0238 | 115.6773 | 2.7157 | 51.7402 | 4.7843 | 2.8942 | 55.1412 | 3.0158 | 57.4581 | 2.4675 | 10.0573 | 0.03801 | 1.4823 | 2.644 | 11.0327
HUGH | Hughenden | NQ | HUGH_66kV_BUS 1 | 66 | 1.4658 | 167.5667 | 1.7367 | 66.1753 | 2.3299 | 1.6222 | 61.816 | 1.7884 | 68.146 | 9.2016 | 27.0743 | 1.3605 | 13.2465 | 9.4594 | 29.2638
HUGH | Hughenden | NQ | HUGH_66kV_BUS 2 | 66 | 1.4658 | 167.5667 | 1.7367 | 66.1753 | 2.3299 | 1.6222 | 61.816 | 1.7884 | 68.146 | 9.2016 | 27.0743 | 1.3605 | 13.2465 | 9.4594 | 29.2638
ICIZ | ICIZ (TF2) | CA | ICIZ_11kV_TEF T2 | 11 | 11.2507 | 214.3545 | 12.036 | 76.4387 | 12.9561 | 11.7171 | 74.4135 | 11.6775 | 74.1621 | 0.04182 | 0.61954 | 0.03645 | 0.49732 | 0.04175 | 0.6203
ILBI | Ilbilbie | MK | ILBI_11kV_TEF T1 | 11 | 0.7786 | 14.8343 | 0.85952 | 5.4587 | 0.95822 | 0.78736 | 5.0004 | 0.86468 | 5.4914 | 2.3678 | 8.6545 | 0.64594 | 6.4594 | 2.3727 | 8.667
ILBI | Ilbilbie | MK | ILBI_33kV_TEF T1 | 33 | 0.8347 | 47.7097 | 0.49124 | 9.3594 | 0.34489 | 0.69229 | 13.1899 | 0.78815 | 15.0163 | 15.4965 | 19.7556 | 25.6688 | 75.1182 | 15.5408 | 19.8681
ILRE | Ilbilbie Regulator (Primary) | MK | ILRE_33kV_TEF Primary | 33 | 0.81736 | 46.7187 | 0.48081 | 9.1606 | 0.33756 | 0.67843 | 12.9259 | 0.77134 | 14.696 | 15.787 | 20.2046 | 26.3391 | 76.7001 | 15.8313 | 20.3171
ILRE | Ilbilbie Regulator (Secondary) | MK | ILRE_33kV_TEF Secondary | 33 | 0.81736 | 46.7187 | 0.48081 | 9.1606 | 0.33756 | 0.67843 | 12.9259 | 0.77134 | 14.696 | 15.787 | 20.2046 | 26.3391 | 76.7001 | 15.8313 | 20.3171
INGH | Ingham T047 | NQ | INGH_11kV_BUS A | 11 | 8.493 | 161.8137 | 9.5083 | 60.3859 | 10.9106 | 9.0995 | 57.7897 | 9.1848 | 58.3313 | 0.05952 | 0.8204 | 0.02876 | 0.55093 | 0.05741 | 0.82802
INGH | Ingham T047 | NQ | INGH_11kV_BUS B | 11 | 8.493 | 161.8137 | 9.5083 | 60.3859 | 10.9106 | 9.0995 | 57.7897 | 9.1848 | 58.3313 | 0.05952 | 0.8204 | 0.02876 | 0.55093 | 0.05741 | 0.82802
INGH | Ingham T047 | NQ | INGH_66kV_BUS A | 66 | 4.293 | 490.7511 | 5.0026 | 190.6257 | 6.1908 | 4.8024 | 182.9967 | 4.8336 | 184.1833 | 1.1072 | 9.7008 | 0.48203 | 5.3232 | 1.0314 | 9.9752
INGH | Ingham T047 | NQ | INGH_66kV_BUS B | 66 | 4.293 | 490.7511 | 5.0026 | 190.6257 | 6.1908 | 4.8024 | 182.9967 | 4.8336 | 184.1833 | 1.1072 | 9.7008 | 0.48203 | 5.3232 | 1.0314 | 9.9752
INGH | Ingham T047 | NQ | INGH_66kV_BUS C | 66 | 4.293 | 490.7511 | 5.0026 | 190.6257 | 6.1908 | 4.8024 | 182.9967 | 4.8336 | 184.1833 | 1.1072 | 9.7008 | 0.48203 | 5.3232 | 1.0314 | 9.9752
INNI | Innisfail T050 | FN | INNI_22kV_BUS 1 | 22 | 11.5661 | 440.7256 | 8.8092 | 111.8923 | 7.1702 | 10.9333 | 138.8716 | 10.2405 | 130.0713 | 0.13478 | 1.2005 | 0.54158 | 2.2732 | 0.12721 | 1.2162
INNI | Innisfail T050 | FN | INNI_22kV_BUS 2 | 22 | 11.5661 | 440.7256 | 8.8092 | 111.8923 | 7.1702 | 10.9333 | 138.8716 | 10.2405 | 130.0713 | 0.13478 | 1.2005 | 0.54158 | 2.2732 | 0.12721 | 1.2162
ISIS | Isis T131 | WB | ISIS_132kV_BUS 1 | 132 | 7.8516 | 1795.1211 | 8.5681 | 652.9765 | 9.6528 | 8.1718 | 622.7777 | 8.4334 | 642.7101 | 1.9373 | 10.5006 | 0.91568 | 7.7237 | 1.8958 | 10.7439
ISIS | Isis T131 | WB | ISIS_132kV_BUS 2 | 132 | 7.8516 | 1795.1211 | 8.5681 | 652.9765 | 9.6528 | 8.1718 | 622.7777 | 8.4334 | 642.7101 | 1.9373 | 10.5006 | 0.91568 | 7.7237 | 1.8958 | 10.7439
ISIS | Isis T131 | WB | ISIS_66kV_BUS 1 | 66 | 8.3065 | 949.5653 | 9.7006 | 369.6442 | 11.7256 | 9.2469 | 352.3547 | 9.2991 | 354.3453 | 0.52954 | 5.0186 | 0.23909 | 2.8363 | 0.48089 | 5.0484
ISIS | Isis T131 | WB | ISIS_66kV_BUS 2 | 66 | 8.3065 | 949.5653 | 9.7006 | 369.6442 | 11.7256 | 9.2469 | 352.3547 | 9.2991 | 354.3453 | 0.52954 | 5.0186 | 0.23909 | 2.8363 | 0.48089 | 5.0484
ISPL | Isaac Plains | MK | ISPL_66kV_BUS | 66 | 6.923 | 791.405 | 5.6576 | 215.585 | 4.7881 | 6.5365 | 249.0743 | 6.3674 | 242.6309 | 1.5079 | 5.8638 | 2.97 | 9.6683 | 1.492 | 5.8773
JAND | Jandowae | SW | JAND_33kV_BUS | 33 | 0.44942 | 25.6881 | 0.32646 | 6.22 | 0.24839 | 0.35755 | 6.8122 | 0.45394 | 8.6486 | 38.2551 | 26.6697 | 46.4875 | 94.8663 | 38.227 | 26.6831
JAND | Jandowae | SW | JAND_11kV_BUS 1 | 11 | 0.99656 | 18.987 | 1.2991 | 8.2503 | 1.8242 | 1.0822 | 6.8729 | 1.408 | 8.9421 | 4.3648 | 5.4857 | 0.1142 | 2.5224 | 4.3616 | 5.4872
JAND | Jandowae | SW | JAND_11kV_TEF T01 | 11 | 0.54875 | 10.455 | 0.61656 | 3.9157 | 0.69634 | 0.53316 | 3.386 | 0.64021 | 4.0659 | 4.6941 | 11.8342 | 0.44354 | 8.8709 | 4.691 | 11.8356
JAND | Jandowae | SW | JAND_11kV_TEF T02 | 11 | 0.99656 | 18.987 | 1.2991 | 8.2503 | 1.8242 | 1.0822 | 6.8729 | 1.408 | 8.9421 | 4.3648 | 5.4857 | 0.1142 | 2.5224 | 4.3616 | 5.4872
JARV | Jarvisfield (TF1) | NQ | JARV_11kV_BUS 1 | 11 | 6.7699 | 128.9849 | 7.2835 | 46.2567 | 7.8751 | 6.9426 | 44.0917 | 7.1816 | 45.6094 | 0.15663 | 1.0199 | 0.07367 | 0.81178 | 0.15434 | 1.0199
JARV | Jarvisfield (TF2) | NQ | JARV_11kV_BUS 2 | 11 | 6.7699 | 128.9849 | 7.2835 | 46.2567 | 7.8751 | 6.9426 | 44.0917 | 7.1816 | 45.6094 | 0.15663 | 1.0199 | 0.07367 | 0.81178 | 0.15434 | 1.0199
JARV | Jarvisfield | NQ | JARV_66kV_BUS 1 | 66 | 5.1957 | 593.9444 | 3.9528 | 150.6222 | 3.1746 | 4.6494 | 177.1642 | 4.9044 | 186.8825 | 2.9867 | 7.4942 | 4.0946 | 15.2184 | 2.904 | 7.4918
JARV | Jarvisfield | NQ | JARV_66kV_BUS 2 | 66 | 5.1957 | 593.9444 | 3.9528 | 150.6222 | 3.1746 | 4.6494 | 177.1642 | 4.9044 | 186.8825 | 2.9867 | 7.4942 | 4.0946 | 15.2184 | 2.904 | 7.4918
JUCR | Julia Creek | NQ | JUCR_33kV_BUS 1 | 33 | 0.42786 | 24.4555 | 0.53713 | 10.2337 | 0.72716 | 0.4802 | 9.149 | 0.55422 | 10.5593 | 18.8274 | 45.2201 | 1.2816 | 19.3782 | 18.8918 | 45.7675
JUCR | Julia Creek | NQ | JUCR_33kV_BUS 2 | 33 | 0.42786 | 24.4555 | 0.53713 | 10.2337 | 0.72716 | 0.4802 | 9.149 | 0.55422 | 10.5593 | 18.8274 | 45.2201 | 1.2816 | 19.3782 | 18.8918 | 45.7675
JUCR | Julia Creek | NQ | JUCR_66kV_BUS 1 | 66 | 0.27085 | 30.9626 | 0.30985 | 11.807 | 0.3629 | 0.26434 | 10.0727 | 0.32443 | 12.3623 | 72.8234 | 136.5492 | 10.9238 | 99.0112 | 73.0812 | 138.7387
JUPO | Jubilee Pocket | MK | JUPO_11kV_BUS 1 | 11 | 6.3062 | 120.1497 | 7.2134 | 45.8115 | 8.3841 | 6.6104 | 41.9815 | 7.1547 | 45.4384 | 0.19736 | 1.0901 | 0.02227 | 0.69804 | 0.19614 | 1.0874
JUPO | Jubilee Pocket | MK | JUPO_11kV_BUS 2 | 11 | 6.3062 | 120.1497 | 7.2134 | 45.8115 | 8.3841 | 6.6104 | 41.9815 | 7.1547 | 45.4384 | 0.19736 | 1.0901 | 0.02227 | 0.69804 | 0.19614 | 1.0874
JUPO | Jubilee Pocket | MK | JUPO_11kV_BUS 3 | 11 | 6.3062 | 120.1497 | 7.2134 | 45.8115 | 8.3841 | 6.6104 | 41.9815 | 7.1547 | 45.4384 | 0.19736 | 1.0901 | 0.02227 | 0.69804 | 0.19614 | 1.0874
JUPO | Jubilee Pocket | MK | JUPO_66kV_BUS 1 | 66 | 2.7118 | 310.0032 | 2.0826 | 79.359 | 1.6755 | 2.3935 | 91.2049 | 2.6012 | 99.1183 | 6.3033 | 14.113 | 7.4912 | 28.8218 | 6.2594 | 14.0166
JUPO | Jubilee Pocket | MK | JUPO_66kV_BUS 2 | 66 | 2.7118 | 310.0032 | 2.0826 | 79.359 | 1.6755 | 2.3935 | 91.2049 | 2.6012 | 99.1183 | 6.3033 | 14.113 | 7.4912 | 28.8218 | 6.2594 | 14.0166
KAIM | Kaimkillenbun | SW | KAIM_11kV_BUS | 11 | 1.3145 | 25.0452 | 1.5243 | 9.6805 | 1.7893 | 1.2881 | 8.1803 | 1.5917 | 10.1088 | 2.2864 | 4.798 | 0.1828 | 3.3062 | 2.2866 | 4.798
KAIM | Kaimkillenbun | SW | KAIM_33kV_BUS | 33 | 0.90305 | 51.6162 | 0.68313 | 13.0154 | 0.53393 | 0.72406 | 13.7951 | 0.91732 | 17.4774 | 18.9325 | 13.4268 | 22.0276 | 43.0419 | 18.9338 | 13.4269
KALA | Kalamia | NQ | KALA_11kV_BUS 1 | 11 | 7.6927 | 146.5653 | 7.3075 | 46.4089 | 6.6616 | 7.4328 | 47.2047 | 7.6619 | 48.6593 | 0.15187 | 0.89534 | 0.07245 | 1.0923 | 0.10364 | 0.86149
KALA | Kalamia | NQ | KALA_66kV_TEF T1 | 66 | 3.121 | 356.7776 | 2.1547 | 82.1066 | 1.6315 | 2.7212 | 103.6914 | 2.9361 | 111.8787 | 6.6432 | 11.6722 | 10.4513 | 30.0393 | 6.4158 | 11.7017
KAME | Kamerunga T053 | FN | KAME_22kV_BUS 1 | 22 | 13.5216 | 515.2418 | 9.6078 | 122.0351 | 7.3355 | 12.8107 | 162.7171 | 11.8597 | 150.6378 | 0.08526 | 1.0298 | 0.56154 | 2.2584 | 0.07919 | 1.0137
KAME | Kamerunga T053 | FN | KAME_22kV_BUS 2 | 22 | 13.5216 | 515.2418 | 9.6078 | 122.0351 | 7.3355 | 12.8107 | 162.7171 | 11.8597 | 150.6378 | 0.08526 | 1.0298 | 0.56154 | 2.2584 | 0.07919 | 1.0137
KEBE | Kewarra Beach | FN | KEBE_22kV_BUS 1 | 22 | 9.0506 | 344.8729 | 6.3205 | 80.2811 | 4.7762 | 8.3911 | 106.581 | 8.1228 | 103.1739 | 0.48737 | 1.4648 | 1.3323 | 3.3226 | 0.46158 | 1.4396
KEBE | Kewarra Beach | FN | KEBE_22kV_BUS 2 | 22 | 9.0506 | 344.8729 | 6.3205 | 80.2811 | 4.7762 | 8.3911 | 106.581 | 8.1228 | 103.1739 | 0.48737 | 1.4648 | 1.3323 | 3.3226 | 0.46158 | 1.4396
KECE | Kelsey Creek East (TF1) | MK | KECE_11kV_BUS 1 | 11 | 12.4892 | 237.9519 | 14.2317 | 90.3832 | 16.4498 | 13.2645 | 84.2406 | 13.9233 | 88.4251 | 0.07404 | 0.55444 | 0.01516 | 0.35693 | 0.07331 | 0.55226
KECE | Kelsey Creek East (TF2) | MK | KECE_11kV_BUS 2 | 11 | 12.4892 | 237.9519 | 14.2317 | 90.3832 | 16.4498 | 13.2645 | 84.2406 | 13.9233 | 88.4251 | 0.07404 | 0.55444 | 0.01516 | 0.35693 | 0.07331 | 0.55226
KECE | Kelsey Creek East (TF3) | MK | KECE_11kV_BUS 3 | 11 | 12.4892 | 237.9519 | 14.2317 | 90.3832 | 16.4498 | 13.2645 | 84.2406 | 13.9233 | 88.4251 | 0.07404 | 0.55444 | 0.01516 | 0.35693 | 0.07331 | 0.55226
KECE | Kelsey Creek East (TF1) | MK | KECE_66kV_TEF T1 | 66 | 5.6161 | 642.0084 | 7.1558 | 272.6705 | 9.6977 | 6.6618 | 253.8474 | 7.0838 | 269.929 | 2.1452 | 7.1485 | 0.40448 | 2.7227 | 2.1191 | 7.0701
KECE | Kelsey Creek East (TF2) | MK | KECE_66kV_TEF T2 | 66 | 5.6237 | 642.8747 | 7.1764 | 273.4579 | 9.7513 | 6.6828 | 254.6484 | 7.1097 | 270.9149 | 2.1395 | 7.1398 | 0.3937 | 2.6939 | 2.1134 | 7.0613
KEMM | Kemmis T067 | MK | KEMM_66kV_BUS 1 | 66 | 5.981 | 683.7255 | 7.4916 | 285.469 | 10.0617 | 7.482 | 285.1034 | 6.9425 | 264.546 | 1.0779 | 6.9247 | 0.88355 | 2.6283 | 1.0832 | 6.9536
KEMM | Kemmis T067 | MK | KEMM_66kV_BUS 2 | 66 | 5.981 | 683.7255 | 7.4916 | 285.469 | 10.0617 | 7.482 | 285.1034 | 6.9425 | 264.546 | 1.0779 | 6.9247 | 0.88355 | 2.6283 | 1.0832 | 6.9536
KESP | Kearneys Spring T167 (TF1) | SW | KESP_110kV_TEF T1 | 110 | 20.0733 | 3824.4834 | 20.4267 | 1297.2692 | 20.4933 | 20.3529 | 1292.5836 | 20.1461 | 1279.4523 | 0.29993 | 3.4678 | 0.3535 | 3.3311 | 0.30169 | 3.4181
KESP | Kearneys Spring T167 (TF2) | SW | KESP_110kV_TEF T2 | 110 | 20.0498 | 3820.0074 | 20.3789 | 1294.2317 | 20.4212 | 20.3174 | 1290.3295 | 20.1099 | 1277.1514 | 0.30063 | 3.4718 | 0.35582 | 3.3469 | 0.30239 | 3.4221
KESP | Kearneys Spring T167 | SW | KESP_11kV_BUS 1 | 11 | 18.644 | 355.215 | 4.0751 | 25.8802 | 2.2857 | 16.1629 | 102.6481 | 16.2306 | 103.078 | 0.01156 | 0.37458 | 0 | 4.395 | 0.01158 | 0.37408
KESP | Kearneys Spring T167 | SW | KESP_11kV_BUS 2 | 11 | 18.644 | 355.215 | 4.0751 | 25.8802 | 2.2857 | 16.1629 | 102.6481 | 16.2306 | 103.078 | 0.01156 | 0.37458 | 0 | 4.395 | 0.01158 | 0.37408
KESP | Kearneys Spring T167 | SW | KESP_11kV_BUS 3 | 11 | 18.644 | 355.215 | 4.0751 | 25.8802 | 2.2857 | 16.1629 | 102.6481 | 16.2306 | 103.078 | 0.01156 | 0.37458 | 0 | 4.395 | 0.01158 | 0.37408
KIDS | Kidston T077 | FN | KIDS_132kV_BUS 1 | 132 | 0.87073 | 199.0765 | 1.1637 | 88.6869 | 1.8658 | 1.149 | 87.5647 | 1.2428 | 94.717 | 30.8846 | 91.1885 | 0.79 | 20.2173 | 31.5324 | 95.258
KIDS | Kidston T077 | FN | KIDS_132kV_BUS 2 | 132 | 0.87073 | 199.0765 | 1.1637 | 88.6869 | 1.8658 | 1.149 | 87.5647 | 1.2428 | 94.717 | 30.8846 | 91.1885 | 0.79 | 20.2173 | 31.5324 | 95.258
KIDS | Kidston T077 | FN | KIDS_6.6kV_BUS 1 | 6.6 | 10.0578 | 114.9763 | 0.02205 | 0.08404 | 0.01116 | 8.6096 | 32.807 | 8.5987 | 32.7654 | 0.08766 | 0.40742 | 569.9998 | 0.17689 | 0.08928 | 0.4176
KIEA | Kilkivan East | WB | KIEA 11kV_BUS 1 | 11 | 6.7157 | 127.9505 | 4.5767 | 29.0659 | 3.4707 | 6.0084 | 38.1588 | 6.1289 | 38.9239 | 0.04635 | 1.0393 | 0 | 2.5 | 0.04553 | 1.0395
KIEA | Kilkivan East | WB | KIEA 11kV_BUS 2 | 11 | 6.7157 | 127.9505 | 4.5767 | 29.0659 | 3.4707 | 6.0084 | 38.1588 | 6.1289 | 38.9239 | 0.04635 | 1.0393 | 0 | 2.5 | 0.04553 | 1.0395
KIEA | Kilkivan East | WB | KIEA 132kV_BUS 1 | 132 | 6.2077 | 1419.263 | 4.7987 | 365.7115 | 3.9002 | 5.5745 | 424.832 | 5.8671 | 447.1351 | 3.4587 | 13.0557 | 3.7972 | 25.2148 | 3.3413 | 13.0619
KIEA | Kilkivan East | WB | KIEA 132kV_BUS 2 | 132 | 6.2074 | 1419.2087 | 4.7985 | 365.6958 | 3.9001 | 5.5743 | 424.8149 | 5.8669 | 447.1179 | 3.4588 | 13.0562 | 3.7974 | 25.216 | 3.3415 | 13.0624
KIEA | Kilkivan East | WB | KIEA 66kV_BUS 1 | 66 | 3.9166 | 447.7325 | 4.5411 | 173.0387 | 5.3986 | 4.2134 | 160.5513 | 4.453 | 169.6811 | 1.5763 | 10.5865 | 0.25355 | 6.308 | 1.5468 | 10.5931
KILL | Killarney (TF1) | SW | KILL_11kV_BUS 1 | 11 | 1.7165 | 32.7043 | 2.2538 | 14.3135 | 3.2389 | 1.9789 | 12.568 | 2.398 | 15.2293 | 2.1147 | 3.4777 | 0.06477 | 1.2954 | 2.1087 | 3.4792
KILL | Killarney (TF2) | SW | KILL_11kV_BUS 2 | 11 | 1.7165 | 32.7043 | 2.2538 | 14.3135 | 3.2389 | 1.9789 | 12.568 | 2.398 | 15.2293 | 2.1147 | 3.4777 | 0.06477 | 1.2954 | 2.1087 | 3.4792
KILL | Killarney (TF3) | SW | KILL_11kV_BUS 3 | 11 | 1.7165 | 32.7043 | 2.2538 | 14.3135 | 3.2389 | 1.9789 | 12.568 | 2.398 | 15.2293 | 2.1147 | 3.4777 | 0.06477 | 1.2954 | 2.1087 | 3.4792
KILL | Killarney | SW | KILL_33kV_BUS | 33 | 0.7778 | 44.4574 | 0.49176 | 9.3693 | 0.35214 | 0.63427 | 12.0845 | 0.7537 | 14.3599 | 18.4498 | 19.6415 | 25.1857 | 72.5177 | 18.395 | 19.6546
KING | Kingaroy | WB | KING_11kV_BUS A | 11 | 11.1564 | 212.5582 | 12.6594 | 80.3978 | 14.6391 | 11.8783 | 75.4375 | 12.3557 | 78.4691 | 0.07284 | 0.62201 | 0.01687 | 0.40309 | 0.07163 | 0.62274
KING | Kingaroy | WB | KING_11kV_BUS B | 11 | 11.1564 | 212.5582 | 12.6594 | 80.3978 | 14.6391 | 11.8783 | 75.4375 | 12.3557 | 78.4691 | 0.07284 | 0.62201 | 0.01687 | 0.40309 | 0.07163 | 0.62274
KING | Kingaroy | WB | KING_66kV_BUS 1 | 66 | 5.1535 | 589.1228 | 3.0215 | 115.1328 | 2.139 | 4.5292 | 172.5855 | 4.6423 | 176.8954 | 2.0149 | 7.8809 | 4.5703 | 24.9458 | 1.9714 | 7.9073
KING | Kingaroy | WB | KING_66kV_BUS 2 | 66 | 5.1535 | 589.1228 | 3.0215 | 115.1328 | 2.139 | 4.5292 | 172.5855 | 4.6423 | 176.8954 | 2.0149 | 7.8809 | 4.5703 | 24.9458 | 1.9714 | 7.9073
KING | Kingaroy | WB | KING_66kV_BUS 3 | 66 | 5.1535 | 589.1228 | 3.0215 | 115.1328 | 2.139 | 4.5292 | 172.5855 | 4.6423 | 176.8954 | 2.0149 | 7.8809 | 4.5703 | 24.9458 | 1.9714 | 7.9073
KIRK | Kirknie | NQ | KIRK_11kV_BUS 1 | 11 | 5.1739 | 98.5754 | 5.6065 | 35.6061 | 6.103 | 5.1963 | 33.001 | 5.6377 | 35.8045 | 0.26012 | 1.325 | 0.05168 | 1.0447 | 0.25945 | 1.3246
KIRK | Kirknie | NQ | KIRK_11kV_BUS 2 | 11 | 5.1739 | 98.5754 | 5.6065 | 35.6061 | 6.103 | 5.1963 | 33.001 | 5.6377 | 35.8045 | 0.26012 | 1.325 | 0.05168 | 1.0447 | 0.25945 | 1.3246
KIRK | Kirknie | NQ | KIRK_66kV_BUS 1 | 66 | 3.3336 | 381.0832 | 2.6075 | 99.3581 | 2.1295 | 2.9374 | 111.9312 | 3.2148 | 122.4996 | 7.504 | 10.089 | 10.3843 | 20.8492 | 7.4798 | 10.0761
KITO | Kilkivan Town (TF1) | WB | KITO_11kV_BUS 1 | 11 | 1.4586 | 27.7898 | 1.5345 | 9.7451 | 1.6187 | 1.5009 | 9.5323 | 1.4995 | 9.5229 | 0.84967 | 4.7141 | 0.72977 | 4.0137 | 0.84878 | 4.7143
KITO | Kilkivan Town (TF2) | WB | KITO_11kV_BUS 2 | 11 | 1.4586 | 27.7898 | 1.5345 | 9.7451 | 1.6187 | 1.5009 | 9.5323 | 1.4995 | 9.5229 | 0.84967 | 4.7141 | 0.72977 | 4.0137 | 0.84878 | 4.7143
KITO | Kilkivan Town | WB | KITO_66kV_BUS | 66 | 3.6914 | 421.9815 | 4.0969 | 156.1121 | 4.6027 | 3.8848 | 148.0319 | 3.9918 | 152.1071 | 1.9702 | 11.1841 | 0.97771 | 7.9267 | 1.9407 | 11.1907
KOCR | Kogan Creek | SW | KOCR_11kV_TEF T1 | 11 | 1.9022 | 36.2411 | 2.1585 | 13.7083 | 2.489 | 1.9681 | 12.4991 | 2.1565 | 13.6958 | 0.79705 | 3.5852 | 0.11929 | 2.3857 | 0.79393 | 3.5867
KOCR | Kogan Creek | SW | KOCR_33kV_TEF T1 | 33 | 1.6903 | 96.6133 | 1.0848 | 20.6683 | 0.79229 | 1.43 | 27.2457 | 1.5985 | 30.4558 | 6.0998 | 10.7951 | 8.3113 | 32.6147 | 6.0717 | 10.8085
KOGA | Kogan Regulator (Regulated) | SW | KOGA_33kV_BUS R1 Downstream | 33 | 1.1042 | 63.1149 | 0.91985 | 17.5256 | 0.78412 | 0.97429 | 18.5627 | 1.0895 | 20.7585 | 8.5205 | 16.9619 | 7.8294 | 29.7498 | 8.5218 | 16.962
KOGA | Kogan Regulator (Unregulated) | SW | KOGA_33kV_BUS R1 Upstream | 33 | 1.1839 | 67.6678 | 0.96866 | 18.4554 | 0.81443 | 1.0342 | 19.7046 | 1.168 | 22.2542 | 8.4503 | 15.5577 | 7.9265 | 28.8633 | 8.4516 | 15.5578
KOUM | Koumala (1 Regulator) | MK | KOUM_11kV_TEF R1 | 11 | 1.8398 | 35.0538 | 2.1747 | 13.811 | 2.6536 | 1.9205 | 12.197 | 2.2137 | 14.0591 | 1.3862 | 3.535 | 0.20603 | 2.0815 | 1.3911 | 3.5475
KOUM | Koumala (2 Regulator) | MK | KOUM_11kV_TEF R2 | 11 | 1.8398 | 35.0538 | 2.1747 | 13.811 | 2.6536 | 1.9205 | 12.197 | 2.2137 | 14.0591 | 1.3862 | 3.535 | 0.20603 | 2.0815 | 1.3911 | 3.5475
KOUM | Koumala | MK | KOUM_33kV_TEF T1 | 33 | 1.2438 | 71.0904 | 0.75201 | 14.3278 | 0.53364 | 1.0241 | 19.5125 | 1.1834 | 22.5473 | 10.6212 | 13.0816 | 15.9447 | 48.5841 | 10.6655 | 13.1941
KUNW | Kunwarara | CA | KUNW_11kV_TEF T1 | 11 | 3.7106 | 70.6963 | 4.4202 | 28.0721 | 5.4409 | 3.9337 | 24.9822 | 4.4695 | 28.3852 | 0.49165 | 1.8174 | 0.01341 | 0.99995 | 0.4917 | 1.8181
KUNW | Kunwarara | CA | KUNW_66kV_TEF T1 | 66 | 1.2294 | 140.5409 | 0.76655 | 29.2094 | 0.55301 | 1.0399 | 39.6242 | 1.1565 | 44.0682 | 17.2166 | 29.4283 | 26.0509 | 93.6045 | 17.2182 | 29.4546
LACR | Lakes Creek | CA | LACR_11kV_BUS LH | 11 | 16.6451 | 317.1321 | 18.8973 | 120.0142 | 21.8772 | 17.6867 | 112.3255 | 18.4865 | 117.4048 | 0.06097 | 0.41525 | 0.01717 | 0.26918 | 0.06088 | 0.41587
LACR | Lakes Creek | CA | LACR_11kV_BUS RH | 11 | 16.6451 | 317.1321 | 18.8973 | 120.0142 | 21.8772 | 17.6867 | 112.3255 | 18.4865 | 117.4048 | 0.06097 | 0.41525 | 0.01717 | 0.26918 | 0.06088 | 0.41587
LACR | Lakes Creek | CA | LACR_66kV_BUS VERT_1 | 66 | 7.4434 | 850.8909 | 6.1191 | 233.1675 | 5.2103 | 6.8896 | 262.5292 | 6.9987 | 266.6876 | 1.5767 | 5.4062 | 2.3173 | 8.9752 | 1.5736 | 5.4283
LACR | Lakes Creek | CA | LACR_66kV_BUS VERT_2 | 66 | 7.4434 | 850.8909 | 6.1191 | 233.1675 | 5.2103 | 6.8896 | 262.5292 | 6.9987 | 266.6876 | 1.5767 | 5.4062 | 2.3173 | 8.9752 | 1.5736 | 5.4283
LACR | Lakes Creek | CA | LACR_66kV_BUS VERT_3 | 66 | 7.4434 | 850.8909 | 6.1191 | 233.1675 | 5.2103 | 6.8896 | 262.5292 | 6.9987 | 266.6876 | 1.5767 | 5.4062 | 2.3173 | 8.9752 | 1.5736 | 5.4283
LACR | Lakes Creek | CA | LACR_66kV_BUS VERT_4 | 66 | 7.4434 | 850.8909 | 6.1191 | 233.1675 | 5.2103 | 6.8896 | 262.5292 | 6.9987 | 266.6876 | 1.5767 | 5.4062 | 2.3173 | 8.9752 | 1.5736 | 5.4283
LAKE | Lakeland | FN | LAKE_132kV_BUS 1 | 132 | 0.9259 | 211.6894 | 0.88894 | 67.7464 | 0.83643 | 0.87771 | 66.8906 | 0.94054 | 71.6791 | 23.0703 | 87.5517 | 12.8336 | 103.4404 | 21.428 | 86.0523
LAKE | Lakeland | FN | LAKE_132kV_BUS 2 | 132 | 0.9259 | 211.6894 | 0.88894 | 67.7464 | 0.83643 | 0.87771 | 66.8906 | 0.94054 | 71.6791 | 23.0703 | 87.5517 | 12.8336 | 103.4404 | 21.428 | 86.0523
LAKE | Lakeland | FN | LAKE_22kV_BUS 1 | 22 | 1.7209 | 65.5764 | 2.1439 | 27.2318 | 2.8297 | 2.0071 | 25.4934 | 2.1033 | 26.7159 | 0.87255 | 8.0718 | 0 | 3.3523 | 0.83642 | 8.0517
LAKE | Lakeland | FN | LAKE_22kV_BUS 2 | 22 | 1.7209 | 65.5764 | 2.1439 | 27.2318 | 2.8297 | 2.0071 | 25.4934 | 2.1033 | 26.7159 | 0.87255 | 8.0718 | 0 | 3.3523 | 0.83642 | 8.0517
LAKE | Lakeland (TF1) | FN | LAKE_66kV_BUS 1 | 66 | 1.3489 | 154.2038 | 1.2405 | 47.2711 | 1.1117 | 1.2782 | 48.707 | 1.3352 | 50.878 | 5.8172 | 30.5238 | 3.8331 | 40.1761 | 5.163 | 29.5763
LAKE | Lakeland (TF2) | FN | LAKE_66kV_BUS 2 | 66 | 1.3489 | 154.2038 | 1.2405 | 47.2711 | 1.1117 | 1.2782 | 48.707 | 1.3352 | 50.878 | 5.8172 | 30.5238 | 3.8331 | 40.1761 | 5.163 | 29.5763
LANN | Lannercost | NQ | LANN_11kV_BUS | 11 | 3.518 | 67.0274 | 3.8952 | 24.738 | 4.3727 | 3.6058 | 22.9002 | 3.884 | 24.667 | 0.41221 | 1.9425 | 0.1038 | 1.4075 | 0.41011 | 1.9501
LANN | Lannercost | NQ | LANN_66kV_BUS 1 | 66 | 1.8854 | 215.5275 | 1.4689 | 55.9738 | 1.2078 | 1.6604 | 63.2702 | 1.8078 | 68.8865 | 11.1027 | 19.2612 | 14.0708 | 38.777 | 11.0268 | 19.5355
LANN | Lannercost | NQ | LANN_66kV_BUS 2 | 66 | 1.8854 | 215.5275 | 1.4689 | 55.9738 | 1.2078 | 1.6604 | 63.2702 | 1.8078 | 68.8865 | 11.1027 | 19.2612 | 14.0708 | 38.777 | 11.0268 | 19.5355
LAQU | Laguna Quays (TF1) | MK | LAQU_11kV_TEF T1 | 11 | 4.9027 | 93.4081 | 5.9039 | 37.4948 | 7.3469 | 5.152 | 32.7198 | 6.0438 | 38.3835 | 0.51098 | 1.3302 | 0.03651 | 0.73043 | 0.51026 | 1.328
LAQU | Laguna Quays (TF2) | MK | LAQU_11kV_TEF T2 | 11 | 4.9027 | 93.4081 | 5.9039 | 37.4948 | 7.3469 | 5.152 | 32.7198 | 6.0438 | 38.3835 | 0.51098 | 1.3302 | 0.03651 | 0.73043 | 0.51026 | 1.328
LAQU | Laguna Quays (TF2) | MK | LAQU_66kV_TEF T1 | 66 | 1.5209 | 173.8587 | 1.1271 | 42.9484 | 0.88313 | 1.283 | 48.8877 | 1.4904 | 56.7921 | 17.1016 | 21.6128 | 20.4964 | 54.105 | 17.0755 | 21.5343
LAQU | Laguna Quays (TF2) | MK | LAQU_66kV_TEF T2 | 66 | 1.5215 | 173.935 | 1.1277 | 42.9703 | 0.88362 | 1.2836 | 48.9101 | 1.4911 | 56.8174 | 17.0934 | 21.6038 | 20.4852 | 54.0731 | 17.0673 | 21.5254
LARO | LARO LV | CA | LARO_11kV_BUS | 11 | 6.0448 | 115.1695 | 6.2924 | 39.9621 | 6.5656 | 6.1718 | 39.1962 | 6.1846 | 39.2775 | 0.06983 | 1.1536 | 0.05776 | 1.0169 | 0.06975 | 1.1544
LARO | LARO HV | CA | LARO_66kV_TEF T1 | 66 | 8.4848 | 969.9383 | 8.4948 | 323.6966 | 8.5455 | 8.6907 | 331.1593 | 8.281 | 315.5476 | 0.43443 | 4.9211 | 0.83292 | 4.8354 | 0.43163 | 4.9487
LEIC | Leichhardt | CA | LEIC_66kV_BUS TRANSFER | 66 | 3.6524 | 417.5228 | 2.7574 | 105.0726 | 2.2086 | 3.2782 | 124.9157 | 3.4262 | 130.5552 | 4.4528 | 10.5773 | 6.9761 | 21.6235 | 4.4689 | 10.5416
LILY | Lilyvale | CA | LILY_66kV_BUS NORTH | 66 | 14.762 | 1687.527 | 17.9864 | 685.375 | 22.9819 | 17.0366 | 649.1824 | 17.3458 | 660.9631 | 0.31438 | 2.822 | 0.09152 | 1.3128 | 0.30347 | 2.8204
LILY | Lilyvale | CA | LILY_66kV_BUS SOUTH | 66 | 14.762 | 1687.527 | 17.9864 | 685.375 | 22.9819 | 17.0366 | 649.1824 | 17.3458 | 660.9631 | 0.31438 | 2.822 | 0.09152 | 1.3128 | 0.30347 | 2.8204
LITT | Littlemore | CA | LITT_11kV_TEF T1 | 11 | 2.8071 | 53.4817 | 3.1587 | 20.0608 | 3.6018 | 2.8762 | 18.2665 | 3.1673 | 20.115 | 0.79065 | 2.3598 | 0.24707 | 1.6579 | 0.79067 | 2.3604
LITT | Littlemore | CA | LITT_11kV_TEF T2 | 11 | 2.8071 | 53.4817 | 3.1587 | 20.0608 | 3.6018 | 2.8762 | 18.2665 | 3.1673 | 20.115 | 0.79065 | 2.3598 | 0.24707 | 1.6579 | 0.79067 | 2.3604
LITT | Littlemore | CA | LITT_66kV_BUS TRANSFER | 66 | 1.3115 | 149.9235 | 0.83786 | 31.9268 | 0.60869 | 1.0944 | 41.7043 | 1.2515 | 47.6902 | 19.5687 | 25.27 | 29.3759 | 82.9735 | 19.5695 | 25.2899
LITT | Littlemore | CA | LITT_66kV_TEF T2 | 66 | 1.3115 | 149.9235 | 0.83786 | 31.9268 | 0.60869 | 1.0944 | 41.7043 | 1.2515 | 47.6902 | 19.5687 | 25.27 | 29.3759 | 82.9735 | 19.5695 | 25.2899
LOCR | Louisa Creek | MK | LOCR_11kV_BUS 1 | 11 | 3.1283 | 59.6017 | 3.2481 | 20.6281 | 3.3801 | 3.1752 | 20.1653 | 3.2097 | 20.3845 | 0.1537 | 2.2279 | 0.09923 | 1.982 | 0.15372 | 2.2297
LOCR | Louisa Creek (TF1) | MK | LOCR_132kV_TEF T1 | 132 | 3.8263 | 874.8071 | 4.3457 | 331.189 | 5.0946 | 4.1178 | 313.8145 | 4.2241 | 321.9229 | 4.3951 | 21.4641 | 2.0951 | 13.6539 | 4.3981 | 21.7204
LOCR | Louisa Creek (TF2) | MK | LOCR_132kV_TEF T2 | 132 | 3.8263 | 874.8071 | 4.3457 | 331.189 | 5.0946 | 4.1178 | 313.8145 | 4.2241 | 321.9229 | 4.3951 | 21.4641 | 2.0951 | 13.6539 | 4.3981 | 21.7204
LOCR | Louisa Creek | MK | LOCR_33kV_BUS 1 | 33 | 9.3478 | 534.2969 | 10.0697 | 191.8538 | 10.9933 | 9.6176 | 183.2409 | 9.9215 | 189.0306 | 0.28174 | 2.2243 | 0.12233 | 1.7415 | 0.28193 | 2.2403
LOCR | Louisa Creek | MK | LOCR_33kV_BUS 2 | 33 | 9.3478 | 534.2969 | 10.0697 | 191.8538 | 10.9933 | 9.6176 | 183.2409 | 9.9215 | 189.0306 | 0.28174 | 2.2243 | 0.12233 | 1.7415 | 0.28193 | 2.2403
LONG | Longreach | CA | LONG_22kV_BUS LH | 22 | 1.5276 | 58.2094 | 2.0506 | 26.0467 | 3.2309 | 2.0425 | 25.9426 | 2.1274 | 27.0213 | 2.1207 | 8.8971 | 0.15016 | 1.9454 | 2.0294 | 9.1403
LONG | Longreach | CA | LONG_22kV_BUS RH | 22 | 1.5276 | 58.2094 | 2.0506 | 26.0467 | 3.2309 | 2.0425 | 25.9426 | 2.1274 | 27.0213 | 2.1207 | 8.8971 | 0.15016 | 1.9454 | 2.0294 | 9.1403
LONG | Longreach | CA | LONG_66kV_BUS 1 | 66 | 0.64456 | 73.6833 | 0.39842 | 15.1819 | 0.29437 | 0.57536 | 21.9241 | 0.56602 | 21.5683 | 17.7347 | 62.5648 | 53.2846 | 175.7982 | 16.9133 | 64.7539
LUCI | Lucinda | NQ | LUCI_11kV_BUS | 11 | 2.1871 | 41.6693 | 2.3295 | 14.7944 | 2.5104 | 2.2107 | 14.0397 | 2.3248 | 14.7642 | 0.51865 | 3.1518 | 0.20141 | 2.5829 | 0.53274 | 3.1743
LUCI | Lucinda | NQ | LUCI_66kV_TEF T1 | 66 | 1.7874 | 204.3304 | 1.2929 | 49.2675 | 1.0428 | 1.5541 | 59.2202 | 1.6636 | 63.3901 | 11.4207 | 20.4813 | 18.0535 | 46.2311 | 11.9278 | 21.292
LYLA | Lyndley Lane | SW | LYLA_22kV_TEF T1 | 22 | 0.46228 | 17.6154 | 0.50427 | 6.4051 | 0.55363 | 0.46769 | 5.9405 | 0.50505 | 6.415 | 5.5985 | 29.7038 | 1.1401 | 22.8021 | 5.5991 | 29.7038
LYLA | Lyndley Lane | SW | LYLA_22kV_TEF T2 | 22 | 0.46228 | 17.6154 | 0.50427 | 6.4051 | 0.55363 | 0.46769 | 5.9405 | 0.50505 | 6.415 | 5.5985 | 29.7038 | 1.1401 | 22.8021 | 5.5991 | 29.7038
LYLA | Lyndley Lane | SW | LYLA_33kV_TEF T1 | 33 | 1.1338 | 64.8034 | 0.68586 | 13.0674 | 0.48677 | 0.94956 | 18.0916 | 1.07 | 20.3859 | 10.0315 | 15.5288 | 15.0782 | 53.6205 | 10.0327 | 15.5289
LYLA | Lyndley Lane | SW | LYLA_33kV_TEF T2 | 33 | 1.1338 | 64.8034 | 0.68586 | 13.0674 | 0.48677 | 0.94956 | 18.0916 | 1.07 | 20.3859 | 10.0315 | 15.5288 | 15.0782 | 53.6205 | 10.0327 | 15.5289
MACI | Maryborough City | WB | MACI_11kV_BUS 1 | 11 | 10.9973 | 209.5271 | 12.185 | 77.3853 | 13.7007 | 11.5636 | 73.4386 | 11.885 | 75.4796 | 0.0654 | 0.63192 | 0.02325 | 0.44753 | 0.06446 | 0.63384
MACI | Maryborough City | WB | MACI_11kV_BUS 2 | 11 | 10.9973 | 209.5271 | 12.185 | 77.3853 | 13.7007 | 11.5636 | 73.4386 | 11.885 | 75.4796 | 0.0654 | 0.63192 | 0.02325 | 0.44753 | 0.06446 | 0.63384
MACI | Maryborough City | WB | MACI_66kV_BUS MACI | 66 | 6.1562 | 703.7484 | 5.8316 | 222.2136 | 5.5857 | 5.9831 | 227.9868 | 6.0254 | 229.5997 | 1.5173 | 6.6381 | 1.6088 | 7.7214 | 1.4836 | 6.707
MACI | Maryborough City | WB | MACI_66kV_BUS MACI_TUAN | 66 | 6.1562 | 703.7484 | 5.8316 | 222.2136 | 5.5857 | 5.9831 | 227.9868 | 6.0254 | 229.5997 | 1.5173 | 6.6381 | 1.6088 | 7.7214 | 1.4836 | 6.707
MACI | Maryborough City | WB | MACI_66kV_BUS WALKERS | 66 | 6.1562 | 703.7484 | 5.8316 | 222.2136 | 5.5857 | 5.9831 | 227.9868 | 6.0254 | 229.5997 | 1.5173 | 6.6381 | 1.6088 | 7.7214 | 1.4836 | 6.707
MACK | Mackay T038 | MK | MACK_33kV_BUS A | 33 | 13.7358 | 785.1093 | 18.6859 | 356.014 | 29.5703 | 18.9838 | 361.6891 | 18.9529 | 361.1008 | 0.20616 | 1.5118 | 0.04202 | 0.29845 | 0.20537 | 1.5238
MACK | Mackay T038 | MK | MACK_33kV_BUS B | 33 | 13.7358 | 785.1093 | 18.6859 | 356.014 | 29.5703 | 18.9838 | 361.6891 | 18.9529 | 361.1008 | 0.20616 | 1.5118 | 0.04202 | 0.29845 | 0.20537 | 1.5238
MACK | Mackay T038 | MK | MACK_33kV_BUS C | 33 | 13.7358 | 785.1093 | 18.6859 | 356.014 | 29.5703 | 18.9838 | 361.6891 | 18.9529 | 361.1008 | 0.20616 | 1.5118 | 0.04202 | 0.29845 | 0.20537 | 1.5238
MACN | Macknade | NQ | MACN_11kV_BUS 1 | 11 | 8.608 | 164.0039 | 6.769 | 42.9889 | 7.2445 | 7.5028 | 47.6492 | 7.6697 | 48.709 | 0.09969 | 0.80542 | 0.1188 | 1.1879 | 0.14997 | 1.0809
MACN | Macknade | NQ | MACN_11kV_BUS 2 | 11 | 8.608 | 164.0039 | 6.769 | 42.9889 | 7.2445 | 7.5028 | 47.6492 | 7.6697 | 48.709 | 0.09969 | 0.80542 | 0.1188 | 1.1879 | 0.14997 | 1.0809
MACN | Macknade | NQ | MACN_66kV_TEF T1 | 66 | 2.549 | 291.3942 | 1.9642 | 74.8477 | 1.6745 | 2.2906 | 87.2839 | 2.3388 | 89.1184 | 6.027 | 15.2994 | 10.2541 | 28.3749 | 6.5643 | 16.1288
MACT | Mackay City | MK | MACT_33kV_BUS 1 | 33 | 12.8638 | 735.2672 | 17.1775 | 327.2749 | 26.0787 | 17.7445 | 338.0775 | 16.5167 | 314.6853 | 0.29462 | 1.6024 | 0.15613 | 0.36698 | 0.29383 | 1.6144
MACT | Mackay City | MK | MACT_11kV_BUS 1 | 11 | 13.9335 | 265.4682 | 15.4326 | 98.0101 | 17.3299 | 14.6711 | 93.1738 | 15.0264 | 95.4303 | 0.04047 | 0.49975 | 0.01246 | 0.35428 | 0.0393 | 0.50087
MACT | Mackay City | MK | MACT_11kV_BUS 2 | 11 | 13.9335 | 265.4682 | 15.4326 | 98.0101 | 17.3299 | 14.6711 | 93.1738 | 15.0264 | 95.4303 | 0.04047 | 0.49975 | 0.01246 | 0.35428 | 0.0393 | 0.50087
MACT | Mackay City | MK | MACT_33kV_BUS 2 | 33 | 14.9396 | 853.9122 | 19.8332 | 377.8727 | 29.6844 | 20.4689 | 389.9853 | 18.8568 | 359.2701 | 0.25208 | 1.38 | 0.14735 | 0.33447 | 0.24153 | 1.3902
MAFU | Max Fulton (TF1) | NQ | MAFU_11kV_BUS 1 | 11 | 21.5039 | 409.7052 | 23.7009 | 150.5211 | 26.3873 | 22.783 | 144.6918 | 22.866 | 145.2186 | 0.04496 | 0.32174 | 0.03058 | 0.23265 | 0.04443 | 0.3217
MAFU | Max Fulton (TF2) | NQ | MAFU_11kV_BUS 2 | 11 | 21.5039 | 409.7052 | 23.7009 | 150.5211 | 26.3873 | 22.783 | 144.6918 | 22.866 | 145.2186 | 0.04496 | 0.32174 | 0.03058 | 0.23265 | 0.04443 | 0.3217
MAFU | Max Fulton (TF1) | NQ | MAFU_66kV_TEF T1 | 66 | 11.2357 | 1284.4089 | 10.1363 | 386.2443 | 9.2143 | 10.6 | 403.9138 | 10.941 | 416.9087 | 0.99888 | 3.5944 | 1.0327 | 4.8474 | 0.97977 | 3.5928
MAFU | Max Fulton (TF2) | NQ | MAFU_66kV_TEF T2 | 66 | 11.5113 | 1315.9158 | 10.5577 | 402.3029 | 9.7292 | 10.9017 | 415.4088 | 11.2922 | 430.2925 | 0.95646 | 3.5134 | 0.91581 | 4.5491 | 0.93734 | 3.5118
MAKA | Mary Kathleen | NQ - MI | MAKA_11kV_TEF T1 | 11 | 0.27606 | 5.2597 | 0.28781 | 1.8278 | 0.30063 | 0.28046 | 1.7812 | 0.28431 | 1.8056 | 3.4613 | 25.0677 | 2.512 | 22.0658 | 3.4586 | 25.0724
MAKA | Mary Kathleen | NQ - MI | MAKA_66kV_TEF T1 | 66 | 0.36981 | 42.2753 | 0.31701 | 12.0797 | 0.27762 | 0.34467 | 13.1339 | 0.35313 | 13.456 | 34.177 | 108.0671 | 43.812 | 164.2006 | 34.0783 | 108.2383
MALC | Malchi | CA | MALC_11kV_BUS 1 | 11 | 8.8642 | 168.8851 | 10.2221 | 64.9191 | 12.0637 | 9.3945 | 59.6633 | 10.115 | 64.2389 | 0.15939 | 0.77184 | 0.03085 | 0.47588 | 0.15944 | 0.77253
MALC | Malchi | CA | MALC_11kV_BUS 2 | 11 | 8.8642 | 168.8851 | 10.2221 | 64.9191 | 12.0637 | 9.3945 | 59.6633 | 10.115 | 64.2389 | 0.15939 | 0.77184 | 0.03085 | 0.47588 | 0.15944 | 0.77253
MALC | Malchi | CA | MALC_66kV_TEF T1 | 66 | 3.6084 | 412.5 | 2.5496 | 97.1514 | 1.9707 | 3.1791 | 121.142 | 3.3666 | 128.2849 | 4.6277 | 10.6546 | 7.4045 | 25.0882 | 4.6295 | 10.6794
MALC | Malchi | CA | MALC_66kV_TEF T2 | 66 | 3.6084 | 412.5 | 2.5496 | 97.1514 | 1.9707 | 3.1791 | 121.142 | 3.3666 | 128.2849 | 4.6277 | 10.6546 | 7.4045 | 25.0882 | 4.6295 | 10.6794
MARE | Mareeba (TF1) | FN | MARE_22kV_BUS 1 | 22 | 5.9699 | 227.4824 | 7.0859 | 90.0031 | 8.7587 | 6.6169 | 84.0461 | 6.9219 | 87.9203 | 0.31723 | 2.3188 | 0.05212 | 1.2268 | 0.30907 | 2.3307
MARE | Mareeba (TF2) | FN | MARE_22kV_BUS 2 | 22 | 5.9699 | 227.4824 | 7.0859 | 90.0031 | 8.7587 | 6.6169 | 84.0461 | 6.9219 | 87.9203 | 0.31723 | 2.3188 | 0.05212 | 1.2268 | 0.30907 | 2.3307
MARE | Mareeba (TF3) | FN | MARE_22kV_BUS 3 | 22 | 5.9699 | 227.4824 | 7.0859 | 90.0031 | 8.7587 | 6.6169 | 84.0461 | 6.9219 | 87.9203 | 0.31723 | 2.3188 | 0.05212 | 1.2268 | 0.30907 | 2.3307
MARE | Mareeba (TF1) | FN | MARE_66kV_BUS 1 | 66 | 4.2041 | 480.5914 | 4.2047 | 160.2204 | 4.2421 | 4.2043 | 160.2047 | 4.2049 | 160.2273 | 2.3861 | 9.6805 | 2.2693 | 9.615 | 2.3126 | 9.7878
MARE | Mareeba (TF2) | FN | MARE_66kV_BUS 2 | 66 | 4.2041 | 480.5914 | 4.2047 | 160.2204 | 4.2421 | 4.2043 | 160.2047 | 4.2049 | 160.2273 | 2.3861 | 9.6805 | 2.2693 | 9.615 | 2.3126 | 9.7878
MARE | Mareeba (TF3) | FN | MARE_66kV_BUS 3 | 66 | 4.2041 | 480.5914 | 4.2047 | 160.2204 | 4.2421 | 4.2043 | 160.2047 | 4.2049 | 160.2273 | 2.3861 | 9.6805 | 2.2693 | 9.615 | 2.3126 | 9.7878
MARY | Maryborough T059 | WB | MARY_132kV_BUS 1 | 132 | 5.4264 | 1240.6519 | 5.9337 | 452.2055 | 6.6169 | 5.5066 | 419.6563 | 5.9537 | 453.7337 | 3.3949 | 15.0724 | 0.84622 | 11.362 | 3.317 | 15.2743
MARY | Maryborough T059 | WB | MARY_132kV_BUS 2 | 132 | 5.4264 | 1240.6519 | 5.9337 | 452.2055 | 6.6169 | 5.5066 | 419.6563 | 5.9537 | 453.7337 | 3.3949 | 15.0724 | 0.84622 | 11.362 | 3.317 | 15.2743
MARY | Maryborough T059 | WB | MARY_132kV_BUS 3 | 132 | 5.4264 | 1240.6519 | 5.9337 | 452.2055 | 6.6169 | 5.5066 | 419.6563 | 5.9537 | 453.7337 | 3.3949 | 15.0724 | 0.84622 | 11.362 | 3.317 | 15.2743
MARY | Maryborough T059 | WB | MARY_66kV_BUS 1 | 66 | 8.1053 | 926.5579 | 9.9703 | 379.9197 | 13.1411 | 9.3488 | 356.2364 | 9.8476 | 375.2422 | 0.93616 | 5.0864 | 0.13286 | 2.2164 | 0.90247 | 5.1554
MARY | Maryborough T059 | WB | MARY_66kV_BUS 2 | 66 | 8.1053 | 926.5579 | 9.9703 | 379.9197 | 13.1411 | 9.3488 | 356.2364 | 9.8476 | 375.2422 | 0.93616 | 5.0864 | 0.13286 | 2.2164 | 0.90247 | 5.1554
MARY | Maryborough T059 | WB | MARY_66kV_BUS 3 | 66 | 8.1053 | 926.5579 | 9.9703 | 379.9197 | 13.1411 | 9.3488 | 356.2364 | 9.8476 | 375.2422 | 0.93616 | 5.0864 | 0.13286 | 2.2164 | 0.90247 | 5.1554
MASO | Marian South | MK | MASO_11kV_BUS 1 | 11 | 10.732 | 204.4716 | 8.2158 | 52.1773 | 7.1287 | 9.4817 | 60.2169 | 9.8595 | 62.6163 | 0.10884 | 0.64178 | 0.05967 | 1.1931 | 0.08758 | 0.70318
MASO | Marian South | MK | MASO_66kV_TEF T1 | 66 | 4.2102 | 481.2914 | 3.078 | 117.2884 | 2.449 | 3.7823 | 144.124 | 3.875 | 147.6567 | 3.3368 | 9.3799 | 5.9185 | 19.9717 | 3.3403 | 9.5116
MCCR | McKinley Creek | MK | MCCR_66kV_TEF T1 | 66 | 3.0062 | 343.651 | 2.2178 | 84.5091 | 1.7615 | 2.7499 | 104.7848 | 2.7404 | 104.4228 | 5.1428 | 12.9602 | 10.7209 | 26.6956 | 5.1211 | 13.0176
MCCR | McKinley Creek (TF1) | MK | MCCR_11kV_BUS 1 | 11 | 5.3349 | 101.6443 | 5.8961 | 37.4451 | 6.5916 | 5.52 | 35.0566 | 5.824 | 36.9874 | 0.18452 | 1.2964 | 0.04166 | 0.93641 | 0.18391 | 1.298
MCCR | McKinley Creek (TF2) | MK | MCCR_11kV_BUS 2 | 11 | 5.3349 | 101.6443 | 5.8961 | 37.4451 | 6.5916 | 5.52 | 35.0566 | 5.824 | 36.9874 | 0.18452 | 1.2964 | 0.04166 | 0.93641 | 0.18391 | 1.298
MCCR | McKinley Creek | MK | MCCR_11kV_BUS 3 | 11 | 5.3349 | 101.6443 | 5.8961 | 37.4451 | 6.5916 | 5.52 | 35.0566 | 5.824 | 36.9874 | 0.18452 | 1.2964 | 0.04166 | 0.93641 | 0.18391 | 1.298
MEAD | Meadowvale | WB | MEAD_11kV_BUS 1 | 11 | 7.7129 | 146.95 | 8.954 | 56.8652 | 10.6908 | 8.2538 | 52.419 | 8.8388 | 56.134 | 0.17556 | 0.88864 | 0.03362 | 0.5291 | 0.17478 | 0.89135
MEAD | Meadowvale | WB | MEAD_11kV_BUS 2 | 11 | 7.7129 | 146.95 | 8.954 | 56.8652 | 10.6908 | 8.2538 | 52.419 | 8.8388 | 56.134 | 0.17556 | 0.88864 | 0.03362 | 0.5291 | 0.17478 | 0.89135
MEAD | Meadowvale | WB | MEAD_66kV_BUS 1 | 66 | 3.0123 | 344.3562 | 2.128 | 81.0865 | 1.6501 | 2.662 | 101.4346 | 2.797 | 106.5817 | 5.1099 | 12.9436 | 8.232 | 30.167 | 5.0816 | 13.0412
MEAN | Meandarra | SW | MEAN_22kV_BUS | 22 | 0.37428 | 14.2619 | 0.47025 | 5.973 | 0.62855 | 0.41857 | 5.3165 | 0.48214 | 6.124 | 13.3481 | 34.8636 | 0.75376 | 15.0751 | 13.3479 | 34.8666
MEAN | Meandarra | SW | MEAN_33kV_BUS | 33 | 0.39712 | 22.6982 | 0.22839 | 4.3515 | 0.15875 | 0.33241 | 6.3333 | 0.37234 | 7.094 | 28.3374 | 44.524 | 45.5089 | 166.5727 | 28.3368 | 44.5309
MELR | Melrose | WB | MELR_11kV_BUS 1 | 11 | 2.9868 | 56.907 | 3.363 | 21.3578 | 3.846 | 3.1504 | 20.0079 | 3.2941 | 20.9205 | 0.48396 | 2.2886 | 0.19623 | 1.5453 | 0.48275 | 2.2893
MELR | Melrose | WB | MELR_11kV_BUS 2 | 11 | 2.9868 | 56.907 | 3.363 | 21.3578 | 3.846 | 3.1504 | 20.0079 | 3.2941 | 20.9205 | 0.48396 | 2.2886 | 0.19623 | 1.5453 | 0.48275 | 2.2893
MELR | Melrose | WB | MELR_66kV_BUS | 66 | 1.461 | 167.0184 | 0.80991 | 30.8619 | 0.55881 | 1.2568 | 47.8884 | 1.3334 | 50.8082 | 10.3584 | 26.7575 | 20.1481 | 96.2748 | 10.3149 | 26.7838
MEMO | Memooloo T236 | CA | MEMO_132kV_BUS 1 | 132 | 1.9355 | 442.5096 | 1.7581 | 133.9844 | 1.609 | 1.8082 | 137.8065 | 1.9087 | 145.4603 | 9.6835 | 42.217 | 7.3412 | 56.0937 | 9.7035 | 42.221
MEMO | Memooloo T236 | CA | MEMO_132kV_BUS 2 | 132 | 1.9355 | 442.5096 | 1.7581 | 133.9844 | 1.609 | 1.8082 | 137.8065 | 1.9087 | 145.4603 | 9.6835 | 42.217 | 7.3412 | 56.0937 | 9.7035 | 42.221
MERI | Merinda | NQ | MERI_11kV_BUS 1 | 11 | 6.7174 | 127.9828 | 7.4618 | 47.3889 | 8.3866 | 7.0749 | 44.9316 | 7.2672 | 46.1527 | 0.10188 | 1.035 | 0.03658 | 0.7288 | 0.10228 | 1.0346
MERI | Merinda | NQ | MERI_11kV_BUS 2 | 11 | 6.7174 | 127.9828 | 7.4618 | 47.3889 | 8.3866 | 7.0749 | 44.9316 | 7.2672 | 46.1527 | 0.10188 | 1.035 | 0.03658 | 0.7288 | 0.10228 | 1.0346
MERI | Merinda | NQ | MERI_11kV_BUS 3 | 11 | 6.7174 | 127.9828 | 7.4618 | 47.3889 | 8.3866 | 7.0749 | 44.9316 | 7.2672 | 46.1527 | 0.10188 | 1.035 | 0.03658 | 0.7288 | 0.10228 | 1.0346
MERI | Merinda | NQ | MERI_66kV_BUS 1 | 66 | 3.7592 | 429.7388 | 4.9452 | 188.4384 | 7.2095 | 4.7585 | 181.3238 | 4.9548 | 188.8025 | 2.3505 | 10.8995 | 0.32026 | 3.1405 | 2.3647 | 10.8844
MERI | Merinda | NQ | MERI_66kV_BUS 2 | 66 | 3.7592 | 429.7388 | 4.9452 | 188.4384 | 7.2095 | 4.7585 | 181.3238 | 4.9548 | 188.8025 | 2.3505 | 10.8995 | 0.32026 | 3.1405 | 2.3647 | 10.8844
MERN | Meringandan (TF1) | SW | MERN_11kV_BUS 1 | 11 | 3.1913 | 60.8034 | 3.6286 | 23.045 | 4.2033 | 3.4099 | 21.6557 | 3.5332 | 22.4389 | 0.25449 | 2.1745 | 0.06992 | 1.3983 | 0.25261 | 2.1748
MERN | Meringandan (TF2) | SW | MERN_11kV_BUS 2 | 11 | 3.1913 | 60.8034 | 3.6286 | 23.045 | 4.2033 | 3.4099 | 21.6557 | 3.5332 | 22.4389 | 0.25449 | 2.1745 | 0.06992 | 1.3983 | 0.25261 | 2.1748
MERN | Meringandan (TF3) | SW | MERN_11kV_BUS 3 | 11 | 3.4546 | 65.8186 | 3.8496 | 24.4485 | 4.3448 | 3.6357 | 23.0897 | 3.7582 | 23.8676 | 0.23445 | 2.0089 | 0.07002 | 1.4003 | 0.22187 | 2.0102
MERN | Meringandan (TF4) | SW | MERN_11kV_BUS 4 | 11 | 3.4546 | 65.8186 | 3.8496 | 24.4485 | 4.3448 | 3.6357 | 23.0897 | 3.7582 | 23.8676 | 0.23445 | 2.0089 | 0.07002 | 1.4003 | 0.22187 | 2.0102
MERN | Meringandan (Highfields) | SW | MERN_33kV_BUS 1 | 33 | 2.9192 | 166.8524 | 0.8836 | 16.8348 | 0.48907 | 2.7296 | 52.0064 | 2.335 | 44.4872 | 1.6611 | 6.9857 | 58.4193 | 21.4483 | 1.6443 | 6.9882
MICB | Mica Creek B Yard | NQ - MI | MICB_132kV_BUS MAIN B | 132 | 7.9766 | 1823.6861 | 10.312 | 785.8841 | 15.9594 | 10.5642 | 805.097 | 10.4515 | 796.5087 | 0.65605 | 10.4892 | 0.15319 | 2.7014 | 0.26125 | 11.1742
MICC | Mica Creek C Yard (TF2) | NQ - MI | GENERATOR 1 | 132 | 7.9268 | 1812.3028 | 10.1814 | 775.928 | 15.5462 | 10.3933 | 792.0787 | 10.2504 | 781.1874 | 0.6666 | 10.5547 | 0.18856 | 2.8812 | 0.2718 | 11.2396
MICC | Mica Creek C Yard (TF1) | NQ - MI | GENERATOR 2 | 132 | 7.9223 | 1811.2888 | 10.1699 | 775.0522 | 15.5104 | 10.3785 | 790.9468 | 10.2331 | 779.8648 | 0.66755 | 10.5606 | 0.19167 | 2.8972 | 0.27274 | 11.2455
MICC | Mica Creek C Yard | NQ - MI | MICC_220kV_BUS 1 | 220 | 2.574 | 980.8399 | 3.4547 | 438.8107 | 5.5342 | 3.5503 | 450.9524 | 3.543 | 450.0179 | 2.4985 | 54.2225 | 0.35525 | 10.9056 | 1.4018 | 56.1252
MICO | Miles-Condamine | SW | MICO_22kV_TEF T1 | 22 | 0.37112 | 14.1416 | 0.39587 | 5.0283 | 0.42397 | 0.37696 | 4.788 | 0.39289 | 4.9904 | 4.6069 | 37.3662 | 1.5301 | 30.6029 | 4.6067 | 37.3693
MICO | Miles-Condamine | SW | MICO_22kV_TEF T2 | 22 | 0.37112 | 14.1416 | 0.39587 | 5.0283 | 0.42397 | 0.37696 | 4.788 | 0.39289 | 4.9904 | 4.6069 | 37.3662 | 1.5301 | 30.6029 | 4.6067 | 37.3693
MICO | Miles-Condamine | SW | MICO_33kV_BUS 1 | 33 | 1.2536 | 71.6553 | 0.80321 | 15.3032 | 0.58934 | 1.0859 | 20.69 | 1.1624 | 22.1462 | 6.9228 | 15.2174 | 11.8996 | 43.4843 | 6.9222 | 15.2243
MIDD | Middlemount | CA | MIDD_22kV_BUS 1 | 22 | 2.4664 | 93.9813 | 2.9048 | 36.8958 | 3.5395 | 2.6534 | 33.7034 | 2.8868 | 36.6671 | 1.429 | 5.4818 | 0.26644 | 3.103 | 1.4035 | 5.5083
MIDD | Middlemount | CA | MIDD_22kV_BUS 3 | 22 | 2.4664 | 93.9813 | 2.9048 | 36.8958 | 3.5395 | 2.6534 | 33.7034 | 2.8868 | 36.6671 | 1.429 | 5.4818 | 0.26644 | 3.103 | 1.4035 | 5.5083
MIDD | Middlemount | CA | MIDD_66kV_BUS 1 | 66 | 1.759 | 201.0848 | 0.9521 | 36.28 | 0.65283 | 1.5078 | 57.4553 | 1.6008 | 60.9972 | 10.4629 | 21.409 | 23.0106 | 81.5746 | 10.2332 | 21.6477
MIDD | Middlemount | CA | MIDD_66kV_BUS 2 | 66 | 1.759 | 201.0848 | 0.9521 | 36.28 | 0.65283 | 1.5078 | 57.4553 | 1.6008 | 60.9972 | 10.4629 | 21.409 | 23.0106 | 81.5746 | 10.2332 | 21.6477
MIDD | Middlemount | CA | MIDD_66kV_BUS 3 | 66 | 1.759 | 201.0848 | 0.9521 | 36.28 | 0.65283 | 1.5078 | 57.4553 | 1.6008 | 60.9972 | 10.4629 | 21.409 | 23.0106 | 81.5746 | 10.2332 | 21.6477
MILC | Millchester T095 (TF1) | NQ | MILC_11kV_BUS 1 | 11 | 5.0326 | 95.8845 | 5.4745 | 34.7676 | 6.0101 | 5.1755 | 32.8691 | 5.4059 | 34.332 | 0.187 | 1.3755 | 0.05935 | 1.0501 | 0.18554 | 1.3783
MILC | Millchester T095 (TF2) | NQ | MILC_11kV_BUS 2 | 11 | 5.0326 | 95.8845 | 5.4745 | 34.7676 | 6.0101 | 5.1755 | 32.8691 | 5.4059 | 34.332 | 0.187 | 1.3755 | 0.05935 | 1.0501 | 0.18554 | 1.3783
MILC | Millchester T095 | NQ | MILC_132kV_TEF T1 | 132 | 2.2466 | 513.6445 | 2.1157 | 161.2374 | 1.9815 | 1.9793 | 150.8437 | 2.367 | 180.3861 | 14.6976 | 34.2981 | 4.1714 | 45.3168 | 14.6518 | 34.4318
MILC | Millchester T095 | NQ | MILC_132kV_TEF T2 | 132 | 2.2466 | 513.6445 | 2.1157 | 161.2374 | 1.9815 | 1.9793 | 150.8437 | 2.367 | 180.3861 | 14.6976 | 34.2981 | 4.1714 | 45.3168 | 14.6518 | 34.4318
MILC | Millchester T095 | NQ | MILC_66kV_BUS 1 | 66 | 3.3309 | 380.7718 | 4.0533 | 154.4523 | 5.1835 | 3.5946 | 136.9714 | 4.1371 | 157.6447 | 4.5953 | 11.7149 | 0.46111 | 5.9692 | 4.5428 | 11.8166
MILC | Millchester T095 | NQ | MILC_66kV_BUS 2 | 66 | 3.3309 | 380.7718 | 4.0533 | 154.4523 | 5.1835 | 3.5946 | 136.9714 | 4.1371 | 157.6447 | 4.5953 | 11.7149 | 0.46111 | 5.9692 | 4.5428 | 11.8166
MILE | Miles | SW | MILE_11kV_BUS 1 | 11 | 3.6214 | 68.9968 | 4.2304 | 26.8664 | 5.0819 | 3.913 | 24.8507 | 4.1557 | 26.3921 | 0.35512 | 1.8962 | 0.07664 | 1.0984 | 0.35497 | 1.8968
MILE | Miles | SW | MILE_11kV_BUS 2 | 11 | 3.6214 | 68.9968 | 4.2304 | 26.8664 | 5.0819 | 3.913 | 24.8507 | 4.1557 | 26.3921 | 0.35512 | 1.8962 | 0.07664 | 1.0984 | 0.35497 | 1.8968
MILE | Miles | SW | MILE_33kV_BUS 1 | 33 | 2.7561 | 157.5322 | 2.1871 | 41.6689 | 1.8134 | 2.5251 | 48.1093 | 2.58 | 49.1556 | 2.5064 | 7.1795 | 3.9234 | 12.9606 | 2.505 | 7.1853
MILE | Miles | SW | MILE_33kV_BUS 2 | 33 | 2.7561 | 157.5322 | 2.1871 | 41.6689 | 1.8134 | 2.5251 | 48.1093 | 2.58 | 49.1556 | 2.5064 | 7.1795 | 3.9234 | 12.9606 | 2.505 | 7.1853
MILE | Miles | SW | MILE_33kV_BUS 3 | 33 | 2.7561 | 157.5322 | 2.1871 | 41.6689 | 1.8134 | 2.5251 | 48.1093 | 2.58 | 49.1556 | 2.5064 | 7.1795 | 3.9234 | 12.9606 | 2.505 | 7.1853
MILE | Miles | SW | MILE_33kV_BUS 5 | 33 | 2.7561 | 157.5322 | 2.1871 | 41.6689 | 1.8134 | 2.5251 | 48.1093 | 2.58 | 49.1556 | 2.5064 | 7.1795 | 3.9234 | 12.9606 | 2.505 | 7.1853
MILL | Millaroo | NQ | MILL_11kV_BUS 1 | 11 | 2.943 | 56.0718 | 3.2222 | 20.4639 | 3.5467 | 2.9363 | 18.6477 | 3.2652 | 20.737 | 0.56093 | 2.3065 | 0.0889 | 1.7779 | 0.56025 | 2.3062
MILL | Millaroo | NQ | MILL_11kV_BUS 2 | 11 | 2.943 | 56.0718 | 3.2222 | 20.4639 | 3.5467 | 2.9363 | 18.6477 | 3.2652 | 20.737 | 0.56093 | 2.3065 | 0.0889 | 1.7779 | 0.56025 | 2.3062
MILL | Millaroo | NQ | MILL_66kV_BUS 1 | 66 | 1.6429 | 187.8128 | 1.2459 | 47.4748 | 0.99778 | 1.4318 | 54.5573 | 1.5812 | 60.2498 | 16.9931 | 19.0298 | 25.4682 | 43.5304 | 16.9688 | 19.017
MILL | Millaroo | NQ | MILL_66kV_BUS 2 | 66 | 1.6429 | 187.8128 | 1.2459 | 47.4748 | 0.99778 | 1.4318 | 54.5573 | 1.5812 | 60.2498 | 16.9931 | 19.0298 | 25.4682 | 43.5304 | 16.9688 | 19.017
MILM | Millmerran Town | SW | MILM_11kV_BUS BRINGALILY | 11 | 1.6806 | 32.0205 | 2.1745 | 13.8102 | 3.039 | 1.9581 | 12.4353 | 2.2426 | 14.2426 | 1.5653 | 3.8513 | 0.07056 | 1.4112 | 1.5498 | 3.8336
MILM | Millmerran Town | SW | MILM_11kV_BUS MILMERRAN TOWN | 11 | 1.6806 | 32.0205 | 2.1745 | 13.8102 | 3.039 | 1.9581 | 12.4353 | 2.2426 | 14.2426 | 1.5653 | 3.8513 | 0.07056 | 1.4112 | 1.5498 | 3.8336
MILM | Millmerran Town | SW | MILM_11kV_BUS ROCKY STREET | 11 | 1.6806 | 32.0205 | 2.1745 | 13.8102 | 3.039 | 1.9581 | 12.4353 | 2.2426 | 14.2426 | 1.5653 | 3.8513 | 0.07056 | 1.4112 | 1.5498 | 3.8336
MILM | Millmerran Town | SW | MILM_33kV_BUS | 33 | 0.81388 | 46.5197 | 0.31608 | 6.0222 | 0.19189 | 0.67409 | 12.8432 | 0.75162 | 14.3202 | 13.4524 | 21.9606 | 14.3154 | 150.8644 | 13.3133 | 21.8018
MILN | Millennium Substation | MK | MILN_11kV_BUS 1 | 11 | 5.5088 | 104.9568 | 0.0097 | 0.06161 | 0.00485 | 4.7725 | 30.3094 | 4.7677 | 30.2787 | 0.10755 | 1.2636 | 2160.0511 | 1.0341 | 0.10744 | 1.2639
MILN | Millennium Substation | MK | MILN_66kV_BUS | 66 | 4.9293 | 563.4905 | 4.1526 | 158.2351 | 3.5909 | 4.5731 | 174.2568 | 4.6842 | 178.4923 | 2.0106 | 8.2624 | 2.5517 | 13.0224 | 2.0065 | 8.2759
MING | Mingela | NQ | MING_11kV_TEF T1 | 11 | 1.1329 | 21.5842 | 1.2185 | 7.7383 | 1.3176 | 1.1566 | 7.3454 | 1.2063 | 7.6611 | 0.45808 | 6.1495 | 0 | 4.8756 | 0.4572 | 6.1508
MING | Mingela | NQ | MING_66kV_TEF T1 | 66 | 1.6703 | 190.9433 | 1.2203 | 46.4979 | 0.94881 | 1.3963 | 53.2076 | 1.6383 | 62.427 | 16.4908 | 18.9151 | 20.2503 | 50.38 | 16.459 | 18.9603
MIRA | Mirani (Reg 1) | MK | MIRA_11kV_TEF R1 | 11 | 3.4296 | 65.3426 | 3.6642 | 23.2708 | 3.9373 | 3.4905 | 22.1674 | 3.6326 | 23.0699 | 0.29565 | 2.0154 | 0.12364 | 1.641 | 0.29546 | 2.0184
MIRA | Mirani (Reg 2) | MK | MIRA_11kV_TEF R2 | 11 | 3.4296 | 65.3426 | 3.6642 | 23.2708 | 3.9373 | 3.4905 | 22.1674 | 3.6326 | 23.0699 | 0.29565 | 2.0154 | 0.12364 | 1.641 | 0.29546 | 2.0184
MIRA | Mirani (Unregulated) | MK | MIRA_1T | 11 | 3.7655 | 71.7428 | 4.0488 | 25.7135 | 4.3827 | 3.8349 | 24.3551 | 4.0182 | 25.5188 | 0.24524 | 1.839 | 0.07323 | 1.4646 | 0.24505 | 1.8419
MIRA | Mirani | MK | MIRA_66kV_TEF T1 | 66 | 2.8262 | 323.0743 | 1.9228 | 73.2702 | 1.4604 | 2.4615 | 93.7952 | 2.6317 | 100.2823 | 6.1922 | 13.4769 | 9.9006 | 34.4241 | 6.1856 | 13.584
MITC | Mitchell | SW | MITC_11kV_BUS 3 | 11 | 0.7777 | 14.8172 | 1.0592 | 6.7269 | 1.6465 | 0.97796 | 6.2109 | 1.1429 | 7.2584 | 5.1088 | 7.3888 | 0.19347 | 2.0465 | 5.1071 | 7.392
MITC | Mitchell | SW | MITC_33kV_BUS 1 | 33 | 0.33287 | 19.0259 | 0.2403 | 4.5783 | 0.18292 | 0.26703 | 5.0876 | 0.33408 | 6.3651 | 44.2382 | 44.8028 | 42.6596 | 136.7918 | 44.2222 | 44.8319
MIVA | Miriam Vale | CA | MIVA_22kV_TEF T5 | 22 | 1.3599 | 51.8188 | 1.616 | 20.5265 | 1.9761 | 1.41 | 17.9091 | 1.6547 | 21.018 | 3.7888 | 9.5504 | 0.3761 | 5.5852 | 3.7889 | 9.5526
MIVA | Miriam Vale | CA | MIVA_66kV_TEF T5 | 66 | 0.89025 | 101.7695 | 0.57822 | 22.033 | 0.42222 | 0.73745 | 28.1008 | 0.85662 | 32.6417 | 30.7139 | 35.6869 | 44.5931 | 118.4917 | 30.7147 | 35.7067
MIVA | Miriam Vale | CA | MIVA_tr_line_22276 | 66 | 0.89025 | 101.7695 | 0.57822 | 22.033 | 0.42222 | 0.73745 | 28.1008 | 0.85662 | 32.6417 | 30.7139 | 35.6869 | 44.5931 | 118.4917 | 30.7147 | 35.7067
MOBA | Mt Bassett (TF1) | MK | MOBA_11kV_BUS 1 | 11 | 8.8309 | 168.2504 | 10.1031 | 64.1636 | 11.8148 | 9.3819 | 59.5828 | 9.932 | 63.0769 | 0.12329 | 0.78142 | 0.02462 | 0.49243 | 0.1232 | 0.78276
MOBA | Mt Bassett (TF2) | MK | MOBA_11kV_BUS 2 | 11 | 8.8309 | 168.2504 | 10.1031 | 64.1636 | 11.8148 | 9.3819 | 59.5828 | 9.932 | 63.0769 | 0.12329 | 0.78142 | 0.02462 | 0.49243 | 0.1232 | 0.78276
MOBA | Mt Bassett | MK | MOBA_11kV_BUS 3 | 11 | 8.8309 | 168.2504 | 10.1031 | 64.1636 | 11.8148 | 9.3819 | 59.5828 | 9.932 | 63.0769 | 0.12329 | 0.78142 | 0.02462 | 0.49243 | 0.1232 | 0.78276
MOBA | Mt Bassett | MK | MOBA_11kV_BUS 4 | 11 | 8.8309 | 168.2504 | 10.1031 | 64.1636 | 11.8148 | 9.3819 | 59.5828 | 9.932 | 63.0769 | 0.12329 | 0.78142 | 0.02462 | 0.49243 | 0.1232 | 0.78276
MOBA | Mt Bassett | MK | MOBA_11kV_BUS 5 | 11 | 8.8309 | 168.2504 | 10.1031 | 64.1636 | 11.8148 | 9.3819 | 59.5828 | 9.932 | 63.0769 | 0.12329 | 0.78142 | 0.02462 | 0.49243 | 0.1232 | 0.78276
MOBA | Mt Bassett | MK | MOBA_33kV_BUS 1 | 33 | 7.6256 | 435.8609 | 6.2666 | 119.3949 | 5.3355 | 7.0231 | 133.8072 | 7.2018 | 137.213 | 0.88798 | 2.601 | 1.2521 | 4.3516 | 0.88719 | 2.613
MOBA | Mt Bassett | MK | MOBA_33kV_BUS 2 | 33 | 7.6256 | 435.8609 | 6.2666 | 119.3949 | 5.3355 | 7.0231 | 133.8072 | 7.2018 | 137.213 | 0.88798 | 2.601 | 1.2521 | 4.3516 | 0.88719 | 2.613
MOBA | Mt Bassett | MK | MOBA_33kV_BUS 3 | 33 | 7.6256 | 435.8609 | 6.2666 | 119.3949 | 5.3355 | 7.0231 | 133.8072 | 7.2018 | 137.213 | 0.88798 | 2.601 | 1.2521 | 4.3516 | 0.88719 | 2.613
MODA | Monduran Dam | WB | MODA_11kV_BUS 1 | 11 | 2.3895 | 45.5252 | 2.6367 | 16.7454 | 2.932 | 2.3913 | 15.1869 | 2.6723 | 16.9712 | 0.57668 | 2.8664 | 0 | 2.13 | 0.57599 | 2.8686
MODA | Monduran Dam | WB | MODA_11kV_BUS 2 | 11 | 2.3895 | 45.5252 | 2.6367 | 16.7454 | 2.932 | 2.3913 | 15.1869 | 2.6723 | 16.9712 | 0.57668 | 2.8664 | 0 | 2.13 | 0.57599 | 2.8686
MODA | Monduran Dam | WB | MODA_3.3kV_BUS | 3.3 | 9.9077 | 56.6298 | 11.249 | 21.4322 | 12.9504 | 10.0022 | 19.0567 | 11.4452 | 21.806 | 0.05165 | 0.20515 | 0 | 0.13887 | 0.05158 | 0.20534
MODA | Monduran Dam | WB | MODA_66kV_BUS | 66 | 1.2471 | 142.5664 | 0.84818 | 32.3198 | 0.63589 | 1.0439 | 39.7798 | 1.2012 | 45.7722 | 20.6618 | 26.5117 | 28.213 | 77.8621 | 20.6368 | 26.5891
MOFO | Mt Fox | NQ | MOFO_33kV_TEF T1 | 33 | 0.17913 | 10.2384 | 0.18401 | 3.5058 | 0.18924 | 0.17956 | 3.4211 | 0.18378 | 3.5015 | 10.6958 | 116.5107 | 5.4868 | 107.5408 | 10.6769 | 116.5793
MOFO | Mt Fox | NQ | MOFO_66kV_TEF T1 | 66 | 1.0102 | 115.4854 | 0.68435 | 26.0773 | 0.51733 | 0.87327 | 33.2762 | 0.94666 | 36.0726 | 20.8362 | 35.8797 | 34.0211 | 95.4314 | 20.7604 | 36.1541
MOGA | Mt Garnet | FN | MOGA_22kV_BUS 1 | 22 | 1.3312 | 50.7267 | 1.6919 | 21.4895 | 2.314 | 1.5421 | 19.5878 | 1.7195 | 21.8408 | 3.8171 | 9.7767 | 0.44582 | 3.8584 | 3.8064 | 9.7889
MOGA | Mt Garnet | FN | MOGA_22kV_BUS 2 | 22 | 1.3312 | 50.7267 | 1.6919 | 21.4895 | 2.314 | 1.5421 | 19.5878 | 1.7195 | 21.8408 | 3.8171 | 9.7767 | 0.44582 | 3.8584 | 3.8064 | 9.7889
MOGA | Mt Garnet | FN | MOGA_66kV_BUS | 66 | 0.68377 | 78.1653 | 0.42292 | 16.1153 | 0.3044 | 0.58119 | 22.1462 | 0.63988 | 24.3826 | 30.3417 | 53.2652 | 48.9699 | 169.7726 | 30.2449 | 53.3749
MOLE | Mt Leyshon | NQ | MOLE_11kV_TEF T1 | 11 | 4.0102 | 76.4037 | 4.5837 | 29.1101 | 5.3431 | 4.1716 | 26.4931 | 4.58 | 29.0869 | 0.34645 | 1.7073 | 0.02853 | 1.0979 | 0.34499 | 1.7101
MOLE | Mt Leyshon | NQ | MOLE_66kV_TEF T1 | 66 | 1.694 | 193.6511 | 1.3429 | 51.1707 | 1.1076 | 1.4717 | 56.08 | 1.6564 | 63.1164 | 11.4451 | 21.9374 | 11.0112 | 43.3311 | 11.3927 | 22.0391
MOMG | Mt Morgan | CA | MOMG_11kV_BUS LH | 11 | 6.08 | 115.8405 | 6.8974 | 43.8045 | 7.9464 | 6.2381 | 39.6172 | 6.9349 | 44.0425 | 0.32969 | 1.1007 | 0.07258 | 0.74702 | 0.32974 | 1.1014
MOMG | Mt Morgan | CA | MOMG_11kV_BUS RH | 11 | 6.08 | 115.8405 | 6.8974 | 43.8045 | 7.9464 | 6.2381 | 39.6172 | 6.9349 | 44.0425 | 0.32969 | 1.1007 | 0.07258 | 0.74702 | 0.32974 | 1.1014
MOMG | Mt Morgan | CA | MOMG_66kV_TEF T1 | 66 | 2.6629 | 304.4136 | 1.8584 | 70.8142 | 1.4182 | 2.27 | 86.4988 | 2.5453 | 96.9906 | 9.2552 | 12.7323 | 13.6067 | 34.069 | 9.2567 | 12.7556
MOMG | Mt Morgan | CA | MOMG_66kV_TEF T2 | 66 | 2.6629 | 304.4136 | 1.8584 | 70.8142 | 1.4182 | 2.27 | 86.4988 | 2.5453 | 96.9906 | 9.2552 | 12.7323 | 13.6067 | 34.069 | 9.2567 | 12.7556
MOMO | Mt Molloy (TF1) | FN | MOMO_22kV_BUS | 22 | 2.5583 | 97.483 | 2.975 | 37.7873 | 3.5513 | 2.7 | 34.2948 | 2.9706 | 37.7319 | 1.3274 | 5.2977 | 0.199 | 3.1917 | 1.3192 | 5.3096
MOMO | Mt Molloy (TF2) | FN | MOMO_22kV_BUS GMS 2 | 22 | 0.57734 | 21.9996 | 0.59558 | 7.5648 | 0.61519 | 0.58059 | 7.3745 | 0.59329 | 7.5358 | 3.2575 | 23.9802 | 2.1291 | 21.8742 | 3.2493 | 23.9921
MOMO | Mt Molloy | FN | MOMO_66kV_BUS 1 | 66 | 1.9493 | 222.8332 | 1.4322 | 54.5755 | 1.1302 | 1.7016 | 64.8385 | 1.8523 | 70.5811 | 10.1556 | 18.9538 | 13.8346 | 42.9017 | 10.0821 | 19.0612
MOMW | Mt Mowbullan | SW | MOMW_11kV_TEF T1 | 11 | 0.62882 | 11.9806 | 0.71846 | 4.5628 | 0.82679 | 0.60896 | 3.8674 | 0.75104 | 4.7698 | 4.6236 | 10.1031 | 0.36689 | 7.3378 | 4.6238 | 10.1031
MOMW | Mt Mowbullan | SW | MOMW_33kV_TEF T1 | 33 | 0.45879 | 26.2236 | 0.34116 | 6.5 | 0.2629 | 0.3642 | 6.9389 | 0.46653 | 8.8886 | 38.3108 | 24.8881 | 45.9433 | 87.8754 | 38.312 | 24.8882
MONT | Monto | CA | MONT_11kV_BUS LH | 11 | 4.2061 | 80.136 | 5.2868 | 33.576 | 7.0451 | 4.5906 | 29.1542 | 5.5025 | 34.9453 | 0.77022 | 1.4716 | 0.05704 | 0.68448 | 0.77023 | 1.4721
MONT | Monto | CA | MONT_11kV_BUS RH | 11 | 4.2061 | 80.136 | 5.2868 | 33.576 | 7.0451 | 4.5906 | 29.1542 | 5.5025 | 34.9453 | 0.77022 | 1.4716 | 0.05704 | 0.68448 | 0.77023 | 1.4721
MONT | Monto | CA | MONT_66KV BUS 2 | 66 | 1.1048 | 126.2913 | 0.73912 | 28.1641 | 0.54736 | 0.9148 | 34.8586 | 1.0692 | 40.7424 | 25.6745 | 27.9355 | 36.7316 | 89.6725 | 25.6749 | 27.9521
MONT | Monto | CA | MONT_66kV_TEF T1 | 66 | 1.1048 | 126.2913 | 0.73912 | 28.1641 | 0.54736 | 0.9148 | 34.8586 | 1.0692 | 40.7424 | 25.6745 | 27.9355 | 36.7316 | 89.6725 | 25.6749 | 27.9521
MONT | Monto | CA | MONT_66kV_TEF T2 | 66 | 1.1048 | 126.2913 | 0.73912 | 28.1641 | 0.54736 | 0.9148 | 34.8586 | 1.0692 | 40.7424 | 25.6745 | 27.9355 | 36.7316 | 89.6725 | 25.6749 | 27.9521
MOOE | Moore | WB | MOOE_11kV_BUS | 11 | 3.2819 | 62.5283 | 3.6075 | 22.9106 | 4.0015 | 3.3796 | 21.4634 | 3.5692 | 22.6678 | 0.47277 | 2.0758 | 0.19623 | 1.5453 | 0.47268 | 2.076
MOOE | Moore | WB | MOOE_66kV_BUS 1 | 66 | 1.9466 | 222.5304 | 1.1713 | 44.6319 | 0.83281 | 1.6544 | 63.0418 | 1.8146 | 69.1441 | 9.9553 | 19.0958 | 15.9737 | 62.9999 | 9.9524 | 19.1032
MOOR | Moorvale | MK | MOOR_11kV_BUS 1 | 11 | 4.843 | 92.2707 | 5.3276 | 33.8347 | 5.9206 | 5.0688 | 32.191 | 5.1971 | 33.0061 | 0.16035 | 1.4336 | 0.06988 | 1.0469 | 0.16044 | 1.4339
MOOR | Moorvale | MK | MOOR_11kV_BUS 2 | 11 | 4.843 | 92.2707 | 5.3276 | 33.8347 | 5.9206 | 5.0688 | 32.191 | 5.1971 | 33.0061 | 0.16035 | 1.4336 | 0.06988 | 1.0469 | 0.16044 | 1.4339
MOOR | Moorvale | MK | MOOR_66kV_TEF T1 | 66 | 2.9321 | 335.1848 | 2.3483 | 89.4825 | 1.9591 | 2.6794 | 102.1004 | 2.7615 | 105.2282 | 3.2572 | 13.9194 | 4.2751 | 24.5971 | 3.2604 | 13.9328
MOPA | Mona Park (TF1) | NQ | MOPA_11kV_BUS 1 | 11 | 4.7421 | 90.3484 | 5.0898 | 32.3247 | 5.4897 | 4.8715 | 30.9382 | 5.0073 | 31.801 | 0.15336 | 1.4652 | 0.06429 | 1.1709 | 0.15188 | 1.4649
MOPA | Mona Park (TF2) | NQ | MOPA_11kV_BUS 2 | 11 | 4.7421 | 90.3484 | 5.0898 | 32.3247 | 5.4897 | 4.8715 | 30.9382 | 5.0073 | 31.801 | 0.15336 | 1.4652 | 0.06429 | 1.1709 | 0.15188 | 1.4649
MOPA | Mona Park | NQ | MOPA_66kV_BUS 1 | 66 | 4.6793 | 534.9167 | 3.3221 | 126.5884 | 2.5646 | 4.1337 | 157.5166 | 4.3737 | 166.6602 | 3.2068 | 8.364 | 4.7776 | 19.4568 | 3.1535 | 8.3553
MOPA | Mona Park | NQ | MOPA_66kV_BUS 2 | 66 | 4.6793 | 534.9167 | 3.3221 | 126.5884 | 2.5646 | 4.1337 | 157.5166 | 4.3737 | 166.6602 | 3.2068 | 8.364 | 4.7776 | 19.4568 | 3.1535 | 8.3553
MOPS | Moranbah Power Station | MK | MOPS_11kV_BUS 1 | 11 | 22.167 | 422.3388 | 0.8056 | 5.1163 | 0.41016 | 19.1779 | 121.7961 | 19.225 | 122.0953 | 0.04172 | 0.31238 | 0.03692 | 25.3896 | 0.03686 | 0.3129
MORA | Moranbah T034 (TF1) | MK | MORA_11kV_BUS A | 11 | 31.1072 | 592.6711 | 1.6567 | 10.5217 | 0.84982 | 27.0795 | 171.9781 | 26.8139 | 170.2913 | 0.02168 | 0.22353 | 4.8231 | 11.2305 | 0.01903 | 0.2237
MORA | Moranbah T034 (TF2*O0518*ON) | MK | MORA_11kV_BUS B | 11 | 31.1072 | 592.6711 | 1.6567 | 10.5217 | 0.84982 | 27.0795 | 171.9781 | 26.8139 | 170.2913 | 0.02168 | 0.22353 | 4.8231 | 11.2305 | 0.01903 | 0.2237
MORA | Moranbah T034 | MK | MORA_66kV_BUS A | 66 | 11.3986 | 1303.0332 | 13.2818 | 506.1036 | 15.9298 | 12.4733 | 475.2959 | 12.8871 | 491.0643 | 0.59067 | 3.6295 | 0.19057 | 2.1033 | 0.56062 | 3.6393
MORA | Moranbah T034 | MK | MORA_66kV_BUS B | 66 | 11.3986 | 1303.0332 | 13.2818 | 506.1036 | 15.9298 | 12.4733 | 475.2959 | 12.8871 | 491.0643 | 0.59067 | 3.6295 | 0.19057 | 2.1033 | 0.56062 | 3.6393
MORO | Mt Rooper | MK | MORO_11kV_TEF T1 | 11 | 3.4982 | 66.6496 | 3.8103 | 24.1989 | 4.1732 | 3.5777 | 22.7214 | 3.7789 | 23.9991 | 0.29345 | 1.9753 | 0.07567 | 1.5124 | 0.29223 | 1.9727
MORO | Mt Rooper | MK | MORO_66kV_TEF T1 | 66 | 2.2728 | 259.8134 | 1.6556 | 63.0861 | 1.2909 | 1.9823 | 75.5359 | 2.1652 | 82.5066 | 7.8431 | 16.6917 | 9.972 | 38.2173 | 7.7993 | 16.5953
MORW | Mt Rawdon | WB | MORW_66kV_TEF T1 | 66 | 1.1131 | 127.2432 | 0.67132 | 25.5808 | 0.47937 | 0.96255 | 36.678 | 1.0231 | 38.9862 | 15.8359 | 34.1683 | 31.0373 | 108.1684 | 15.7598 | 34.2074
MOSI | Mt Sibley (TF1) | SW | MOSI_11kV_BUS 1 | 11 | 2.9349 | 55.9173 | 3.7763 | 23.9826 | 5.2649 | 3.4188 | 21.712 | 3.885 | 24.6728 | 0.84368 | 2.2262 | 0.04114 | 0.8229 | 0.8437 | 2.2257
MOSI | Mt Sibley (TF2) | SW | MOSI_11kV_BUS 2 | 11 | 2.9349 | 55.9173 | 3.7763 | 23.9826 | 5.2649 | 3.4188 | 21.712 | 3.885 | 24.6728 | 0.84368 | 2.2262 | 0.04114 | 0.8229 | 0.8437 | 2.2257
MOSI | Mt Sibley (TF3) | SW | MOSI_11kV_BUS 3 | 11 | 2.9349 | 55.9173 | 3.7763 | 23.9826 | 5.2649 | 3.4188 | 21.712 | 3.885 | 24.6728 | 0.84368 | 2.2262 | 0.04114 | 0.8229 | 0.8437 | 2.2257
MOSI | Mt Sibley | SW | MOSI_33kV_BUS 1 | 33 | 1.4407 | 82.3491 | 0.58052 | 11.0604 | 0.35757 | 1.3284 | 25.3097 | 1.1889 | 22.6524 | 7.2228 | 12.6293 | 66.5525 | 46.6683 | 7.2229 | 12.6248
MOSI | Mt Sibley | SW | MOSI_33kV_BUS 2 | 33 | 1.4407 | 82.3491 | 0.58052 | 11.0604 | 0.35757 | 1.3284 | 25.3097 | 1.1889 | 22.6524 | 7.2228 | 12.6293 | 66.5525 | 46.6683 | 7.2229 | 12.6248
MOSI | Mt Sibley | SW | MOSI_33kV_BUS 3 | 33 | 1.4407 | 82.3491 | 0.58052 | 11.0604 | 0.35757 | 1.3284 | 25.3097 | 1.1889 | 22.6524 | 7.2228 | 12.6293 | 66.5525 | 46.6683 | 7.2229 | 12.6248
MOSS | Mossman (TF1) | FN | MOSS_22kV_BUS 1 | 22 | 4.8213 | 183.7157 | 4.2689 | 54.2223 | 3.8246 | 4.4678 | 56.7492 | 4.715 | 59.8881 | 0.40987 | 2.8688 | 0.1553 | 4.0326 | 0.39021 | 2.8708
MOSS | Mossman (TF2) | FN | MOSS_22kV_BUS 2 | 22 | 4.8213 | 183.7157 | 4.2689 | 54.2223 | 3.8246 | 4.4678 | 56.7492 | 4.715 | 59.8881 | 0.40987 | 2.8688 | 0.1553 | 4.0326 | 0.39021 | 2.8708
MOTY | Mt Tyson | SW | pole6065148_tr_line_47122 | 33 | 1.152 | 65.8451 | 0.80888 | 15.4112 | 0.60767 | 0.95525 | 18.2 | 1.1321 | 21.5691 | 12.4385 | 13.279 | 15.981 | 39.8108 | 12.2994 | 13.1202
MOUR | Moura T027 (TF1) | CA | MOUR_11kV_TEF T5 | 11 | 15.1541 | 288.724 | 12.8513 | 81.6169 | 11.1967 | 13.7899 | 87.5776 | 14.6777 | 93.2157 | 0.05375 | 0.45786 | 0.00139 | 0.70867 | 0.05389 | 0.46064
MOUR | Moura T027 (TF2) | CA | MOUR_11kV_TEF T6 | 11 | 15.107 | 287.8274 | 12.8232 | 81.4379 | 11.1798 | 13.7515 | 87.3341 | 14.6347 | 92.9431 | 0.05377 | 0.4593 | 0.00139 | 0.70937 | 0.05391 | 0.46209
MOUR | Moura T027 | CA | MOUR_22kV_TEF T5 | 22 | 5.1827 | 197.486 | 4.7964 | 60.9222 | 4.4744 | 4.8494 | 61.5957 | 5.1639 | 65.5898 | 0.29951 | 2.6792 | 0.00253 | 3.3488 | 0.30009 | 2.6904
MOUR | Moura T027 | CA | MOUR_22kV_TEF T6 | 22 | 5.1827 | 197.486 | 4.7964 | 60.9222 | 4.4744 | 4.8494 | 61.5957 | 5.1639 | 65.5898 | 0.29951 | 2.6792 | 0.00253 | 3.3488 | 0.30009 | 2.6904
MOUR | Moura T027 | CA | MOUR_66kV_BUS EAST | 66 | 6.0142 | 687.5209 | 7.4061 | 282.2099 | 9.7952 | 6.8466 | 260.8894 | 7.4169 | 282.6211 | 1.5156 | 6.8027 | 0.1253 | 2.9771 | 1.5226 | 6.902
MOUR | Moura T027 | CA | MOUR_66kV_BUS TRANSFER | 66 | 6.0142 | 687.5209 | 7.4061 | 282.2099 | 9.7952 | 6.8466 | 260.8894 | 7.4169 | 282.6211 | 1.5156 | 6.8027 | 0.1253 | 2.9771 | 1.5226 | 6.902
MOUR | Moura T027 | CA | MOUR_66kV_BUS WEST | 66 | 6.0142 | 687.5209 | 7.4061 | 282.2099 | 9.7952 | 6.8466 | 260.8894 | 7.4169 | 282.6211 | 1.5156 | 6.8027 | 0.1253 | 2.9771 | 1.5226 | 6.902
MUCK | Muckadilla Regulator (Un-Regulated) | SW | MUCK_33kV_R1 Downstream | 33 | 0.56522 | 32.3069 | 0.45427 | 8.655 | 0.36849 | 0.45287 | 8.6283 | 0.58476 | 11.1411 | 24.8576 | 27.5134 | 16.4191 | 66.5394 | 24.8417 | 27.5424
MUCK | Muckadilla Regulator (Regulated) | SW | MUCK_33kV_R1 Upstream | 33 | 0.59278 | 33.8817 | 0.47086 | 8.9711 | 0.37736 | 0.46946 | 8.9443 | 0.61466 | 11.7109 | 24.7447 | 25.2538 | 16.6665 | 65.4634 | 24.7287 | 25.2828
MUNG | Mungar QR T123 | WB | MUNG_132kV_TEF T1 | 132 | 2.996 | 684.972 | 1.719 | 131.0051 | 1.2046 | 2.6408 | 201.2534 | 2.6872 | 204.7893 | 7.665 | 26.9139 | 20.0767 | 88.145 | 7.451 | 26.9631
MUNG | Mungar QR T123 | WB | MUNG_132kV_TEF T2 | 132 | 2.996 | 684.972 | 1.719 | 131.0051 | 1.2046 | 2.6408 | 201.2534 | 2.6872 | 204.7893 | 7.665 | 26.9139 | 20.0767 | 88.145 | 7.451 | 26.9631
MURG | Murgon (TF1) | WB | MURG_11kV_BUS 1 | 11 | 6.3708 | 121.3792 | 7.7033 | 48.9224 | 9.7208 | 7.0468 | 44.7533 | 7.6466 | 48.5624 | 0.23073 | 1.0721 | 0.02369 | 0.53302 | 0.22991 | 1.0723
MURG | Murgon (TF2) | WB | MURG_11kV_BUS 2 | 11 | 6.3708 | 121.3792 | 7.7033 | 48.9224 | 9.7208 | 7.0468 | 44.7533 | 7.6466 | 48.5624 | 0.23073 | 1.0721 | 0.02369 | 0.53302 | 0.22991 | 1.0723
MURG | Murgon | WB | MURG_66kV_BUS LOWER_1 | 66 | 2.0163 | 230.4989 | 1.631 | 62.1501 | 1.3688 | 1.855 | 70.6851 | 1.8961 | 72.252 | 7.4535 | 19.4084 | 11.3008 | 33.7028 | 7.424 | 19.415
MURG | Murgon | WB | MURG_66kV_BUS LOWER_2 | 66 | 2.0163 | 230.4989 | 1.631 | 62.1501 | 1.3688 | 1.855 | 70.6851 | 1.8961 | 72.252 | 7.4535 | 19.4084 | 11.3008 | 33.7028 | 7.424 | 19.415
MURG | Murgon | WB | MURG_66kV_BUS UPPER_1 | 66 | 2.0163 | 230.4989 | 1.631 | 62.1501 | 1.3688 | 1.855 | 70.6851 | 1.8961 | 72.252 | 7.4535 | 19.4084 | 11.3008 | 33.7028 | 7.424 | 19.415
MURG | Murgon | WB | MURG_66kV_BUS UPPER_2 | 66 | 2.0163 | 230.4989 | 1.631 | 62.1501 | 1.3688 | 1.855 | 70.6851 | 1.8961 | 72.252 | 7.4535 | 19.4084 | 11.3008 | 33.7028 | 7.424 | 19.415
MUTA | Mutarnee | NQ | MUTA_11kV_TEF T1 | 11 | 0.94324 | 17.9712 | 0.98332 | 6.2449 | 1.0276 | 0.94836 | 6.0229 | 0.98098 | 6.2301 | 1.7363 | 7.1999 | 1.1464 | 6.4 | 1.7342 | 7.2075
MUTA | Mutarnee | NQ | MUTA_66kV_TEF T1 | 66 | 1.1714 | 133.9109 | 0.8872 | 33.8068 | 0.71388 | 1.0241 | 39.0238 | 1.121 | 42.716 | 21.2389 | 28.797 | 30.603 | 63.6189 | 21.163 | 29.0713
MUTO | Mundubbera Town | WB | MUTO_11kV_BUS 1 | 11 | 4.5472 | 86.6358 | 6.0685 | 38.54 | 9.0879 | 5.6364 | 35.7956 | 6.3673 | 40.4378 | 0.61836 | 1.4065 | 0.02012 | 0.40187 | 0.61227 | 1.411
MUTO | Mundubbera Town | WB | MUTO_11kV_BUS 2 | 11 | 4.5472 | 86.6358 | 6.0685 | 38.54 | 9.0879 | 5.6364 | 35.7956 | 6.3673 | 40.4378 | 0.61836 | 1.4065 | 0.02012 | 0.40187 | 0.61227 | 1.411
MUTO | Mundubbera Town | WB | MUTO_11kV_BUS 3 | 11 | 4.5472 | 86.6358 | 6.0685 | 38.54 | 9.0879 | 5.6364 | 35.7956 | 6.3673 | 40.4378 | 0.61836 | 1.4065 | 0.02012 | 0.40187 | 0.61227 | 1.411
MUTO | Mundubbera Town | WB | MUTO_66kV_BUS 1 | 66 | 0.97221 | 111.1389 | 0.62928 | 23.9789 | 0.4647 | 0.84843 | 32.3297 | 0.89698 | 34.1795 | 21.9269 | 37.1247 | 44.3649 | 104.987 | 21.7819 | 37.2721
MUTO | Mundubbera Town | WB | MUTO_66kV_BUS 2 | 66 | 0.97221 | 111.1389 | 0.62928 | 23.9789 | 0.4647 | 0.84843 | 32.3297 | 0.89698 | 34.1795 | 21.9269 | 37.1247 | 44.3649 | 104.987 | 21.7819 | 37.2721
NANA | Nanango | WB | NANA_11kV_BUS 1 | 11 | 5.1146 | 97.4466 | 5.9543 | 37.8151 | 7.1001 | 5.3599 | 34.0401 | 5.976 | 37.9529 | 0.43976 | 1.2933 | 0.09638 | 0.79518 | 0.43855 | 1.294
NANA | Nanango | WB | NANA_11kV_BUS 2 | 11 | 5.1146 | 97.4466 | 5.9543 | 37.8151 | 7.1001 | 5.3599 | 34.0401 | 5.976 | 37.9529 | 0.43976 | 1.2933 | 0.09638 | 0.79518 | 0.43855 | 1.294
NANA | Nanango | WB | NANA_66kV_BUS | 66 | 1.9246 | 220.0175 | 1.203 | 45.8417 | 0.86605 | 1.6134 | 61.4784 | 1.8247 | 69.531 | 12.3615 | 17.9332 | 18.519 | 59.3016 | 12.3178 | 17.9596
NAND | Nandi | SW | NAND_11kV_BUS G/DALE | 11 | 2.3411 | 44.6041 | 2.6954 | 17.1184 | 3.1489 | 2.3428 | 14.8785 | 2.7731 | 17.6119 | 1.0334 | 2.7997 | 0.08011 | 1.8744 | 1.0335 | 2.7997
NAND | Nandi | SW | NAND_11kV_BUS_LOUDIN | 11 | 2.3411 | 44.6041 | 2.6954 | 17.1184 | 3.1489 | 2.3428 | 14.8785 | 2.7731 | 17.6119 | 1.0334 | 2.7997 | 0.08011 | 1.8744 | 1.0335 | 2.7997
NAND | Nandi | SW | NAND_33kV_BUS | 33 | 1.753 | 100.1966 | 1.3054 | 24.8717 | 1.0209 | 1.4431 | 27.4955 | 1.7457 | 33.2604 | 8.5792 | 8.3284 | 10.0342 | 23.101 | 8.5805 | 8.3285
NEBO | Nebo H011 (TF3) | MK | NEBO_11kV_TEF T3 | 11 | 3.2474 | 61.871 | 1.8287 | 11.6137 | 1.2728 | 2.8529 | 18.1185 | 2.9123 | 18.4955 | 0.11817 | 2.148 | 0 | 7.161 | 0.11835 | 2.1492
NESM | Neil Smith (TF1) | NQ | NESM_11kV_BUS 1 | 11 | 19.3567 | 368.794 | 20.9867 | 133.2832 | 22.9046 | 19.9918 | 126.9651 | 20.6092 | 130.8858 | 0.03808 | 0.35889 | 0.01396 | 0.27683 | 0.03756 | 0.35887
NESM | Neil Smith (TF2) | NQ | NESM_11kV_BUS 2 | 11 | 19.3567 | 368.794 | 20.9867 | 133.2832 | 22.9046 | 19.9918 | 126.9651 | 20.6092 | 130.8858 | 0.03808 | 0.35889 | 0.01396 | 0.27683 | 0.03756 | 0.35887
NESM | Neil Smith | NQ | NESM_66kV_TEF T1 | 66 | 8.7206 | 996.9032 | 6.2738 | 239.0644 | 4.8894 | 7.7761 | 296.3097 | 8.1051 | 308.8462 | 1.776 | 4.4664 | 2.9682 | 10.0264 | 1.7572 | 4.4667
NESM | Neil Smith | NQ | NESM_66kV_TEF T2 | 66 | 10.4068 | 1189.6584 | 8.8587 | 337.5613 | 7.6977 | 9.6768 | 368.7366 | 9.9325 | 378.4804 | 1.1595 | 3.8572 | 1.46 | 5.9748 | 1.1405 | 3.8557
NEWL | Newlands T069 | NQ | NEWL_66kV_BUS 1 | 66 | 4.6885 | 535.9713 | 5.8672 | 223.5713 | 7.8303 | 5.39 | 205.3849 | 5.8789 | 224.0168 | 2.4108 | 8.6089 | 0.28431 | 3.5878 | 2.4202 | 8.6161
NEWL | Newlands T069 | NQ | NEWL_66kV_BUS 2 | 66 | 4.6885 | 535.9713 | 5.8672 | 223.5713 | 7.8303 | 5.39 | 205.3849 | 5.8789 | 224.0168 | 2.4108 | 8.6089 | 0.28431 | 3.5878 | 2.4202 | 8.6161
NOCL | North Cloncurry (TF1) | NQ - MI | NOCL_11kV_BUS 1 | 11 | 4.7809 | 91.0882 | 5.6737 | 36.0327 | 6.9948 | 5.2656 | 33.4411 | 5.5654 | 35.3449 | 0.2355 | 1.4421 | 0.03856 | 0.76994 | 0.23276 | 1.4469
NOCL | North Cloncurry (TF2) | NQ - MI | NOCL_11kV_BUS 3 | 11 | 4.7809 | 91.0882 | 5.6737 | 36.0327 | 6.9948 | 5.2656 | 33.4411 | 5.5654 | 35.3449 | 0.2355 | 1.4421 | 0.03856 | 0.76994 | 0.23276 | 1.4469
NOCL | North Cloncurry | NQ - MI | NOCL_66kV_BUS | 66 | 1.6623 | 190.0236 | 1.553 | 59.176 | 1.4645 | 1.6049 | 61.155 | 1.6204 | 61.7456 | 7.09 | 24.1985 | 7.892 | 29.3652 | 6.9913 | 24.3698
NOMA | North Mackay (TF1) | MK | NOMA_11kV_BUS 1 | 11 | 10.3064 | 196.3632 | 12.6083 | 80.0736 | 16.2766 | 11.9642 | 75.9831 | 12.186 | 77.3915 | 0.06169 | 0.67502 | 0.01525 | 0.30496 | 0.06032 | 0.67658
NOMA | North Mackay (TF2) | MK | NOMA_11kV_BUS 2 | 11 | 10.3064 | 196.3632 | 12.6083 | 80.0736 | 16.2766 | 11.9642 | 75.9831 | 12.186 | 77.3915 | 0.06169 | 0.67502 | 0.01525 | 0.30496 | 0.06032 | 0.67658
NOMA | North Mackay (TF1) | MK | NOMA_33kV_BUS 1 | 33 | 6.2437 | 356.8771 | 7.6487 | 145.7276 | 9.9164 | 7.3837 | 140.6787 | 7.2815 | 138.7319 | 0.41798 | 3.3305 | 0.22404 | 1.4781 | 0.40561 | 3.3446
NOMA | North Mackay (TF2) | MK | NOMA_33kV_BUS 2 | 33 | 6.2437 | 356.8771 | 7.6487 | 145.7276 | 9.9164 | 7.3837 | 140.6787 | 7.2815 | 138.7319 | 0.41798 | 3.3305 | 0.22404 | 1.4781 | 0.40561 | 3.3446
NORM | Normanton | FN | NORM_22kV_BUS 1 | 22 | 0.95367 | 36.3398 | 1.3377 | 16.9912 | 2.264 | 1.3734 | 17.4441 | 1.4284 | 18.1425 | 3.2531 | 14.2849 | 0.00831 | 1.9719 | 2.9337 | 14.4586
NORM | Normanton | FN | NORM_22kV_BUS 2 | 22 | 0.95367 | 36.3398 | 1.3377 | 16.9912 | 2.264 | 1.3734 | 17.4441 | 1.4284 | 18.1425 | 3.2531 | 14.2849 | 0.00831 | 1.9719 | 2.9337 | 14.4586
NORM | Normanton | FN | NORM_6.6kV_BUS 1 | 6.6 | 2.7805 | 31.7852 | 0 | 0 | 0 | 2.4005 | 9.1472 | 2.4005 | 9.1472 | 0.30006 | 1.4773 | 329999969.002 | -28.6636 | 0.27121 | 1.4926
NORM | Normanton | FN | NORM_6.6kV_BUS 2 | 6.6 | 2.7805 | 31.7852 | 0 | 0 | 0 | 2.4005 | 9.1472 | 2.4005 | 9.1472 | 0.30006 | 1.4773 | 329999969.002 | -28.6636 | 0.27121 | 1.4926
NORM | Normanton | FN | NORM_T01 3MI | 66 | 0.34831 | 39.8175 | 0.47403 | 18.0628 | 0.74971 | 0.46518 | 17.7259 | 0.49637 | 18.9141 | 31.3585 | 116.1815 | 0.2891 | 24.2953 | 29.3755 | 117.6832
NORM | Normanton | FN | NORM_T02 3MI | 66 | 0.34831 | 39.8175 | 0.47403 | 18.0628 | 0.74971 | 0.46518 | 17.7259 | 0.49637 | 18.9141 | 31.3585 | 116.1815 | 0.2891 | 24.2953 | 29.3755 | 117.6832
NORW | Norwin (TF2) | SW | NORW_11kV_BUS 2 | 11 | 2.0427 | 38.9185 | 2.7055 | 17.182 | 3.9268 | 2.4087 | 15.297 | 2.8607 | 18.1681 | 1.675 | 2.9821 | 0.05109 | 1.0218 | 1.6596 | 2.9645
NORW | Norwin (TF1) | SW | NORW_11kV_BUS T1 | 11 | 2.0427 | 38.9185 | 2.7055 | 17.182 | 3.9268 | 2.4087 | 15.297 | 2.8607 | 18.1681 | 1.675 | 2.9821 | 0.05109 | 1.0218 | 1.6596 | 2.9645
NORW | Norwin (TF3) | SW | NORW_11kV_BUS T3 | 11 | 2.0427 | 38.9185 | 2.7055 | 17.182 | 3.9268 | 2.4087 | 15.297 | 2.8607 | 18.1681 | 1.675 | 2.9821 | 0.05109 | 1.0218 | 1.6596 | 2.9645
NORW | Norwin | SW | NORW_33kV_BUS 2 | 33 | 0.91486 | 52.2915 | 0.59495 | 11.3354 | 0.43228 | 0.76426 | 14.5611 | 0.88017 | 16.7695 | 14.6156 | 17.6434 | 21.6463 | 57.587 | 14.4764 | 17.4846
NORW | Norwin | SW | NORW_33kV_BUS T1 | 33 | 0.91486 | 52.2915 | 0.59495 | 11.3354 | 0.43228 | 0.76426 | 14.5611 | 0.88017 | 16.7695 | 14.6156 | 17.6434 | 21.6463 | 57.587 | 14.4764 | 17.4846
NORW | Norwin | SW | NORW_33kV_BUS T3 | 33 | 0.91486 | 52.2915 | 0.59495 | 11.3354 | 0.43228 | 0.76426 | 14.5611 | 0.88017 | 16.7695 | 14.6156 | 17.6434 | 21.6463 | 57.587 | 14.4764 | 17.4846
NOST | North Street | SW | NOST_11kV_BUS 1 | 11 | 9.8383 | 187.445 | 2.232 | 14.1752 | 1.1512 | 9.0857 | 57.702 | 7.9624 | 50.5684 | 0.09684 | 0.70355 | 9.0204 | 0.40809 | 0.09679 | 0.70306
NOST | North Street | SW | NOST_11kV_BUS 2 | 11 | 9.8383 | 187.445 | 2.232 | 14.1752 | 1.1512 | 9.0857 | 57.702 | 7.9624 | 50.5684 | 0.09684 | 0.70355 | 9.0204 | 0.40809 | 0.09679 | 0.70306
NOST | North Street | SW | NOST_11kV_BUS 3 | 11 | 9.8383 | 187.445 | 2.232 | 14.1752 | 1.1512 | 9.0857 | 57.702 | 7.9624 | 50.5684 | 0.09684 | 0.70355 | 9.0204 | 0.40809 | 0.09679 | 0.70306
NOST | North Street | SW | NOST_11kV_BUS 4 | 11 | 9.8383 | 187.445 | 2.232 | 14.1752 | 1.1512 | 9.0857 | 57.702 | 7.9624 | 50.5684 | 0.09684 | 0.70355 | 9.0204 | 0.40809 | 0.09679 | 0.70306
NOST | North Street | SW | NOST_11kV_BUS 5 | 11 | 9.8383 | 187.445 | 2.232 | 14.1752 | 1.1512 | 9.0857 | 57.702 | 7.9624 | 50.5684 | 0.09684 | 0.70355 | 9.0204 | 0.40809 | 0.09679 | 0.70306
NOST | North Street | SW | NOST_11kV_BUS 6 | 11 | 9.8383 | 187.445 | 2.232 | 14.1752 | 1.1512 | 9.0857 | 57.702 | 7.9624 | 50.5684 | 0.09684 | 0.70355 | 9.0204 | 0.40809 | 0.09679 | 0.70306
NOST | North Street | SW | NOST_11kV_BUS 7 | 11 | 9.8383 | 187.445 | 2.232 | 14.1752 | 1.1512 | 9.0857 | 57.702 | 7.9624 | 50.5684 | 0.09684 | 0.70355 | 9.0204 | 0.40809 | 0.09679 | 0.70306
NOST | North Street | SW | NOST_33kV_BUS 1 | 33 | 7.6314 | 436.1926 | 1.1069 | 21.0897 | 0.56515 | 6.8873 | 131.2205 | 6.342 | 120.8313 | 0.68796 | 2.6591 | 55.2411 | -0.64508 | 0.6875 | 2.6547
NOST | North Street | SW | NOST_33kV_BUS 2 | 33 | 7.6314 | 436.1926 | 1.1069 | 21.0897 | 0.56515 | 6.8873 | 131.2205 | 6.342 | 120.8313 | 0.68796 | 2.6591 | 55.2411 | -0.64508 | 0.6875 | 2.6547
NOST | North Street | SW | NOST_33kV_BUS 3 | 33 | 7.6314 | 436.1926 | 1.1069 | 21.0897 | 0.56515 | 6.8873 | 131.2205 | 6.342 | 120.8313 | 0.68796 | 2.6591 | 55.2411 | -0.64508 | 0.6875 | 2.6547
OAKE | Oakey | SW | OAKE_11kV_BUS 1 | 11 | 15.5941 | 297.108 | 17.6425 | 112.0447 | 20.3146 | 16.8737 | 107.1622 | 16.9218 | 107.4676 | 0.0236 | 0.4474 | 0.01489 | 0.29151 | 0.0252 | 0.4474
OAKE | Oakey | SW | OAKE_11kV_BUS 2 | 11 | 15.5941 | 297.108 | 17.6425 | 112.0447 | 20.3146 | 16.8737 | 107.1622 | 16.9218 | 107.4676 | 0.0236 | 0.4474 | 0.01489 | 0.29151 | 0.0252 | 0.4474
OAKE | Oakey | SW | OAKE_33kV_BUS 1 | 33 | 14.9159 | 852.5569 | 1.1581 | 22.0654 | 0.58113 | 13.2046 | 251.5811 | 12.6249 | 240.5356 | 0.0784 | 1.403 | 54.074 | -0.52275 | 0.09279 | 1.403
OAKE | Oakey | SW | OAKE_33kV_BUS 2 | 33 | 14.9159 | 852.5569 | 1.1581 | 22.0654 | 0.58113 | 13.2046 | 251.5811 | 12.6249 | 240.5356 | 0.0784 | 1.403 | 54.074 | -0.52275 | 0.09279 | 1.403
OAKY | Oakey T189 (TF1) | SW | OAKY_33kV_TEF T3 | 33 | 14.9159 | 852.5569 | 1.1581 | 22.0654 | 0.58113 | 13.2046 | 251.5811 | 12.6249 | 240.5356 | 0.0784 | 1.403 | 54.074 | -0.52275 | 0.09279 | 1.403
OAKY | Oakey T189 (TF2) | SW | OAKY_33kV_TEF T4 | 33 | 14.9159 | 852.5569 | 1.1581 | 22.0654 | 0.58113 | 13.2046 | 251.5811 | 12.6249 | 240.5356 | 0.0784 | 1.403 | 54.074 | -0.52275 | 0.09279 | 1.403
OONN | Oonoonba | NQ | OONN_11kV_BUS 1 | 11 | 15.6779 | 298.7043 | 16.8773 | 107.185 | 18.2639 | 16.0624 | 102.0101 | 16.6592 | 105.7998 | 0.04331 | 0.44348 | 0.01118 | 0.35103 | 0.04279 | 0.44345
OONN | Oonoonba | NQ | OONN_11kV_BUS 2 | 11 | 15.6779 | 298.7043 | 16.8773 | 107.185 | 18.2639 | 16.0624 | 102.0101 | 16.6592 | 105.7998 | 0.04331 | 0.44348 | 0.01118 | 0.35103 | 0.04279 | 0.44345
OONN | Oonoonba | NQ | OONN_11kV_BUS 3 | 11 | 15.6779 | 298.7043 | 16.8773 | 107.185 | 18.2639 | 16.0624 | 102.0101 | 16.6592 | 105.7998 | 0.04331 | 0.44348 | 0.01118 | 0.35103 | 0.04279 | 0.44345
OONN | Oonoonba | NQ | OONN_66kV_BUS 1 | 66 | 11.8961 | 1359.9091 | 9.5117 | 362.4434 | 7.9088 | 10.9439 | 417.0176 | 11.1412 | 424.5372 | 1.1566 | 3.3282 | 1.7988 | 5.9153 | 1.1379 | 3.3271
OONN | Oonoonba | NQ | OONN_66kV_BUS 2 | 66 | 11.8961 | 1359.9091 | 9.5117 | 362.4434 | 7.9088 | 10.9439 | 417.0176 | 11.1412 | 424.5372 | 1.1566 | 3.3282 | 1.7988 | 5.9153 | 1.1379 | 3.3271
OWAN | Owanyilla | WB | OWAN_11kV_BUS | 11 | 7.6504 | 145.7594 | 8.5839 | 54.5148 | 9.7871 | 8.0261 | 50.9723 | 8.4374 | 53.5847 | 0.1394 | 0.90253 | 0.03761 | 0.61461 | 0.13867 | 0.90413
OWAN | Owanyilla | WB | OWAN_11kV_TEF T1 | 11 | 7.6504 | 145.7594 | 8.5839 | 54.5148 | 9.7871 | 8.0261 | 50.9723 | 8.4374 | 53.5847 | 0.1394 | 0.90253 | 0.03761 | 0.61461 | 0.13867 | 0.90413
OWAN | Owanyilla | WB | OWAN_11kV_TEF T2 | 11 | 7.6504 | 145.7594 | 8.5839 | 54.5148 | 9.7871 | 8.0261 | 50.9723 | 8.4374 | 53.5847 | 0.1394 | 0.90253 | 0.03761 | 0.61461 | 0.13867 | 0.90413
OWAN | Owanyilla | WB | OWAN_66kV_BUS | 66 | 3.813 | 435.884 | 2.7091 | 103.2289 | 2.1043 | 3.368 | 128.3393 | 3.5506 | 135.2966 | 3.6647 | 10.365 | 5.4373 | 23.8513 | 3.6383 | 10.4226
PACO | Pacific Coal | WB | PACO_66kV_BUS | 66 | 12.3056 | 1406.7158 | 10.7147 | 408.2832 | 9.5028 | 11.5807 | 441.2838 | 11.7418 | 447.4228 | 0.93149 | 3.2768 | 1.2195 | 4.7652 | 0.92859 | 3.2842
PAJI | Pajingo | NQ | PAJI_11kV_TEF T1 | 11 | 3.2058 | 61.0779 | 3.9164 | 24.8727 | 5.003 | 3.4451 | 21.8791 | 4.0069 | 25.4476 | 0.78776 | 2.0318 | 0.05905 | 1.0295 | 0.7863 | 2.0347
PAJI | Pajingo | NQ | PAJI_66kV_TEF T1 | 66 | 0.93956 | 107.4062 | 0.67748 | 25.8153 | 0.52412 | 0.7898 | 30.0955 | 0.91466 | 34.8534 | 26.2334 | 36.0838 | 30.7736 | 93.656 | 26.1809 | 36.1855
PAMP | Pampas | SW | PAMP_11kV_BUS ST RONANS | 11 | 3.2754 | 62.4052 | 4.1828 | 26.5644 | 5.7018 | 3.8876 | 24.6897 | 4.1593 | 26.415 | 0.4552 | 2.084 | 0.03862 | 0.77248 | 0.43975 | 2.0663
PAMP | Pampas | SW | PAMP_11kV_BUS T1 | 11 | 3.2754 | 62.4052 | 4.1828 | 26.5644 | 5.7018 | 3.8876 | 24.6897 | 4.1593 | 26.415 | 0.4552 | 2.084 | 0.03862 | 0.77248 | 0.43975 | 2.0663
PAMP | Pampas | SW | PAMP_11kV_BUS T3 | 11 | 3.2754 | 62.4052 | 4.1828 | 26.5644 | 5.7018 | 3.8876 | 24.6897 | 4.1593 | 26.415 | 0.4552 | 2.084 | 0.03862 | 0.77248 | 0.43975 | 2.0663
PAMP | Pampas | SW | PAMP_11kV_BUS YANDILLA | 11 | 3.2754 | 62.4052 | 4.1828 | 26.5644 | 5.7018 | 3.8876 | 24.6897 | 4.1593 | 26.415 | 0.4552 | 2.084 | 0.03862 | 0.77248 | 0.43975 | 2.0663
PAMP | Pampas | SW | PAMP_33kV_BUS 1 | 33 | 1.6925 | 96.7382 | 0.47223 | 8.9972 | 0.27035 | 1.4444 | 27.5199 | 1.5201 | 28.9622 | 3.7492 | 11.8032 | 0.00576 | 109.49 | 3.6101 | 11.6444
PAMP | Pampas | SW | PAMP_33kV_BUS 2 | 33 | 1.6925 | 96.7382 | 0.47223 | 8.9972 | 0.27035 | 1.4444 | 27.5199 | 1.5201 | 28.9622 | 3.7492 | 11.8032 | 0.00576 | 109.49 | 3.6101 | 11.6444
PAMP | Pampas | SW | PAMP_33kV_BUS 3 | 33 | 1.6925 | 96.7382 | 0.47223 | 8.9972 | 0.27035 | 1.4444 | 27.5199 | 1.5201 | 28.9622 | 3.7492 | 11.8032 | 0.00576 | 109.49 | 3.6101 | 11.6444
PAMP | Pampas | SW | PAMP_33kV_BUS R1 Downstream | 33 | 1.6925 | 96.7382 | 0.47223 | 8.9972 | 0.27035 | 1.4444 | 27.5199 | 1.5201 | 28.9622 | 3.7492 | 11.8032 | 0.00576 | 109.49 | 3.6101 | 11.6444
PAMP | Pampas | SW | PAMP_33kV_BUS R1 Upstream | 33 | 1.8556 | 106.0612 | 1.205 | 22.9582 | 0.88078 | 1.684 | 32.0847 | 1.6708 | 31.8336 | 3.6928 | 10.6751 | 10.052 | 28.0352 | 3.5537 | 10.5162
PAND | Pandoin | CA | PAND_22kV_BUS 1 | 22 | 5.2734 | 200.945 | 5.6511 | 71.7783 | 6.094 | 5.4611 | 69.3651 | 5.5164 | 70.0674 | 0.19625 | 2.6423 | 0.1192 | 2.1123 | 0.19642 | 2.6452
PAND | Pandoin | CA | PAND_22kV_BUS 2 | 22 | 5.2734 | 200.945 | 5.6511 | 71.7783 | 6.094 | 5.4611 | 69.3651 | 5.5164 | 70.0674 | 0.19625 | 2.6423 | 0.1192 | 2.1123 | 0.19642 | 2.6452
PAND | Pandoin | CA | PAND_66kV_BUS 1 | 66 | 8.6972 | 994.2189 | 9.5551 | 364.0999 | 10.6647 | 9.2689 | 353.1941 | 9.1679 | 349.346 | 0.69341 | 4.7694 | 0.56918 | 3.4489 | 0.69491 | 4.7957
PAND | Pandoin | CA | PAND_66kV_TEF T1 | 66 | 8.6972 | 994.2189 | 9.5551 | 364.0999 | 10.6647 | 9.2689 | 353.1941 | 9.1679 | 349.346 | 0.69341 | 4.7694 | 0.56918 | 3.4489 | 0.69491 | 4.7957
PAND | Pandoin | CA | PAND_66kV_TEF T2 | 66 | 8.6972 | 994.2189 | 9.5551 | 364.0999 | 10.6647 | 9.2689 | 353.1941 | 9.1679 | 349.346 | 0.69341 | 4.7694 | 0.56918 | 3.4489 | 0.69491 | 4.7957
PAPS | Pajingo Pumps | NQ | PAPS_66kV_TEF T1 | 66 | 1.8761 | 214.4635 | 1.5461 | 58.9158 | 1.3102 | 1.6441 | 62.6468 | 1.8503 | 70.5058 | 10.0995 | 19.9293 | 8.9378 | 35.9912 | 10.0471 | 20.031
PARK | Parkhurst | CA | PARK_11kV_BUS 1 | 11 | 18.1572 | 345.9413 | 20.1794 | 128.1563 | 22.7508 | 19.1884 | 121.8625 | 19.6117 | 124.5511 | 0.0344 | 0.38321 | 0.01341 | 0.26822 | 0.03442 | 0.3839
PARK | Parkhurst | CA | PARK_11kV_BUS 2 | 11 | 18.1572 | 345.9413 | 20.1794 | 128.1563 | 22.7508 | 19.1884 | 121.8625 | 19.6117 | 124.5511 | 0.0344 | 0.38321 | 0.01341 | 0.26822 | 0.03442 | 0.3839
PARK | Parkhurst | CA | PARK_11kV_BUS 3 | 11 | 18.1572 | 345.9413 | 20.1794 | 128.1563 | 22.7508 | 19.1884 | 121.8625 | 19.6117 | 124.5511 | 0.0344 | 0.38321 | 0.01341 | 0.26822 | 0.03442 | 0.3839
PARK | Parkhurst | CA | PARK_66kV_BUS | 66 | 9.9605 | 1138.6432 | 10.0316 | 382.2563 | 10.1549 | 10.2419 | 390.2691 | 9.7421 | 371.2248 | 0.75571 | 4.1398 | 1.0799 | 3.9599 | 0.75625 | 4.1647
PEAR | Peter Arlett | NQ | PEAR_11kV_BUS 1 | 11 | 17.3445 | 330.4568 | 18.8646 | 119.8066 | 20.6694 | 18.018 | 114.43 | 18.4462 | 117.1488 | 0.032694 | 0.40145 | 0.011714 | 0.30545 | 0.032195 | 0.40142
PEAR | Peter Arlett | NQ | PEAR_11kV_BUS 2 | 11 | 17.3445 | 330.4568 | 18.8646 | 119.8066 | 20.6694 | 18.018 | 114.43 | 18.4462 | 117.1488 | 0.032694 | 0.40145 | 0.011714 | 0.30545 | 0.032195 | 0.40142
PEAR | Peter Arlett | NQ | PEAR_66kV_BUS 1 | 66 | 11.8375 | 1353.2101 | 8.9902 | 342.5711 | 7.2392 | 10.8814 | 414.6371 | 10.8726 | 414.3021 | 0.75569 | 3.4593 | 1.4525 | 6.7557 | 0.73771 | 3.4584
PEAR | Peter Arlett | NQ | PEAR_66kV_BUS 2 | 66 | 11.8375 | 1353.2101 | 8.9902 | 342.5711 | 7.2392 | 10.8814 | 414.6371 | 10.8726 | 414.3021 | 0.75569 | 3.4593 | 1.4525 | 6.7557 | 0.73771 | 3.4584
PECR | Perseverance Creek (TF2) | SW | PECR_11kV_TEF T2 | 11 | 2.9064 | 55.375 | 3.8366 | 24.3657 | 5.082 | 4.4263 | 28.1109 | 2.4482 | 15.5481 | 0.66857 | 2.3092 | 1.2043 | 0.2185 | 0.66857 | 2.3087
PECR | Perseverance Creek | SW | PECR_33kV_BUS 1 | 33 | 2.0265 | 115.8302 | 0.82604 | 15.7382 | 0.51216 | 1.684 | 32.0841 | 1.8594 | 35.4256 | 5.3568 | 8.8484 | 9.0139 | 55.8336 | 5.3568 | 8.8445
PERA | Peranga (TF1) | SW | PERA_11kV_BUS BRYMAROO | 11 | 1.7952 | 34.2039 | 2.2534 | 14.3107 | 2.9998 | 1.973 | 12.5304 | 2.3325 | 14.8131 | 1.5816 | 3.5558 | 0.08027 | 1.6055 | 1.5832 | 3.5558
PERA | Peranga (TF3) | SW | PERA_11kV_BUS E/GREEN | 11 | 1.7952 | 34.2039 | 2.2534 | 14.3107 | 2.9998 | 1.973 | 12.5304 | 2.3325 | 14.8131 | 1.5816 | 3.5558 | 0.08027 | 1.6055 | 1.5832 | 3.5558
PERA | Peranga | SW | PERA_11kV_BUS QUINALOW | 11 | 1.7952 | 34.2039 | 2.2534 | 14.3107 | 2.9998 | 1.973 | 12.5304 | 2.3325 | 14.8131 | 1.5816 | 3.5558 | 0.08027 | 1.6055 | 1.5832 | 3.5558
PERA | Peranga | SW | PERA_33kV_BUS | 33 | 0.94619 | 54.0819 | 0.43724 | 8.3306 | 0.28311 | 0.85829 | 16.3527 | 0.80365 | 15.3116 | 13.5122 | 17.5531 | 76.9476 | 64.2285 | 13.5266 | 17.5531
PERA | Peranga | SW | PERA_33kV_BUS T1 | 33 | 0.94619 | 54.0819 | 0.43724 | 8.3306 | 0.28311 | 0.85829 | 16.3527 | 0.80365 | 15.3116 | 13.5122 | 17.5531 | 76.9476 | 64.2285 | 13.5266 | 17.5531
PERA | Peranga | SW | PERA_33kV_BUS T3 | 33 | 0.94619 | 54.0819 | 0.43724 | 8.3306 | 0.28311 | 0.85829 | 16.3527 | 0.80365 | 15.3116 | 13.5122 | 17.5531 | 76.9476 | 64.2285 | 13.5266 | 17.5531
PIAL | Pialba | WB | PIAL_11kV_BUS 1 | 11 | 5.401 | 102.9034 | 5.8405 | 37.0921 | 6.3812 | 5.5911 | 35.5083 | 5.7239 | 36.3515 | 0.11473 | 1.2885 | 0.04651 | 0.99652 | 0.11439 | 1.2931
PIAL | Pialba | WB | PIAL_11kV_BUS 2 | 11 | 5.401 | 102.9034 | 5.8405 | 37.0921 | 6.3812 | 5.5911 | 35.5083 | 5.7239 | 36.3515 | 0.11473 | 1.2885 | 0.04651 | 0.99652 | 0.11439 | 1.2931
PIAL | Pialba | WB | PIAL_66kV_BUS 1 | 66 | 3.884 | 444.0047 | 2.6046 | 99.2465 | 1.9809 | 3.492 | 133.0633 | 3.4816 | 132.6667 | 2.456 | 10.5095 | 6.0916 | 25.8303 | 2.4434 | 10.6763
PIAL | Pialba | WB | PIAL_66kV_BUS 2 | 66 | 3.884 | 444.0047 | 2.6046 | 99.2465 | 1.9809 | 3.492 | 133.0633 | 3.4816 | 132.6667 | 2.456 | 10.5095 | 6.0916 | 25.8303 | 2.4434 | 10.6763
PINN | Pinnacle | MK | PINN_11kV_BUS 1 | 11 | 4.9644 | 94.5842 | 5.7334 | 36.4121 | 6.7847 | 5.2298 | 33.2136 | 5.709 | 36.2573 | 0.33458 | 1.3669 | 0.06303 | 0.84464 | 0.33439 | 1.3699
PINN | Pinnacle | MK | PINN_11kV_BUS 2 | 11 | 4.9644 | 94.5842 | 5.7334 | 36.4121 | 6.7847 | 5.2298 | 33.2136 | 5.709 | 36.2573 | 0.33458 | 1.3669 | 0.06303 | 0.84464 | 0.33439 | 1.3699
PINN | Pinnacle | MK | PINN_11kV_BUS 3 | 11 | 4.9644 | 94.5842 | 5.7334 | 36.4121 | 6.7847 | 5.2298 | 33.2136 | 5.709 | 36.2573 | 0.33458 | 1.3669 | 0.06303 | 0.84464 | 0.33439 | 1.3699
PINN | Pinnacle | MK | PINN_66kV_BUS 1 | 66 | 1.9781 | 226.1287 | 1.2809 | 48.8073 | 0.9458 | 1.6972 | 64.6737 | 1.848 | 70.4172 | 9.7758 | 18.8001 | 15.5069 | 53.9965 | 9.7692 | 18.9073
PINN | Pinnacle | MK | PINN_66kV_BUS 2 | 66 | 1.9781 | 226.1287 | 1.2809 | 48.8073 | 0.9458 | 1.6972 | 64.6737 | 1.848 | 70.4172 | 9.7758 | 18.8001 | 15.5069 | 53.9965 | 9.7692 | 18.9073
PIRR | Pirrinuan (TF1) | SW | PIRR_11kV_BUS 1 | 11 | 2.2369 | 42.6195 | 2.6028 | 16.5298 | 3.0934 | 2.3011 | 14.6141 | 2.6448 | 16.797 | 0.84753 | 3.0061 | 0.02382 | 1.8551 | 0.84767 | 3.0061
PIRR | Pirrinuan (TF2) | SW | PIRR_11kV_BUS 2 | 11 | 2.2369 | 42.6195 | 2.6028 | 16.5298 | 3.0934 | 2.3011 | 14.6141 | 2.6448 | 16.797 | 0.84753 | 3.0061 | 0.02382 | 1.8551 | 0.84767 | 3.0061
PIRR | Pirrinuan | SW | PIRR_33kV_BUS 1 | 33 | 1.7228 | 98.4687 | 1.0953 | 20.8681 | 0.79658 | 1.4564 | 27.7486 | 1.6272 | 31.0018 | 6.2931 | 10.4127 | 9.2812 | 32.2559 | 6.2943 | 10.4128
PIVA | Pioneer Valley T141 | MK | PIVA_66kV_BUS 1 | 66 | 8.3676 | 956.5427 | 10.3097 | 392.8541 | 13.6185 | 9.9616 | 379.5887 | 9.8994 | 377.2195 | 0.53894 | 4.9802 | 0.24594 | 2.1094 | 0.51723 | 5.0376
PIVA | Pioneer Valley T141 | MK | PIVA_66kV_BUS 2 | 66 | 8.3676 | 956.5427 | 10.3097 | 392.8541 | 13.6185 | 9.9616 | 379.5887 | 9.8994 | 377.2195 | 0.53894 | 4.9802 | 0.24594 | 2.1094 | 0.51723 | 5.0376
PLAN | Planella (TF1) | MK | PLAN_11kV_BUS 1 | 11 | 5.7067 | 108.7278 | 7.3244 | 46.5159 | 10.226 | 6.906 | 43.8588 | 7.3092 | 46.4199 | 0.23338 | 1.2017 | 0.02073 | 0.41482 | 0.232 | 1.2033
PLAN | Planella (TF2) | MK | PLAN_11kV_BUS 2 | 11 | 5.7067 | 108.7278 | 7.3244 | 46.5159 | 10.226 | 6.906 | 43.8588 | 7.3092 | 46.4199 | 0.23338 | 1.2017 | 0.02073 | 0.41482 | 0.232 | 1.2033
PLAN | Planella | MK | PLAN_33kV_BUS 1 | 33 | 2.8568 | 163.2893 | 2.4064 | 45.8485 | 2.0812 | 2.6951 | 51.3487 | 2.6704 | 50.8779 | 1.9138 | 7.0821 | 3.1502 | 11.0037 | 1.9015 | 7.0961
PLEY | Pleystowe | MK | PLEY_11kV_BUS 1 | 11 | 6.292 | 119.8789 | 7.5613 | 48.0206 | 9.4552 | 6.8228 | 43.3303 | 7.5828 | 48.1572 | 0.28885 | 1.0721 | 0.02795 | 0.55909 | 0.28816 | 1.0738
PLEY | Pleystowe | MK | PLEY_11kV_BUS 2 | 11 | 6.292 | 119.8789 | 7.5613 | 48.0206 | 9.4552 | 6.8228 | 43.3303 | 7.5828 | 48.1572 | 0.28885 | 1.0721 | 0.02795 | 0.55909 | 0.28816 | 1.0738
PLEY | Pleystowe | MK | PLEY_11kV_BUS 3 | 11 | 6.292 | 119.8789 | 7.5613 | 48.0206 | 9.4552 | 6.8228 | 43.3303 | 7.5828 | 48.1572 | 0.28885 | 1.0721 | 0.02795 | 0.55909 | 0.28816 | 1.0738
PLEY | Pleystowe | MK | PLEY_11kV_BUS 4 | 11 | 6.292 | 119.8789 | 7.5613 | 48.0206 | 9.4552 | 6.8228 | 43.3303 | 7.5828 | 48.1572 | 0.28885 | 1.0721 | 0.02795 | 0.55909 | 0.28816 | 1.0738
PLEY | Pleystowe | MK | PLEY_33kV_BUS 1 | 33 | 4.0463 | 231.2777 | 2.5325 | 48.2501 | 1.8377 | 3.4694 | 66.1008 | 3.7641 | 71.7163 | 2.348 | 4.6167 | 3.9177 | 14.0384 | 2.3418 | 4.632
PLEY | Pleystowe | MK | PLEY_33kV_BUS 2 | 33 | 4.0463 | 231.2777 | 2.5325 | 48.2501 | 1.8377 | 3.4694 | 66.1008 | 3.7641 | 71.7163 | 2.348 | 4.6167 | 3.9177 | 14.0384 | 2.3418 | 4.632
PLEY | Pleystowe | MK | PLEY_33kV_BUS 3 | 33 | 4.0463 | 231.2777 | 2.5325 | 48.2501 | 1.8377 | 3.4694 | 66.1008 | 3.7641 | 71.7163 | 2.348 | 4.6167 | 3.9177 | 14.0384 | 2.3418 | 4.632
PLEY | Pleystowe | MK | PLEY_33kV_BUS 4 | 33 | 4.0463 | 231.2777 | 2.5325 | 48.2501 | 1.8377 | 3.4694 | 66.1008 | 3.7641 | 71.7163 | 2.348 | 4.6167 | 3.9177 | 14.0384 | 2.3418 | 4.632
PLEY | Pleystowe | MK | PLEY_11kV_BUS 1 | 11 | 6.292 | 119.8789 | 7.5613 | 48.0206 | 9.4552 | 6.8228 | 43.3303 | 7.5828 | 48.1572 | 0.28885 | 1.0721 | 0.02795 | 0.55909 | 0.28816 | 1.0738
POCU | Port Curtis | CA | POCU_11kV_BUS A | 11 | 25.3449 | 482.8856 | 2.1827 | 13.8617 | 1.0984 | 22.4773 | 142.7503 | 21.3855 | 135.8161 | 0.02099 | 0.27484 | 9.5326 | 0.17789 | 0.02099 | 0.2753
POCU | Port Curtis | CA | POCU_11kV_BUS B | 11 | 25.3449 | 482.8856 | 2.1827 | 13.8617 | 1.0984 | 22.4773 | 142.7503 | 21.3855 | 135.8161 | 0.02099 | 0.27484 | 9.5326 | 0.17789 | 0.02099 | 0.2753
POCU | Port Curtis | CA | POCU_66kV_BUS 1 | 66 | 11.8967 | 1359.974 | 11.8986 | 453.3959 | 11.9516 | 12.0757 | 460.1445 | 11.7152 | 446.4106 | 0.48235 | 3.4902 | 0.65976 | 3.4461 | 0.48232 | 3.5066
POCU | Port Curtis | CA | POCU_66kV_BUS 2 | 66 | 11.8967 | 1359.974 | 11.8986 | 453.3959 | 11.9516 | 12.0757 | 460.1445 | 11.7152 | 446.4106 | 0.48235 | 3.4902 | 0.65976 | 3.4461 | 0.48232 | 3.5066
POVE | Point Vernon | WB | POVE_11kV_BUS 1 | 11 | 12.7617 | 243.1422 | 16.3756 | 103.9993 | 23.0852 | 15.5198 | 98.5639 | 16.4047 | 104.1837 | 0.09979 | 0.53829 | 0.00756 | 0.18189 | 0.09945 | 0.54292
POVE | Point Vernon | WB | POVE_11kV_BUS 2 | 11 | 12.7617 | 243.1422 | 16.3756 | 103.9993 | 23.0852 | 15.5198 | 98.5639 | 16.4047 | 104.1837 | 0.09979 | 0.53829 | 0.00756 | 0.18189 | 0.09945 | 0.54292
POVE | Point Vernon | WB | POVE_66kV_BUS 1 | 66 | 3.163 | 361.5787 | 2.0611 | 78.5374 | 1.5421 | 2.8375 | 108.1215 | 2.8277 | 107.7483 | 3.3205 | 12.8303 | 8.7353 | 33.2221 | 3.308 | 12.9971
POZI | Pozieres | SW | POZI_11kV_BUS 1 | 11 | 2.4082 | 45.8814 | 3.1098 | 19.75 | 4.3631 | 2.8112 | 17.8534 | 3.2117 | 20.397 | 1.0768 | 2.6942 | 0.0491 | 0.98195 | 1.0754 | 2.6945
POZI | Pozieres | SW | POZI_11kV_BUS 2 | 11 | 2.4082 | 45.8814 | 3.1098 | 19.75 | 4.3631 | 2.8112 | 17.8534 | 3.2117 | 20.397 | 1.0768 | 2.6942 | 0.0491 | 0.98195 | 1.0754 | 2.6945
POZI | Pozieres | SW | POZI_33kV_BUS 1 | 33 | 1.1663 | 66.6609 | 0.59083 | 11.2568 | 0.38487 | 1.1104 | 21.1567 | 0.93892 | 17.8889 | 9.2496 | 15.4098 | 64.5071 | 35.8085 | 9.2364 | 15.4131
POZI | Pozieres | SW | POZI_33kV_BUS 2 | 33 | 1.1663 | 66.6609 | 0.59083 | 11.2568 | 0.38487 | 1.1104 | 21.1567 | 0.93892 | 17.8889 | 9.2496 | 15.4098 | 64.5071 | 35.8085 | 9.2364 | 15.4131
POZI | Pozieres | SW | POZI_33kV_BUS 3 | 33 | 1.1663 | 66.6609 | 0.59083 | 11.2568 | 0.38487 | 1.1104 | 21.1567 | 0.93892 | 17.8889 | 9.2496 | 15.4098 | 64.5071 | 35.8085 | 9.2364 | 15.4131
PROS | Proserpine T039 | MK | PROS_66kV_BUS 1 | 66 | 5.6842 | 649.7941 | 7.3419 | 279.7659 | 10.1879 | 6.8526 | 261.1198 | 7.3229 | 279.0407 | 2.0941 | 7.0705 | 0.30795 | 2.4712 | 2.0681 | 6.992
PROS | Proserpine T039 | MK | PROS_66kV_BUS 2 | 66 | 5.6842 | 649.7941 | 7.3419 | 279.7659 | 10.1879 | 6.8526 | 261.1198 | 7.3229 | 279.0407 | 2.0941 | 7.0705 | 0.30795 | 2.4712 | 2.0681 | 6.992
PROT | Proston | WB | PROT_11kV_BUS 1 | 11 | 2.1841 | 41.6133 | 2.5494 | 16.191 | 3.0374 | 2.2247 | 14.1285 | 2.6115 | 16.5852 | 1.3658 | 2.8926 | 0.2622 | 1.872 | 1.365 | 2.8928
PROT | Proston | WB | PROT_11kV_BUS 2 | 11 | 2.1841 | 41.6133 | 2.5494 | 16.191 | 3.0374 | 2.2247 | 14.1285 | 2.6115 | 16.5852 | 1.3658 | 2.8926 | 0.2622 | 1.872 | 1.365 | 2.8928
PROT | Proston | WB | PROT_66kV_BUS STRUNG | 66 | 0.77463 | 88.5522 | 0.59555 | 22.6936 | 0.47697 | 0.64978 | 24.7598 | 0.76933 | 29.3155 | 39.7309 | 36.7434 | 49.6842 | 93.6022 | 39.7014 | 36.75
PURR | Purrawunda (TF1) | SW | PURR_11kV_BUS 1 | 11 | 3.097 | 59.0057 | 3.9981 | 25.3914 | 5.6149 | 3.6626 | 23.2608 | 4.0911 | 25.982 | 0.72211 | 2.1374 | 0.03773 | 0.75469 | 0.72206 | 2.1369
PURR | Purrawunda (TF2) | SW | PURR_11kV_BUS 2 | 11 | 3.097 | 59.0057 | 3.9981 | 25.3914 | 5.6149 | 3.6626 | 23.2608 | 4.0911 | 25.982 | 0.72211 | 2.1374 | 0.03773 | 0.75469 | 0.72206 | 2.1369
PURR | Purrawunda | SW | PURR_33kV_BUS 1 | 33 | 1.5096 | 86.2858 | 0.61447 | 11.7073 | 0.37673 | 1.4051 | 26.7717 | 1.2312 | 23.4576 | 6.1594 | 12.4441 | 64.4983 | 42.7317 | 6.1589 | 12.4397
PURR | Purrawunda | SW | PURR_33kV_BUS 2 | 33 | 1.5096 | 86.2858 | 0.61447 | 11.7073 | 0.37673 | 1.4051 | 26.7717 | 1.2312 | 23.4576 | 6.1594 | 12.4441 | 64.4983 | 42.7317 | 6.1589 | 12.4397
PURR | Purrawunda | SW | PURR_33kV_BUS 3 | 33 | 1.5096 | 86.2858 | 0.61447 | 11.7073 | 0.37673 | 1.4051 | 26.7717 | 1.2312 | 23.4576 | 6.1594 | 12.4441 | 64.4983 | 42.7317 | 6.1589 | 12.4397
QUIL | Quilpie (TF1) | SW | QUIL_11kV_BUS T1 | 11 | 0.85375 | 16.2661 | 1.208 | 7.6719 | 2.0592 | 1.2097 | 7.6828 | 1.3229 | 8.4013 | 3.9724 | 7.154 | 0.05426 | 1.0851 | 3.9706 | 7.1572
QUIL | Quilpie (TF2) | SW | QUIL_11kV_BUS T2 | 11 | 0.85375 | 16.2661 | 1.208 | 7.6719 | 2.0592 | 1.2097 | 7.6828 | 1.3229 | 8.4013 | 3.9724 | 7.154 | 0.05426 | 1.0851 | 3.9706 | 7.1572
QUIL | Quilpie | SW | QUIL_66kV_BUS | 66 | 0.16118 | 18.4258 | 0.07788 | 2.9675 | 0.05112 | 0.13703 | 5.2214 | 0.1466 | 5.5863 | 141.0517 | 218.4776 | 387.2997 | 1032.3941 | 140.9877 | 218.5935
RAGL | Raglan | CA | RAGL_22kV_TEF T1 | 22 | 2.9345 | 111.8177 | 3.304 | 41.9663 | 3.7645 | 2.9623 | 37.6262 | 3.3502 | 42.5531 | 1.4005 | 4.5508 | 0.24239 | 3.2123 | 1.4006 | 4.5531
RAGL | Raglan | CA | RAGL_22kV_TEF T2 | 22 | 2.9345 | 111.8177 | 3.304 | 41.9663 | 3.7645 | 2.9623 | 37.6262 | 3.3502 | 42.5531 | 1.4005 | 4.5508 | 0.24239 | 3.2123 | 1.4006 | 4.5531
RAGL | Raglan | CA | RAGL_66kV_TEF T1 | 66 | 2.6313 | 300.7944 | 1.7989 | 68.5458 | 1.3501 | 2.193 | 83.564 | 2.5454 | 96.9921 | 10.4233 | 12.0467 | 14.5318 | 36.1766 | 10.4241 | 12.0677
RAGL | Raglan | CA | RAGL_66kV_TEF T2 | 66 | 2.6313 | 300.7944 | 1.7989 | 68.5458 | 1.3501 | 2.193 | 83.564 | 2.5454 | 96.9921 | 10.4233 | 12.0467 | 14.5318 | 36.1766 | 10.4241 | 12.0677
RAPS | RAAF Power Station | NQ | RAPS_11kV_BUS 1 | 11 | 9.0259 | 171.9663 | 8.8044 | 55.9158 | 8.5456 | 9.5742 | 60.8043 | 8.1671 | 51.8682 | 0.19867 | 0.74806 | 0.41697 | 0.7402 | 0.18386 | 0.75383
RASM | Rasmussen | NQ | RASM_11kV_BUS 1 | 11 | 14.2801 | 272.0731 | 15.5291 | 98.6229 | 16.9215 | 14.775 | 93.8341 | 15.2207 | 96.6644 | 0.04259 | 0.48735 | 0.01191 | 0.37377 | 0.0411 | 0.48508
RASM | Rasmussen | NQ | RASM_11kV_BUS 2 | 11 | 14.2801 | 272.0731 | 15.5291 | 98.6229 | 16.9215 | 14.775 | 93.8341 | 15.2207 | 96.6644 | 0.04259 | 0.48735 | 0.01191 | 0.37377 | 0.0411 | 0.48508
RASM | Rasmussen | NQ | RASM_66kV_BUS 1 | 66 | 9.2378 | 1056.028 | 6.5278 | 248.7438 | 5.0379 | 8.3455 | 318.0071 | 8.4433 | 321.7337 | 1.1279 | 4.395 | 2.2449 | 9.9504 | 1.1058 | 4.39
RASM | Rasmussen | NQ | RASM_66kV_BUS 2 | 66 | 9.2378 | 1056.028 | 6.5278 | 248.7438 | 5.0379 | 8.3455 | 318.0071 | 8.4433 | 321.7337 | 1.1279 | 4.395 | 2.2449 | 9.9504 | 1.1058 | 4.39
RASM | Rasmussen | NQ | RASM_66kV_BUS 3 | 66 | 9.2378 | 1056.028 | 6.5278 | 248.7438 | 5.0379 | 8.3455 | 318.0071 | 8.4433 | 321.7337 | 1.1279 | 4.395 | 2.2449 | 9.9504 | 1.1058 | 4.39
RAVE | Ravenshoe | FN | RAVE_22kV_BUS 1 | 22 | 2.7802 | 105.9391 | 3.0741 | 39.0461 | 3.435 | 2.7918 | 35.4603 | 3.1131 | 39.5419 | 1.0775 | 4.9087 | 0.00054 | 3.6254 | 0.97687 | 4.9454
RAVE | Ravenshoe | FN | RAVE_66kV_BUS 1 | 66 | 1.4195 | 162.2736 | 0.82427 | 31.409 | 0.58124 | 1.2278 | 46.7857 | 1.2937 | 49.2949 | 11.4012 | 27.2381 | 23.1827 | 90.8217 | 11.1361 | 27.4832
RAVN | Ravenswood | NQ | RAVN_11kV_TEF T1 | 11 | 2.0545 | 39.1431 | 2.1503 | 13.6564 | 2.2549 | 2.0712 | 13.154 | 2.1409 | 13.5966 | 0.57503 | 3.3514 | 0.32962 | 2.9304 | 0.57433 | 3.3517
RAVN | Ravenswood | NQ | RAVN_66kV_TEF T1 | 66 | 2.3893 | 273.1336 | 1.5915 | 60.6455 | 1.1854 | 2.0384 | 77.6744 | 2.2609 | 86.1533 | 8.835 | 15.156 | 12.7783 | 42.594 | 8.8098 | 15.1681
RGSS | Ravenswood Gold | NQ | RGSS_66kV_BUS 1 | 66 | 2.2992 | 262.8365 | 1.5297 | 58.2884 | 1.1382 | 1.9579 | 74.6076 | 2.1783 | 83.0047 | 9.3376 | 15.6575 | 13.4387 | 44.3563 | 9.3123 | 15.67
RICH | Richmond | NQ | RICH_33kV_BUS 1 | 33 | 0.8289 | 47.3778 | 1.0442 | 19.8945 | 1.446 | 0.9587 | 18.2657 | 1.0715 | 20.415 | 8.2 | 23.9174 | 0.57904 | 9.3679 | 8.2645 | 24.4648
RICH | Richmond | NQ | RICH_33kV_BUS 2 | 33 | 0.8289 | 47.3778 | 1.0442 | 19.8945 | 1.446 | 0.9587 | 18.2657 | 1.0715 | 20.415 | 8.2 | 23.9174 | 0.57904 | 9.3679 | 8.2645 | 24.4648
RICH | Richmond | NQ | RICH_33kV_BUS 3 | 33 | 0.8289 | 47.3778 | 1.0442 | 19.8945 | 1.446 | 0.9587 | 18.2657 | 1.0715 | 20.415 | 8.2 | 23.9174 | 0.57904 | 9.3679 | 8.2645 | 24.4648
RICH | Richmond | NQ | RICH_66kV_BUS 1 | 66 | 0.52441 | 59.9481 | 0.60685 | 23.1242 | 0.73707 | 0.53435 | 20.3614 | 0.62697 | 23.8907 | 31.5557 | 73.4364 | 4.406 | 46.7521 | 31.8135 | 75.626
RICH | Richmond | NQ | RICH_66kV_BUS 2 | 66 | 0.52441 | 59.9481 | 0.60685 | 23.1242 | 0.73707 | 0.53435 | 20.3614 | 0.62697 | 23.8907 | 31.5557 | 73.4364 | 4.406 | 46.7521 | 31.8135 | 75.626
ROEA | Roma East | SW | ROEA_11kV_BUS 1 | 11 | 5.4238 | 103.3373 | 6.3853 | 40.5522 | 7.7708 | 5.8819 | 37.3553 | 6.2987 | 40.002 | 0.23674 | 1.2661 | 0.03537 | 0.70743 | 0.23496 | 1.2693
ROEA | Roma East | SW | ROEA_11kV_BUS 2 | 11 | 5.4238 | 103.3373 | 6.3853 | 40.5522 | 7.7708 | 5.8819 | 37.3553 | 6.2987 | 40.002 | 0.23674 | 1.2661 | 0.03537 | 0.70743 | 0.23496 | 1.2693
ROEA | Roma East | SW | ROEA_33kV_BUS 1 | 33 | 3.9213 | 224.1355 | 3.4289 | 65.3295 | 3.0565 | 3.6696 | 69.9155 | 3.7685 | 71.8004 | 1.8123 | 5.028 | 2.2063 | 7.3052 | 1.7963 | 5.057
ROEA | Roma East | SW | ROEA_33kV_BUS 2 | 33 | 3.9213 | 224.1355 | 3.4289 | 65.3295 | 3.0565 | 3.6696 | 69.9155 | 3.7685 | 71.8004 | 1.8123 | 5.028 | 2.2063 | 7.3052 | 1.7963 | 5.057
ROGL | Rockhampton T023 (TF2) | CA | ROGL_11kV_BUS RH | 11 | 17.3861 | 331.2505 | 18.881 | 119.9106 | 20.6966 | 18.1709 | 115.4009 | 18.3555 | 116.573 | 0.02519 | 0.40103 | 0.01367 | 0.30539 | 0.02522 | 0.40174
ROGL | Rockhampton T023 | CA | ROGL_66kV_BUS 4 | 66 | 12.0879 | 1381.8359 | 14.3182 | 545.5971 | 17.7152 | 13.828 | 526.9167 | 13.5667 | 516.9597 | 0.41445 | 3.4428 | 0.28522 | 1.8002 | 0.41563 | 3.4684
ROGL | Rockhampton T023 (TF1) | CA | ROGL_11kV_BUS LH | 11 | 17.3861 | 331.2505 | 18.881 | 119.9106 | 20.6966 | 18.1709 | 115.4009 | 18.3555 | 116.573 | 0.02519 | 0.40103 | 0.01367 | 0.30539 | 0.02522 | 0.40174
ROLE | Rolleston | CA | ROLE_132kV_TEF T1 | 132 | 1.3427 | 306.9788 | 1.536 | 117.0556 | 1.7889 | 1.3906 | 105.9769 | 1.5395 | 117.3298 | 13.9122 | 60.8665 | 1.442 | 39.3619 | 13.9322 | 60.8704
ROLE | Rolleston (TF 1) | CA | ROLE_22kV_BUS 1 | 22 | 4.4824 | 170.8015 | 4.9904 | 63.3861 | 5.5899 | 5.1263 | 65.113 | 4.4138 | 56.0624 | 0.38645 | 3.093 | 0.849 | 2.055 | 0.38701 | 3.0932
ROLE | Rolleston (TF 2) | CA | ROLE_22kV_BUS 2 | 22 | 4.4824 | 170.8015 | 4.9904 | 63.3861 | 5.5899 | 5.1263 | 65.113 | 4.4138 | 56.0624 | 0.38645 | 3.093 | 0.849 | 2.055 | 0.38701 | 3.0932
ROLE | Rolleston | CA | ROLE_66kV_BUS 1 | 66 | 2.1089 | 241.0791 | 2.6912 | 102.547 | 3.7128 | 2.5154 | 95.8489 | 2.69 | 102.5018 | 3.6245 | 19.5426 | 0.15475 | 7.0491 | 3.6295 | 19.5435
ROLE | Rolleston | CA | ROLE_66kV_BUS 2 | 66 | 2.1089 | 241.0791 | 2.6912 | 102.547 | 3.7128 | 2.5154 | 95.8489 | 2.69 | 102.5018 | 3.6245 | 19.5426 | 0.15475 | 7.0491 | 3.6295 | 19.5435
ROLE | Rolleston | CA | ROLE_66kV_BUS 3 | 66 | 2.1089 | 241.0791 | 2.6912 | 102.547 | 3.7128 | 2.5154 | 95.8489 | 2.69 | 102.5018 | 3.6245 | 19.5426 | 0.15475 | 7.0491 | 3.6295 | 19.5435
ROLL | Rollingstone | NQ | ROLL_11kV_TEF T1 | 11 | 1.7509 | 33.3597 | 1.8528 | 11.7671 | 1.9643 | 1.744 | 11.0756 | 1.8673 | 11.8587 | 0.76014 | 3.9168 | 0.24091 | 3.3399 | 0.75881 | 3.9169
ROLL | Rollingstone | NQ | ROLL_66kV_TEF T1 | 66 | 1.5001 | 171.4842 | 1.0386 | 39.5754 | 0.78202 | 1.2451 | 47.4438 | 1.4609 | 55.668 | 18.6924 | 20.7689 | 24.9091 | 62.309 | 18.6447 | 20.7715
ROMA | Roma T083 (TF1) | SW | ROMA_132kV_BUS 1 | 132 | 3.5702 | 816.2558 | 4.2236 | 321.882 | 5.2599 | 3.8645 | 294.5157 | 4.2278 | 322.2008 | 6.1335 | 22.6661 | 0.86966 | 12.3397 | 5.8774 | 23.1304
ROMA | Roma T083 (TF2) | SW | ROMA_132kV_BUS 2 | 132 | 3.5702 | 816.2558 | 4.2236 | 321.882 | 5.2599 | 3.8645 | 294.5157 | 4.2278 | 322.2008 | 6.1335 | 22.6661 | 0.86966 | 12.3397 | 5.8774 | 23.1304
ROMA | Roma T083 | SW | ROMA_33kV_BUS 1 | 33 | 7.2945 | 416.9345 | 9.1782 | 174.8672 | 12.5179 | 8.6687 | 165.1617 | 9.095 | 173.2827 | 0.42453 | 2.8416 | 0.03162 | 1.0834 | 0.40852 | 2.8706
ROMA | Roma T083 | SW | ROMA_33kV_BUS 2 | 33 | 7.2945 | 416.9345 | 9.1782 | 174.8672 | 12.5179 | 8.6687 | 165.1617 | 9.095 | 173.2827 | 0.42453 | 2.8416 | 0.03162 | 1.0834 | 0.40852 | 2.8706
ROMA | Roma T083 | SW | ROMA_66kV_BUS | 66 | 3.7043 | 423.4558 | 4.8081 | 183.2121 | 6.938 | 4.6444 | 176.9754 | 4.797 | 182.7901 | 1.6729 | 11.1913 | 0.18814 | 3.4239 | 1.6089 | 11.3074
ROPL | Ross Plains (TF1) | NQ | ROPL_11kV_BUS 1 | 11 | 13.4006 | 255.316 | 14.3301 | 91.0085 | 15.3939 | 13.7923 | 87.5927 | 14.0588 | 89.2856 | 0.04384 | 0.51947 | 0.02082 | 0.41961 | 0.04333 | 0.51943
ROPL | Ross Plains (TF2) | NQ | ROPL_11kV_BUS 2 | 11 | 13.4006 | 255.316 | 14.3301 | 91.0085 | 15.3939 | 13.7923 | 87.5927 | 14.0588 | 89.2856 | 0.04384 | 0.51947 | 0.02082 | 0.41961 | 0.04333 | 0.51943
ROPL | Ross Plains | NQ | ROPL_66kV_BUS 1 | 66 | 11.3614 | 1298.7794 | 8.3758 | 319.1591 | 6.6251 | 10.388 | 395.8376 | 10.3867 | 395.7857 | 0.82905 | 3.595 | 1.6832 | 7.4522 | 0.81067 | 3.5937
ROPL | Ross Plains | NQ | ROPL_66kV_BUS 2 | 66 | 11.3614 | 1298.7794 | 8.3758 | 319.1591 | 6.6251 | 10.388 | 395.8376 | 10.3867 | 395.7857 | 0.82905 | 3.595 | 1.6832 | 7.4522 | 0.81067 | 3.5937
ROSE | ROSE Rosella (TF1) | MK | ROSE_11kV_BUS 1 | 11 | 5.8155 | 110.8006 | 6.5006 | 41.2846 | 7.3723 | 6.0465 | 38.4002 | 6.4268 | 40.8159 | 0.19259 | 1.1857 | 0.04115 | 0.82247 | 0.19244 | 1.1875
ROSE | ROSE Rosella (TF2) | MK | ROSE_11kV_BUS 2 | 11 | 5.8155 | 110.8006 | 6.5006 | 41.2846 | 7.3723 | 6.0465 | 38.4002 | 6.4268 | 40.8159 | 0.19259 | 1.1857 | 0.04115 | 0.82247 | 0.19244 | 1.1875
ROSE | Rosella (TF1 with MACK G1 ) | MK | ROSE_33kV_BUS 1 | 33 | 5.9169 | 338.1965 | 3.7929 | 72.2637 | 2.7919 | 5.1294 | 97.7289 | 5.4704 | 104.2259 | 1.363 | 3.2693 | 2.2862 | 9.2468 | 1.3616 | 3.2853
ROSE | Rosella (TF1 with MACK G1 ) | MK | ROSE_33kV_BUS 1 | 33 | 5.9169 | 338.1965 | 3.7929 | 72.2637 | 2.7919 | 5.1294 | 97.7289 | 5.4704 | 104.2259 | 1.363 | 3.2693 | 2.2862 | 9.2468 | 1.3616 | 3.2853
ROSE | ROSE Rosella (TF2) | MK | ROSE_33kV_BUS 2 | 33 | 5.9169 | 338.1965 | 3.7929 | 72.2637 | 2.7919 | 5.1294 | 97.7289 | 5.4704 | 104.2259 | 1.363 | 3.2693 | 2.2862 | 9.2468 | 1.3616 | 3.2853
ROSO | Rockhampton South | CA | ROSO_66kV_TEF T1 | 66 | 10.0183 | 1145.2508 | 9.8872 | 376.7513 | 9.8165 | 10.0583 | 383.2722 | 9.8463 | 375.1939 | 0.83725 | 4.0993 | 1.0178 | 4.2056 | 0.83849 | 4.125
ROSO | Rockhampton South | CA | ROSO_66kV_TEF T2 | 66 | 10.0183 | 1145.2508 | 9.8872 | 376.7513 | 9.8165 | 10.0583 | 383.2722 | 9.8463 | 375.1939 | 0.83725 | 4.0993 | 1.0178 | 4.2056 | 0.83849 | 4.125
ROSO | Rockhampton South (TF1) | CA | ROSO_11kV_BUS LH | 11 | 18.0727 | 344.3313 | 20.0584 | 127.388 | 22.5768 | 19.0505 | 120.987 | 19.5279 | 124.0191 | 0.03736 | 0.38474 | 0.0141 | 0.27087 | 0.03739 | 0.38546
ROSO | Rockhampton South (TF2) | CA | ROSO_11kV_BUS RH | 11 | 18.0727 | 344.3313 | 20.0584 | 127.388 | 22.5768 | 19.0505 | 120.987 | 19.5279 | 124.0191 | 0.03736 | 0.38474 | 0.0141 | 0.27087 | 0.03739 | 0.38546
ROSS | H013 Ross | NQ | ROSS_132kV_BUS 2 | 132 | 20.0813 | 4591.2004 | 22.3996 | 1707.0818 | 25.3783 | 21.6836 | 1652.5109 | 21.3545 | 1627.4347 | 0.57185 | 4.1353 | 0.44209 | 2.8365 | 0.52923 | 4.1493
ROSS | H013 Ross | NQ | ROSS_132kV_BUS 3 | 132 | 20.0813 | 4591.2004 | 22.3996 | 1707.0818 | 25.3783 | 21.6836 | 1652.5109 | 21.3545 | 1627.4347 | 0.57185 | 4.1353 | 0.44209 | 2.8365 | 0.52923 | 4.1493
ROSS | H013 Ross | NQ | ROSS_132kV_BUS 4 | 132 | 20.0813 | 4591.2004 | 22.3996 | 1707.0818 | 25.3783 | 21.6836 | 1652.5109 | 21.3545 | 1627.4347 | 0.57185 | 4.1353 | 0.44209 | 2.8365 | 0.52923 | 4.1493
ROST | Rocky Street | WB | ROST_11kV_BUS 1 | 11 | 11.535 | 219.7703 | 12.7966 | 81.2696 | 14.413 | 12.1345 | 77.0644 | 12.4844 | 79.2865 | 0.05772 | 0.60293 | 0.01796 | 0.42476 | 0.05678 | 0.60484
ROST | Rocky Street | WB | ROST_11kV_BUS 2 | 11 | 11.535 | 219.7703 | 12.7966 | 81.2696 | 14.413 | 12.1345 | 77.0644 | 12.4844 | 79.2865 | 0.05772 | 0.60293 | 0.01796 | 0.42476 | 0.05678 | 0.60484
ROST | Rocky Street | WB | ROST_66kV_TEF T1 | 66 | 6.3788 | 729.1922 | 6.179 | 235.4499 | 6.0443 | 6.2551 | 238.3509 | 6.3084 | 240.3836 | 1.4311 | 6.4139 | 1.4035 | 7.0109 | 1.3974 | 6.4829
ROST | Rocky Street | WB | ROST_66kV_TEF T2 | 66 | 6.3788 | 729.1922 | 6.179 | 235.4499 | 6.0443 | 6.2551 | 238.3509 | 6.3084 | 240.3836 | 1.4311 | 6.4139 | 1.4035 | 7.0109 | 1.3974 | 6.4829
ROWE | Roma West (TF1) | SW | ROWE_11kV_BUS 1 | 11 | 3.3242 | 63.3347 | 3.85 | 24.4509 | 4.5687 | 3.5042 | 22.2545 | 3.837 | 24.3681 | 0.54541 | 2.0296 | 0.1127 | 1.247 | 0.54363 | 2.0328
ROWE | Roma West (TF2) | SW | ROWE_11kV_BUS 2 | 11 | 3.3242 | 63.3347 | 3.85 | 24.4509 | 4.5687 | 3.5042 | 22.2545 | 3.837 | 24.3681 | 0.54541 | 2.0296 | 0.1127 | 1.247 | 0.54363 | 2.0328
ROWE | Roma West | SW | ROWE_33kV_BUS 1 | 33 | 2.6041 | 148.8469 | 1.9527 | 37.2044 | 1.5589 | 2.2798 | 43.4355 | 2.4846 | 47.338 | 3.8944 | 7.043 | 5.2174 | 15.3467 | 3.8784 | 7.072
ROWE | Roma West | SW | ROWE_33kV_BUS 2 | 33 | 2.6041 | 148.8469 | 1.9527 | 37.2044 | 1.5589 | 2.2798 | 43.4355 | 2.4846 | 47.338 | 3.8944 | 7.043 | 5.2174 | 15.3467 | 3.8784 | 7.072
RYWU | Rywung (Regulated) | SW | RYWU_33kV_BUS R1 Downstream | 33 | 1.0008 | 57.2013 | 0.76656 | 14.6049 | 0.60617 | 0.81315 | 15.4926 | 1.0128 | 19.2956 | 16.6465 | 12.7074 | 19.3757 | 37.4712 | 16.6184 | 12.7208
RYWU | Rywung (Unregulated) | SW | RYWU_33kV_BUS R1 Upstream | 33 | 1.0287 | 58.7997 | 0.7871 | 14.9963 | 0.62021 | 0.8295 | 15.804 | 1.0453 | 19.9161 | 16.6016 | 11.809 | 19.3286 | 36.5692 | 16.5735 | 11.8224
SAGE | St. George (TF1) | SW | SAGE_33kV_BUS 1 | 33 | 0.77106 | 44.072 | 1.1044 | 21.0425 | 1.9465 | 1.1516 | 21.9412 | 1.2083 | 23.0209 | 9.9319 | 25.3015 | 0.1516 | 2.6684 | 9.9159 | 25.3304
SAGE | St. George (TF2) | SW | SAGE_33kV_BUS 2 | 33 | 0.77106 | 44.072 | 1.1044 | 21.0425 | 1.9465 | 1.1516 | 21.9412 | 1.2083 | 23.0209 | 9.9319 | 25.3015 | 0.1516 | 2.6684 | 9.9159 | 25.3304
SAGE | St. George | SW | SAGE_66kV_BUS 1 | 66 | 0.42278 | 48.3302 | 0.5879 | 22.4022 | 0.96352 | 0.57969 | 22.089 | 0.62946 | 23.9858 | 39.2277 | 91.0545 | 0.98039 | 16.3977 | 39.1637 | 91.1702
SAGE | St. George | SW | SAGE_66kV_BUS 2 | 66 | 0.42278 | 48.3302 | 0.5879 | 22.4022 | 0.96352 | 0.57969 | 22.089 | 0.62946 | 23.9858 | 39.2277 | 91.0545 | 0.98039 | 16.3977 | 39.1637 | 91.1702
SAGE | St. George | SW | SAGE_66kV_BUS 3 | 66 | 0.42278 | 48.3302 | 0.5879 | 22.4022 | 0.96352 | 0.57969 | 22.089 | 0.62946 | 23.9858 | 39.2277 | 91.0545 | 0.98039 | 16.3977 | 39.1637 | 91.1702
SAGT | St. George Town (TF1) | SW | SAGT_11kV_BUS ALFRED ST EAST | 11 | 1.5934 | 30.3587 | 2.159 | 13.7117 | 3.3383 | 2.0553 | 13.053 | 2.2706 | 14.4206 | 1.6234 | 4.0727 | 0.04913 | 0.98255 | 1.6216 | 4.0759
SAGT | St. George Town (TF2) | SW | SAGT_11kV_BUS ALFRED ST WEST | 11 | 1.5934 | 30.3587 | 2.159 | 13.7117 | 3.3383 | 2.0553 | 13.053 | 2.2706 | 14.4206 | 1.6234 | 4.0727 | 0.04913 | 0.98255 | 1.6216 | 4.0759
SAGT | St. George Town (TF3) | SW | SAGT_11kV_BUS SCOTT ST | 11 | 1.5934 | 30.3587 | 2.159 | 13.7117 | 3.3383 | 2.0553 | 13.053 | 2.2706 | 14.4206 | 1.6234 | 4.0727 | 0.04913 | 0.98255 | 1.6216 | 4.0759
SAGT | St. George Town | SW | SAGT_33kV_BUS | 33 | 0.67147 | 38.3796 | 0.82784 | 15.7725 | 1.0797 | 0.78153 | 14.8901 | 0.80511 | 15.3395 | 14.1682 | 27.8116 | 5.3444 | 12.4296 | 14.1522 | 27.8405
SARI | Sarina (TF1) | MK | SARI_11kV_BUS 1 | 11 | 11.0655 | 210.8268 | 10.9998 | 69.858 | 12.3496 | 10.7172 | 68.0632 | 11.4777 | 72.8931 | 0.12217 | 0.61939 | 0.02788 | 0.56577 | 0.12021 | 0.70087
SARI | Sarina (TF2) | MK | SARI_11kV_BUS 2 | 11 | 11.0655 | 210.8268 | 10.9998 | 69.858 | 12.3496 | 10.7172 | 68.0632 | 11.4777 | 72.8931 | 0.12217 | 0.61939 | 0.02788 | 0.56577 | 0.12021 | 0.70087
SARI | Sarina | MK | SARI_33kV_BUS 1 | 33 | 5.3098 | 303.4982 | 3.1033 | 59.1266 | 2.2589 | 4.5528 | 86.7426 | 4.7471 | 90.445 | 1.3687 | 3.7021 | 3.0214 | 11.8355 | 1.4285 | 3.8689
SARI | Sarina | MK | SARI_33kV_BUS 2 | 33 | 5.3098 | 303.4982 | 3.1033 | 59.1266 | 2.2589 | 4.5528 | 86.7426 | 4.7471 | 90.445 | 1.3687 | 3.7021 | 3.0214 | 11.8355 | 1.4285 | 3.8689
SAUN | Saunders | NQ | SAUN_11kV_TEF T1 | 11 | 3.7537 | 71.5173 | 3.9066 | 24.8101 | 4.0708 | 3.7708 | 23.948 | 3.899 | 24.7622 | 0.22246 | 1.8478 | 0.10015 | 1.6416 | 0.22114 | 1.8478
SAUN | Saunders | NQ | SAUN_66kV_TEF T1 | 66 | 4.8568 | 555.2086 | 3.5158 | 133.9704 | 2.7339 | 4.1932 | 159.7834 | 4.6494 | 177.1654 | 4.4034 | 7.4224 | 5.7923 | 17.8249 | 4.3557 | 7.4249
SHUT | Shutehaven | MK | SHUT_22kV_TEF T1 | 22 | 3.5607 | 135.6826 | 4.2961 | 54.5685 | 5.3777 | 3.8829 | 49.3197 | 4.293 | 54.5281 | 0.95595 | 3.8056 | 0.08395 | 1.9507 | 0.95108 | 3.7949
SHUT | Shutehaven | MK | SHUT_66kV_TEF T1 | 66 | 2.2714 | 259.6586 | 1.6544 | 63.0421 | 1.2899 | 1.9812 | 75.4939 | 2.1638 | 82.4523 | 7.8488 | 16.7012 | 9.9895 | 38.2443 | 7.8049 | 16.6048
SKIA | Skid 'A' (Mt Bassett) | MK | SKIA_11kV_TEF T1 | 11 | 3.323 | 63.3118 | 3.4845 | 22.1294 | 3.6607 | 3.3066 | 20.9994 | 3.5105 | 22.295 | 0.22193 | 2.0906 | 0.00242 | 1.8156 | 0.22184 | 2.0919
SKIA | Skid 'A' (Mt Bassett) | MK | SKIA_33kV_TEF T1 | 33 | 7.5967 | 434.2068 | 6.2481 | 119.0426 | 5.3227 | 6.9944 | 133.2606 | 7.1794 | 136.785 | 0.908 | 2.6051 | 1.2745 | 4.3545 | 0.90721 | 2.6172
SKIE | Skid 'E' (Chinchilla) | SW | SKIE_11kV_TEF T1 | 11 | 3.1964 | 60.9004 | 3.3908 | 21.5346 | 3.6083 | 3.2029 | 20.3413 | 3.4017 | 21.6038 | 0.23459 | 2.173 | 0.00121 | 1.8156 | 0.23146 | 2.1745
SKIE | Skid 'E' (Chinchilla) | SW | SKIE_33kV_TEF T1 | 33 | 5.9891 | 342.3244 | 5.3972 | 102.8308 | 4.8997 | 5.4509 | 103.8539 | 6.0047 | 114.4045 | 1.0219 | 3.3469 | 0.54136 | 4.658 | 0.9938 | 3.3603
SKIF | Skid 'F' (Broxburn) | SW | F2620 COPPS HILL | 11 | 3.193 | 60.8355 | 3.9382 | 25.0112 | 5.0535 | 3.5378 | 22.4679 | 3.952 | 25.0987 | 0.64969 | 2.0894 | 0.06371 | 0.98692 | 0.63423 | 2.0718
SKIF | Skid 'F' (Broxburn) | SW | BROX_AB13920 | 33 | 1.9363 | 110.6742 | 1.289 | 24.5592 | 0.94735 | 1.6733 | 31.8799 | 1.834 | 34.9417 | 5.2738 | 9.4534 | 7.9985 | 26.4215 | 5.1347 | 9.2945
SKIJ | Skid J | MK | SKIJ_11kV_BUS 1 | 11 | 6.0643 | 115.5404 | 6.3221 | 40.1505 | 6.6136 | 6.1779 | 39.235 | 6.2298 | 39.5648 | 0.0838 | 1.149 | 0.05779 | 1.0077 | 0.08286 | 1.1509
SKIJ | Skid J | MK | SKIJ_66kV_TEF T1 | 66 | 8.1053 | 926.5579 | 9.9703 | 379.9197 | 13.1411 | 9.3488 | 356.2364 | 9.8476 | 375.2422 | 0.93616 | 5.0864 | 0.13286 | 2.2164 | 0.90247 | 5.1554
SOBL | South Blackwater | CA | SOBL_22kV_TEF T1 | 22 | 1.8291 | 69.698 | 1.9727 | 25.056 | 2.1389 | 1.8811 | 23.8929 | 1.9413 | 24.6583 | 1.1289 | 7.5549 | 0.55518 | 5.9555 | 1.1307 | 7.5509
SOBL | South Blackwater (ex 6014) | CA | SOBL_66kV_BUS 1 | 66 | 2.741 | 313.3438 | 1.8728 | 71.365 | 1.4195 | 2.4391 | 92.9434 | 2.519 | 95.9856 | 5.1639 | 14.3937 | 9.9563 | 35.2488 | 5.18 | 14.3579
SOBL | South Blackwater (ex 6014) | CA | SOBL_66kV_BUS 2 | 66 | 2.741 | 313.3438 | 1.8728 | 71.365 | 1.4195 | 2.4391 | 92.9434 | 2.519 | 95.9856 | 5.1639 | 14.3937 | 9.9563 | 35.2488 | 5.18 | 14.3579
SOBL | South Blackwater (ex 6061) | CA | SOBL_66kV_BUS 3 | 66 | 2.741 | 313.3438 | 1.8728 | 71.365 | 1.4195 | 2.4391 | 92.9434 | 2.519 | 95.9856 | 5.1639 | 14.3937 | 9.9563 | 35.2488 | 5.18 | 14.3579
SOBL | South Blackwater (ex 6061) | CA | SOBL_66kV_BUS 4 | 66 | 2.741 | 313.3438 | 1.8728 | 71.365 | 1.4195 | 2.4391 | 92.9434 | 2.519 | 95.9856 | 5.1639 | 14.3937 | 9.9563 | 35.2488 | 5.18 | 14.3579
SOBU | South Bundaberg | WB | SOBU_11kV_BUS 1 | 11 | 10.3041 | 196.3199 | 11.605 | 73.7019 | 13.3367 | 10.9192 | 69.3461 | 11.3407 | 72.0231 | 0.08316 | 0.67291 | 0.02325 | 0.44753 | 0.08241 | 0.67573
SOBU | South Bundaberg | WB | SOBU_11kV_BUS 2 | 11 | 10.3041 | 196.3199 | 11.605 | 73.7019 | 13.3367 | 10.9192 | 69.3461 | 11.3407 | 72.0231 | 0.08316 | 0.67291 | 0.02325 | 0.44753 | 0.08241 | 0.67573
SOBU | South Bundaberg | WB | SOBU_66kV_BUS 1 | 66 | 4.9931 | 570.7849 | 4.1209 | 157.0275 | 3.5406 | 4.6616 | 177.6312 | 4.6503 | 177.201 | 2.1569 | 8.1136 | 3.4813 | 13.1828 | 2.1297 | 8.2151
SOBU | South Bundaberg | WB | SOBU_66kV_BUS 2 | 66 | 4.9931 | 570.7849 | 4.1209 | 157.0275 | 3.5406 | 4.6616 | 177.6312 | 4.6503 | 177.201 | 2.1569 | 8.1136 | 3.4813 | 13.1828 | 2.1297 | 8.2151
SOBU | South Bundaberg | WB | SOBU_66kV_BUS 3 | 66 | 4.9931 | 570.7849 | 4.1209 | 157.0275 | 3.5406 | 4.6616 | 177.6312 | 4.6503 | 177.201 | 2.1569 | 8.1136 | 3.4813 | 13.1828 | 2.1297 | 8.2151
SOKO | South Kolan | WB | SOKO_11kV_BUS 1 | 11 | 7.8576 | 149.7078 | 8.6366 | 54.8501 | 9.6107 | 8.242 | 52.3435 | 8.4107 | 53.415 | 0.09111 | 0.88445 | 0.04222 | 0.6454 | 0.09042 | 0.8866
SOKO | South Kolan | WB | SOKO_11kV_BUS 2 | 11 | 7.8576 | 149.7078 | 8.6366 | 54.8501 | 9.6107 | 8.242 | 52.3435 | 8.4107 | 53.415 | 0.09111 | 0.88445 | 0.04222 | 0.6454 | 0.09042 | 0.8866
SOKO | South Kolan | WB | SOKO_66kV_BUS LOWER A | 66 | 4.7722 | 545.5412 | 3.9032 | 148.732 | 3.3244 | 4.4633 | 170.073 | 4.4222 | 168.5077 | 1.7601 | 8.6057 | 3.1051 | 14.2466 | 1.7351 | 8.6832
SOKO | South Kolan | WB | SOKO_66kV_BUS LOWER B | 66 | 4.7722 | 545.5412 | 3.9032 | 148.732 | 3.3244 | 4.4633 | 170.073 | 4.4222 | 168.5077 | 1.7601 | 8.6057 | 3.1051 | 14.2466 | 1.7351 | 8.6832
SOKO | South Kolan | WB | SOKO_66kV_BUS UPPER A | 66 | 4.7722 | 545.5412 | 3.9032 | 148.732 | 3.3244 | 4.4633 | 170.073 | 4.4222 | 168.5077 | 1.7601 | 8.6057 | 3.1051 | 14.2466 | 1.7351 | 8.6832
SOKO | South Kolan | WB | SOKO_66kV_BUS UPPER B | 66 | 4.7722 | 545.5412 | 3.9032 | 148.732 | 3.3244 | 4.4633 | 170.073 | 4.4222 | 168.5077 | 1.7601 | 8.6057 | 3.1051 | 14.2466 | 1.7351 | 8.6832
SOMA | South Mackay (TF1) | MK | SOMA_11kV_BUS 1 | 11 | 10.1263 | 192.9319 | 11.7661 | 74.7246 | 14.061 | 10.9057 | 69.2605 | 11.5568 | 73.3955 | 0.11051 | 0.68098 | 0.02005 | 0.40137 | 0.11038 | 0.6825
SOMA | South Mackay (TF2) | MK | SOMA_11kV_BUS 2 | 11 | 10.1263 | 192.9319 | 11.7661 | 74.7246 | 14.061 | 10.9057 | 69.2605 | 11.5568 | 73.3955 | 0.11051 | 0.68098 | 0.02005 | 0.40137 | 0.11038 | 0.6825
SOMA | South Mackay | MK | SOMA_33kV_BUS 1 | 33 | 7.9241 | 452.9232 | 5.6436 | 107.5247 | 4.3967 | 7.0894 | 135.0713 | 7.2958 | 139.0028 | 0.8141 | 2.5164 | 1.448 | 5.6615 | 0.81299 | 2.5301
SOMA | South Mackay | MK | SOMA_33kV_BUS 2 | 33 | 7.9241 | 452.9232 | 5.6436 | 107.5247 | 4.3967 | 7.0894 | 135.0713 | 7.2958 | 139.0028 | 0.8141 | 2.5164 | 1.448 | 5.6615 | 0.81299 | 2.5301
SOTO | South Toowoomba T043 (TF1) | SW | SOTO_110kV_BUS 1 | 110 | 17.5588 | 3345.405 | 16.7686 | 1064.9459 | 15.8566 | 17.2558 | 1095.8885 | 17.1599 | 1089.7997 | 0.38603 | 3.9604 | 0.49747 | 4.5642 | 0.38779 | 3.9107
SOTO | South Toowoomba T043 (TF2) | SW | SOTO_110kV_BUS 2 | 110 | 17.5588 | 3345.405 | 16.7686 | 1064.9459 | 15.8566 | 17.2558 | 1095.8885 | 17.1599 | 1089.7997 | 0.38603 | 3.9604 | 0.49747 | 4.5642 | 0.38779 | 3.9107
SOTO | South Toowoomba T043 | SW | SOTO_11kV_BUS 1 | 11 | 13.0365 | 248.3788 | 2.2798 | 14.4786 | 1.1565 | 11.869 | 75.3782 | 10.7218 | 68.0925 | 0.02864 | 0.53519 | 9.0197 | 0.39392 | 0.02866 | 0.53469
SOTO | South Toowoomba T043 | SW | SOTO_11kV_BUS 2 | 11 | 13.0365 | 248.3788 | 2.2798 | 14.4786 | 1.1565 | 11.869 | 75.3782 | 10.7218 | 68.0925 | 0.02864 | 0.53519 | 9.0197 | 0.39392 | 0.02866 | 0.53469
SOTO | South Toowoomba T043 | SW | SOTO_11kV_BUS 3 | 11 | 13.0365 | 248.3788 | 2.2798 | 14.4786 | 1.1565 | 11.869 | 75.3782 | 10.7218 | 68.0925 | 0.02864 | 0.53519 | 9.0197 | 0.39392 | 0.02866 | 0.53469
SOTO | South Toowoomba T043 | SW | SOTO_33kV_BUS 1 | 33 | 16.4532 | 940.4246 | 1.1584 | 22.0706 | 0.57989 | 14.5631 | 277.4651 | 13.9845 | 266.4408 | 0.08049 | 1.2714 | 54.0848 | -0.50571 | 0.08065 | 1.267
SOTO | South Toowoomba T043 | SW | SOTO_33kV_BUS 2 | 33 | 16.4532 | 940.4246 | 1.1584 | 22.0706 | 0.57989 | 14.5631 | 277.4651 | 13.9845 | 266.4408 | 0.08049 | 1.2714 | 54.0848 | -0.50571 | 0.08065 | 1.267
SOTO | South Toowoomba T043 | SW | SOTO_33kV_BUS 3 | 33 | 16.4532 | 940.4246 | 1.1584 | 22.0706 | 0.57989 | 14.5631 | 277.4651 | 13.9845 | 266.4408 | 0.08049 | 1.2714 | 54.0848 | -0.50571 | 0.08065 | 1.267
SOWC | South Walker Switching | MK | Dragline | 66 | 3.4011 | 388.8042 | 2.3718 | 90.3777 | 1.8232 | 3.078 | 117.2869 | 3.0846 | 117.5405 | 3.8383 | 11.7111 | 8.695 | 26.9821 | 3.8412 | 11.7327
STAM | Stamford | NQ | STAM_33kV_TEF T1 | 33 | 0.14959 | 8.5503 | 0.15447 | 2.943 | 0.1603 | 0.15055 | 2.8683 | 0.15383 | 2.9309 | 15.1354 | 139.2811 | 8.9372 | 126.0276 | 15.1998 | 139.8285
STAM | Stamford | NQ | STAM_66kV_TEF T1 | 66 | 0.7162 | 81.8727 | 0.54249 | 20.6716 | 0.44833 | 0.63094 | 24.0419 | 0.67136 | 25.5823 | 24.7926 | 53.0142 | 33.8772 | 107.931 | 25.0504 | 55.2037
STAN | Stanthorpe | SW | STAN_110kV_BUS | 110 | 1.2958 | 246.8801 | 1.8257 | 115.9474 | 3.0724 | 1.8023 | 114.463 | 1.9977 | 126.8726 | 28.9425 | 45.4939 | 0.61829 | 7.8385 | 28.8209 | 45.5241
STAN | Stanthorpe | SW | STAN_33kV_BUS 1 | 33 | 2.8031 | 160.217 | 1.0114 | 19.2695 | 0.56311 | 2.6758 | 50.9807 | 2.188 | 41.6876 | 3.2411 | 6.7389 | 54.0555 | 0.74803 | 3.2278 | 6.7422
STAN | Stanthorpe | SW | STAN_33kV_BUS 2 | 33 | 2.8031 | 160.217 | 1.0114 | 19.2695 | 0.56311 | 2.6758 | 50.9807 | 2.188 | 41.6876 | 3.2411 | 6.7389 | 54.0555 | 0.74803 | 3.2278 | 6.7422
STTO | Stanthorpe Town | SW | STTO_11kV_BUS 1 | 11 | 4.754 | 90.5763 | 5.9487 | 37.7796 | 7.9146 | 5.3878 | 34.2171 | 6.0164 | 38.209 | 0.42937 | 1.4056 | 0.02993 | 0.59855 | 0.4279 | 1.4059
STTO | Stanthorpe Town | SW | STTO_11kV_BUS 2 | 11 | 4.754 | 90.5763 | 5.9487 | 37.7796 | 7.9146 | 5.3878 | 34.2171 | 6.0164 | 38.209 | 0.42937 | 1.4056 | 0.02993 | 0.59855 | 0.4279 | 1.4059
STTO | Stanthorpe Town | SW | STTO_33kV_BUS 1 | 33 | 2.5864 | 147.8329 | 0.97761 | 18.6259 | 0.55227 | 2.4769 | 47.191 | 2.0135 | 38.3628 | 3.5949 | 7.2633 | 54.7576 | 2.8365 | 3.5817 | 7.2666
STTO | Stanthorpe Town | SW | STTO_33kV_BUS 2 | 33 | 2.5864 | 147.8329 | 0.97761 | 18.6259 | 0.55227 | 2.4769 | 47.191 | 2.0135 | 38.3628 | 3.5949 | 7.2633 | 54.7576 | 2.8365 | 3.5817 | 7.2666
STUA | Stuart | NQ | STUA_11kV_BUS A | 11 | 18.4197 | 350.9416 | 19.5041 | 123.868 | 20.7182 | 18.9069 | 120.075 | 19.1352 | 121.5246 | 0.02061 | 0.37871 | 0.0101 | 0.31598 | 0.02007 | 0.37865
STUA | Stuart | NQ | STUA_11kV_BUS B | 11 | 18.4197 | 350.9416 | 19.5041 | 123.868 | 20.7182 | 18.9069 | 120.075 | 19.1352 | 121.5246 | 0.02061 | 0.37871 | 0.0101 | 0.31598 | 0.02007 | 0.37865
STUA | Stuart | NQ | STUA_11kV_BUS C | 11 | 18.4197 | 350.9416 | 19.5041 | 123.868 | 20.7182 | 18.9069 | 120.075 | 19.1352 | 121.5246 | 0.02061 | 0.37871 | 0.0101 | 0.31598 | 0.02007 | 0.37865
STUA | Stuart | NQ | STUA_66kV_BUS 1 | 66 | 18.3068 | 2092.747 | 20.075 | 764.9591 | 22.1648 | 19.3228 | 736.2983 | 19.3823 | 738.5643 | 0.37847 | 2.2581 | 0.25648 | 1.6704 | 0.35907 | 2.256
STUA | Stuart | NQ | STUA_66kV_BUS 2 | 66 | 18.3068 | 2092.747 | 20.075 | 764.9591 | 22.1648 | 19.3228 | 736.2983 | 19.3823 | 738.5643 | 0.37847 | 2.2581 | 0.25648 | 1.6704 | 0.35907 | 2.256
TANB | Tanby | CA | TANB_22kV_BUS 1 | 22 | 4.403 | 167.7776 | 5.1608 | 65.5516 | 6.1485 | 4.6766 | 59.401 | 5.1246 | 65.0918 | 0.68812 | 3.0978 | 0.0732 | 1.8252 | 0.66799 | 3.0722
TANB | Tanby | CA | TANB_22kV_BUS 2 | 22 | 4.403 | 167.7776 | 5.1608 | 65.5516 | 6.1485 | 4.6766 | 59.401 | 5.1246 | 65.0918 | 0.68812 | 3.0978 | 0.0732 | 1.8252 | 0.66799 | 3.0722
TANB | Tanby | CA | TANB_22kV_BUS 3 | 22 | 4.403 | 167.7776 | 5.1608 | 65.5516 | 6.1485 | 4.6766 | 59.401 | 5.1246 | 65.0918 | 0.68812 | 3.0978 | 0.0732 | 1.8252 | 0.66799 | 3.0722
TANB | Tanby | CA | TANB_66kV_BUS 1 | 66 | 3.1352 | 358.3999 | 2.0391 | 77.7009 | 1.504 | 2.7341 | 104.1843 | 2.9049 | 110.6928 | 5.6815 | 12.1024 | 10.1816 | 33.6157 | 5.611 | 12.0906
TANB | Tanby | CA | TANB_66kV_BUS 2 | 66 | 3.1352 | 358.3999 | 2.0391 | 77.7009 | 1.504 | 2.7341 | 104.1843 | 2.9049 | 110.6928 | 5.6815 | 12.1024 | 10.1816 | 33.6157 | 5.611 | 12.0906
TARA | Tara (TF2) | SW | TARA_11kV_BUS BILTON ST(1) | 11 | 0.54325 | 10.3504 | 0.63181 | 4.0126 | 0.7471 | 0.54308 | 3.449 | 0.65333 | 4.1492 | 4.936 | 11.8759 | 0.38978 | 7.7956 | 4.9361 | 11.8759
TARA | Tara (TF1) | SW | TARA_11kV_BUS FRY ST(1) | 11 | 0.70867 | 13.502 | 0.87738 | 5.5721 | 1.1346 | 0.73997 | 4.6994 | 0.92166 | 5.8533 | 4.7735 | 8.6262 | 0.22729 | 4.5459 | 4.7736 | 8.6262
TARA | Tara | SW | TARA_33kV_BUS | 33 | 0.38124 | 21.7908 | 0.2811 | 5.3557 | 0.21817 | 0.31209 | 5.9462 | 0.38001 | 7.2402 | 40.9159 | 36.7226 | 49.5139 | 107.6219 | 40.9172 | 36.7227
TARE | Tara Regulator (Unregulated) | SW | TARE_33kV_R Downstream | 33 | 0.42608 | 24.3535 | 0.31683 | 6.0363 | 0.24737 | 0.35006 | 6.6695 | 0.42469 | 8.0915 | 36.1041 | 33.4135 | 43.0808 | 94.7226 | 36.1054 | 33.4136
TARE | Tara Regulator (Regulated) | SW | TARE_33kV_R Upstream | 33 | 0.42608 | 24.3535 | 0.31683 | 6.0363 | 0.24737 | 0.35006 | 6.6695 | 0.42469 | 8.0915 | 36.1041 | 33.4135 | 43.0808 | 94.7226 | 36.1054 | 33.4136
TARO | Tarong | WB | TARO_66kV_BUS 1 | 66 | 16.9421 | 1936.7421 | 18.2007 | 693.5385 | 19.721 | 17.4957 | 666.6771 | 17.8366 | 679.6677 | 0.10174 | 2.4723 | 0.01129 | 1.9546 | 0.09883 | 2.4796
TARO | Tarong | WB | TARO_66kV_BUS 2 | 66 | 16.9421 | 1936.7421 | 18.2007 | 693.5385 | 19.721 | 17.4957 | 666.6771 | 17.8366 | 679.6677 | 0.10174 | 2.4723 | 0.01129 | 1.9546 | 0.09883 | 2.4796
TECR | H063 Teebar Creek | WB | TECR_132kV_BUS 1 | 132 | 10.5588 | 2414.0672 | 11.5049 | 876.7907 | 12.7827 | 11.1064 | 846.4175 | 11.1601 | 850.5171 | 0.91113 | 7.8878 | 0.5878 | 5.8695 | 0.8684 | 7.9761
TECR | H063 Teebar Creek | WB | TECR_132kV_BUS 2 | 132 | 10.5588 | 2414.0672 | 11.5049 | 876.7907 | 12.7827 | 11.1064 | 846.4175 | 11.1601 | 850.5171 | 0.91113 | 7.8878 | 0.5878 | 5.8695 | 0.8684 | 7.9761
THAL | Thalanga | NQ | THAL_11kV_TEF T1 | 11 | 2.8369 | 54.0499 | 3.1294 | 19.8741 | 3.5066 | 2.9159 | 18.5187 | 3.1109 | 19.7569 | 0.40555 | 2.4289 | 0.08405 | 1.765 | 0.40393 | 2.4434
THAL | Thalanga | NQ | THAL_66kV_TEF T1 | 66 | 1.606 | 183.5883 | 1.3379 | 50.98 | 1.1597 | 1.4361 | 54.7235 | 1.5591 | 59.4081 | 11.5114 | 23.424 | 12.0815 | 39.8433 | 11.453 | 23.9445
THEO | Theodore (TF1) | CA | THEO_22kV_TEF T1 | 22 | 2.533 | 96.5218 | 3.2005 | 40.652 | 4.3551 | 3.0262 | 38.4383 | 3.153 | 40.0489 | 0.96598 | 5.4307 | 0.16431 | 2.0553 | 0.96675 | 5.4417
THEO | Theodore (TF2) | CA | THEO_22kV_TEF T2 | 22 | 2.533 | 96.5218 | 3.2005 | 40.652 | 4.3551 | 3.0262 | 38.4383 | 3.153 | 40.0489 | 0.96598 | 5.4307 | 0.16431 | 2.0553 | 0.96675 | 5.4417
THEO | Theodore (TF3) | CA | THEO_22kV_TEF T3 | 22 | 2.533 | 96.5218 | 3.2005 | 40.652 | 4.3551 | 3.0262 | 38.4383 | 3.153 | 40.0489 | 0.96598 | 5.4307 | 0.16431 | 2.0553 | 0.96675 | 5.4417
THEO | Theodore | CA | THEO_66kV_TEF T1 | 66 | 1.346 | 153.8706 | 0.80395 | 30.6348 | 0.57442 | 1.1961 | 45.5768 | 1.202 | 45.8005 | 7.213 | 30.2941 | 20.6085 | 91.7498 | 7.22 | 30.3934
THEO | Theodore | CA | THEO_66kV_TEF T2 | 66 | 1.346 | 153.8706 | 0.80395 | 30.6348 | 0.57442 | 1.1961 | 45.5768 | 1.202 | 45.8005 | 7.213 | 30.2941 | 20.6085 | 91.7498 | 7.22 | 30.3934
THEO | Theodore | CA | THEO_66kV_TEF T3 | 66 | 1.346 | 153.8706 | 0.80395 | 30.6348 | 0.57442 | 1.1961 | 45.5768 | 1.202 | 45.8005 | 7.213 | 30.2941 | 20.6085 | 91.7498 | 7.22 | 30.3934
TIDH | Tinaroo Dam Hydro | FN | TIDH_22kV_TEF T1 | 22 | 0.87704 | 33.4197 | 0.66258 | 8.4159 | 0.51861 | 0.70756 | 8.9872 | 0.88758 | 11.2738 | 12.8312 | 9.4419 | 15.135 | 29.4614 | 12.8204 | 9.454
TIER | Tieri | CA | TIER_22kV_BUS 1 | 22 | 3.2327 | 123.1817 | 3.5416 | 44.9839 | 3.9119 | 3.3148 | 42.1031 | 3.5126 | 44.6166 | 0.767 | 4.2535 | 0.23833 | 3.1945 | 0.76455 | 4.2542
TIER | Tieri | CA | TIER_22kV_BUS 2 | 22 | 3.2327 | 123.1817 | 3.5416 | 44.9839 | 3.9119 | 3.3148 | 42.1031 | 3.5126 | 44.6166 | 0.767 | 4.2535 | 0.23833 | 3.1945 | 0.76455 | 4.2542
TIER | Tieri | CA | TIER_66kV_BUS 1 | 66 | 3.9348 | 449.8135 | 2.7524 | 104.8814 | 2.1119 | 3.4627 | 131.9464 | 3.6704 | 139.8612 | 4.7581 | 9.5308 | 8.0563 | 23.1121 | 4.736 | 9.5374
TIER | Tieri | CA | TIER_66kV_BUS 2 | 66 | 3.9348 | 449.8135 | 2.7524 | 104.8814 | 2.1119 | 3.4627 | 131.9464 | 3.6704 | 139.8612 | 4.7581 | 9.5308 | 8.0563 | 23.1121 | 4.736 | 9.5374
TOMA | Townsville Marina SS (MF07) | NQ | TOMA_11kV_BUS A | 11 | 22.5921 | 430.4372 | 25.2435 | 160.318 | 28.5204 | 25.2004 | 160.0442 | 23.1834 | 147.2341 | 0.08286 | 0.29791 | 0.08725 | 0.19514 | 0.08233 | 0.29787
TOMA | Townsville Marina SS (TOPO08) | NQ | TOMA_11kV_BUS B | 11 | 22.5921 | 430.4372 | 25.2435 | 160.318 | 28.5204 | 25.2004 | 160.0442 | 23.1834 | 147.2341 | 0.08286 | 0.29791 | 0.08725 | 0.19514 | 0.08233 | 0.29787
TOPO | Townsville Port (TF1) | NQ | TOPO_11kV_BUS 1 | 11 | 20.716 | 394.693 | 22.6831 | 144.0572 | 25.0525 | 21.9847 | 139.6219 | 21.7795 | 138.3186 | 0.04956 | 0.33356 | 0.04043 | 0.24634 | 0.04902 | 0.33352
TOPO | Townsville Port (TF2) | NQ | TOPO_11kV_BUS 2 | 11 | 20.716 | 394.693 | 22.6831 | 144.0572 | 25.0525 | 21.9847 | 139.6219 | 21.7795 | 138.3186 | 0.04956 | 0.33356 | 0.04043 | 0.24634 | 0.04902 | 0.33352
TOPO | Townsville Port | NQ | TOPO_11kV_BUS 3 | 11 | 20.716 | 394.693 | 22.6831 | 144.0572 | 25.0525 | 21.9847 | 139.6219 | 21.7795 | 138.3186 | 0.04956 | 0.33356 | 0.04043 | 0.24634 | 0.04902 | 0.33352
TOPO | Townsville Port | NQ | TOPO_66kV_BUS 1A | 66 | 13.6149 | 1556.3966 | 14.198 | 541.0175 | 14.7964 | 13.6665 | 520.7646 | 14.1813 | 540.3817 | 0.71585 | 2.9943 | 0.4434 | 2.673 | 0.69674 | 2.9927
TOPO | Townsville Port | NQ | TOPO_66kV_BUS 1B | 66 | 13.6149 | 1556.3966 | 14.198 | 541.0175 | 14.7964 | 13.6665 | 520.7646 | 14.1813 | 540.3817 | 0.71585 | 2.9943 | 0.4434 | 2.673 | 0.69674 | 2.9927
TOPO | Townsville Port | NQ | TOPO_66kV_BUS 2 | 66 | 13.6149 | 1556.3966 | 14.198 | 541.0175 | 14.7964 | 13.6665 | 520.7646 | 14.1813 | 540.3817 | 0.71585 | 2.9943 | 0.4434 | 2.673 | 0.69674 | 2.9927
TOPS | Townsville Power Station | NQ | TOPS_66kV_TEF T1 | 66 | 8.8835 | 1015.5208 | 8.9432 | 340.7809 | 8.989 | 8.6777 | 330.665 | 9.1409 | 348.3148 | 0.86704 | 4.638 | 0.37611 | 4.6261 | 0.80301 | 4.6468
TORQ | Torquay | WB | TORQ_11kV_BUS 1 | 11 | 14.2312 | 271.1404 | 17.4136 | 110.5913 | 23.1169 | 16.4573 | 104.518 | 17.2298 | 109.4242 | 0.07626 | 0.48497 | 0.01122 | 0.21062 | 0.07706 | 0.49674
TORQ | Torquay | WB | TORQ_11kV_BUS 2 | 11 | 14.2312 | 271.1404 | 17.4136 | 110.5913 | 23.1169 | 16.4573 | 104.518 | 17.2298 | 109.4242 | 0.07626 | 0.48497 | 0.01122 | 0.21062 | 0.07706 | 0.49674
TORQ | Torquay | WB | TORQ_66kV_BUS 1 | 66 | 4.0363 | 461.414 | 2.6674 | 101.6433 | 2.0182 | 3.6147 | 137.7369 | 3.6129 | 137.6691 | 2.3735 | 10.1106 | 5.9008 | 25.5171 | 2.3699 | 10.3001
TORQ | Torquay | WB | TORQ_66kV_BUS 2 | 66 | 4.0363 | 461.414 | 2.6674 | 101.6433 | 2.0182 | 3.6147 | 137.7369 | 3.6129 | 137.6691 | 2.3735 | 10.1106 | 5.9008 | 25.5171 | 2.3699 | 10.3001
TORQ | Torquay | WB | TORQ_66kV_BUS 3 | 66 | 4.0363 | 461.414 | 2.6674 | 101.6433 | 2.0182 | 3.6147 | 137.7369 | 3.6129 | 137.6691 | 2.3735 | 10.1106 | 5.9008 | 25.5171 | 2.3699 | 10.3001
TORR | Torrington T116 (TF1) | SW | TORR_110kV_TEF T1 | 110 | 8.7269 | 1662.6908 | 8.2764 | 525.6244 | 7.8176 | 8.3014 | 527.2079 | 8.7389 | 554.9958 | 1.2407 | 7.9096 | 0.6282 | 9.3645 | 1.2417 | 7.8602
TORR | Torrington T116 (TF2) | SW | TORR_110kV_TEF T2 | 110 | 8.7161 | 1660.6425 | 7.9105 | 502.3818 | 7.1954 | 8.1823 | 519.6465 | 8.567 | 544.0788 | 1.2425 | 7.9193 | 0.79052 | 10.5052 | 1.2435 | 7.8699
TORR | Torrington T116 (TF1) | SW | TORR_11kV_BUS 1 | 11 | 13.2174 | 251.8246 | 2.275 | 14.4484 | 1.1553 | 12.024 | 76.3624 | 10.8804 | 69.0995 | 0.03788 | 0.52726 | 9.0266 | 0.37294 | 0.03783 | 0.52677
TORR | Torrington T116 (TF2) | SW | TORR_11kV_BUS 2 | 11 | 13.2174 | 251.8246 | 2.275 | 14.4484 | 1.1553 | 12.024 | 76.3624 | 10.8804 | 69.0995 | 0.03788 | 0.52726 | 9.0266 | 0.37294 | 0.03783 | 0.52677
TORR | Torrington T116 | SW | TORR_33kV_BUS 1 | 33 | 15.0518 | 860.3242 | 1.1683 | 22.2582 | 0.58384 | 13.3478 | 254.3102 | 12.764 | 243.187 | 0.10164 | 1.3889 | 53.6064 | -4.1364 | 0.10118 | 1.3845
TORR | Torrington T116 | SW | TORR_33kV_BUS 2 | 33 | 15.0518 | 860.3242 | 1.1683 | 22.2582 | 0.58384 | 13.3478 | 254.3102 | 12.764 | 243.187 | 0.10164 | 1.3889 | 53.6064 | -4.1364 | 0.10118 | 1.3845
TULL | Tully T048 | FN | TULL_22kV_BUS 1 | 22 | 8.0732 | 307.6296 | 6.5884 | 83.6845 | 5.564 | 7.5216 | 95.5367 | 7.529 | 95.6317 | 0.12341 | 1.7263 | 0.18419 | 2.8952 | 0.1131 | 1.7266
TULL | Tully T048 | FN | TULL_22kV_BUS 2 | 22 | 8.0732 | 307.6296 | 6.5884 | 83.6845 | 5.564 | 7.5216 | 95.5367 | 7.529 | 95.6317 | 0.12341 | 1.7263 | 0.18419 | 2.8952 | 0.1131 | 1.7266
TURK | Turkinje T055 (TF1) | FN | TURK_66kV_BUS 1 | 66 | 5.2662 | 602.0094 | 6.5889 | 251.0691 | 8.9408 | 6.3141 | 240.5978 | 6.4412 | 245.444 | 1.1154 | 7.8808 | 0.25669 | 3.0626 | 1.0419 | 7.9881
TURK | Turkinje T055 (TF1) | FN | TURK_66kV_BUS 2 | 66 | 5.2662 | 602.0094 | 6.5889 | 251.0691 | 8.9408 | 6.3141 | 240.5978 | 6.4412 | 245.444 | 1.1154 | 7.8808 | 0.25669 | 3.0626 | 1.0419 | 7.9881
TWCE | Toowoomba Central | SW | TWCE_110kV_TEF T1 | 110 | 16.8307 | 3206.6787 | 16.1738 | 1027.1769 | 15.39 | 16.553 | 1051.2599 | 16.5181 | 1049.04 | 0.55405 | 4.1142 | 0.65479 | 4.6604 | 0.55581 | 4.0645
TWCE | Toowoomba Central | SW | TWCE_110kV_TEF T2 | 110 | 16.8313 | 3206.7852 | 16.1743 | 1027.203 | 15.3903 | 16.5536 | 1051.2964 | 16.5185 | 1049.0666 | 0.55391 | 4.1141 | 0.65473 | 4.6604 | 0.55567 | 4.0644
TWCE | Toowoomba Central | SW | TWCE_11kV_BUS 1 | 11 | 18.75 | 357.2348 | 4.5292 | 28.7643 | 2.5736 | 16.2566 | 103.2436 | 16.3415 | 103.7826 | 0.01288 | 0.37242 | 0 | 3.8836 | 0.0129 | 0.37192
TWCE | Toowoomba Central | SW | TWCE_11kV_BUS 2 | 11 | 18.75 | 357.2348 | 4.5292 | 28.7643 | 2.5736 | 16.2566 | 103.2436 | 16.3415 | 103.7826 | 0.01288 | 0.37242 | 0 | 3.8836 | 0.0129 | 0.37192
TWCE | Toowoomba Central | SW | TWCE_11kV_BUS 3 | 11 | 18.75 | 357.2348 | 4.5292 | 28.7643 | 2.5736 | 16.2566 | 103.2436 | 16.3415 | 103.7826 | 0.01288 | 0.37242 | 0 | 3.8836 | 0.0129 | 0.37192
VERM | Vermont | CA | VERM_22kV_BUS 1 | 22 | 4.1951 | 159.8551 | 4.8082 | 61.0724 | 5.6338 | 4.5048 | 57.2183 | 4.6865 | 59.5267 | 0.4121 | 3.3049 | 0.10344 | 2.0555 | 0.4128 | 3.3075
VERM | Vermont | CA | VERM_22kV_BUS 2 | 22 | 4.1951 | 159.8551 | 4.8082 | 61.0724 | 5.6338 | 4.5048 | 57.2183 | 4.6865 | 59.5267 | 0.4121 | 3.3049 | 0.10344 | 2.0555 | 0.4128 | 3.3075
VERM | Vermont | CA | VERM_66kV_BUS | 66 | 3.6188 | 413.6836 | 2.9306 | 111.6722 | 2.4666 | 3.3463 | 127.5125 | 3.3847 | 128.9727 | 2.778 | 11.2448 | 4.3157 | 19.2426 | 2.7842 | 11.2681
WAEA | Warwick East (TF1*C0516*ON) | SW | WAEA_11kV_BUS 1 | 11 | 10.3885 | 197.9267 | 5.5738 | 35.3983 | 3.1672 | 10.5032 | 66.7046 | 7.5099 | 47.6942 | 0.0826 | 0.66746 | 3.1955 | 0.35895 | 0.07852 | 0.66816
WAEA | Warwick East (TF2*C0516*ON) | SW | WAEA_11kV_BUS 2 | 11 | 10.3885 | 197.9267 | 5.5738 | 35.3983 | 3.1672 | 10.5032 | 66.7046 | 7.5099 | 47.6942 | 0.0826 | 0.66746 | 3.1955 | 0.35895 | 0.07852 | 0.66816
WAEA | Warwick East | SW | WAEA_33kV_BUS 1 | 33 | 7.3763 | 421.6138 | 7.3468 | 139.9762 | 7.3136 | 7.2972 | 139.0309 | 7.4249 | 141.4628 | 0.6046 | 2.7765 | 0.4905 | 2.8355 | 0.56794 | 2.7828
WAEA | Warwick East | SW | WAEA_33kV_BUS 2 | 33 | 7.3763 | 421.6138 | 7.3468 | 139.9762 | 7.3136 | 7.2972 | 139.0309 | 7.4249 | 141.4628 | 0.6046 | 2.7765 | 0.4905 | 2.8355 | 0.56794 | 2.7828
WAGG | Waggamba T156 | SW | WAGG_132kV_TEF T1 | 132 | 1.9575 | 447.5525 | 2.3234 | 177.0678 | 2.8581 | 2.2104 | 168.4572 | 2.224 | 169.4883 | 6.6115 | 42.3135 | 2.9693 | 22.3938 | 6.1424 | 42.3931
WAGG | Waggamba T156 | SW | WAGG_33kV_BUS GOONDIWINDI | 33 | 3.3167 | 189.5743 | 2.672 | 50.9077 | 2.2368 | 3.0307 | 57.7433 | 3.1324 | 59.6797 | 0.42679 | 6.3048 | 0 | 10.903 | 0.39746 | 6.3097
WAGG | Waggamba T156 | SW | WAGG_66kV_BUS ESSENTIAL ENERGY | 66 | 2.4145 | 276.016 | 3.3383 | 127.2066 | 5.4112 | 3.4055 | 129.7683 | 3.4332 | 130.8222 | 1.7086 | 17.2764 | 0.17259 | 2.9366 | 1.5913 | 17.2963
WALK | Walkers | WB | MARYBOROUGH CITY | 11 | 10.6816 | 203.5118 | 11.8085 | 74.994 | 13.2388 | 11.4452 | 72.6869 | 11.2926 | 71.7178 | 0.1277 | 0.64149 | 0.10093 | 0.45413 | 0.12676 | 0.6434
WALK | Walkers | WB | WALK_11kV_BUS | 11 | 11.0515 | 210.5591 | 3.5468 | 22.5253 | 2.1158 | 9.5916 | 60.9149 | 9.6416 | 61.2324 | 0.07991 | 0.62711 | 0.46126 | 4.6207 | 0.07897 | 0.62903
WALK | Walkers | WB | WALK_11kV_BUS FURNACE | 11 | 11.0515 | 210.5591 | 3.5468 | 22.5253 | 2.1158 | 9.5916 | 60.9149 | 9.6416 | 61.2324 | 0.07991 | 0.62711 | 0.46126 | 4.6207 | 0.07897 | 0.62903
WALK | Walkers | WB | WALK_66kV_TEF T1 | 66 | 6.1369 | 701.5444 | 5.8037 | 221.1521 | 5.5506 | 5.9613 | 227.1576 | 6.0015 | 228.6858 | 1.5249 | 6.6583 | 1.6291 | 7.7791 | 1.4912 | 6.7272
WALK | Walkers | WB | WALK_66kV_TEF T2 | 66 | 6.1369 | 701.5444 | 5.8037 | 221.1521 | 5.5506 | 5.9613 | 227.1576 | 6.0015 | 228.6858 | 1.5249 | 6.6583 | 1.6291 | 7.7791 | 1.4912 | 6.7272
WALL | Wallaville | WB | WALL_11kV_BUS 1 | 11 | 6.0819 | 115.8754 | 7.5549 | 47.9803 | 9.922 | 6.6836 | 42.4464 | 7.7462 | 49.1952 | 0.4305 | 1.065 | 0.03193 | 0.49469 | 0.42981 | 1.0672
WALL | Wallaville | WB | WALL_11kV_BUS 2 | 11 | 6.0819 | 115.8754 | 7.5549 | 47.9803 | 9.922 | 6.6836 | 42.4464 | 7.7462 | 49.1952 | 0.4305 | 1.065 | 0.03193 | 0.49469 | 0.42981 | 1.0672
WALL | Wallaville | WB | WALL_66kV_BUS | 66 | 1.6735 | 191.3067 | 1.1522 | 43.9039 | 0.87218 | 1.4165 | 53.9753 | 1.6026 | 61.0681 | 14.3484 | 20.5318 | 19.814 | 56.6451 | 14.3235 | 20.6093
WAND | Wandoan (TF1) | SW | WAND_22kV_BUS 1 | 22 | 0.71356 | 27.1904 | 1.0018 | 12.7245 | 1.6778 | 1.004 | 12.753 | 1.0785 | 13.6983 | 7.3875 | 18.1341 | 0.1411 | 2.822 | 7.3872 | 18.1371
WAND | Wandoan (TF1) | SW | WAND_22kV_BUS 2 | 22 | 0.71356 | 27.1904 | 1.0018 | 12.7245 | 1.6778 | 1.004 | 12.753 | 1.0785 | 13.6983 | 7.3875 | 18.1341 | 0.1411 | 2.822 | 7.3872 | 18.1371
WAND | Wandoan | SW | WAND_33kV_BUS 1 | 33 | 0.54987 | 31.4293 | 0.30519 | 5.8147 | 0.21021 | 0.46815 | 8.9195 | 0.50636 | 9.6475 | 16.3043 | 34.4522 | 29.5513 | 127.5067 | 16.3038 | 34.4591
WAND | Wandoan | SW | WAND_33kV_BUS 2 | 33 | 0.54987 | 31.4293 | 0.30519 | 5.8147 | 0.21021 | 0.46815 | 8.9195 | 0.50636 | 9.6475 | 16.3043 | 34.4522 | 29.5513 | 127.5067 | 16.3038 | 34.4591
WARW | Warwick (CCT 735) | SW | WARW_110kV_BUS 1 | 110 | 4.0424 | 770.1744 | 4.8409 | 307.4411 | 6.0113 | 4.3805 | 278.2018 | 4.8377 | 307.2328 | 5.0183 | 16.5395 | 0.79414 | 8.8441 | 4.8967 | 16.5697
WARW | Warwick (CCT 736) | SW | WARW_110kV_BUS 2 | 110 | 4.0424 | 770.1744 | 4.8409 | 307.4411 | 6.0113 | 4.3805 | 278.2018 | 4.8377 | 307.2328 | 5.0183 | 16.5395 | 0.79414 | 8.8441 | 4.8967 | 16.5697
WARW | Warwick | SW | WARW_11kV_BUS 1 | 11 | 3.4357 | 65.4586 | 3.5901 | 22.8004 | 3.7601 | 3.5097 | 22.2898 | 3.5286 | 22.4099 | 0.1934 | 2.0244 | 0.14826 | 1.764 | 0.18932 | 2.0251
WARW | Warwick | SW | WARW_33kV_BUS 1 | 33 | 9.0062 | 514.7718 | 11.5924 | 220.8654 | 16.2498 | 10.9689 | 208.9858 | 11.5505 | 220.0657 | 0.40625 | 2.2916 | 0.0234 | 0.775 | 0.36959 | 2.2979
WARW | Warwick | SW | WARW_33kV_BUS 2 | 33 | 9.0062 | 514.7718 | 11.5924 | 220.8654 | 16.2498 | 10.9689 | 208.9858 | 11.5505 | 220.0657 | 0.40625 | 2.2916 | 0.0234 | 0.775 | 0.36959 | 2.2979
WEBU | West Bundaberg | WB | WEBU_11kV_BUS 1 | 11 | 14.7861 | 281.7138 | 16.942 | 107.596 | 19.9619 | 16.0927 | 102.2023 | 16.3466 | 103.8151 | 0.04176 | 0.47065 | 0.01649 | 0.28913 | 0.04097 | 0.47336
WEBU | West Bundaberg | WB | WEBU_11kV_BUS 2 | 11 | 14.7861 | 281.7138 | 16.942 | 107.596 | 19.9619 | 16.0927 | 102.2023 | 16.3466 | 103.8151 | 0.04176 | 0.47065 | 0.01649 | 0.28913 | 0.04097 | 0.47336
WEBU | West Bundaberg | WB | WEBU_66kV_TEF T1 | 66 | 6.3534 | 726.2882 | 6.1081 | 232.7487 | 5.9595 | 6.3227 | 240.9252 | 6.1438 | 234.1099 | 0.9097 | 6.5349 | 1.3218 | 7.1845 | 0.88148 | 6.6325
WEBU | West Bundaberg | WB | WEBU_66kV_TEF T2 | 66 | 6.3534 | 726.2882 | 6.1081 | 232.7487 | 5.9595 | 6.3227 | 240.9252 | 6.1438 | 234.1099 | 0.9097 | 6.5349 | 1.3218 | 7.1845 | 0.88148 | 6.6325
WEDA | West Dalby (TF1) | SW | WEDA_11kV_BUS DRAYTON ST | 11 | 5.9868 | 114.0631 | 6.8489 | 43.4966 | 7.993 | 6.3499 | 40.3272 | 6.7367 | 42.7841 | 0.21605 | 1.1468 | 0.05563 | 0.72749 | 0.21619 | 1.1469
WEDA | West Dalby (TF2) | SW | WEDA_11kV_BUS EDWARD ST | 11 | 5.9868 | 114.0631 | 6.8489 | 43.4966 | 7.993 | 6.3499 | 40.3272 | 6.7367 | 42.7841 | 0.21605 | 1.1468 | 0.05563 | 0.72749 | 0.21619 | 1.1469
WEDA | West Dalby (TF3) | SW | WEDA_11kV_BUS NICHOLSON ST | 11 | 5.9868 | 114.0631 | 6.8489 | 43.4966 | 7.993 | 6.3499 | 40.3272 | 6.7367 | 42.7841 | 0.21605 | 1.1468 | 0.05563 | 0.72749 | 0.21619 | 1.1469
WEDA | West Dalby | SW | WEDA_33kV_BUS 1 | 33 | 5.1869 | 296.4689 | 4.7202 | 89.9327 | 4.3223 | 4.7964 | 91.3843 | 5.1659 | 98.4236 | 1.4438 | 3.7743 | 1.2227 | 5.1224 | 1.445 | 3.7744
WEDA | West Dalby | SW | WEDA_33kV_BUS 2 | 33 | 5.1869 | 296.4689 | 4.7202 | 89.9327 | 4.3223 | 4.7964 | 91.3843 | 5.1659 | 98.4236 | 1.4438 | 3.7743 | 1.2227 | 5.1224 | 1.445 | 3.7744
WEMA | West Mackay (TF2) | MK | WEMA_11kV_BUS 1 | 11 | 12.0541 | 229.662 | 13.3678 | 84.897 | 15.0403 | 12.7612 | 81.0446 | 12.9584 | 82.2968 | 0.04517 | 0.57779 | 0.02037 | 0.40697 | 0.04508 | 0.57913
WEMA | West Mackay (TF1) | MK | WEMA_11kV_BUS 2 | 11 | 12.0541 | 229.662 | 13.3678 | 84.897 | 15.0403 | 12.7612 | 81.0446 | 12.9584 | 82.2968 | 0.04517 | 0.57779 | 0.02037 | 0.40697 | 0.04508 | 0.57913
WEMA | West Mackay (TF1) | MK | WEMA_33kV_TEF T1 | 33 | 12.9994 | 743.017 | 16.3351 | 311.226 | 22.1882 | 15.9379 | 303.6569 | 15.6468 | 298.1118 | 0.25252 | 1.5923 | 0.12091 | 0.60121 | 0.25173 | 1.6044
WEMA | West Mackay (TF2) | MK | WEMA_33kV_TEF T2 | 33 | 13.5197 | 772.7565 | 18.323 | 349.1 | 28.7527 | 18.7393 | 357.0316 | 18.3238 | 349.1151 | 0.2276 | 1.5334 | 0.07128 | 0.31213 | 0.22681 | 1.5454
WETO | West Toowoomba | SW | WETO_11kV_BUS 1 | 11 | 11.3272 | 215.8118 | 2.2611 | 14.3598 | 1.1546 | 10.3834 | 65.9436 | 9.2445 | 58.7106 | 0.05405 | 0.61446 | 9.0196 | 0.39172 | 0.054 | 0.61397
WETO | West Toowoomba | SW | WETO_11kV_BUS 2 | 11 | 11.3272 | 215.8118 | 2.2611 | 14.3598 | 1.1546 | 10.3834 | 65.9436 | 9.2445 | 58.7106 | 0.05405 | 0.61446 | 9.0196 | 0.39172 | 0.054 | 0.61397
WETO | West Toowoomba | SW | WETO_11kV_BUS 3 | 11 | 11.3272 | 215.8118 | 2.2611 | 14.3598 | 1.1546 | 10.3834 | 65.9436 | 9.2445 | 58.7106 | 0.05405 | 0.61446 | 9.0196 | 0.39172 | 0.054 | 0.61397
WETO | West Toowoomba | SW | WETO_11kV_BUS 4 | 11 | 11.3272 | 215.8118 | 2.2611 | 14.3598 | 1.1546 | 10.3834 | 65.9436 | 9.2445 | 58.7106 | 0.05405 | 0.61446 | 9.0196 | 0.39172 | 0.054 | 0.61397
WETO | West Toowoomba | SW | WETO_11kV_BUS 5 | 11 | 11.3272 | 215.8118 | 2.2611 | 14.3598 | 1.1546 | 10.3834 | 65.9436 | 9.2445 | 58.7106 | 0.05405 | 0.61446 | 9.0196 | 0.39172 | 0.054 | 0.61397
WETO | West Toowoomba | SW | WETO_11kV_BUS 6 | 11 | 11.3272 | 215.8118 | 2.2611 | 14.3598 | 1.1546 | 10.3834 | 65.9436 | 9.2445 | 58.7106 | 0.05405 | 0.61446 | 9.0196 | 0.39172 | 0.054 | 0.61397
WETO | West Toowoomba | SW | WETO_33kV_BUS 1 | 33 | 10.3331 | 590.6147 | 1.1449 | 21.8129 | 0.57722 | 9.2442 | 176.1259 | 8.6729 | 165.2401 | 0.3102 | 2.0047 | 54.2527 | -1.602 | 0.30974 | 2.0003
WETO | West Toowoomba | SW | WETO_33kV_BUS 2 | 33 | 10.3331 | 590.6147 | 1.1449 | 21.8129 | 0.57722 | 9.2442 | 176.1259 | 8.6729 | 165.2401 | 0.3102 | 2.0047 | 54.2527 | -1.602 | 0.30974 | 2.0003
WETO | West Toowoomba | SW | WETO_33kV_BUS 3 | 33 | 10.3331 | 590.6147 | 1.1449 | 21.8129 | 0.57722 | 9.2442 | 176.1259 | 8.6729 | 165.2401 | 0.3102 | 2.0047 | 54.2527 | -1.602 | 0.30974 | 2.0003
WETO | West Toowoomba | SW | WETO_33kV_BUS 4 | 33 | 10.3331 | 590.6147 | 1.1449 | 21.8129 | 0.57722 | 9.2442 | 176.1259 | 8.6729 | 165.2401 | 0.3102 | 2.0047 | 54.2527 | -1.602 | 0.30974 | 2.0003
WEWA | West Warwick | SW | WEWA_11kV_BUS 1 | 11 | 5.7965 | 110.4376 | 6.8471 | 43.4847 | 8.357 | 6.3544 | 40.3556 | 6.7031 | 42.5707 | 0.19526 | 1.1894 | 0.0358 | 0.65204 | 0.19119 | 1.1901
WEWA | West Warwick | SW | WEWA_11kV_BUS 2 | 11 | 5.7965 | 110.4376 | 6.8471 | 43.4847 | 8.357 | 6.3544 | 40.3556 | 6.7031 | 42.5707 | 0.19526 | 1.1894 | 0.0358 | 0.65204 | 0.19119 | 1.1901
WEWA | West Warwick | SW | WEWA_33kV_BUS 1 | 33 | 4.0974 | 234.1962 | 2.81 | 53.5376 | 2.1364 | 3.6704 | 69.9298 | 3.7425 | 71.3046 | 1.463 | 4.9019 | 2.8906 | 11.8055 | 1.4263 | 4.9081
WEWA | West Warwick | SW | WEWA_33kV_BUS 2 | 33 | 4.1327 | 236.2162 | 2.8514 | 54.327 | 2.1748 | 3.7059 | 70.6068 | 3.7767 | 71.9563 | 1.4473 | 4.8609 | 2.8419 | 11.5723 | 1.4106 | 4.8672
WIHI | Windy Hill | FN | WIHI_22kV_GEN G1 | 22 | 2.6344 | 100.3856 | 2.4447 | 31.0517 | 2.285 | 2.4721 | 31.3996 | 2.6244 | 33.335 | 1.1315 | 5.1814 | 0.56411 | 6.5219 | 1.012 | 5.2271
WIIS | Wiggins Island (TF1*C0114*ON) | CA | WIIS_132kV_BUS 1 | 132 | 16.4632 | 3764.003 | 14.5585 | 1109.5086 | 13.1941 | 15.7071 | 1197.0451 | 15.5954 | 1188.5314 | 0.58914 | 5.0579 | 0.89443 | 6.9707 | 0.59081 | 5.1214
WIIS | Wiggins Island (TF2*C0114*ON) | CA | WIIS_132kV_BUS 2 | 132 | 16.3987 | 3749.2535 | 14.486 | 1103.9799 | 13.1166 | 15.6382 | 1191.7899 | 15.5312 | 1183.6392 | 0.5934 | 5.0776 | 0.89961 | 7.0169 | 0.59507 | 5.1411
WIIS | Wiggins Island (TF1*C0114*ON) | CA | WIIS_132kV_TEF T1 | 132 | 16.4632 | 3764.003 | 14.5585 | 1109.5086 | 13.1941 | 15.7071 | 1197.0451 | 15.5954 | 1188.5314 | 0.58914 | 5.0579 | 0.89443 | 6.9707 | 0.59081 | 5.1214
WIIS | Wiggins Island (TF2*C0114*ON) | CA | WIIS_132kV_TEF T2 | 132 | 16.3987 | 3749.2535 | 14.486 | 1103.9799 | 13.1166 | 15.6382 | 1191.7899 | 15.5312 | 1183.6392 | 0.5934 | 5.0776 | 0.89961 | 7.0169 | 0.59507 | 5.1411
WIIS | Wiggins Island | CA | WIIS_22kV_TEF T1 | 22 | 21.0966 | 803.8873 | 4.4589 | 56.6361 | 2.4966 | 18.2658 | 232.0067 | 18.3132 | 232.6085 | 0.02762 | 0.66172 | 0.17654 | 8.0725 | 0.02766 | 0.66348
WIIS | Wiggins Island | CA | WIIS_22kV_TEF T2 | 22 | 21.0966 | 803.8873 | 4.4589 | 56.6361 | 2.4966 | 18.2658 | 232.0067 | 18.3132 | 232.6085 | 0.02762 | 0.66172 | 0.17654 | 8.0725 | 0.02766 | 0.66348
WINT | Winton | NQ | WINT_11kV_BUS 1 | 11 | 1.5225 | 29.0066 | 2.1677 | 13.7664 | 3.8443 | 2.2722 | 14.4304 | 2.3867 | 15.1578 | 1.609 | 4.2973 | 0.01355 | 0.45437 | 1.6161 | 4.3581
WINT | Winton | NQ | WINT_11kV_BUS 4 | 11 | 1.5225 | 29.0066 | 2.1677 | 13.7664 | 3.8443 | 2.2722 | 14.4304 | 2.3867 | 15.1578 | 1.609 | 4.2973 | 0.01355 | 0.45437 | 1.6161 | 4.3581
WINT | Winton | NQ | WINT_33kV_BUS | 33 | 0.35795 | 20.4598 | 0.45883 | 8.7419 | 0.64381 | 0.41948 | 7.9921 | 0.47204 | 8.9935 | 17.2187 | 55.9598 | 0.12586 | 20.156 | 17.2772 | 56.4984
WINT | Winton | NQ | WINT_66kV_BUS 1 | 66 | 0.32616 | 37.2851 | 0.20304 | 7.737 | 0.14883 | 0.28194 | 10.7432 | 0.29832 | 11.3675 | 55.1901 | 116.0584 | 108.1846 | 345.0531 | 55.4479 | 118.248
WIRR | Wirralie | NQ | WIRR_33kV_BUS | 33 | 0.17522 | 10.0152 | 0.18136 | 3.4554 | 0.18783 | 0.17442 | 3.3232 | 0.1824 | 3.4752 | 15.3497 | 118.6194 | 5.4868 | 107.5408 | 15.352 | 118.6212
WIRR | Wirralie | NQ | WIRR_66kV_TEF T1 | 66 | 0.70647 | 80.7605 | 0.49323 | 18.7946 | 0.37351 | 0.58672 | 22.3572 | 0.6885 | 26.2355 | 39.4515 | 44.3146 | 51.8973 | 130.1942 | 39.4609 | 44.3218
WOOD | Woodhouse Station | NQ | WOOD_11kV_TEF T1 | 11 | 0.27564 | 5.2516 | 0.27641 | 1.7554 | 0.27718 | 0.27584 | 1.7518 | 0.27621 | 1.7542 | 3.9398 | 25.0367 | 3.8485 | 24.8366 | 3.9392 | 25.0364
WOOD | Woodhouse Station | NQ | WOOD_66kV_TEF T1 | 66 | 5.2932 | 605.0966 | 4.3406 | 165.3991 | 3.6696 | 4.8612 | 185.2377 | 5.0205 | 191.3053 | 3.2875 | 7.2041 | 4.701 | 12.2966 | 3.2641 | 7.1945
WOOG | Woodgate | WB | WOOG_11kV_TEF T1 | 11 | 2.8559 | 54.412 | 3.1005 | 19.691 | 3.3889 | 2.9159 | 18.5184 | 3.0777 | 19.546 | 0.35744 | 2.4201 | 0.09425 | 1.8705 | 0.35609 | 2.4209
WOOG | Woodgate | WB | WOOG_66kV_TEF T1 | 66 | 1.9109 | 218.4487 | 1.2398 | 47.243 | 0.91547 | 1.662 | 63.3317 | 1.7701 | 67.4496 | 9.4748 | 19.7845 | 16.9823 | 55.2737 | 9.4262 | 19.8143
WOON | Woongarra | WB | WOON_3.3kV_BUS | 3.3 | 13.3691 | 76.4145 | 13.9259 | 26.5323 | 14.5486 | 13.6074 | 25.9256 | 13.7319 | 26.1628 | 0.01754 | 0.15579 | 0.01317 | 0.13717 | 0.01748 | 0.15598
WOON | Woongarra | WB | WOON_66kV_BUS | 66 | 5.4781 | 626.2313 | 4.8597 | 185.178 | 4.4023 | 5.1893 | 197.7405 | 5.2419 | 199.744 | 1.7485 | 7.4496 | 2.1599 | 10.2806 | 1.7235 | 7.5271
WOSO | Woodstock South (TF1) | NQ | WOSO_11kV_BUS 1 | 11 | 3.0519 | 58.1459 | 3.2662 | 20.7429 | 3.5048 | 3.0316 | 19.2529 | 3.3048 | 20.9885 | 0.45328 | 2.2437 | 0.08839 | 1.8514 | 0.45269 | 2.244
WOSO | Woodstock South | NQ | WOSO_66kV_BUS 1 | 66 | 2.1731 | 248.423 | 1.5514 | 59.1179 | 1.189 | 1.8095 | 68.9497 | 2.1259 | 81.0062 | 13.1359 | 14.1237 | 17.2061 | 40.1608 | 13.1149 | 14.1324
WOSO | Woodstock South | NQ | WOSO_66kV_BUS 2 | 66 | 2.1731 | 248.423 | 1.5514 | 59.1179 | 1.189 | 1.8095 | 68.9497 | 2.1259 | 81.0062 | 13.1359 | 14.1237 | 17.2061 | 40.1608 | 13.1149 | 14.1324
WOTO | Woolooga Town | WB | WOTO_11kV_BUS 1 | 11 | 6.0736 | 115.7172 | 6.8756 | 43.6658 | 7.9084 | 6.3209 | 40.1433 | 6.8298 | 43.3751 | 0.24341 | 1.1243 | 0.05308 | 0.7515 | 0.24265 | 1.1246
WOTO | Woolooga Town | WB | WOTO_11kV_BUS 2 | 11 | 6.0736 | 115.7172 | 6.8756 | 43.6658 | 7.9084 | 6.3209 | 40.1433 | 6.8298 | 43.3751 | 0.24341 | 1.1243 | 0.05308 | 0.7515 | 0.24265 | 1.1246
WOTO | Woolooga Town | WB | WOTO_11kV_BUS 3 | 11 | 6.0736 | 115.7172 | 6.8756 | 43.6658 | 7.9084 | 6.3209 | 40.1433 | 6.8298 | 43.3751 | 0.24341 | 1.1243 | 0.05308 | 0.7515 | 0.24265 | 1.1246
WOTO | Woolooga Town | WB | WOTO_66kV_TEF T2 | 66 | 2.781 | 317.9116 | 2.2644 | 86.2863 | 1.9042 | 2.4855 | 94.7099 | 2.6904 | 102.5161 | 6.8561 | 13.4243 | 8.0429 | 24.2501 | 6.8287 | 13.4365
WOWA | Wowan | CA | WOWA_22kV_BUS 1 | 22 | 2.6139 | 99.6038 | 3.098 | 39.3498 | 3.7759 | 2.7096 | 34.4161 | 3.1676 | 40.2341 | 1.9265 | 4.986 | 0.19644 | 2.9356 | 1.9267 | 4.9883
WOWA | Wowan | CA | WOWA_22kV_BUS 2 | 22 | 2.6139 | 99.6038 | 3.098 | 39.3498 | 3.7759 | 2.7096 | 34.4161 | 3.1676 | 40.2341 | 1.9265 | 4.986 | 0.19644 | 2.9356 | 1.9267 | 4.9883
WOWA | Wowan | CA | WOWA_22kV_BUS 3 | 22 | 2.6139 | 99.6038 | 3.098 | 39.3498 | 3.7759 | 2.7096 | 34.4161 | 3.1676 | 40.2341 | 1.9265 | 4.986 | 0.19644 | 2.9356 | 1.9267 | 4.9883
WOWA | Wowan | CA | WOWA_66kV_BUS 1 | 66 | 1.736 | 198.4495 | 1.1732 | 44.7045 | 0.87514 | 1.4465 | 55.1197 | 1.6759 | 63.8585 | 15.5709 | 18.4542 | 21.8269 | 56.2532 | 15.572 | 18.4752
WOWA | Wowan | CA | WOWA_66kV_BUS 2 | 66 | 1.736 | 198.4495 | 1.1732 | 44.7045 | 0.87514 | 1.4465 | 55.1197 | 1.6759 | 63.8585 | 15.5709 | 18.4542 | 21.8269 | 56.2532 | 15.572 | 18.4752
WOWA | Wowan | CA | WOWA_66kV_BUS 3 | 66 | 1.736 | 198.4495 | 1.1732 | 44.7045 | 0.87514 | 1.4465 | 55.1197 | 1.6759 | 63.8585 | 15.5709 | 18.4542 | 21.8269 | 56.2532 | 15.572 | 18.4752
YALK | Yalkula | FN | YALK_132kV_BUS | 132 | 2.3801 | 544.1604 | 2.4498 | 186.7028 | 2.5257 | 2.3812 | 181.4692 | 2.452 | 186.8659 | 8.7349 | 34.1217 | 6.0676 | 31.6344 | 8.3946 | 34.246
YANO | Yarranlea North SF | SW | YANO_110kV | 110 | 5.2076 | 992.1758 | 3.6516 | 231.9078 | 2.5935 | 4.7378 | 300.893 | 5.0206 | 318.8505 | 5.9646 | 12.0179 | 8.4401 | 30.9422 | 4.7296 | 11.1575
YARA | Yarranlea T010 (TF1) | SW | YARA_110kV_TEF T1 | 110 | 5.1802 | 986.9577 | 3.6458 | 231.5384 | 2.5996 | 4.706 | 298.8686 | 4.9951 | 317.2335 | 6.0165 | 12.0713 | 8.4188 | 30.8724 | 4.8019 | 11.2346
YARA | Yarranlea T010 (TF2) | SW | YARA_110kV_TEF T2 | 110 | 5.18 | 986.9288 | 3.6385 | 231.0783 | 2.5919 | 4.7054 | 298.8355 | 4.9936 | 317.1335 | 6.0173 | 12.0714 | 8.4564 | 30.9799 | 4.8026 | 11.2346
YARA | Yarranlea T010 | SW | YARA_33kV_BUS 1 | 33 | 6.812 | 389.3596 | 10.1735 | 193.8305 | 17.9433 | 10.7733 | 205.2586 | 10.7244 | 204.3273 | 0.57003 | 3.0237 | 0.03889 | 0.2035 | 0.43091 | 2.8649
YARA | Yarranlea T010 | SW | YARA_33kV_BUS 2 | 33 | 6.812 | 389.3596 | 10.1735 | 193.8305 | 17.9433 | 10.7733 | 205.2586 | 10.7244 | 204.3273 | 0.57003 | 3.0237 | 0.03889 | 0.2035 | 0.43091 | 2.8649
YARR | Yarraman | WB | YARR_11kV_BUS 1 | 11 | 3.8941 | 74.1918 | 4.7955 | 30.4553 | 6.1739 | 4.1288 | 26.2216 | 4.9757 | 31.6001 | 0.83184 | 1.5897 | 0.07835 | 0.82904 | 0.83063 | 1.5905
YARR | Yarraman | WB | YARR_11kV_BUS 2 | 11 | 3.8941 | 74.1918 | 4.7955 | 30.4553 | 6.1739 | 4.1288 | 26.2216 | 4.9757 | 31.6001 | 0.83184 | 1.5897 | 0.07835 | 0.82904 | 0.83063 | 1.5905
YARR | Yarraman | WB | YARR_66kV_BUS | 66 | 1.0876 | 124.3258 | 0.72832 | 27.7525 | 0.53729 | 0.89105 | 33.9535 | 1.0607 | 40.4196 | 27.1258 | 27.3848 | 36.9391 | 91.8631 | 27.0821 | 27.4112
YARW | Yarwun Switching Station | CA | YARW_66kV_pole4229800_tr_line_15129 | 66 | 2.7216 | 311.1191 | 1.8304 | 69.7481 | 1.3677 | 2.2994 | 87.6188 | 2.5982 | 99.0052 | 8.6784 | 12.7237 | 12.2467 | 36.531 | 8.6783 | 12.7402
YASO | Yarranlea South (TF1) | SW | YASO_11kV_BUS 1 | 11 | 2.1717 | 41.3756 | 2.2985 | 14.5974 | 2.4254 | 2.2204 | 14.1013 | 2.2607 | 14.3576 | 0.43347 | 3.1879 | 0.26891 | 2.6908 | 0.41801 | 3.1703
YASO | Yarranlea South (TF2) | SW | YASO_11kV_BUS 2 | 11 | 2.1717 | 41.3756 | 2.2985 | 14.5974 | 2.4254 | 2.2204 | 14.1013 | 2.2607 | 14.3576 | 0.43347 | 3.1879 | 0.26891 | 2.6908 | 0.41801 | 3.1703
YASO | Yarranlea South | SW | YASO_33kV_BUS | 33 | 4.4474 | 254.2036 | 4.0428 | 77.0264 | 3.5675 | 4.2994 | 81.9142 | 4.2968 | 81.8653 | 1.481 | 4.4741 | 1.8832 | 6.0332 | 1.3419 | 4.3153
YEPP | Yeppoon | CA | YEPP_11kV_BUS 1 | 11 | 11.3904 | 217.0164 | 14.2293 | 90.3679 | 18.8731 | 12.8989 | 81.9188 | 14.3661 | 91.2373 | 0.17548 | 0.58769 | 0.0126 | 0.25217 | 0.17434 | 0.58775
YEPP | Yeppoon | CA | YEPP_11kV_BUS 2 | 11 | 11.3904 | 217.0164 | 14.2293 | 90.3679 | 18.8731 | 12.8989 | 81.9188 | 14.3661 | 91.2373 | 0.17548 | 0.58769 | 0.0126 | 0.25217 | 0.17434 | 0.58775
YEPP | Yeppoon | CA | YEPP_22kV_BUS 1 | 22 | 2.1101 | 80.4047 | 1.013 | 12.867 | 0.66532 | 1.8179 | 23.0906 | 1.8962 | 24.0848 | 0.90013 | 6.5601 | 0.05078 | 28.216 | 0.89557 | 6.5604
YEPP | Yeppoon | CA | YEPP_22kV_BUS 2 | 22 | 2.1101 | 80.4047 | 1.013 | 12.867 | 0.66532 | 1.8179 | 23.0906 | 1.8962 | 24.0848 | 0.90013 | 6.5601 | 0.05078 | 28.216 | 0.89557 | 6.5604
YEPP | Yeppoon | CA | YEPP_22kV_BUS 3 | 22 | 2.1101 | 80.4047 | 1.013 | 12.867 | 0.66532 | 1.8179 | 23.0906 | 1.8962 | 24.0848 | 0.90013 | 6.5601 | 0.05078 | 28.216 | 0.89557 | 6.5604
YEPP | Yeppoon | CA | YEPP_66kV_BUS 1 | 66 | 3.1233 | 357.0424 | 2.045 | 77.9268 | 1.5147 | 2.7145 | 103.4347 | 2.9029 | 110.6154 | 5.863 | 12.072 | 10.1306 | 33.3431 | 5.8219 | 12.0743
YEPP | Yeppoon | CA | YEPP_66kV_BUS 2 | 66 | 3.1233 | 357.0424 | 2.045 | 77.9268 | 1.5147 | 2.7145 | 103.4347 | 2.9029 | 110.6154 | 5.863 | 12.072 | 10.1306 | 33.3431 | 5.8219 | 12.0743