## Disclaimer
Distribution Feeder Limitations
(Ergon Energy Distribution Annual Planning Report 2021)
This workbook forms part of the Ergon Energy Distribution Annual Planning Report 2021 (DAPR) and should be read in conjunction with the report document.
Readers are encouraged to take into account the details and content portrayed in the ‘Introduction & Notes’ section of this workbook when reviewing the associated data.
Disclaimer
Ergon Energy’s Distribution Annual Planning Report (DAPR) is prepared and made available solely for information purposes. While care was taken in the preparation of the information in the DAPR, and it is provided in good faith, Ergon Energy accepts no responsibility or liability (including without limitation, liability to any person by reason of negligence or negligent mis-statement) for any loss or damage that may be incurred by any person acting in reliance on this information or assumptions drawn from it, except to the extent that liability under any applicable Queensland or Commonwealth of Australia statute cannot be excluded.
It contains assumptions regarding, among other things, economic growth and load forecasts which may or may not prove to be correct. The forecasts included in the DAPR involve subjective judgements and analysis which are subject to significant uncertainties and contingencies, many of which are out of the control of Ergon Energy. Ergon Energy makes no representation or warranty as to the accuracy, reliability, completeness or suitability for any particular purpose of the information in this document. All information should be independently investigated, reviewed, analysed and verified, and must not be relied upon in connection with any investment proposal or decision. The information contained in the DAPR is subject to annual review. Ergon Energy is obligated to publish future editions by 31st December, in accordance with the National Electricity Rules.
All financials presented in the DAPR or within this document are correct at the time of writing and represent the existing organisational accounting treatment, which may be subject to change. Energy Queensland is finalising the alignment of its Cost Allocation Methodology between Ergon Energy and Energex, potentially impacting the treatment of some Capital and Operational Project costs.
Forecasted data is subject to ongoing variation due to COVID 19 impacts.
All presented project costings and milestones (as of October 2021) are subject to change.

## Introduction & Notes
Distribution Feeder Limitations
(Ergon Energy Distribution Annual Planning Report 2021)
This workbook presents primary distribution feeders which are currently experiencing overload or are forecast to experience an overload in the next 2 years.
This workbook forms part of the Ergon Energy Distribution Annual Planning Report 2021 (DAPR) and should be read in conjunction with the report document.
Forecasted data is subject to ongoing variation due to COVID 19 impacts.
Contents
The 'Distribution Feeder Limitations' tab of this workbook includes the following information for each constrained distribution feeder:
- Ergon Energy region
- Distribution feeder name, ID & location
- Load exceedance after 2 yrs (MVA)
- Forecast season that exceedance occurs (Summer / Winter)
- Forecast year that exceedance occurs
- Forecast month/s that exceedance occurs
- Load reduction needed to delay the exceedance by 12 months (MW)
(assumed power factor of 0.9)
1. Potential Solutions
Suggested solutions, in order or preference, are included under the 'Potential Solutions' tab.
2. Committed Solutions:
Committed investments to address current distribution network limitations are included under the 'Committed Solutions' tab.
Connection points for possible load reduction:
In all cases, the connection point to apply load reduction would be downsteam of the substation exit feeder cable and/or first section of line.
Exclusions:
Dedicated customer connection assets are excluded from the analysis.
NOTE: All financials presented in this document are correct at the time of writing (i.e. October 2021) and represent the existing organisational accounting treatment, which may be subject to change. Energy Queensland is still finalising the alignment of its Cost Allocation Methodology between Ergon and Energex, potentially impacting the treatment of some Capital and Operational Project costs.

## Potential Solutions
Solutions:
Distribution feeder capacity problems can be solved in a number of ways, depending on the local characteristics of the distribution feeder. The constraints identified in this document are a trigger for further planning studies and in many cases do not constitute plant risk, are acceptable, and do not require augmentation due to multiple factors such as:
- Minimal load growth on the feeder and/or adjacent feeders.
- Customer density or feeder topology constraints that do not allow for planning constraints to be met.
- Feeder topology that allows for simple switching in a contingency but for regional depot support is configured in a certain manner.
- Short term customer behaviour changes (such as abnormal weather conditions).
- Medium term network topology changes due to planned works in a region.
Where action is required to solve a feeder constraint, possible solutions (in approximate order of preference based on network cost) include:
Network Reconfiguration
- Transferring existing load to adjacent feeders if capacity is available; and
- Re-rating or dynamic rating of the underground exit cable or overhead feeder.
Demand Management initiatives that reduce customer loading
- Energy efficient appliances
- Power factor correction
- Shift loads (e.g. pool pumps, HW storage etc.) to control load tariff
- Shift loads to a time-of-use tariff
- Air conditioning ‘Peak Smart’
- Customer EG units
- Call off load
- Commercial and industrial demand management
- Customer embedded generation to ‘peak lop’
- Network embedded generation to ‘peak lop’
- Energy storage.
Network Augmentation
- Replacing the underground exit cable or overhead feeder
- Creating new substations and/or feeders and transferring existing load.
In each instance, actual solutions are subject to a detailed study and business case. In some cases, a committed project is already in place.

## Distribution Feeder Limit 2021
Distribution Feeder Limitations (Ergon Energy Distribution Annual Planning Report 2021)
Region | Feeder name | Feeder ID | Feeder Location | Load exceedance after 2 yrs (MVA) | Season of exceedance | Year of exceedance | Month of exceedance | Load reduction to defer exceedance by 12 mths (MW) @ 0.9pf | Connection Point | Potenital Solutions
Northern | GE-01 | 25273297 | GLENELG 66/19.1KV SUB (GLEE) | 0.0856 | Summer | 2020/2021 | Dec-Feb | 0.077 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | SB202 | 40200483 | SBSS SOUTH BLACKWATER 66/22KV SUB | 0.0973 | Summer | 2020/2021 | Dec-Feb | 0.0876 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | RS-H | 50000168 | ROCKY STREET 66/11KV SUB (RS) | 0.817 | Summer | 2020/2021 | Dec-Feb | 0.7819 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | F4468 | 82912886 | KEARNEYS SPRINGS 110/11KV SUB (KESP) | 1.9999 | Summer | 2020/2021 | Dec-Feb | 1.9542 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | HP-03 | 20007314 | HERMIT PARK 66/11KV SUB (HP) | 0.7963 | Summer | 2020/2021 | Dec-Feb | 0.746 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | KR-C | 50000092 | KINGAROY 66/11KV SUB (KING) | 1.4616 | Summer | 2020/2021 | Dec-Feb | 1.3154 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | F4610 | 60330968 | T116 TORRINGTON 110/33/11KV SUB | 1.6492 | Winter | 2020/2021 | Mar-Nov | 1.3795 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | 3220 | 84653808 | WIRR (WIRRALIE) 66/33KV SUBSTATION | 0.0326 | Summer | 2020/2021 | Dec-Feb | 0.0293 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | 2HAM | 83896573 | EDMONTON 132/22KV SUB (EDMONTON) | 1.936 | Summer | 2020/2021 | Dec-Feb | 1.6742 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | PB-C | 50000154 | PIALBA 66/11KV SUB (PB) | 0.9835 | Summer | 2020/2021 | Dec-Feb | 0.8851 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | RG114 | 40001135 | RTON GLENMORE RD 132/66/11KV SUB (RGBS) | 0.8807 | Summer | 2020/2021 | Dec-Feb | 0.7927 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | 2NOR | 10020673 | NORMANTON 66/22KV SUB (NORM) | 0.0455 | Summer | 2020/2021 | Dec-Feb | 0.0657 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | GC-C | 50000059 | GOOTCHIE 66/11KV SUB | 0.0139 | Summer | 2020/2021 | Dec-Feb | 0.0125 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | F3055 | 60026754 | NORTH STREET 33/11KV SUB (NOST) (ME020) | 0.7391 | Summer | 2020/2021 | Dec-Feb | 0.6652 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | F133R | 60026691 | ROMA WEST 33/11KV SUB | 0.3083 | Summer | 2020/2021 | Dec-Feb | 0.2775 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | HP-04 | 20007334 | HERMIT PARK 66/11KV SUB (HP) | 0.4892 | Summer | 2020/2021 | Dec-Feb | 0.4403 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | F3843 | 60026797 | OAKEY 33/11KV SUB (OAKE) | 1.0127 | Summer | 2020/2021 | Dec-Feb | 0.9115 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | WB-J | 50000211 | WEST BUNDABERG 66/11KV SUB (WEBU) | 0.8886 | Summer | 2020/2021 | Dec-Feb | 0.7512 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | 417 | 83909007 | MORANBAH 132/66/11KV SUB (MORA) | 0.8698 | Summer | 2020/2021 | Dec-Feb | 0.7369 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | RS109 | 40001146 | RSSS ROCKHAMPTON SOUTH 66/11KV SUB | 0.2935 | Summer | 2020/2021 | Dec-Feb | 0.2904 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | CN103 | 40001091 | CANNING STREET 66/11KV SUB (CNSS) | 0.4265 | Summer | 2020/2021 | Dec-Feb | 0.4267 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | WB-F | 50000207 | WEST BUNDABERG 66/11KV SUB (WEBU) | 0.4529 | Summer | 2020/2021 | Dec-Feb | 0.4076 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | CN108 | 40001094 | CANNING STREET 66/11KV SUB (CNSS) | 0.3392 | Summer | 2020/2021 | Dec-Feb | 0.3474 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | GA-02 | 20005832 | GARBUTT (TO46) 132/66/11KV SUB (GA) | 0.3304 | Summer | 2020/2021 | Dec-Feb | 0.2974 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | FV110 | 40001099 | FRENCHVILLE 66/11KV SUB (FVSS) | 0.3711 | Summer | 2020/2021 | Dec-Feb | 0.334 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | DG-04 | 20004700 | DAN GLEESON 132/66/11KV SUB (DAGL) | 0.377 | Summer | 2020/2021 | Dec-Feb | 0.3393 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | RG104 | 40001128 | RTON GLENMORE RD 132/66/11KV SUB (RGBS) | 0.2379 | Summer | 2020/2021 | Dec-Feb | 0.2443 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | RS105 | 40001143 | RSSS ROCKHAMPTON SOUTH 66/11KV SUB | 0.1588 | Summer | 2020/2021 | Dec-Feb | 0.1429 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | F088S | 60322051 | SAINT GEORGE TOWN 33/11KV SUB | 0.0432 | Summer | 2020/2021 | Dec-Feb | 0.0514 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | BLRI-08 | 82914276 | BLACKRIVER 66/11KV SUB (BLRI) | 0.3575 | Summer | 2020/2021 | Dec-Feb | 0.2398 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | GA-05 | 20005919 | GARBUTT (TO46) 132/66/11KV SUB (GA) | 0.0004 | Summer | 2020/2021 | Dec-Feb | 0.0684 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | AL-10 | 25274650 | ALAN SHERRIFF 132/11KV SUB (ALSH) | 0.0375 | Summer | 2020/2021 | Dec-Feb | 0.0337 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | DG-10 | 20004903 | DAN GLEESON 132/66/11KV SUB (DAGL) | 0.0447 | Summer | 2020/2021 | Dec-Feb | 0.0403 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | BO11 | 82982249 | BOHLE 66/11KV SUB (BOHL) | 0.0187 | Summer | 2020/2021 | Dec-Feb | 0.056 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | KR-G | 50000096 | KINGAROY 66/11KV SUB (KING) | 2.1438 | Summer | 2020/2021 | Dec-Feb | 1.9294 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Central | 216 | 30053783 | MORANBAH 132/66/11KV SUB (MORA) | 1.4863 | Summer | 2020/2021 | Dec-Feb | 1.3377 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | F3385 | 60026776 | PAMPAS 33/11KV SUB | 0.033136 | Summer | 2020/2021 | Dec-Feb | 0.14754 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Central | MA108 | 40001110 | MASS MALCHI 66/11KV SUB | 1.5441 | Summer | 2020/2021 | Dec-Feb | 1.3377 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | 2RIR | 10020825 | GORDONVALE 22KV SUB (GORDONVALE) | 2.7664 | Summer | 2020/2021 | Dec-Feb | 2.1262 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Central | MA123 | 82561111 | MASS MALCHI 66/11KV SUB | 1.5441 | Summer | 2020/2021 | Dec-Feb | 1.3377 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Central | 389 | 30189394 | PLANELLA 33/11KV SUB (PLAN) | 1.6979 | Summer | 2020/2021 | Dec-Feb | 1.418 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | F4130 | 60026820 | EAST TOOWOOMBA 33/11KV SUB | 1.143 | Summer | 2020/2021 | Dec-Feb | 1.0287 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | MC-E | 50000110 | MARYBOROUGH CITY 66/11KV SUB | 1.0529 | Summer | 2020/2021 | Dec-Feb | 1.0328 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet

## Committed Solutions 2021
WR Ref. | Limitation | Location | Committed Solution | Region
1387849 | Distribution Feeder Limitation Address voltage constraint | Multiple Locations | Arena Noja Synchrophasor - Target Comissioning: Dec-20 - Cost: $1.3M ± 30% | Southern
328478 | Distribution Feeder Limitation Address capacity constraints | GRAC - Gracemere | Gracemere Substation - New Feeder 3x Exits and SKID - Target Comissioning: Apr-22 - Cost: $1.9M ± 30% | Southern
1677841 | Distribution Feeder Limitation Address capacity constraints | SOMA - South Mackay | Milton St Feeder Tie - Install new RMU and conductor rebuild - Target Comissioning: Mar-23 - Cost: $0.4M ± 30% | Northern
1665340 | Distribution Feeder Limitation Address reliability issues | DEGI - Degilbo | Install 11kV SWER isolator and ACR for Coringa Feeder and subsequent SWER - Target Comissioning: Mar-23 - Cost: $0.1M ± 30% | Southern
1632592 | Distribution Feeder Limitation Addess capacity constraints | MORA - Moranbah | Reconductor 1.8km Township No.4 Feeder from Moranbah - Target Comissioning: Dec-22 - Cost: $0.3M ± 30% | Northern
1631930 | Distribution Feeder Limitation Address feeder capacity | FREN - Frenchville | Install three Air Break Switches (ABS) and recofigure Norman Rd 11kV Feeder - Target Comissioning: Mar-23 - Cost: $0.2M ± 30% | Southern
1631927 | Distribution Feeder Limitation Address voltage constraints | MOUR - Moura | Install new SWER voltage regulator and reconductor 4.5km of the Moura Rural 22kV Feeder - Target Comissioning: Apr-23 - Cost: $0.4M ± 30% | Southern
1631924 | Distribution Feeder Limitation Address voltage constraints | PAND - Pandoin | Reconductor 3.6km of Glendale Rd 22kV Feeder - Target Comissioning: Mar-23 - Cost: $0.4M ± 30% | Southern
1629313 | Distribution Feeder Limitation Addess load transfer constraints | MILL - Millaroo | Reconductor constrained distribution feeder (F3535) from Millmerran - Target Comissioning: Feb-23 - Cost: $0.9M ± 30% | Southern
1614080 | Distribution Feeder Limitation Address voltage and capacity constraints | GOOT - Gootchie | Replace distribution transformers and reconductor line for Glenwood Feeder - Target Comissioning: Mar-23 - Cost: $0.4M ± 30% | Southern
1603258 | Distribution Feeder Limitation Address capacity constraints | MIRA - Mirani | Reroute and replace conductor for both Mirani and Wier 11kV Feeders - Target Comissioning: Jul-23 - Cost: $0.5M ± 30% | Northern
1567115 | Distribution Feeder Limitation Addess capacity constraints | CONO - Collinsville North | Removal of SCS Collinsville Solar PV Construction near Collinsville North - Low Risk - Target Comissioning: Jun-21 - Cost: $0.3M ± 30% | Northern
1562527 | Distribution Feeder Limitation Address voltage unbalance constraints | CARI - Cape River | Install 11kV Close Delta Voltage Regulators with communications for the CR-01 Feeder - Target Comissioning: Mar-23 - Cost: $0.1M ± 30% | Northern
1519581 | Distribution Feeder Limitation Addess capacity constraints | CONO - Collinsville North | Removal of SCS Collinsville Solar PV Construction near Collinsville North - High Risk - Target Comissioning: Mar-21 - Cost: $0.8M ± 30% | Northern
1503629 | Distribution Feeder Limitation Address capacity constraints | PLAN - Planella | Install new RMU and conductor 11kV Blacks Beach Feeder - Target Comissioning: Jul-23 - Cost: $0.8M ± 30% | Northern
1451730 | Distribution Feeder Limitation Address voltage constraints | PAND - Pandoin | Upgrade of Millman Rd (PD203) feeder from Pandoin - Target Comissioning: Jan-22 - Cost: $0.8M ± 30% | Southern
1422990 | Distribution Feeder Limitation Address voltage constraints | STTO - Stanthorpe Town | 33kV Stage 3 work for distribution feeder (F4135) from Ballandean - Target Comissioning: Jan-23 - Cost: $0.3M ± 30% | Southern
1422989 | Distribution Feeder Limitation Address voltage and capacity constraints | STTO - Stanthorpe Town | Stanthorpe Town Substation - F4135 Short St 33 Feeder Ballandean 33kV Stage 2 - Target Comissioning: Jan-23 - Cost: $0.4M ± 30% | Southern
1401431 | Distribution Feeder Limitation Address capacity constraints | EDMO - Edmonton | Install 2km of underground cable and reconfigure 22kV Hambledon (2HAM) Feeder - Target Comissioning: Nov-23 - Cost: $1.5M ± 30% | Northern
1397957 | Distribution Feeder Limitation Addess capacity constraints | SOTO - South Toowoomba | Increase design temperature for distribution feeder (F4715) from South Toowoomba - Target Comissioning: Nov-21 - Cost: $0.4M ± 30% | Southern
1186380 | Distribution Feeder Limitation Addess capacity constraints | DURO - Duchess Road | New feeder tie (DR-08 and DR-12) from Duchess Road - Target Comissioning: Feb-22 - Cost: $0.5M ± 30% | Northern
1185511 | Distribution Feeder Limitation Address voltage constraints | TULL - Tully | Reconductor 2.9km of distribution feeder (2TMI) - Tully - Target Comissioning: Apr-22 - Cost: $0.3M ± 30% | Northern
1183459 | Distribution Feeder Limitation Address voltage constraints | NOCL - North Cloncurry | Reconductor 31km (NC-02 Feeder) from North Cloncurry - Target Comissioning: Mar-22 - Cost: $1.5M ± 30% | Northern
1183343 | Distribution Feeder Limitation Address voltage constraints | HUGH - Hughenden | Install SWER Reactors - Hughenden - Target Comissioning: Dec-21 - Cost: $0.2M ± 30% | Northern
1180974 | Distribution Feeder Limitation Addess capacity constraints | ALSH - Alan Sherriff | Reconductor 1.4km (ALSH-08) - Alan Sherriff - Target Comissioning: Jun-21 - Cost: $0.5M ± 30% | Northern
1175062 | Distribution Feeder Limitation Addess capacity constraints | BLRI - Black River | New underground feeder 5km and 2x 11kV 3 switch GMS at Black River - Target Comissioning: Sep-21 - Cost: $1.4M ± 30% | Northern
1174163 | Distribution Feeder Limitation Address voltage constraints | GLEE - Glenelg | Switched reactors from Glenelg - Target Comissioning: May-22 - Cost: $0.3M ± 30% | Northern
1173715 | Distribution Feeder Limitation Addess capacity constraints | MOPA - Mona Park | New overhead Cherry feeder 2.5km from Mona Park MONA-06) - Target Comissioning: Feb-23 - Cost: $0.2M ± 30% | Northern
1173703 | Distribution Feeder Limitation Address voltage constraints | BAMB - Bambaroo | New 3km overhead feeder from Bambaroo (BA-02) - Target Comissioning: Oct-21 - Cost: $0.3M ± 30% | Northern
1171451 | Distribution Feeder Limitation Addess capacity constraints | PAMP - Pampas | Install 3x200A regulator (F3385) - Pampas - Target Comissioning: Jan-22 - Cost: $0.3M ± 30% | Southern
1170934 | Distribution Feeder Limitation Addess capacity constraints | GOOB - Gooburrum | Upgrade exit cable (FD-1489) from Gooburrum - Target Comissioning: Nov-21 - Cost: $0.6M ± 30% | Southern
168413 | Distribution Feeder Limitation Addess capacity constraints | KESP - Kearneys Spring | Establish 3x Distribution Feeders out of Kearneys Spring - Target Comissioning: Jun-22 - Cost: $4.9M ± 30% | Southern
1635558 | Distribution Feeder Limitation Address capacity constraints | KAME - Kamerunga | Replace 650m conductor of 22kV Cook No.1 (2CO1) Feeder - Target Comissioning: Jan-23 - Cost: $0.4M ± 30% | Northern
1635552 | Distribution Feeder Limitation Address capacity constraints | EDMO - Edmonton | Install recloser, gas switch and reconductor sections of 22kV Hambledon (2HAM) Feeder - Target Comissioning: Mar-23 - Cost: $0.3M ± 30% | Northern