## Disclaimer
Distribution Feeder Limitations
(Ergon Energy Distribution Annual Planning Report 2019-20 to 2023-24)
This workbook forms part of the Ergon Energy Distribution Annual Planning Report 2019-20 to 2023-24 (DAPR) and should be read in conjunction with the report document.
Readers are encouraged to take into account the details and content portrayed in the ‘Introduction & Notes’ section of this workbook when reviewing the associated data.
Disclaimer
Ergon Energy’s Distribution Annual Planning Report (DAPR) is prepared and made available solely for information purposes. While care was taken in the preparation of the information in the DAPR, and it is provided in good faith, Ergon Energy accepts no responsibility or liability (including without limitation, liability to any person by reason of negligence or negligent mis-statement) for any loss or damage that may be incurred by any person acting in reliance on this information or assumptions drawn from it, except to the extent that liability under any applicable Queensland or Commonwealth of Australia statute cannot be excluded.
It contains assumptions regarding, among other things, economic growth and load forecasts which may or may not prove to be correct. The forecasts included in the DAPR involve subjective judgements and analysis which are subject to significant uncertainties and contingencies, many of which are out of the control of Ergon Energy. Ergon Energy makes no representation or warranty as to the accuracy, reliability, completeness or suitability for any particular purpose of the information in this document. All information should be independently investigated, reviewed, analysed and verified, and must not be relied upon in connection with any investment proposal or decision. The information contained in the DAPR is subject to annual review. Ergon Energy is obligated to publish future editions by 31st December, in accordance with the National Electricity Rules.
All financials presented in the DAPR or within this document are correct at the time of writing and represent the existing organisational accounting treatment, which may be subject to change. Energy Queensland is finalising the alignment of its Cost Allocation Methodology between Ergon Energy and Energex, potentially impacting the treatment of some Capital and Operational Project costs.

## Introduction & Notes
Distribution Feeder Limitations
(Ergon Energy Distribution Annual Planning Report 2019-20 to 2023-24)
This workbook presents primary distribution feeders which are currently experiencing overload or are forecast to experience an overload in the next 2 years.
This workbook forms part of the Ergon Energy Distribution Annual Planning Report 2019-20 to 2023-24 (DAPR) and should be read in conjunction with the report document.
Contents
The 'Distribution Feeder Limitations' tab of this workbook includes the following information for each constrained distribution feeder:
- Ergon Energy region
- Distribution feeder name, ID & location
- Load exceedance after 2 yrs (MVA)
- Forecast season that exceedance occurs (Summer / Winter)
- Forecast year that exceedance occurs
- Forecast month/s that exceedance occurs
- Load reduction needed to delay the exceedance by 12 months (MW)
(assumed power factor of 0.9)
1. Potential Solutions
Suggested solutions, in order or preference, are included under the 'Potential Solutions' tab.
2. Committed Solutions:
Committed investments to address current distribution network limitations are included under the 'Committed Solutions' tab.
Connection points for possible load reduction:
In all cases, the connection point to apply load reduction would be downsteam of the substation exit feeder cable and/or first section of line.
Exclusions:
Dedicated customer connection assets are excluded from the analysis.
NOTE: All financials presented in this document are correct at the time of writing and represent the existing organisational accounting treatment, which may be subject to change. Energy Queensland is still finalising the alignment of its Cost Allocation Methodology between Ergon and Energex, potentially impacting the treatment of some Capital and Operational Project costs.

## Potential Solutions
Solutions:
Distribution feeder capacity problems can be solved in a number of ways, depending on the local characteristics of the distribution feeder. The constraints identified in this document are a trigger for further planning studies and in many cases do not constitute plant risk, are acceptable, and do not require augmentation due to multiple factors such as:
-Minimal load growth on the feeder and/or adjacent feeders.
-Customer density or feeder topology constraints that do not allow for planning constraints to be met.
-Feeder topology that allows for simple switching in a contingency but for regional depot support is configured in a certain manner.
-Short term customer behaviour changes (such as abnormal weather conditions).
-Medium term network topology changes due to planned works in a region.
Where action is required to solve a feeder constraint, possible solutions (in approximate order of preference based on network cost) include:
> Network Reconfiguration
- transferring existing load to adjacent feeders if capacity is available; and
- re-rating or dynamic rating of the underground exit cable or overhead feeder.
> Demand Management initiatives that reduce customer loading
- Energy efficient appliances
- Power factor correction
- Shift loads (e.g. pool pumps, HW storage etc.) to control load tariff
- Shift loads to a time-of-use tariff
- Air conditioning ‘Peak Smart’
- Customer EG units
- Call off load
- Commercial and industrial demand management
- Customer embedded generation to ‘peak lop’
- Network embedded generation to ‘peak lop’
- Energy storage.
> Network Augmentation:
- replacing the underground exit cable or overhead feeder
- creating new substations and/or feeders and transferring existing load.
In each instance, actual solutions are subject to a detailed study and business case. In some cases, a committed project is already in place.

## Distribution Feeder Limitations
Distribution Feeder Limitations (Ergon Energy Distribution Annual Planning Report 2019-20 to 2023-24)
Region | Feeder name | Feeder ID | Feeder Location | Load exceedance after 2 yrs (MVA) | Season of exceedance | Year of exceedance | Month of exceedance | Load reduction to defer exceedance by 12 mths (MW) @ 0.9pf | Connection Point | Possible solutions
Northern | HP-06 | 20007373 | HERMIT PARK 66/11KV SUB (HP) - Hermitpark No.06 | 1.3946 | Summer | 2018/2018 | Dec-Feb | 1.2493 | Refer to "Introduction & Notes" sheet | Refer to "Solutions" sheet
Northern | HP-04 | 20007334 | HERMIT PARK 66/11KV SUB (HP) - Hermitpark No.04 | 1.2201 | Summer | 2018/2018 | Dec-Feb | 1.1039 | Refer to "Introduction & Notes" sheet | Refer to "Solutions" sheet
Northern | 2HAM | 83896573 | EDMONTON 132/22KV SUB (EDMONTON) - Hambledon Fdr | 3.1632 | Summer | 2018/2018 | Dec-Feb | 2.7914 | Refer to "Introduction & Notes" sheet | Refer to "Solutions" sheet
Northern | HP-03 | 20007314 | HERMIT PARK 66/11KV SUB (HP) - Hermitpark No.03 | 1.2325 | Summer | 2018/2018 | Dec-Feb | 1.1191 | Refer to "Introduction & Notes" sheet | Refer to "Solutions" sheet
Northern | GE-01 | 25273297 | GLENELG 66/19.1KV SUB (GLEE) - Corfield Swer | 0.058582 | Summer | 2018/2018 | Dec-Feb | 0.052964 | Refer to "Introduction & Notes" sheet | Refer to "Solutions" sheet
Southern | F206C | 60026701 | CHARLEVILLE 66/22/11KV SUB (MW7) - Augathella | 0.52969 | Summer | 2018/2018 | Dec-Feb | 0.49152 | Refer to "Introduction & Notes" sheet | Refer to "Solutions" sheet
Northern | RM-05 | 20011656 | RASMUSSEN 66/11KV SUB (RASM) - Rasmussen No.05 | 1.4907 | Summer | 2018/2018 | Dec-Feb | 1.3458 | Refer to "Introduction & Notes" sheet | Refer to "Solutions" sheet
Southern | F2530 | 60026725 | CLIFTON 33/11KV SUB (ME399) - Clifton West | 0.32897 | Summer | 2018/2018 | Dec-Feb | 0.29262 | Refer to "Introduction & Notes" sheet | Refer to "Solutions" sheet
Northern | DG-07 | 20004796 | DAN GLEESON 132/66/11KV SUB (DG) - Dangleeson No.07 | 1.0126 | Summer | 2018/2018 | Dec-Feb | 0.85439 | Refer to "Introduction & Notes" sheet | Refer to "Solutions" sheet
Northern | BO-03 | 20002752 | BOHLE 66/11KV SUB (BOHL) - Bohle No.03 | 2.1418 | Summer | 2018/2018 | Dec-Feb | 1.781 | Refer to "Introduction & Notes" sheet | Refer to "Solutions" sheet
Southern | RG114 | 40001135 | RTON GLENMORE RD 132/66/11KV SUB (RGBS) - Wandal | 1.1301 | Summer | 2018/2018 | Dec-Feb | 1.025 | Refer to "Introduction & Notes" sheet | Refer to "Solutions" sheet
Southern | WL-A | 50000229 | WOOLOOGA 66/11KV SUB (WL) - Bells Bridge | 0.39798 | Summer | 2018/2018 | Dec-Feb | 0.34445 | Refer to "Introduction & Notes" sheet | Refer to "Solutions" sheet
Southern | 14100 | 85018902 | GLADSTONE SOUTH 132/66/11KV SUB (T019) - Philip Street | 1.4525 | Summer | 2018/2018 | Dec-Feb | 1.3072 | Refer to "Introduction & Notes" sheet | Refer to "Solutions" sheet
Northern | EA-04 | 20005482 | EAST AYR SPILLER ST 66/11KV SUB (EAAY) - Eastayr No.04 | 0.30697 | Summer | 2018/2018 | Dec-Feb | 0.27263 | Refer to "Introduction & Notes" sheet | Refer to "Solutions" sheet
Southern | F090S | 60026680 | ROO WORKS 33/11KV SUB (MC054) - Surat Road | 0.077377 | Summer | 2018/2018 | Dec-Feb | 0.072681 | Refer to "Introduction & Notes" sheet | Refer to "Solutions" sheet
Northern | BO-10 | 20003088 | BOHLE 66/11KV SUB (BOHL) - Bohle No.10 | 1.0312 | Summer | 2018/2018 | Dec-Feb | 0.86206 | Refer to "Introduction & Notes" sheet | Refer to "Solutions" sheet
Southern | F073C | 60026673 | CHINCHILLA 132/110/33KV SUB (T013) - Fairymeadow | 0.15704 | Summer | 2018/2018 | Dec-Feb | 0.48636 | Refer to "Introduction & Notes" sheet | Refer to "Solutions" sheet
Northern | AL26 | 83924127 | ALAN SHERRIFF 132/11KV SUB (ALSH) - Al26 | 1.131 | Summer | 2018/2018 | Dec-Feb | 0.99035 | Refer to "Introduction & Notes" sheet | Refer to "Solutions" sheet
Southern | WB-J | 50000211 | WEST BUNDABERG 66/11KV SUB (WEBU) - Avoca St | 1.3125 | Summer | 2018/2018 | Dec-Feb | 1.1393 | Refer to "Introduction & Notes" sheet | Refer to "Solutions" sheet
Southern | WV-E | 50000235 | WALLAVILLE 66/11KV SUB (WV) - Wallaville | 0.12795 | Summer | 2018/2018 | Dec-Feb | 0.11288 | Refer to "Introduction & Notes" sheet | Refer to "Solutions" sheet
Northern | BO-04 | 20002914 | BOHLE 66/11KV SUB (BOHL) - Bohle No.04 | 0.80081 | Summer | 2018/2018 | Dec-Feb | 0.72426 | Refer to "Introduction & Notes" sheet | Refer to "Solutions" sheet
Southern | KR-C | 50000092 | KINGAROY 66/11KV SUB (KING) - Kingaroy North | 1.1443 | Summer | 2018/2018 | Dec-Feb | 0.96087 | Refer to "Introduction & Notes" sheet | Refer to "Solutions" sheet
Northern | BN-07 | 20002698 | BOWEN 66/11KV SUB (BOWE) - Bowen No.07 | 0.75864 | Summer | 2018/2018 | Dec-Feb | 0.6793 | Refer to "Introduction & Notes" sheet | Refer to "Solutions" sheet
Northern | AL-08 | 25274647 | ALAN SHERRIFF 132/11KV SUB (ALSH) - Alan Sherriff No.08 11Kv Feeder | 0.90283 | Summer | 2018/2018 | Dec-Feb | 0.82149 | Refer to "Introduction & Notes" sheet | Refer to "Solutions" sheet
Southern | F3843 | 60026797 | OAKEY 33/11KV SUB (OAKE) - Oakey Abattoir | 1.0638 | Summer | 2018/2018 | Dec-Feb | 0.97349 | Refer to "Introduction & Notes" sheet | Refer to "Solutions" sheet
Northern | AL13 | 83879451 | ALAN SHERRIFF 132/11KV SUB (ALSH) - Al13 Fdr | 0.72206 | Summer | 2018/2018 | Dec-Feb | 0.66563 | Refer to "Introduction & Notes" sheet | Refer to "Solutions" sheet
Northern | 355 | 30053865 | MIRANI 66/11KV SUB (MIRA) - Mirani | 0.038587 | Summer | 2018/2018 | Dec-Feb | 0.013031 | Refer to "Introduction & Notes" sheet | Refer to "Solutions" sheet
Southern | F3055 | 60026754 | NORTH STREET 33/11KV SUB (NOST) (ME020) - Harlaxton | 0.62833 | Summer | 2018/2018 | Dec-Feb | 0.57687 | Refer to "Introduction & Notes" sheet | Refer to "Solutions" sheet
Southern | RS109 | 40001146 | ROCKHAMPTON SOUTH 66/11KV SUB (RSSS) - Denham St | 0.39336 | Summer | 2018/2018 | Dec-Feb | 0.37565 | Refer to "Introduction & Notes" sheet | Refer to "Solutions" sheet
Northern | BO-07 | 20003026 | BOHLE 66/11KV SUB (BOHL) - Bohle No.07 | 0.84153 | Summer | 2018/2018 | Dec-Feb | 0.69881 | Refer to "Introduction & Notes" sheet | Refer to "Solutions" sheet
Northern | DG-08 | 20004893 | DAN GLEESON 132/66/11KV SUB (DG) - Dangleeson No.08 | 0.62196 | Summer | 2018/2018 | Dec-Feb | 0.55977 | Refer to "Introduction & Notes" sheet | Refer to "Solutions" sheet
Northern | RASM-02 | 83897505 | RASMUSSEN 66/11KV SUB (RASM) - Rasmussen No.02 | 0.74125 | Summer | 2018/2018 | Dec-Feb | 0.65733 | Refer to "Introduction & Notes" sheet | Refer to "Solutions" sheet
Southern | BW210 | 40001035 | BLACKWATER 132/66/22KV SUB (BWBS) - Blackwater Town | 0.70645 | Summer | 2018/2018 | Dec-Feb | 0.69419 | Refer to "Introduction & Notes" sheet | Refer to "Solutions" sheet
Northern | 105 | 30053748 | CANNONVALE 66/11KV SUB (CANN) - Island Drive | 0.5413 | Summer | 2018/2018 | Dec-Feb | 0.44461 | Refer to "Introduction & Notes" sheet | Refer to "Solutions" sheet
Northern | DR-05 | 20005265 | DUCHESS ROAD 132/11KV SUB (DURO) - Duchessrd No.05 | 0.4893 | Summer | 2018/2018 | Dec-Feb | 0.47369 | Refer to "Introduction & Notes" sheet | Refer to "Solutions" sheet
Southern | RS105 | 40001143 | ROCKHAMPTON SOUTH 66/11KV SUB (RSSS) - East Lane | 0.36344 | Summer | 2018/2018 | Dec-Feb | 0.32445 | Refer to "Introduction & Notes" sheet | Refer to "Solutions" sheet
Northern | PA-16 | 25267836 | PETER ARLETT 66/11KV SUB (PA) - Peterarlett No.16 | 0.60427 | Summer | 2018/2018 | Dec-Feb | 0.51094 | Refer to "Introduction & Notes" sheet | Refer to "Solutions" sheet
Southern | F109R | 60026685 | ROMA EAST (MW002) 33/11KV SUB (MW002) - Bowen Street | 0.13508 | Summer | 2018/2018 | Dec-Feb | 0.14572 | Refer to "Introduction & Notes" sheet | Refer to "Solutions" sheet
Northern | GA-02 | 20005832 | GARBUTT (TO46) 132/66/11KV SUB (GA) - Garbutt No.02 | 0.38975 | Summer | 2018/2018 | Dec-Feb | 0.35409 | Refer to "Introduction & Notes" sheet | Refer to "Solutions" sheet
Southern | PB-C | 50000154 | PIALBA 66/11KV SUB (PB) - Doolong South | 0.43367 | Summer | 2018/2018 | Dec-Feb | 0.34215 | Refer to "Introduction & Notes" sheet | Refer to "Solutions" sheet
Southern | F3215 | 60026768 | EAST TOOWOOMBA 33/11KV SUB (ME085) - James Street | 0.20738 | Summer | 2018/2018 | Dec-Feb | 0.22015 | Refer to "Introduction & Notes" sheet | Refer to "Solutions" sheet
Southern | F3525 | 60026788 | WARWICK EAST 33/11KV SUB - Mill Hill | 0.39844 | Summer | 2018/2018 | Dec-Feb | 0.3763 | Refer to "Introduction & Notes" sheet | Refer to "Solutions" sheet
Southern | F4480 | 60026836 | EAST TOOWOOMBA 33/11KV SUB (ME085) - View Street | 0.44192 | Winter | 2018/2018 | Mar-Nov | 0.39325 | Refer to "Introduction & Notes" sheet | Refer to "Solutions" sheet
Southern | FV110 | 40001099 | FRENCHVILLE 66/11KV SUB (FVSS) - Norman Rd | 0.46937 | Summer | 2018/2018 | Dec-Feb | 0.38846 | Refer to "Introduction & Notes" sheet | Refer to "Solutions" sheet
Southern | RG104 | 40001128 | RTON GLENMORE RD 132/66/11KV SUB (RGBS) - Victoria Pde | 0.28673 | Summer | 2018/2018 | Dec-Feb | 0.26109 | Refer to "Introduction & Notes" sheet | Refer to "Solutions" sheet
Southern | CN108 | 40001094 | CANNING STREET 66/11KV SUB (CNSS) - Upper Dawson Rd | 0.31605 | Summer | 2018/2018 | Dec-Feb | 0.31365 | Refer to "Introduction & Notes" sheet | Refer to "Solutions" sheet
Northern | RM-08 | 20011759 | RASMUSSEN 66/11KV SUB (RASM) - Rasmussen No.08 | 0.27868 | Summer | 2018/2018 | Dec-Feb | 0.24776 | Refer to "Introduction & Notes" sheet | Refer to "Solutions" sheet
Northern | BL-02 | 20002331 | BLUEWATER 66/11KV SUB (BL) - Bluewater No.02 | 0.19365 | Summer | 2018/2018 | Dec-Feb | 0.14735 | Refer to "Introduction & Notes" sheet | Refer to "Solutions" sheet
Southern | CN103 | 40001091 | CANNING STREET 66/11KV SUB (CNSS) - Athelstane | 0.23898 | Summer | 2018/2018 | Dec-Feb | 0.23966 | Refer to "Introduction & Notes" sheet | Refer to "Solutions" sheet
Northern | AV-07 | 20001148 | AITKENVALE 66/11KV SUB (AV) - Aitkenvale No.07 | 0.19812 | Summer | 2018/2018 | Dec-Feb | 0.17236 | Refer to "Introduction & Notes" sheet | Refer to "Solutions" sheet
Southern | SB-J | 50000180 | SOUTH BUNDABERG 66/11KV SUB (SB) - Lows Rd | 0.21145 | Summer | 2018/2018 | Dec-Feb | 0.1903 | Refer to "Introduction & Notes" sheet | Refer to "Solutions" sheet
Northern | GA-08 | 20005978 | GARBUTT (TO46) 132/66/11KV SUB (GA) - Garbutt No.08 | 0.13389 | Summer | 2018/2018 | Dec-Feb | 0.14673 | Refer to "Introduction & Notes" sheet | Refer to "Solutions" sheet
Southern | F4575 | 60026841 | WEST WARWICK 33/11KV SUB (WEWA) - Wentworth Street | 0.13499 | Summer | 2018/2018 | Dec-Feb | 0.12836 | Refer to "Introduction & Notes" sheet | Refer to "Solutions" sheet
Southern | TQ-K | 82888836 | TORQUAY 66/11KV SUB (TORQ) - Dayman St | 0.30168 | Summer | 2018/2018 | Dec-Feb | 0.23199 | Refer to "Introduction & Notes" sheet | Refer to "Solutions" sheet
Northern | GA-05 | 20005919 | GARBUTT (TO46) 132/66/11KV SUB (GA) - Garbutt No.05 | 0.083902 | Summer | 2018/2018 | Dec-Feb | 0.096073 | Refer to "Introduction & Notes" sheet | Refer to "Solutions" sheet
Southern | WB-F | 50000207 | WEST BUNDABERG 66/11KV SUB (WEBU) - Foundry | 0.15832 | Summer | 2018/2018 | Dec-Feb | 0.1471 | Refer to "Introduction & Notes" sheet | Refer to "Solutions" sheet
Northern | 2HAR | 10134518 | EDMONTON 132/22KV SUB (EDMONTON) - Hardy Rd | 0.26358 | Summer | 2018/2018 | Dec-Feb | 0.21045 | Refer to "Introduction & Notes" sheet | Refer to "Solutions" sheet
Southern | CB-J | 82915259 | BUNDABERG CENTRAL 66/11KV SUB (BUCE) - Racecourse Fdr | 0.19279 | Summer | 2018/2018 | Dec-Feb | 0.15668 | Refer to "Introduction & Notes" sheet | Refer to "Solutions" sheet
Northern | AL01 | 83879448 | ALAN SHERRIFF 132/11KV SUB (ALSH) - Al01 Fdr | 0.072551 | Summer | 2018/2018 | Dec-Feb | 0.072342 | Refer to "Introduction & Notes" sheet | Refer to "Solutions" sheet
Southern | F4610 | 60330968 | TORRINGTON (T116) 110/33/11KV SUB (T116) - Westbrook | 0.28644 | Summer | 2018/2018 | Dec-Feb | 0.19297 | Refer to "Introduction & Notes" sheet | Refer to "Solutions" sheet
Southern | F4145 | 60026822 | SOUTH TOOWOOMBA 110/33/11KV SUB (T043) - Smithfield | 0.076404 | Winter | 2018/2018 | Mar-Nov | 0.093632 | Refer to "Introduction & Notes" sheet | Refer to "Solutions" sheet
Northern | BLRI-05 | 84737242 | BLACKRIVER 66/11KV SUB (BLRI) - Blri-05 Fdr | 0.2899 | Summer | 2018/2018 | Dec-Feb | 0.18103 | Refer to "Introduction & Notes" sheet | Refer to "Solutions" sheet
Southern | FV111 | 40001100 | FRENCHVILLE 66/11KV SUB (FVSS) - Frenchville Rd | 0.091174 | Summer | 2018/2018 | Dec-Feb | 0.082057 | Refer to "Introduction & Notes" sheet | Refer to "Solutions" sheet
Northern | 2MA1 | 10020838 | MAREEBA 66/22KV SUB (MAREEBA) - Mareeba No1 | 0.073698 | Summer | 2018/2018 | Dec-Feb | 0.0709 | Refer to "Introduction & Notes" sheet | Refer to "Solutions" sheet
Northern | 2TT1 | 10020764 | TULLY 132/22KV SUB (TULLY) - Tully Town No1 | 0.10174 | Summer | 2018/2018 | Dec-Feb | 0.075906 | Refer to "Introduction & Notes" sheet | Refer to "Solutions" sheet
Southern | KR-D | 50000093 | KINGAROY 66/11KV SUB (KING) - Coolabunia | 0.084398 | Summer | 2018/2018 | Dec-Feb | 0.058049 | Refer to "Introduction & Notes" sheet | Refer to "Solutions" sheet
Southern | F130R | 60026690 | ROMA WEST 33/11KV SUB (MW003) - Roma Hospital | 0.01434 | Summer | 2018/2018 | Dec-Feb | 0.01933 | Refer to "Introduction & Notes" sheet | Refer to "Solutions" sheet
Northern | OONN-08 | 82912323 | OONOONBA 66/11KV SUB (OONN) - Oonoonba No.08 | 0.29826 | Summer | 2018/2018 | Dec-Feb | 0.099491 | Refer to "Introduction & Notes" sheet | Refer to "Solutions" sheet

## Committed Solutions
WR Ref. | Limitation | Location | Committed Solution | Region
168413 | Distribution Feeder Limitation Address capacity constraints | KESP - Kearney Springs | Kearney Springs new 3xFdrs - Target Commissioning - Apr-22 - Cost: $3.5M ± 30% | Southern
328478 | Distribution Feeder Limitation Address capacity constraints | GRAC - Gracemere | Gracemere Substation 3 x 11kV Fdr Exits - GRAC SKID - Target Commissioning - Jun-21 - Cost: $1.3M ± 30% | Southern
648277 | Distribution Feeder Limitation Voltage quality of supply and voltage performance constraints | FD-1469 - Childers Town | Childers Town Feeder Upgrade 104 HDBC reconductor - Commissioned - Jul-19 - Cost: $0.3M ± 30% | Southern
1168639 | Distribution Feeder Limitation Voltage quality of supply and voltage performance constraints | FD-1574 - Torquay | TORQ Torquay - FD-1574 Reconductor 400m of 11kV Feeder - Commissioned - Jul-19 - Cost: $0.2M ± 30% | Southern
1168802 | Distribution Feeder Limitation Address voltage constraint | FD-3117 - Roma North | FD-3117 - Install a 19.1kV, 50A SWER volt reg, surge div, fuse - Target Commissioning - Apr-20 - Cost: $0.1M ± 30% | Southern
1168816 | Distribution Feeder Limitation Address voltage constraint | FD-3117 - Roma North | FD-3117 - Install a 19.1kV, 50A SWER volt reg, surge div, fuse - Target Commissioning - Jun-20 - Cost: $0.1M ± 30% | Southern
1170345 | Distribution Feeder Limitation Address voltage constraint | FD-3095 - Chinchilla | Chinchillla F069C 33kV Regulator FD-3095 - Target Commissioning - Jul-20 - Cost: $0.1M ± 30% | Southern
1170934 | Distribution Feeder Limitation Address capacity constraint | FD-1489 - Booyan | Booyan FD-1489 - Upgrade Exit Cable - Target Commissioning - Apr-21 - Cost: $0.1M ± 30% | Southern
1171124 | Distribution Feeder Limitation Address voltage constraint | FD-1934 - Walla Street Feeder | Bundaberg FD-1934 - Upgrade 11kV OH to Pluto - Commissioned - Sep-19 - Cost: $0.4M ± 30% | Southern
1171308 | Distribution Feeder Limitation Voltage quality of supply and voltage performance constraints | FD-1547 - Dunrowran | Dunrowan FD-1547 - Recond 3km 7/.080 Cu with with Moon/Iodine - Commissioned - Jul-19 - Cost: $0.5M ± 30% | Southern
1171855 | Distribution Feeder Limitation Address voltage constraint | KAME - Kamerunga | Kamerunga 2BLW 22kV OD 200A Reg CH24-5 - Commissioned - Aug-19 - Cost: $0.2M ± 30% | Northern
1173259 | Distribution Feeder Limitation Voltage quality of supply and voltage performance constraints | YEPP - Yeppoon | Yeppon - Upgrade UG cable to 400A - Target Commissioning - Dec-20 - Cost: $0.2M ± 30% | Southern
1173703 | Distribution Feeder Limitation Voltage quality of supply and voltage performance constraints | BAMB - Bambaroo | BAMB - 3km new OH conductor - Target Commissioning - Apr-21 - Cost: $0.3M ± 30% | Northern
1173715 | Distribution Feeder Limitation Address voltage and capacity constraints | MOPA - Mona Park | Mona Park - 2.5km new Cherry OH conductor - Target Commissioning - Oct-20 - Cost: $0.3M ± 30% | Northern
1177748 | Distribution Feeder Limitation Address capacity and load trasfer constraints | Multiple Locations | SafetyNet Implementation Central Stage 5TIER MIDD Motorised Isolator - Commissioned - Jul-19 - Cost: $0.7M ± 30% | NA
1177749 | Distribution Feeder Limitation Address asset condition | TR91697194 - Comet | SafetyNet Implementation Central Stage 6COME CM-T1 TR91697194 - Target Commissioning - Dec-19 - Cost: $2.1M ± 30% | Central
1178059 | Distribution Feeder Limitation Voltage quality of supply and voltage performance constraints | CLON - Cloncurry | Cloncurry - CC-01 2.2km OH reconductor (Stage 1) - Target Commissioning - Dec-20 - Cost: $0.01M ± 30% | Northern
1178076 | Distribution Feeder Limitation Address voltage and capacity constraints | PO5034142 - Einasleigh | Einasleigh New GE 2EIN 22kV CD 100A Reg G720A PO5034142 - Target Commissioning - Jan-20 - Cost: $0.4M ± 30% | Northern
1179339 | Distribution Feeder Limitation Address voltage and capacity constraints | KAME - Kamerunga | Kamerunga - 1.1km new UG cable - Commissioned - May-19 - Cost: $0.4M ± 30% | Northern
1180974 | Distribution Feeder Limitation Voltage quality of supply and voltage performance constraints | ALSH - Alan Sherriff | Alan Sherriff - 1.4km Reconductor - Target Commissioning - Jan-20 - Cost: $0.2M ± 30% | Northern
1181195 | Distribution Feeder Limitation Address voltage constraint | JUCR - Julia Creek | Julia Creek - Install Star Connected 50A Reg - Commissioned - Sep-19 - Cost: $0.2M ± 30% | Northern
1181196 | Distribution Feeder Limitation Address voltage constraint | JUCR - Julia Creek | Julia Creek New Fdr JC JC06 Star Connected 50A Reg JUCRSS - Commissioned - Sep-19 - Cost: $0.2M ± 30% | Northern
1181335 | Distribution Feeder Limitation Address voltage constraint | MOSI - Mount Sibly | Open-delta Reg PE11085 Upgrd to Clsd Del Strategic Closed Delta Regulator Program - Target Commissioning - Jun-21 - Cost: $0.1M ± 30% | Southern
1181336 | Distribution Feeder Limitation Address voltage constraint | KESP - Kearney Springs | Open-delta Regulator PE585378 Upgrd CD Strategic Closed Delta Regulator Program - Target Commissioning - Jun-21 - Cost: $0.1M ± 30% | Southern
1181337 | Distribution Feeder Limitation Address voltage constraint | SOTO - South Toowoomba | Open-delta Regulator PE581707 Upgrd CD Strategic Closed Delta Regulator Program - Target Commissioning - Sep-20 - Cost: $0.1M ± 30% | Southern
1181338 | Distribution Feeder Limitation Address voltage constraint | OAKE - Oakey | Open-delta Regulator PE09769 Upgrd to CD Strategic Closed Delta Regulator Program - Target Commissioning - Jun-21 - Cost: $0.1M ± 30% | Southern
1183366 | Distribution Feeder Limitation Address voltage constraint | SP-105991 - Sub, Ayr No.4 11kV feeder | Ayr - New SP-105991 - AY-01 100A ID Regulator - Target Commissioning - Dec-20 - Cost: $0.1M ± 30% | Northern
1183459 | Distribution Feeder Limitation Voltage quality of supply and voltage performance constraints | NOCL - North Cloncurry | North Cloncurry - NC-02 Reconductor 21km - Target Commissioning - Dec-21 - Cost: $0.04M ± 30% | Northern
1183478 | Distribution Feeder Limitation Address voltage and capacity constraints | KAME - Kamerunga | Kamerunga - 2FRE Feeder Extension - Target Commissioning - Jun-20 - Cost: $0.03M ± 30% | Northern
1183479 | Distribution Feeder Limitation Voltage quality of supply and voltage performance constraints | CANO - Cairns North | Cairns North - Reconductor 1.1km of OH 7/0.104 to Pluto - Target Commissioning - May-20 - Cost: $0.3M ± 30% | Northern
1183527 | Distribution Feeder Limitation Address capacity constraints | Multiple Locations | LR Strategy - fast first trip to ACRs - Commissioned - Sep-19 - Cost: $0.6M ± 30% | NA
1185382 | Distribution Feeder Limitation Address capacity and load trasfer constraints | GARB - Garbutt (T046) | Garbutt - GA-08 Reconfig and UG Ext - Target Commissioning - Mar-20 - Cost: $0.02M ± 30% | Northern
1186380 | Distribution Feeder Limitation Address capacity and load trasfer constraints | DURO - Duchess Road | Duchess Road - Fdr DR-08 New Fdr Tie to DR-12 - Target Commissioning - Apr-20 - Cost: $0.2M ± 30% | Northern
1249761 | Distribution Feeder Limitation Address voltage and capacity constraints | FD-3069 - Chinchilla | Miles Condamine F060T and Tara F067C Fdrs - Install Gas Switch & LFI - Commissioned - Nov-19 - Cost: $0.1M ± 30% | Southern
1263584 | Distribution Feeder Limitation Address capacity and load trasfer constraints | BDS254 - Steel Oats Rd Spur | Steel Oats Rd Spur - BDS254 - Aug 2.5 km of HV with 6/1/3.00 Apple - Commissioned - Sep-19 - Cost: $0.3M ± 30% | Northern
1312876 | Distribution Feeder Limitation Address capacity constraint | CHIA - Almaden Fdr | Protection Primary Reach Defect Recloser Program - Chillagoe, Almaden Fdr - Commissioned - Jul-19 - Cost: $0.1M ± 30% | Northern
1360646 | Distribution Feeder Limitation Address voltage constraint | PO2076665 - Lazzarin Rd Brandon | NQ HH AY-07 ACR Lazzarin Rd Brandon - near Pole 2076665 - Commissioned - Dec-19 - Cost: $0.1M ± 30% | Northern
1363837 | Distribution Feeder Limitation Address voltage constraint | ROMA - Roma | Roma - F049R Injune New ACR - Commissioned - Aug-19 - Cost: $0.1M ± 30% | Southern
1387849 | Distribution Feeder Limitation Address voltage constraint | Multiple Locations | ARENA NOJA SYNCHROPHASOR - Target Commissioning - Jan-21 - Cost: $0.9M ± 30% | NA
1397957 | Distribution Feeder Limitation Address voltage and capacity constraints | FD-1667 - Pampas | Yandilla Feeder F4715 IncreaseDesignTmp - FD-1667 - Pampas - Target Commissioning - Jun-21 - Cost: $0.2M ± 30% | Southern
1422987 | Distribution Feeder Limitation Address voltage and capacity constraints | FD-1638 - Ballandean | Ballandean - F4135 33kV Stage 1 - FD-1638 - Target Commissioning - Sep-21 - Cost: $0.01M ± 30% | Southern
1422989 | Distribution Feeder Limitation Address voltage and capacity constraints | FD-1638 - Ballandean | Ballandean - F4135 Ballandean 33kV Stage 2 - FD-1638 - Target Commissioning - Oct-22 - Cost: $0.4M ± 30% | Southern
1443631 | Distribution Feeder Limitation Address voltage and capacity constraints | SOKO - South Kolan | South Kolan - SK-D AND SK-B exist cables - replace cast iron potheads - Target Commissioning - May-20 - Cost: $0.2M ± 30% | Southern
1458959 | Distribution Feeder Limitation Address voltage and capacity constraints | FD-1537 - Gooburrum Fdr | Meadvale - Gooburrum Fdr - ACR & RCGS, upgrade 2 RCGS - FD-1537 - Target Commissioning - Jul-21 - Cost: $0.2M ± 30% | Southern
1236790 | Distribution Feeder Limitation Address voltage and capacity constraints | HEPA - Hermit Park | Hermit Park substation refurbishment - Target Commissioning - Feb-24 - Cost: $3.5M ± 30% | Northern
1422990 | Distribution Feeder Limitation Address voltage and capacity constraints | FD-1638 - Short St | Short St F4135 Fdr Ballandean Township 33kV Stage 3 - Target Commissioning - Oct-22 - Cost: $0.2M ± 30% | Southern
1170461 | Distribution Feeder Limitation Address voltage and capacity constraints | SP-174560 - Redgum | F099D Redgum SWER Iso ACR - West Dalby - Commissioned - Sep-19 - Cost: $0.1M ± 30% | Southern
1466401 | Distribution Feeder Limitation Address voltage and capacity constraints | FD-1485 - Coach Rd | Coach Rd Underpass - 11kV UG under 66kV - Commissioned - Oct-19 - Cost: $0.1M ± 30% | Southern