## Coversheet
Generation Application Checklist and GPS Issues Register
This document is to be used by the Proponent, relevant NSP and AEMO to determine whether a generation connection has included all of the required information, and to allow tracking of comments and issues.
Once the Application has been accepted, this document will be used to track issues related to the GPS, GPS Compliance report and RUG.
Proponents are to make note of:
The Power System Model Guidelines
AEMO Access Standard Assessment Guide
AEMO Dynamic Model Acceptance Guideline
AEMO Connection Application Submission Review Checklist
AEMO Modelling Requirements
AEMO PSCAD v5 Factsheet
AEMO System Strength Impact Assessment Guidelines
AEMO PSSE 36 Transition
Please note this list is a general list and may not reflect all requirements in some cases. Please discuss specific questions with your project sponsor prior to application. It is the responsibility of the proponent to ensure that they have the most current version of the checklist before submitting. It is strongly recommended that when submitting your connection application you have a file structure that easily navigable, files are referenced in the checklist as appropriate and that a transmittal is provided to ensure that any files that may blocked or lost are identified quickly to ensure minimal rework
Release:
2025-05-27
ver 2.7
Additional details regarding site layout and construction preferences
Status
Submitted. Detail review in due diligence phase.
Not submitted.
Submitted. Submission not acceptable.
Not submitted. To be submitted post detailed design.
Quality
Preliminary review indicates consistency.
Preliminary review indicates lack of consistency.
Model Checks
Preliminary review indicates model suitable to commence due diligence.
Preliminary review indicates model is not suitable to commence due diligence.
Submitted. Model to be reviewed in Due Diligence.

## Application review checklist
Item | Description | Customer Check and File/s Reference | NSP Status | NSP Comment | AEMO Comment | Reference
Documentation completeness checklist
1 | Ergon Energy DRE including the Preliminary Assessment (PA) as a separate attachment
2 | Completed Application Form and nomination of preference for contestable works, DCT works
3 | Payment - does the customer wish to have an invoice issued during the completeness review?
4 | Completed AEMO Checklist
5 | Indication of preference, whether to pay the SSC and undergo a stability assessment, or a full assessment
6 | Site Location and Layout drawings - if relevant, switchroom location with proposed location of network interface - if required, access easements and roadway for plant delivery
7 | Single line diagrams of the proposed: • Connection arrangement and generating system clearly showing the connection point including primary electrical SLD for all collector circuits as relevant, showing switching arrangements for each generating unit.
• Revenue meters and Power quality meters (can be provided once detailed design is complete)
• Indicative protection systems including relays, CTs, VTs and isolation points
• Auxiliary supply arrangement, detailing desired auxiliary arrangement
• Preliminary SCADA and communications SLD
8 | Proposed Generator Performance Standards (GPS) in Microsoft Word format. NB: The latest GPS template to be used. Available at: https://www.aemo.com.au/-/media/Files/Electricity/NEM/Network_Connections/AEMO-Template-Generator-Performance-Standards.docx The submission of the proposed GPS must be in accordance with the template and NER version at the time of making the Connection Application. If the Connection Application is rejected for quality or completeness purposes, it is important that the GPS template and NER version is reviewed and updated for a subsequent submission.
9 | Connection studies report(s) detailing and demonstrating how the applicant intends to meet each of the performance standards. NB: This report must include studies using RMS PSS®E models and PSCAD/EMTDC models as a minimum according to the requirements outlined in the Access Standard Assessment Guide. This guide can be found at: https://www.aemo.com.au/-/media/Files/Electricity/NEM/Network_Connections/Access-Standard-Assessment-Guide-20190131.pdf NB: As stated in that guide; “…Negotiated access standards can be proposed by an Applicant under NER clause 5.3.4 and are to be assessed by the connecting NSP and AEMO (for AEMO advisory matters) but the Applicant’s proposal must comply with NER clause 5.3.4A(b1) and (b2). Importantly, the Applicant must demonstrate that the proposed negotiated access standard is as close as reasonably practicable to the automatic access standard, noting that “if a connection applicant proposes a lower level of performance because it is not commercially feasible to meet the automatic access standard, AEMO and the NSP are not required to consider commercial feasibility in their assessment of the proposed negotiated access standard.”” This means that the report we are expecting will have supporting evidence to justify the nomination of Negotiated Access. This will need to be a detailed technical justification and may include options analysis for achieving Automatic Access.
10 | A complete set of RMS PSS®E software simulation models (in .DLL or .obj/.lib in V34.5 format and V36 format) representing the generating system that meet the Generating System Model Guidelines and Modelling Requirements. RMS PSS®E model files include (.sav, .raw, .dyr files) and sequence component data and connection numbers for Transformer vector group orientation. Generator impedance data must be consistent with the equipment data sheets and S5.2.8, and facilitate calculation of short-circuit currents (e.g. using ‘IEC’ method)
11 | PSSE Model Acceptance Test Report as per Dynamic Model Acceptance Guideline. This guideline can be found at: https://aemo.com.au/-/media/files/electricity/nem/network_connections/model-acceptance-test-guideline-nov-2021.pdf
12 | Releasable user guide (RUG) incorporating details on how to use all PSS®E simulation models including load flow setup of the generating system, generating system voltage control scheme details, model control modes , dynamic setup with details of the model’s ICONs, CONs, STATEs and VARs. https://aemo.com.au/-/media/files/electricity/nem/network_connections/transmission-and-distribution/guideline-and-template-for-preparation-of-a-releasable-user-guide.pdf RUG is consistent with and meets the requirements of information in the AEMO Template RUG Template is available at: https://www.aemo.com.au/-/media/Files/Electricity/NEM/Network_Connections/Transmission-and-Distribution/Template-for-preparation-of-a-Releasable-User-Guide.docx
13 | A complete set of PSCAD software simulation models including user guides (item 14) representing the generating system that meet the Power System Model Guidelines. The model shall also comply with Modelling Requirements (https://aemo.com.au/en/energy-systems/electricity/national-electricity-market-nem/participate-in-the-market/network-connections/modelling-requirements). Please note the NEM has transitioned to PSCAD v5. As such, models will now need to be submitted in v5. V5 Models must be compiled with Intel OneAPI Fortran Compiler: Classic 2021.x (32-bit & 64-bit). Models shall be delivered in a format that allows for maintenance for life of asset. (e.g. .dll, support files). NB. As per PSMG it is important that elements such as OLTC tap changers are represented accurately.
14 | Releasable user guide (RUG) incorporating details on how to use all PSCAD simulation models RUG is consistent with and meets the requirements of information in the AEMO Template RUG Template is available at: https://www.aemo.com.au/-/media/Files/Electricity/NEM/Network_Connections/Transmission-and-Distribution/Template-for-preparation-of-a-Releasable-User-Guide.docx
15 | PSCAD Model Acceptance Test (MAT). See https://aemo.com.au/-/media/files/electricity/nem/network_connections/model-acceptance-test-guideline-nov-2021.pdf for further information.
16 | Voltage Control Strategy document (and explanation of how the generating system meets S5.2.5.13 and S5.2.5.1, primary, secondary and tertiary control and equipment responses (switching logic where used) including examples for achieving Max and Min PF ranges)
17 | Generating System Design Datasheets including all referenced documents within the datasheets (Schedule 5.5 of the NER) S- Standard D- Design R1 – Registered pre- connection R2 – Registered post- connection Note: Not applicable data sheets shall be “greyed” out and not removed from the datasheets submission prior to AEMO reviewing and accepting it as “not applicable”.
18 | Generating system capability curve during steady state conditions and transients Capability curve points in MS Excel format.
19 | Protection and control scheme details including those required to be modelled to assess the impact of the proposed generating system connection (can be provided once detailed design is complete).
20 | Confirmation of validity of models at low SCR levels. PSCAD - Supported by factory or laboratory testing (OEM). PSSe - Supported by model benchmarking against PSCAD (Item 23).
21 | Certification of the minimum SCR at which system can reliably operate, noting the requirements of S5.2.5.15. This should be supported by site specific PSCAD studies and included as a separate report.
22 | Nomination of whether the applicant intends to pay the system strength charge and undergo a stability assessment, or to undergo a full assessment
23 | Benchmarking report for the PSS®E and PSCAD responses, to confirm validity of PSS®E models and demonstrate minimum SCR for which the PSS®E model is valid
24 | Transformer and collector feeder energisation study NB: A standard for plant energisation is available https://www.ergon.com.au/__data/assets/pdf_file/0010/1090666/STNW1179-Standard-for-Plant-Energisation.pdf. The presentation of results shall demonstrate compliant performance, where achieving that compliant performance may require the use of mitigations which shall be identified, discussed and modelled in the study report.
25 | Model source code associated with all PSS®E user written simulation models. The source must be for the model as applied and used in the assessment of the GPS and its Releasable User Guide. It must meet FORTAN/FLX source requirements as in Modelling Requirements (can be supplied to AEMO only).
26 | A set of functional block diagrams for RMS PSS®E models and PSCAD/EMTDC models including all functions between feedback signals and generating system output. The parameters of each functional block including all settings, gains, time constants, delays, deadbands and limits, as expected to be represented in standard Laplace block diagram. The characteristics of non-linear elements. The model functional block diagram illustrates all derivative states including derivative state variable names consistent with the block diagrams and the model settings/parameters.
27 | A map of parameters for PSS®E and PSCAD™ Models , including conversion process where applicable
28 | Audio Frequency Load Control (AFLC) Compliance Studies Study must demonstrate that the proposed plant does not sink the AFLC signal as described in the DRE.
29 | Harmonic Compliance Studies Compliance studies should be reflective of guidance provided by TR IEC 61000.3.6 2012 and AS/NZS 61000.3.6 2001 (including harmonic polygons). NB: The harmonic compliance studies must be completed against the Harmonic Allocation provided by the NSP. If you do not believe that you have been provided a Harmonic Allocation, please inform your Customer Sponsor and the Network Connection team asap.
30 | Norton equivalent complex impedance of the generating system, (current source and parallel connected impedance) consisting of complex frequency dependent impedance in the positive and negative and zero sequence, and positive, negative and zero sequence current emissions, fully representing the generator at the point of connection. Alternatively, a Powerfactory model which can be utilised for harmonic analysis. N.B. If the generator can be operated under the terms of the GPS in a number of configurations that will result in significant variations to the Norton model, then a Norton model of each of such different operating configurations must be provided.
Information consistency and quality check
31 | PSS®E and PSCAD Models are consistent in the physical representation of the Generating System
32 | PSS®E and PSCAD Models are consistent with the data sheets and the representation in the Generator Performance Standard – connection study report
33 | PSS®E and PSCAD Models – parameters and performances are consistent with the following items: - Protection systems – over-voltage, over- frequency, under-voltage and under-frequency settings - Any other limitations or protection systems that would otherwise limit accuracy of one of the models, e.g. Multiple LVRT capability and protection settings for overspeed or oscillatory protection - Disturbance ride through logic and performance is consistent for the application of balanced disturbances, where models are consistent during and after the applied disturbance - Plant control system parameters and (step/induced disturbance) responses including and where applicable: o Active Power Controller o Frequency Controller o Voltage, PF and/or Reactive Power Controller To support these requirements the Applicant has provided PSSE/ PSCAD benchmarking assessment of the generating system based on a SMIB case setup taking into consideration lowest SCR conditions at POC. Application of balanced 3 phase voltage disturbance for a range of retained voltage profiles is overlayed against the accuracy requirements. Signals taken into consideration are Power, Voltage and Reactive Power.
34 | Single Line diagrams align with the model representation
35 | Protection settings report does not over-rule any other requirement in the GPS (i.e. quality check to ensure that protection settings design (which may be undertaken at detailed design stage) does not impede any otherwise agreed GPS item or stated capability)
Initial model check
36 | PSS®E model is provided as per Power System Model Guidelines. PSS®E model version is also consistent with Modelling Requirements. When the PSS®E model is opened and executed with PSSE software version used by AEMO: - The model does not result in unstable initialisation or initialisation that requires settling -The model does not result in initialisation or run time errors including non-convergence or suspect state errors - The model is dynamically stable for all possible ranges of system strength (short circuit ratio and X/R ratio) where the generating system would be in operation. - The model allows active power, voltage, power factor, and reactive power reference change to be performed
37 | PSCAD model is provided as per Power System Model Guidelines. PSCAD model version is also consistent with Modelling Requirements. When the PSCAD model is opened and executed: - The model is dynamically stable for all possible ranges of system strength (short circuit ratio and X/R ratio) where the generating system would be in operation, and the model presented in the SMIB case is representative of the lowest SCR for the generating system. - The model initialises and is able to remain stable at rated output and prior to application of any disturbance. - The model is able to run through a balanced fault application in the SMIB case and achieve stable operating condition upon removal of the fault/disturbance. - The model is able to run through an unbalanced single phase and phase-to- phase-to-ground disturbance application in the SMIB case and achieve stable operating condition upon removal of the disturbance. - The generating system (model) meets the requirements of the NER under the definition of “continuous uninterrupted operation” including “responding so as to not exacerbate or prolong the disturbance”. - The model allows active power, voltage, power factor, and reactive power reference change to be performed
Required for registration
38 | Updated models, design documentation, technical information to reflect detailed design updates. Governance information such as communications system failure control design.
39 | Energy Conversion Model (required 3 months prior to registration)
40 | GPS Compliance Test Plan ('Commissioning Plan') (required 3 months prior to commissioning)
41 | SCADA signal list (at least 3 months prior to registration)
42 | Full Assessment, if required

## DataCategories
Data is coded in categories, according to the stage at which it is available in the build-up of data during the process of forming a connection or obtaining access to a network, with data acquired at each stage being carried forward, or enhanced in subsequent stages, e.g. by testing. The Power System Model Guidelines, Power System Design Data Sheet and Power System Setting Data Sheet identify for each type of data, its category in terms of clause S5.5.2. Codes: S = Standard Planning Data; D = Detailed Planning Data; R = Registered Data (R1 pre-connection, R2 post-connection)
Preliminary system planning data Preliminary system planning data is required for submission with the application to connect, to allow the Network Service Provider to prepare an offer of terms and conditions for a connection agreement and to assess the requirement for, and effect of, network augmentation or extension options. Such data is normally limited to the items denoted as Standard Planning Data (S) in the Power System Model Guidelines, Power System Design Data Sheet, Power System Setting Data Sheet and in schedules 5.5.3 to 5.5.5. The Network Service Provider may, in cases where there is reasonable doubt as to the viability of a proposal, require the submission of other data before making an offer to connect or to amend a connection agreement.
Registered system planning data Registered system planning data is the class of data which will be included in the connection agreement signed by both parties. It consists of the preliminary system planning data plus those items denoted in the attached schedules as Detailed Planning Data (D). The latter must be submitted by the Registered Participant in time for inclusion in the connection agreement.
Registered data Registered Data consists of data validated and agreed between the Network Service Provider and the Registered Participant, such data being: (a) prior to actual connection and provision of access, data derived from manufacturers' data, detailed design calculations, works or site tests etc. (R1); and (b) after connection, data derived from on-system testing (R2). All of the data will, from this stage, be categorised and referred to as Registered Data; but for convenience the schedules omit placing a higher ranked code next to items which are expected to already be valid at an earlier stage.

## GPS
NSP Comments and Issues List
Item | Section | Reference | Issue/Comment | Proponent Response | AEMO comments | NSP Comments | Issue Status | Resolution Required for Connection Offer? | Reference Information
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21

## RUG
NSP Comments and Issues List
Item | Section | Reference | Issue/Comment | Proponent Response | AEMO comments | NSP Comments | Issue Status | Resolution Required for Connection Offer? | Reference Information
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21

## GPS Compliance report
NSP Comments and Issues List
Item | Section | Reference | Issue/Comment | Proponent Response | AEMO comments | NSP Comments | Issue Status | Resolution Required for Connection Offer? | Reference Information
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21