## Notes
Transmission Feeders Forecasts (Energex Distribution Annual Planning Report 2019-20 to 2023-24)
This workbook provides 5 year forecast capacity and loading information for transmission feeders in the Energex network.
This workbook forms part of the Energex Distribution Annual Planning Report 2019-20 to 2023-24 (DAPR) and should be read in conjunction with the report document.
Energex Distribution Annual Planning Report is prepared and made available solely for information purposes. While care was taken in the preparation of the information in this report, and it is provided in good faith, Energex accepts no responsibility or liability (including without limitation, liability to any person by reason of negligence or negligent mis-statement) for any loss or damage that may be incurred by any person acting in reliance on this information or assumptions drawn from it, except to the extent that liability under any applicable Queensland or Commonwealth of Australia statute cannot be excluded.
It contains assumptions regarding, among other things, economic growth and load forecasts which may or may not prove to be correct. The forecasts included in the document involve subjective judgements and analysis which are subject to significant uncertainties and contingencies, many of which are out of the control of Energex. Energex makes no representation or warranty as to the accuracy, reliability, completeness or suitability for any particular purpose of the information in this document. All information should be independently investigated, reviewed, analysed and verified, and must not be relied upon in connection with any investment proposal or decision.
All financials presented in this document are correct at the time of writing and represent the existing organisational accounting treatment, which may be subject to change. Energy Queensland is finalising the alignment of its Cost Allocation Methodology between Ergon and Energex, potentially impacting the treatment of some Capital and Operational Project costs.
The following sections list the 132 kV and 110 kV feeders, their forecast loads and their capacity limitations. The feeder loads are calculated from load flow results using forecast substation demands. For the transmission and sub-transmission feeders, load flow studies are conducted for system normal and single contingency situations.
These tables show information about the feeder capacity, load at risk, and the compliance of each feeder with its security standard. To assess whether a feeder meets its security standard, four possible risk periods are considered: winter day, winter night, summer day and summer night. The highest risk period for each season is displayed for each year of the forward planning period.
The forecast and capacity cut-off date for the winter season is 1 June of each year, and for the summer season is 1 December of each year. For example, 2019 winter forecast includes all committed projects with a proposed commissioning date up to 1 June 2019, and the 2019/20 summer forecast includes all committed projects with a proposed commissioning date up to 1 December 2019.
Due to the modelling complexity of the 132 kV and 110 kV, two dominant risk periods are considered in the analysis: summer day and winter night.
Peak, reconciled, compensated load forecasts have been used in the 132 kV and 110 kV feeder analyses, with 50 PoE forecast load used for single contingency studies, and 10 PoE forecast load used for system normal studies. The analysis includes load transfers expected from committed projects with the proposed timings scheduled in the program of work as of May 2019, and the 132 kV and 110 kV studies are based on the summer 2018/19 Queensland peak generation scenario.
Feeder capacities are shown for 2HEC, ECC and NCC. These ratings have also been adjusted for known committed project proposals. All load transfers associated with contingent condition include acceptable feeder voltage profiles.
Although the conductor rating is generally the limiting factor for feeder capacity, there are other significant items of plant, such as the feeder circuit breaker, that can also restrict capacity. Furthermore, other factors such as voltage constraints and load sharing between parallel underground feeders can sometimes de‑rate the capacity of the feeders due to thermal characteristic constraints. Each of these factors has been taken into account in the production of the forecast tables.
The tables also show, for each of the next five years, the compliance of each feeder with its security standard. The peak risk period is the one with the highest calculated load at risk (normal or contingency). Load at risk is calculated using the forecast loads, the feeder capacity, and the capacity of the network to allow the transfer of load away from the feeder to an alternative source of supply. A detailed explanation of the derivation of load at risk is provided in Section F.2.4. If there is no load at risk, then a feeder meets the security standard.
Interconnected or feeders that supply multiple customers are examined in the following tables. Feeders exclusively supplying a customer owned substation or dedicated to a customer are not included in these tables. For transmission and sub-transmission feeders, if there is any load at risk during normal or contingent conditions, the feeder is flagged as not meeting the security standard. Although this may in some cases arise due to inadequate supply for only short periods of time, this approach has been adopted as the best means of fully assessing whether the security standard is being met. As such it will provide evidence of benefits arising from such activities as the installation of remotely controlled switchgear to bolster remote transfer capabilities where these exist.
The 132 kV and 110 kV forecast tables provide load at risk based on a contingent event. The contingency scenario considered in the analysis includes the Powerlink upstream network. Due to the meshed nature of the transmission network, a contingent event on a connection point substation or a Powerlink 275 kV transmission network element would have the potential to change load flow dynamics of the system and cause unprecedented overload conditions. As the limitation stems from the upstream network, these results are subsequently used as inputs to joint planning activities to address the limitation prudently or economically.
A definition of terms is shown in the table below.
Definition of Terms Feeder Capacity and Forecast Tables
Term | Definition
NCC Rating (A) | Normal Cyclic Capacity - the total capacity with all network components and equipment intact.
This is the maximum permissible peak daily loading for a given load cycle that a feeder can supply each day of its life. For overhead feeders, the NCC is the conductor rating with an assumed 1m/s wind, orthogonal to the line. For underground cables, the NCC assumes that there are sufficient temperature and current operating margins from the thermal inertia of the cable and its surroundings.
10 PoE Load (A) | Peak load forecast with 10% probability of being exceeded (one in every 10 years will be exceeded). Based on normal expected growth rates and weather corrected starting loads.
Power Factor (System Normal) | Lowest power factor along the feeder at 10 PoE Peak Load.
LARn (A) | Security standard load at risk under system normal condition, expressed in Amps.
LARn (MW) | Security standard load at risk under system normal condition, expressed in MW, assuming the nominal system voltages and lowest power factor.
(LARn (A) x Nominal Voltage x Power Factor (System Normal) x sqrt(3))
1000000
ECC Rating (A) | Emergency Cyclic Capacity – the long term firm delivery capacity under single contingency conditions.
Some underground cables are installed in close proximity to other circuits and are normally de‑rated to allow for the heat generated by the adjacent cables. ECC is the higher capacity available when any adjacent circuits have been unloaded. For overhead conductors which do not benefit from this phenomenon, the ECC is synonymous with the NCC.
50 PoE Load (A) | Peak load forecast with 50% probability of being exceeded (one in every two years will be exceeded). Based on normal expected growth rates & weather corrected starting loads.
Hours PA > 95% Peak Load | The forecast number of hours per annum where the load exceeded 95% of the peak 50 PoE demand.
Raw LAR (A) | The amount of load exceeding ECC rating. (Load – ECC Rating)
2-Hour Rating (A) | Two Hour Emergency Capacity (2HEC) – the short term firm delivery capacity under single contingency conditions.
For overhead feeders, the 2HEC is the conductor rating with an assumed 2m/s wind, orthogonal to the line (compared to the 1.0 m/s wind speed used for NCC ratings).
For underground cables, the 2HEC assumes that there are sufficient temperature and current operating margins immediately prior to the contingency to extract additional capacity from the thermal inertia of the cable and its surrounds.
Auto Trans Avail (A) | SCADA or automatically controlled load transfers that can be implemented within one minute. Examples include auto changeover switching to alternate feeders.
A blank entry indicates that this type of transfer is not considered as available in the evaluation of security standard compliance.
Remote Trans Avail (A) | Load transfers that can be implemented through SCADA switching procedures by the network control officer. It is assumed that this can generally be achieved within 30 minutes.
A blank entry indicates that this type of transfer is not considered as available in the evaluation of security standard compliance.
Manual Trans Avail (A) | Load transfers can also be deployed via manually controlled switchgear locally by field staff. It is assumed the implementation of manual switching procedures to isolate the faulted portion of the network whilst restoring supply to fault free portions can be fully implemented within three hours (urban) or four hours (rural).
Manual transfers are obtained from load flow studies performed on each 11 kV distribution feeder based on the forecast 2018/19 load, the sum of all available 11 kV transfers at a substation is multiplied by a 0.75 factor to account for diversity and to provide an error margin. The same amount of transfers is applied throughout the forward planning period.
A blank entry indicates that this type of transfer is not considered as available in the evaluation of security standard compliance.
POPS | Plant Overload Protection Scheme (POPS) consists of several applications which continuously monitor specific items of plant for overload conditions. If overload conditions are detected and validated, POPS will initiate predefined actions in order to relieve the overload condition.
Mobile Gen Reqd (A) | The amount of generation required under the contingency, capped at the maximum MVA allowable under the security standard requirements.
Where required, alternate supply from mobile generators can be sourced within 8 hours (urban) or 12hours (rural). These are generally smaller 500kVA units that do not require transport permits or police escorts and can be rapidly deployed. Up to 4 MVA (urban) or 10 MVA (rural) of mobile generation may be committed to a single contingency event.
LARc (A) | Security standards load at risk under single contingency condition, expressed in Amps.
LARc (MW) | Estimated generation / load reduction required to defer the forecast system limitation.
This is the security standard load at risk under single contingency condition, expressed in MW, assuming the nominal system voltages and the lowest power factor on the feeder under system normal condition.
(LARc (A) x Nominal Voltage x Power Factor (System Normal) x sqrt(3))
1000000
Customer Category | For security standard application, the general type of customer a sub-transmission, or transmission feeder is supplying.
The Load at Risk (LAR) is evaluated for both normal (LARn) and contingent (LARc) conditions. Under normal conditions, the loading on a substation is not to exceed the normal cyclic capacity (NCC) of the supplying feeders. Under contingent conditions, the loading of a substation is not to exceed the available supply, whilst taking into consideration the security of supply standards of the supplying feeder.
Load at risk is the shortfall between the feeder forecast load (either 10 PoE or 50 PoE) and the available supply. The equations for feeder LAR are as follows:
· LARn = 10 PoE – NCC where NCC is the normal cyclic capacity
· LARc = 50 PoE – available capacity – available supply (within security standard timeframe)
Network security standards are not being met if LARn or LARc is greater than 0.
Generally, there are two available capacities and four available sources of supply that can be deployed upon loss of a major network component such as a sub-transmission/transmission feeder.
Types of available capacity:
· Emergency Cyclic Capacity (ECC) – Some underground cables are installed in close proximity to other circuits and are normally de-rated to allow for the heat generated by the adjacent cables. ECC is the higher capacity available when any adjacent circuits have been unloaded. For overhead conductors which do not benefit from this phenomenon, the ECC is synonymous with the NCC.
· Two Hour Emergency Capacity (2HEC) – For overhead feeders, the 2HEC is the conductor rating with an assumed 2m/s wind, orthogonal to the line (compared to the 1.0 m/s wind speed used for NCC ratings). For underground cables, the 2HEC assumes that there are sufficient temperature and current operating margins immediately prior to the contingency to extract additional capacity from the thermal inertia of the cable and its surroundings. The philosophy of using 2HEC feeder ratings assumes that load is reduced to ECC (if appropriate) or NCC by the end of 2 hours at this capacity.
Types of available supply:
· Automatic Transfers (AT) – SCADA or automatically controlled load transfers that can be implemented within 1 minute. Examples include auto changeover switching to alternate feeders. Such capacity has been considered where it is available.
· Remote Transfers (RT) – Most of the transmission and sub-transmission network employs remotely controlled switchgear. Some load transfers can therefore be achieved through SCADA switching procedures.
· Manual Transfers (MT) – Load transfers can also be deployed via manually controlled switchgear. The implementation of manual switching procedures to isolate the faulted portion of the network whilst restoring supply to fault free portions can be fully implemented within 3 hours (urban) or 4 hours (rural) and is available for extended periods.
· Mobile Generation (MG) – Alternate supply from mobile generators can be sourced within 8 hours (urban) or 12 hours (rural). These are generally smaller 500 kVA units that do not require transport permits or police escorts and can be rapidly deployed. Up to 4 MVA (urban) or 10 MVA (rural) of mobile generation may be committed to a single contingency event.

## Index
Feeder names in ascending order
Index
F7259/1
F7259/2
F7289
F750
F766
F767
F713
F714
F7231
F7232
F7287/3
F7288/3
F7230
F7362
F752
F753
F809
F810
F829
F833
F834
F835
F914
F915
F830
F905
F7266
F7267
F7321
F7365
F781
F782
F807
F808
F704
F7351
F7354
F7377
F787
F788/1
F788/2
F788/3
F793
F799
F820
F837
F836
F843
F904/1
F904/2
F904/3
F726
F727
F7348
F7193
F7229
F7283
F7297
F798
F907
F917
F916
F706
F754
F755
F779
F780
F794
F826
F827
F838
F839
F918
F919
F7270
F7271
F7272
F7273
F7274
F745/2
F745/3
F745/4
F745/5
F746/2
F746/3
F746/4
F746/5
F7189/1
F7189/2
F7189/3
F7298
F777
F778
F790
F795/1
F795/2
F795/3
F796
F797
F803
F804
F815
F816
F819
F821
F844
F851
PWD-WMD#1
PWD-WMD#2
F817
F818
F7337
F7338
F7341
F7342
F7344
F7345
F7358
F737/1
F737/2
F738/1
F738/2
F739
F740
F741
F742
F7299
F743
F744
F745/1
F746/1
F831
F912
F913
F7186
F7343
F747/1
F747/2
F748/1
F748/2

## 110-132kV Feeders-Summer
110 kV/132 kV Fdr Sum | From | To | Plant OOS | Parameter | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24
ABERMAIN Connection Point:
F7259/1 | Abermain | Wulkuraka Tee |  | NCC Rating (A) | 407 | 407 | 407 | 407 | 407
|  |  |  | 10 PoE Load (A) | 397 | 403 | 402 | 401 | 402
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | F726 | ECC Rating (A) | 407 | 407 | 407 | 407 | 407
|  |  |  | 50 PoE Load (A) | 527 | 554 | 554 | 550 | 548
|  |  |  | Hours PA>95% Peak Load | 5.5 | 5.5 | 5.5 | 5.5 | 5.5
|  |  |  | Raw LAR (A) | 120 | 148 | 147 | 143 | 141
|  |  |  | 2Hr Rating (A) | 491 | 491 | 491 | 491 | 491
Auto Trans Avail (A)
|  |  |  | Remote Trans Avail (A) | 47 | 46 | 46 | 46 | 45
|  |  |  | Manual Trans Avail (A) | 26 | 26 | 26 | 26 | 26
|  |  |  | POPS | No | No | No | No | No
|  |  |  | Mobile Gen Reqd (A) | 47 | 52 | 52 | 52 | 52
|  |  |  | LARc (A) | 36 | 64 | 63 | 59 | 57
|  |  |  | LARc (MW) | 6.6 | 11.9 | 11.8 | 11 | 10.6
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | No | No | No | No | No
F7259/2 | Wulkuraka Tee | Lockrose |  | NCC Rating (A) | 407 | 407 | 407 | 407 | 407
|  |  |  | 10 PoE Load (A) | 375 | 378 | 376 | 375 | 376
|  |  |  | Power Factor (System Normal) | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | F726 | ECC Rating (A) | 407 | 407 | 407 | 407 | 407
|  |  |  | 50 PoE Load (A) | 496 | 523 | 523 | 519 | 517
|  |  |  | Hours PA>95% Peak Load | 4.5 | 4.5 | 4.5 | 4.5 | 4.5
|  |  |  | Raw LAR (A) | 89 | 116 | 116 | 112 | 110
|  |  |  | 2Hr Rating (A) | 491 | 491 | 491 | 491 | 491
Auto Trans Avail (A)
|  |  |  | Remote Trans Avail (A) | 47 | 46 | 46 | 46 | 45
|  |  |  | Manual Trans Avail (A) | 26 | 26 | 26 | 26 | 26
|  |  |  | POPS | No | No | No | No | No
|  |  |  | Mobile Gen Reqd (A) | 16 | 43 | 43 | 40 | 38
|  |  |  | LARc (A) | 5 | 32 | 32 | 28 | 26
|  |  |  | LARc (MW) | 0.9 | 6.1 | 6 | 5.2 | 4.8
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | No | No | No | No | No
ABERMAIN Connection Point:
F7289 | Lockrose | Gatton |  | NCC Rating (A) | 441 | 441 | 441 | 441 | 441
|  |  |  | 10 PoE Load (A) | 0 | 0 | 0 | 0 | 0
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
BELMONT Connection Point:
F750 | Belmont | Beenleigh |  | NCC Rating (A) | 524 | 524 | 524 | 524 | 524
|  |  |  | 10 PoE Load (A) | 357 | 357 | 361 | 366 | 360
|  |  |  | Power Factor (System Normal) | 0.97 | 0.93 | 0.95 | 0.95 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F766 | Belmont | Cleveland |  | NCC Rating (A) | 1394 | 1394 | 1394 | 1394 | 1394
|  |  |  | 10 PoE Load (A) | 445 | 443 | 444 | 446 | 454
|  |  |  | Power Factor (System Normal) | 0.97 | 0.97 | 0.97 | 0.97 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F767 | Belmont | Cleveland |  | NCC Rating (A) | 1394 | 1394 | 1394 | 1394 | 1394
|  |  |  | 10 PoE Load (A) | 445 | 443 | 444 | 446 | 440
|  |  |  | Power Factor (System Normal) | 0.97 | 0.97 | 0.97 | 0.97 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
BLACKSTONE Connection Point:
F713 | Blackstone | Raceview |  | NCC Rating (A) | 756 | 756 | 756 | 756 | 756
|  |  |  | 10 PoE Load (A) | 327 | 327 | 330 | 333 | 335
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F714 | Blackstone | Raceview |  | NCC Rating (A) | 756 | 756 | 756 | 756 | 756
|  |  |  | 10 PoE Load (A) | 326 | 327 | 330 | 333 | 335
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
CBD EAST Connection Point:
F7231 | Wellington Road | Charlotte St |  | NCC Rating (A) | 1184 | 1184 | 1184 | 1184 | 1184
|  |  |  | 10 PoE Load (A) | 543 | 545 | 564 | 588 | 601
|  |  |  | Power Factor (System Normal) | 1 | 1 | 1 | 0.99 | 1
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | CBD | CBD | CBD | CBD | CBD
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F7232 | Wellington Road | Charlotte St |  | NCC Rating (A) | 1184 | 1184 | 1184 | 1184 | 1184
|  |  |  | 10 PoE Load (A) | 543 | 545 | 564 | 588 | 601
|  |  |  | Power Factor (System Normal) | 1 | 1 | 1 | 0.99 | 1
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | CBD | CBD | CBD | CBD | CBD
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F7287/3 | Tingalpa Tee | Wellington Road |  | NCC Rating (A) | 1130 | 1130 | 1130 | 1130 | 1130
|  |  |  | 10 PoE Load (A) | 904 | 938 | 958 | 958 | 975
|  |  |  | Power Factor (System Normal) | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | F7288 | ECC Rating (A) | 1255 | 1255 | 1255 | 1255 | 1255
|  |  |  | 50 PoE Load (A) | 1426 | 1464 | 1493 | 1500 | 1523
|  |  |  | Raw LAR (A) | 171 | 209 | 238 | 245 | 268
|  |  |  | 2Hr Rating (A) | 1600 | 1600 | 1600 | 1600 | 1600
Auto Trans Avail (A)
|  |  |  | Remote Trans Avail (A) | 284 | 255 | 248 | 250 | 812
Manual Trans Avail (A)
|  |  |  | POPS | No | No | No | No | No
|  |  |  | Mobile Gen Reqd (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | CBD | CBD | CBD | CBD | CBD
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
CBD EAST Connection Point:
F7288/3 | Tingalpa Tee | Wellington Road |  | NCC Rating (A) | 1130 | 1130 | 1130 | 1130 | 1130
|  |  |  | 10 PoE Load (A) | 900 | 936 | 954 | 954 | 971
|  |  |  | Power Factor (System Normal) | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | F7287 | ECC Rating (A) | 1255 | 1255 | 1255 | 1255 | 1255
|  |  |  | 50 PoE Load (A) | 1423 | 1460 | 1490 | 1496 | 1519
|  |  |  | Raw LAR (A) | 168 | 205 | 235 | 241 | 264
|  |  |  | 2Hr Rating (A) | 1600 | 1600 | 1600 | 1600 | 1600
Auto Trans Avail (A)
|  |  |  | Remote Trans Avail (A) | 284 | 255 | 248 | 250 | 812
Manual Trans Avail (A)
|  |  |  | POPS | No | No | No | No | No
|  |  |  | Mobile Gen Reqd (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | CBD | CBD | CBD | CBD | CBD
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F7230 | Wellington Road | Coorparoo |  | NCC Rating (A) | 1155 | 1155 | 1155 | 1155 | 1155
|  |  |  | 10 PoE Load (A) | 210 | 210 | 210 | 210 | 209
|  |  |  | Power Factor (System Normal) | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F7362 | Wellington Road | Coorparoo |  | NCC Rating (A) | 1155 | 1155 | 1155 | 1155 | 1155
|  |  |  | 10 PoE Load (A) | 210 | 210 | 210 | 210 | 209
|  |  |  | Power Factor (System Normal) | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
CBD EAST Connection Point:
F752 | Murarrie | Newstead |  | NCC Rating (A) | 1352 | 1352 | 1352 | 1352 | 1352
|  |  |  | 10 PoE Load (A) | 396 | 407 | 417 | 422 | 424
|  |  |  | Power Factor (System Normal) | 0.97 | 0.97 | 0.96 | 0.97 | 0.97
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | CBD | CBD | CBD | CBD | CBD
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F753 | Murarrie | Newstead |  | NCC Rating (A) | 1352 | 1352 | 1352 | 1352 | 1352
|  |  |  | 10 PoE Load (A) | 396 | 407 | 417 | 422 | 424
|  |  |  | Power Factor (System Normal) | 0.97 | 0.97 | 0.96 | 0.97 | 0.97
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | CBD | CBD | CBD | CBD | CBD
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F809 | Newstead | Victoria Park |  | NCC Rating (A) | 655 | 655 | 655 | 655 | 655
|  |  |  | 10 PoE Load (A) | 141 | 142 | 145 | 146 | 149
|  |  |  | Power Factor (System Normal) | 1 | 1 | 1 | 1 | 1
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | CBD | CBD | CBD | CBD | CBD
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F810 | Newstead | Victoria Park |  | NCC Rating (A) | 655 | 655 | 655 | 655 | 655
|  |  |  | 10 PoE Load (A) | 141 | 142 | 145 | 146 | 149
|  |  |  | Power Factor (System Normal) | 1 | 1 | 1 | 1 | 1
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | CBD | CBD | CBD | CBD | CBD
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F829 | Charlotte St | Ann St |  | NCC Rating (A) | 909 | 909 | 909 | 909 | 909
|  |  |  | 10 PoE Load (A) | 297 | 301 | 301 | 299 | 308
|  |  |  | Power Factor (System Normal) | 1 | 1 | 0.99 | 1 | 1
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | CBD | CBD | CBD | CBD | CBD
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
CBD EAST Connection Point:
F833 | Charlotte St | Ann St |  | NCC Rating (A) | 909 | 909 | 909 | 909 | 909
|  |  |  | 10 PoE Load (A) | 297 | 301 | 301 | 299 | 308
|  |  |  | Power Factor (System Normal) | 1 | 1 | 0.99 | 1 | 1
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | CBD | CBD | CBD | CBD | CBD
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F834 | McLachlan St | Ann St |  | NCC Rating (A) | 908 | 908 | 908 | 908 | 908
|  |  |  | 10 PoE Load (A) | 361 | 364 | 363 | 359 | 375
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.96 | 0.98 | 0.97
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | CBD | CBD | CBD | CBD | CBD
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F835 | McLachlan St | Victoria Park |  | NCC Rating (A) | 908 | 908 | 908 | 908 | 908
|  |  |  | 10 PoE Load (A) | 304 | 311 | 306 | 303 | 321
|  |  |  | Power Factor (System Normal) | 1 | 1 | 1 | 1 | 1
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | CBD | CBD | CBD | CBD | CBD
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F914 | Newstead | McLachlan St |  | NCC Rating (A) | 1232 | 1232 | 1232 | 1232 | 1232
|  |  |  | 10 PoE Load (A) | 138 | 137 | 147 | 151 | 149
|  |  |  | Power Factor (System Normal) | 0.81 | 0.83 | 0.79 | 0.83 | 0.81
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | CBD | CBD | CBD | CBD | CBD
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F915 | Newstead | McLachlan St |  | NCC Rating (A) | 1232 | 1232 | 1232 | 1232 | 1232
|  |  |  | 10 PoE Load (A) | 138 | 137 | 147 | 151 | 149
|  |  |  | Power Factor (System Normal) | 0.81 | 0.83 | 0.79 | 0.83 | 0.81
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | CBD | CBD | CBD | CBD | CBD
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
CBD SOUTH Connection Point:
F830 | West End | Charlotte St |  | NCC Rating (A) | 651 | 651 | 651 | 651 | 651
|  |  |  | 10 PoE Load (A) | 276 | 306 | 342 | 349 | 365
|  |  |  | Power Factor (System Normal) | 0.35 | 0.34 | 0.28 | 0.33 | 0.3
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | CBD | CBD | CBD | CBD | CBD
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F905 | Rocklea | West End |  | NCC Rating (A) | 653 | 653 | 653 | 653 | 653
|  |  |  | 10 PoE Load (A) | 511 | 529 | 539 | 549 | 558
|  |  |  | Power Factor (System Normal) | 0.94 | 0.93 | 0.9 | 0.93 | 0.91
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | PLQ_H2TR4 | ECC Rating (A) | 653 | 653 | 653 | 653 | 653
|  |  |  | 50 PoE Load (A) | 744 | 758 | 752 | 758 | 784
|  |  |  | Raw LAR (A) | 91 | 105 | 99 | 105 | 131
|  |  |  | 2Hr Rating (A) | 822 | 822 | 822 | 822 | 822
Auto Trans Avail (A)
|  |  |  | Remote Trans Avail (A) | 353 | 395 | 377 | 353 | 368
Manual Trans Avail (A)
|  |  |  | POPS | No | No | No | No | No
|  |  |  | Mobile Gen Reqd (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  | PLQ_H2TR5 | ECC Rating (A) | 653 | 653 | 653 | 653 | 653
|  |  |  | 50 PoE Load (A) |  |  |  |  | 661
|  |  |  | Raw LAR (A) |  |  |  |  | 8
|  |  |  | 2Hr Rating (A) |  |  |  |  | 822
Auto Trans Avail (A)
|  |  |  | Remote Trans Avail (A) |  |  |  |  | 249
Manual Trans Avail (A)
|  |  |  | POPS |  |  |  |  | No
|  |  |  | Mobile Gen Reqd (A) |  |  |  |  | 0
|  |  |  | LARc (A) |  |  |  |  | 0
|  |  |  | LARc (MW) |  |  |  |  | 0
|  |  |  | Customer Category | CBD | CBD | CBD | CBD | CBD
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
CBD WEST Connection Point:
F7266 | Milton | Customer |  | NCC Rating (A) | 908 | 908 | 908 | 908 | 908
|  |  |  | 10 PoE Load (A) | 231 | 248 | 266 | 273 | 282
|  |  |  | Power Factor (System Normal) | 0.67 | 0.64 | 0.64 | 0.67 | 0.64
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | CBD | CBD | CBD | CBD | CBD
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F7267 | Milton | Makerston St |  | NCC Rating (A) | 908 | 908 | 908 | 908 | 908
|  |  |  | 10 PoE Load (A) | 256 | 279 | 300 | 310 | 328
|  |  |  | Power Factor (System Normal) | 0.72 | 0.69 | 0.69 | 0.73 | 0.7
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | CBD | CBD | CBD | CBD | CBD
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F7321 | Customer | Makerston St |  | NCC Rating (A) | 908 | 908 | 908 | 908 | 908
|  |  |  | 10 PoE Load (A) | 138 | 156 | 174 | 181 | 195
|  |  |  | Power Factor (System Normal) | 0.5 | 0.47 | 0.48 | 0.53 | 0.51
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | CBD | CBD | CBD | CBD | CBD
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F7365 | Kelvin Grove | Milton |  | NCC Rating (A) | 905 | 905 | 905 | 905 | 905
|  |  |  | 10 PoE Load (A) | 272 | 287 | 304 | 310 | 321
|  |  |  | Power Factor (System Normal) | 0.8 | 0.78 | 0.77 | 0.8 | 0.77
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | CBD | CBD | CBD | CBD | CBD
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F781 | Ashgrove West | Kelvin Grove |  | NCC Rating (A) | 857 | 857 | 857 | 857 | 857
|  |  |  | 10 PoE Load (A) | 365 | 378 | 393 | 398 | 408
|  |  |  | Power Factor (System Normal) | 0.89 | 0.87 | 0.86 | 0.88 | 0.86
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | CBD | CBD | CBD | CBD | CBD
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
CBD WEST Connection Point:
F782 | Ashgrove West | Milton |  | NCC Rating (A) | 857 | 857 | 857 | 857 | 857
|  |  |  | 10 PoE Load (A) | 430 | 447 | 467 | 474 | 487
|  |  |  | Power Factor (System Normal) | 0.87 | 0.85 | 0.84 | 0.86 | 0.84
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | CBD | CBD | CBD | CBD | CBD
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F807 | Makerston St | Charlotte St |  | NCC Rating (A) | 588 | 588 | 588 | 588 | 588
|  |  |  | 10 PoE Load (A) | 119 | 133 | 148 | 152 | 159
|  |  |  | Power Factor (System Normal) | 0.4 | 0.37 | 0.3 | 0.35 | 0.3
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | CBD | CBD | CBD | CBD | CBD
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F808 | Makerston St | Charlotte St |  | NCC Rating (A) | 588 | 588 | 588 | 588 | 588
|  |  |  | 10 PoE Load (A) | 152 | 168 | 188 | 192 | 200
|  |  |  | Power Factor (System Normal) | 0.32 | 0.31 | 0.25 | 0.31 | 0.29
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | CBD | CBD | CBD | CBD | CBD
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
LOGANLEA Connection Point:
F704 | Beenleigh | Yatala |  | NCC Rating (A) | 908 | 908 | 908 | 908 | 908
|  |  |  | 10 PoE Load (A) | 479 | 501 | 519 | 528 | 520
|  |  |  | Power Factor (System Normal) | 0.99 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | F7283 | ECC Rating (A) | 908 | 908 | 908 | 908 | 908
|  |  |  | 50 PoE Load (A) | 909 | 932 | 954 | 975 | 992
|  |  |  | Raw LAR (A) | 1 | 24 | 46 | 67 | 84
|  |  |  | 2Hr Rating (A) | 1049 | 1049 | 1049 | 1049 | 1049
Auto Trans Avail (A)
|  |  |  | Remote Trans Avail (A) | 286 | 285 | 284 | 282 | 280
Manual Trans Avail (A)
|  |  |  | POPS | No | No | No | No | No
|  |  |  | Mobile Gen Reqd (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F7351 | Jimboomba | Beaudesert |  | NCC Rating (A) | 578 | 578 | 578 | 578 | 578
|  |  |  | 10 PoE Load (A) | 258.7 | 258.3 | 269.9 | 281.6 | 293.3
|  |  |  | Power Factor (System Normal) | 0.94 | 0.94 | 0.94 | 0.94 | 0.94
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | F7351 | ECC Rating (A)
|  |  |  | 50 PoE Load (A) | 220.8 | 223.8 | 233.4 | 242.9 | 251.2
|  |  |  | Hours PA>95% Peak Load | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
|  |  |  | Raw LAR (A) | 220.8 | 223.8 | 233.4 | 242.9 | 251.2
2Hr Rating (A)
|  |  |  | Auto Trans Avail (A) | 38.1 | 37.8 | 37.6 | 37.5 | 37.3
|  |  |  | Remote Trans Avail (A) | 196.5 | 199.8 | 120.2 | 118 | 120.1
Manual Trans Avail (A)
|  |  |  | POPS | No | No | No | No | No
|  |  |  | Mobile Gen Reqd (A) | 0 | 0 | 52 | 52 | 52
|  |  |  | LARc (A) | 0 | 0 | 23 | 34.8 | 41.4
|  |  |  | LARc (MW) | 0 | 0 | 4.1 | 6.2 | 7.4
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | No | No | No
LOGANLEA Connection Point:
F7354 | Loganlea | Jimboomba |  | NCC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | 10 PoE Load (A) | 416 | 425 | 446 | 465 | 483
|  |  |  | Power Factor (System Normal) | 0.9 | 0.91 | 0.9 | 0.9 | 0.9
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F7377 | Yatala | Coomera |  | NCC Rating (A) | 908 | 908 | 908 | 908 | 908
|  |  |  | 10 PoE Load (A) | 167 | 180 | 196 | 207 | 199
|  |  |  | Power Factor (System Normal) | 0.96 | 1 | 1 | 1 | 1
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F787 | Loganlea | Beenleigh |  | NCC Rating (A) | 1047 | 1047 | 1047 | 1047 | 1047
|  |  |  | 10 PoE Load (A) | 539 | 567 | 568 | 569 | 567
|  |  |  | Power Factor (System Normal) | 0.94 | 0.92 | 0.93 | 0.93 | 0.93
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F788/1 | Beenleigh | Russell Island Tee |  | NCC Rating (A) | 184 | 184 | 184 | 184 | 184
|  |  |  | 10 PoE Load (A) | 49 | 50 | 50 | 51 | 52
|  |  |  | Power Factor (System Normal) | 1 | 1 | 1 | 1 | 1
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F788/2 | Russell Island Tee | Stradbroke Island |  | NCC Rating (A) | 184 | 184 | 184 | 184 | 184
|  |  |  | 10 PoE Load (A) | 25 | 25 | 25 | 25 | 25
|  |  |  | Power Factor (System Normal) | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
LOGANLEA Connection Point:
F788/3 | Russell Island Tee | Russell Island |  | NCC Rating (A) | 681 | 681 | 681 | 681 | 681
|  |  |  | 10 PoE Load (A) | 25 | 26 | 27 | 27 | 28
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F793 | Loganlea | North Springwood |  | NCC Rating (A) | 640 | 640 | 640 | 640 | 640
|  |  |  | 10 PoE Load (A) | 72 | 71 | 70 | 70 | 69
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.99
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F799 | Loganlea | North Springwood |  | NCC Rating (A) | 640 | 640 | 640 | 640 | 640
|  |  |  | 10 PoE Load (A) | 189 | 187 | 186 | 184 | 182
|  |  |  | Power Factor (System Normal) | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F820 | Loganlea | Jimboomba |  | NCC Rating (A) | 743 | 743 | 743 | 743 | 743
|  |  |  | 10 PoE Load (A) | 286 | 293 | 307 | 320 | 332
|  |  |  | Power Factor (System Normal) | 0.94 | 0.94 | 0.94 | 0.94 | 0.93
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F837 | Loganlea | Beenleigh |  | NCC Rating (A) | 1047 | 1047 | 1047 | 1047 | 1047
|  |  |  | 10 PoE Load (A) | 539 | 567 | 568 | 569 | 567
|  |  |  | Power Factor (System Normal) | 0.94 | 0.92 | 0.93 | 0.93 | 0.93
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
LOGANLEA Connection Point:
F836 | Loganlea | Browns Plains |  | NCC Rating (A) | 627 | 627 | 627 | 627 | 627
|  |  |  | 10 PoE Load (A) | 258 | 256 | 256 | 256 | 254
|  |  |  | Power Factor (System Normal) | 0.95 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F843 | Loganlea | Browns Plains |  | NCC Rating (A) | 684 | 684 | 684 | 684 | 684
|  |  |  | 10 PoE Load (A) | 329 | 327 | 327 | 326 | 324
|  |  |  | Power Factor (System Normal) | 0.95 | 0.95 | 0.95 | 0.95 | 0.95
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F904/1 | Beenleigh | Rocky Point Tee |  | NCC Rating (A) | 625 | 625 | 625 | 625 | 625
|  |  |  | 10 PoE Load (A) | 64 | 64 | 65 | 65 | 66
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F904/2 | Rocky Point Tee | Rocky Point |  | NCC Rating (A) | 640 | 640 | 640 | 640 | 640
|  |  |  | 10 PoE Load (A) | 0 | 0 | 0 | 0 | 0
Power Factor (System Normal)
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F904/3 | Rocky Point Tee | Ibis |  | NCC Rating (A) | 309 | 309 | 309 | 309 | 309
|  |  |  | 10 PoE Load (A) | 65 | 66 | 66 | 67 | 67
|  |  |  | Power Factor (System Normal) | 0.91 | 0.91 | 0.91 | 0.91 | 0.91
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
MIDDLE RIDGE Connection Point:
F726 | Postmans Ridge | Gatton |  | NCC Rating (A) | 441 | 441 | 441 | 441 | 441
|  |  |  | 10 PoE Load (A) | 196 | 216 | 213 | 214 | 210
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | F7259 | ECC Rating (A) | 441 | 441 | 441 | 441 | 441
|  |  |  | 50 PoE Load (A) | 514 | 539 | 537 | 532 | 530
|  |  |  | Hours PA>95% Peak Load | 4.5 | 4.5 | 4.5 | 4.5 | 4.5
|  |  |  | Raw LAR (A) | 73 | 98 | 96 | 91 | 89
|  |  |  | 2Hr Rating (A) | 535 | 535 | 535 | 535 | 535
Auto Trans Avail (A)
|  |  |  | Remote Trans Avail (A) | 47 | 46 | 46 | 46 | 45
|  |  |  | Manual Trans Avail (A) | 26 | 26 | 26 | 26 | 26
|  |  |  | POPS | No | No | No | No | No
|  |  |  | Mobile Gen Reqd (A) | 0 | 26 | 24 | 19 | 18
|  |  |  | LARc (A) | 0 | 4 | 2 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0.74686 | 0.37343 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | No | No | Yes | Yes
F727 | Middle Ridge | Postmans Ridge |  | NCC Rating (A) | 441 | 441 | 441 | 441 | 441
|  |  |  | 10 PoE Load (A) | 182 | 191 | 190 | 190 | 188
|  |  |  | Power Factor (System Normal) | 1 | 1 | 1 | 1 | 1
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F7348 | Middle Ridge | Postmans Ridge |  | NCC Rating (A) | 1000 | 1000 | 1000 | 1000 | 1000
|  |  |  | 10 PoE Load (A) | 209 | 220 | 219 | 218 | 217
|  |  |  | Power Factor (System Normal) | 0.93 | 0.93 | 0.93 | 0.93 | 0.93
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
MOLENDINAR Connection Point:
F7193 | Molendinar | Cades County |  | NCC Rating (A) | 895 | 895 | 895 | 895 | 895
|  |  |  | 10 PoE Load (A) | 526 | 521 | 522 | 531 | 546
|  |  |  | Power Factor (System Normal) | 0.9 | 0.91 | 0.91 | 0.91 | 0.91
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F7229 | Molendinar | Robina |  | NCC Rating (A) | 929 | 929 | 929 | 929 | 929
|  |  |  | 10 PoE Load (A) | 134 | 140 | 133 | 140 | 151
|  |  |  | Power Factor (System Normal) | 0.08 | 0.07 | 0.08 | 0.05 | 0.02
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F7283 | Cades County | Coomera |  | NCC Rating (A) | 908 | 908 | 908 | 908 | 908
|  |  |  | 10 PoE Load (A) | 536 | 544 | 544 | 558 | 587
|  |  |  | Power Factor (System Normal) | 0.85 | 0.87 | 0.88 | 0.87 | 0.87
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | F704 | ECC Rating (A) | 908 | 908 | 908 | 908 | 908
|  |  |  | 50 PoE Load (A) |  |  | 915 | 934 | 946
|  |  |  | Raw LAR (A) |  |  | 7 | 26 | 38
|  |  |  | 2Hr Rating (A) |  |  | 1049 | 1049 | 1049
Auto Trans Avail (A)
|  |  |  | Remote Trans Avail (A) |  |  | 284 | 282 | 280
Manual Trans Avail (A)
|  |  |  | POPS |  |  | No | No | No
|  |  |  | Mobile Gen Reqd (A) |  |  | 0 | 0 | 0
|  |  |  | LARc (A) |  |  | 0 | 0 | 0
|  |  |  | LARc (MW) |  |  | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
MOLENDINAR Connection Point:
F7297 | Molendinar | Cades County |  | NCC Rating (A) | 895 | 895 | 895 | 895 | 895
|  |  |  | 10 PoE Load (A) | 526 | 521 | 522 | 531 | 546
|  |  |  | Power Factor (System Normal) | 0.9 | 0.91 | 0.91 | 0.91 | 0.91
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F798 | Molendinar | Nerang |  | NCC Rating (A) | 929 | 929 | 929 | 929 | 929
|  |  |  | 10 PoE Load (A) | 217 | 220 | 215 | 218 | 223
|  |  |  | Power Factor (System Normal) | 0.71 | 0.7 | 0.71 | 0.69 | 0.62
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F907 | Molendinar | Southport |  | NCC Rating (A) | 785 | 785 | 785 | 785 | 785
|  |  |  | 10 PoE Load (A) | 197 | 197 | 198 | 199 | 199
|  |  |  | Power Factor (System Normal) | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F917 | Molendinar | Southport |  | NCC Rating (A) | 777 | 777 | 777 | 777 | 777
|  |  |  | 10 PoE Load (A) | 229 | 229 | 230 | 231 | 231
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F916 | Molendinar | Surfers Paradise |  | NCC Rating (A) | 1037 | 1037 | 1037 | 1037 | 1037
|  |  |  | 10 PoE Load (A) | 493 | 504 | 498 | 507 | 521
|  |  |  | Power Factor (System Normal) | 0.77 | 0.76 | 0.78 | 0.76 | 0.69
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
MUDGEERABA Connection Point:
F706 | Mudgeeraba | Nerang |  | NCC Rating (A) | 929 | 929 | 929 | 929 | 929
|  |  |  | 10 PoE Load (A) | 163 | 167 | 162 | 168 | 179
|  |  |  | Power Factor (System Normal) | 0.75 | 0.73 | 0.75 | 0.73 | 0.66
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F754 | Mudgeeraba | Burleigh Heads |  | NCC Rating (A) | 678 | 678 | 678 | 678 | 678
|  |  |  | 10 PoE Load (A) | 378 | 377 | 377 | 378 | 377
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F755 | Mudgeeraba | Burleigh Heads |  | NCC Rating (A) | 678 | 678 | 678 | 678 | 678
|  |  |  | 10 PoE Load (A) | 379 | 378 | 378 | 379 | 377
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F779 | Mudgeeraba | Merrimac |  | NCC Rating (A) | 1333 | 1333 | 1333 | 1333 | 1333
|  |  |  | 10 PoE Load (A) | 257 | 262 | 257 | 264 | 275
|  |  |  | Power Factor (System Normal) | 0.86 | 0.85 | 0.87 | 0.85 | 0.81
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F780 | Mudgeeraba | Merrimac |  | NCC Rating (A) | 1333 | 1333 | 1333 | 1333 | 1333
|  |  |  | 10 PoE Load (A) | 257 | 262 | 257 | 264 | 275
|  |  |  | Power Factor (System Normal) | 0.86 | 0.85 | 0.87 | 0.85 | 0.81
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
MUDGEERABA Connection Point:
F794 | Mudgeeraba | Robina |  | NCC Rating (A) | 929 | 929 | 929 | 929 | 929
|  |  |  | 10 PoE Load (A) | 297 | 297 | 295 | 299 | 305
|  |  |  | Power Factor (System Normal) | 0.97 | 0.96 | 0.97 | 0.96 | 0.94
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F826 | Broadbeach | Surfers Paradise |  | NCC Rating (A) | 537 | 537 | 537 | 537 | 537
|  |  |  | 10 PoE Load (A) | 158 | 164 | 156 | 164 | 177
|  |  |  | Power Factor (System Normal) | 0.09 | 0.08 | 0.09 | 0.06 | 0.03
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F827 | Broadbeach | Surfers Paradise |  | NCC Rating (A) | 537 | 537 | 537 | 537 | 537
|  |  |  | 10 PoE Load (A) | 158 | 164 | 156 | 164 | 177
|  |  |  | Power Factor (System Normal) | 0.09 | 0.08 | 0.09 | 0.06 | 0.03
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F838 | Mudgeeraba | Varsity Lakes |  | NCC Rating (A) | 1272 | 1272 | 1272 | 1272 | 1272
|  |  |  | 10 PoE Load (A) | 106 | 105 | 105 | 105 | 104
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F839 | Mudgeeraba | Varsity Lakes |  | NCC Rating (A) | 1272 | 1272 | 1272 | 1272 | 1272
|  |  |  | 10 PoE Load (A) | 106 | 105 | 105 | 105 | 104
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
MUDGEERABA Connection Point:
F918 | Merrimac | Broadbeach |  | NCC Rating (A) | 1214 | 1214 | 1214 | 1214 | 1214
|  |  |  | 10 PoE Load (A) | 196 | 202 | 196 | 204 | 217
|  |  |  | Power Factor (System Normal) | 0.74 | 0.72 | 0.75 | 0.74 | 0.67
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F919 | Merrimac | Broadbeach |  | NCC Rating (A) | 1214 | 1214 | 1214 | 1214 | 1214
|  |  |  | 10 PoE Load (A) | 196 | 203 | 196 | 204 | 217
|  |  |  | Power Factor (System Normal) | 0.74 | 0.72 | 0.75 | 0.73 | 0.67
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
MURARRIE Connection Point:
F7270 | Murarrie | Lytton Bulk |  | NCC Rating (A) | 1009 | 1009 | 1009 | 1009 | 1009
|  |  |  | 10 PoE Load (A) | 322 | 326 | 325 | 339 | 340
|  |  |  | Power Factor (System Normal) | 0.99 | 0.99 | 0.99 | 0.96 | 0.99
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F7271 | Murarrie | Lytton Bulk |  | NCC Rating (A) | 1009 | 1009 | 1009 | 1009 | 1009
|  |  |  | 10 PoE Load (A) | 322 | 326 | 325 | 339 | 340
|  |  |  | Power Factor (System Normal) | 0.99 | 0.99 | 0.99 | 0.96 | 0.99
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F7272 | Murarrie | Doboy |  | NCC Rating (A) | 908 | 908 | 908 | 908 | 908
|  |  |  | 10 PoE Load (A) | 250 | 250 | 253 | 253 | 258
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F7273 | Murarrie | Doboy |  | NCC Rating (A) | 908 | 908 | 908 | 908 | 908
|  |  |  | 10 PoE Load (A) | 250 | 250 | 253 | 253 | 258
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F7274 | Murarrie | Doboy |  | NCC Rating (A) | 908 | 908 | 908 | 908 | 908
|  |  |  | 10 PoE Load (A) | 250 | 250 | 253 | 253 | 258
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
PALMWOODS Connection Point:
F745/2 | Moodlu | Beerwah Tee |  | NCC Rating (A) | 768 | 768 | 768 | 768 | 768
|  |  |  | 10 PoE Load (A) | 229 | 231 | 229 | 226 | 220
|  |  |  | Power Factor (System Normal) | 1 | 1 | 0.98 | 0.99 | 0.97
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F745/3 | Moodlu | Caboolture |  | NCC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 10 PoE Load (A) | 431 | 434 | 439 | 442 | 443
|  |  |  | Power Factor (System Normal) | 0.97 | 0.97 | 0.97 | 0.97 | 0.97
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F745/4 | Palmwoods | Beerwah Tee |  | NCC Rating (A) | 768 | 768 | 768 | 768 | 768
|  |  |  | 10 PoE Load (A) | 376 | 380 | 375 | 377 | 368
|  |  |  | Power Factor (System Normal) | 0.99 | 0.99 | 1 | 1 | 1
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F745/5 | Beerwah Tee | Beerwah |  | NCC Rating (A) | 684 | 684 | 684 | 684 | 684
|  |  |  | 10 PoE Load (A) | 149 | 151 | 154 | 155 | 155
|  |  |  | Power Factor (System Normal) | 0.95 | 0.95 | 0.94 | 0.94 | 0.94
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F746/2 | Moodlu | Beerwah Tee |  | NCC Rating (A) | 768 | 768 | 768 | 768 | 768
|  |  |  | 10 PoE Load (A) | 230 | 231 | 229 | 227 | 220
|  |  |  | Power Factor (System Normal) | 1 | 1 | 0.98 | 0.99 | 0.97
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
PALMWOODS Connection Point:
F746/3 | Moodlu | Caboolture |  | NCC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 10 PoE Load (A) | 432 | 435 | 440 | 443 | 444
|  |  |  | Power Factor (System Normal) | 0.97 | 0.97 | 0.97 | 0.97 | 0.97
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F746/4 | Palmwoods | Beerwah Tee |  | NCC Rating (A) | 768 | 768 | 768 | 768 | 768
|  |  |  | 10 PoE Load (A) | 377 | 380 | 375 | 377 | 368
|  |  |  | Power Factor (System Normal) | 0.99 | 0.99 | 1 | 1 | 1
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F746/5 | Beerwah Tee | Beerwah |  | NCC Rating (A) | 976 | 976 | 976 | 976 | 976
|  |  |  | 10 PoE Load (A) | 149 | 151 | 154 | 155 | 155
|  |  |  | Power Factor (System Normal) | 0.95 | 0.95 | 0.94 | 0.94 | 0.94
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
PALMWOODS 132 kV Connection Point:
F7189/1 | Palmwoods | Image Flat |  | NCC Rating (A) | 748 | 748 | 748 | 748 | 748
|  |  |  | 10 PoE Load (A) | 119 | 117 | 108 | 107 | 107
|  |  |  | Power Factor (System Normal) | 0.1 | 0.12 | 0.1 | 0.1 | 0.11
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F7189/2 | Image Flat | Cooroy |  | NCC Rating (A) | 703 | 703 | 703 | 703 | 703
|  |  |  | 10 PoE Load (A) | 182 | 179 | 177 | 177 | 170
|  |  |  | Power Factor (System Normal) | 0.79 | 0.8 | 0.82 | 0.83 | 0.86
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F7189/3 | Image Flat | Nambour |  | NCC Rating (A) | 524 | 524 | 524 | 524 | 524
|  |  |  | 10 PoE Load (A) | 155 | 155 | 155 | 156 | 156
|  |  |  | Power Factor (System Normal) | 1 | 1 | 1 | 1 | 1
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F7298 | Sunrise Hills | Noosaville |  | NCC Rating (A) | 684 | 684 | 684 | 684 | 684
|  |  |  | 10 PoE Load (A) | 78 | 77 | 77 | 77 | 76
|  |  |  | Power Factor (System Normal) | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F777 | Palmwoods | Mooloolaba |  | NCC Rating (A) | 1078 | 1078 | 1078 | 1078 | 1078
|  |  |  | 10 PoE Load (A) | 560 | 326 | 335 | 343 | 346
|  |  |  | Power Factor (System Normal) | 1 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
PALMWOODS 132 kV Connection Point:
F778 | Palmwoods | Mooloolaba |  | NCC Rating (A) | 1078 | 1078 | 1078 | 1078 | 1078
|  |  |  | 10 PoE Load (A) | 560 | 326 | 335 | 343 | 346
|  |  |  | Power Factor (System Normal) | 1 | 0.98 | 0.98 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F790 | Sunrise Hills | Noosaville |  | NCC Rating (A) | 684 | 684 | 684 | 684 | 684
|  |  |  | 10 PoE Load (A) | 78 | 78 | 78 | 78 | 77
|  |  |  | Power Factor (System Normal) | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F795/1 | Palmwoods | Image Flat |  | NCC Rating (A) | 748 | 748 | 748 | 748 | 748
|  |  |  | 10 PoE Load (A) | 119 | 117 | 109 | 107 | 107
|  |  |  | Power Factor (System Normal) | 0.1 | 0.12 | 0.09 | 0.09 | 0.11
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F795/2 | Image Flat | Cooroy |  | NCC Rating (A) | 703 | 703 | 703 | 703 | 703
|  |  |  | 10 PoE Load (A) | 182 | 180 | 178 | 177 | 171
|  |  |  | Power Factor (System Normal) | 0.79 | 0.79 | 0.82 | 0.83 | 0.86
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F795/3 | Image Flat | Nambour |  | NCC Rating (A) | 524 | 524 | 524 | 524 | 524
|  |  |  | 10 PoE Load (A) | 155 | 155 | 155 | 156 | 156
|  |  |  | Power Factor (System Normal) | 1 | 1 | 1 | 1 | 1
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
PALMWOODS 132 kV Connection Point:
F796 | Cooroy | Sunrise Hills |  | NCC Rating (A) | 684 | 684 | 684 | 684 | 684
|  |  |  | 10 PoE Load (A) | 242 | 241 | 245 | 245 | 244
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F797 | Cooroy | Sunrise Hills |  | NCC Rating (A) | 684 | 684 | 684 | 684 | 684
|  |  |  | 10 PoE Load (A) | 242 | 241 | 245 | 245 | 244
|  |  |  | Power Factor (System Normal) | 0.96 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F803 | Mooloolaba | Caloundra |  | NCC Rating (A) | 684 | 684 | 684 | 684 | 684
|  |  |  | 10 PoE Load (A) | 203 | 206 | 215 | 221 | 224
|  |  |  | Power Factor (System Normal) | 0.97 | 0.97 | 0.97 | 0.98 | 0.98
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F804 | Caloundra | Currimundi |  | NCC Rating (A) | 664 | 664 | 664 | 664 | 664
|  |  |  | 10 PoE Load (A) | 18 | 20 | 18 | 20 | 21
|  |  |  | Power Factor (System Normal) | 1 | 1 | 1 | 0.86 | 0.91
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F815 | Mooloolaba | Alexandra Headlands |  | NCC Rating (A) | 684 | 684 | 684 | 684 | 684
|  |  |  | 10 PoE Load (A) | 276 | 128 | 132 | 132 | 136
|  |  |  | Power Factor (System Normal) | 0.96 | 0.55 | 0.55 | 0.52 | 0.53
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
PALMWOODS 132 kV Connection Point:
F816 | Mooloolaba | West Maroochydore |  | NCC Rating (A) | 684 | 684 | 684 | 684 | 684
|  |  |  | 10 PoE Load (A) | 200 | 133 | 137 | 143 | 142
|  |  |  | Power Factor (System Normal) | 0.97 | 0.74 | 0.75 | 0.76 | 0.77
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F819 | Mooloolaba | Kawana |  | NCC Rating (A) | 627 | 627 | 627 | 627 | 627
|  |  |  | 10 PoE Load (A) | 305 | 308 | 321 | 331 | 335
|  |  |  | Power Factor (System Normal) | 0.98 | 0.98 | 0.98 | 0.99 | 0.99
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F821 | West Maroochydore | Alexandra Headlands |  | NCC Rating (A) | 684 | 684 | 684 | 684 | 684
|  |  |  | 10 PoE Load (A) | 69 | 255 | 265 | 268 | 276
|  |  |  | Power Factor (System Normal) | 0.88 | 1 | 1 | 1 | 1
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F844 | Kawana | Birtinya |  | NCC Rating (A) | 664 | 664 | 664 | 664 | 664
|  |  |  | 10 PoE Load (A) | 177 | 181 | 192 | 203 | 206
|  |  |  | Power Factor (System Normal) | 1 | 1 | 1 | 1 | 1
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F851 | Birtinya | Currimundi |  | NCC Rating (A) | 664 | 664 | 664 | 664 | 664
|  |  |  | 10 PoE Load (A) | 92 | 95 | 94 | 93 | 95
|  |  |  | Power Factor (System Normal) | 1 | 1 | 1 | 1 | 1
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
PALMWOODS 132 kV Connection Point:
PWD-WMD#1 | Palmwoods | West Maroochydore |  | NCC Rating (A) |  | 1018 | 1018 | 1018 | 1018
|  |  |  | 10 PoE Load (A) |  | 246 | 253 | 257 | 260
|  |  |  | Power Factor (System Normal) |  | 0.9932 | 0.99 | 0.99 | 0.99
|  |  |  | LARn (A) |  | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) |  | 0 | 0 | 0 | 0
|  |  |  | Customer Category |  | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std |  | Yes | Yes | Yes | Yes
PWD-WMD#2 | Palmwoods | West Maroochydore |  | NCC Rating (A) |  | 1018 | 1018 | 1018 | 1018
|  |  |  | 10 PoE Load (A) |  | 246 | 253 | 257 | 260
|  |  |  | Power Factor (System Normal) |  | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | LARn (A) |  | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) |  | 0 | 0 | 0 | 0
|  |  |  | Customer Category |  | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std |  | Yes | Yes | Yes | Yes
ROCKLEA Connection Point:
F817 | Rocklea | Archerfield |  | NCC Rating (A) | 908 | 908 | 908 | 908 | 908
|  |  |  | 10 PoE Load (A) | 193 | 190 | 187 | 184 | 181
|  |  |  | Power Factor (System Normal) | 0.94 | 0.94 | 0.94 | 0.94 | 0.94
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F818 | Rocklea | Archerfield |  | NCC Rating (A) | 908 | 908 | 908 | 908 | 908
|  |  |  | 10 PoE Load (A) | 193 | 190 | 187 | 184 | 181
|  |  |  | Power Factor (System Normal) | 0.94 | 0.94 | 0.94 | 0.94 | 0.94
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
SOUTH PINE Connection Point:
F7337 | Nudgee | Myrtletown |  | NCC Rating (A) | 1106 | 1106 | 1106 | 1106 | 1106
|  |  |  | 10 PoE Load (A) | 111 | 110 | 112 | 111 | 110
|  |  |  | Power Factor (System Normal) | 0.97 | 0.97 | 0.97 | 0.97 | 0.97
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | High Sec | High Sec | High Sec | High Sec | High Sec
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F7338 | Nudgee | Myrtletown |  | NCC Rating (A) | 1106 | 1106 | 1106 | 1106 | 1106
|  |  |  | 10 PoE Load (A) | 111 | 110 | 112 | 111 | 110
|  |  |  | Power Factor (System Normal) | 0.97 | 0.97 | 0.97 | 0.97 | 0.97
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | High Sec | High Sec | High Sec | High Sec | High Sec
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F7341 | South Pine | Nudgee |  | NCC Rating (A) | 1553 | 1553 | 1553 | 1553 | 1553
|  |  |  | 10 PoE Load (A) | 668 | 690 | 744 | 744 | 742
|  |  |  | Power Factor (System Normal) | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F7342 | South Pine | Nudgee |  | NCC Rating (A) | 1553 | 1553 | 1553 | 1553 | 1553
|  |  |  | 10 PoE Load (A) | 669 | 691 | 745 | 745 | 743
|  |  |  | Power Factor (System Normal) | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F7344 | South Pine | Griffin |  | NCC Rating (A) | 1220 | 1220 | 1220 | 1220 | 1220
|  |  |  | 10 PoE Load (A) | 332 | 332 | 333 | 336 | 343
|  |  |  | Power Factor (System Normal) | 0.99 | 0.99 | 1 | 1 | 0.99
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
SOUTH PINE Connection Point:
F7345 | South Pine | Griffin |  | NCC Rating (A) | 1220 | 1220 | 1220 | 1220 | 1220
|  |  |  | 10 PoE Load (A) | 332 | 332 | 333 | 336 | 343
|  |  |  | Power Factor (System Normal) | 0.99 | 0.99 | 1 | 1 | 0.99
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F7358 | Griffin | Hays Inlet |  | NCC Rating (A) | 1373 | 1373 | 1373 | 1373 | 1373
|  |  |  | 10 PoE Load (A) | 266 | 264 | 261 | 262 | 267
|  |  |  | Power Factor (System Normal) | 0.98 | 0.99 | 1 | 1 | 0.99
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F737/1 | South Pine | Bunyaville |  | NCC Rating (A) | 918 | 918 | 918 | 918 | 918
|  |  |  | 10 PoE Load (A) | 499 | 497 | 445 | 443 | 439
|  |  |  | Power Factor (System Normal) | 0.99 | 0.99 | 1 | 1 | 1
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F737/2 | Bunyaville | Stafford |  | NCC Rating (A) | 1264 | 1264 | 1264 | 1264 | 1264
|  |  |  | 10 PoE Load (A) | 497 | 496 | 444 | 442 | 438
|  |  |  | Power Factor (System Normal) | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F738/1 | South Pine | Bunyaville |  | NCC Rating (A) | 918 | 918 | 918 | 918 | 918
|  |  |  | 10 PoE Load (A) | 499 | 497 | 445 | 443 | 439
|  |  |  | Power Factor (System Normal) | 0.99 | 0.99 | 1 | 1 | 1
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
SOUTH PINE Connection Point:
F738/2 | Bunyaville B | Stafford |  | NCC Rating (A) | 1264 | 1264 | 1264 | 1264 | 1264
|  |  |  | 10 PoE Load (A) | 497 | 496 | 444 | 442 | 438
|  |  |  | Power Factor (System Normal) | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F739 | South Pine | Bald Hills |  | NCC Rating (A) | 1600 | 1600 | 1600 | 1600 | 1600
|  |  |  | 10 PoE Load (A) | 257 | 254 | 252 | 251 | 249
|  |  |  | Power Factor (System Normal) | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F740 | South Pine | Sandgate |  | NCC Rating (A) | 1600 | 1600 | 1600 | 1600 | 1600
|  |  |  | 10 PoE Load (A) | 245 | 243 | 242 | 241 | 238
|  |  |  | Power Factor (System Normal) | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F741 | South Pine | Hays Inlet |  | NCC Rating (A) | 635 | 635 | 635 | 635 | 635
|  |  |  | 10 PoE Load (A) | 289 | 295 | 299 | 301 | 299
|  |  |  | Power Factor (System Normal) | 1 | 1 | 0.99 | 0.99 | 0.99
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F742 | South Pine | Hays Inlet |  | NCC Rating (A) | 635 | 635 | 635 | 635 | 635
|  |  |  | 10 PoE Load (A) | 288 | 293 | 298 | 300 | 298
|  |  |  | Power Factor (System Normal) | 1 | 1 | 0.99 | 0.99 | 0.99
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
SOUTH PINE Connection Point:
F7299 | South Pine | Brendale |  | NCC Rating (A) | 949 | 949 | 949 | 949 | 949
|  |  |  | 10 PoE Load (A) | 325 | 322 | 321 | 321 | 319
|  |  |  | Power Factor (System Normal) | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F743 | South Pine | Brendale |  | NCC Rating (A) | 594 | 594 | 594 | 594 | 594
|  |  |  | 10 PoE Load (A) | 325 | 322 | 321 | 321 | 319
|  |  |  | Power Factor (System Normal) | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F744 | South Pine | Brendale |  | NCC Rating (A) | 594 | 594 | 594 | 594 | 594
|  |  |  | 10 PoE Load (A) | 325 | 322 | 321 | 321 | 319
|  |  |  | Power Factor (System Normal) | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F745/1 | South Pine | Moodlu |  | NCC Rating (A) | 768 | 768 | 768 | 768 | 768
|  |  |  | 10 PoE Load (A) | 230 | 232 | 258 | 252 | 268
|  |  |  | Power Factor (System Normal) | 0.85 | 0.85 | 0.8 | 0.83 | 0.8
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F746/1 | South Pine | Moodlu |  | NCC Rating (A) | 768 | 768 | 768 | 768 | 768
|  |  |  | 10 PoE Load (A) | 231 | 232 | 258 | 252 | 269
|  |  |  | Power Factor (System Normal) | 0.85 | 0.85 | 0.8 | 0.83 | 0.8
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
SOUTH PINE Connection Point:
F831 | Bald Hills | Sandgate |  | NCC Rating (A) | 1600 | 1600 | 1600 | 1600 | 1600
|  |  |  | 10 PoE Load (A) | 226 | 226 | 224 | 223 | 221
|  |  |  | Power Factor (System Normal) | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F912 | Nudgee | Meeandah |  | NCC Rating (A) | 532 | 532 | 532 | 532 | 532
|  |  |  | 10 PoE Load (A) | 134 | 149 | 153 | 156 | 159
|  |  |  | Power Factor (System Normal) | 0.94 | 0.94 | 0.94 | 0.94 | 0.94
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F913 | Nudgee | Meeandah |  | NCC Rating (A) | 532 | 532 | 532 | 532 | 532
|  |  |  | 10 PoE Load (A) | 135 | 149 | 153 | 156 | 159
|  |  |  | Power Factor (System Normal) | 0.94 | 0.94 | 0.94 | 0.94 | 0.94
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Urban | Urban | Urban | Urban | Urban
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
WOOLOOGA 132 kV Connection Point:
F7186 | Cooran | Cooroy |  | NCC Rating (A) | 734 | 734 | 734 | 734 | 734
|  |  |  | 10 PoE Load (A) | 353 | 350 | 352 | 352 | 343
|  |  |  | Power Factor (System Normal) | 0.9 | 0.9 | 0.92 | 0.92 | 0.93
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F7343 | Traveston | Cooran |  | NCC Rating (A) | 734 | 734 | 734 | 734 | 734
|  |  |  | 10 PoE Load (A) | 374 | 371 | 374 | 374 | 365
|  |  |  | Power Factor (System Normal) | 0.93 | 0.93 | 0.95 | 0.94 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
F747/1 | Gympie | Traveston |  | NCC Rating (A) | 734 | 734 | 734 | 734 | 734
|  |  |  | 10 PoE Load (A) | 388 | 385 | 389 | 389 | 381
|  |  |  | Power Factor (System Normal) | 0.95 | 0.95 | 0.96 | 0.96 | 0.97
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
WOOLOOGA 132 kV Connection Point:
F747/2 | Woolooga | Gympie |  | NCC Rating (A) | 763 | 763 | 763 | 763 | 763
|  |  |  | 10 PoE Load (A) | 585 | 581 | 588 | 587 | 578
|  |  |  | Power Factor (System Normal) | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | PLQ_810 | ECC Rating (A) | 763 | 763 | 763 | 763 | 763
|  |  |  | 50 PoE Load (A) | 865 | 863 | 862 | 872 | 862
|  |  |  | Raw LAR (A) | 102 | 100 | 99 | 109 | 92
|  |  |  | 2Hr Rating (A) | 893 | 893 | 893 | 893 | 893
Auto Trans Avail (A)
|  |  |  | Remote Trans Avail (A) | 614 | 615 | 613 | 623 | 607
Manual Trans Avail (A)
|  |  |  | POPS | No | No | No | No | No
|  |  |  | Mobile Gen Reqd (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  | F748 | ECC Rating (A) | 763 | 763 | 763 | 763 | 763
|  |  |  | 50 PoE Load (A) | 783 | 783 | 785 | 789 | 782
|  |  |  | Raw LAR (A) | 20 | 20 | 22 | 26 | 19
|  |  |  | 2Hr Rating (A) | 893 | 893 | 893 | 893 | 893
Auto Trans Avail (A)
Remote Trans Avail (A)
Manual Trans Avail (A)
|  |  |  | POPS | No | No | No | No | No
|  |  |  | Mobile Gen Reqd (A) | 20 | 20 | 22 | 26 | 19
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
WOOLOOGA 132 kV Connection Point:
F748/1 | Gympie | Cooroy |  | NCC Rating (A) | 734 | 734 | 734 | 734 | 734
|  |  |  | 10 PoE Load (A) | 476 | 473 | 478 | 478 | 468
|  |  |  | Power Factor (System Normal) | 0.95 | 0.95 | 0.96 | 0.96 | 0.96
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | PLQ_810 | ECC Rating (A) | 734 | 734 | 734 | 734 | 734
|  |  |  | 50 PoE Load (A) | 801 | 798 | 799 | 808 | 799
|  |  |  | Raw LAR (A) | 67 | 64 | 65 | 74 | 65
|  |  |  | 2Hr Rating (A) | 861 | 861 | 861 | 861 | 861
Auto Trans Avail (A)
|  |  |  | Remote Trans Avail (A) | 778 | 778 | 777 | 778 | 771
Manual Trans Avail (A)
|  |  |  | POPS | No | No | No | No | No
|  |  |  | Mobile Gen Reqd (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes
WOOLOOGA 132 kV Connection Point:
F748/2 | Woolooga | Gympie |  | NCC Rating (A) | 763 | 763 | 763 | 763 | 763
|  |  |  | 10 PoE Load (A) | 574.5 | 570.3 | 571.6 | 571.8 | 568
|  |  |  | Power Factor (System Normal) | 0.98 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | LARn (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARn (MW) | 0 | 0 | 0 | 0 | 0
|  |  | PLQ_810 | ECC Rating (A) | 763 | 763 | 763 | 763 | 763
|  |  |  | 50 PoE Load (A) | 883.4 | 881.8 | 880.5 | 880.5 | 872.3
|  |  |  | Raw LAR (A) | 120.4 | 118.8 | 117.5 | 117.5 | 109.3
|  |  |  | 2Hr Rating (A) | 893 | 893 | 893 | 893 | 893
Auto Trans Avail (A)
|  |  |  | Remote Trans Avail (A) | 749 | 749 | 750 | 745 | 742
Manual Trans Avail (A)
|  |  |  | POPS | No | No | No | No | No
|  |  |  | Mobile Gen Reqd (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  | F747 | ECC Rating (A) | 763 | 763 | 763 | 763 | 763
|  |  |  | 50 PoE Load (A) | 781.3 | 781.5 | 783.5 | 788.1 | 777.7
|  |  |  | Raw LAR (A) | 18.3 | 18.5 | 20.5 | 25.1 | 14.7
|  |  |  | 2Hr Rating (A) | 893 | 893 | 893 | 893 | 893
Auto Trans Avail (A)
|  |  |  | Remote Trans Avail (A) | 469 | 469 | 472 | 479 | 472
Manual Trans Avail (A)
|  |  |  | POPS | No | No | No | No | No
|  |  |  | Mobile Gen Reqd (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | LARc (MW) | 0 | 0 | 0 | 0 | 0
|  |  |  | Customer Category | Rural | Rural | Rural | Rural | Rural
|  |  |  | Meets Sec Std | Yes | Yes | Yes | Yes | Yes