## Notes
Sub-Transmission Feeders Forecasts (Energex Distribution Annual Planning Report 2020-21 to 2024-25)
This workbook provides 5 year forecast capacity and loading information for sub-transmission feeders in the Energex network.
This workbook forms part of the Energex Distribution Annual Planning Report 2020-21 to 2024-25 (DAPR) and should be read in conjunction with the report document.
Energex Distribution Annual Planning Report is prepared and made available solely for information purposes. While care was taken in the preparation of the information in this report, and it is provided in good faith, Energex accepts no responsibility or liability (including without limitation, liability to any person by reason of negligence or negligent mis-statement) for any loss or damage that may be incurred by any person acting in reliance on this information or assumptions drawn from it, except to the extent that liability under any applicable Queensland or Commonwealth of Australia statute cannot be excluded.
It contains assumptions regarding, among other things, economic growth and load forecasts which may or may not prove to be correct. The forecasts included in the document involve subjective judgements and analysis which are subject to significant uncertainties and contingencies, many of which are out of the control of Energex. Furthermore, forecasted data is subject to ongoing variation due to COVID 19 impacts. Energex makes no representation or warranty as to the accuracy, reliability, completeness or suitability for any particular purpose of the information in this document. All information should be independently investigated, reviewed, analysed and verified, and must not be relied upon in connection with any investment proposal or decision.
The following sections list the 33kV feeders, their forecast loads, power factor, customer category and available load transfers. The feeder loads are calculated from load flow results using forecast substation demands. For the transmission and sub-transmission feeders, load flow studies are conducted for system normal and single contingency situations.
The forecast and capacity cut-off date for the winter season is 1 June of each year, and for the summer season is 1 December of each year. For example, 2021 winter forecast includes all committed projects with a proposed commissioning date up to 1 June 2021, and the 2020/21 summer forecast includes all committed projects with a proposed commissioning date up to 1 December 2020.
Assessment of 33 kV feeders is performed under four possible risk periods: winter day, winter night, summer day and summer night. For the summer table, the worst case (highest) load between summer day and summer night has been represented in the table.
Peak, reconciled, compensated load forecasts have been used in the 33kV feeder analyses, with 50 PoE forecast load used for single contingency studies, and 10 PoE forecast load used for system normal studies.
Feeder capacities are shown for ECC and NCC. These ratings have also been adjusted for known committed projects. All load transfers associated with contingent condition include acceptable feeder voltage profiles.
Although the conductor rating is generally the limiting factor for feeder capacity, there are other significant items of plant, such as the feeder circuit breaker, that can also restrict capacity. Furthermore, other factors such as voltage constraints and load sharing between parallel underground feeders can sometimes de‑rate the capacity of the feeders due to thermal characteristic constraints. Each of these factors has been taken into account in the production of the forecast tables.
Interconnected feeders that supply multiple customers are examined in the following tables. Feeders exclusively supplying a customer owned substation or dedicated to a customer are not included in these tables.
A definition of terms is shown in the table below.
Definition of Terms Feeder Capacity and Forecast Tables
Term | Definition
NCC Rating (A) | Normal Cyclic Capacity - the total capacity with all network components and equipment intact. This is the maximum permissible peak daily loading for a given load cycle that a feeder can supply each day of its life. For overhead feeders, the NCC is the conductor rating with an assumed 1m/s wind, orthogonal to the line. For underground cables, the NCC assumes that there are sufficient temperature and current operating margins from the thermal inertia of the cable and its surroundings.
10 PoE Load (A) | Peak load forecast with 10% probability of being exceeded (one in every 10 years will be exceeded). Based on normal expected growth rates and weather corrected starting loads.
Power Factor (System Normal) | Lowest power factor along the feeder at 10 PoE Peak Load. Where the Power Factor is either 0 the feeder is a normally open feeder that does not have load under System Normal conditions.
ECC Rating (A) | Emergency Cyclic Capacity – the long term firm delivery capacity under single contingency conditions. Some underground cables are installed in close proximity to other circuits and are normally de‑rated to allow for the heat generated by the adjacent cables. ECC is the higher capacity available when any adjacent circuits have been unloaded. For overhead conductors which do not benefit from this phenomenon, the ECC is synonymous with the NCC.
50 PoE Load (A) | Peak load forecast with 50% probability of being exceeded (one in every two years will be exceeded). Based on normal expected growth rates & weather corrected starting loads. This is the worst case (highest) load forecast beween summer day and summer night.
Customer Category | For security standard application, the general type of customer a sub-transmission, or transmission feeder is supplying.
Transfers | This is the total amount of load transfers that are available following the worst case network contingency. This includes automatic transfers that are controlled automatically through SCADA and are generally implemented within a minute, load transfers that can be implemented through screen switching by a network controller, manual transfers that are deployed via manually controlled switchgear locally by field staff, and mobile generation which can be deployed by field staff by moving generation to specific sites. It should be noted under the Safety Net in the Distribution Authority, it is generally assumed that 4MVA (70A) of generation is available for Urban feeders to meet this criteria and 10MVA (170A) is available for Rural feeders. These values have been used as a default in the forecast tables where these are sufficient to reduce the 50PoE load below the ECC rating. Where the load is still above the ECC rating, specific load transfers have been calculated for the feeder to determine whether the Safety Net criteria is met.
Hours PA > 95% Peak Load | The forecast number of hours per annum where the load exceeded 95% of the peak 50 PoE demand. This information is not readily available for every feeder without significant analysis being undertaken. As such, this has only been provided where a feeder does not meet the Safety Net criteria or is otherwise in the Limitations and Proposed Solutions table.

## 33kV Feeders-Summer
Bulk Supply Name | Feeder | From Substation | To Substation | Attributes | 2021 | 2022 | 2023 | 2024 | 2025 | Customer Category | Transfers (Amps) | Hours PA > 95% Peak Load
Abermain Bulk | 357-1 | Abermain BS | 357 Tee1 | NCC Rating (A) | 505 | 505 | 505 | 505 | 505 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 171 | 170 | 169 | 168 | 166
|  |  |  | Power Factor | 0.974 | 0.974 | 0.974 | 0.974 | 0.975
|  |  |  | ECC Rating (A) | 505 | 505 | 505 | 505 | 505
|  |  |  | 50 POE Load (A) | 386 | 385 | 385 | 385 | 383
Abermain Bulk | 357-2 | 357 Tee1 | Redbank | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 365 | 364 | 365 | 365 | 365
Abermain Bulk | 357-3 | 357 Tee1 | Moggill | NCC Rating (A) | 710 | 710 | 710 | 710 | 710 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 172 | 171 | 170 | 169 | 167
|  |  |  | Power Factor | 0.977 | 0.977 | 0.977 | 0.977 | 0.977
|  |  |  | ECC Rating (A) | 710 | 710 | 710 | 710 | 710
|  |  |  | 50 POE Load (A) | 347 | 340 | 339 | 337 | 333
Abermain Bulk | 358-1 | Abermain BS | Ebbw Vale | NCC Rating (A) | 473 | 473 | 473 | 473 | 473 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 753 | 753 | 753 | 753 | 753
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Abermain Bulk | 364-1 | Marburg | Rosewood | NCC Rating (A) | 155 | 155 | 155 | 155 | 155 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 85 | 93 | 99 | 106 | 107
|  |  |  | Power Factor | 0.999 | 1 | 1 | 1 | 1
|  |  |  | ECC Rating (A) | 155 | 155 | 155 | 155 | 155
|  |  |  | 50 POE Load (A) | 125 | 141 | 148 | 155 | 157
Abermain Bulk | 365-1 | Abermain BS | 365 Tee1 | NCC Rating (A) | 746 | 746 | 746 | 746 | 746 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 376 | 419 | 443 | 465 | 470
|  |  |  | Power Factor | 0.93 | 0.925 | 0.92 | 0.916 | 0.915
|  |  |  | ECC Rating (A) | 746 | 746 | 746 | 746 | 746
|  |  |  | 50 POE Load (A) | 617 | 705 | 736 | 765 | 773
Abermain Bulk | 365-2 | 365 Tee1 | 366 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Abermain Bulk | 365-3 | 365 Tee1 | Karrabin | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 376 | 420 | 443 | 466 | 471
|  |  |  | Power Factor | 0.949 | 0.947 | 0.944 | 0.942 | 0.941
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 617 | 705 | 736 | 765 | 773
Abermain Bulk | 366-1 | Abermain BS | 366 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 411 | 458 | 484 | 508 | 513
|  |  |  | Power Factor | 0.93 | 0.925 | 0.92 | 0.916 | 0.915
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 620 | 708 | 738 | 767 | 775
Abermain Bulk | 366-2 | 366 Tee1 | Karrabin | NCC Rating (A) | 758 | 758 | 758 | 758 | 758 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 411 | 458 | 484 | 508 | 514
|  |  |  | Power Factor | 0.948 | 0.946 | 0.943 | 0.94 | 0.94
|  |  |  | ECC Rating (A) | 758 | 758 | 758 | 758 | 758
|  |  |  | 50 POE Load (A) | 620 | 708 | 738 | 767 | 775
Abermain Bulk | 366-3 | 366 Tee1 | 365 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Abermain Bulk | 367-1 | Abermain BS | Mt Crosby West | NCC Rating (A) | 530 | 530 | 530 | 530 | 530 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 279 | 279 | 283 | 283 | 283
|  |  |  | Power Factor | 0.935 | 0.935 | 0.956 | 0.956 | 0.956
|  |  |  | ECC Rating (A) | 530 | 530 | 530 | 530 | 530
|  |  |  | 50 POE Load (A) | 469 | 465 | 469 | 465 | 465
Abermain Bulk | 368-1 | Abermain BS | Mt Crosby | NCC Rating (A) | 529 | 529 | 529 | 529 | 529 | HighSec | 0 | NA
|  |  |  | 10 POE Load (A) | 217 | 218 | 219 | 218 | 218
|  |  |  | Power Factor | 0.924 | 0.924 | 0.949 | 0.949 | 0.95
|  |  |  | ECC Rating (A) | 529 | 529 | 529 | 529 | 529
|  |  |  | 50 POE Load (A) | 469 | 469 | 474 | 467 | 467
Abermain Bulk | 369-1 | Abermain BS | Nth Ipswich | NCC Rating (A) | 499 | 499 | 499 | 499 | 499 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 222 | 224 | 226 | 228 | 229
|  |  |  | Power Factor | 0.992 | 0.991 | 0.991 | 0.991 | 0.991
|  |  |  | ECC Rating (A) | 499 | 499 | 499 | 499 | 499
|  |  |  | 50 POE Load (A) | 419 | 417 | 422 | 426 | 428
Abermain Bulk | 370-1 | Abermain BS | Nth Ipswich | NCC Rating (A) | 499 | 499 | 499 | 499 | 499 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 226 | 228 | 230 | 232 | 233
|  |  |  | Power Factor | 0.992 | 0.992 | 0.992 | 0.991 | 0.991
|  |  |  | ECC Rating (A) | 499 | 499 | 499 | 499 | 499
|  |  |  | 50 POE Load (A) | 419 | 417 | 421 | 425 | 427
Abermain Bulk | 387-1 | Abermain BS | Marburg | NCC Rating (A) | 290 | 290 | 290 | 290 | 290 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 184 | 196 | 205 | 214 | 216
|  |  |  | Power Factor | 0.987 | 0.986 | 0.984 | 0.982 | 0.982
|  |  |  | ECC Rating (A) | 290 | 290 | 290 | 290 | 290
|  |  |  | 50 POE Load (A) | 225 | 242 | 256 | 270 | 273
Abermain Bulk | 3901-1 | Karrabin | Amberley | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 205 | 207 | 227 | 247 | 248
|  |  |  | Power Factor | 0.931 | 0.929 | 0.924 | 0.92 | 0.919
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | 50 POE Load (A) | 366 | 362 | 400 | 438 | 441
Abermain Bulk | 420-1 | Mt Crosby West | Mt Crosby | NCC Rating (A) | 349 | 349 | 349 | 349 | 349 | HighSec | 0 | NA
|  |  |  | 10 POE Load (A) | 11 | 11 | 17 | 18 | 18
|  |  |  | Power Factor | 0.769 | 0.771 | 0.979 | 0.978 | 0.979
|  |  |  | ECC Rating (A) | 349 | 349 | 349 | 349 | 349
|  |  |  | 50 POE Load (A) | 242 | 242 | 242 | 238 | 238
Abermain Bulk | 436-1 | Amberley | 436 Tee1 | NCC Rating (A) | 351 | 351 | 351 | 351 | 351 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 66 | 64 | 62 | 62 | 64
|  |  |  | Power Factor | 0.944 | 0.932 | 0.923 | 0.914 | 0.912
|  |  |  | ECC Rating (A) | 351 | 351 | 351 | 351 | 351
|  |  |  | 50 POE Load (A) | 224 | 228 | 236 | 245 | 250
Abermain Bulk | 436-2 | 436 Tee1 | Ebeneezer | NCC Rating (A) | 403 | 403 | 403 | 403 | 403 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 403 | 403 | 403 | 403 | 403
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Abermain Bulk | 436-4 | 436 Tee1 | Rosewood | NCC Rating (A) | 208 | 208 | 208 | 208 | 208 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 67 | 64 | 63 | 62 | 64
|  |  |  | Power Factor | 0.942 | 0.93 | 0.92 | 0.913 | 0.912
|  |  |  | ECC Rating (A) | 208 | 208 | 208 | 208 | 208
|  |  |  | 50 POE Load (A) | 224 | 228 | 236 | 245 | 250
Abermain Bulk | 445-1 | Abermain BS | Moggill | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 234 | 233 | 232 | 231 | 228
|  |  |  | Power Factor | 0.968 | 0.969 | 0.969 | 0.969 | 0.969
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | 50 POE Load (A) | 339 | 333 | 331 | 330 | 326
Abermain Bulk | 475-1 | Karrabin | Amberley | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 203 | 205 | 224 | 244 | 246
|  |  |  | Power Factor | 0.932 | 0.93 | 0.926 | 0.921 | 0.921
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | 50 POE Load (A) | 366 | 362 | 400 | 438 | 441
Abermain Bulk | 673-1 | Moggill | Kenmore | NCC Rating (A) | 636 | 636 | 636 | 636 | 636 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 5 | 5 | 5 | 5 | 5
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 636 | 636 | 636 | 636 | 636
|  |  |  | 50 POE Load (A) | 5 | 5 | 5 | 5 | 5
Algester Bulk | 3400-1 | Algester BS | Calamvale | NCC Rating (A) | 694 | 694 | 694 | 694 | 694 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 368 | 366 | 366 | 364 | 360
|  |  |  | Power Factor | 0.983 | 0.983 | 0.983 | 0.984 | 0.984
|  |  |  | ECC Rating (A) | 765 | 765 | 765 | 765 | 765
|  |  |  | 50 POE Load (A) | 638 | 635 | 633 | 630 | 624
Algester Bulk | 3402-1 | Algester BS | Acacia Ridge | NCC Rating (A) | 687 | 687 | 687 | 687 | 687 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 150 | 149 | 148 | 148 | 148
|  |  |  | Power Factor | 0.992 | 0.992 | 0.993 | 0.993 | 0.993
|  |  |  | ECC Rating (A) | 739 | 739 | 739 | 739 | 739
|  |  |  | 50 POE Load (A) | 286 | 283 | 282 | 282 | 280
Algester Bulk | 3403-1 | Algester BS | Acacia Ridge | NCC Rating (A) | 687 | 687 | 687 | 687 | 687 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 151 | 149 | 149 | 148 | 148
|  |  |  | Power Factor | 0.992 | 0.992 | 0.993 | 0.993 | 0.993
|  |  |  | ECC Rating (A) | 739 | 739 | 739 | 739 | 739
|  |  |  | 50 POE Load (A) | 286 | 283 | 282 | 282 | 280
Algester Bulk | 3405-1 | Algester BS | Calamvale | NCC Rating (A) | 694 | 694 | 694 | 694 | 694 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 368 | 367 | 366 | 364 | 361
|  |  |  | Power Factor | 0.983 | 0.983 | 0.983 | 0.984 | 0.984
|  |  |  | ECC Rating (A) | 765 | 765 | 765 | 765 | 765
|  |  |  | 50 POE Load (A) | 638 | 635 | 633 | 630 | 624
Archerfield Bulk | 597-1 | Rocklea | Salisbury | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 182 | 175 | 170 | 167 | 164
|  |  |  | Power Factor | 0.966 | 0.967 | 0.968 | 0.968 | 0.968
|  |  |  | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
|  |  |  | 50 POE Load (A) | 165 | 160 | 156 | 154 | 152
Archerfield Bulk | 635-1 | Archerfield BS | Coopers Plains | NCC Rating (A) | 523 | 523 | 523 | 523 | 523 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 373 | 302 | 288 | 279 | 274
|  |  |  | Power Factor | 0.99 | 0.997 | 0.986 | 0.987 | 0.988
|  |  |  | ECC Rating (A) | 523 | 523 | 523 | 523 | 523
|  |  |  | 50 POE Load (A) | 346 | 281 | 268 | 262 | 257
Archerfield Bulk | 650-1 | Archerfield BS | Rocklea | NCC Rating (A) | 650 | 650 | 650 | 650 | 650 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 238 | 233 | 228 | 237 | 234
|  |  |  | Power Factor | 0.983 | 0.984 | 0.985 | 0.961 | 0.961
|  |  |  | ECC Rating (A) | 740 | 740 | 740 | 740 | 740
|  |  |  | 50 POE Load (A) | 462 | 455 | 447 | 443 | 438
Archerfield Bulk | 651-1 | Archerfield BS | Rocklea | NCC Rating (A) | 650 | 650 | 650 | 650 | 650 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 236 | 230 | 226 | 234 | 232
|  |  |  | Power Factor | 0.983 | 0.984 | 0.985 | 0.961 | 0.961
|  |  |  | ECC Rating (A) | 740 | 740 | 740 | 740 | 740
|  |  |  | 50 POE Load (A) | 462 | 455 | 447 | 443 | 438
Ashgrove West Bulk | 432-1 | Ashgrove West BS | Toowong | NCC Rating (A) | 476 | 476 | 476 | 476 | 476 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 14 | 14 | 14 | 14 | 14
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 476 | 476 | 476 | 476 | 476
|  |  |  | 50 POE Load (A) | 14 | 14 | 14 | 14 | 14
Ashgrove West Bulk | 552-1 | Ashgrove West BS | Ashgrove | NCC Rating (A) | 598 | 598 | 598 | 598 | 598 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 184 | 184 | 183 | 183 | 181
|  |  |  | Power Factor | 0.999 | 0.999 | 0.999 | 0.999 | 1
|  |  |  | ECC Rating (A) | 598 | 598 | 598 | 598 | 598
|  |  |  | 50 POE Load (A) | 240 | 239 | 239 | 238 | 236
Ashgrove West Bulk | 565-1 | Ashgrove West BS | Ashgrove | NCC Rating (A) | 851 | 851 | 851 | 851 | 851 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 127 | 127 | 126 | 126 | 125
|  |  |  | Power Factor | 0.984 | 0.984 | 0.984 | 0.984 | 0.984
|  |  |  | ECC Rating (A) | 851 | 851 | 851 | 851 | 851
|  |  |  | 50 POE Load (A) | 168 | 167 | 167 | 166 | 165
Ashgrove West Bulk | 570-1 | Ashgrove West BS | Ashgrove | NCC Rating (A) | 598 | 598 | 598 | 598 | 598 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 180 | 179 | 179 | 178 | 177
|  |  |  | Power Factor | 0.999 | 0.999 | 0.999 | 0.999 | 0.999
|  |  |  | ECC Rating (A) | 672 | 672 | 672 | 672 | 672
|  |  |  | 50 POE Load (A) | 238 | 237 | 237 | 236 | 234
Ashgrove West Bulk | 585-1 | Ashgrove West BS | The Gap | NCC Rating (A) | 622 | 622 | 622 | 622 | 622 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 174 | 173 | 173 | 172 | 170
|  |  |  | Power Factor | 0.979 | 0.979 | 0.979 | 0.979 | 0.98
|  |  |  | ECC Rating (A) | 622 | 622 | 622 | 622 | 622
|  |  |  | 50 POE Load (A) | 144 | 143 | 143 | 142 | 141
Ashgrove West Bulk | 586-1 | Ashgrove West BS | The Gap | NCC Rating (A) | 622 | 622 | 622 | 622 | 622 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 196 | 195 | 194 | 193 | 192
|  |  |  | Power Factor | 0.981 | 0.981 | 0.981 | 0.981 | 0.981
|  |  |  | ECC Rating (A) | 622 | 622 | 622 | 622 | 622
|  |  |  | 50 POE Load (A) | 162 | 161 | 161 | 160 | 159
Ashgrove West Bulk | 590-1 | Ashgrove BS | Toowong | NCC Rating (A) | 705 | 705 | 705 | 705 | 705 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 341 | 341 | 342 | 342 | 341
|  |  |  | Power Factor | 0.977 | 0.978 | 0.977 | 0.977 | 0.977
|  |  |  | ECC Rating (A) | 705 | 705 | 705 | 705 | 705
|  |  |  | 50 POE Load (A) | 614 | 613 | 615 | 615 | 614
Ashgrove West Bulk | 591-1 | Ashgrove BS | Toowong | NCC Rating (A) | 705 | 705 | 705 | 705 | 705 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 341 | 341 | 342 | 342 | 341
|  |  |  | Power Factor | 0.977 | 0.977 | 0.977 | 0.977 | 0.977
|  |  |  | ECC Rating (A) | 705 | 705 | 705 | 705 | 705
|  |  |  | 50 POE Load (A) | 614 | 613 | 615 | 615 | 614
Ashgrove West Bulk | 675-1 | Ashgrove | Newmarket | NCC Rating (A) | 492 | 492 | 492 | 492 | 492 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 17 | 17 | 17 | 17 | 17
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 492 | 492 | 492 | 492 | 492
|  |  |  | 50 POE Load (A) | 17 | 17 | 17 | 17 | 17
Ashgrove West Bulk | 676-1 | Ashgrove | Newmarket | NCC Rating (A) | 492 | 492 | 492 | 492 | 492 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 17 | 17 | 17 | 17 | 17
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 492 | 492 | 492 | 492 | 492
|  |  |  | 50 POE Load (A) | 17 | 17 | 17 | 17 | 17
Beaudesert Bulk | 314-1 | Beaudesert BS | Jimboomba | NCC Rating (A) | 512 | 512 | 512 | 512 | 512 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 512 | 512 | 512 | 512 | 512
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Beaudesert Bulk | 404-1 | Beaudesert | Innisplain | NCC Rating (A) | 155 | 155 | 155 | 155 | 155 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 114 | 116 | 118 | 120 | 122
|  |  |  | Power Factor | 0.981 | 0.981 | 0.98 | 0.98 | 0.98
|  |  |  | ECC Rating (A) | 155 | 155 | 155 | 155 | 155
|  |  |  | 50 POE Load (A) | 98 | 99 | 101 | 103 | 104
Beaudesert Bulk | 466-1 | Beaudesert BS | Bromelton | NCC Rating (A) | 403 | 403 | 403 | 403 | 403 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 99 | 114 | 129 | 143 | 151
|  |  |  | Power Factor | 0.991 | 0.986 | 0.982 | 0.99 | 0.988
|  |  |  | ECC Rating (A) | 403 | 403 | 403 | 403 | 403
|  |  |  | 50 POE Load (A) | 154 | 179 | 205 | 227 | 240
Beaudesert Bulk | 467-1 | Beaudesert BS | Bromelton | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 66 | 76 | 86 | 95 | 101
|  |  |  | Power Factor | 1 | 0.999 | 0.998 | 1 | 1
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | 50 POE Load (A) | 156 | 181 | 207 | 230 | 243
Beaudesert Bulk | 468-1 | Beaudesert BS | Beaudesert | NCC Rating (A) | 579 | 579 | 579 | 579 | 579 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 337 | 342 | 347 | 352 | 357
|  |  |  | Power Factor | 0.91 | 0.909 | 0.908 | 0.906 | 0.905
|  |  |  | ECC Rating (A) | 579 | 579 | 579 | 579 | 579
|  |  |  | 50 POE Load (A) | 355 | 358 | 363 | 367 | 371
Beaudesert Bulk | 469-1 | Beaudesert BS | 469 Tee1 | NCC Rating (A) | 537 | 537 | 537 | 537 | 537 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 348 | 352 | 358 | 363 | 368
|  |  |  | Power Factor | 0.95 | 0.949 | 0.948 | 0.947 | 0.946
|  |  |  | ECC Rating (A) | 537 | 537 | 537 | 537 | 537
|  |  |  | 50 POE Load (A) | 577 | 583 | 592 | 601 | 609
Beaudesert Bulk | 469-2 | 469 Tee1 | Beaudesert | NCC Rating (A) | 579 | 579 | 579 | 579 | 579 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 203 | 207 | 212 | 218 | 222
|  |  |  | Power Factor | 0.952 | 0.951 | 0.95 | 0.948 | 0.947
|  |  |  | ECC Rating (A) | 579 | 579 | 579 | 579 | 579
|  |  |  | 50 POE Load (A) | 444 | 450 | 458 | 467 | 475
Beaudesert Bulk | 469-3 | 469 Tee1 | Mt Tamborine Bus 2 | NCC Rating (A) | 512 | 512 | 512 | 512 | 512 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 145 | 145 | 146 | 146 | 146
|  |  |  | Power Factor | 0.958 | 0.958 | 0.958 | 0.958 | 0.958
|  |  |  | ECC Rating (A) | 512 | 512 | 512 | 512 | 512
|  |  |  | 50 POE Load (A) | 284 | 284 | 285 | 285 | 284
Beenleigh Bulk | 3590-1 | Beenleigh BS | Loganholme | NCC Rating (A) | 766 | 766 | 766 | 766 | 766 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 431 | 428 | 427 | 425 | 423
|  |  |  | Power Factor | 0.987 | 0.987 | 0.987 | 0.987 | 0.987
|  |  |  | ECC Rating (A) | 766 | 766 | 766 | 766 | 766
|  |  |  | 50 POE Load (A) | 651 | 647 | 673 | 670 | 666
Beenleigh Bulk | 3591-1 | Cornubia | Loganholme | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 66 | 65 | 65 | 65 | 65
|  |  |  | Power Factor | 0.999 | 0.999 | 0.999 | 0.999 | 0.999
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 447 | 444 | 471 | 469 | 466
Beenleigh Bulk | 3600-1 | Yatala | Stapylton | NCC Rating (A) | 713 | 713 | 713 | 713 | 713 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 101 | 100 | 100 | 99 | 99
|  |  |  | Power Factor | 0.969 | 0.97 | 0.97 | 0.97 | 0.97
|  |  |  | ECC Rating (A) | 713 | 713 | 713 | 713 | 713
|  |  |  | 50 POE Load (A) | 194 | 192 | 191 | 191 | 190
Beenleigh Bulk | 3601-1 | Yatala | Stapylton | NCC Rating (A) | 713 | 713 | 713 | 713 | 713 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 97 | 96 | 95 | 95 | 95
|  |  |  | Power Factor | 0.967 | 0.967 | 0.967 | 0.967 | 0.967
|  |  |  | ECC Rating (A) | 713 | 713 | 713 | 713 | 713
|  |  |  | 50 POE Load (A) | 194 | 193 | 192 | 191 | 190
Beenleigh Bulk | 3620-1 | Beenleigh BS | Logan Village | NCC Rating (A) | 490 | 490 | 490 | 490 | 490 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 490 | 490 | 490 | 490 | 490
|  |  |  | 50 POE Load (A) | 367 | 338 | 348 | 355 | 362
Beenleigh Bulk | 402-1 | Beenleigh BS | 402 Tee1 | NCC Rating (A) | 579 | 579 | 579 | 579 | 579 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 245 | 245 | 246 | 247 | 247
|  |  |  | Power Factor | 0.952 | 0.952 | 0.952 | 0.952 | 0.952
|  |  |  | ECC Rating (A) | 579 | 579 | 579 | 579 | 579
|  |  |  | 50 POE Load (A) | 382 | 382 | 386 | 386 | 386
Beenleigh Bulk | 402-2 | 402 Tee1 | Tamborine Village | NCC Rating (A) | 439 | 439 | 439 | 439 | 439 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 93 | 94 | 94 | 95 | 95
|  |  |  | Power Factor | 0.987 | 0.987 | 0.987 | 0.987 | 0.987
|  |  |  | ECC Rating (A) | 439 | 439 | 439 | 439 | 439
|  |  |  | 50 POE Load (A) | 84 | 84 | 85 | 86 | 86
Beenleigh Bulk | 402-3 | 402 Tee1 | Mt Tamborine Bus 1 | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 152 | 152 | 152 | 152 | 152
|  |  |  | Power Factor | 0.967 | 0.967 | 0.967 | 0.967 | 0.967
|  |  |  | ECC Rating (A) | 812 | 812 | 812 | 812 | 812
|  |  |  | 50 POE Load (A) | 299 | 299 | 301 | 301 | 301
Beenleigh Bulk | 405-1 | Beenleigh BS | 405 Tee1 | NCC Rating (A) | 807 | 807 | 807 | 807 | 807 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 308 | 306 | 306 | 304 | 302
|  |  |  | Power Factor | 0.98 | 0.98 | 0.98 | 0.981 | 0.981
|  |  |  | ECC Rating (A) | 807 | 807 | 807 | 807 | 807
|  |  |  | 50 POE Load (A) | 665 | 661 | 693 | 690 | 685
Beenleigh Bulk | 405-3 | 405 Tee1 | Cornubia | NCC Rating (A) | 774 | 774 | 774 | 774 | 774 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 308 | 307 | 306 | 305 | 303
|  |  |  | Power Factor | 0.984 | 0.985 | 0.985 | 0.985 | 0.985
|  |  |  | ECC Rating (A) | 774 | 774 | 774 | 774 | 774
|  |  |  | 50 POE Load (A) | 665 | 661 | 693 | 690 | 685
Beenleigh Bulk | 419-1 | Loganholme | Tanah Merah | NCC Rating (A) | 712 | 712 | 712 | 712 | 712 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 712 | 712 | 712 | 712 | 712
|  |  |  | 50 POE Load (A) | 294 | 292 | 294 | 292 | 289
Beenleigh Bulk | 426-1 | Beenleigh BS | Yatala | NCC Rating (A) | 740 | 740 | 740 | 740 | 740 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 101 | 100 | 99 | 99 | 98
|  |  |  | Power Factor | 0.545 | 0.545 | 0.545 | 0.545 | 0.545
|  |  |  | ECC Rating (A) | 740 | 740 | 740 | 740 | 740
|  |  |  | 50 POE Load (A) | 194 | 192 | 191 | 190 | 189
Beenleigh Bulk | 427-1 | Beenleigh BS | Yatala | NCC Rating (A) | 740 | 740 | 740 | 740 | 740 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 96 | 95 | 95 | 95 | 94
|  |  |  | Power Factor | 0.969 | 0.969 | 0.97 | 0.97 | 0.97
|  |  |  | ECC Rating (A) | 740 | 740 | 740 | 740 | 740
|  |  |  | 50 POE Load (A) | 194 | 192 | 191 | 191 | 189
Beenleigh Bulk | 453-1 | Beenleigh BS | Beenleigh Nth | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 766 | 770 | 777 | 781 | 784
|  |  |  | Power Factor | 0.966 | 0.966 | 0.966 | 0.965 | 0.965
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 662 | 666 | 669 | 673 | 676
Beenleigh Bulk | 496-1 | Beenleigh Nth | Bethania | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 434 | 435 | 438 | 439 | 440
|  |  |  | Power Factor | 0.976 | 0.976 | 0.976 | 0.976 | 0.976
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | 50 POE Load (A) | 355 | 356 | 357 | 358 | 359
Beerwah Bulk | 324-1 | Woodford | Kilcoy | NCC Rating (A) | 348 | 348 | 348 | 348 | 348 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 259 | 247 | 250 | 252 | 251
|  |  |  | Power Factor | 0.963 | 0.969 | 0.968 | 0.967 | 0.972
|  |  |  | ECC Rating (A) | 348 | 348 | 348 | 348 | 348
|  |  |  | 50 POE Load (A) | 232 | 230 | 233 | 235 | 235
Beerwah Bulk | 428-1 | Beerwah BS | Woodford | NCC Rating (A) | 351 | 351 | 351 | 351 | 351 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 292 | 277 | 278 | 282 | 282
|  |  |  | Power Factor | 0.935 | 0.943 | 0.942 | 0.941 | 0.946
|  |  |  | ECC Rating (A) | 351 | 351 | 351 | 351 | 351
|  |  |  | 50 POE Load (A) | 258 | 252 | 256 | 257 | 257
Beerwah Bulk | 447-1 | Somerset Dam | Kilcoy | NCC Rating (A) | 155 | 155 | 155 | 155 | 155 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 155 | 155 | 155 | 155 | 155
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Beerwah Bulk | 477-1 | 477 Tee1 | Maleny | NCC Rating (A) | 155 | 155 | 155 | 155 | 155 | Rural | 170 | 2
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 155 | 155 | 155 | 155 | 155
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Beerwah Bulk | 477-2 | 477 Tee1 | Woodford | NCC Rating (A) | 300 | 300 | 300 | 300 | 300 | Rural | 170 | 6
|  |  |  | 10 POE Load (A) | 206 | 206 | 206 | 206 | 205
|  |  |  | Power Factor | 0.983 | 0.983 | 0.983 | 0.983 | 0.983
|  |  |  | ECC Rating (A) | 300 | 300 | 300 | 300 | 300
|  |  |  | 50 POE Load (A) | 178 | 178 | 178 | 178 | 177
Beerwah Bulk | 477-3 | Beerwah | 477 Tee1 | NCC Rating (A) | 711 | 711 | 711 | 711 | 711 | Rural | 170 | 6
|  |  |  | 10 POE Load (A) | 206 | 206 | 206 | 205 | 204
|  |  |  | Power Factor | 0.974 | 0.974 | 0.974 | 0.974 | 0.975
|  |  |  | ECC Rating (A) | 711 | 711 | 711 | 711 | 711
|  |  |  | 50 POE Load (A) | 178 | 178 | 178 | 178 | 177
Beerwah Bulk | 608-1 | Beerwah BS | Landsborough | NCC Rating (A) | 412 | 412 | 412 | 412 | 412 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 264 | 286 | 296 | 306 | 315
|  |  |  | Power Factor | 0.972 | 0.968 | 0.968 | 0.966 | 0.965
|  |  |  | ECC Rating (A) | 412 | 412 | 412 | 412 | 412
|  |  |  | 50 POE Load (A) | 233 | 253 | 262 | 271 | 278
Belmont Bulk | 527-1 | Mt Gravatt | Upper Mt Gravatt | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 108 | 107 | 108 | 108 | 108
|  |  |  | Power Factor | 0.983 | 0.982 | 0.982 | 0.872 | 0.872
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | 50 POE Load (A) | 193 | 193 | 193 | 193 | 194
Belmont Bulk | 631-1 | Belmont BS | Mt Gravatt | NCC Rating (A) | 420 | 420 | 420 | 420 | 420 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 281 | 280 | 281 | 281 | 281
|  |  |  | Power Factor | 0.997 | 0.997 | 0.997 | 0.997 | 0.0997
|  |  |  | ECC Rating (A) | 465 | 465 | 465 | 465 | 465
|  |  |  | 50 POE Load (A) | 443 | 443 | 444 | 444 | 444
Belmont Bulk | 632-1 | Belmont BS | Mt Gravatt | NCC Rating (A) | 420 | 420 | 420 | 420 | 420 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 279 | 279 | 279 | 279 | 279
|  |  |  | Power Factor | 0.997 | 0.997 | 0.997 | 0.997 | 0.997
|  |  |  | ECC Rating (A) | 452 | 452 | 452 | 452 | 452
|  |  |  | 50 POE Load (A) | 443 | 442 | 443 | 443 | 443
Belmont Bulk | 647-1 | Belmont BS | Eight Mile Plains Bus 2 | NCC Rating (A) | 479 | 479 | 479 | 479 | 479 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 276 | 274 | 273 | 272 | 270
|  |  |  | Power Factor | 0.92 | 0.92 | 0.92 | 0.921 | 0.921
|  |  |  | ECC Rating (A) | 479 | 479 | 479 | 479 | 479
|  |  |  | 50 POE Load (A) | 513 | 510 | 508 | 504 | 502
Belmont Bulk | 660-1 | Belmont BS | Scrub Road | NCC Rating (A) | 676 | 676 | 676 | 676 | 676 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 282 | 281 | 280 | 279 | 276
|  |  |  | Power Factor | 0.994 | 0.995 | 0.995 | 0.995 | 0.995
|  |  |  | ECC Rating (A) | 751 | 751 | 751 | 751 | 751
|  |  |  | 50 POE Load (A) | 495 | 493 | 493 | 490 | 486
Belmont Bulk | 661-1 | Belmont BS | Scrub Road | NCC Rating (A) | 676 | 676 | 676 | 676 | 676 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 285 | 284 | 283 | 282 | 279
|  |  |  | Power Factor | 0.994 | 0.995 | 0.995 | 0.995 | 0.995
|  |  |  | ECC Rating (A) | 751 | 751 | 751 | 751 | 751
|  |  |  | 50 POE Load (A) | 495 | 493 | 493 | 490 | 486
Belmont Bulk | 662-1 | Belmont BS | Upper Mt Gravatt | NCC Rating (A) | 656 | 656 | 656 | 656 | 656 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 221 | 221 | 221 | 270 | 268
|  |  |  | Power Factor | 0.978 | 0.978 | 0.978 | 0.99 | 0.99
|  |  |  | ECC Rating (A) | 737 | 737 | 737 | 737 | 737
|  |  |  | 50 POE Load (A) | 303 | 303 | 303 | 492 | 489
Belmont Bulk | 663-1 | Belmont BS | Upper Mt Gravatt | NCC Rating (A) | 656 | 656 | 656 | 656 | 656 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 224 | 224 | 224 | 273 | 272
|  |  |  | Power Factor | 0.978 | 0.978 | 0.978 | 0.99 | 0.991
|  |  |  | ECC Rating (A) | 737 | 737 | 737 | 737 | 737
|  |  |  | 50 POE Load (A) | 305 | 305 | 305 | 492 | 489
Belmont Bulk | 692-1 | Belmont BS | Holland Pk East | NCC Rating (A) | 421 | 421 | 421 | 421 | 421 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 186 | 186 | 186 | 186 | 185
|  |  |  | Power Factor | 0.962 | 0.962 | 0.962 | 0.962 | 0.962
|  |  |  | ECC Rating (A) | 465 | 465 | 465 | 465 | 465
|  |  |  | 50 POE Load (A) | 333 | 333 | 333 | 332 | 331
Belmont Bulk | 693-1 | Belmont BS | Holland Pk East | NCC Rating (A) | 421 | 421 | 421 | 421 | 421 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 188 | 187 | 188 | 187 | 187
|  |  |  | Power Factor | 0.962 | 0.962 | 0.962 | 0.962 | 0.962
|  |  |  | ECC Rating (A) | 465 | 465 | 465 | 465 | 465
|  |  |  | 50 POE Load (A) | 333 | 333 | 333 | 332 | 331
Brendale Bulk | 303-1 | Brendale BS | Albany Ck | NCC Rating (A) | 725 | 725 | 725 | 725 | 725 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 262 | 262 | 261 | 260 | 258
|  |  |  | Power Factor | 0.975 | 0.975 | 0.975 | 0.975 | 0.975
|  |  |  | ECC Rating (A) | 824 | 824 | 824 | 824 | 824
|  |  |  | 50 POE Load (A) | 458 | 457 | 456 | 453 | 449
Brendale Bulk | 309-1 | Brendale BS | 309 Tee1 | NCC Rating (A) | 627 | 627 | 627 | 627 | 627 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 313 | 313 | 312 | 310 | 308
|  |  |  | Power Factor | 0.962 | 0.962 | 0.962 | 0.962 | 0.962
|  |  |  | ECC Rating (A) | 627 | 627 | 627 | 627 | 627
|  |  |  | 50 POE Load (A) | 566 | 564 | 563 | 561 | 557
Brendale Bulk | 309-2 | 309 Tee1 | Samford | NCC Rating (A) | 711 | 711 | 711 | 711 | 711 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 87 | 87 | 87 | 86 | 85
|  |  |  | Power Factor | 0.988 | 0.988 | 0.988 | 0.988 | 0.988
|  |  |  | ECC Rating (A) | 711 | 711 | 711 | 711 | 711
|  |  |  | 50 POE Load (A) | 265 | 264 | 263 | 262 | 259
Brendale Bulk | 309-3 | 309 Tee1 | Arana Hills | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 227 | 227 | 227 | 225 | 224
|  |  |  | Power Factor | 0.964 | 0.964 | 0.964 | 0.964 | 0.964
|  |  |  | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
|  |  |  | 50 POE Load (A) | 610 | 609 | 608 | 606 | 602
Brendale Bulk | 310-1 | Brendale BS | 310 Tee1 | NCC Rating (A) | 627 | 627 | 627 | 627 | 627 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 463 | 462 | 462 | 459 | 456
|  |  |  | Power Factor | 0.961 | 0.961 | 0.961 | 0.961 | 0.961
|  |  |  | ECC Rating (A) | 627 | 627 | 627 | 627 | 627
|  |  |  | 50 POE Load (A) | 587 | 585 | 585 | 582 | 579
Brendale Bulk | 310-2 | 310 Tee1 | Arana Hills | NCC Rating (A) | 792 | 792 | 792 | 792 | 792 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 464 | 462 | 462 | 460 | 457
|  |  |  | Power Factor | 0.973 | 0.973 | 0.973 | 0.973 | 0.973
|  |  |  | ECC Rating (A) | 792 | 792 | 792 | 792 | 792
|  |  |  | 50 POE Load (A) | 587 | 586 | 585 | 582 | 579
Brendale Bulk | 310-3 | 310 Tee1 | 569 Tee1 | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Brendale Bulk | 333-1 | Brendale BS | Lawnton | NCC Rating (A) | 732 | 732 | 732 | 732 | 732 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 344 | 364 | 366 | 367 | 368
|  |  |  | Power Factor | 0.975 | 0.972 | 0.972 | 0.972 | 0.972
|  |  |  | ECC Rating (A) | 732 | 732 | 732 | 732 | 732
|  |  |  | 50 POE Load (A) | 511 | 546 | 549 | 550 | 551
Brendale Bulk | 3340-1 | Brendale Bs | Strathpine | NCC Rating (A) | 512 | 512 | 512 | 512 | 512 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 142 | 143 | 138 | 136 | 135
|  |  |  | Power Factor | 0.976 | 0.975 | 0.977 | 0.978 | 0.979
|  |  |  | ECC Rating (A) | 512 | 512 | 512 | 512 | 512
|  |  |  | 50 POE Load (A) | 211 | 213 | 207 | 203 | 201
Brendale Bulk | 334-1 | Lawnton | 334 Tee1 | NCC Rating (A) | 578 | 578 | 578 | 578 | 578 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 39 | 45 | 46 | 46 | 47
|  |  |  | Power Factor | 0.815 | 0.903 | 0.91 | 0.916 | 0.924
|  |  |  | ECC Rating (A) | 578 | 578 | 578 | 578 | 578
|  |  |  | 50 POE Load (A) | 214 | 214 | 214 | 213 | 212
Brendale Bulk | 334-2 | 334 Tee1 | Whiteside | NCC Rating (A) | 750 | 750 | 750 | 750 | 750 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 70 | 69 | 69 | 68 | 68
|  |  |  | Power Factor | 0.919 | 0.919 | 0.919 | 0.919 | 0.919
|  |  |  | ECC Rating (A) | 750 | 750 | 750 | 750 | 750
|  |  |  | 50 POE Load (A) | 138 | 138 | 138 | 137 | 136
Brendale Bulk | 334-3 | 334 Tee1 | Nth Pine Dam | NCC Rating (A) | 578 | 578 | 578 | 578 | 578 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 90 | 98 | 99 | 99 | 100
|  |  |  | Power Factor | 1 | 0.999 | 0.999 | 0.999 | 0.999
|  |  |  | ECC Rating (A) | 578 | 578 | 578 | 578 | 578
|  |  |  | 50 POE Load (A) | 161 | 174 | 175 | 176 | 177
Brendale Bulk | 335-1 | Brendale BS | 335 Tee1 | NCC Rating (A) | 485 | 485 | 485 | 485 | 485 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 224 | 233 | 234 | 234 | 234
|  |  |  | Power Factor | 0.961 | 0.959 | 0.959 | 0.959 | 0.959
|  |  |  | ECC Rating (A) | 485 | 485 | 485 | 485 | 485
|  |  |  | 50 POE Load (A) | 287 | 302 | 304 | 304 | 304
Brendale Bulk | 335-2 | 335 Tee | Whiteside | NCC Rating (A) | 750 | 750 | 750 | 750 | 750 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 85 | 85 | 85 | 85 | 84
|  |  |  | Power Factor | 0.942 | 0.942 | 0.942 | 0.942 | 0.942
|  |  |  | ECC Rating (A) | 750 | 750 | 750 | 750 | 750
|  |  |  | 50 POE Load (A) | 136 | 136 | 136 | 135 | 134
Brendale Bulk | 335-3 | 335 Tee | Nth Pine Dam | NCC Rating (A) | 485 | 485 | 485 | 485 | 485 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 141 | 149 | 150 | 150 | 150
|  |  |  | Power Factor | 0.979 | 0.976 | 0.976 | 0.976 | 0.976
|  |  |  | ECC Rating (A) | 485 | 485 | 485 | 485 | 485
|  |  |  | 50 POE Load (A) | 208 | 222 | 224 | 224 | 225
Brendale Bulk | 336-1 | Brendale BS | Strathpine | NCC Rating (A) | 455 | 455 | 455 | 455 | 455 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 162 | 163 | 158 | 156 | 154
|  |  |  | Power Factor | 0.992 | 0.991 | 0.993 | 0.993 | 0.994
|  |  |  | ECC Rating (A) | 455 | 455 | 455 | 455 | 455
|  |  |  | 50 POE Load (A) | 224 | 227 | 220 | 216 | 214
Brendale Bulk | 3364-1 | Brendale BS | Albany Ck | NCC Rating (A) | 725 | 725 | 725 | 725 | 725 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 269 | 268 | 268 | 266 | 264
|  |  |  | Power Factor | 0.975 | 0.975 | 0.975 | 0.975 | 0.975
|  |  |  | ECC Rating (A) | 824 | 824 | 824 | 824 | 824
|  |  |  | 50 POE Load (A) | 457 | 456 | 455 | 452 | 448
Brendale Bulk | 337-1 | Brendale BS | Strathpine | NCC Rating (A) | 490 | 490 | 490 | 490 | 490 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 134 | 135 | 131 | 129 | 127
|  |  |  | Power Factor | 0.987 | 0.987 | 0.988 | 0.989 | 0.99
|  |  |  | ECC Rating (A) | 490 | 490 | 490 | 490 | 490
|  |  |  | 50 POE Load (A) | 199 | 201 | 195 | 192 | 190
Brendale Bulk | 342-1 | Brendale BS | Bald Hills Bus 2 | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 189 | 188 | 188 | 187 | 185
|  |  |  | Power Factor | 0.964 | 0.965 | 0.965 | 0.965 | 0.965
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | 50 POE Load (A) | 294 | 293 | 292 | 291 | 289
Brendale Bulk | 349-1 | Brendale BS | Lawnton | NCC Rating (A) | 717 | 717 | 717 | 717 | 717 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 358 | 379 | 381 | 382 | 383
|  |  |  | Power Factor | 0.973 | 0.97 | 0.97 | 0.97 | 0.97
|  |  |  | ECC Rating (A) | 717 | 717 | 717 | 717 | 717
|  |  |  | 50 POE Load (A) | 516 | 552 | 554 | 556 | 557
Brendale Bulk | 464-1 | Brendale BS | Samford | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 224 | 223 | 223 | 222 | 220
|  |  |  | Power Factor | 0.962 | 0.962 | 0.963 | 0.963 | 0.963
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | 50 POE Load (A) | 307 | 306 | 306 | 305 | 302
Browns Plains Bulk | 406A-1 | Bethania | Kingston | NCC Rating (A) | 529 | 529 | 529 | 529 | 529 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 529 | 529 | 529 | 529 | 529
|  |  |  | 50 POE Load (A) | 357 | 360 | 362 | 363 | 363
Browns Plains Bulk | 406B-1 | Crestmead | Kingston | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | 50 POE Load (A) | 357 | 360 | 362 | 363 | 363
Browns Plains Bulk | 478-1 | Browns Plains BS | Nth Maclean | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 561 | 578 | 580 | 592 | 606
Browns Plains Bulk | 481-1 | Browns Plains BS | Cresmead | NCC Rating (A) | 705 | 705 | 705 | 705 | 705 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 252 | 287 | 287 | 287 | 285
|  |  |  | Power Factor | 0.97 | 0.966 | 0.966 | 0.966 | 0.966
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 464 | 535 | 535 | 534 | 531
Browns Plains Bulk | 482-1 | Browns Plains BS | Cresmead | NCC Rating (A) | 704 | 704 | 704 | 704 | 704 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 254 | 289 | 289 | 288 | 287
|  |  |  | Power Factor | 0.97 | 0.965 | 0.965 | 0.965 | 0.966
|  |  |  | ECC Rating (A) | 704 | 704 | 704 | 704 | 704
|  |  |  | 50 POE Load (A) | 464 | 535 | 535 | 534 | 531
Browns Plains Bulk | 542-1 | Browns Plains BS | Heathwood | NCC Rating (A) | 704 | 704 | 704 | 704 | 704 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 572 | 571 | 573 | 572 | 569
|  |  |  | Power Factor | 0.956 | 0.956 | 0.956 | 0.956 | 0.956
|  |  |  | ECC Rating (A) | 704 | 704 | 704 | 704 | 704
|  |  |  | 50 POE Load (A) | 527 | 526 | 527 | 527 | 524
Burleigh Heads Bulk | 3751-1 | Burleigh Hds BS | Currumbin | NCC Rating (A) | 606 | 606 | 606 | 606 | 606 | Urban | 321 | NA
|  |  |  | 10 POE Load (A) | 606 | 608 | 612 | 614 | 614
|  |  |  | Power Factor | 0.955 | 0.955 | 0.954 | 0.953 | 0.953
|  |  |  | ECC Rating (A) | 695 | 695 | 695 | 695 | 695
|  |  |  | 50 POE Load (A) | 934 | 937 | 942 | 946 | 946
Burleigh Heads Bulk | 3755-1 | Burleigh Hds BS | Currumbin | NCC Rating (A) | 606 | 606 | 606 | 606 | 606 | Urban | 321 | NA
|  |  |  | 10 POE Load (A) | 606 | 607 | 611 | 614 | 614
|  |  |  | Power Factor | 0.955 | 0.955 | 0.954 | 0.953 | 0.953
|  |  |  | ECC Rating (A) | 695 | 695 | 695 | 695 | 695
|  |  |  | 50 POE Load (A) | 934 | 937 | 942 | 945 | 945
Burleigh Heads Bulk | 3756-1 | Burleigh Hds BS | 3756 Tee1 | NCC Rating (A) | 715 | 715 | 715 | 715 | 715 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 193 | 193 | 194 | 195 | 195
|  |  |  | Power Factor | 0.969 | 0.969 | 0.969 | 0.967 | 0.967
|  |  |  | ECC Rating (A) | 715 | 715 | 715 | 715 | 715
|  |  |  | 50 POE Load (A) | 274 | 274 | 276 | 277 | 277
Burleigh Heads Bulk | 3756-2 | 3756 Tee1 | Palm Beach | NCC Rating (A) | 532 | 532 | 532 | 532 | 532 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 183 | 183 | 184 | 184 | 184
|  |  |  | Power Factor | 0.984 | 0.984 | 0.984 | 0.978 | 0.978
|  |  |  | ECC Rating (A) | 532 | 532 | 532 | 532 | 532
|  |  |  | 50 POE Load (A) | 347 | 348 | 350 | 350 | 350
Burleigh Heads Bulk | 3756-3 | 3756 Tee1 | 3756 Tee2 | NCC Rating (A) | 636 | 636 | 636 | 636 | 636 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 29 | 29 | 30 | 29 | 29
|  |  |  | Power Factor | 0.834 | 0.835 | 0.836 | 0.899 | 0.899
|  |  |  | ECC Rating (A) | 636 | 636 | 636 | 636 | 636
|  |  |  | 50 POE Load (A) | 240 | 241 | 243 | 244 | 244
Burleigh Heads Bulk | 3756-4 | 3756 Tee2 | Currumbin | NCC Rating (A) | 717 | 717 | 717 | 717 | 717 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 29 | 29 | 30 | 29 | 29
|  |  |  | Power Factor | 0.829 | 0.83 | 0.831 | 0.894 | 0.894
|  |  |  | ECC Rating (A) | 717 | 717 | 717 | 717 | 717
|  |  |  | 50 POE Load (A) | 240 | 241 | 243 | 244 | 244
Burleigh Heads Bulk | 393-1 | Currumbin | Kirra | NCC Rating (A) | 403 | 403 | 403 | 403 | 403 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 309 | 310 | 313 | 316 | 318
|  |  |  | Power Factor | 0.947 | 0.947 | 0.947 | 0.946 | 0.946
|  |  |  | ECC Rating (A) | 403 | 403 | 403 | 403 | 403
|  |  |  | 50 POE Load (A) | 284 | 285 | 288 | 290 | 292
Burleigh Heads Bulk | 395-1 | Burleigh Hds BS | Miami | NCC Rating (A) | 654 | 654 | 654 | 654 | 654 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 495 | 499 | 504 | 508 | 510
|  |  |  | Power Factor | 0.961 | 0.961 | 0.961 | 0.96 | 0.96
|  |  |  | ECC Rating (A) | 654 | 654 | 654 | 654 | 654
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Burleigh Heads Bulk | 396-1 | Burleigh Hds BS | Palm Beach | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 221 | 222 | 223 | 224 | 224
|  |  |  | Power Factor | 0.967 | 0.966 | 0.966 | 0.964 | 0.964
|  |  |  | ECC Rating (A) | 806 | 806 | 806 | 806 | 806
|  |  |  | 50 POE Load (A) | 349 | 350 | 352 | 352 | 352
Burleigh Heads Bulk | 397-1 | Burleigh Hds BS | 397 Tee1 | NCC Rating (A) | 602 | 602 | 602 | 602 | 602 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 602 | 602 | 602 | 602 | 602
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Burleigh Heads Bulk | 397-3 | 397 Tee1 | 397 Tee2 | NCC Rating (A) | 529 | 529 | 529 | 529 | 529 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 529 | 529 | 529 | 529 | 529
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Burleigh Heads Bulk | 397-4 | 397 Tee2 | 3700 Tee1 | NCC Rating (A) | 362 | 362 | 362 | 362 | 362 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 362 | 362 | 362 | 362 | 362
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Burleigh Heads Bulk | 397-5 | 397 Tee2 | Mudgeeraba BS | NCC Rating (A) | 703 | 703 | 703 | 703 | 703 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 703 | 703 | 703 | 703 | 703
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Caboolture Bulk | 321-1 | Caboolture BS | Caboolture West | NCC Rating (A) | 509 | 509 | 509 | 509 | 509 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 288 | 290 | 292 | 294 | 294
|  |  |  | Power Factor | 0.973 | 0.973 | 0.973 | 0.973 | 0.973
|  |  |  | ECC Rating (A) | 509 | 509 | 509 | 509 | 509
|  |  |  | 50 POE Load (A) | 392 | 395 | 397 | 399 | 399
Caboolture Bulk | 322-1 | Caboolture BS | Caboolture West | NCC Rating (A) | 509 | 509 | 509 | 509 | 509 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 300 | 302 | 304 | 305 | 306
|  |  |  | Power Factor | 0.964 | 0.964 | 0.964 | 0.963 | 0.963
|  |  |  | ECC Rating (A) | 509 | 509 | 509 | 509 | 509
|  |  |  | 50 POE Load (A) | 398 | 401 | 404 | 406 | 406
Caboolture Bulk | 323-1 | Caboolture West | 323 Tee1 | NCC Rating (A) | 251 | 510 | 510 | 510 | 510 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 78 | 77 | 77 | 77 | 77
|  |  |  | Power Factor | 0.986 | 0.987 | 0.987 | 0.987 | 0.987
|  |  |  | ECC Rating (A) | 251 | 510 | 510 | 510 | 510
|  |  |  | 50 POE Load (A) | 262 | 246 | 246 | 246 | 245
Caboolture Bulk | 323-2 | 323 Tee1 | Wamuran | NCC Rating (A) | 457 | 457 | 457 | 457 | 457 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 78 | 77 | 77 | 77 | 77
|  |  |  | Power Factor | 0.985 | 0.984 | 0.984 | 0.984 | 0.984
|  |  |  | ECC Rating (A) | 457 | 457 | 457 | 457 | 457
|  |  |  | 50 POE Load (A) | 71 | 69 | 69 | 69 | 69
Caboolture Bulk | 323-3 | 323 Tee1 | Woodford | NCC Rating (A) | 251 | 271 | 271 | 271 | 271 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 251 | 271 | 271 | 271 | 271
|  |  |  | 50 POE Load (A) | 190 | 177 | 177 | 177 | 176
Caboolture Bulk | 350-1 | Caboolture BS | Ningi | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 429 | 440 | 442 | 443 | 443
|  |  |  | Power Factor | 0.96 | 0.96 | 0.959 | 0.959 | 0.959
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 729 | 758 | 762 | 762 | 763
Caboolture Bulk | 412-1 | Caboolture BS | Toorbul Pt | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 341 | 352 | 354 | 354 | 355
|  |  |  | Power Factor | 0.945 | 0.945 | 0.944 | 0.944 | 0.944
|  |  |  | ECC Rating (A) | 823 | 823 | 823 | 823 | 823
|  |  |  | 50 POE Load (A) | 773 | 806 | 813 | 813 | 815
Caboolture Bulk | 417-1 | Ningi | Toorbul Pt | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 253 | 265 | 266 | 266 | 266
|  |  |  | Power Factor | 0.985 | 0.985 | 0.985 | 0.985 | 0.985
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 567 | 595 | 598 | 598 | 599
Caboolture Bulk | 431-1 | Toorbul Point | Bribie Is | NCC Rating (A) | 396 | 396 | 396 | 396 | 396 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 231 | 232 | 233 | 233 | 234
|  |  |  | Power Factor | 0.974 | 0.974 | 0.974 | 0.974 | 0.974
|  |  |  | ECC Rating (A) | 443 | 443 | 443 | 443 | 443
|  |  |  | 50 POE Load (A) | 396 | 398 | 400 | 400 | 400
Caboolture Bulk | 448-1 | Morayfield Nth | 448 Tee1 | NCC Rating (A) | 776 | 776 | 776 | 776 | 776 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 627 | 643 | 652 | 660 | 664
|  |  |  | Power Factor | 0.978 | 0.977 | 0.976 | 0.976 | 0.975
|  |  |  | ECC Rating (A) | 776 | 776 | 776 | 776 | 776
|  |  |  | 50 POE Load (A) | 660 | 676 | 685 | 691 | 695
Caboolture Bulk | 448-2 | 448 Tee1 | Morayfield | NCC Rating (A) | 698 | 698 | 698 | 698 | 698 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 612 | 630 | 641 | 650 | 656
|  |  |  | Power Factor | 0.984 | 0.982 | 0.981 | 0.98 | 0.98
|  |  |  | ECC Rating (A) | 698 | 698 | 698 | 698 | 698
|  |  |  | 50 POE Load (A) | 528 | 545 | 555 | 562 | 567
Caboolture Bulk | 448-3 | 448 Tee1 | Caboolture West | NCC Rating (A) | 485 | 485 | 485 | 485 | 485 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 26 | 23 | 22 | 20 | 19
|  |  |  | Power Factor | 0.668 | 0.632 | 0.614 | 0.593 | 0.566
|  |  |  | ECC Rating (A) | 485 | 485 | 485 | 485 | 485
|  |  |  | 50 POE Load (A) | 139 | 137 | 137 | 137 | 136
Caboolture Bulk | 457-1 | Toorbul Pt | Bribie Island | NCC Rating (A) | 402 | 402 | 402 | 402 | 402 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 230 | 231 | 232 | 232 | 232
|  |  |  | Power Factor | 0.978 | 0.978 | 0.978 | 0.978 | 0.978
|  |  |  | ECC Rating (A) | 512 | 512 | 512 | 512 | 512
|  |  |  | 50 POE Load (A) | 397 | 398 | 400 | 400 | 401
Caboolture Bulk | 461-1 | Caboolture BS | Morayfield Nth | NCC Rating (A) | 676 | 676 | 676 | 676 | 676 | Urban | 238 | NA
|  |  |  | 10 POE Load (A) | 554 | 562 | 568 | 573 | 576
|  |  |  | Power Factor | 0.972 | 0.972 | 0.971 | 0.97 | 0.97
|  |  |  | ECC Rating (A) | 758 | 758 | 758 | 758 | 758
|  |  |  | 50 POE Load (A) | 871 | 884 | 894 | 901 | 905
Caboolture Bulk | 499-1 | Caboolture BS | Morayfield Nth | NCC Rating (A) | 676 | 676 | 676 | 676 | 676 | Urban | 239 | NA
|  |  |  | 10 POE Load (A) | 558 | 566 | 572 | 577 | 580
|  |  |  | Power Factor | 0.972 | 0.972 | 0.971 | 0.97 | 0.97
|  |  |  | ECC Rating (A) | 758 | 758 | 758 | 758 | 758
|  |  |  | 50 POE Load (A) | 872 | 886 | 895 | 902 | 906
Cleveland Bulk | 3550-1 | Cleveland BS | Victoria Pt | NCC Rating (A) | 746 | 746 | 746 | 746 | 746 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 546 | 548 | 552 | 553 | 554
|  |  |  | Power Factor | 0.97 | 0.97 | 0.969 | 0.969 | 0.969
|  |  |  | ECC Rating (A) | 746 | 746 | 746 | 746 | 746
|  |  |  | 50 POE Load (A) | 658 | 660 | 665 | 666 | 668
Cleveland Bulk | 3570-1 | Capalaba South | Capalaba | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 105 | 105 | 105 | 105 | 105
|  |  |  | Power Factor | 0.964 | 0.964 | 0.964 | 0.965 | 0.965
|  |  |  | ECC Rating (A) | 553 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 323 | 323 | 323 | 322 | 320
Cleveland Bulk | 3580-1 | Redland Bay | 3580 Tee1 | NCC Rating (A) | 717 | 717 | 717 | 717 | 717 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 55 | 56 | 57 | 58 | 59
|  |  |  | Power Factor | 0.97 | 0.971 | 0.97 | 0.97 | 0.969
|  |  |  | ECC Rating (A) | 717 | 717 | 717 | 717 | 717
|  |  |  | 50 POE Load (A) | 334 | 336 | 340 | 343 | 345
Cleveland Bulk | 3580-2 | 3580 Tee1 | Mt Cotton | NCC Rating (A) | 527 | 527 | 527 | 527 | 527 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 55 | 56 | 57 | 58 | 59
|  |  |  | Power Factor | 0.977 | 0.977 | 0.977 | 0.976 | 0.976
|  |  |  | ECC Rating (A) | 527 | 527 | 527 | 527 | 527
|  |  |  | 50 POE Load (A) | 334 | 336 | 340 | 342 | 345
Cleveland Bulk | 3580-3 | 3580 Tee1 | Cornubia | NCC Rating (A) | 717 | 717 | 717 | 717 | 717 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 717 | 717 | 717 | 717 | 717
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Cleveland Bulk | 371-1 | Cleveland BS | Birkdale | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 489 | 486 | 486 | 484 | 482
|  |  |  | Power Factor | 0.967 | 0.967 | 0.967 | 0.968 | 0.968
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 595 | 592 | 592 | 590 | 587
Cleveland Bulk | 372-1 | Cleveland BS | Raby Bay | NCC Rating (A) | 611 | 611 | 611 | 611 | 611 | Urban | 308 | NA
|  |  |  | 10 POE Load (A) | 435 | 435 | 438 | 439 | 439
|  |  |  | Power Factor | 0.971 | 0.971 | 0.971 | 0.971 | 0.971
|  |  |  | ECC Rating (A) | 686 | 686 | 686 | 686 | 686
|  |  |  | 50 POE Load (A) | 758 | 759 | 764 | 765 | 767
Cleveland Bulk | 373-1 | Raby Bay | Capalaba | NCC Rating (A) | 715 | 715 | 715 | 715 | 715 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 366 | 363 | 363 | 361 | 359
|  |  |  | Power Factor | 0.967 | 0.968 | 0.968 | 0.968 | 0.968
|  |  |  | ECC Rating (A) | 715 | 715 | 715 | 715 | 715
|  |  |  | 50 POE Load (A) | 571 | 568 | 568 | 565 | 562
Cleveland Bulk | 374-1 | Cleveland BS | Capalaba South | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 422 | 419 | 419 | 418 | 416
|  |  |  | Power Factor | 0.956 | 0.957 | 0.957 | 0.957 | 0.957
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 612 | 609 | 609 | 606 | 603
Cleveland Bulk | 375-1 | Cleveland BS | 375 Tee1 | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 205 | 206 | 207 | 208 | 208
|  |  |  | Power Factor | 0.983 | 0.983 | 0.982 | 0.982 | 0.982
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | 50 POE Load (A) | 474 | 476 | 480 | 482 | 484
Cleveland Bulk | 375-2 | 375 Tee1 | Mt Cotton | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 205 | 206 | 207 | 208 | 208
|  |  |  | Power Factor | 0.984 | 0.984 | 0.984 | 0.984 | 0.984
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | 50 POE Load (A) | 474 | 476 | 480 | 482 | 484
Cleveland Bulk | 375-3 | 375 Tee1 | 425 Tee1 | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Cleveland Bulk | 413-1 | Cleveland BS | Raby Bay | NCC Rating (A) | 611 | 611 | 611 | 611 | 611 | Urban | 320 | NA
|  |  |  | 10 POE Load (A) | 440 | 440 | 443 | 444 | 445
|  |  |  | Power Factor | 0.971 | 0.972 | 0.971 | 0.971 | 0.971
|  |  |  | ECC Rating (A) | 611 | 611 | 611 | 611 | 611
|  |  |  | 50 POE Load (A) | 758 | 760 | 764 | 766 | 767
Cleveland Bulk | 425-1 | Cleveland BS | Victoria Pt | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 242 | 243 | 245 | 245 | 246
|  |  |  | Power Factor | 0.983 | 0.983 | 0.983 | 0.983 | 0.983
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | 50 POE Load (A) | 590 | 592 | 597 | 598 | 599
Cleveland Bulk | 465-1 | Victoria Pt | Redland Bay | NCC Rating (A) | 508 | 508 | 508 | 508 | 508 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 317 | 319 | 322 | 324 | 325
|  |  |  | Power Factor | 0.379 | 0.966 | 0.966 | 0.966 | 0.966
|  |  |  | ECC Rating (A) | 508 | 508 | 508 | 508 | 508
|  |  |  | 50 POE Load (A) | 456 | 458 | 462 | 464 | 465
Cleveland Bulk | 484-1 | Capalaba | Birkdale | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 151 | 151 | 151 | 150 | 149
|  |  |  | Power Factor | 1 | 1 | 1 | 1 | 1
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | 50 POE Load (A) | 590 | 589 | 589 | 586 | 583
Coomera Bulk | 3640-1 | Coomera BS | Hope Is | NCC Rating (A) | 716 | 716 | 716 | 716 | 716 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 392 | 397 | 402 | 406 | 409
|  |  |  | Power Factor | 0.966 | 0.965 | 0.964 | 0.964 | 0.964
|  |  |  | ECC Rating (A) | 713 | 713 | 713 | 713 | 713
|  |  |  | 50 POE Load (A) | 619 | 626 | 635 | 647 | 643
Coomera Bulk | 3641-1 | Coomera BS | Pimpama East | NCC Rating (A) | 713 | 713 | 713 | 713 | 713 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 330 | 344 | 360 | 373 | 387
|  |  |  | Power Factor | 0.976 | 0.974 | 0.972 | 0.97 | 0.97
|  |  |  | ECC Rating (A) | 713 | 713 | 713 | 713 | 713
|  |  |  | 50 POE Load (A) | 570 | 595 | 622 | 652 | 666
Coomera Bulk | 3642-1 | Coomera BS | Pimpama East | NCC Rating (A) | 713 | 713 | 713 | 713 | 713 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 332 | 347 | 362 | 376 | 390
|  |  |  | Power Factor | 0.976 | 0.974 | 0.972 | 0.97 | 0.97
|  |  |  | ECC Rating (A) | 713 | 713 | 713 | 713 | 713
|  |  |  | 50 POE Load (A) | 569 | 595 | 622 | 653 | 665
Coomera Bulk | 394-1 | Coomera BS | Hope Is | NCC Rating (A) | 716 | 716 | 716 | 716 | 716 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 401 | 406 | 412 | 416 | 419
|  |  |  | Power Factor | 0.972 | 0.971 | 0.97 | 0.97 | 0.97
|  |  |  | ECC Rating (A) | 716 | 716 | 716 | 716 | 716
|  |  |  | 50 POE Load (A) | 620 | 628 | 636 | 649 | 645
Coorparoo Bulk | 3429-1 | Coorparoo BS | Holland Park | NCC Rating (A) | 735 | 735 | 735 | 735 | 735 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 218 | 219 | 220 | 220 | 220
|  |  |  | Power Factor | 0.973 | 0.973 | 0.973 | 0.973 | 0.973
|  |  |  | ECC Rating (A) | 790 | 790 | 790 | 790 | 790
|  |  |  | 50 POE Load (A) | 392 | 392 | 394 | 395 | 394
Coorparoo Bulk | 3430-1 | Coorparoo BS | Holland Park | NCC Rating (A) | 735 | 735 | 735 | 735 | 735 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 214 | 214 | 215 | 216 | 215
|  |  |  | Power Factor | 0.973 | 0.973 | 0.973 | 0.973 | 0.973
|  |  |  | ECC Rating (A) | 790 | 790 | 790 | 790 | 790
|  |  |  | 50 POE Load (A) | 393 | 393 | 395 | 395 | 395
Coorparoo Bulk | 584-4 | 584 Tee2 | Coorparoo BS | NCC Rating (A) | 721 | 721 | 721 | 721 | 721 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 721 | 721 | 721 | 721 | 721
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Coorparoo Bulk | 612-1 | Coorparoo BS | Camp Hill | NCC Rating (A) | 766 | 766 | 766 | 766 | 766 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 338 | 338 | 338 | 338 | 337
|  |  |  | Power Factor | 0.97 | 0.97 | 0.97 | 0.971 | 0.971
|  |  |  | ECC Rating (A) | 766 | 766 | 766 | 766 | 766
|  |  |  | 50 POE Load (A) | 564 | 563 | 564 | 563 | 561
Coorparoo Bulk | 613-1 | Coorparoo BS | Camp Hill | NCC Rating (A) | 766 | 766 | 766 | 766 | 766 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 338 | 338 | 338 | 338 | 337
|  |  |  | Power Factor | 0.97 | 0.97 | 0.97 | 0.971 | 0.971
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 564 | 563 | 564 | 563 | 561
Coorparoo Bulk | 648-1 | Scrub Rd | 648 Tee1 | NCC Rating (A) | 597 | 597 | 597 | 597 | 597 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 597 | 597 | 597 | 597 | 597
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Coorparoo Bulk | 648-2 | 648 Tee1 | 584 Tee1 | NCC Rating (A) | 348 | 348 | 348 | 348 | 348 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 348 | 348 | 348 | 348 | 348
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Coorparoo Bulk | 648-3 | 648 Tee1 | Camp Hill | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Doboy Bulk | 3426-1 | Queensport | Bulimba | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 306 | 309 | 310 | 355 | 384
|  |  |  | Power Factor | 0.959 | 0.959 | 0.959 | 0.989 | 0.986
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 455 | 455 | 456 | 491 | 532
Doboy Bulk | 414-1 | Doboy BS | Tingalpa | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 198 | 201 | 201 | 200 | 199
|  |  |  | Power Factor | 0.961 | 0.961 | 0.961 | 0.961 | 0.961
|  |  |  | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
|  |  |  | 50 POE Load (A) | 415 | 413 | 413 | 412 | 405
Doboy Bulk | 416-1 | Doboy BS | Murarrie | NCC Rating (A) | 355 | 355 | 355 | 355 | 355 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 207 | 218 | 217 | 219 | 218
|  |  |  | Power Factor | 0.981 | 0.995 | 0.995 | 0.995 | 0.995
|  |  |  | ECC Rating (A) | 470 | 470 | 470 | 470 | 470
|  |  |  | 50 POE Load (A) | 398 | 421 | 419 | 419 | 417
Doboy Bulk | 443-1 | Queensport | Bulimba | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 217 | 219 | 219 | 251 | 272
|  |  |  | Power Factor | 0.966 | 0.966 | 0.966 | 0.992 | 0.99
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | 50 POE Load (A) | 457 | 457 | 458 | 495 | 536
Doboy Bulk | 558-1 | Hemmant | Tingalpa | NCC Rating (A) | 680 | 680 | 680 | 680 | 680 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 267 | 268 | 268 | 268 | 266
|  |  |  | Power Factor | 0.956 | 0.956 | 0.956 | 0.956 | 0.957
|  |  |  | ECC Rating (A) | 680 | 680 | 680 | 680 | 680
|  |  |  | 50 POE Load (A) | 411 | 410 | 410 | 409 | 402
Doboy Bulk | 563-1 | Doboy BS | Hemmant | NCC Rating (A) | 371 | 371 | 371 | 371 | 371 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 208 | 223 | 222 | 222 | 221
|  |  |  | Power Factor | 0.965 | 0.965 | 0.966 | 0.966 | 0.966
|  |  |  | ECC Rating (A) | 429 | 429 | 429 | 429 | 429
|  |  |  | 50 POE Load (A) | 358 | 385 | 384 | 383 | 381
Doboy Bulk | 564-1 | Doboy BS | Hemmant | NCC Rating (A) | 371 | 371 | 371 | 371 | 371 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 200 | 214 | 213 | 213 | 213
|  |  |  | Power Factor | 0.96 | 0.961 | 0.961 | 0.961 | 0.962
|  |  |  | ECC Rating (A) | 429 | 429 | 429 | 429 | 429
|  |  |  | 50 POE Load (A) | 357 | 384 | 383 | 382 | 379
Doboy Bulk | 575C-1 | Doboy BS | Murarrie | NCC Rating (A) | 355 | 355 | 355 | 355 | 355 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 196 | 206 | 205 | 208 | 208
|  |  |  | Power Factor | 0.979 | 0.994 | 0.994 | 0.994 | 0.995
|  |  |  | ECC Rating (A) | 475 | 475 | 475 | 475 | 475
|  |  |  | 50 POE Load (A) | 398 | 421 | 419 | 419 | 417
Doboy Bulk | 581-1 | Doboy BS | Queensport | NCC Rating (A) | 661 | 661 | 661 | 661 | 661 | Urban | 166 | 3.5
|  |  |  | 10 POE Load (A) | 531 | 535 | 535 | 573 | 595
|  |  |  | Power Factor | 0.973 | 0.973 | 0.973 | 0.986 | 0.984
|  |  |  | ECC Rating (A) | 785 | 785 | 785 | 785 | 785
|  |  |  | 50 POE Load (A) | 926 | 923 | 924 | 955 | 994
Doboy Bulk | 645-1 | Doboy BS | Gibson Island | NCC Rating (A) | 433 | 433 | 433 | 433 | 433 | HighSec | 0 | NA
|  |  |  | 10 POE Load (A) | 5 | 5 | 5 | 5 | 5
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 433 | 433 | 433 | 433 | 433
|  |  |  | 50 POE Load (A) | 156 | 156 | 156 | 156 | 155
Doboy Bulk | 677-1 | Doboy BS | Queensport | NCC Rating (A) | 661 | 661 | 661 | 661 | 661 | Urban | 166 | 1.5
|  |  |  | 10 POE Load (A) | 529 | 533 | 534 | 571 | 593
|  |  |  | Power Factor | 0.973 | 0.973 | 0.973 | 0.986 | 0.984
|  |  |  | ECC Rating (A) | 785 | 785 | 785 | 785 | 785
|  |  |  | 50 POE Load (A) | 925 | 923 | 924 | 955 | 994
Gatton Bulk | 377-1 | Gatton BS | 377 Tee1 | NCC Rating (A) | 821 | 821 | 821 | 821 | 821 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 293 | 302 | 302 | 301 | 300
|  |  |  | Power Factor | 0.983 | 0.982 | 0.982 | 0.982 | 0.982
|  |  |  | ECC Rating (A) | 959 | 959 | 959 | 959 | 959
|  |  |  | 50 POE Load (A) | 472 | 461 | 461 | 460 | 459
Gatton Bulk | 377-2 | 377 Tee1 | 487 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Gatton Bulk | 377-3 | 377 Tee1 | 377 Tee2 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 293 | 302 | 302 | 302 | 300
|  |  |  | Power Factor | 0.983 | 0.982 | 0.982 | 0.982 | 0.982
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 473 | 461 | 461 | 460 | 459
Gatton Bulk | 377-4 | 377 Tee2 | Gatton | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 294 | 302 | 302 | 302 | 301
|  |  |  | Power Factor | 0.986 | 0.985 | 0.985 | 0.985 | 0.985
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | 50 POE Load (A) | 473 | 461 | 461 | 461 | 459
Gatton Bulk | 377-5 | 377 Tee2 | Glenmore Grove | NCC Rating (A) | 355 | 355 | 355 | 355 | 355 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 355 | 355 | 355 | 355 | 355
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Gatton Bulk | 3859-1 | Gatton BS | Springfield Central | NCC Rating (A) | 764 | 764 | 764 | 764 | 764 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 36 | 36 | 36 | 36 | 35
|  |  |  | Power Factor | 0.943 | 0.943 | 0.943 | 0.943 | 0.943
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 65 | 64 | 64 | 64 | 63
Gatton Bulk | 3860-1 | Gatton BS | Springfield Central | NCC Rating (A) | 764 | 764 | 764 | 764 | 764 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 36 | 36 | 36 | 36 | 35
|  |  |  | Power Factor | 0.942 | 0.942 | 0.942 | 0.942 | 0.943
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 65 | 64 | 64 | 64 | 63
Gatton Bulk | 487-1 | Gatton BS | 487 Tee1 | NCC Rating (A) | 821 | 821 | 821 | 821 | 821 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 286 | 293 | 293 | 292 | 291
|  |  |  | Power Factor | 0.981 | 0.98 | 0.98 | 0.98 | 0.981
|  |  |  | ECC Rating (A) | 821 | 821 | 821 | 821 | 821
|  |  |  | 50 POE Load (A) | 559 | 551 | 551 | 550 | 548
Gatton Bulk | 487-2 | 487 Tee1 | 377 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Gatton Bulk | 487-3 | 487 Tee1 | 487 Tee2 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 287 | 294 | 293 | 293 | 292
|  |  |  | Power Factor | 0.981 | 0.98 | 0.98 | 0.98 | 0.981
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 560 | 552 | 551 | 551 | 548
Gatton Bulk | 487-6 | 487 Tee3 | 3844 Tee1 | NCC Rating (A) | 251 | 251 | 251 | 251 | 251 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 251 | 251 | 251 | 251 | 251
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Gatton Bulk | 487-8 | 487 Tee4 | 3844 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Gatton Bulk | 487-9 | 487 Tee2 | Gatton | NCC Rating (A) | 713 | 713 | 713 | 713 | 713 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 202 | 209 | 209 | 209 | 209
|  |  |  | Power Factor | 0.993 | 0.992 | 0.992 | 0.992 | 0.992
|  |  |  | ECC Rating (A) | 713 | 713 | 713 | 713 | 713
|  |  |  | 50 POE Load (A) | 476 | 469 | 469 | 469 | 467
Gatton Bulk | 531-1 | Gatton | Tenthill | NCC Rating (A) | 155 | 155 | 200 | 200 | 200 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 74 | 74 | 74 | 75 | 75
|  |  |  | Power Factor | 0.982 | 0.982 | 0.982 | 0.982 | 0.982
|  |  |  | ECC Rating (A) | 155 | 155 | 200 | 200 | 200
|  |  |  | 50 POE Load (A) | 68 | 68 | 68 | 69 | 69
Gatton Bulk | 532-1 | Tenthill | 532 Tee1 | NCC Rating (A) | 208 | 208 | 208 | 208 | 208 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 208 | 208 | 208 | 208 | 208
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Gatton Bulk | 533-1 | Tenthill | Mt Sylvia | NCC Rating (A) | 78 | 78 | 78 | 78 | 78 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 16 | 16 | 16 | 16 | 16
|  |  |  | Power Factor | 0.908 | 0.908 | 0.907 | 0.907 | 0.907
|  |  |  | ECC Rating (A) | 78 | 78 | 78 | 78 | 78
|  |  |  | 50 POE Load (A) | 15 | 15 | 15 | 15 | 15
Goodna Bulk | 3800-1 | Goodna BS | Cooneana | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 92 | 103 | 115 | 127 | 139
|  |  |  | Power Factor | 0.986 | 0.992 | 0.99 | 0.989 | 0.988
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | 50 POE Load (A) | 161 | 183 | 204 | 222 | 242
Goodna Bulk | 3801-1 | Goodna BS | Carol Pk Central | NCC Rating (A) | 720 | 720 | 720 | 720 | 720 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 269 | 269 | 272 | 273 | 274
|  |  |  | Power Factor | 0.99 | 0.991 | 0.99 | 0.99 | 0.99
|  |  |  | ECC Rating (A) | 765 | 765 | 765 | 765 | 765
|  |  |  | 50 POE Load (A) | 450 | 454 | 457 | 453 | 455
Goodna Bulk | 3802-1 | Goodna BS | Springfield | NCC Rating (A) | 592 | 592 | 592 | 592 | 592 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 406 | 419 | 429 | 437 | 445
|  |  |  | Power Factor | 0.989 | 0.988 | 0.988 | 0.987 | 0.987
|  |  |  | ECC Rating (A) | 675 | 675 | 675 | 675 | 675
|  |  |  | 50 POE Load (A) | 689 | 698 | 714 | 718 | 729
Goodna Bulk | 3803-1 | Goodna BS | Carol Park | NCC Rating (A) | 502 | 502 | 502 | 502 | 502 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 245 | 251 | 256 | 260 | 264
|  |  |  | Power Factor | 0.995 | 0.995 | 0.994 | 0.994 | 0.994
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | 50 POE Load (A) | 335 | 347 | 353 | 354 | 358
Goodna Bulk | 3805-1 | Goodna BS | Carol Park | NCC Rating (A) | 502 | 502 | 502 | 502 | 502 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 224 | 230 | 234 | 238 | 241
|  |  |  | Power Factor | 0.994 | 0.993 | 0.993 | 0.992 | 0.992
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | 50 POE Load (A) | 322 | 333 | 339 | 340 | 344
Goodna Bulk | 3806-1 | Goodna BS | Springfield | NCC Rating (A) | 592 | 592 | 592 | 592 | 592 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 405 | 417 | 427 | 436 | 443
|  |  |  | Power Factor | 0.989 | 0.988 | 0.988 | 0.987 | 0.987
|  |  |  | ECC Rating (A) | 675 | 675 | 675 | 675 | 675
|  |  |  | 50 POE Load (A) | 688 | 698 | 714 | 718 | 729
Goodna Bulk | 3807-1 | Goodna BS | Redbank | NCC Rating (A) | 748 | 748 | 748 | 748 | 748 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 362 | 361 | 362 | 362 | 362
|  |  |  | Power Factor | 0.963 | 0.962 | 0.962 | 0.962 | 0.962
|  |  |  | ECC Rating (A) | 748 | 748 | 748 | 748 | 748
|  |  |  | 50 POE Load (A) | 350 | 345 | 346 | 346 | 349
Goodna Bulk | 3808-1 | Goodna BS | Carol Pk Central | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 270 | 270 | 272 | 274 | 275
|  |  |  | Power Factor | 0.99 | 0.991 | 0.991 | 0.99 | 0.99
|  |  |  | ECC Rating (A) | 748 | 748 | 748 | 748 | 748
|  |  |  | 50 POE Load (A) | 450 | 454 | 457 | 454 | 455
Goodna Bulk | 3809-1 | Goodna BS | Cooneana | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 105 | 117 | 131 | 145 | 158
|  |  |  | Power Factor | 0.987 | 0.993 | 0.991 | 0.99 | 0.989
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | 50 POE Load (A) | 160 | 182 | 204 | 222 | 242
Goodna Bulk | 3880-1 | Carol Park | Springfield Central | NCC Rating (A) | 742 | 742 | 742 | 742 | 742 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 196 | 214 | 225 | 235 | 245
|  |  |  | Power Factor | 0.995 | 0.994 | 0.993 | 0.993 | 0.992
|  |  |  | ECC Rating (A) | 742 | 742 | 742 | 742 | 742
|  |  |  | 50 POE Load (A) | 346 | 387 | 406 | 419 | 437
Goodna Bulk | 3881-1 | Springfield | Springfield Central | NCC Rating (A) | 742 | 742 | 742 | 742 | 742 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 220 | 240 | 252 | 263 | 274
|  |  |  | Power Factor | 0.991 | 0.99 | 0.989 | 0.988 | 0.988
|  |  |  | ECC Rating (A) | 742 | 742 | 742 | 742 | 742
|  |  |  | 50 POE Load (A) | 343 | 382 | 401 | 414 | 431
Goodna Bulk | 456-1 | Wacol Sth | 456 Tee1 | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 1 | 1 | 1 | 1 | 1
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Goodna Bulk | 456-2 | 456 Tee1 | Carol Pk Central | NCC Rating (A) | 441 | 441 | 441 | 441 | 441 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 100 | 105 | 109 | 111 | 114
|  |  |  | Power Factor | 1 | 1 | 1 | 0.999 | 0.999
|  |  |  | ECC Rating (A) | 441 | 441 | 441 | 441 | 441
|  |  |  | 50 POE Load (A) | 177 | 186 | 190 | 191 | 194
Goodna Bulk | 456-3 | 456 Tee1 | Carol Pk | NCC Rating (A) | 441 | 441 | 441 | 441 | 441 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 100 | 105 | 109 | 111 | 114
|  |  |  | Power Factor | 1 | 1 | 0.999 | 0.999 | 0.999
|  |  |  | ECC Rating (A) | 441 | 441 | 441 | 441 | 441
|  |  |  | 50 POE Load (A) | 177 | 186 | 190 | 191 | 194
Griffin Bulk | 312-1 | Kallangur | Narangba | NCC Rating (A) | 422 | 422 | 422 | 422 | 422 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 422 | 422 | 422 | 422 | 422
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Griffin Bulk | 320-1 | Griffin BS | 320 Tee1 | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Urban | 70 | 0.5
|  |  |  | 10 POE Load (A) | 401 | 403 | 407 | 416 | 423
|  |  |  | Power Factor | 0.987 | 0.987 | 0.987 | 0.987 | 0.986
|  |  |  | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
|  |  |  | 50 POE Load (A) | 518 | 521 | 526 | 536 | 545
Griffin Bulk | 320-2 | 320 Tee1 | Mango Hill Bus 2 | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Urban | 70 | 0.5
|  |  |  | 10 POE Load (A) | 320 | 321 | 324 | 324 | 323
|  |  |  | Power Factor | 0.998 | 0.998 | 0.998 | 0.997 | 0.997
|  |  |  | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
|  |  |  | 50 POE Load (A) | 552 | 555 | 560 | 563 | 564
Griffin Bulk | 320-3 | 320 Tee1 | Kalangur | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Urban | 70 | 0.5
|  |  |  | 10 POE Load (A) | 101 | 102 | 104 | 112 | 120
|  |  |  | Power Factor | 0.922 | 0.923 | 0.923 | 0.929 | 0.931
|  |  |  | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
|  |  |  | 50 POE Load (A) | 305 | 308 | 312 | 327 | 344
Griffin Bulk | 3329-1 | Griffin BS | 3329 Tee1 | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 431 | 434 | 439 | 453 | 466
|  |  |  | Power Factor | 0.976 | 0.976 | 0.976 | 0.974 | 0.973
|  |  |  | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
|  |  |  | 50 POE Load (A) | 484 | 488 | 493 | 510 | 527
Griffin Bulk | 3329-2 | 3329 Tee1 | 3330 Tee1 | NCC Rating (A) | 748 | 748 | 748 | 748 | 748 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 422 | 422 | 422 | 422 | 422
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Griffin Bulk | 3329-3 | 3329 Tee1 | Kallangur | NCC Rating (A) | 711 | 711 | 711 | 711 | 711 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 432 | 435 | 440 | 454 | 467
|  |  |  | Power Factor | 0.977 | 0.976 | 0.976 | 0.974 | 0.973
|  |  |  | ECC Rating (A) | 711 | 711 | 711 | 711 | 711
|  |  |  | 50 POE Load (A) | 485 | 489 | 494 | 511 | 528
Griffin Bulk | 3330-1 | Griffin BS | 3330 Tee1 | NCC Rating (A) | 717 | 717 | 717 | 717 | 717 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 222 | 224 | 226 | 233 | 240
|  |  |  | Power Factor | 0.986 | 0.986 | 0.986 | 0.984 | 0.983
|  |  |  | ECC Rating (A) | 717 | 717 | 717 | 717 | 717
|  |  |  | 50 POE Load (A) | 350 | 353 | 357 | 369 | 381
Griffin Bulk | 3330-2 | 3330 Tee1 | 3329 Tee1 | NCC Rating (A) | 523 | 523 | 523 | 523 | 523 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 523 | 523 | 523 | 523 | 523
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Griffin Bulk | 3330-3 | 3330 Tee1 | APM | NCC Rating (A) | 717 | 717 | 717 | 717 | 717 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 222 | 224 | 227 | 233 | 240
|  |  |  | Power Factor | 0.987 | 0.986 | 0.986 | 0.985 | 0.984
|  |  |  | ECC Rating (A) | 717 | 717 | 717 | 717 | 717
|  |  |  | 50 POE Load (A) | 350 | 353 | 357 | 369 | 381
Griffin Bulk | 3331-1 | 3331 Tee1 | Kallangur | NCC Rating (A) | 717 | 717 | 717 | 717 | 717 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 184 | 186 | 189 | 195 | 202
|  |  |  | Power Factor | 0.987 | 0.987 | 0.986 | 0.985 | 0.984
|  |  |  | ECC Rating (A) | 717 | 717 | 717 | 717 | 717
|  |  |  | 50 POE Load (A) | 312 | 315 | 319 | 331 | 343
Griffin Bulk | 3331-3 | Aust Paper Mills | 3331 Tee1 | NCC Rating (A) | 717 | 717 | 717 | 717 | 717 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 222 | 224 | 227 | 233 | 240
|  |  |  | Power Factor | 0.987 | 0.987 | 0.987 | 0.985 | 0.985
|  |  |  | ECC Rating (A) | 717 | 717 | 717 | 717 | 717
|  |  |  | 50 POE Load (A) | 350 | 353 | 357 | 369 | 381
Griffin Bulk | 3359-1 | 3359 Tee1 | Hays Inlet | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Griffin Bulk | 3359-2 | 3359 Tee1 | 3359 Tee2 | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 322 | 323 | 326 | 330 | 333
|  |  |  | Power Factor | 0.958 | 0.958 | 0.957 | 0.957 | 0.957
|  |  |  | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
|  |  |  | 50 POE Load (A) | 548 | 551 | 556 | 559 | 560
Griffin Bulk | 3359-3 | 3359 Tee2 | 3359 Tee3 | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 322 | 324 | 326 | 330 | 333
|  |  |  | Power Factor | 0.958 | 0.958 | 0.957 | 0.957 | 0.957
|  |  |  | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
|  |  |  | 50 POE Load (A) | 548 | 551 | 556 | 559 | 561
Griffin Bulk | 3359-4 | 3359 Tee3 | Mango Hill Bus 2 | NCC Rating (A) | 762 | 762 | 762 | 762 | 762 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 322 | 324 | 327 | 331 | 334
|  |  |  | Power Factor | 0.958 | 0.958 | 0.957 | 0.957 | 0.957
|  |  |  | ECC Rating (A) | 762 | 762 | 762 | 762 | 762
|  |  |  | 50 POE Load (A) | 549 | 552 | 556 | 560 | 561
Griffin Bulk | 3359-5 | 3359 Tee2 | P51001-D | NCC Rating (A) | 495 | 553 | 553 | 553 | 553 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 495 | 553 | 553 | 553 | 553
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Griffin Bulk | 3359-6 | 3359 Tee3 | X18574-E | NCC Rating (A) | 495 | 582 | 582 | 582 | 582 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 495 | 582 | 582 | 582 | 582
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Griffin Bulk | 3359-7 | Griffin BS | 3359 Tee1 | NCC Rating (A) | 703 | 703 | 703 | 703 | 703 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 321 | 323 | 326 | 330 | 333
|  |  |  | Power Factor | 0.953 | 0.952 | 0.952 | 0.951 | 0.951
|  |  |  | ECC Rating (A) | 703 | 703 | 703 | 703 | 703
|  |  |  | 50 POE Load (A) | 548 | 551 | 556 | 559 | 560
Griffin Bulk | 338-1 | Griffin BS | Strathpine | NCC Rating (A) | 348 | 348 | 348 | 348 | 348 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 348 | 348 | 348 | 348 | 348
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Gympie Bulk | 3004-1 | Coondoo Ck Reg | Tin Can Bay | NCC Rating (A) | 127 | 127 | 127 | 127 | 127 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 43 | 43 | 43 | 43 | 43
|  |  |  | Power Factor | 0.999 | 0.999 | 0.999 | 0.999 | 0.999
|  |  |  | ECC Rating (A) | 127 | 127 | 127 | 127 | 127
|  |  |  | 50 POE Load (A) | 42 | 42 | 42 | 42 | 42
Gympie Bulk | 3005-1 | Coondoo Ck Reg | Tin Can Bay | NCC Rating (A) | 582 | 582 | 582 | 582 | 582 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 101 | 101 | 100 | 99 | 101
|  |  |  | Power Factor | 0.994 | 0.994 | 0.994 | 0.994 | 0.994
|  |  |  | ECC Rating (A) | 582 | 582 | 582 | 582 | 582
|  |  |  | 50 POE Load (A) | 97 | 96 | 97 | 96 | 96
Gympie Bulk | 3009-1 | Gympie BS | Gympie Nth | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 139 | 138 | 138 | 138 | 138
|  |  |  | Power Factor | 0.973 | 0.973 | 0.973 | 0.973 | 0.973
|  |  |  | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
|  |  |  | 50 POE Load (A) | 247 | 246 | 246 | 246 | 245
Gympie Bulk | 3011-1 | Gympie BS | Gympie Nth | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 139 | 138 | 138 | 138 | 138
|  |  |  | Power Factor | 0.973 | 0.973 | 0.973 | 0.973 | 0.973
|  |  |  | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
|  |  |  | 50 POE Load (A) | 247 | 246 | 246 | 246 | 245
Gympie Bulk | 339/2-1 | Amamoor | 339 Tee1 | NCC Rating (A) | 155 | 155 | 155 | 155 | 155 | Rural | 170 | 3
|  |  |  | 10 POE Load (A) | 56 | 55 | 59 | 59 | 58
|  |  |  | Power Factor | 0.991 | 0.992 | 0.976 | 0.977 | 0.978
|  |  |  | ECC Rating (A) | 155 | 155 | 155 | 155 | 155
|  |  |  | 50 POE Load (A) | 58 | 57 | 57 | 56 | 56
Gympie Bulk | 339/2-2 | 339 Tee1 | Imbil | NCC Rating (A) | 200 | 200 | 200 | 200 | 200 | Rural | 170 | 3
|  |  |  | 10 POE Load (A) | 43 | 43 | 47 | 46 | 46
|  |  |  | Power Factor | 0.999 | 0.999 | 0.988 | 0.988 | 0.989
|  |  |  | ECC Rating (A) | 200 | 200 | 200 | 200 | 200
|  |  |  | 50 POE Load (A) | 45 | 45 | 44 | 44 | 43
Gympie Bulk | 339/2-5 | 339 Tee2 | 340 Tee2 | NCC Rating (A) | 155 | 155 | 155 | 155 | 155 | Rural | 170 | 3
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 155 | 155 | 155 | 155 | 155
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Gympie Bulk | 339-1 | Gympie BS | 339 Tee1 | NCC Rating (A) | 742 | 742 | 742 | 742 | 742 | Rural | 170 | 3
|  |  |  | 10 POE Load (A) | 149 | 157 | 169 | 168 | 167
|  |  |  | Power Factor | 0.952 | 0.951 | 0.952 | 0.952 | 0.953
|  |  |  | ECC Rating (A) | 742 | 742 | 742 | 742 | 742
|  |  |  | 50 POE Load (A) | 152 | 160 | 159 | 159 | 158
Gympie Bulk | 339-2 | 339 Tee1 | Amamoor | NCC Rating (A) | 210 | 210 | 210 | 210 | 210 | Rural | 170 | 3
|  |  |  | 10 POE Load (A) | 149 | 158 | 169 | 169 | 168
|  |  |  | Power Factor | 0.951 | 0.949 | 0.949 | 0.949 | 0.949
|  |  |  | ECC Rating (A) | 210 | 210 | 210 | 210 | 210
|  |  |  | 50 POE Load (A) | 152 | 160 | 160 | 159 | 158
Gympie Bulk | 339-3 | 339 Tee1 | 340 Tee1 | NCC Rating (A) | 210 | 210 | 210 | 210 | 210 | Rural | 170 | 3
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 210 | 210 | 210 | 210 | 210
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Gympie Bulk | 340-1 | Gympie BS | 340 Tee1 | NCC Rating (A) | 349 | 349 | 349 | 349 | 349 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 65 | 65 | 65 | 65 | 65
|  |  |  | Power Factor | 0.964 | 0.964 | 0.964 | 0.964 | 0.964
|  |  |  | ECC Rating (A) | 349 | 349 | 349 | 349 | 349
|  |  |  | 50 POE Load (A) | 132 | 132 | 132 | 132 | 132
Gympie Bulk | 340-2 | 340 Tee1 | 339 Tee1 | NCC Rating (A) | 349 | 349 | 349 | 349 | 349 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 349 | 349 | 349 | 349 | 349
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Gympie Bulk | 340-4 | 340 Tee1 | 340 Tee2 | NCC Rating (A) | 349 | 349 | 349 | 349 | 349 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 65 | 65 | 65 | 65 | 65
|  |  |  | Power Factor | 0.963 | 0.963 | 0.963 | 0.963 | 0.963
|  |  |  | ECC Rating (A) | 349 | 349 | 349 | 349 | 349
|  |  |  | 50 POE Load (A) | 132 | 132 | 132 | 132 | 132
Gympie Bulk | 340-5 | 340 Tee2 | 340 Tee3 | NCC Rating (A) | 328 | 328 | 328 | 328 | 328 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 328 | 328 | 328 | 328 | 328
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Gympie Bulk | 340-6 | 340 Tee3 | 339 Tee2 | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Gympie Bulk | 340-7 | 339 Tee2 | Kenilworth | NCC Rating (A) | 208 | 208 | 208 | 208 | 208 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 208 | 208 | 208 | 208 | 208
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Gympie Bulk | 340-8 | 340 Tee3 | Black Mountain | NCC Rating (A) | 328 | 328 | 328 | 328 | 328 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 328 | 328 | 328 | 328 | 328
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Gympie Bulk | 340-9 | 340 Tee2 | Gympie South | NCC Rating (A) | 403 | 403 | 403 | 403 | 403 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 66 | 66 | 66 | 66 | 66
|  |  |  | Power Factor | 0.948 | 0.948 | 0.948 | 0.948 | 0.948
|  |  |  | ECC Rating (A) | 403 | 403 | 403 | 403 | 403
|  |  |  | 50 POE Load (A) | 133 | 133 | 133 | 133 | 133
Gympie Bulk | 341-1 | Gympie BS | 341 Tee1 | NCC Rating (A) | 211 | 211 | 211 | 211 | 211 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 188 | 188 | 189 | 188 | 188
|  |  |  | Power Factor | 0.998 | 0.998 | 0.998 | 0.998 | 0.998
|  |  |  | ECC Rating (A) | 211 | 211 | 211 | 211 | 211
|  |  |  | 50 POE Load (A) | 452 | 449 | 451 | 451 | 448
Gympie Bulk | 341-2 | 341 Tee1 | Customer | NCC Rating (A) | 410 | 410 | 410 | 410 | 410 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 46 | 46 | 46 | 46 | 45
|  |  |  | Power Factor | 0.933 | 0.933 | 0.933 | 0.933 | 0.931
|  |  |  | ECC Rating (A) | 463 | 463 | 463 | 463 | 463
|  |  |  | 50 POE Load (A) | 236.8999 | 236.9671 | 237.5518 | 237.4063 | 236.2456
Gympie Bulk | 341-3 | 341 Tee1 | Coondoo Ck Reg | NCC Rating (A) | 210 | 210 | 210 | 210 | 210 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 151 | 151 | 152 | 151 | 151
|  |  |  | Power Factor | 0.996 | 0.996 | 0.996 | 0.996 | 0.996
|  |  |  | ECC Rating (A) | 210 | 210 | 210 | 210 | 210
|  |  |  | 50 POE Load (A) | 163 | 162 | 163 | 162 | 162
Gympie Bulk | 341-4 | Coondoo Ck Reg | 341 Tee2 | NCC Rating (A) | 717 | 717 | 717 | 717 | 717 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 144 | 144 | 142 | 142 | 144
|  |  |  | Power Factor | 0.996 | 0.996 | 0.996 | 0.996 | 0.996
|  |  |  | ECC Rating (A) | 717 | 717 | 717 | 717 | 717
|  |  |  | 50 POE Load (A) | 138 | 138 | 138 | 138 | 138
Gympie Bulk | 351-1 | Gympie BS | Gympie Sth | NCC Rating (A) | 355 | 355 | 355 | 355 | 355 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 75 | 75 | 75 | 75 | 75
|  |  |  | Power Factor | 0.959 | 0.959 | 0.958 | 0.959 | 0.959
|  |  |  | ECC Rating (A) | 355 | 355 | 355 | 355 | 355
|  |  |  | 50 POE Load (A) | 133 | 133 | 133 | 133 | 133
Gympie Bulk | 429-1 | Gympie BS | 429 Tee1 | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 259 | 259 | 260 | 259 | 258
|  |  |  | Power Factor | 0.959 | 0.959 | 0.958 | 0.959 | 0.959
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | 50 POE Load (A) | 287 | 287 | 288 | 288 | 286
Gympie Bulk | 429-2 | 429 Tee1 | Goomboorian | NCC Rating (A) | 461 | 461 | 461 | 461 | 461 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 48 | 48 | 48 | 48 | 48
|  |  |  | Power Factor | 0.994 | 0.994 | 0.994 | 0.994 | 0.994
|  |  |  | ECC Rating (A) | 461 | 461 | 461 | 461 | 461
|  |  |  | 50 POE Load (A) | 44 | 44 | 44 | 43 | 43
Gympie Bulk | 429-3 | 429 Tee1 | Toolara Forest | NCC Rating (A) | 410 | 410 | 410 | 410 | 410 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 211 | 211 | 212 | 212 | 211
|  |  |  | Power Factor | 0.964 | 0.965 | 0.964 | 0.965 | 0.964
|  |  |  | ECC Rating (A) | 463 | 463 | 463 | 463 | 463
|  |  |  | 50 POE Load (A) | 244 | 244 | 245 | 245 | 243
Hays Inlet Bulk | 305-1 | Hays Inlet BS | Deception Bay | NCC Rating (A) | 759 | 759 | 759 | 759 | 759 | Urban | 266 | NA
|  |  |  | 10 POE Load (A) | 726 | 729 | 734 | 737 | 738
|  |  |  | Power Factor | 0.963 | 0.962 | 0.962 | 0.962 | 0.962
|  |  |  | ECC Rating (A) | 759 | 759 | 759 | 759 | 759
|  |  |  | 50 POE Load (A) | 976 | 980 | 988 | 992 | 996
Hays Inlet Bulk | 311-1 | Hays Inlet BS | Deception Bay | NCC Rating (A) | 623 | 623 | 623 | 623 | 623 | Urban | 154 | 4.5
|  |  |  | 10 POE Load (A) | 241 | 242 | 244 | 245 | 245
|  |  |  | Power Factor | 0.975 | 0.975 | 0.975 | 0.974 | 0.974
|  |  |  | ECC Rating (A) | 623 | 623 | 623 | 623 | 623
|  |  |  | 50 POE Load (A) | 714 | 717 | 722 | 724 | 726
Hays Inlet Bulk | 3250-1 | Deception Bay | Burpengary | NCC Rating (A) | 713 | 713 | 713 | 713 | 713 | Urban | 256 | NA
|  |  |  | 10 POE Load (A) | 440 | 442 | 446 | 449 | 451
|  |  |  | Power Factor | 0.973 | 0.972 | 0.972 | 0.972 | 0.972
|  |  |  | ECC Rating (A) | 713 | 713 | 713 | 713 | 713
|  |  |  | 50 POE Load (A) | 825 | 830 | 838 | 843 | 847
Hays Inlet Bulk | 325-1 | Hays Inlet BS | Scarborough | NCC Rating (A) | 529 | 529 | 529 | 529 | 529 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 318 | 321 | 324 | 326 | 328
|  |  |  | Power Factor | 0.981 | 0.981 | 0.981 | 0.981 | 0.981
|  |  |  | ECC Rating (A) | 529 | 529 | 529 | 529 | 529
|  |  |  | 50 POE Load (A) | 403 | 405 | 410 | 412 | 414
Hays Inlet Bulk | 3251-1 | Burpengary | Morayfield | NCC Rating (A) | 464 | 464 | 464 | 464 | 464 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 464 | 464 | 464 | 464 | 464
|  |  |  | 50 POE Load (A) | 559 | 579 | 590 | 597 | 603
Hays Inlet Bulk | 326-1 | Redcliffe | Scarborough | NCC Rating (A) | 322 | 322 | 322 | 322 | 322 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 40 | 42 | 44 | 46 | 48
|  |  |  | Power Factor | 1 | 0.999 | 0.999 | 0.998 | 0.998
|  |  |  | ECC Rating (A) | 322 | 322 | 322 | 322 | 322
|  |  |  | 50 POE Load (A) | 320 | 324 | 329 | 333 | 336
Hays Inlet Bulk | 327-1 | Hays Inlet BS | Mango Hill Bus 1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 477 | 484 | 492 | 498 | 503
|  |  |  | Power Factor | 0.964 | 0.963 | 0.962 | 0.962 | 0.961
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 398 | 403 | 409 | 414 | 419
Hays Inlet Bulk | 329-1 | Redcliffe | Duffield Rd | NCC Rating (A) | 578 | 578 | 578 | 578 | 578 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 119 | 120 | 121 | 122 | 123
|  |  |  | Power Factor | 0.979 | 0.978 | 0.978 | 0.978 | 0.978
|  |  |  | ECC Rating (A) | 578 | 578 | 578 | 578 | 578
|  |  |  | 50 POE Load (A) | 257 | 258 | 260 | 262 | 264
Hays Inlet Bulk | 330-1 | Hays Inlet BS | Duffield Rd | NCC Rating (A) | 543 | 543 | 543 | 543 | 543 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 276 | 277 | 279 | 280 | 280
|  |  |  | Power Factor | 0.974 | 0.974 | 0.974 | 0.974 | 0.974
|  |  |  | ECC Rating (A) | 578 | 578 | 578 | 578 | 578
|  |  |  | 50 POE Load (A) | 395 | 396 | 398 | 399 | 399
Hays Inlet Bulk | 331-1 | Hays Inlet BS | Duffield Rd | NCC Rating (A) | 543 | 543 | 543 | 543 | 543 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 276 | 277 | 277 | 277 | 277
|  |  |  | Power Factor | 0.97 | 0.97 | 0.969 | 0.969 | 0.969
|  |  |  | ECC Rating (A) | 573 | 573 | 573 | 573 | 573
|  |  |  | 50 POE Load (A) | 395 | 396 | 397 | 398 | 398
Hays Inlet Bulk | 332-1 | Hays Inlet BS | Redcliffe | NCC Rating (A) | 524 | 524 | 524 | 524 | 524 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 298 | 298 | 301 | 303 | 304
|  |  |  | Power Factor | 0.962 | 0.962 | 0.961 | 0.961 | 0.961
|  |  |  | ECC Rating (A) | 524 | 524 | 524 | 524 | 524
|  |  |  | 50 POE Load (A) | 412 | 413 | 418 | 420 | 421
Hays Inlet Bulk | 451-1 | Narangba | Burpengary | NCC Rating (A) | 422 | 422 | 422 | 422 | 422 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 59 | 59 | 58 | 57 | 55
|  |  |  | Power Factor | 0.99 | 0.99 | 0.992 | 0.994 | 0.997
|  |  |  | ECC Rating (A) | 422 | 422 | 422 | 422 | 422
|  |  |  | 50 POE Load (A) | 433 | 435 | 440 | 445 | 450
Hays Inlet Bulk | 497-1 | Hays Inlet BS | Narangba | NCC Rating (A) | 713 | 713 | 713 | 713 | 713 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 488 | 491 | 496 | 500 | 503
|  |  |  | Power Factor | 0.967 | 0.966 | 0.966 | 0.966 | 0.966
|  |  |  | ECC Rating (A) | 713 | 713 | 713 | 713 | 713
|  |  |  | 50 POE Load (A) | 819 | 824 | 832 | 837 | 841
Jimboomba Bulk | 470-1 | Jimboomba BS | Logan Village | NCC Rating (A) | 512 | 512 | 512 | 512 | 512 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 429 | 403 | 415 | 416 | 425
|  |  |  | Power Factor | 0.967 | 0.97 | 0.969 | 0.968 | 0.966
|  |  |  | ECC Rating (A) | 512 | 512 | 512 | 512 | 512
|  |  |  | 50 POE Load (A) | 360.36 | 338.52 | 348.6 | 349.44 | 357
Jimboomba Bulk | 479-1 | Jimboomba BS | Nth Maclean | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 675 | 693 | 701 | 704 | 723
|  |  |  | Power Factor | 0.937 | 0.934 | 0.935 | 0.934 | 0.932
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 565 | 586 | 588 | 509 | 513
Lockrose Bulk | 378-1 | Lockrose BS | 378 Tee1 | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 216 | 243 | 245 | 247 | 248
|  |  |  | Power Factor | 0.985 | 0.977 | 0.977 | 0.976 | 0.976
|  |  |  | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
|  |  |  | 50 POE Load (A) | 393 | 341 | 345 | 347 | 349
Lockrose Bulk | 378-2 | 378 Tee1 | Glenmore Grove | NCC Rating (A) | 800 | 442 | 442 | 442 | 442 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 95 | 130 | 131 | 131 | 131
|  |  |  | Power Factor | 1 | 0.986 | 0.986 | 0.986 | 0.986
|  |  |  | ECC Rating (A) | 800 | 442 | 442 | 442 | 442
|  |  |  | 50 POE Load (A) | 166 | 112 | 113 | 113 | 114
Lockrose Bulk | 378-3 | 378 Tee1 | 378 Tee2 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 122 | 113 | 115 | 116 | 117
|  |  |  | Power Factor | 0.967 | 0.976 | 0.975 | 0.974 | 0.974
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 228 | 229 | 232 | 234 | 236
Lockrose Bulk | 378-4 | 378 Tee2 | 532 Tee1 | NCC Rating (A) | 200 | 200 | 200 | 200 | 200 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 200 | 200 | 200 | 200 | 200
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Lockrose Bulk | 378-5 | 378 Tee2 | Laidley | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 123 | 114 | 115 | 116 | 117
|  |  |  | Power Factor | 0.97 | 0.978 | 0.977 | 0.977 | 0.976
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 228 | 229 | 232 | 234 | 236
Lockrose Bulk | 380-1 | Murrumba | 380 Tee1 | NCC Rating (A) | 200 | 200 | 200 | 200 | 200 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 69 | 70 | 62 | 61 | 62
|  |  |  | Power Factor | 0.97 | 0.97 | 0.988 | 0.988 | 0.987
|  |  |  | ECC Rating (A) | 200 | 200 | 200 | 200 | 200
|  |  |  | 50 POE Load (A) | 163 | 163 | 164 | 164 | 165
Lockrose Bulk | 380-2 | 380 Tee1 | Somerset Dam | NCC Rating (A) | 160 | 160 | 160 | 160 | 160 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 7 | 7 | 7 | 7 | 7
|  |  |  | Power Factor | 0.987 | 0.987 | 0.987 | 0.987 | 0.987
|  |  |  | ECC Rating (A) | 160 | 160 | 160 | 160 | 160
|  |  |  | 50 POE Load (A) | 9 | 8 | 8 | 8 | 8
Lockrose Bulk | 380-3 | 380 Tee1 | Toogoolahwah | NCC Rating (A) | 200 | 200 | 200 | 200 | 200 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 63 | 63 | 55 | 54 | 55
|  |  |  | Power Factor | 0.967 | 0.967 | 0.986 | 0.986 | 0.986
|  |  |  | ECC Rating (A) | 200 | 200 | 200 | 200 | 200
|  |  |  | 50 POE Load (A) | 156 | 156 | 157 | 157 | 158
Lockrose Bulk | 381-1 | Lockrose BS | 381 Tee1 | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 201 | 212 | 212 | 212 | 213
|  |  |  | Power Factor | 0.986 | 0.972 | 0.972 | 0.972 | 0.972
|  |  |  | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
|  |  |  | 50 POE Load (A) | 447 | 389 | 389 | 390 | 390
Lockrose Bulk | 381-2 | 381 Tee1 | 382 Tee1 | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Lockrose Bulk | 381-3 | 381 Tee1 | 381 Tee2 | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 201 | 212 | 212 | 213 | 213
|  |  |  | Power Factor | 0.987 | 0.973 | 0.973 | 0.973 | 0.973
|  |  |  | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
|  |  |  | 50 POE Load (A) | 447 | 389 | 389 | 390 | 390
Lockrose Bulk | 381-4 | 381 Tee2 | 383 Tee1 | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Lockrose Bulk | 381-5 | 381 Tee2 | 381 Tee3 | NCC Rating (A) | 293 | 553 | 553 | 553 | 553 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 201 | 212 | 212 | 213 | 213
|  |  |  | Power Factor | 0.99 | 0.977 | 0.977 | 0.977 | 0.977
|  |  |  | ECC Rating (A) | 293 | 553 | 553 | 553 | 553
|  |  |  | 50 POE Load (A) | 448 | 389 | 389 | 390 | 390
Lockrose Bulk | 381-6 | 381 Tee3 | Coominya TR2 | NCC Rating (A) | 403 | 403 | 403 | 403 | 403 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 85 | 83 | 83 | 84 | 83
|  |  |  | Power Factor | 0.998 | 0.998 | 0.998 | 0.998 | 0.998
|  |  |  | ECC Rating (A) | 403 | 403 | 403 | 403 | 403
|  |  |  | 50 POE Load (A) | 94 | 85 | 85 | 85 | 85
Lockrose Bulk | 381-7 | 381 Tee3 | 381 Tee4 | NCC Rating (A) | 293 | 582 | 582 | 582 | 582 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 116 | 130 | 130 | 130 | 130
|  |  |  | Power Factor | 0.992 | 0.97 | 0.97 | 0.971 | 0.97
|  |  |  | ECC Rating (A) | 293 | 582 | 582 | 582 | 582
|  |  |  | 50 POE Load (A) | 354 | 304 | 304 | 305 | 305
Lockrose Bulk | 381-8 | 381 Tee4 | Coominya TR1 | NCC Rating (A) | 403 | 403 | 403 | 403 | 403 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 59 | 58 | 58 | 58 | 58
|  |  |  | Power Factor | 0.999 | 0.999 | 0.999 | 0.999 | 0.999
|  |  |  | ECC Rating (A) | 403 | 403 | 403 | 403 | 403
|  |  |  | 50 POE Load (A) | 65 | 59 | 59 | 59 | 59
Lockrose Bulk | 381-9 | 381 Tee4 | Paddys Gully | NCC Rating (A) | 155 | 200 | 200 | 200 | 200 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 58 | 75 | 74 | 74 | 74
|  |  |  | Power Factor | 0.978 | 0.923 | 0.924 | 0.925 | 0.924
|  |  |  | ECC Rating (A) | 155 | 200 | 200 | 200 | 200
|  |  |  | 50 POE Load (A) | 289 | 246 | 246 | 246 | 246
Lockrose Bulk | 382-1 | Lockrose BS | 382 Tee1 | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 202 | 183 | 182 | 183 | 183
|  |  |  | Power Factor | 0.951 | 0.971 | 0.971 | 0.972 | 0.971
|  |  |  | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
|  |  |  | 50 POE Load (A) | 224 | 224 | 224 | 224 | 225
Lockrose Bulk | 382-2 | 382 Tee1 | 381 Tee1 | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Lockrose Bulk | 382-3 | 382 Tee1 | Paddys Gully | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 203 | 183 | 183 | 183 | 183
|  |  |  | Power Factor | 0.951 | 0.971 | 0.972 | 0.972 | 0.972
|  |  |  | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
|  |  |  | 50 POE Load (A) | 224 | 224 | 224 | 225 | 225
Lockrose Bulk | 3828-1 | Paddy's Gully | Esk | NCC Rating (A) | 155 | 155 | 700 | 700 | 700 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 114 | 115 | 120 | 118 | 120
|  |  |  | Power Factor | 0.988 | 0.988 | 0.98 | 0.98 | 0.979
|  |  |  | ECC Rating (A) | 155 | 155 | 400 | 400 | 400
|  |  |  | 50 POE Load (A) | 220 | 219 | 212 | 213 | 213
Lockrose Bulk | 3829-1 | Paddy's Gully | Murrumba | NCC Rating (A) | 155 | 155 | 155 | 155 | 155 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 118 | 120 | 110 | 109 | 111
|  |  |  | Power Factor | 0.951 | 0.951 | 0.964 | 0.964 | 0.964
|  |  |  | ECC Rating (A) | 155 | 155 | 155 | 155 | 155
|  |  |  | 50 POE Load (A) | 212 | 211 | 213 | 213 | 213
Lockrose Bulk | 3831-1 | Lockrose BS | Tarampa | NCC Rating (A) | 355 | 355 | 355 | 355 | 355 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 173 | 173 | 173 | 173 | 172
|  |  |  | Power Factor | 0.948 | 0.948 | 0.948 | 0.948 | 0.948
|  |  |  | ECC Rating (A) | 355 | 355 | 355 | 355 | 355
|  |  |  | 50 POE Load (A) | 147 | 147 | 147 | 147 | 146
Lockrose Bulk | 3832-1 | Tarampa | 383 Tee1 | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Lockrose Bulk | 3832-2 | 3832 Tee1 | 381 Tee1 | NCC Rating (A) | 155 | 700 | 700 | 700 | 700 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 155 | 700 | 700 | 700 | 700
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Lockrose Bulk | 3832-3 | 3832 Tee1 | Lowood | NCC Rating (A) | 434 | 434 | 434 | 434 | 434 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 434 | 434 | 434 | 434 | 434
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Lockrose Bulk | 3840-1 | Esk | Toogoolawah | NCC Rating (A) | 155 | 155 | 155 | 155 | 155 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 46 | 46 | 52 | 52 | 53
|  |  |  | Power Factor | 1 | 1 | 0.991 | 0.991 | 0.991
|  |  |  | ECC Rating (A) | 155 | 155 | 155 | 155 | 155
|  |  |  | 50 POE Load (A) | 161 | 161 | 155 | 156 | 156
Lockrose Bulk | 384-1 | Lockrose BS | 384 Tee1 | NCC Rating (A) | 451 | 451 | 451 | 451 | 451 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 226 | 203 | 205 | 206 | 207
|  |  |  | Power Factor | 0.984 | 0.991 | 0.991 | 0.991 | 0.991
|  |  |  | ECC Rating (A) | 451 | 451 | 451 | 451 | 451
|  |  |  | 50 POE Load (A) | 395 | 281 | 285 | 287 | 289
Lockrose Bulk | 384-2 | 384 Tee1 | Glenmore Grove | NCC Rating (A) | 293 | 293 | 293 | 293 | 293 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 96 | 60 | 61 | 61 | 61
|  |  |  | Power Factor | 0.95 | 0.987 | 0.987 | 0.987 | 0.987
|  |  |  | ECC Rating (A) | 293 | 293 | 293 | 293 | 293
|  |  |  | 50 POE Load (A) | 165 | 52 | 52 | 53 | 53
Lockrose Bulk | 384-3 | 384 Tee1 | Laidley1 | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 132 | 142 | 144 | 146 | 147
|  |  |  | Power Factor | 0.999 | 0.995 | 0.995 | 0.995 | 0.995
|  |  |  | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
|  |  |  | 50 POE Load (A) | 230 | 229 | 232 | 235 | 236
Lockrose Bulk | 3870-1 | Lockrose BS | Lowood | NCC Rating (A) | 703 | 703 | 703 | 703 | 703 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 199 | 200 | 202 | 202 | 203
|  |  |  | Power Factor | 0.954 | 0.954 | 0.953 | 0.953 | 0.953
|  |  |  | ECC Rating (A) | 703 | 703 | 703 | 703 | 703
|  |  |  | 50 POE Load (A) | 167 | 168 | 169 | 170 | 170
Lockrose Bulk | 3871-1 | Lowood | Wivenhoe | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 140 | 140 | 141 | 142 | 142
|  |  |  | Power Factor | 0.972 | 0.972 | 0.972 | 0.972 | 0.972
|  |  |  | ECC Rating (A) | 432 | 432 | 432 | 432 | 432
|  |  |  | 50 POE Load (A) | 115 | 116 | 117 | 117 | 117
Loganlea Bulk | 407-1 | Loganlea BS | Woodridge | NCC Rating (A) | 777 | 777 | 777 | 777 | 777 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 338 | 334 | 332 | 330 | 332
|  |  |  | Power Factor | 0.989 | 0.989 | 0.99 | 0.99 | 0.99
|  |  |  | ECC Rating (A) | 777 | 777 | 777 | 777 | 777
|  |  |  | 50 POE Load (A) | 588 | 582 | 600 | 598 | 593
Loganlea Bulk | 408-1 | Loganlea BS | Kingston | NCC Rating (A) | 529 | 529 | 529 | 529 | 529 | Urban | 280 | NA
|  |  |  | 10 POE Load (A) | 380 | 358 | 359 | 359 | 360
|  |  |  | Power Factor | 0.948 | 0.953 | 0.953 | 0.953 | 0.953
|  |  |  | ECC Rating (A) | 529 | 529 | 529 | 529 | 529
|  |  |  | 50 POE Load (A) | 611 | 571 | 573 | 574 | 574
Loganlea Bulk | 409-1 | Loganlea BS | Woodridge | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 302 | 299 | 297 | 296 | 297
|  |  |  | Power Factor | 0.99 | 0.991 | 0.991 | 0.991 | 0.991
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | 50 POE Load (A) | 590 | 584 | 603 | 600 | 595
Loganlea Bulk | 418-1 | Loganlea BS | Tanah Merah | NCC Rating (A) | 631 | 631 | 631 | 631 | 631 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 331 | 329 | 327 | 325 | 322
|  |  |  | Power Factor | 0.976 | 0.976 | 0.976 | 0.976 | 0.976
|  |  |  | ECC Rating (A) | 631 | 631 | 631 | 631 | 631
|  |  |  | 50 POE Load (A) | 286 | 284 | 283 | 281 | 279
Loganlea Bulk | 452-1 | Loganlea BS | Kingston | NCC Rating (A) | 510 | 510 | 510 | 510 | 510 | Urban | 280 | NA
|  |  |  | 10 POE Load (A) | 309 | 291 | 292 | 292 | 292
|  |  |  | Power Factor | 0.98 | 0.983 | 0.983 | 0.983 | 0.983
|  |  |  | ECC Rating (A) | 510 | 510 | 510 | 510 | 510
|  |  |  | 50 POE Load (A) | 614 | 573 | 575 | 575 | 576
Lytton Bulk | 3302-1 | Lytton BS | Fisherman Is B | NCC Rating (A) | 650 | 650 | 650 | 650 | 650 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 210 | 257 | 258 | 258 | 268
|  |  |  | Power Factor | 0.913 | 0.915 | 0.914 | 0.914 | 0.914
|  |  |  | ECC Rating (A) | 650 | 650 | 650 | 650 | 650
|  |  |  | 50 POE Load (A) | 418 | 508 | 511 | 511 | 539
Lytton Bulk | 3303-1 | Lytton BS | Fisherman Is B | NCC Rating (A) | 600 | 600 | 600 | 600 | 600 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 209 | 256 | 258 | 258 | 267
|  |  |  | Power Factor | 0.913 | 0.915 | 0.914 | 0.914 | 0.914
|  |  |  | ECC Rating (A) | 600 | 600 | 600 | 600 | 600
|  |  |  | 50 POE Load (A) | 418 | 508 | 511 | 511 | 539
Lytton Bulk | 490-1 | Lytton BS | Gibson Island | NCC Rating (A) | 628 | 628 | 628 | 628 | 628 | HighSec | 0 | NA
|  |  |  | 10 POE Load (A) | 158 | 158 | 159 | 159 | 157
|  |  |  | Power Factor | 0.978 | 0.978 | 0.978 | 0.978 | 0.978
|  |  |  | ECC Rating (A) | 628 | 628 | 628 | 628 | 628
|  |  |  | 50 POE Load (A) | 305 | 304 | 304 | 304 | 303
Lytton Bulk | 491-1 | Lytton BS | Lytton | NCC Rating (A) | 450 | 450 | 450 | 450 | 450 | HighSec | 314 | NA
|  |  |  | 10 POE Load (A) | 237 | 254 | 255 | 255 | 268
|  |  |  | Power Factor | 0.999 | 0.997 | 0.997 | 0.997 | 0.994
|  |  |  | ECC Rating (A) | 450 | 450 | 450 | 450 | 450
|  |  |  | 50 POE Load (A) | 470 | 498 | 499 | 499 | 531
Lytton Bulk | 492-1 | Lytton BS | Gibson Island | NCC Rating (A) | 463 | 463 | 463 | 463 | 463 | HighSec | 0 | NA
|  |  |  | 10 POE Load (A) | 151 | 152 | 152 | 152 | 151
|  |  |  | Power Factor | 0.996 | 0.996 | 0.996 | 0.996 | 0.996
|  |  |  | ECC Rating (A) | 463 | 463 | 463 | 463 | 463
|  |  |  | 50 POE Load (A) | 305 | 304 | 304 | 304 | 303
Lytton Bulk | 493-1 | Lytton BS | Lytton | NCC Rating (A) | 536 | 536 | 536 | 536 | 536 | HighSec | 0 | NA
|  |  |  | 10 POE Load (A) | 238 | 255 | 256 | 256 | 269
|  |  |  | Power Factor | 0.98 | 0.972 | 0.972 | 0.972 | 0.963
|  |  |  | ECC Rating (A) | 536 | 536 | 536 | 536 | 536
|  |  |  | 50 POE Load (A) | 469 | 497 | 499 | 499 | 530
Lytton Bulk | 494-1 | Fisherman Is B | Fishermans Is | NCC Rating (A) | 488 | 488 | 488 | 488 | 488 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 91 | 136 | 137 | 137 | 151
|  |  |  | Power Factor | 0.983 | 0.978 | 0.978 | 0.978 | 0.977
|  |  |  | ECC Rating (A) | 488 | 488 | 488 | 488 | 488
|  |  |  | 50 POE Load (A) | 179 | 270 | 268 | 268 | 295
Lytton Bulk | 495-1 | Fisherman Is B | Fisherman Is | NCC Rating (A) | 600 | 600 | 600 | 600 | 600 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 92 | 138 | 139 | 139 | 153
|  |  |  | Power Factor | 0.915 | 0.909 | 0.909 | 0.909 | 0.907
|  |  |  | ECC Rating (A) | 600 | 600 | 600 | 600 | 600
|  |  |  | 50 POE Load (A) | 178 | 269 | 267 | 267 | 294
Lytton Bulk | 560-1 | Lytton BS | 560 Tee1 | NCC Rating (A) | 527 | 527 | 527 | 527 | 527 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 198 | 178 | 178 | 178 | 177
|  |  |  | Power Factor | 0.96 | 0.986 | 0.986 | 0.986 | 0.986
|  |  |  | ECC Rating (A) | 527 | 527 | 527 | 527 | 527
|  |  |  | 50 POE Load (A) | 487 | 486 | 486 | 484 | 481
Lytton Bulk | 560-14 | 560 Tee1 | 560 Tee2 | NCC Rating (A) | 367 | 367 | 367 | 367 | 367 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 82 | 74 | 74 | 73 | 73
|  |  |  | Power Factor | 0.96 | 0.986 | 0.986 | 0.986 | 0.986
|  |  |  | ECC Rating (A) | 367 | 367 | 367 | 367 | 367
|  |  |  | 50 POE Load (A) | 201 | 200 | 200 | 200 | 198
Lytton Bulk | 560-15 | 560 Tee1 | 560 Tee2 | NCC Rating (A) | 351 | 351 | 351 | 351 | 351 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 117 | 105 | 105 | 105 | 104
|  |  |  | Power Factor | 0.937 | 0.969 | 0.969 | 0.969 | 0.969
|  |  |  | ECC Rating (A) | 351 | 351 | 351 | 351 | 351
|  |  |  | 50 POE Load (A) | 287 | 286 | 286 | 284 | 283
Lytton Bulk | 560-16 | Lota | 560 Tee1 | NCC Rating (A) | 983 | 983 | 983 | 983 | 983 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 202 | 180 | 181 | 180 | 179
|  |  |  | Power Factor | 0.946 | 0.976 | 0.976 | 0.976 | 0.976
|  |  |  | ECC Rating (A) | 983 | 983 | 983 | 983 | 983
|  |  |  | 50 POE Load (A) | 490 | 488 | 488 | 486 | 484
Lytton Bulk | 560-2 | 560 Tee1 | Tingalpa | NCC Rating (A) | 600 | 600 | 600 | 600 | 600 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 600 | 600 | 600 | 600 | 600
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Lytton Bulk | 560-3 | 560 Tee1 | 560 Tee2 | NCC Rating (A) | 600 | 600 | 600 | 600 | 600 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 198 | 178 | 179 | 178 | 177
|  |  |  | Power Factor | 0.963 | 0.987 | 0.987 | 0.988 | 0.988
|  |  |  | ECC Rating (A) | 600 | 600 | 600 | 600 | 600
|  |  |  | 50 POE Load (A) | 487 | 486 | 486 | 484 | 481
Lytton Bulk | 560-5 | Lota | 560 Tee2 | NCC Rating (A) | 704 | 704 | 704 | 704 | 704 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 117 | 105 | 105 | 104 | 104
|  |  |  | Power Factor | 0.963 | 0.988 | 0.988 | 0.988 | 0.988
|  |  |  | ECC Rating (A) | 704 | 704 | 704 | 704 | 704
|  |  |  | 50 POE Load (A) | 287 | 286 | 286 | 284 | 283
Lytton Bulk | 569-1 | Lytton BS | Lota | NCC Rating (A) | 490 | 582 | 582 | 582 | 582 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 353 | 367 | 368 | 366 | 364
|  |  |  | Power Factor | 0.973 | 0.959 | 0.959 | 0.959 | 0.959
|  |  |  | ECC Rating (A) | 490 | 582 | 582 | 582 | 582
|  |  |  | 50 POE Load (A) | 474 | 467 | 467 | 465 | 462
Lytton Bulk | 599-1 | Hemmant | Lindum | NCC Rating (A) | 443 | 443 | 443 | 443 | 443 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 443 | 443 | 443 | 443 | 443
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Lytton Bulk | 681-1 | Lindum | Wynnum | NCC Rating (A) | 661 | 661 | 661 | 661 | 661 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 213 | 213 | 215 | 215 | 215
|  |  |  | Power Factor | 0.961 | 0.961 | 0.961 | 0.961 | 0.961
|  |  |  | ECC Rating (A) | 790 | 790 | 790 | 790 | 790
|  |  |  | 50 POE Load (A) | 381 | 382 | 384 | 385 | 385
Lytton Bulk | 682-1 | Lindum | Wynnum | NCC Rating (A) | 661 | 661 | 661 | 661 | 661 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 204 | 205 | 206 | 206 | 206
|  |  |  | Power Factor | 0.961 | 0.961 | 0.961 | 0.961 | 0.961
|  |  |  | ECC Rating (A) | 790 | 790 | 790 | 790 | 790
|  |  |  | 50 POE Load (A) | 382 | 383 | 385 | 386 | 386
Lytton Bulk | 687-1 | Lytton BS | 687 Tee1 | NCC Rating (A) | 758 | 758 | 758 | 758 | 758 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 151 | 151 | 152 | 152 | 152
|  |  |  | Power Factor | 0.987 | 0.987 | 0.987 | 0.987 | 0.987
|  |  |  | ECC Rating (A) | 758 | 758 | 758 | 758 | 758
|  |  |  | 50 POE Load (A) | 366 | 367 | 370 | 370 | 370
Lytton Bulk | 687-2 | 687 Tee1 | Lytton | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Lytton Bulk | 687-3 | 687 Tee1 | Lindum | NCC Rating (A) | 636 | 636 | 636 | 636 | 636 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 151 | 152 | 153 | 153 | 153
|  |  |  | Power Factor | 0.984 | 0.984 | 0.984 | 0.984 | 0.984
|  |  |  | ECC Rating (A) | 636 | 636 | 636 | 636 | 636
|  |  |  | 50 POE Load (A) | 367 | 368 | 370 | 371 | 371
Lytton Bulk | 688-1 | Lytton BS | Lindum | NCC Rating (A) | 636 | 636 | 636 | 636 | 636 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 263 | 264 | 265 | 266 | 266
|  |  |  | Power Factor | 0.957 | 0.956 | 0.956 | 0.956 | 0.956
|  |  |  | ECC Rating (A) | 636 | 636 | 636 | 636 | 636
|  |  |  | 50 POE Load (A) | 366 | 367 | 369 | 370 | 370
Meeandah Bulk | 3374-1 | Whinstanes | Hamilton Lands | NCC Rating (A) | 476 | 700 | 700 | 700 | 700 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 114 | 87 | 88 | 87 | 87
|  |  |  | Power Factor | 0.938 | 0.915 | 0.915 | 0.915 | 0.915
|  |  |  | ECC Rating (A) | 476 | 700 | 700 | 700 | 700
|  |  |  | 50 POE Load (A) | 245 | 247 | 247 | 246 | 245
Meeandah Bulk | 506-1 | Meeandah BS | Hamilton Lands | NCC Rating (A) | 720 | 720 | 720 | 720 | 720 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 213 | 199 | 200 | 200 | 199
|  |  |  | Power Factor | 0.973 | 0.976 | 0.976 | 0.976 | 0.976
|  |  |  | ECC Rating (A) | 787 | 787 | 787 | 787 | 787
|  |  |  | 50 POE Load (A) | 343 | 334 | 333 | 333 | 333
Meeandah Bulk | 513-1 | Meeandah BS | Hamilton Lands | NCC Rating (A) | 720 | 720 | 720 | 720 | 720 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 211 | 198 | 198 | 198 | 198
|  |  |  | Power Factor | 0.973 | 0.976 | 0.976 | 0.976 | 0.976
|  |  |  | ECC Rating (A) | 787 | 787 | 787 | 787 | 787
|  |  |  | 50 POE Load (A) | 342 | 333 | 332 | 333 | 332
Meeandah Bulk | 556-1 | Meeandah BS | Whinstanes | NCC Rating (A) | 704 | 704 | 704 | 704 | 704 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 137 | 164 | 164 | 164 | 164
|  |  |  | Power Factor | 0.948 | 0.948 | 0.947 | 0.947 | 0.948
|  |  |  | ECC Rating (A) | 704 | 704 | 704 | 704 | 704
|  |  |  | 50 POE Load (A) | 246 | 247 | 247 | 246 | 245
Meeandah Bulk | 609-1 | Meeandah BS | Myrtletown | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Meeandah Bulk | 610-1 | Meeandah BS | Myrtletown | NCC Rating (A) | 748 | 748 | 748 | 748 | 748 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 748 | 748 | 748 | 748 | 748
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Molendinar Bulk | 3670-1 | Molendinar BS | Parkwood | NCC Rating (A) | 710 | 710 | 710 | 710 | 710 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 366 | 367 | 383 | 384 | 399
|  |  |  | Power Factor | 0.968 | 0.968 | 0.967 | 0.966 | 0.965
|  |  |  | ECC Rating (A) | 710 | 710 | 710 | 710 | 710
|  |  |  | 50 POE Load (A) | 565 | 567 | 587 | 589 | 607
Molendinar Bulk | 3671-1 | Molendinar BS | Parkwood | NCC Rating (A) | 708 | 708 | 708 | 708 | 708 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 291 | 292 | 304 | 305 | 317
|  |  |  | Power Factor | 0.976 | 0.976 | 0.975 | 0.975 | 0.974
|  |  |  | ECC Rating (A) | 708 | 708 | 708 | 708 | 708
|  |  |  | 50 POE Load (A) | 456 | 457 | 478 | 480 | 500
Molendinar Bulk | 389-1 | Parkwood | 389 Tee1 | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 358 | 360 | 357 | 359 | 353
|  |  |  | Power Factor | 0.976 | 0.976 | 0.976 | 0.975 | 0.976
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | 50 POE Load (A) | 736 | 740 | 743 | 747 | 746
Molendinar Bulk | 389-2 | F389 Tee1 | Labrador | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 256 | 259 | 261 | 265 | 266
|  |  |  | Power Factor | 0.93 | 0.93 | 0.93 | 0.929 | 0.929
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | 50 POE Load (A) | 411 | 414 | 420 | 424 | 427
Molendinar Bulk | 389-3 | F389 Tee1 | Hollywell | NCC Rating (A) | 631 | 631 | 631 | 631 | 631 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 113 | 112 | 107 | 106 | 100
|  |  |  | Power Factor | 0.99 | 0.989 | 0.985 | 0.984 | 0.977
|  |  |  | ECC Rating (A) | 717 | 717 | 717 | 717 | 717
|  |  |  | 50 POE Load (A) | 640 | 642 | 645 | 646 | 647
Molendinar Bulk | 390-1 | Molendinar BS | F390 Tee1 | NCC Rating (A) | 637 | 637 | 637 | 637 | 637 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 141 | 140 | 140 | 140 | 139
|  |  |  | Power Factor | 0.995 | 0.995 | 0.995 | 0.995 | 0.995
|  |  |  | ECC Rating (A) | 637 | 637 | 637 | 637 | 637
|  |  |  | 50 POE Load (A) | 531 | 533 | 538 | 541 | 542
Molendinar Bulk | 390-2 | F390 Tee | Bundall | NCC Rating (A) | 653 | 653 | 653 | 653 | 653 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 141 | 140 | 140 | 140 | 139
|  |  |  | Power Factor | 0.994 | 0.994 | 0.994 | 0.994 | 0.994
|  |  |  | ECC Rating (A) | 653 | 653 | 653 | 653 | 653
|  |  |  | 50 POE Load (A) | 307 | 305 | 304 | 304 | 303
Molendinar Bulk | 390-3 | F390 Tee | Miami | NCC Rating (A) | 529 | 529 | 529 | 529 | 529 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 529 | 529 | 529 | 529 | 529
|  |  |  | 50 POE Load (A) | 476 | 480 | 485 | 489 | 491
Molendinar Bulk | 391-1 | Molendinar BS | Bundall | NCC Rating (A) | 623 | 623 | 623 | 623 | 623 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 175 | 174 | 174 | 174 | 173
|  |  |  | Power Factor | 0.985 | 0.985 | 0.985 | 0.985 | 0.985
|  |  |  | ECC Rating (A) | 623 | 623 | 623 | 623 | 623
|  |  |  | 50 POE Load (A) | 299 | 297 | 296 | 296 | 294
Molendinar Bulk | 392-1 | Molendinar BS | Gaven | NCC Rating (A) | 708 | 708 | 708 | 708 | 708 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 276 | 275 | 275 | 274 | 273
|  |  |  | Power Factor | 0.989 | 0.989 | 0.989 | 0.989 | 0.99
|  |  |  | ECC Rating (A) | 708 | 708 | 708 | 708 | 708
|  |  |  | 50 POE Load (A) | 498 | 496 | 496 | 494 | 492
Molendinar Bulk | 421-1 | Molendinar BS | Arundel | NCC Rating (A) | 673 | 673 | 673 | 673 | 673 | Urban | 553 | NA
|  |  |  | 10 POE Load (A) | 498 | 497 | 504 | 505 | 509
|  |  |  | Power Factor | 0.977 | 0.978 | 0.977 | 0.977 | 0.976
|  |  |  | ECC Rating (A) | 721 | 721 | 721 | 721 | 721
|  |  |  | 50 POE Load (A) | 796 | 796 | 807 | 808 | 815
Molendinar Bulk | 458-1 | Molendinar BS | Labrador | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 205 | 206 | 210 | 211 | 214
|  |  |  | Power Factor | 0.971 | 0.971 | 0.97 | 0.97 | 0.97
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | 50 POE Load (A) | 422 | 426 | 432 | 436 | 440
Molendinar Bulk | 473-1 | Molendinar BS | Gaven | NCC Rating (A) | 717 | 717 | 717 | 717 | 717 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 277 | 276 | 276 | 275 | 274
|  |  |  | Power Factor | 0.989 | 0.989 | 0.989 | 0.989 | 0.99
|  |  |  | ECC Rating (A) | 717 | 717 | 717 | 717 | 717
|  |  |  | 50 POE Load (A) | 498 | 497 | 496 | 495 | 492
Molendinar Bulk | 474A-1 | Arundel | Hollywell | NCC Rating (A) | 631 | 631 | 631 | 631 | 631 | Urban | 517 | NA
|  |  |  | 10 POE Load (A) | 606 | 609 | 619 | 622 | 630
|  |  |  | Power Factor | 0.974 | 0.974 | 0.973 | 0.973 | 0.973
|  |  |  | ECC Rating (A) | 631 | 631 | 631 | 631 | 631
|  |  |  | 50 POE Load (A) | 730 | 734 | 747 | 751 | 761
Molendinar Bulk | 474B-1 | Hope Is | Hollywell | NCC Rating (A) | 786 | 786 | 786 | 786 | 786 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 786 | 786 | 786 | 786 | 786
|  |  |  | 50 POE Load (A) | 324 | 328 | 332 | 335 | 338
Molendinar Bulk | 486-1 | Molendinar BS | Arundel | NCC Rating (A) | 673 | 673 | 673 | 673 | 673 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 498 | 498 | 504 | 506 | 509
|  |  |  | Power Factor | 0.977 | 0.977 | 0.977 | 0.977 | 0.976
|  |  |  | ECC Rating (A) | 721 | 721 | 721 | 721 | 721
|  |  |  | 50 POE Load (A) | 797 | 796 | 807 | 809 | 815
Mudgeeraba Bulk | 3700-1 | Mudgeeraba BS | 3700 Tee1 | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 250 | 252 | 254 | 254 | 255
|  |  |  | Power Factor | 0.964 | 0.963 | 0.963 | 0.963 | 0.963
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 440 | 442 | 446 | 447 | 448
Mudgeeraba Bulk | 3700-2 | 3700 Tee1 | 3701 Tee1 | NCC Rating (A) | 723 | 723 | 723 | 723 | 723 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 723 | 723 | 723 | 723 | 723
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Mudgeeraba Bulk | 3700-3 | 3700 Tee1 | 3700 Tee2 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 250 | 252 | 254 | 255 | 255
|  |  |  | Power Factor | 0.964 | 0.964 | 0.963 | 0.963 | 0.963
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 440 | 443 | 446 | 447 | 448
Mudgeeraba Bulk | 3700-4 | 3700 Tee2 | 3702 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Mudgeeraba Bulk | 3700-5 | 3700 Tee2 | Mudgeeraba Pkg | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 250 | 252 | 254 | 255 | 255
|  |  |  | Power Factor | 0.966 | 0.966 | 0.966 | 0.966 | 0.966
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 440 | 443 | 446 | 447 | 448
Mudgeeraba Bulk | 3701-1 | Mudgeeraba | Mudgeeraba Pkg | NCC Rating (A) | 529 | 529 | 529 | 529 | 529 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 273 | 274 | 276 | 277 | 278
|  |  |  | Power Factor | 0.924 | 0.924 | 0.923 | 0.923 | 0.923
|  |  |  | ECC Rating (A) | 529 | 529 | 529 | 529 | 529
|  |  |  | 50 POE Load (A) | 439 | 441 | 444 | 446 | 447
Nambour Bulk | 307-1 | Nambour BS | 307 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 86 | 86 | 87 | 88 | 88
|  |  |  | Power Factor | 0.938 | 0.938 | 0.938 | 0.938 | 0.937
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 415 | 416 | 420 | 420 | 421
Nambour Bulk | 307-2 | 307 Tee1 | Yandina | NCC Rating (A) | 755 | 755 | 755 | 755 | 755 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 87 | 87 | 88 | 89 | 89
|  |  |  | Power Factor | 0.932 | 0.932 | 0.932 | 0.932 | 0.932
|  |  |  | ECC Rating (A) | 755 | 755 | 755 | 755 | 755
|  |  |  | 50 POE Load (A) | 148 | 149 | 151 | 151 | 152
Nambour Bulk | 344-1 | Nambour BS | Maleny | NCC Rating (A) | 155 | 155 | 155 | 155 | 200 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 130 | 130 | 130 | 129 | 124
|  |  |  | Power Factor | 0.99 | 0.99 | 0.99 | 0.99 | 0.991
|  |  |  | ECC Rating (A) | 155 | 155 | 155 | 155 | 200
|  |  |  | 50 POE Load (A) | 122 | 122 | 122 | 121 | 116
Nambour Bulk | 345-1 | Nambour BS | Kenilworth | NCC Rating (A) | 208 | 208 | 208 | 208 | 208 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 87 | 87 | 86 | 86 | 85
|  |  |  | Power Factor | 0.984 | 0.985 | 0.985 | 0.985 | 0.985
|  |  |  | ECC Rating (A) | 208 | 208 | 208 | 208 | 208
|  |  |  | 50 POE Load (A) | 79 | 78 | 78 | 77 | 77
Nambour Bulk | 347-1 | Nambour BS | 347 Tee1 | NCC Rating (A) | 412 | 412 | 412 | 412 | 412 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 188 | 190 | 192 | 193 | 194
|  |  |  | Power Factor | 0.954 | 0.954 | 0.954 | 0.953 | 0.953
|  |  |  | ECC Rating (A) | 412 | 412 | 412 | 412 | 412
|  |  |  | 50 POE Load (A) | 388 | 392 | 396 | 398 | 400
Nambour Bulk | 347-2 | 347 Tee1 | Palmwoods Central | NCC Rating (A) | 357 | 357 | 357 | 357 | 357 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 189 | 190 | 192 | 193 | 194
|  |  |  | Power Factor | 0.958 | 0.958 | 0.958 | 0.958 | 0.958
|  |  |  | ECC Rating (A) | 357 | 357 | 357 | 357 | 357
|  |  |  | 50 POE Load (A) | 389 | 392 | 396 | 399 | 401
Nambour Bulk | 347-3 | 347 Tee1 | Landsborough | NCC Rating (A) | 403 | 403 | 403 | 403 | 403 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 403 | 403 | 403 | 403 | 403
|  |  |  | 50 POE Load (A) | 256 | 281 | 293 | 303 | 313
Nambour Bulk | 348-1 | Nambour BS | Palmwoods Central | NCC Rating (A) | 403 | 403 | 403 | 403 | 403 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 241 | 243 | 246 | 247 | 248
|  |  |  | Power Factor | 0.944 | 0.943 | 0.943 | 0.942 | 0.942
|  |  |  | ECC Rating (A) | 403 | 403 | 403 | 403 | 403
|  |  |  | 50 POE Load (A) | 379 | 382 | 386 | 388 | 390
Nambour Bulk | 489-1 | Nambour BS | Yandina | NCC Rating (A) | 293 | 293 | 293 | 293 | 293 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 78 | 79 | 80 | 80 | 81
|  |  |  | Power Factor | 1 | 1 | 1 | 1 | 1
|  |  |  | ECC Rating (A) | 293 | 293 | 293 | 293 | 293
|  |  |  | 50 POE Load (A) | 195 | 196 | 197 | 198 | 198
Nudgee Bulk | 3280-1 | Hendra | Clayfield | NCC Rating (A) | 0 | 725 | 725 | 725 | 725 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 6 | 6 | 6 | 6
|  |  |  | Power Factor | 0 | 1 | 1 | 1 | 1
|  |  |  | ECC Rating (A) | 0 | 725 | 725 | 725 | 725
|  |  |  | 50 POE Load (A) | 0 | 6 | 6 | 6 | 6
Nudgee Bulk | 535-1 | Hendra | Nundah | NCC Rating (A) | 285 | 0 | 0 | 0 | 0 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 95 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 1 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 285 | 0 | 0 | 0 | 0
|  |  |  | 50 POE Load (A) | 193 | 0 | 0 | 0 | 0
Nudgee Bulk | 540-1 | Hendra | Nundah | NCC Rating (A) | 285 | 704 | 704 | 704 | 704 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 95 | 254 | 255 | 256 | 256
|  |  |  | Power Factor | 1 | 0.979 | 0.979 | 0.978 | 0.978
|  |  |  | ECC Rating (A) | 285 | 704 | 704 | 704 | 704
|  |  |  | 50 POE Load (A) | 193 | 406 | 408 | 408 | 408
Nudgee Bulk | 593-1 | Nudgee BS | Nundah | NCC Rating (A) | 696 | 696 | 696 | 696 | 696 | Urban | 192 | NA
|  |  |  | 10 POE Load (A) | 589 | 662 | 663 | 663 | 661
|  |  |  | Power Factor | 0.983 | 0.971 | 0.971 | 0.971 | 0.971
|  |  |  | ECC Rating (A) | 696 | 696 | 696 | 696 | 696
|  |  |  | 50 POE Load (A) | 676 | 771 | 772 | 772 | 770
Nudgee Bulk | 604-1 | Nudgee BS | Geebung | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 198 | 196 | 194 | 193 | 197
|  |  |  | Power Factor | 0.996 | 0.996 | 0.996 | 0.997 | 0.99
|  |  |  | ECC Rating (A) | 491 | 491 | 491 | 491 | 491
|  |  |  | 50 POE Load (A) | 293 | 289 | 286 | 284 | 282
Nudgee Bulk | 605-1 | Nudgee BS | Geebung | NCC Rating (A) | 432 | 432 | 432 | 432 | 432 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 199 | 196 | 194 | 193 | 198
|  |  |  | Power Factor | 0.996 | 0.996 | 0.997 | 0.997 | 0.99
|  |  |  | ECC Rating (A) | 491 | 491 | 491 | 491 | 491
|  |  |  | 50 POE Load (A) | 293 | 289 | 286 | 284 | 282
Nudgee Bulk | 622-1 | Nudgee BS | Hendra | NCC Rating (A) | 738 | 738 | 738 | 738 | 738 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 313 | 466 | 468 | 469 | 469
|  |  |  | Power Factor | 0.938 | 0.957 | 0.957 | 0.957 | 0.957
|  |  |  | ECC Rating (A) | 738 | 738 | 738 | 738 | 738
|  |  |  | 50 POE Load (A) | 533 | 699 | 701 | 701 | 699
Nudgee Bulk | 623-1 | Nudgee BS | Hendra | NCC Rating (A) | 738 | 738 | 738 | 738 | 738 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 313 | 466 | 468 | 469 | 469
|  |  |  | Power Factor | 0.938 | 0.957 | 0.957 | 0.957 | 0.957
|  |  |  | ECC Rating (A) | 738 | 738 | 738 | 738 | 738
|  |  |  | 50 POE Load (A) | 533 | 699 | 701 | 701 | 699
Nudgee Bulk | 636-1 | Hendra | Clayfield | NCC Rating (A) | 302 | 725 | 725 | 725 | 725 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 379 | 381 | 382 | 381
|  |  |  | Power Factor | 0 | 0.948 | 0.947 | 0.947 | 0.947
|  |  |  | ECC Rating (A) | 302 | 725 | 725 | 725 | 725
|  |  |  | 50 POE Load (A) | 161 | 336 | 337 | 337 | 336
Nudgee Bulk | 643-1 | Hendra | Hamilton | NCC Rating (A) | 711 | 711 | 711 | 711 | 711 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 212 | 214 | 216 | 217 | 217
|  |  |  | Power Factor | 0.963 | 0.963 | 0.963 | 0.963 | 0.963
|  |  |  | ECC Rating (A) | 760 | 760 | 760 | 760 | 760
|  |  |  | 50 POE Load (A) | 382 | 385 | 387 | 389 | 390
Nudgee Bulk | 674-1 | Hendra | Hamilton | NCC Rating (A) | 711 | 711 | 711 | 711 | 711 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 212 | 214 | 215 | 216 | 217
|  |  |  | Power Factor | 0.963 | 0.963 | 0.963 | 0.963 | 0.963
|  |  |  | ECC Rating (A) | 760 | 760 | 760 | 760 | 760
|  |  |  | 50 POE Load (A) | 382 | 385 | 388 | 390 | 390
Nudgee Bulk | 683-1 | Nudgee BS | Geebung | NCC Rating (A) | 478 | 478 | 478 | 478 | 478 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 195 | 192 | 190 | 189 | 193
|  |  |  | Power Factor | 0.992 | 0.992 | 0.993 | 0.993 | 0.985
|  |  |  | ECC Rating (A) | 478 | 478 | 478 | 478 | 478
|  |  |  | 50 POE Load (A) | 287 | 283 | 280 | 278 | 276
Nudgee Bulk | 684-1 | Nudgee BS | Geebung | NCC Rating (A) | 525 | 525 | 525 | 525 | 525 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 525 | 525 | 525 | 525 | 525
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Postmans Ridge Bulk | 376-1 | Postmans Ridge BS | Helidon | NCC Rating (A) | 290 | 290 | 290 | 290 | 290 | Rural | 170 | 6
|  |  |  | 10 POE Load (A) | 56 | 56 | 56 | 56 | 56
|  |  |  | Power Factor | 0.962 | 0.962 | 0.962 | 0.962 | 0.962
|  |  |  | ECC Rating (A) | 290 | 290 | 290 | 290 | 290
|  |  |  | 50 POE Load (A) | 49 | 49 | 50 | 50 | 50
Postmans Ridge Bulk | 379-1 | Postmans Ridge BS | Carpendale | NCC Rating (A) | 200 | 200 | 200 | 200 | 200 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 31 | 31 | 32 | 32 | 32
|  |  |  | Power Factor | 0.996 | 0.996 | 0.996 | 0.996 | 0.996
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | 50 POE Load (A) | 27 | 27 | 28 | 28 | 28
Postmans Ridge Bulk | 379-2 | Carpendale | Tenthill | NCC Rating (A) | 155 | 155 | 155 | 155 | 155 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 155 | 155 | 155 | 155 | 155
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Raceview Bulk | 354-1 | Raceview BS | Roderick St | NCC Rating (A) | 497 | 497 | 497 | 497 | 497 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 323 | 322 | 323 | 324 | 324
|  |  |  | Power Factor | 0.991 | 0.991 | 0.991 | 0.991 | 0.991
|  |  |  | ECC Rating (A) | 517 | 517 | 517 | 517 | 517
|  |  |  | 50 POE Load (A) | 449 | 447 | 448 | 449 | 449
Raceview Bulk | 355-1 | Roderick St | Booval | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 169 | 167 | 168 | 168 | 168
|  |  |  | Power Factor | 0.992 | 0.992 | 0.992 | 0.992 | 0.992
|  |  |  | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
|  |  |  | 50 POE Load (A) | 453 | 451 | 452 | 453 | 453
Raceview Bulk | 361-1 | Raceview BS | Booval | NCC Rating (A) | 631 | 631 | 631 | 631 | 631 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 369 | 369 | 370 | 371 | 371
|  |  |  | Power Factor | 0.988 | 0.988 | 0.988 | 0.988 | 0.988
|  |  |  | ECC Rating (A) | 631 | 631 | 631 | 631 | 631
|  |  |  | 50 POE Load (A) | 545 | 545 | 547 | 548 | 548
Raceview Bulk | 362-1 | Raceview BS | 362 Tee1 | NCC Rating (A) | 357 | 357 | 357 | 357 | 357 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 156 | 157 | 158 | 158 | 159
|  |  |  | Power Factor | 0.982 | 0.982 | 0.982 | 0.982 | 0.982
|  |  |  | ECC Rating (A) | 357 | 357 | 357 | 357 | 357
|  |  |  | 50 POE Load (A) | 340 | 366 | 376 | 384 | 391
Raceview Bulk | 362-2 | 362 Tee1 | Flinders | NCC Rating (A) | 708 | 708 | 708 | 708 | 708 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 50 | 49 | 48 | 48 | 47
|  |  |  | Power Factor | 0.652 | 0.637 | 0.629 | 0.622 | 0.615
|  |  |  | ECC Rating (A) | 708 | 708 | 708 | 708 | 708
|  |  |  | 50 POE Load (A) | 171 | 195 | 203 | 211 | 218
Raceview Bulk | 362-3 | 362 Tee1 | Kalbar | NCC Rating (A) | 708 | 708 | 708 | 708 | 708 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 193 | 192 | 193 | 193 | 192
|  |  |  | Power Factor | 0.954 | 0.955 | 0.954 | 0.954 | 0.954
|  |  |  | ECC Rating (A) | 708 | 708 | 708 | 708 | 708
|  |  |  | 50 POE Load (A) | 306 | 305 | 306 | 306 | 305
Raceview Bulk | 363-1 | Raceview BS | 363 Tee1 | NCC Rating (A) | 351 | 351 | 351 | 351 | 351 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 153 | 154 | 155 | 156 | 156
|  |  |  | Power Factor | 0.987 | 0.987 | 0.987 | 0.987 | 0.987
|  |  |  | ECC Rating (A) | 351 | 351 | 351 | 351 | 351
|  |  |  | 50 POE Load (A) | 323 | 347 | 356 | 364 | 370
Raceview Bulk | 363-2 | 363 Tee1 | Flinders | NCC Rating (A) | 403 | 403 | 403 | 403 | 403 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 12 | 12 | 12 | 12 | 11
|  |  |  | Power Factor | 0.842 | 0.804 | 0.783 | 0.76 | 0.731
|  |  |  | ECC Rating (A) | 403 | 403 | 403 | 403 | 403
|  |  |  | 50 POE Load (A) | 174 | 196 | 203 | 210 | 217
Raceview Bulk | 363-3 | 363 Tee1 | Kalbar | NCC Rating (A) | 374 | 374 | 374 | 374 | 374 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 160 | 160 | 160 | 160 | 160
|  |  |  | Power Factor | 0.999 | 0.999 | 0.999 | 0.999 | 0.999
|  |  |  | ECC Rating (A) | 374 | 374 | 374 | 374 | 374
|  |  |  | 50 POE Load (A) | 325 | 325 | 326 | 325 | 324
Raceview Bulk | 3960-1 | Ipswich Sth | Yamanto | NCC Rating (A) | 711 | 711 | 711 | 711 | 711 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 398 | 428 | 440 | 450 | 458
|  |  |  | Power Factor | 0.942 | 0.941 | 0.94 | 0.939 | 0.939
|  |  |  | ECC Rating (A) | 711 | 711 | 711 | 711 | 711
|  |  |  | 50 POE Load (A) | 416 | 445 | 455 | 463 | 469
Raceview Bulk | 3972-1 | Yamanto | Flinders | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 156 | 154 | 154 | 153 | 152
|  |  |  | Power Factor | 0.894 | 0.892 | 0.891 | 0.89 | 0.89
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 242 | 286 | 300 | 314 | 326
Raceview Bulk | 3980-1 | Kalbar | Boonah | NCC Rating (A) | 713 | 713 | 713 | 713 | 713 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 93 | 93 | 93 | 93 | 92
|  |  |  | Power Factor | 0.975 | 0.975 | 0.975 | 0.975 | 0.975
|  |  |  | ECC Rating (A) | 713 | 713 | 713 | 713 | 713
|  |  |  | 50 POE Load (A) | 145 | 145 | 144 | 144 | 144
Raceview Bulk | 401-1 | Kalbar | Boonah | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 90 | 89 | 89 | 89 | 89
|  |  |  | Power Factor | 0.982 | 0.982 | 0.982 | 0.982 | 0.982
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | 50 POE Load (A) | 146 | 145 | 145 | 145 | 145
Raceview Bulk | 411-1 | Raceview BS | Booval | NCC Rating (A) | 558 | 558 | 558 | 558 | 558 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 312 | 312 | 313 | 314 | 314
|  |  |  | Power Factor | 0.994 | 0.994 | 0.994 | 0.994 | 0.994
|  |  |  | ECC Rating (A) | 631 | 631 | 631 | 631 | 631
|  |  |  | 50 POE Load (A) | 530 | 530 | 531 | 533 | 532
Raceview Bulk | 509A-1 | Raceview BS | Ipswich Sth | NCC Rating (A) | 721 | 721 | 721 | 721 | 721 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 424 | 444 | 457 | 468 | 478
|  |  |  | Power Factor | 0.962 | 0.96 | 0.959 | 0.958 | 0.958
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 675 | 711 | 731 | 748 | 763
Raceview Bulk | 509B-1 | Raceview BS | Cooneana | NCC Rating (A) | 455 | 455 | 455 | 455 | 455 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 455 | 455 | 455 | 455 | 455
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Raceview Bulk | 510A-1 | Raceview BS | Ipswich Sth | NCC Rating (A) | 721 | 721 | 721 | 721 | 721 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 419 | 440 | 452 | 463 | 473
|  |  |  | Power Factor | 0.962 | 0.96 | 0.959 | 0.958 | 0.958
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 675 | 711 | 731 | 748 | 763
Raceview Bulk | 510B-1 | Raceview BS | Cooneana | NCC Rating (A) | 426 | 426 | 426 | 426 | 426 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 426 | 426 | 426 | 426 | 426
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Richlands Bulk | 3818-1 | Richlands BS | Wacol | NCC Rating (A) | 750 | 750 | 750 | 750 | 750 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 126 | 125 | 124 | 123 | 122
|  |  |  | Power Factor | 0.99 | 0.991 | 0.991 | 0.991 | 0.991
|  |  |  | ECC Rating (A) | 750 | 750 | 750 | 750 | 750
|  |  |  | 50 POE Load (A) | 245 | 242 | 240 | 239 | 238
Richlands Bulk | 454-1 | Richlands BS | Wacol Sth | NCC Rating (A) | 430 | 430 | 430 | 430 | 430 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 194 | 192 | 191 | 191 | 190
|  |  |  | Power Factor | 0.969 | 0.969 | 0.969 | 0.969 | 0.969
|  |  |  | ECC Rating (A) | 460 | 460 | 460 | 460 | 460
|  |  |  | 50 POE Load (A) | 372 | 369 | 367 | 367 | 365
Richlands Bulk | 455-1 | Richlands BS | Wacol Sth | NCC Rating (A) | 430 | 430 | 430 | 430 | 430 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 195 | 193 | 192 | 192 | 191
|  |  |  | Power Factor | 0.969 | 0.969 | 0.969 | 0.969 | 0.969
|  |  |  | ECC Rating (A) | 460 | 460 | 460 | 460 | 460
|  |  |  | 50 POE Load (A) | 372 | 369 | 367 | 367 | 364
Richlands Bulk | 543-1 | Inala | 543 Tee1 | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 563 | 562 | 563 | 563 | 560
Richlands Bulk | 543-2 | 543 Tee1 | Coopers Plains | NCC Rating (A) | 348 | 348 | 348 | 348 | 348 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 348 | 348 | 348 | 348 | 348
|  |  |  | 50 POE Load (A) | 367 | 290 | 276 | 270 | 265
Richlands Bulk | 543-3 | 543 Tee1 | Heathwood | NCC Rating (A) | 807 | 807 | 807 | 807 | 807 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 807 | 807 | 807 | 807 | 807
|  |  |  | 50 POE Load (A) | 563 | 563 | 564 | 563 | 561
Richlands Bulk | 616-1 | Richlands BS | Darra | NCC Rating (A) | 407 | 407 | 407 | 407 | 407 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 246 | 242 | 240 | 239 | 237
|  |  |  | Power Factor | 0.909 | 0.902 | 0.925 | 0.923 | 0.92
|  |  |  | ECC Rating (A) | 440 | 440 | 440 | 440 | 440
|  |  |  | 50 POE Load (A) | 361 | 356 | 353 | 351 | 349
Richlands Bulk | 617-1 | Richlands BS | Darra | NCC Rating (A) | 407 | 407 | 407 | 407 | 407 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 254 | 250 | 248 | 246 | 245
|  |  |  | Power Factor | 0.909 | 0.903 | 0.925 | 0.923 | 0.92
|  |  |  | ECC Rating (A) | 440 | 440 | 440 | 440 | 440
|  |  |  | 50 POE Load (A) | 366 | 361 | 358 | 356 | 354
Richlands Bulk | 618-1 | Richlands BS | Inala | NCC Rating (A) | 818 | 818 | 818 | 818 | 818 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 355 | 356 | 359 | 360 | 360
|  |  |  | Power Factor | 0.989 | 0.989 | 0.989 | 0.989 | 0.989
|  |  |  | ECC Rating (A) | 818 | 818 | 818 | 818 | 818
|  |  |  | 50 POE Load (A) | 668 | 669 | 671 | 672 | 670
Richlands Bulk | 619-1 | Richlands BS | Inala | NCC Rating (A) | 550 | 550 | 550 | 550 | 550 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 230 | 230 | 232 | 233 | 233
|  |  |  | Power Factor | 0.99 | 0.99 | 0.989 | 0.989 | 0.989
|  |  |  | ECC Rating (A) | 550 | 550 | 550 | 550 | 550
|  |  |  | 50 POE Load (A) | 538 | 539 | 542 | 544 | 543
Richlands Bulk | 620-1 | Richlands BS | Oxley | NCC Rating (A) | 324 | 324 | 324 | 324 | 324 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 187 | 185 | 184 | 184 | 182
|  |  |  | Power Factor | 0.96 | 0.96 | 0.96 | 0.96 | 0.96
|  |  |  | ECC Rating (A) | 359 | 359 | 359 | 359 | 359
|  |  |  | 50 POE Load (A) | 339 | 336 | 334 | 333 | 331
Richlands Bulk | 621-1 | Richlands BS | Oxley | NCC Rating (A) | 324 | 324 | 324 | 324 | 324 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 178 | 176 | 176 | 175 | 174
|  |  |  | Power Factor | 0.955 | 0.955 | 0.955 | 0.955 | 0.955
|  |  |  | ECC Rating (A) | 359 | 359 | 359 | 359 | 359
|  |  |  | 50 POE Load (A) | 339 | 336 | 334 | 333 | 331
Richlands Bulk | 641-1 | Darra | Jindalee | NCC Rating (A) | 703 | 703 | 703 | 703 | 703 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 154 | 153 | 153 | 152 | 151
|  |  |  | Power Factor | 0.971 | 0.971 | 0.971 | 0.971 | 0.971
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | 50 POE Load (A) | 260 | 259 | 258 | 257 | 255
Richlands Bulk | 642-1 | Darra | Jindalee | NCC Rating (A) | 703 | 703 | 703 | 703 | 703 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 151 | 150 | 150 | 149 | 148
|  |  |  | Power Factor | 0.97 | 0.97 | 0.97 | 0.97 | 0.97
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | 50 POE Load (A) | 260 | 259 | 258 | 257 | 255
Richlands Bulk | 679-1 | Richlands BS | Wacol | NCC Rating (A) | 605 | 605 | 605 | 605 | 605 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 128 | 126 | 125 | 125 | 124
|  |  |  | Power Factor | 0.991 | 0.991 | 0.992 | 0.992 | 0.992
|  |  |  | ECC Rating (A) | 605 | 605 | 605 | 605 | 605
|  |  |  | 50 POE Load (A) | 246 | 242 | 240 | 239 | 238
Richlands Bulk | 680-1 | Richlands BS | Wacol | NCC Rating (A) | 750 | 750 | 750 | 750 | 750 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 120 | 118 | 117 | 117 | 116
|  |  |  | Power Factor | 0.991 | 0.991 | 0.991 | 0.992 | 0.992
|  |  |  | ECC Rating (A) | 750 | 750 | 750 | 750 | 750
|  |  |  | 50 POE Load (A) | 115 | 113 | 113 | 112 | 111
Richlands Bulk | 700-1 | Richlands BS | Darra | NCC Rating (A) | 517 | 517 | 517 | 517 | 517 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 194 | 192 | 190 | 189 | 187
|  |  |  | Power Factor | 0.939 | 0.934 | 0.952 | 0.95 | 0.948
|  |  |  | ECC Rating (A) | 517 | 517 | 517 | 517 | 517
|  |  |  | 50 POE Load (A) | 285 | 282 | 279 | 278 | 276
Runcorn Bulk | 3440-1 | Runcorn BS | Sunnybank | NCC Rating (A) | 544 | 544 | 544 | 544 | 544 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 453 | 485 | 486 | 486 | 486
|  |  |  | Power Factor | 0.987 | 0.985 | 0.985 | 0.984 | 0.984
|  |  |  | ECC Rating (A) | 544 | 544 | 544 | 544 | 544
|  |  |  | 50 POE Load (A) | 502 | 540 | 541 | 541 | 541
Runcorn Bulk | 433-1 | Runcorn BS | Calamvale | NCC Rating (A) | 406 | 406 | 406 | 406 | 406 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 406 | 406 | 406 | 406 | 406
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Runcorn Bulk | 434-1 | Runcorn | Calamvale | NCC Rating (A) | 406 | 406 | 406 | 406 | 406 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 406 | 406 | 406 | 406 | 406
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Runcorn Bulk | 459A-1 | Upper Mt Gravatt | Sunnybank | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 96 | 102 | 102 | 0 | 0
|  |  |  | Power Factor | 0.93 | 0.926 | 0.926 | 0.926 | 0.926
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | 50 POE Load (A) | 513 | 554 | 555 | 555 | 555
Runcorn Bulk | 459B-1 | Runcorn BS | Upper Mt Gravatt | NCC Rating (A) | 801 | 801 | 801 | 801 | 801 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 94 | 101 | 101 | 101 | 101
|  |  |  | Power Factor | 0.942 | 0.937 | 0.937 | 0.937 | 0.937
|  |  |  | ECC Rating (A) | 801 | 801 | 801 | 801 | 801
|  |  |  | 50 POE Load (A) | 513 | 553 | 554 | 554 | 554
Runcorn Bulk | 667-1 | Runcorn BS | Acacia Ridge | NCC Rating (A) | 426 | 426 | 426 | 426 | 426 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 28 | 28 | 28 | 28 | 28
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 426 | 426 | 426 | 426 | 426
|  |  |  | 50 POE Load (A) | 28 | 28 | 28 | 28 | 28
Runcorn Bulk | 668-1 | Runcorn BS | Acacia Ridge | NCC Rating (A) | 426 | 426 | 426 | 426 | 426 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 28 | 28 | 28 | 28 | 28
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 426 | 426 | 426 | 426 | 426
|  |  |  | 50 POE Load (A) | 28 | 28 | 28 | 28 | 28
Runcorn Bulk | 690-1 | Runcorn BS | Runcorn | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 224 | 224 | 224 | 222 | 222
|  |  |  | Power Factor | 0.973 | 0.974 | 0.973 | 0.973 | 0.973
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | 50 POE Load (A) | 355 | 355 | 355 | 353 | 353
Runcorn Bulk | 691-1 | Runcorn BS | Runcorn | NCC Rating (A) | 553 | 553 | 553 | 553 | 553 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 177 | 177 | 177 | 176 | 176
|  |  |  | Power Factor | 0.974 | 0.974 | 0.974 | 0.974 | 0.974
|  |  |  | ECC Rating (A) | 553 | 553 | 553 | 553 | 553
|  |  |  | 50 POE Load (A) | 356 | 355 | 356 | 354 | 353
Runcorn Bulk | 694-1 | Runcorn BS | Eight Mile Plains Bus 1 | NCC Rating (A) | 531 | 531 | 531 | 531 | 531 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 255 | 254 | 253 | 252 | 250
|  |  |  | Power Factor | 0.956 | 0.956 | 0.956 | 0.956 | 0.957
|  |  |  | ECC Rating (A) | 531 | 531 | 531 | 531 | 531
|  |  |  | 50 POE Load (A) | 478 | 475 | 473 | 470 | 467
Sandgate Bulk | 3290-1 | Sandgate BS | Bald Hills Bus 1 | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 149 | 148 | 148 | 148 | 147
|  |  |  | Power Factor | 0.994 | 0.994 | 0.994 | 0.994 | 0.994
|  |  |  | ECC Rating (A) | 853 | 853 | 853 | 853 | 853
|  |  |  | 50 POE Load (A) | 297 | 295 | 295 | 293 | 291
Sandgate Bulk | 505-1 | Sandgate BS | Zilmere | NCC Rating (A) | 700 | 700 | 700 | 700 | 700 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 307 | 300 | 299 | 298 | 296
|  |  |  | Power Factor | 0.967 | 0.971 | 0.971 | 0.972 | 0.972
|  |  |  | ECC Rating (A) | 700 | 700 | 700 | 700 | 700
|  |  |  | 50 POE Load (A) | 390 | 378 | 377 | 376 | 373
Sandgate Bulk | 524-1 | Sandgate BS | Geebung | NCC Rating (A) | 453 | 453 | 453 | 453 | 453 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 206 | 201 | 201 | 200 | 199
|  |  |  | Power Factor | 0.981 | 0.984 | 0.985 | 0.985 | 0.985
|  |  |  | ECC Rating (A) | 453 | 453 | 453 | 453 | 453
|  |  |  | 50 POE Load (A) | 331 | 319 | 318 | 317 | 315
Sandgate Bulk | 524-2 | Geebung | Zillmere | NCC Rating (A) | 410 | 410 | 410 | 410 | 410 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 212 | 207 | 207 | 206 | 204
|  |  |  | Power Factor | 0.957 | 0.961 | 0.962 | 0.962 | 0.962
|  |  |  | ECC Rating (A) | 410 | 410 | 410 | 410 | 410
|  |  |  | 50 POE Load (A) | 336 | 324 | 323 | 322 | 319
Sandgate Bulk | 561-1 | Sandgate BS | Brighton TR1 | NCC Rating (A) | 786 | 786 | 786 | 786 | 786 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 101 | 101 | 101 | 100 | 100
|  |  |  | Power Factor | 0.986 | 0.986 | 0.986 | 0.986 | 0.986
|  |  |  | ECC Rating (A) | 786 | 786 | 786 | 786 | 786
|  |  |  | 50 POE Load (A) | 171 | 171 | 171 | 170 | 169
Sandgate Bulk | 656-1 | Sandgate BS | Brighton TR2 | NCC Rating (A) | 270 | 270 | 270 | 270 | 270 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 97 | 97 | 97 | 96 | 96
|  |  |  | Power Factor | 0.996 | 0.996 | 0.996 | 0.996 | 0.996
|  |  |  | ECC Rating (A) | 270 | 270 | 270 | 270 | 270
|  |  |  | 50 POE Load (A) | 173 | 172 | 172 | 172 | 171
Sandgate Bulk | 664-1 | Geebung | Zillmere | NCC Rating (A) | 410 | 410 | 410 | 410 | 410 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 25 | 25 | 25 | 25 | 25
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 410 | 410 | 410 | 410 | 410
|  |  |  | 50 POE Load (A) | 25 | 25 | 25 | 25 | 25
Sandgate Bulk | 671-1 | Sandagate BS | Zillmere | NCC Rating (A) | 495 | 507 | 507 | 507 | 507 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 170 | 177 | 177 | 176 | 175
|  |  |  | Power Factor | 0.995 | 0.99 | 0.99 | 0.99 | 0.99
|  |  |  | ECC Rating (A) | 495 | 507 | 507 | 507 | 507
|  |  |  | 50 POE Load (A) | 273 | 280 | 279 | 278 | 276
Stafford Bulk | 502-1 | Kedron | Clayfield | NCC Rating (A) | 304 | 0 | 0 | 0 | 0 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 191 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0.941 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 304 | 0 | 0 | 0 | 0
|  |  |  | 50 POE Load (A) | 335 | 0 | 0 | 0 | 0
Stafford Bulk | 522-1 | Kedron | Chermside | NCC Rating (A) | 281 | 0 | 0 | 0 | 0 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 281 | 0 | 0 | 0 | 0
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Stafford Bulk | 525-1 | Chermside | Zillmere | NCC Rating (A) | 311 | 0 | 0 | 0 | 0 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 311 | 0 | 0 | 0 | 0
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Stafford Bulk | 534-1 | Kedron | Clayfield | NCC Rating (A) | 304 | 0 | 0 | 0 | 0 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 189 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0.941 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 304 | 0 | 0 | 0 | 0
|  |  |  | 50 POE Load (A) | 335 | 0 | 0 | 0 | 0
Stafford Bulk | 548-1 | Stafford BS | Enoggera | NCC Rating (A) | 836 | 836 | 836 | 836 | 836 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 579 | 575 | 577 | 578 | 575
|  |  |  | Power Factor | 0.971 | 0.972 | 0.972 | 0.972 | 0.972
|  |  |  | ECC Rating (A) | 963 | 963 | 963 | 963 | 963
|  |  |  | 50 POE Load (A) | 1011 | 1006 | 1008 | 1007 | 1003
Stafford Bulk | 550-1 | Stafford BS | Chermside | NCC Rating (A) | 668 | 668 | 668 | 668 | 668 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 388 | 384 | 385 | 386 | 385
|  |  |  | Power Factor | 0.986 | 0.986 | 0.986 | 0.986 | 0.987
|  |  |  | ECC Rating (A) | 789 | 789 | 789 | 789 | 789
|  |  |  | 50 POE Load (A) | 709 | 704 | 706 | 706 | 704
Stafford Bulk | 551-1 | Stafford BS | Chermside | NCC Rating (A) | 668 | 668 | 668 | 668 | 668 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 387 | 383 | 384 | 385 | 384
|  |  |  | Power Factor | 0.986 | 0.986 | 0.986 | 0.986 | 0.987
|  |  |  | ECC Rating (A) | 789 | 789 | 789 | 789 | 789
|  |  |  | 50 POE Load (A) | 709 | 704 | 706 | 706 | 704
Stafford Bulk | 567-1 | Stafford BS | Kedron | NCC Rating (A) | 576 | 576 | 576 | 576 | 576 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 469 | 280 | 281 | 282 | 282
|  |  |  | Power Factor | 0.974 | 0.991 | 0.991 | 0.991 | 0.991
|  |  |  | ECC Rating (A) | 643 | 643 | 643 | 643 | 643
|  |  |  | 50 POE Load (A) | 828 | 493 | 496 | 496 | 496
Stafford Bulk | 568-1 | Stafford BS | Kedron | NCC Rating (A) | 576 | 576 | 576 | 576 | 576 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 472 | 282 | 283 | 284 | 284
|  |  |  | Power Factor | 0.974 | 0.991 | 0.991 | 0.991 | 0.991
|  |  |  | ECC Rating (A) | 643 | 643 | 643 | 643 | 643
|  |  |  | 50 POE Load (A) | 828 | 493 | 496 | 496 | 496
Stafford Bulk | 594-1 | Stafford BS | Enoggera | NCC Rating (A) | 836 | 836 | 836 | 836 | 836 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 576 | 572 | 573 | 574 | 571
|  |  |  | Power Factor | 0.971 | 0.972 | 0.972 | 0.972 | 0.972
|  |  |  | ECC Rating (A) | 963 | 963 | 963 | 963 | 963
|  |  |  | 50 POE Load (A) | 1012 | 1006 | 1008 | 1007 | 1003
Stafford Bulk | 595-1 | Enoggera | Grovely | NCC Rating (A) | 720 | 720 | 720 | 720 | 720 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 250 | 248 | 247 | 247 | 245
|  |  |  | Power Factor | 0.967 | 0.966 | 0.967 | 0.967 | 0.967
|  |  |  | ECC Rating (A) | 720 | 720 | 720 | 720 | 720
|  |  |  | 50 POE Load (A) | 432 | 428 | 427 | 425 | 422
Stafford Bulk | 596-1 | Enoggera | Grovely | NCC Rating (A) | 720 | 720 | 720 | 720 | 720 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 252 | 249 | 249 | 249 | 247
|  |  |  | Power Factor | 0.967 | 0.967 | 0.967 | 0.967 | 0.967
|  |  |  | ECC Rating (A) | 720 | 720 | 720 | 720 | 720
|  |  |  | 50 POE Load (A) | 432 | 428 | 427 | 425 | 422
Stafford Bulk | 607-1 | Chermside | Zillmere | NCC Rating (A) | 311 | 311 | 311 | 311 | 311 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 311 | 311 | 311 | 311 | 311
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Sunrise Hills Bulk | 308-1 | Perigian | 308 Tee1 | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 503 | 504 | 507 | 508 | 508
|  |  |  | Power Factor | 0.924 | 0.924 | 0.923 | 0.923 | 0.923
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | 50 POE Load (A) | 450 | 451 | 454 | 454 | 454
Sunrise Hills Bulk | 308-2 | 308 Tee1 | Coolum | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 503 | 504 | 507 | 508 | 508
|  |  |  | Power Factor | 0.938 | 0.938 | 0.938 | 0.938 | 0.937
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | 50 POE Load (A) | 450 | 451 | 454 | 454 | 454
Sunrise Hills Bulk | 308-3 | 308 Tee1 | 307 Tee2 | NCC Rating (A) | 529 | 529 | 529 | 529 | 529 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 529 | 529 | 529 | 529 | 529
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Sunrise Hills Bulk | 3100-1 | Sunrise Hills BS | 3100 Tee1 | NCC Rating (A) | 793 | 793 | 793 | 793 | 793 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 754 | 757 | 763 | 764 | 765
|  |  |  | Power Factor | 0.927 | 0.926 | 0.925 | 0.925 | 0.925
|  |  |  | ECC Rating (A) | 793 | 793 | 793 | 793 | 793
|  |  |  | 50 POE Load (A) | 662 | 664 | 669 | 670 | 671
Sunrise Hills Bulk | 3100-2 | 3100 Tee1 | Peregian | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 754 | 757 | 763 | 764 | 765
|  |  |  | Power Factor | 0.927 | 0.926 | 0.925 | 0.925 | 0.925
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | 50 POE Load (A) | 662 | 664 | 669 | 671 | 671
Sunrise Hills Bulk | 343-1 | Sunrise Hills BS | 343 Tee1 | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 424 | 421 | 421 | 419 | 418
|  |  |  | Power Factor | 0.97 | 0.971 | 0.97 | 0.971 | 0.971
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | 50 POE Load (A) | 657 | 652 | 650 | 648 | 644
Sunrise Hills Bulk | 343-2 | 343 Tee1 | Tewantin | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 164 | 162 | 160 | 158 | 156
|  |  |  | Power Factor | 0.949 | 0.949 | 0.95 | 0.95 | 0.951
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | 50 POE Load (A) | 425 | 420 | 417 | 414 | 411
Sunrise Hills Bulk | 343-3 | 343 Tee1 | Cooroy | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 265 | 265 | 267 | 267 | 268
|  |  |  | Power Factor | 0.983 | 0.983 | 0.983 | 0.983 | 0.983
|  |  |  | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
|  |  |  | 50 POE Load (A) | 238 | 238 | 239 | 239 | 239
Sunrise Hills Bulk | 346-1 | Sunrise Hills BS | 346 Tee1 | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 297 | 294 | 293 | 291 | 289
|  |  |  | Power Factor | 0.964 | 0.964 | 0.964 | 0.964 | 0.965
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 346 | 342 | 340 | 337 | 334
Sunrise Hills Bulk | 346-2 | 346 Tee1 | Tewantin | NCC Rating (A) | 780 | 780 | 780 | 780 | 780 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 297 | 294 | 293 | 291 | 289
|  |  |  | Power Factor | 0.964 | 0.964 | 0.964 | 0.964 | 0.965
|  |  |  | ECC Rating (A) | 780 | 780 | 780 | 780 | 780
|  |  |  | 50 POE Load (A) | 423 | 418 | 414 | 412 | 408
Sunrise Hills Bulk | 346-3 | 346 Tee1 | 3100 Tee1 | NCC Rating (A) | 529 | 529 | 529 | 529 | 529 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 529 | 529 | 529 | 529 | 529
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Sunrise Hills Bulk | 488-1 | Cooroy | 488 Tee1 | NCC Rating (A) | 582 | 582 | 582 | 582 | 582 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 145 | 145 | 146 | 146 | 146
|  |  |  | Power Factor | 0.992 | 0.992 | 0.991 | 0.991 | 0.991
|  |  |  | ECC Rating (A) | 582 | 582 | 582 | 582 | 582
|  |  |  | 50 POE Load (A) | 131 | 131 | 132 | 132 | 132
Sunrise Hills Bulk | 488-3 | 488 Tee1 | 488 Tee2 | NCC Rating (A) | 293 | 293 | 293 | 293 | 293 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 145 | 145 | 146 | 146 | 146
|  |  |  | Power Factor | 0.992 | 0.992 | 0.991 | 0.991 | 0.991
|  |  |  | ECC Rating (A) | 293 | 293 | 293 | 293 | 293
|  |  |  | 50 POE Load (A) | 131 | 131 | 132 | 132 | 132
Sunrise Hills Bulk | 488-4 | 488 Tee2 | Black Mtn | NCC Rating (A) | 293 | 293 | 293 | 293 | 293 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 78 | 78 | 78 | 78 | 78
|  |  |  | Power Factor | 0.991 | 0.991 | 0.99 | 0.99 | 0.99
|  |  |  | ECC Rating (A) | 293 | 293 | 293 | 293 | 293
|  |  |  | 50 POE Load (A) | 71 | 71 | 71 | 71 | 71
Sunrise Hills Bulk | 488-5 | 488 Tee2 | 488 Tee3 | NCC Rating (A) | 293 | 403 | 403 | 403 | 403 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 67 | 67 | 68 | 68 | 68
|  |  |  | Power Factor | 0.994 | 0.994 | 0.994 | 0.994 | 0.994
|  |  |  | ECC Rating (A) | 293 | 403 | 403 | 403 | 403
|  |  |  | 50 POE Load (A) | 60 | 60 | 61 | 61 | 61
Sunrise Hills Bulk | 488-6 | 488 Tee3 | Eumundi | NCC Rating (A) | 438 | 438 | 438 | 438 | 438 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 68 | 67 | 68 | 68 | 68
|  |  |  | Power Factor | 0.993 | 0.993 | 0.993 | 0.993 | 0.993
|  |  |  | ECC Rating (A) | 438 | 438 | 438 | 438 | 438
|  |  |  | 50 POE Load (A) | 60 | 60 | 61 | 61 | 61
Sunrise Hills Bulk | 488-7 | 488 Tee3 | Yandina | NCC Rating (A) | 293 | 403 | 403 | 403 | 403 | Rural | 170 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 293 | 403 | 403 | 403 | 403
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Tennyson Bulk | 3390-1 | Taringa | Indooroopilly | NCC Rating (A) | 728 | 728 | 728 | 728 | 728 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 135 | 134 | 134 | 134 | 133
|  |  |  | Power Factor | 0.944 | 0.944 | 0.944 | 0.944 | 0.944
|  |  |  | ECC Rating (A) | 728 | 728 | 728 | 728 | 728
|  |  |  | 50 POE Load (A) | 169 | 168 | 168 | 168 | 167
Tennyson Bulk | 3393-1 | Tennyson BS | St Lucia TR1 | NCC Rating (A) | 610 | 610 | 610 | 610 | 610 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 159 | 159 | 158 | 158 | 157
|  |  |  | Power Factor | 0.985 | 0.985 | 0.985 | 0.985 | 0.985
|  |  |  | ECC Rating (A) | 610 | 610 | 610 | 610 | 610
|  |  |  | 50 POE Load (A) | 306 | 305 | 305 | 304 | 302
Tennyson Bulk | 3394-1 | Tennyson BS | St Lucia TR2 | NCC Rating (A) | 610 | 610 | 610 | 610 | 610 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 150 | 150 | 150 | 149 | 148
|  |  |  | Power Factor | 0.987 | 0.987 | 0.987 | 0.987 | 0.988
|  |  |  | ECC Rating (A) | 610 | 610 | 610 | 610 | 610
|  |  |  | 50 POE Load (A) | 140 | 140 | 140 | 140 | 139
Tennyson Bulk | 3460-1 | Annerley | Buranda | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 211 | 220 | 247 | 248 | 248
|  |  |  | Power Factor | 0.964 | 0.963 | 0.992 | 0.992 | 0.992
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 392 | 410 | 486 | 488 | 488
Tennyson Bulk | 3461-1 | Annerley | Buranda | NCC Rating (A) | 800 | 800 | 800 | 800 | 800 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 211 | 220 | 248 | 248 | 248
|  |  |  | Power Factor | 0.964 | 0.963 | 0.992 | 0.992 | 0.992
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 392 | 410 | 486 | 488 | 488
Tennyson Bulk | 410-1 | Sherwood | Indooroopilly | NCC Rating (A) | 400 | 400 | 400 | 400 | 400 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 266 | 265 | 265 | 265 | 264
|  |  |  | Power Factor | 0.961 | 0.961 | 0.961 | 0.962 | 0.962
|  |  |  | ECC Rating (A) | 451 | 451 | 451 | 451 | 451
|  |  |  | 50 POE Load (A) | 380 | 379 | 380 | 380 | 378
Tennyson Bulk | 460-1 | Tennyson BS | Sherwood | NCC Rating (A) | 763 | 763 | 763 | 763 | 763 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 435 | 434 | 435 | 434 | 431
|  |  |  | Power Factor | 0.979 | 0.979 | 0.979 | 0.979 | 0.979
|  |  |  | ECC Rating (A) | 763 | 763 | 763 | 763 | 763
|  |  |  | 50 POE Load (A) | 526 | 524 | 524 | 523 | 520
Tennyson Bulk | 480-1 | Taringa | St Lucia | NCC Rating (A) | 610 | 610 | 610 | 610 | 610 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 161 | 161 | 160 | 160 | 159
|  |  |  | Power Factor | 0.989 | 0.989 | 0.989 | 0.989 | 0.99
|  |  |  | ECC Rating (A) | 610 | 610 | 610 | 610 | 610
|  |  |  | 50 POE Load (A) | 304 | 303 | 303 | 303 | 301
Tennyson Bulk | 504-1 | Tennyson BS | Taringa | NCC Rating (A) | 601 | 601 | 601 | 601 | 601 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 352 | 352 | 353 | 352 | 351
|  |  |  | Power Factor | 0.981 | 0.981 | 0.981 | 0.981 | 0.981
|  |  |  | ECC Rating (A) | 713 | 713 | 713 | 713 | 713
|  |  |  | 50 POE Load (A) | 465 | 464 | 465 | 465 | 462
Tennyson Bulk | 507A-1 | Toowong | Indooroopilly | NCC Rating (A) | 735 | 735 | 735 | 735 | 735 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 138 | 137 | 137 | 137 | 136
|  |  |  | Power Factor | 0.949 | 0.949 | 0.949 | 0.949 | 0.95
|  |  |  | ECC Rating (A) | 858 | 858 | 858 | 858 | 858
|  |  |  | 50 POE Load (A) | 171 | 170 | 170 | 170 | 168
Tennyson Bulk | 507B-1 | Toowong | Taringa | NCC Rating (A) | 727 | 727 | 727 | 727 | 727 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 136 | 135 | 135 | 135 | 134
|  |  |  | Power Factor | 0.962 | 0.962 | 0.962 | 0.962 | 0.963
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 169 | 168 | 168 | 168 | 166
Tennyson Bulk | 511-1 | Tennyson BS | Moorooka | NCC Rating (A) | 739 | 739 | 739 | 739 | 739 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 157 | 157 | 158 | 159 | 160
|  |  |  | Power Factor | 0.963 | 0.962 | 0.962 | 0.962 | 0.962
|  |  |  | ECC Rating (A) | 753 | 753 | 753 | 753 | 753
|  |  |  | 50 POE Load (A) | 280 | 287 | 290 | 292 | 294
Tennyson Bulk | 514-1 | Tennyson BS | Moorooka | NCC Rating (A) | 739 | 739 | 739 | 739 | 739 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 158 | 160 | 161 | 163 | 164
|  |  |  | Power Factor | 0.963 | 0.963 | 0.963 | 0.963 | 0.963
|  |  |  | ECC Rating (A) | 753 | 753 | 753 | 753 | 753
|  |  |  | 50 POE Load (A) | 280 | 287 | 289 | 292 | 294
Tennyson Bulk | 515-1 | Tennyson BS | Sherwood | NCC Rating (A) | 740 | 740 | 740 | 740 | 740 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 461 | 460 | 460 | 459 | 456
|  |  |  | Power Factor | 0.983 | 0.983 | 0.983 | 0.983 | 0.983
|  |  |  | ECC Rating (A) | 740 | 740 | 740 | 740 | 740
|  |  |  | 50 POE Load (A) | 556 | 554 | 555 | 554 | 550
Tennyson Bulk | 523A&B-1 | Tennyson BS | Rocklea | NCC Rating (A) | 602 | 0 | 0 | 0 | 0 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 602 | 0 | 0 | 0 | 0
|  |  |  | 50 POE Load (A) | 0 | 0 | 0 | 0 | 0
Tennyson Bulk | 523A-1 | Tennyson BS | Rocklea | NCC Rating (A) | 0 | 650 | 650 | 650 | 650 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 8 | 8 | 8 | 8
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 0 | 650 | 650 | 650 | 650
|  |  |  | 50 POE Load (A) | 0 | 8 | 8 | 8 | 8
Tennyson Bulk | 539-1 | Sherwood | Kenmore | NCC Rating (A) | 495 | 495 | 495 | 495 | 495 | Urban | 340 | NA
|  |  |  | 10 POE Load (A) | 295 | 294 | 293 | 292 | 289
|  |  |  | Power Factor | 0.969 | 0.97 | 0.97 | 0.97 | 0.97
|  |  |  | ECC Rating (A) | 495 | 495 | 495 | 495 | 495
|  |  |  | 50 POE Load (A) | 580 | 577 | 576 | 573 | 567
Tennyson Bulk | 554-1 | Tennyson BS | Sherwood | NCC Rating (A) | 716 | 716 | 716 | 716 | 716 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 490 | 489 | 489 | 488 | 485
|  |  |  | Power Factor | 0.981 | 0.981 | 0.981 | 0.981 | 0.981
|  |  |  | ECC Rating (A) | 716 | 716 | 716 | 716 | 716
|  |  |  | 50 POE Load (A) | 577 | 575 | 576 | 575 | 571
Tennyson Bulk | 571-1 | Indooroopilly | Kenmore | NCC Rating (A) | 527 | 527 | 527 | 527 | 527 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 382 | 380 | 379 | 377 | 373
|  |  |  | Power Factor | 0.954 | 0.954 | 0.955 | 0.955 | 0.956
|  |  |  | ECC Rating (A) | 527 | 527 | 527 | 527 | 527
|  |  |  | 50 POE Load (A) | 572 | 569 | 567 | 564 | 558
Tennyson Bulk | 606-1 | Tennyson BS | Taringa | NCC Rating (A) | 601 | 601 | 601 | 601 | 601 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 354 | 354 | 354 | 354 | 352
|  |  |  | Power Factor | 0.981 | 0.981 | 0.981 | 0.981 | 0.981
|  |  |  | ECC Rating (A) | 713 | 713 | 713 | 713 | 713
|  |  |  | 50 POE Load (A) | 466 | 465 | 466 | 466 | 463
Tennyson Bulk | 637-1 | Tennyson BS | Annerley | NCC Rating (A) | 716 | 716 | 716 | 716 | 716 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 357 | 366 | 402 | 403 | 404
|  |  |  | Power Factor | 0.969 | 0.968 | 0.988 | 0.988 | 0.988
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 654 | 671 | 742 | 746 | 746
Tennyson Bulk | 638-1 | Tennyson BS | Annerley | NCC Rating (A) | 716 | 716 | 716 | 716 | 716 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 358 | 367 | 403 | 405 | 405
|  |  |  | Power Factor | 0.969 | 0.968 | 0.988 | 0.988 | 0.988
|  |  |  | ECC Rating (A) | 800 | 800 | 800 | 800 | 800
|  |  |  | 50 POE Load (A) | 654 | 671 | 742 | 746 | 746
Tennyson Bulk | F703-1 | Sherwood | Indooroopilly | NCC Rating (A) | 400 | 400 | 400 | 400 | 400 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 268 | 268 | 268 | 268 | 266
|  |  |  | Power Factor | 0.962 | 0.962 | 0.962 | 0.962 | 0.962
|  |  |  | ECC Rating (A) | 451 | 451 | 451 | 451 | 451
|  |  |  | 50 POE Load (A) | 382 | 381 | 382 | 381 | 380
Victoria Park Bulk | 627-1 | Victoria Pk BS | Astor Tce | NCC Rating (A) | 415 | 415 | 415 | 415 | 415 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 0 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0.968 | 0.968 | 0.968 | 0.968 | 0.968
|  |  |  | ECC Rating (A) | 415 | 415 | 415 | 415 | 415
|  |  |  | 50 POE Load (A) | 219 | 218 | 219 | 219 | 219
Victoria Park Bulk | 628-1 | Victoria Pk BS | Astor Tce | NCC Rating (A) | 415 | 415 | 415 | 415 | 415 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 231 | 230 | 231 | 231 | 231
|  |  |  | Power Factor | 0.988 | 0.988 | 0.988 | 0.988 | 0.988
|  |  |  | ECC Rating (A) | 415 | 415 | 415 | 415 | 415
|  |  |  | 50 POE Load (A) | 448 | 446 | 447 | 447 | 447
Victoria Park Bulk | 639-1 | Victoria Pk BS | Newmarket | NCC Rating (A) | 503 | 503 | 503 | 503 | 503 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 226 | 225 | 225 | 224 | 223
|  |  |  | Power Factor | 0.968 | 0.968 | 0.968 | 0.968 | 0.968
|  |  |  | ECC Rating (A) | 585 | 585 | 585 | 585 | 585
|  |  |  | 50 POE Load (A) | 396 | 394 | 394 | 393 | 391
Victoria Park Bulk | 649-1 | Victoria Pk BS | Astor Tce | NCC Rating (A) | 415 | 415 | 415 | 415 | 415 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 234 | 233 | 233 | 234 | 234
|  |  |  | Power Factor | 0.988 | 0.988 | 0.988 | 0.988 | 0.988
|  |  |  | ECC Rating (A) | 415 | 415 | 415 | 415 | 415
|  |  |  | 50 POE Load (A) | 448 | 446 | 447 | 447 | 446
Victoria Park Bulk | 653-1 | Victoria Pk BS | Newmarket | NCC Rating (A) | 503 | 503 | 503 | 503 | 503 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 226 | 225 | 225 | 224 | 223
|  |  |  | Power Factor | 0.968 | 0.968 | 0.968 | 0.968 | 0.968
|  |  |  | ECC Rating (A) | 585 | 585 | 585 | 585 | 585
|  |  |  | 50 POE Load (A) | 396 | 394 | 394 | 393 | 391
Victoria Park Bulk | 659B-1 | Victoria Pk BS | Clayfield | NCC Rating (A) | 330 | 0 | 0 | 0 | 0 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 6 | 0 | 0 | 0 | 0
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 330 | 0 | 0 | 0 | 0
|  |  |  | 50 POE Load (A) | 161 | 0 | 0 | 0 | 0
Victoria Park Bulk | 689-1 | Victoria Pk BS | Astor Tce | NCC Rating (A) | 538 | 538 | 538 | 538 | 538 | Urban | 70 | NA
|  |  |  | 10 POE Load (A) | 9 | 9 | 9 | 9 | 9
|  |  |  | Power Factor | 0 | 0 | 0 | 0 | 0
|  |  |  | ECC Rating (A) | 538 | 538 | 538 | 538 | 538
|  |  |  | 50 POE Load (A) | 9 | 9 | 9 | 9 | 9