## Disclaimer
Substations Forecast
(Ergon Energy Distribution Annual Planning Report 2023)
This workbook forms part of the Ergon Energy Distribution Annual Planning Report 2023 (DAPR) and should be read in conjunction with the report document.
Readers are encouraged to take into account the details and content portrayed in the ‘Introduction & Notes’ section of this workbook when reviewing the associated data.
Disclaimer
Ergon Energy’s Distribution Annual Planning Report (DAPR) is prepared and made available solely for information purposes. While care was taken in the preparation of the information in the DAPR, and it is provided in good faith, Ergon Energy accepts no responsibility or liability (including without limitation, liability to any person by reason of negligence or negligent mis-statement) for any loss or damage that may be incurred by any person acting in reliance on this information or assumptions drawn from it, except to the extent that liability under any applicable Queensland or Commonwealth of Australia statute cannot be excluded.
It contains assumptions regarding, among other things, economic growth and load forecasts which may or may not prove to be correct. The forecasts included in the DAPR involve subjective judgements and analysis which are subject to significant uncertainties and contingencies, many of which are out of the control of Ergon Energy. Ergon Energy makes no representation or warranty as to the accuracy, reliability, completeness or suitability for any particular purpose of the information in this document. All information should be independently investigated, reviewed, analysed and verified, and must not be relied upon in connection with any investment proposal or decision. The information contained in the DAPR is subject to annual review. Ergon Energy is obligated to publish future editions by 31st December, in accordance with the National Electricity Rules.
All financials presented in the DAPR or within this document are correct at the time of writing and represent the existing organisational accounting treatment, which may be subject to change. Energy Queensland is finalising the alignment of its Cost Allocation Methodology between Ergon Energy and Energex, potentially impacting the treatment of some Capital and Operational Project costs.
Forecasted data is subject to ongoing variation due to regulatory review in 2025.

## Introduction & Notes
Substations Forecast (Ergon Energy Distribution Annual Planning Report 2023)
This workbook provides 5 year forecast capacity and loading information for each Ergon Energy owned Substation in the Ergon Energy network.
This workbook forms part of the Ergon Energy Distribution Annual Planning Report 2023(DAPR) and should be read in conjunction with the report document.
Forecasted data is subject to ongoing variation due to regulatory review in 2025.
Zone Substations
A zone substation refers to an Ergon Energy owned substation that converts energy from transmission or subtransmission voltages to distribution voltages.
Bulk Supply Substations and Transmission Connection Points
A Bulk Supply Substation refers to an Ergon Energy owned substations that converts energy from transmission voltage levels to sub-transmission voltage levels.
Some Ergon Owned Bulk Supply Substations contain asset boundaries with the Transmission Network Service Provider and therefore are also the Transmission Connection Point. Demand forecasts for other TCPs are reported in a separate workbook.
Load Forecasts
The summer and winter load forecasts are provided in the row named 10 PoE Load.
(Note: The 50 PoE Load is used to address Safety Net requirements.)
"Hours PA > 95% Peak Load" gives the hours per year that load is above 95% of the peak load.
· 'zero' values occur for small substations with no metering installed to provide this data
· 'N/A' values occur for new substation which does not yet have history on this data to be able to determine future forecasts.
The peak load given is a compensated load, which is the load with reactive compensation in service.
Capacity
Substation capacity is based on transformer ratings only.
NCC (Normal Cyclic Capacity) Rating is the total capacity of the substation with all transformers in service. Where the NCC rating is not available the manufacturer's transformer profile is used.
ECC (Emergency Cyclic Capacity) Rating is the firm delivery capacities with the largest transformer out of service.
Transfer Capability
The load transfer capabilities of each substation are broken up into the following categories:
· Auto Trans Avail: Transfers conducted automatically by a distribution management system
· Remote Trans Avail: Transfers conducted by a Network Operator located in one of the Operational Control Centres
· Manual Trans Avail: Transfers which require manual switching by a field crew
· Mobile Plant Avail: Supply which can be restored by the use of a mobile substation, HV injection generation or distributed low voltage generation.
The transfer capabilities align with the various time requirements to have certain load levels restored under Ergon Energy’s Safety Net requirements.
Load Shedding
The load shedding rows are defined as follows:
· Shed (30min): Loads to large customers which can be disconnected by remote operation of switchgear
· Shed (4Hour): Loads to large customers which need manual switching by field crews to disconnect them from the network.
Security
The load at risk assessments (LARn and LARc) are assessments of the potential load at risk in a substation. If there are values in the LARn or LARc columns the “Meets Security Standard” row will change to “No” for those columns.
The LARn is calculated by comparing the 10 PoE with the NCC rating. If the 10 PoE load is greater than the NCC rating then there is potentially load at risk under normal operating conditions for the substation.
If there is a value of LARc then Ergon Energy may potentially fail to meet its obligations in the occurrence of a Safety Net event. The LARc value is determined as follows: The Raw LAR is arrived at by comparing the 50 PoE load with the ECC rating. If the 50 PoE load is the greater than the ECC rating then contingencies need to be in place to meet Ergon Energy’s Safety Net obligations. The transfer capabilities, mobile plant capacities and load shed allowances are then taken from the Raw LAR value to give the LARc value.
For the implementation of Safety Net Ergon Energy operates two Substation categories
· Regional Centres are towns/cities with a population of more than 6,000 people
· Rural/Remote is used for substations servicing all other areas of the state.
The time required to restore certain load levels for each category is less for the Regional Centre category.
Under Ergon Energy’s Safety Net large customers are exempt from reporting. While all efforts are made to restore supply to them, load shedding can be used to disconnect these customers from the network if required in a contingency event.
Embedded Generation
The embedded generation reported for the substation is the nameplate rating of embedded generation connected to the low voltage side of the substation.

## capacity (hidden)
INDEX | Sheet Name | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28
6 | AGWA | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
7 | AITK | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
8 | ALLO | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
9 | ALSH | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36
10 | ALST | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
11 | ATHE | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
12 | AWOO | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
13 | AYRZ | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
14 | BALB | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
15 | BAMB | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
16 | BARC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | BARG | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
18 | BARR | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
19 | BEGA | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38
20 | BERS | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38
21 | BEWE | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5
22 | BILO | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
23 | BING | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
24 | BLAC | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
25 | BLAK | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
26 | BLRI | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31
27 | BLUE | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
28 | BODA | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1
29 | BOHL | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
30 | BORE | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
31 | BOWE | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
32 | BROX | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | BUCE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | BULL | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
35 | BUND | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116
36 | CACI | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119
37 | CAFE | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
38 | CALE | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
39 | CALL | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
40 | CANN | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
41 | CANO | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
42 | CARI | bar: 2023/24 to 2027/28
43 | CARM | bar: 2023/24 to 2027/28
44 | CAST | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32
45 | CAWD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46 | CEPL | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
47 | CHAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | CHAR | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
49 | CHIA | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3
50 | CHIL | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
51 | CHIN | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
52 | CHTO | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5
53 | CHTW | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
54 | CHUM | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
55 | CLBS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
56 | CLER | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
57 | CLIF | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32
58 | CLIN | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32
59 | CLON | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15 | 5.15
60 | CLSO | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3
61 | COLU | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
62 | COME | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3
63 | COOK | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
64 | COOM | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
65 | CPRE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
66 | CRAI | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
67 | CRAN | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
68 | CRED | bar: 2023/24 to 2027/28
69 | CRNE | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3
70 | CROY | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
71 | CUNN | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
72 | DACE | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32
73 | DAGL | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
74 | DEGI | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
75 | DIMB | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
76 | DISR | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
77 | Duchr2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78 | DURO | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
79 | DYSA | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
80 | EAAY | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
81 | EABU | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
82 | EATO | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
83 | EIDS | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
84 | ELRO | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2
85 | EMER | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
86 | ETON | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
87 | EUDA | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
88 | EVEL | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3
89 | FARL | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
90 | FARN | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
91 | FREN | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
92 | GARB | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42
93 | GAYN | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
94 | GEOR | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
95 | GEOR1 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
96 | GIRU | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
97 | GIVE | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5
98 | GLEE | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63
99 | GLEL | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76
100 | GLEL33 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64
101 | GLEN | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
102 | GLFS | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
103 | GLNO | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
104 | GLSO | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
105 | GOOB | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
106 | GOOT | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3
107 | Gracem
108 | GRCR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
109 | GREN | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
110 | GRSO
111 | GUML | bar: 2023/24 to 2027/28
112 | GUTH | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
113 | HAPU | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
114 | HELE | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
115 | HEPA | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
116 | HIGH | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
117 | HOHI | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
118 | HOWA | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
119 | HUGH | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
120 | ILBI | bar: 2023/24 to 2027/28
121 | INGH | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
122 | ISIS | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114
123 | JAND | 3.15 | 3.15 | 3.15 | 3.15 | 3.15 | 3.15 | 3.15 | 3.15 | 3.15 | 3.15
124 | JARV | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
125 | JCRK
126 | JUCR | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3
127 | JUPO | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19
128 | KAIM | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
129 | KALA | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
130 | KECE | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5
131 | KESP | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
132 | KIDS | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
133 | KILK | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39
134 | KILL | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
135 | KING | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
136 | KIRK | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
137 | KITO | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
138 | KOCR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
139 | KOUM | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
140 | LACR | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32
141 | LAKE | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
142 | LANN | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3
143 | LAQU | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
144 | LARO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
145 | LITT | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
146 | LOCR | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3
147 | LONG | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
148 | LUCI | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
149 | LYLA | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75
150 | MACI | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28
151 | MACN | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
152 | MACT | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
153 | MAFU | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42
154 | MAKA | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
155 | MALC | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
156 | MARE | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
157 | MARY | 224 | 224 | 224 | 224 | 224 | 224 | 224 | 224 | 224 | 224
158 | MASO | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
159 | MCCR | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
160 | MEAD | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 9.5
161 | MEAN | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
162 | MERI | 14.3 | 14.3 | 14.3 | 14.3 | 14.3 | 14.3 | 14.3 | 14.3 | 14.3 | 14.3
163 | MERN | 12.6 | 12.6 | 12.6 | 12.6 | 12.6 | 12.6 | 12.6 | 12.6 | 12.6 | 12.6
164 | MICO | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
165 | MIDD | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
166 | MILC | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
167 | MILE | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5
168 | MILL | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
169 | MILM | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3
170 | MING | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
171 | MIRA | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
172 | MITC | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
173 | MIVA | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3
174 | MOBA | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
175 | MODA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | MOFO | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63
177 | MOGA | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
178 | MOLP | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
179 | MOMO | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
180 | MOMR | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
181 | MOMW | bar: 2023/24 to 2027/28
182 | MONT | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5
183 | MOOR | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
184 | MOPA | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
185 | MORO | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
186 | MOSI | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
187 | MOSS | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18
188 | MOUR
189 | MURG | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17
190 | MUTA | bar: 2023/24 to 2027/28
191 | MUTO | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32
192 | NANA | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
193 | NAND | 3.15 | 3.15 | 3.15 | 3.15 | 3.15 | 3.15 | 3.15 | 3.15 | 3.15 | 3.15
194 | NEBO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
195 | NESM | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
196 | NOCL | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
197 | NOMA | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
198 | NORM | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
199 | NORW | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
200 | NOST | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
201 | OAKE | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
202 | OONN | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38
203 | OWAN | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18
204 | PAMP | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
205 | PAND | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
206 | PARK | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
207 | PEAR | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41
208 | PERA | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
209 | PIAL | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
210 | PINN | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
211 | PIRR | 3.15 | 3.15 | 3.15 | 3.15 | 3.15 | 3.15 | 3.15 | 3.15 | 3.15 | 3.15
212 | PLAN | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26
213 | PLEY | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
214 | POVE | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
215 | POZI | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
216 | PRMI | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
217 | PROT | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
218 | PURR | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5
219 | QUIL | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
220 | RAGL | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
221 | RASM | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38
222 | RAVE | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
223 | RAVN | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
224 | RICH | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
225 | ROEA | 12.6 | 12.6 | 12.6 | 12.6 | 12.6 | 12.6 | 12.6 | 12.6 | 12.6 | 12.6
226 | ROGL | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
227 | ROLE | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
228 | ROLL | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
229 | ROMA | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
230 | ROPL | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
231 | ROSE | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
232 | ROSO | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
233 | ROST | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
234 | ROWE | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3
235 | ROWO | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
236 | SAGE | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
237 | SAGT | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
238 | SARI | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
239 | SAUN | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
240 | SHUT | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
241 | SKIE | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
242 | SOBL | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
243 | SOBU | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28
244 | SOKO | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
245 | SOMA | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
246 | SOTO | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34
247 | STAM | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63
248 | STAN | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
249 | STTO | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
250 | STUA | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42
251 | T002 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
252 | T019 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
253 | T032
254 | T043 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72
255 | T047
256 | T058 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
257 | T072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
258 | T083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
259 | T095 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
260 | T116 | 128 | 128 | 128 | 128 | 128 | 128 | 128 | 128 | 128 | 128
261 | T130 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
262 | T156 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33
263 | T159 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
264 | T163 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
265 | T166 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
266 | T176 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
267 | T188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
268 | T189 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96
269 | T198 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160
270 | TANB | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
271 | TARA | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
272 | THEO | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
273 | TIER | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
274 | TOPO | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38
275 | TORQ | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42
276 | TORR | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
277 | TUAN | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
278 | TWCE | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64
279 | VERM | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
280 | WAEA | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
281 | WAGG
282 | WALL | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
283 | WAND | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
284 | WEBU | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
285 | WEDA | 12.55 | 12.55 | 12.55 | 12.55 | 12.55 | 12.55 | 12.55 | 12.55 | 12.55 | 12.55
286 | WEMA | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
287 | WETO | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
288 | WEWA | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
289 | WINT | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
290 | WIRR | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63 | 0.63
291 | WOOD | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
292 | WOOG | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
293 | WOOL | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
294 | WOSO | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3
295 | WOWA | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
296 | YARA | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
297 | YARR | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
298 | YASO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
299 | YEPP | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32
300 | Z1313 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
301 | Z1314 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
302 | Z1326
303 | Z1327 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
304 | Z1350 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
305 | Z300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
306 | Z454
307 | Z1553 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10

## firm_capacity (hidden)
INDEX | Sheet Name | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28
6 | AGWA | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
7 | AITK | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
8 | ALLO | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
9 | ALSH | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18
10 | ALST | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
11 | ATHE | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
12 | AWOO | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
13 | AYRZ | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
14 | BALB | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | BAMB | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | BARC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | BARG | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
18 | BARR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | BEGA | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19
20 | BERS | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19
21 | BEWE | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
22 | BILO | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
23 | BING | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
24 | BLAC | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
25 | BLAK | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
26 | BLRI | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
27 | BLUE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | BODA | bar: 2023/24 to 2027/28
29 | BOHL | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
30 | BORE | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
31 | BOWE | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
32 | BROX | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | BUCE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | BULL | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
35 | BUND | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76
36 | CACI | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
37 | CAFE | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
38 | CALE | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
39 | CALL | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
40 | CANN | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
41 | CANO | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
42 | CARI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
43 | CARM | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
44 | CAST | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
45 | CAWD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
46 | CEPL | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
47 | CHAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
48 | CHAR | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
49 | CHIA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 | CHIL | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
51 | CHIN | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
52 | CHTO | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
53 | CHTW | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
54 | CHUM | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
55 | CLBS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
56 | CLER | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
57 | CLIF | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
58 | CLIN | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
59 | CLON | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
60 | CLSO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
61 | COLU | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
62 | COME | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
63 | COOK | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
64 | COOM | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
65 | CPRE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
66 | CRAI | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
67 | CRAN | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
68 | CRED | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
69 | CRNE | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
70 | CROY | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
71 | CUNN | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
72 | DACE | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
73 | DAGL | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
74 | DEGI | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
75 | DIMB | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
76 | DISR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
77 | Duchr2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
78 | DURO | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
79 | DYSA | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
80 | EAAY | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
81 | EABU | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
82 | EATO | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
83 | EIDS | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
84 | ELRO | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1
85 | EMER | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
86 | ETON | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
87 | EUDA | bar: 2023/24 to 2027/28
88 | EVEL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
89 | FARL | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
90 | FARN | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
91 | FREN | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
92 | GARB | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
93 | GAYN | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
94 | GEOR | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
95 | GEOR1 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
96 | GIRU | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
97 | GIVE | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
98 | GLEE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
99 | GLEL | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38
100 | GLEL33 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32
101 | GLEN | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
102 | GLFS | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
103 | GLNO | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
104 | GLSO | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
105 | GOOB | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
106 | GOOT | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
107 | Gracem
108 | GRCR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
109 | GREN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
110 | GRSO
111 | GUML | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
112 | GUTH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
113 | HAPU | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
114 | HELE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
115 | HEPA | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
116 | HIGH | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
117 | HOHI | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
118 | HOWA | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
119 | HUGH | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
120 | ILBI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
121 | INGH | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
122 | ISIS | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
123 | JAND | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75
124 | JARV | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
125 | JCRK
126 | JUCR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
127 | JUPO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
128 | KAIM | bar: 2023/24 to 2027/28
129 | KALA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
130 | KECE | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5
131 | KESP | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
132 | KIDS | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
133 | KILK | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
134 | KILL | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
135 | KING | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
136 | KIRK | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
137 | KITO | bar: 2023/24 to 2027/28
138 | KOCR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
139 | KOUM | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
140 | LACR | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
141 | LAKE | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
142 | LANN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
143 | LAQU | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
144 | LARO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
145 | LITT | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
146 | LOCR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
147 | LONG | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
148 | LUCI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
149 | LYLA | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
150 | MACI | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14
151 | MACN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
152 | MACT | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
153 | MAFU | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
154 | MAKA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155 | MALC | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
156 | MARE | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
157 | MARY | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144
158 | MASO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
159 | MCCR | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
160 | MEAD | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
161 | MEAN | bar: 2023/24 to 2027/28
162 | MERI | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3
163 | MERN | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3
164 | MICO | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75
165 | MIDD | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
166 | MILC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
167 | MILE | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
168 | MILL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
169 | MILM | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
170 | MING | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
171 | MIRA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
172 | MITC | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75
173 | MIVA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
174 | MOBA | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5
175 | MODA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | MOFO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
177 | MOGA | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
178 | MOLP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
179 | MOMO | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
180 | MOMR | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
181 | MOMW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
182 | MONT | 6.25 | 6.25 | 6.25 | 6.25 | 6.25 | 6.25 | 6.25 | 6.25 | 6.25 | 6.25
183 | MOOR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
184 | MOPA | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
185 | MORO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
186 | MOSI | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
187 | MOSS | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
188 | MOUR
189 | MURG | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5
190 | MUTA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
191 | MUTO | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
192 | NANA | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
193 | NAND | bar: 2023/24 to 2027/28
194 | NEBO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
195 | NESM | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
196 | NOCL | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
197 | NOMA | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
198 | NORM | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
199 | NORW | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
200 | NOST | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
201 | OAKE | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
202 | OONN | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19
203 | OWAN | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
204 | PAMP | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
205 | PAND | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
206 | PARK | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
207 | PEAR | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
208 | PERA | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75
209 | PIAL | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5
210 | PINN | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
211 | PIRR | bar: 2023/24 to 2027/28
212 | PLAN | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
213 | PLEY | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
214 | POVE | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
215 | POZI | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
216 | PRMI | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
217 | PROT | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
218 | PURR | 6.25 | 6.25 | 6.25 | 6.25 | 6.25 | 6.25 | 6.25 | 6.25 | 6.25 | 6.25
219 | QUIL | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
220 | RAGL | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
221 | RASM | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19
222 | RAVE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
223 | RAVN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
224 | RICH | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3
225 | ROEA | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3
226 | ROGL | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
227 | ROLE | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
228 | ROLL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
229 | ROMA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
230 | ROPL | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
231 | ROSE | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5
232 | ROSO | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
233 | ROST | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
234 | ROWE | 3.15 | 3.15 | 3.15 | 3.15 | 3.15 | 3.15 | 3.15 | 3.15 | 3.15 | 3.15
235 | ROWO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
236 | SAGE | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
237 | SAGT | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
238 | SARI | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
239 | SAUN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
240 | SHUT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
241 | SKIE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
242 | SOBL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
243 | SOBU | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14
244 | SOKO | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
245 | SOMA | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5
246 | SOTO | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
247 | STAM | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
248 | STAN | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
249 | STTO | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
250 | STUA | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
251 | T002 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
252 | T019 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
253 | T032
254 | T043 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35
255 | T047
256 | T058 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
257 | T072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
258 | T083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
259 | T095 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
260 | T116 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64
261 | T130 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
262 | T156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
263 | T159 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
264 | T163 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
265 | T166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
266 | T176 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
267 | T188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
268 | T189 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
269 | T198 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
270 | TANB | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
271 | TARA | bar: 2023/24 to 2027/28
272 | THEO | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
273 | TIER | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
274 | TOPO | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19
275 | TORQ | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
276 | TORR | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
277 | TUAN | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
278 | TWCE | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32
279 | VERM | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
280 | WAEA | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
281 | WAGG
282 | WALL | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
283 | WAND | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
284 | WEBU | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
285 | WEDA | 6.25 | 6.25 | 6.25 | 6.25 | 6.25 | 6.25 | 6.25 | 6.25 | 6.25 | 6.25
286 | WEMA | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
287 | WETO | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
288 | WEWA | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
289 | WINT | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
290 | WIRR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
291 | WOOD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
292 | WOOG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
293 | WOOL | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
294 | WOSO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
295 | WOWA | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
296 | YARA | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
297 | YARR | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
298 | YASO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
299 | YEPP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
300 | Z1313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
301 | Z1314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
302 | Z1326
303 | Z1327 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
304 | Z1350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
305 | Z300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
306 | Z454
307 | Z1553 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10

## INDEX
Firm Capacity for Embedded Generation (MVA)
|  |  | SUMMER |  |  |  |  | WINTER
Substation List | Substation Type |  | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2023 | 2024 | 2025 | 2026 | 2027
Agnes Water (66/22kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | AGWA | Agnes Water (66/22kV) | 44 | NCC Rating (MVA)
Aitkenvale (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | AITK | Aitkenvale (66/11kV) | 44 | Contracted non-network (MVA)
Alan Sherriff (132/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | ALSH | Alan Sherriff (132/11kV) | 44 | 10 PoE Load (MVA)
Alfred Street (33/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | ALST | Alfred Street (33/11kV) | 44 | LARn (MVA)
Allora (33/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | ALLO | Allora (33/11kV) | 44 | LARn (MW)
Atherton (66/22kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | ATHE | Atherton (66/22kV) | 44 | Power Factor at Peak Load
Awoonga (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 8.7 | 8.7 | 8.7 | 7.5 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | AWOO | Awoonga (66/11kV) | 44 | ECC Rating (MVA)
Ayr (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | AYRZ | Ayr (66/11kV) | 44 | 50 PoE Load (MVA)
Balberra (33/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BALB | Balberra (33/11kV) | 44 | 50 PoE Load > 95% (MVA)
Bambaroo (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BAMB | Bambaroo (66/11kV) | 44 | Hours PA > 95% Peak Load
Barcaldine (66/22kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BARC | Barcaldine (66/22kV) | 44 | Raw LAR (MVA)
Barcaldine BSP (132/66kV) | Bulk Supply | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | T072 | Barcaldine BSP (132/66kV) | 42 | Auto Trans Avail (MVA)
Bargara (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | BARG | Bargara (66/11kV) | 44 | Remote Trans Avail (MVA)
Barratta (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BARR | Barratta (66/11kV) | 44 | Manual Trans Avail (MVA)
Bedford Weir (66/22kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | BEWE | Bedford Weir (66/22kV) | 44 | Mobile Plant Avail (MVA)
Belgian Gardens (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | BEGA | Belgian Gardens (66/11kV) | 44 | Shed(30min)
Berserker (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | BERS | Berserker (66/11kV) | 44 | Shed(4Hour)
Biloela (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | BILO | Biloela (66/11kV) | 44 | Capacity for Embedded Generation (MVA)
Bingegang (66/22kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | BING | Bingegang (66/22kV) | 44 | Firm Capacity for Embedded Generation (MVA)
Black River (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | BLRI | Black River (66/11kV) | 44 | LARc (MVA)
Blackall (66/22kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | BLAK | Blackall (66/22kV) | 44 | LARc (MW)
Blackwater (66/22kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | BLAC | Blackwater (66/22kV) | 44 | Substation Category
Blackwater BSP (132/66kV) | Bulk Supply | Firm Capacity for Embedded Generation (MVA) | [10 empty] | T032 | Blackwater BSP (132/66kV) | 42 | Meets Security Standard
Bluewater (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BLUE | Bluewater (66/11kV) | 44
Boat Creek BSP (132/66kV) | Bulk Supply | Firm Capacity for Embedded Generation (MVA) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | T130 | Boat Creek BSP (132/66kV) | 42
Bohle (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | BOHL | Bohle (66/11kV) | 44
Boondooma Dam (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | BODA | Boondooma Dam (66/11kV) | 44
Bowen (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | BOWE | Bowen (66/11kV) | 44
Boyne Residential (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | BORE | Boyne Residential (66/11kV) | 44
Broadlea BSP (132/66kV) | Bulk Supply | Firm Capacity for Embedded Generation (MVA) | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | T198 | Broadlea BSP (132/66kV) | 42
Broxburn (33/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | BROX | Broxburn (33/11kV) | 44
Bullyard (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | BULL | Bullyard (66/11kV) | 44
Bundaberg BSP (132/66kV) | Bulk Supply | Firm Capacity for Embedded Generation (MVA) | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | BUND | Bundaberg BSP (132/66kV) | 42
Bundaberg Central (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | BUCE | Bundaberg Central (66/11kV) | 44
Cairns City (132/22kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | CACI | Cairns City (132/22kV) | 44
Cairns North (132/22kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | CANO | Cairns North (132/22kV) | 44
Calen (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | CALE | Calen (66/11kV) | 44
Calliope (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | CALL | Calliope (66/11kV) | 44
Canning Street (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | CAST | Canning Street (66/11kV) | 44
Cannonvale (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | CANN | Cannonvale (66/11kV) | 44
Cape Ferguson (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAFE | Cape Ferguson (66/11kV) | 44
Cape River (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CARI | Cape River (66/11kV) | 44
Cape River East 132/66kV (66/33kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CPRE | Cape River East 132/66kV (66/33kV) | 44
Carmila (33/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CARM | Carmila (33/11kV) | 44
Cecil Plains (33/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | CEPL | Cecil Plains (33/11kV) | 44
Charleville (66/2211kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | CHAR | Charleville (66/2211kV) | 44
Charleville 11kV (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Z1313 | Charleville 11kV (66/11kV) | 44
Charleville 22kV (66/22kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Z1314 | Charleville 22kV (66/22kV) | 44
Charters Towers (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | CHTO | Charters Towers (66/11kV) | 44
Childers (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | CHIL | Childers (66/11kV) | 44
Chillagoe (66/22kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CHIA | Chillagoe (66/22kV) | 44
Chinchilla BSP (132/33kV) | Bulk Supply | Firm Capacity for Embedded Generation (MVA) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | CHIN | Chinchilla BSP (132/33kV) | 42
Chinchilla Town (33/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | CHTW | Chinchilla Town (33/11kV) | 44
Chumvale BSP (220/66kV) | Bulk Supply | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CHUM | Chumvale BSP (220/66kV) | 42
Clare South (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CLSO | Clare South (66/11kV) | 44
Clermont (66/22kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | CLER | Clermont (66/22kV) | 44
Clermont BSP (132/66kV) | Bulk Supply | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CLBS | Clermont BSP (132/66kV) | 42
Clifton (33/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | CLIF | Clifton (33/11kV) | 44
Clinton (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | CLIN | Clinton (66/11kV) | 44
Cloncurry (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | CLON | Cloncurry (66/11kV) | 44
Columboola BSP (132/33kV) | Bulk Supply | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | COLU | Columboola BSP (132/33kV) | 42
Comet (66/22kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | COME | Comet (66/22kV) | 44
Cooktown (66/22kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | COOK | Cooktown (66/22kV) | 44
Coominglah (66/22kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | COOM | Coominglah (66/22kV) | 44
Craiglie (132/22kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | CRAI | Craiglie (132/22kV) | 44
Cranbrook (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | CRAN | Cranbrook (66/11kV) | 44
Crediton (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRED | Crediton (66/11kV) | 44
Crows Nest (33/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CRNE | Crows Nest (33/11kV) | 44
Croydon (66/22kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | CROY | Croydon (66/22kV) | 44
Cunnamulla (66/22kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | CUNN | Cunnamulla (66/22kV) | 44
Cunnamulla 11kV (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | [10 empty] | Z1326 | Cunnamulla 11kV (66/11kV) | 44
Cunnamulla 22kV (66/22kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | Z1327 | Cunnamulla 22kV (66/22kV) | 44
Daandine BSP (110/33kV) | Bulk Supply | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | T188 | Daandine BSP (110/33kV) | 42
Dalby Central (33/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | DACE | Dalby Central (33/11kV) | 44
Dalby East BSP (110/33kV) | Bulk Supply | Firm Capacity for Embedded Generation (MVA) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | T002 | Dalby East BSP (110/33kV) | 42
Dan Gleeson (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | DAGL | Dan Gleeson (66/11kV) | 44
Degilbo (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEGI | Degilbo (66/11kV) | 44
Dimbulah (66/22kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DIMB | Dimbulah (66/22kV) | 44
Disraeli (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DISR | Disraeli (66/11kV) | 44
Duchess Road (132/66kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | DURO | Duchess Road (132/66kV) | 44
Duchess Road (11/66kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Duchr2 | Duchess Road (11/66kV) | 44
Dysart (66/22kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | DYSA | Dysart (66/22kV) | 44
East Ayr (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | EAAY | East Ayr (66/11kV) | 44
East Bundaberg (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | EABU | East Bundaberg (66/11kV) | 44
East Toowoomba (33/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | EATO | East Toowoomba (33/11kV) | 44
Eidsvold (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | EIDS | Eidsvold (66/11kV) | 44
Ellwoods Road (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | 4.1 | ELRO | Ellwoods Road (66/11kV) | 44
Emerald (66/22kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | EMER | Emerald (66/22kV) | 44
Eton (33/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | ETON | Eton (33/11kV) | 44
Eungella Dam (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | [10 empty] | EUDA | Eungella Dam (66/11kV) | 44 | bar: SUMMER 2023/24 to WINTER 2027
Evelyn (66/22kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | EVEL | Evelyn (66/22kV) | 44
Farleigh (33/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | FARL | Farleigh (33/11kV) | 44
Farnsfield (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | FARN | Farnsfield (66/11kV) | 44
Frenchville (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | FREN | Frenchville (66/11kV) | 44
Friend Street (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | GLFS | Friend Street (66/11kV) | 44
Garbutt (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | GARB | Garbutt (66/11kV) | 44
Gayndah (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | GAYN | Gayndah (66/11kV) | 44
Georgetown (66/22kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | GEOR | Georgetown (66/22kV) | 44
Georgetown BSP (132/66kV) | Bulk Supply | Firm Capacity for Embedded Generation (MVA) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | GEOR1 | Georgetown BSP (132/66kV) | 42
Giru (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | 3.3 | GIRU | Giru (66/11kV) | 44
Givelda (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | GIVE | Givelda (66/11kV) | 44
Gladstone North BSP (132/66kV) | Bulk Supply | Firm Capacity for Embedded Generation (MVA) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | GLNO | Gladstone North BSP (132/66kV) | 42
Gladstone South (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | GLSO | Gladstone South (66/11kV) | 44
Gladstone South BSP (132/66kV) | Bulk Supply | Firm Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | T019 | Gladstone South BSP (132/66kV) | 42
Glenden (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | GLEN | Glenden (66/11kV) | 44
Glenelg (66/33kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | GLEE | Glenelg (66/33kV) | 44
Glenella 11kV (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | GLEL | Glenella 11kV (66/11kV) | 44
Glenella 33kV (66/33kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | GLEL33 | Glenella 33kV (66/33kV) | 44
Gooburrum (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | [10 empty] | GOOB | Gooburrum (66/11kV) | 44 | bar: SUMMER 2023/24 to WINTER 2027
Gooburrum (66/3.3kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Z1350 | Gooburrum (66/3.3kV) | 44
Gootchie (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | GOOT | Gootchie (66/11kV) | 44
Gracemere (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | [10 empty] | Gracem | Gracemere (66/11kV) | 41
Granite Creek (66/22kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | GRCR | Granite Creek (66/22kV) | 44
Granite Creek BSP (132/66kV) | Bulk Supply | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | T166 | Granite Creek BSP (132/66kV) | 42
Greenvale (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | GREN | Greenvale (66/11kV) | 44
Gumlu (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | GUML | Gumlu (66/11kV) | 44
Guthalungra (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | GUTH | Guthalungra (66/11kV) | 44
Haughton (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | HAPU | Haughton (66/11kV) | 44
Helenvale (66/22kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | HELE | Helenvale (66/22kV) | 44
Hermit Park (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | HEPA | Hermit Park (66/11kV) | 44
Highfields (33/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | HIGH | Highfields (33/11kV) | 44
Home Hill (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | HOHI | Home Hill (66/11kV) | 44
Howard (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | HOWA | Howard (66/11kV) | 44
Hughenden (66/33kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | HUGH | Hughenden (66/33kV) | 44
Ilbilbie (33/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ILBI | Ilbilbie (33/11kV) | 44
Ingham (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | INGH | Ingham (66/11kV) | 44
Ingham BSP (132/66kV) | Bulk Supply | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | T047 | Ingham BSP (132/66kV) | 42
Isis BSP (132/66kV) | Bulk Supply | Firm Capacity for Embedded Generation (MVA) | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | ISIS | Isis BSP (132/66kV) | 42
Jandowae (33/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | JAND | Jandowae (33/11kV) | 44
Jardine Creek (66/132kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | [10 empty] | JCRK | Jardine Creek (66/132kV) | 44
Jarvisfield (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | JARV | Jarvisfield (66/11kV) | 44
Jubilee Pocket (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | JUPO | Jubilee Pocket (66/11kV) | 44
Julia Creek (66/33kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | JUCR | Julia Creek (66/33kV) | 44
Kaimkillenbun (33/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | [10 empty] | KAIM | Kaimkillenbun (33/11kV) | 44 | bar: SUMMER 2023/24 to WINTER 2027
Kalamia (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | KALA | Kalamia (66/11kV) | 44
Kearneys Spring (110/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | KESP | Kearneys Spring (110/11kV) | 44
Kelsey Creek East (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | KECE | Kelsey Creek East (66/11kV) | 44
Kidston (132/6.6kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | KIDS | Kidston (132/6.6kV) | 44
Kilkivan BSP (132/66kV) | Bulk Supply | Firm Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | KILK | Kilkivan BSP (132/66kV) | 42
Kilkivan Town (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | KITO | Kilkivan Town (66/11kV) | 44
Killarney (33/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | KILL | Killarney (33/11kV) | 44
Kingaroy (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | KING | Kingaroy (66/11kV) | 44
Kirknie (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | KIRK | Kirknie (66/11kV) | 44
Kogan Creek (33/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | KOCR | Kogan Creek (33/11kV) | 44
Koumala (33/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | KOUM | Koumala (33/11kV) | 44
Laguna Quays (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | LAQU | Laguna Quays (66/11kV) | 44
Lakeland (66/22kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | LAKE | Lakeland (66/22kV) | 44
Lakeland BSP (132/66kV) | Bulk Supply | Firm Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | T159 | Lakeland BSP (132/66kV) | 42
Lakes Creek (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | LACR | Lakes Creek (66/11kV) | 44
Lannercost (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | LANN | Lannercost (66/11kV) | 44
Littlemore (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | [10 empty] | LITT | Littlemore (66/11kV) | 44 | bar: SUMMER 2023/24 to WINTER 2027
Longreach (66/22kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | LONG | Longreach (66/22kV) | 44
Louisa Creek (33/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | LOCR | Louisa Creek (33/11kV) | 44
Louisa Creek BSP (132/33kV) | Bulk Supply | Firm Capacity for Embedded Generation (MVA) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | T176 | Louisa Creek BSP (132/33kV) | 42
Lucinda (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | LUCI | Lucinda (66/11kV) | 44
Lyndley Lane (33/22kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | LYLA | Lyndley Lane (33/22kV) | 44
Mackay City (33/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | MACT | Mackay City (33/11kV) | 44
Macknade (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MACN | Macknade (66/11kV) | 44
Malchi (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | MALC | Malchi (66/11kV) | 44
Mareeba (66/22kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | MARE | Mareeba (66/22kV) | 44
Marian South (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MASO | Marian South (66/11kV) | 44
Mary Kathleen (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MAKA | Mary Kathleen (66/11kV) | 44
Maryborough BSP (132/66kV) | Bulk Supply | Firm Capacity for Embedded Generation (MVA) | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | MARY | Maryborough BSP (132/66kV) | 42
Maryborough City (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | MACI | Maryborough City (66/11kV) | 44
Max Fulton (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | MAFU | Max Fulton (66/11kV) | 44
McKinley Creek (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | MCCR | McKinley Creek (66/11kV) | 44
Meadowvale (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | MEAD | Meadowvale (66/11kV) | 44
Meandarra (33/22kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | [10 empty] | MEAN | Meandarra (33/22kV) | 44 | bar: SUMMER 2023/24 to WINTER 2027
Merinda (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | MERI | Merinda (66/11kV) | 44
Meringandan (33/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | MERN | Meringandan (33/11kV) | 44
Middlemount (66/22kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | MIDD | Middlemount (66/22kV) | 44
Miles | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | MICO | Miles | 44
Miles (33/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MILE | Miles (33/11kV) | 44
Millaroo (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MILL | Millaroo (66/11kV) | 44
Millchester (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MILC | Millchester (66/11kV) | 44
Millchester BSP (132/66kV) | Bulk Supply | Firm Capacity for Embedded Generation (MVA) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | T095 | Millchester BSP (132/66kV) | 42
Millmerran (33/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MILM | Millmerran (33/11kV) | 44
Mingela (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MING | Mingela (66/11kV) | 44
Mirani (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MIRA | Mirani (66/11kV) | 44
Miriam Vale (66/22kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MIVA | Miriam Vale (66/22kV) | 44
Mitchell (33/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0.75 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 | 0 | MITC | Mitchell (33/11kV) | 44
Mona Park (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MOPA | Mona Park (66/11kV) | 44
Monduran Dam (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MODA | Monduran Dam (66/11kV) | 44
Monduran Dam DNR (66/3.3kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Z300 | Monduran Dam DNR (66/3.3kV) | 44
Monto (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 6.25 | 6.25 | 6.25 | 6.25 | 6.25 | 6.25 | 6.25 | 6.25 | 6.25 | 6.25 | MONT | Monto (66/11kV) | 44
Moorvale (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MOOR | Moorvale (66/11kV) | 44
Mossman (66/22kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MOSS | Mossman (66/22kV) | 44
Mount Fox (66/33kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MOFO | Mount Fox (66/33kV) | 44
Mount Leyshon Pump (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MOLP | Mount Leyshon Pump (66/11kV) | 44
Mount Rooper (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MORO | Mount Rooper (66/11kV) | 44
Moura (11/22kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | [10 empty] | MOUR | Moura (11/22kV) | 44
Mt Bassett (33/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | MOBA | Mt Bassett (33/11kV) | 44
Mt Garnet (66/22kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | MOGA | Mt Garnet (66/22kV) | 44
Mt Molloy (66/22kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | MOMO | Mt Molloy (66/22kV) | 44
Mt Morgan (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | MOMR | Mt Morgan (66/11kV) | 44
Mt Mowbullan (33/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MOMW | Mt Mowbullan (33/11kV) | 44
Mt Sibley (33/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MOSI | Mt Sibley (33/11kV) | 44
Mundubbera Town (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | MUTO | Mundubbera Town (66/11kV) | 44
Murgon (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 5.8 | 5.8 | 5.8 | 5.8 | 5.8 | 5.8 | 5.8 | 5.8 | 5.8 | 5.8 | MURG | Murgon (66/11kV) | 44
Mutarnee (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | MUTA | Mutarnee (66/11kV) | 44
Nanango (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | NANA | Nanango (66/11kV) | 44
Nandi (33/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | [10 empty] | NAND | Nandi (33/11kV) | 44 | bar: SUMMER 2023/24 to WINTER 2027
Nebo (132/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NEBO | Nebo (132/11kV) | 44
Neil Smith (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | NESM | Neil Smith (66/11kV) | 44
Normanton (66/22kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | NORM | Normanton (66/22kV) | 44
North Cloncurry (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | NOCL | North Cloncurry (66/11kV) | 44
North Mackay (33/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | NOMA | North Mackay (33/11kV) | 44
North Street (33/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 15 | 15 | 0 | 0 | 0 | 15 | 15 | NOST | North Street (33/11kV) | 44
Norwin (33/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | NORW | Norwin (33/11kV) | 44
Oakey (33/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | OAKE | Oakey (33/11kV) | 44
Oakey BSP (110/33kV) | Bulk Supply | Firm Capacity for Embedded Generation (MVA) | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | T189 | Oakey BSP (110/33kV) | 42
Oonoonba (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | OONN | Oonoonba (66/11kV) | 44
Owanyilla (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | OWAN | Owanyilla (66/11kV) | 44
Pampas (33/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PAMP | Pampas (33/11kV) | 44
Pandoin (66/22kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | PAND | Pandoin (66/22kV) | 44
Parkhurst (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | PARK | Parkhurst (66/11kV) | 44
Peranga (33/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PERA | Peranga (33/11kV) | 44
Peter Arlett (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | PEAR | Peter Arlett (66/11kV) | 44
Pialba (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 12.5 | 12.5 | 12.5 | 12.5 | 0 | 12.5 | 12.5 | 12.5 | 12.5 | 0 | PIAL | Pialba (66/11kV) | 44
Pialba South (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 12.5 | 0 | 0 | 0 | 0 | 12.5 | PISO | Pialba South (66/11kV) | 44
Pinnacle (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | PINN | Pinnacle (66/11kV) | 44
Pirrinuan (33/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PIRR | Pirrinuan (33/11kV) | 44
Planella (33/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | PLAN | Planella (33/11kV) | 44
Pleystowe (33/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | PLEY | Pleystowe (33/11kV) | 44
Point Vernon (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | POVE | Point Vernon (66/11kV) | 44
Pozieres (33/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | POZI | Pozieres (33/11kV) | 44
Proserpine Mill (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PRMI | Proserpine Mill (66/11kV) | 44
Proston (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | PROT | Proston (66/11kV) | 44
Purrawunda (33/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 6.25 | 6.25 | 6.25 | 6.25 | 6.25 | 6.25 | 6.25 | 6.25 | 6.25 | 6.25 | PURR | Purrawunda (33/11kV) | 44
Quilpie (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | QUIL | Quilpie (66/11kV) | 44
Raglan (66/22kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | RAGL | Raglan (66/22kV) | 44
Rasmussen (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | RASM | Rasmussen (66/11kV) | 44
Ravenshoe (66/22kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | RAVE | Ravenshoe (66/22kV) | 44
Ravenswood (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | RAVN | Ravenswood (66/11kV) | 44
Richmond (66/33kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | RICH | Richmond (66/33kV) | 44
Rockhampton Glenmore (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | ROGL | Rockhampton Glenmore (66/11kV) | 44
Rockhampton South (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | ROSO | Rockhampton South (66/11kV) | 44
Rocky Street (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | ROST | Rocky Street (66/11kV) | 44
Rolleston (66/22kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | ROLE | Rolleston (66/22kV) | 44
Rolleston BSP (132/66kV) | Bulk Supply | Firm Capacity for Embedded Generation (MVA) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | T163 | Rolleston BSP (132/66kV) | 42
Rollingstone (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ROLL | Rollingstone (66/11kV) | 44
Roma 33kV BSP (132/33kV) | Bulk Supply | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | T083 | Roma 33kV BSP (132/33kV) | 42
Roma 66kV BSP (132/66kV) | Bulk Supply | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ROMA | Roma 66kV BSP (132/66kV) | 42
Roma East (33/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | ROEA | Roma East (33/11kV) | 44
Roma West (33/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 3.15 | 3.15 | 3.15 | 3.15 | 3.15 | 3.15 | 3.15 | 3.15 | 3.15 | 3.15 | ROWE | Roma West (33/11kV) | 44
Roo Works (33/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ROWO | Roo Works (33/11kV) | 44
Rosella (33/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | ROSE | Rosella (33/11kV) | 44
Ross Plains (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | ROPL | Ross Plains (66/11kV) | 44
Sarina (33/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | SARI | Sarina (33/11kV) | 44
Saunders (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | SAUN | Saunders (66/11kV) | 44
Shutehaven (66/22kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | SHUT | Shutehaven (66/22kV) | 44
Skid B (Cawdor) (33/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CAWD | Skid B (Cawdor) (33/11kV) | 44
Skid D (Landing Road) (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | LARO | Skid D (Landing Road) (66/11kV) | 44
Skid E (Chinchilla) (33/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | SKIE | Skid E (Chinchilla) (33/11kV) | 44
Skid K (Charlton) (33/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | CHAL | Skid K (Charlton) (33/11kV) | 44
South Blackwater (66/22kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | SOBL | South Blackwater (66/22kV) | 44
South Bundaberg (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | SOBU | South Bundaberg (66/11kV) | 44
South Kolan (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | SOKO | South Kolan (66/11kV) | 44
South Mackay (33/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | SOMA | South Mackay (33/11kV) | 44
South Toowoomba (33/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | SOTO | South Toowoomba (33/11kV) | 44
South Toowoomba BSP (110/33kV) | Bulk Supply | Firm Capacity for Embedded Generation (MVA) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | T043 | South Toowoomba BSP (110/33kV) | 42
St. George (66/33kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | SAGE | St. George (66/33kV) | 44
St. George Town (33/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | SAGT | St. George Town (33/11kV) | 44
Stamford (66/33kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | STAM | Stamford (66/33kV) | 44
Stanthorpe BSP (110/33kV) | Bulk Supply | Firm Capacity for Embedded Generation (MVA) | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | STAN | Stanthorpe BSP (110/33kV) | 42
Stanthorpe Town (33/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | STTO | Stanthorpe Town (33/11kV) | 44
Stuart (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | STUA | Stuart (66/11kV) | 44
Tanby (66/22kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | TANB | Tanby (66/22kV) | 44
Tara (33/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TARA | Tara (33/11kV) | 44
Theodore (66/22kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | THEO | Theodore (66/22kV) | 44
Tieri (66/22kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | TIER | Tieri (66/22kV) | 44
Toowoomba Central (110/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | TWCE | Toowoomba Central (110/11kV) | 44
Torquay (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | TORQ | Torquay (66/11kV) | 44
Torrington (33/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | TORR | Torrington (33/11kV) | 44
Torrington BSP (110/33kV) | Bulk Supply | Firm Capacity for Embedded Generation (MVA) | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | T116 | Torrington BSP (110/33kV) | 42
Townsville Port (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | TOPO | Townsville Port (66/11kV) | 44
Tuan (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | TUAN | Tuan (66/11kV) | 44
Vermont (66/22kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | VERM | Vermont (66/22kV) | 44
Waggamba 132/33kV (66/33kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | [10 empty] | WAGG | Waggamba 132/33kV (66/33kV) | 44
Waggamba 132/66kV (66/66kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | [10 empty] | Z454 | Waggamba 132/66kV (66/66kV) | 44
Waggamba BSP (132/66kV) | Bulk Supply | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | T156 | Waggamba BSP (132/66kV) | 42
Wallaville (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | WALL | Wallaville (66/11kV) | 44
Wandoan (33/22kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | WAND | Wandoan (33/22kV) | 44
Warwick BSP (110/33kV) | Bulk Supply | Firm Capacity for Embedded Generation (MVA) | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | T058 | Warwick BSP (110/33kV) | 42
Warwick East (33/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | WAEA | Warwick East (33/11kV) | 44
West Bundaberg (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | WEBU | West Bundaberg (66/11kV) | 44
West Dalby (33/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 6.25 | 6.25 | 6.25 | 6.25 | 6.25 | 6.25 | 6.25 | 6.25 | 6.25 | 6.25 | WEDA | West Dalby (33/11kV) | 44
West Mackay (33/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | WEMA | West Mackay (33/11kV) | 44
West Toowoomba (33/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | WETO | West Toowoomba (33/11kV) | 44
West Warwick (33/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | WEWA | West Warwick (33/11kV) | 44
Winton (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | WINT | Winton (66/11kV) | 44
Wirralie (66/33kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WIRR | Wirralie (66/33kV) | 44
Woodgate (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WOOG | Woodgate (66/11kV) | 44
Woodhouse Station (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WOOD | Woodhouse Station (66/11kV) | 44
Woodstock South (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | WOSO | Woodstock South (66/11kV) | 44
Woolooga (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | WOOL | Woolooga (66/11kV) | 44
Wowan (66/22kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | WOWA | Wowan (66/22kV) | 44
Yarraman (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | YARR | Yarraman (66/11kV) | 44
Yarranlea BSP (110/33kV) | Bulk Supply | Firm Capacity for Embedded Generation (MVA) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | YARA | Yarranlea BSP (110/33kV) | 42
Yarranlea South (33/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | YASO | Yarranlea South (33/11kV) | 44
Yeppoon (66/11kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | YEPP | Yeppoon (66/11kV) | 44
Yeppoon (11/22kV) | Zone Substation | Firm Capacity for Embedded Generation (MVA) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | Z1553 | Yeppoon (11/22kV) | 44

## AGWA
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | AGWA - Agnes Water (66/22kV) | [8 empty] | Supply |  | T166 - Granite Creek BSP
| Description |  |  |  | Region is Capricornia
Transformer size is 2x66/22kV 15/20MVA ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.7% W -1.2%2025 S -0.6% W -1.4%2026 S -0.1% W -1.1%2027 S 0.7% W -0.5%
|  |  | Latest Peak Compensated Load | [5 empty] | 6.1 MVA on 05/07/2022 at 17:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 48 | 48 | 48 |  | 48 |  | 48 | 55.6 |  | 55.6 |  | 55.6 | 55.6 | 55.6
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 5.6 | 5.6 | 5.6 |  | 5.6 |  | 5.7 | 6.4 |  | 6.3 |  | 6.3 | 6.2 | 6.1
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.999 | 0.999 | 0.999 |  | 0.999 |  | 0.999 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | ECC Rating (MVA) |  | 24 | 24 | 24 |  | 24 |  | 24 | 27.8 |  | 27.8 |  | 27.8 | 27.8 | 27.8
|  |  |  | 50 PoE Load (MVA) |  | 5.4 | 5.3 | 5.3 |  | 5.4 |  | 5.4 | 5.8 |  | 5.7 |  | 5.6 | 5.6 | 5.5
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Hours PA > 95% Peak Load |  | 13 | 13 | 13 |  | 13 |  | 13 | 13 |  | 13 |  | 13 | 13 | 13
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 2.5 | 2.5 | 2.5 |  | 2.5 |  | 2.5 | 2.5 |  | 2.5 |  | 2.5 | 2.5 | 2.5
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 30 | 30 | 30 |  | 30 |  | 30 | 30 |  | 30 |  | 30 | 30 | 30
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 15 | 15 | 15 |  | 15 |  | 15 | 15 |  | 15 |  | 15 | 15 | 15
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## AITK
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | AITK - Aitkenvale (66/11kV) | [8 empty] | Supply |  | TMES - Townsville Mesh
| Description |  |  |  | Region is Nth Queensland
Transformer size is 2x66/11kV 15/20/25MVA ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.2% W -0.9%2025 S -1.6% W -1.5%2026 S -1.0% W -1.0%2027 S -0.4% W -0.9
|  |  | Latest Peak Compensated Load | [5 empty] | 19.1 MVA on 21/11/2022 at 16:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 61.6 | 61.6 | 61.6 |  | 61.6 |  | 61.6 | 64.7 |  | 64.7 |  | 64.7 | 64.7 | 64.7
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 25.3 | 24.9 | 24.6 |  | 24.5 |  | 24.6 | 13.3 |  | 13.2 |  | 13 | 12.8 | 12.7
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.998 | 0.998 | 0.998 |  | 0.998 |  | 0.998 | 0.988 |  | 0.988 |  | 0.988 | 0.988 | 0.988
|  |  |  | ECC Rating (MVA) |  | 34.3 | 34.3 | 34.3 |  | 34.3 |  | 34.3 | 35.8 |  | 35.8 |  | 35.8 | 35.8 | 35.8
|  |  |  | 50 PoE Load (MVA) |  | 22 | 21.7 | 21.5 |  | 21.4 |  | 21.5 | 12.7 |  | 12.6 |  | 12.4 | 12.3 | 12.1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 1.1 | 1.1 | 1.1 |  | 1.1 |  | 1.1 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  |  | Hours PA > 95% Peak Load |  | 12 | 12 | 12 |  | 12 |  | 12 | 12 |  | 12 |  | 12 | 12 | 12
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 25 | 25 | 25 |  | 25 |  | 25 | 25 |  | 25 |  | 25 | 25 | 25
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 15 | 15 | 15 |  | 15 |  | 15 | 15 |  | 15 |  | 15 | 15 | 15
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## ALLO
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | ALLO - Allora (33/11kV) | [8 empty] | Supply |  | T058 - Warwick BSP
| Description |  |  |  | Region is South West
Transformer size is 2x33/11kV 3MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.7% W -0.3%2025 S -0.5% W -0.1%2026 S -0.1% W 0.2%,2027 S 0.6% W 0.2%
|  |  | Latest Peak Compensated Load | [5 empty] | 5.1 MVA on 04/07/2022 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 7.3 | 7.3 | 7.3 |  | 7.3 |  | 11 | 7.9 |  | 7.9 |  | 7.9 | 7.9 | 7.9
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 5.2 | 5.1 | 5.1 |  | 5.2 |  | 5.2 | 5.4 |  | 5.4 |  | 5.4 | 5.4 | 5.4
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.96 | 0.96 | 0.96 |  | 0.96 |  | 0.96 | 0.988 |  | 0.988 |  | 0.988 | 0.988 | 0.988
|  |  |  | ECC Rating (MVA) |  | 4.2 | 4.2 | 4.2 |  | 4.2 |  | 8.3 | 4.4 |  | 4.4 |  | 4.4 | 4.4 | 4.4
|  |  |  | 50 PoE Load (MVA) |  | 4.9 | 4.9 | 4.9 |  | 4.9 |  | 5 | 5.2 |  | 5.2 |  | 5.2 | 5.2 | 5.2
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Hours PA > 95% Peak Load |  | 9.5 | 9.5 | 9.5 |  | 9.5 |  | 9.5 | 9.5 |  | 9.5 |  | 9.5 | 9.5 | 9.5
|  |  |  | Raw LAR (MVA) |  | 0.7 | 0.7 | 0.7 |  | 0.7 |  |  | 0.8 |  | 0.8 |  | 0.8 | 0.8 | 0.8
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 6 | 6 | 6 |  | 6 |  | 6 | 6 |  | 6 |  | 6 | 6 | 6
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 3 | 3 | 3 |  | 3 |  | 3 | 3 |  | 3 |  | 3 | 3 | 3
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## ALSH
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | ALSH - Alan Sherriff (132/11kV) | [8 empty] | Supply |  | QASF - Alan Sherriff TCP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 2x132/11kV 18/22.5/30MVA ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.1% W -0.2%2025 S -0.8% W -0.0%2026 S -0.2% W 0.3%,2027 S 0.7% W 0.6%
|  |  | Latest Peak Compensated Load | [5 empty] | 29 MVA on 02/02/2023 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 70 | 70 | 70 |  | 70 |  | 70 | 73.5 |  | 73.5 |  | 73.5 | 73.5 | 73.5
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 31.2 | 31 | 30.9 |  | 31.1 |  | 31.6 | 20.2 |  | 20.2 |  | 20.2 | 20.2 | 20.4
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.98 | 0.98 | 0.98 |  | 0.98 |  | 0.98 | 0.996 |  | 0.996 |  | 0.996 | 0.996 | 0.996
|  |  |  | ECC Rating (MVA) |  | 38.5 | 38.5 | 38.5 |  | 38.5 |  | 38.5 | 40.3 |  | 40.3 |  | 40.3 | 40.3 | 40.3
|  |  |  | 50 PoE Load (MVA) |  | 29.3 | 29 | 29 |  | 29.2 |  | 29.6 | 19.9 |  | 19.8 |  | 19.8 | 19.9 | 20
|  |  |  | 50 PoE Load > 95% (MVA) |  | 1.5 | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Hours PA > 95% Peak Load |  | 8.5 | 8.5 | 8.5 |  | 8.5 |  | 8.5 | 8.5 |  | 8.5 |  | 8.5 | 8.5 | 8.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 36 | 36 | 36 |  | 36 |  | 36 | 36 |  | 36 |  | 36 | 36 | 36
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 18 | 18 | 18 |  | 18 |  | 18 | 18 |  | 18 |  | 18 | 18 | 18
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## ALST
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | ALST - Alfred Street (33/11kV) | [8 empty] | Supply |  | MACK - Mackay BSP
| Description |  |  |  | Region is Mackay
Transformer size is 2x33/11kV 35/40MVA ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.0% W -0.5%2025 S -1.2% W -0.9%2026 S -0.6% W -0.4%2027 S 0.1% W -0.3%
|  |  | Latest Peak Compensated Load | [5 empty] | 20.9 MVA on 21/11/2022 at 13:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 90.7 | 90.7 | 90.7 |  | 90.7 |  | 90.7 | 93.7 |  | 93.7 |  | 93.7 | 93.7 | 93.7
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 23.9 | 23.6 | 23.5 |  | 23.5 |  | 23.7 | 14.3 |  | 14.3 |  | 14.1 | 14.1 | 14
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.98 | 0.98 | 0.98 |  | 0.98 |  | 0.98 | 0.946 |  | 0.946 |  | 0.946 | 0.946 | 0.946
|  |  |  | ECC Rating (MVA) |  | 48 | 48 | 48 |  | 48 |  | 48 | 50.4 |  | 50.4 |  | 50.4 | 50.4 | 50.4
|  |  |  | 50 PoE Load (MVA) |  | 22 | 21.7 | 21.6 |  | 21.6 |  | 21.8 | 13.5 |  | 13.5 |  | 13.3 | 13.3 | 13.2
|  |  |  | 50 PoE Load > 95% (MVA) |  | 1.1 | 1.1 | 1.1 |  | 1.1 |  | 1.1 | 0.7 |  | 0.7 |  | 0.7 | 0.7 | 0.7
|  |  |  | Hours PA > 95% Peak Load |  | 4.5 | 4.5 | 4.5 |  | 4.5 |  | 4.5 | 4.5 |  | 4.5 |  | 4.5 | 4.5 | 4.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 70 | 70 | 70 |  | 70 |  | 70 | 70 |  | 70 |  | 70 | 70 | 70
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 35 | 35 | 35 |  | 35 |  | 35 | 35 |  | 35 |  | 35 | 35 | 35
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## ATHE
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | ATHE - Atherton (66/22kV) | [8 empty] | Supply |  | TURK - Turkinje 66kV BSP
| Description |  |  |  | Region is Far North
Transformer size is 1x66/22kV 24/30/40MVA ONAN/ODAN/ODAF;1x66/22kV 24/30/40MVA ONAN/ONAF/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 1.7 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.4% W 0.1%,2025 S -0.4% W 0.4%,2026 S 0.1% W 0.6%, 2027 S 0.8% W 0.7%
|  |  | Latest Peak Compensated Load | [5 empty] | 23.9 MVA on 01/11/2022 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 88.1 | 88.1 | 88.1 |  | 88.1 |  | 88.1 | 97.4 |  | 97.4 |  | 97.4 | 97.4 | 97.4
|  |  |  | Contracted non-network (MVA) |  | 0.8 | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | 10 PoE Load (MVA) |  | 24.4 | 24.3 | 24.4 |  | 24.6 |  | 25 | 24.7 |  | 24.8 |  | 24.9 | 25 | 25.2
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.999 | 0.999 | 0.999 |  | 0.999 |  | 0.999 | 0.999 |  | 0.999 |  | 0.999 | 0.999 | 0.999
|  |  |  | ECC Rating (MVA) |  | 50.8 | 50.8 | 50.8 |  | 50.8 |  | 50.8 | 53.5 |  | 53.5 |  | 53.5 | 53.5 | 53.5
|  |  |  | 50 PoE Load (MVA) |  | 23.6 | 23.5 | 23.5 |  | 23.7 |  | 24.1 | 24.3 |  | 24.4 |  | 24.4 | 24.6 | 24.8
|  |  |  | 50 PoE Load > 95% (MVA) |  | 1.2 | 1.2 | 1.2 |  | 1.2 |  | 1.2 | 1.2 |  | 1.2 |  | 1.2 | 1.2 | 1.2
|  |  |  | Hours PA > 95% Peak Load |  | 37 | 37 | 37 |  | 37 |  | 37 | 37 |  | 37 |  | 37 | 37 | 37
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 48 | 48 | 48 |  | 48 |  | 48 | 48 |  | 48 |  | 48 | 48 | 48
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 24 | 24 | 24 |  | 24 |  | 24 | 24 |  | 24 |  | 24 | 24 | 24
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## AWOO
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | AWOO - Awoonga (66/11kV) | [8 empty] | Supply |  | T019 - Gladstone South BSP
| Description |  |  |  | Region is Capricornia
Transformer size is 2x66/11kV 7.5/10MVA ONAF/OB
Capacity of commissioned Embedded Generation (with Connection Agreements) is 1.1 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.9% W -0.5%2025 S -0.6% W -0.1%2026 S -0.2% W 0.1%,2027 S 0.5% W 0.2%
|  |  | Latest Peak Compensated Load | [5 empty] | 6.2 MVA on 13/02/2023 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 24.4 | 24.4 | 24.4 |  | 24.4 |  | 24.4 | 25.7 |  | 25.7 |  | 25.7 | 25.7 | 25.7
|  |  |  | Contracted non-network (MVA) |  | 1.1 | 1.1 | 1.1 |  | 1.1 |  | 1.1 | 1.1 |  | 1.1 |  | 1.1 | 1.1 | 1.1
|  |  |  | 10 PoE Load (MVA) |  | 6.2 | 7.6 | 7.5 |  | 7.6 |  | 7.6 | 6 |  | 7.3 |  | 7.3 | 7.3 | 7.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.967 | 0.967 | 0.953 |  | 0.967 |  | 0.953 | 0.969 |  | 0.969 |  | 0.969 | 0.969 | 0.969
|  |  |  | ECC Rating (MVA) |  | 14 | 14 | 14 |  | 14 |  | 14 | 14.5 |  | 14.5 |  | 14.5 | 14.5 | 14.5
|  |  |  | 50 PoE Load (MVA) |  | 6 | 7.5 | 7.4 |  | 7.5 |  | 7.5 | 5.8 |  | 7.2 |  | 7.2 | 7.2 | 7.2
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.3 | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.3 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  |  | Hours PA > 95% Peak Load |  | 166 | 166 | 166 |  | 166 |  | 166 | 166 |  | 166 |  | 166 | 166 | 166
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 17.5 | 17.5 | 17.5 |  | 15 |  | 17.5 | 17.5 |  | 17.5 |  | 17.5 | 17.5 | 17.5
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 8.7 | 8.7 | 8.7 |  | 7.5 |  | 8.7 | 8.7 |  | 8.7 |  | 8.7 | 8.7 | 8.7
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## AYRZ
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | AYRZ - Ayr (66/11kV) | [8 empty] | Supply |  | T193 - Clare South BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 2x66/11kV 7.5/10MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.9% W -0.3%2025 S -0.8% W -0.2%2026 S -0.3% W 0.1%,2027 S 0.3% W 0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 8.5 MVA on 14/12/2022 at 20:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 23.9 | 23.9 | 23.9 |  | 23.9 |  | 23.9 | 25.4 |  | 25.4 |  | 25.4 | 25.4 | 25.4
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 9.9 | 9.8 | 9.8 |  | 9.8 |  | 9.9 | 5.2 |  | 5.2 |  | 5.2 | 5.2 | 5.2
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.948 | 0.948 | 0.948 |  | 0.948 |  | 0.948 | 0.949 |  | 0.949 |  | 0.949 | 0.949 | 0.949
|  |  |  | ECC Rating (MVA) |  | 13.6 | 13.6 | 13.6 |  | 13.6 |  | 13.6 | 14.2 |  | 14.2 |  | 14.2 | 14.2 | 14.2
|  |  |  | 50 PoE Load (MVA) |  | 9.1 | 9 | 9 |  | 9 |  | 9.1 | 5 |  | 5 |  | 5 | 5 | 5
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Hours PA > 95% Peak Load |  | 14 | 14 | 14 |  | 14 |  | 14 | 14 |  | 14 |  | 14 | 14 | 14
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 15 | 15 | 15 |  | 15 |  | 15 | 15 |  | 15 |  | 15 | 15 | 15
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 7.5 | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 | 7.5
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## BALB
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | BALB - Balberra (33/11kV) | [8 empty] | Supply |  | T065 - Alligator Creek BSP
| Description |  |  |  | Region is Mackay
Transformer size is 1x33/11kV 5MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.8% W -0.7%2025 S -0.6% W -0.5%2026 S -0.1% W -0.1%2027 S 0.7% W 0.6%
|  |  | Latest Peak Compensated Load | [5 empty] | 2.5 MVA on 10/01/2023 at 19:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 7 | 7 | 7 |  | 7 |  | 7 | 7.5 |  | 7.5 |  | 7.5 | 7.5 | 7.5
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 2.7 | 2.7 | 2.7 |  | 2.7 |  | 2.7 | 1.3 |  | 1.2 |  | 1.2 | 1.2 | 1.2
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.964 | 0.964 | 0.964 |  | 0.964 |  | 0.964 | 0.981 |  | 0.981 |  | 0.981 | 0.981 | 0.981
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 2.6 | 2.6 | 2.6 |  | 2.6 |  | 2.6 | 1.1 |  | 1.1 |  | 1.1 | 1.1 | 1.1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 | 5 | 5
|  |  |  | Raw LAR (MVA) |  | 2.6 | 2.6 | 2.6 |  | 2.6 |  | 2.6 | 1.1 |  | 1.1 |  | 1.1 | 1.1 | 1.1
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 1.9 | 1.9 | 1.9 |  | 1.9 |  | 1.9 | 1.9 |  | 1.9 |  | 1.9 | 1.9 | 1.9
|  |  |  | Mobile Plant Avail (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 | 2 | 2
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 | 5 | 5
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## BAMB
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | BAMB - Bambaroo (66/11kV) | [8 empty] | Supply |  | T047 - Ingham BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/11kV 1.5MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.5% W -1.1%2025 S -1.3% W -0.7%2026 S -0.9% W -0.5%2027 S -0.3% W -0.5
|  |  | Latest Peak Compensated Load | [5 empty] | 0.3 MVA on 14/12/2022 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 2.2 | 2.2 | 2.2 |  | 2.2 |  | 2.2 | 2.2 |  | 2.2 |  | 2.2 | 2.2 | 2.2
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 0.4 | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.949 | 0.949 | 0.949 |  | 0.949 |  | 0.949 | 0.927 |  | 0.927 |  | 0.927 | 0.927 | 0.927
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 0.4 | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 35.5 | 35.5 | 35.5 |  | 35.5 |  | 35.5 | 35.5 |  | 35.5 |  | 35.5 | 35.5 | 35.5
|  |  |  | Raw LAR (MVA) |  | 0.4 | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 1.5 | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.5 | 1.5
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## BARC
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | BARC - Barcaldine (66/22kV) | [8 empty] | Supply |  | T072 - Barcaldine BSP
| Description |  |  |  | Region is Capricornia
Transformer size is 1x66/22kV 8/10MVA ONAN/ONAF; 1 x 66/22kV 25/32MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 28.4 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.9% W -0.4%2025 S -0.7% W -0.2%2026 S -0.3% W 0.1%,2027 S 0.5% W 0.2%
|  |  | Latest Peak Compensated Load | [5 empty] | 7.4 MVA on 08/12/2022 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 25.8 | 25.8 | 25.8 |  | 25.8 |  | 25.8 | 30 |  | 30 |  | 30 | 30 | 30
|  |  |  | Contracted non-network (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 7.5 | 7.5 | 7.5 |  | 7.5 |  | 7.6 | 7.1 |  | 7 |  | 7 | 7 | 7
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 1 | 1 | 1 |  | 1 |  | 1 | 0.986 |  | 0.986 |  | 0.986 | 0.986 | 0.986
|  |  |  | ECC Rating (MVA) |  | 14.2 | 14.2 | 14.2 |  | 14.2 |  | 14.2 | 15 |  | 15 |  | 15 | 15 | 15
|  |  |  | 50 PoE Load (MVA) |  | 7.2 | 7.2 | 7.1 |  | 7.2 |  | 7.3 | 6.8 |  | 6.7 |  | 6.7 | 6.7 | 6.7
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.4 | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Hours PA > 95% Peak Load |  | 4.5 | 4.5 | 4.5 |  | 4.5 |  | 4.5 | 4.5 |  | 4.5 |  | 4.5 | 4.5 | 4.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 | 5 | 5
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## BARG
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | BARG - Bargara (66/11kV) | [8 empty] | Supply |  | BUND - Bundaberg BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 2x66/11kV 15/18/25MVA ONAN/ODAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 4.4 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.2% W 0.1%,2025 S -0.2% W 0.7%,2026 S 0.3% W 0.9%, 2027 S 0.6% W 0.6%
|  |  | Latest Peak Compensated Load | [5 empty] | 14.6 MVA on 13/02/2023 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 69.9 | 69.9 | 69.9 |  | 69.9 |  | 69.9 | 74.8 |  | 74.8 |  | 74.8 | 74.8 | 74.8
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 14.8 | 14.8 | 14.8 |  | 14.9 |  | 15.1 | 15.4 |  | 15.4 |  | 15.5 | 15.6 | 15.7
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.995 | 0.995 | 0.995 |  | 0.995 |  | 0.995 | 0.998 |  | 0.998 |  | 0.998 | 0.998 | 0.998
|  |  |  | ECC Rating (MVA) |  | 37.4 | 37.4 | 37.4 |  | 37.4 |  | 37.4 | 37.4 |  | 37.4 |  | 37.4 | 37.4 | 37.4
|  |  |  | 50 PoE Load (MVA) |  | 14 | 14 | 14 |  | 14.1 |  | 14.3 | 14.1 |  | 14.1 |  | 14.2 | 14.4 | 14.5
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.7 | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.7 | 0.7
|  |  |  | Hours PA > 95% Peak Load |  | 8 | 8 | 8 |  | 8 |  | 8 | 8 |  | 8 |  | 8 | 8 | 8
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 30 | 30 | 30 |  | 30 |  | 30 | 30 |  | 30 |  | 30 | 30 | 30
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 15 | 15 | 15 |  | 15 |  | 15 | 15 |  | 15 |  | 15 | 15 | 15
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## BARR
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | BARR - Barratta (66/11kV) | [8 empty] | Supply |  | T193 - Clare South BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/11kV 5MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.0% W -0.5%2025 S -0.9% W -0.5%2026 S -0.4% W -0.2%2027 S 0.2% W -0.2%
|  |  | Latest Peak Compensated Load | [5 empty] | 2 MVA on 14/12/2022 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 5.6 | 5.6 | 5.6 |  | 5.6 |  | 5.6 | 6.3 |  | 6.3 |  | 6.3 | 6.3 | 6.3
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 2.5 | 2.5 | 2.5 |  | 2.5 |  | 2.5 | 1.2 |  | 1.2 |  | 1.2 | 1.2 | 1.2
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.865 | 0.865 | 0.865 |  | 0.865 |  | 0.865 | 0.897 |  | 0.897 |  | 0.897 | 0.897 | 0.897
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 2.4 | 2.3 | 2.3 |  | 2.3 |  | 2.4 | 1.1 |  | 1.1 |  | 1.1 | 1.1 | 1.1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 13.5 | 13.5 | 13.5 |  | 13.5 |  | 13.5 | 13.5 |  | 13.5 |  | 13.5 | 13.5 | 13.5
|  |  |  | Raw LAR (MVA) |  | 2.4 | 2.3 | 2.3 |  | 2.3 |  | 2.4 | 1.1 |  | 1.1 |  | 1.1 | 1.1 | 1.1
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | Mobile Plant Avail (MVA) |  | 2.4 | 2.4 | 2.4 |  | 2.4 |  | 2.4 | 2.4 |  | 2.4 |  | 2.4 | 2.4 | 2.4
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 4 | 4 | 4 |  | 4 |  | 4 | 4 |  | 4 |  | 4 | 4 | 4
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## BEGA
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | BEGA - Belgian Gardens (66/11kV) | [8 empty] | Supply |  | TMES - Townsville Mesh
| Description |  |  |  | Region is Nth Queensland
Transformer size is 2x66/11kV 19/26/32MVA ONAN/ODAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.2% W 0.6%,2025 S -0.1% W 0.8%,2026 S 0.4% W 1.1%, 2027 S 1.6% W 1.9%
|  |  | Latest Peak Compensated Load | [5 empty] | 12.6 MVA on 16/11/2022 at 20:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 73.9 | 73.9 | 73.9 |  | 73.9 |  | 73.9 | 76.6 |  | 76.6 |  | 76.6 | 76.6 | 76.6
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 15.7 | 15.7 | 15.7 |  | 16 |  | 16.4 | 8.8 |  | 8.8 |  | 8.9 | 9 | 9.2
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.996 | 0.996 | 0.996 |  | 0.996 |  | 0.996 | 0.999 |  | 0.999 |  | 0.999 | 0.999 | 0.999
|  |  |  | ECC Rating (MVA) |  | 40.9 | 40.9 | 40.9 |  | 40.9 |  | 40.9 | 42.2 |  | 42.2 |  | 42.2 | 42.2 | 42.2
|  |  |  | 50 PoE Load (MVA) |  | 14.6 | 14.6 | 14.7 |  | 14.9 |  | 15.3 | 8.5 |  | 8.6 |  | 8.7 | 8.8 | 8.9
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.7 | 0.7 | 0.7 |  | 0.7 |  | 0.8 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  |  | Hours PA > 95% Peak Load |  | 25.5 | 25.5 | 25.5 |  | 25.5 |  | 25.5 | 25.5 |  | 25.5 |  | 25.5 | 25.5 | 25.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 38 | 38 | 38 |  | 38 |  | 38 | 38 |  | 38 |  | 38 | 38 | 38
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 19 | 19 | 19 |  | 19 |  | 19 | 19 |  | 19 |  | 19 | 19 | 19
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## BERS
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | BERS - Berserker (66/11kV) | [8 empty] | Supply |  | RMES - Rockhampton Mesh
| Description |  |  |  | Region is Capricornia
Transformer size is 2x66/11kV 19/26/32MVA ONAN/ODAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -4.2% W -2.2%2025 S -2.7% W -1.6%2026 S -2.3% W -1.4%2027 S -1.8% W -1.5
|  |  | Latest Peak Compensated Load | [5 empty] | 21.3 MVA on 13/02/2023 at 16:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 78.5 | 78.5 | 78.5 |  | 78.5 |  | 78.5 | 88 |  | 88 |  | 88 | 88 | 88
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 21.2 | 20.6 | 20.2 |  | 19.8 |  | 19.7 | 12.8 |  | 12.7 |  | 12.5 | 12.4 | 12.2
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 0.979 |  | 0.979 | 0.979 | 0.979
|  |  |  | ECC Rating (MVA) |  | 42.7 | 42.7 | 42.7 |  | 42.7 |  | 42.7 | 46.5 |  | 46.5 |  | 46.5 | 46.5 | 46.5
|  |  |  | 50 PoE Load (MVA) |  | 20.1 | 19.5 | 19.1 |  | 18.7 |  | 18.7 | 12 |  | 11.7 |  | 11.5 | 11.3 | 11.2
|  |  |  | 50 PoE Load > 95% (MVA) |  | 1 | 1 | 1 |  | 0.9 |  | 0.9 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  |  | Hours PA > 95% Peak Load |  | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 | 5 | 5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 38 | 38 | 38 |  | 38 |  | 38 | 38 |  | 38 |  | 38 | 38 | 38
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 19 | 19 | 19 |  | 19 |  | 19 | 19 |  | 19 |  | 19 | 19 | 19
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## BEWE
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | BEWE - Bedford Weir (66/22kV) | [8 empty] | Supply |  | T032 - Blackwater BSP
| Description |  |  |  | Region is Capricornia
Transformer size is 1x66/22kV 10MVA ONAN;1x66/22kV 7.5/10MVA ON/OB
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.0% W -0.6%2025 S -1.0% W -0.5%2026 S -0.5% W -0.2%2027 S 0.2% W -0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 8.1 MVA on 03/01/2023 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 20.9 | 20.9 | 20.9 |  | 20.9 |  | 20.9 | 23.3 |  | 23.3 |  | 23.3 | 23.3 | 23.3
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 8.5 | 8.4 | 8.4 |  | 8.4 |  | 8.5 | 6.9 |  | 6.8 |  | 6.8 | 6.8 | 6.8
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.959 | 0.962 | 0.959 |  | 0.959 |  | 0.959 | 0.966 |  | 0.966 |  | 0.966 | 0.966 | 0.966
|  |  |  | ECC Rating (MVA) |  | 12 | 12 | 12 |  | 12 |  | 12 | 12.9 |  | 12.9 |  | 12.9 | 12.9 | 12.9
|  |  |  | 50 PoE Load (MVA) |  | 8.1 | 8.1 | 8 |  | 8 |  | 8.1 | 6.7 |  | 6.6 |  | 6.6 | 6.6 | 6.6
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.4 | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Hours PA > 95% Peak Load |  | 20 | 20 | 20 |  | 20 |  | 20 | 20 |  | 20 |  | 20 | 20 | 20
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 17.5 | 17.5 | 17.5 |  | 17.5 |  | 17.5 | 17.5 |  | 17.5 |  | 17.5 | 17.5 | 17.5
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 7.5 | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 | 7.5
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## BILO
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | BILO - Biloela (66/11kV) | [8 empty] | Supply |  | T026 - Biloela BSP
| Description |  |  |  | Region is Capricornia
Transformer size is 1x66/11kV 15/20MVA ONAN/ONAF;1x66/11kV 25/32MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.0% W -0.5%2025 S -0.9% W -0.3%2026 S -0.5% W 0.0%,2027 S 0.2% W 0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 15.9 MVA on 13/02/2023 at 16:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 47.3 | 47.3 | 47.3 |  | 47.3 |  | 47.3 | 55 |  | 55 |  | 55 | 55 | 55
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 16.4 | 16.3 | 16.2 |  | 16.2 |  | 16.4 | 11.9 |  | 11.8 |  | 11.8 | 11.8 | 11.8
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.966 | 0.966 | 0.966 |  | 0.966 |  | 0.966 | 0.988 |  | 0.989 |  | 0.989 | 0.989 | 0.989
|  |  |  | ECC Rating (MVA) |  | 27.2 | 27.2 | 27.2 |  | 27.2 |  | 27.2 | 29.9 |  | 29.9 |  | 29.9 | 29.9 | 29.9
|  |  |  | 50 PoE Load (MVA) |  | 15.9 | 15.7 | 15.7 |  | 15.7 |  | 15.9 | 11.6 |  | 11.6 |  | 11.5 | 11.5 | 11.5
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.8 | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  |  | Hours PA > 95% Peak Load |  | 5.5 | 5.5 | 5.5 |  | 5.5 |  | 5.5 | 5.5 |  | 5.5 |  | 5.5 | 5.5 | 5.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 6.1 | 6.1 | 6.1 |  | 6.1 |  | 6.1 | 6.1 |  | 6.1 |  | 6.1 | 6.1 | 6.1
|  |  |  | Mobile Plant Avail (MVA) |  | 3.3 | 3.3 | 3.3 |  | 3.3 |  | 3.3 | 3.3 |  | 3.3 |  | 3.3 | 3.3 | 3.3
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 1.9 | 1.9 | 1.9 |  | 1.9 |  | 1.9 | 1.9 |  | 1.9 |  | 1.9 | 1.9 | 1.9
|  |  |  | Capacity for Embedded Generation (MVA) |  | 40 | 40 | 40 |  | 40 |  | 40 | 40 |  | 40 |  | 40 | 40 | 40
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 15 | 15 | 15 |  | 15 |  | 15 | 15 |  | 15 |  | 15 | 15 | 15
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## BING
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | BING - Bingegang (66/22kV) | [8 empty] | Supply |  | T032 - Blackwater BSP
| Description |  |  |  | Region is Capricornia
Transformer size is 2x66/22kV 5MVA ON
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.1% W -0.7%2025 S -0.8% W -0.3%2026 S -0.4% W -0.1%2027 S 0.4% W 0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 1.4 MVA on 02/03/2023 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 11 | 11 | 11 |  | 11 |  | 11 | 12 |  | 12 |  | 12 | 12 | 12
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 1.5 | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.4 |  | 1.4 |  | 1.4 | 1.4 | 1.4
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.987 | 0.987 | 0.987 |  | 0.987 |  | 0.987 | 0.99 |  | 0.99 |  | 0.99 | 0.99 | 0.99
|  |  |  | ECC Rating (MVA) |  | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6 | 7.1 |  | 7.1 |  | 7.1 | 7.1 | 7.1
|  |  |  | 50 PoE Load (MVA) |  | 1.4 | 1.4 | 1.4 |  | 1.4 |  | 1.4 | 1.3 |  | 1.3 |  | 1.3 | 1.3 | 1.3
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 36.5 | 36.5 | 36.5 |  | 36.5 |  | 36.5 | 36.5 |  | 36.5 |  | 36.5 | 36.5 | 36.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 | 5 | 5
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## BLAC
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | BLAC - Blackwater (66/22kV) | [8 empty] | Supply |  | T032 - Blackwater BSP
| Description |  |  |  | Region is Capricornia
Transformer size is 2x11/22kV 7.5/10MVA ONAN/ONAF;2x132/22kV 160 MVA
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.0% W -0.7%2025 S -0.9% W -0.6%2026 S -0.5% W -0.3%2027 S 0.2% W -0.2%
|  |  | Latest Peak Compensated Load | [5 empty] | 9.8 MVA on 14/02/2023 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 40 | 40 | 40 |  | 40 |  | 40 | 44 |  | 44 |  | 44 | 44 | 44
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 10.4 | 10.3 | 11.2 |  | 11.2 |  | 11.3 | 7.5 |  | 7.5 |  | 8.1 | 8.1 | 8.1
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.981 | 0.981 | 0.981 |  | 0.981 |  | 0.981 | 0.992 |  | 0.992 |  | 0.992 | 0.992 | 0.992
|  |  |  | ECC Rating (MVA) |  | 33 | 33 | 33 |  | 33 |  | 33 | 36 |  | 36 |  | 36 | 36 | 36
|  |  |  | 50 PoE Load (MVA) |  | 9.9 | 9.9 | 10.8 |  | 10.8 |  | 10.9 | 7.1 |  | 7.1 |  | 7.7 | 7.7 | 7.7
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  |  | Hours PA > 95% Peak Load |  | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 | 5 | 5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 15 | 15 | 15 |  | 15 |  | 15 | 15 |  | 15 |  | 15 | 15 | 15
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 7.5 | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 | 7.5
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## BLAK
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | BLAK - Blackall (66/22kV) | [8 empty] | Supply |  | T072 - Barcaldine BSP
| Description |  |  |  | Region is Capricornia
Transformer size is 2x66/22kV 5/6.25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.3% W -0.9%2025 S -1.1% W -0.6%2026 S -0.7% W -0.4%2027 S 0.0% W -0.3%
|  |  | Latest Peak Compensated Load | [5 empty] | 4.5 MVA on 07/12/2022 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 13.9 | 13.9 | 13.9 |  | 13.9 |  | 13.9 | 16.5 |  | 16.5 |  | 16.5 | 16.5 | 16.5
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 4.7 | 4.6 | 4.6 |  | 4.6 |  | 4.6 | 4.1 |  | 4.1 |  | 4 | 4 | 4
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.999 | 0.999 | 0.999 |  | 0.999 |  | 0.999 | 0.981 |  | 0.981 |  | 0.981 | 0.981 | 0.981
|  |  |  | ECC Rating (MVA) |  | 8.1 | 8.1 | 8.1 |  | 8.1 |  | 8.1 | 9.3 |  | 9.3 |  | 9.3 | 9.3 | 9.3
|  |  |  | 50 PoE Load (MVA) |  | 4.4 | 4.4 | 4.4 |  | 4.4 |  | 4.4 | 3.9 |  | 3.9 |  | 3.9 | 3.9 | 3.8
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 4 | 4 | 4 |  | 4 |  | 4 | 4 |  | 4 |  | 4 | 4 | 4
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 | 5 | 5
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## BLRI
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | BLRI - Black River (66/11kV) | [8 empty] | Supply |  | TMES - Townsville Mesh
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/11kV 15/20MVA ONAN/ONAF;1x66/11kV 16/20MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 4.4 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -1.3% W 2.3%,2025 S 0.9% W 2.5%, 2026 S 1.3% W 2.7%, 2027 S 1.9% W 2.5%
|  |  | Latest Peak Compensated Load | [5 empty] | 25.2 MVA on 14/12/2022 at 20:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 56 | 56 | 56 |  | 56 |  | 56 | 59.1 |  | 59.1 |  | 59.1 | 59.1 | 59.1
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 29.2 | 29.5 | 29.9 |  | 30.5 |  | 31.2 | 16.5 |  | 16.9 |  | 17.4 | 17.8 | 18.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.999 | 0.999 | 0.999 |  | 0.999 |  | 0.999 | 0.998 |  | 0.998 |  | 0.998 | 0.998 | 0.998
|  |  |  | ECC Rating (MVA) |  | 29.9 | 29.9 | 29.9 |  | 29.9 |  | 29.9 | 29.9 |  | 29.9 |  | 29.9 | 29.9 | 29.9
|  |  |  | 50 PoE Load (MVA) |  | 27.8 | 28.1 | 28.4 |  | 29 |  | 29.7 | 15.8 |  | 16.2 |  | 16.6 | 17.1 | 17.5
|  |  |  | 50 PoE Load > 95% (MVA) |  | 1.4 | 1.4 | 1.4 |  | 1.5 |  | 1.5 | 0.8 |  | 0.8 |  | 0.8 | 0.9 | 0.9
|  |  |  | Hours PA > 95% Peak Load |  | 6 | 6 | 6 |  | 6 |  | 6 | 6 |  | 6 |  | 6 | 6 | 6
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 4 | 4 | 4 |  | 4 |  | 4 | 4 |  | 4 |  | 4 | 4 | 4
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 31 | 31 | 31 |  | 31 |  | 31 | 31 |  | 31 |  | 31 | 31 | 31
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 15 | 15 | 15 |  | 15 |  | 15 | 15 |  | 15 |  | 15 | 15 | 15
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## BLUE
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | BLUE - Bluewater (66/11kV) | [8 empty] | Supply |  | TMES - Townsville Mesh
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/11kV 5MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.8% W -0.2%2025 S -0.5% W 0.1%,2026 S -0.1% W 0.4%,2027 S 0.6% W 0.5%
|  |  | Latest Peak Compensated Load | [5 empty] | 4.2 MVA on 14/12/2022 at 19:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 5.3 | 5.3 | 5.3 |  | 5.3 |  | 5.3 | 5.5 |  | 5.5 |  | 5.5 | 5.5 | 5.5
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 4.7 | 4.7 | 4.6 |  | 4.7 |  | 4.7 | 2.9 |  | 2.9 |  | 2.9 | 2.9 | 3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.997 | 0.997 | 0.997 |  | 0.997 |  | 0.997 | 0.999 |  | 0.999 |  | 0.999 | 0.999 | 0.999
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 4.5 | 4.5 | 4.5 |  | 4.5 |  | 4.5 | 2.8 |  | 2.7 |  | 2.8 | 2.8 | 2.8
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 5.5 | 5.5 | 5.5 |  | 5.5 |  | 5.5 | 5.5 |  | 5.5 |  | 5.5 | 5.5 | 5.5
|  |  |  | Raw LAR (MVA) |  | 4.5 | 4.5 | 4.5 |  | 4.5 |  | 4.5 | 2.8 |  | 2.7 |  | 2.8 | 2.8 | 2.8
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 3.5 | 3.5 | 3.5 |  | 3.5 |  | 3.5 | 3.5 |  | 3.5 |  | 3.5 | 3.5 | 3.5
|  |  |  | Mobile Plant Avail (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 | 2 | 2
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 | 5 | 5
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## BODA
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | BODA - Boondooma Dam (66/11kV) | [8 empty] | Supply |  | H018 - Tarong BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 1x66/11kV 4.1MVA ONAN;1x66/11kV 1MVA ONAN(Standby)
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.0% W -0.6%2025 S -0.7% W -0.2%2026 S -0.3% W 0.0%,2027 S 0.3% W 0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 2.1 MVA on 09/06/2022 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 5.2 | 5.2 | 5.2 |  | 5.2 |  | 5.2 | 5.5 |  | 5.5 |  | 5.5 | 5.5 | 5.5
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2.1 |  | 2.1 |  | 2.1 | 2.1 | 2.1
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.972 | 0.974 | 0.974 |  | 0.974 |  | 0.972 | 0.956 |  | 0.956 |  | 0.956 | 0.956 | 0.956
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2.1 |  | 2.1 |  | 2.1 | 2.1 | 2.1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 1347 | 1347 | 1347 |  | 1347 |  | 1347 | 1347 |  | 1347 |  | 1347 | 1347 | 1347
|  |  |  | Raw LAR (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2.1 |  | 2.1 |  | 2.1 | 2.1 | 2.1
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 1.1 | 1.1 | 1.1 |  | 1.1 |  | 1.1 | 1.1 |  | 1.1 |  | 1.1 | 1.1 | 1.1
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 2.1 | 2.1 | 2.1 |  | 2.1 |  | 2.1 | 2.1 |  | 2.1 |  | 2.1 | 2.1 | 2.1
|  |  |  | Capacity for Embedded Generation (MVA) |  | 4.1 | 4.1 | 4.1 |  | 4.1 |  | 4.1 | 4.1 |  | 4.1 |  | 4.1 | 4.1 | 4.1
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## BOHL
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | BOHL - Bohle (66/11kV) | [8 empty] | Supply |  | TMES - Townsville Mesh
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/11kV 15/20/25MVA ODAN/ONAF/ODAF;1x66/11kV 15/20/25MVA ONAN/ONAF/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 4.7 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.3% W 0.2%,2025 S -0.3% W 0.2%,2026 S 0.2% W 0.6%, 2027 S 1.0% W 0.8%
|  |  | Latest Peak Compensated Load | [5 empty] | 19.5 MVA on 16/03/2023 at 13:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 52.7 | 52.7 | 52.7 |  | 52.7 |  | 52.7 | 55.3 |  | 55.3 |  | 55.3 | 55.3 | 55.3
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 23.8 | 23.8 | 23.8 |  | 24.1 |  | 24.5 | 17.2 |  | 17.3 |  | 17.3 | 17.4 | 17.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.99 | 0.99 | 0.99 |  | 0.99 |  | 0.99 | 0.997 |  | 0.997 |  | 0.997 | 0.997 | 0.997
|  |  |  | ECC Rating (MVA) |  | 26.4 | 26.4 | 26.4 |  | 26.4 |  | 26.4 | 27.8 |  | 27.8 |  | 27.8 | 27.8 | 27.8
|  |  |  | 50 PoE Load (MVA) |  | 22.7 | 22.7 | 22.7 |  | 22.9 |  | 23.4 | 16.4 |  | 16.4 |  | 16.5 | 16.6 | 16.7
|  |  |  | 50 PoE Load > 95% (MVA) |  | 1.1 | 1.1 | 1.1 |  | 1.1 |  | 1.2 | 0.8 |  | 0.8 |  | 0.8 | 0.8 | 0.8
|  |  |  | Hours PA > 95% Peak Load |  | 23.5 | 23.5 | 23.5 |  | 23.5 |  | 23.5 | 23.5 |  | 23.5 |  | 23.5 | 23.5 | 23.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 4.5 | 4.5 | 4.5 |  | 4.5 |  | 4.5 | 4.5 |  | 4.5 |  | 4.5 | 4.5 | 4.5
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 18.4 | 18.4 | 18.4 |  | 18.4 |  | 18.4 | 18.4 |  | 18.4 |  | 18.4 | 18.4 | 18.4
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 9.2 | 9.2 | 9.2 |  | 9.2 |  | 9.2 | 9.2 |  | 9.2 |  | 9.2 | 9.2 | 9.2
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## BORE
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | BORE - Boyne Residential (66/11kV) | [8 empty] | Supply |  | T019 - Gladstone South BSP
| Description |  |  |  | Region is Capricornia
Transformer size is 2x66/11kV 7.5/10MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.6% W -0.3%2025 S -0.4% W -0.1%2026 S 0.0% W 0.2%, 2027 S 0.8% W 0.4%
|  |  | Latest Peak Compensated Load | [5 empty] | 11.1 MVA on 13/02/2023 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 26 | 26 | 26 |  | 26 |  | 26 | 29.9 |  | 29.9 |  | 29.9 | 29.9 | 29.9
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 11.4 | 11.3 | 11.4 |  | 11.4 |  | 11.6 | 10.7 |  | 10.7 |  | 10.7 | 10.7 | 10.7
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.996 | 0.996 | 0.996 |  | 0.996 |  | 0.996 | 0.998 |  | 0.998 |  | 0.998 | 0.998 | 0.998
|  |  |  | ECC Rating (MVA) |  | 14.3 | 14.3 | 14.3 |  | 14.3 |  | 14.3 | 15 |  | 15 |  | 15 | 15 | 15
|  |  |  | 50 PoE Load (MVA) |  | 11.1 | 11 | 11 |  | 11.1 |  | 11.3 | 9.6 |  | 9.5 |  | 9.5 | 9.5 | 9.6
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | Hours PA > 95% Peak Load |  | 5.5 | 5.5 | 5.5 |  | 5.5 |  | 5.5 | 5.5 |  | 5.5 |  | 5.5 | 5.5 | 5.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 | 5 | 5
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## BOWE
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | BOWE - Bowen (66/11kV) | [8 empty] | Supply |  | T181 - Bowen North BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 2x66/11kV 15/16MVA ONAN/OFDAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.6% W -0.1%2025 S -0.5% W 0.1%,2026 S 0.0% W 0.4%, 2027 S 0.8% W 0.6%
|  |  | Latest Peak Compensated Load | [5 empty] | 13.1 MVA on 02/02/2023 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 39.8 | 39.8 | 39.8 |  | 39.8 |  | 39.8 | 44.4 |  | 44.4 |  | 44.4 | 44.4 | 44.4
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 13.6 | 13.6 | 13.6 |  | 13.7 |  | 13.9 | 10.3 |  | 10.3 |  | 10.3 | 10.3 | 10.4
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.998 | 0.998 | 0.998 |  | 0.998 |  | 0.998 | 0.994 |  | 0.994 |  | 0.994 | 0.994 | 0.994
|  |  |  | ECC Rating (MVA) |  | 22.4 | 22.4 | 22.4 |  | 22.4 |  | 22.4 | 23.9 |  | 23.9 |  | 23.9 | 23.9 | 23.9
|  |  |  | 50 PoE Load (MVA) |  | 13.1 | 13.1 | 13.1 |  | 13.2 |  | 13.4 | 9.7 |  | 9.7 |  | 9.7 | 9.7 | 9.8
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.7 | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | Hours PA > 95% Peak Load |  | 20.5 | 20.5 | 20.5 |  | 20.5 |  | 20.5 | 20.5 |  | 20.5 |  | 20.5 | 20.5 | 20.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 15.4 | 15.4 | 15.4 |  | 15.4 |  | 15.4 | 15.4 |  | 15.4 |  | 15.4 | 15.4 | 15.4
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 7.7 | 7.7 | 7.7 |  | 7.7 |  | 7.7 | 7.7 |  | 7.7 |  | 7.7 | 7.7 | 7.7
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## BROX
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | BROX - Broxburn (33/11kV) | [8 empty] | Supply |  | YARA - Yarranlea BSP
| Description |  |  |  | Region is South West
Transformer size is 1x33/11kV 10MVA SKID;2x33/11kV 5MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.9% W -0.4%2025 S -0.9% W -0.4%2026 S -0.4% W -0.0%2027 S 0.3% W 0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 8.4 MVA on 13/02/2023 at 17:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 16.5 | 16.5 | 16.5 |  | 16.5 |  | 16.5 | 16.5 |  | 16.5 |  | 16.5 | 16.5 | 16.5
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 9.6 | 10.1 | 10.1 |  | 10.1 |  | 10.2 | 8.8 |  | 9.3 |  | 9.3 | 9.3 | 9.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.956 | 0.956 | 0.956 |  | 0.956 |  | 0.956 | 0.98 |  | 0.98 |  | 0.98 | 0.98 | 0.98
|  |  |  | ECC Rating (MVA) |  | 11.5 | 11.5 | 11.5 |  | 11.5 |  | 11.5 | 12 |  | 12 |  | 12 | 12 | 12
|  |  |  | 50 PoE Load (MVA) |  | 8.8 | 9.3 | 9.3 |  | 9.3 |  | 9.4 | 8.4 |  | 8.9 |  | 8.8 | 8.8 | 8.8
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.4 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  |  | Hours PA > 95% Peak Load |  | 5.5 | 5.5 | 5.5 |  | 5.5 |  | 5.5 | 5.5 |  | 5.5 |  | 5.5 | 5.5 | 5.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | Mobile Plant Avail (MVA) |  | 12.5 | 12.5 | 12.5 |  | 12.5 |  | 12.5 | 12.5 |  | 12.5 |  | 12.5 | 12.5 | 12.5
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 | 5 | 5
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## BUCE
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | BUCE - Bundaberg Central (66/11kV) | [8 empty] | Supply |  | BUND - Bundaberg BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 2x66/11kV 19/26/32MVA ONAN/ODAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.4% W -1.0%2025 S -1.6% W -1.1%2026 S -1.0% W -0.6%2027 S -0.1% W -0.4
|  |  | Latest Peak Compensated Load | [5 empty] | 15.6 MVA on 09/03/2023 at 13:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 80.3 | 80.3 | 80.3 |  | 80.3 |  | 80.3 | 87.4 |  | 87.4 |  | 87.4 | 87.4 | 87.4
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 16.8 | 16.5 | 16.4 |  | 16.3 |  | 16.5 | 12.4 |  | 12.3 |  | 12.1 | 12.1 | 12
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.957 | 0.957 | 0.957 |  | 0.957 |  | 0.957 | 0.97 |  | 0.97 |  | 0.97 | 0.97 | 0.97
|  |  |  | ECC Rating (MVA) |  | 43.1 | 43.1 | 43.1 |  | 43.1 |  | 43.1 | 45.8 |  | 45.8 |  | 45.8 | 45.8 | 45.8
|  |  |  | 50 PoE Load (MVA) |  | 15.8 | 15.5 | 15.4 |  | 15.4 |  | 15.6 | 11.5 |  | 11.4 |  | 11.3 | 11.2 | 11.2
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.8 | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  |  | Hours PA > 95% Peak Load |  | 3 | 3 | 3 |  | 3 |  | 3 | 3 |  | 3 |  | 3 | 3 | 3
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 38 | 38 | 38 |  | 38 |  | 38 | 38 |  | 38 |  | 38 | 38 | 38
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 19 | 19 | 19 |  | 19 |  | 19 | 19 |  | 19 |  | 19 | 19 | 19
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## BULL
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | BULL - Bullyard (66/11kV) | [8 empty] | Supply |  | BUND - Bundaberg BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 2x66/11kV 5MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.7% W -0.2%2025 S -0.5% W 0.1%,2026 S -0.1% W 0.3%,2027 S 0.5% W 0.3%
|  |  | Latest Peak Compensated Load | [5 empty] | 2.1 MVA on 03/01/2023 at 20:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 14.2 | 14.2 | 14.2 |  | 14.2 |  | 14.2 | 15 |  | 15 |  | 15 | 15 | 15
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 2.5 | 2.5 | 2.5 |  | 2.5 |  | 2.6 | 1.7 |  | 1.7 |  | 1.7 | 1.7 | 1.7
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.937 | 0.937 | 0.937 |  | 0.937 |  | 0.937 | 0.948 |  | 0.948 |  | 0.948 | 0.948 | 0.948
|  |  |  | ECC Rating (MVA) |  | 7.5 | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 | 7.5
|  |  |  | 50 PoE Load (MVA) |  | 2.3 | 2.3 | 2.3 |  | 2.3 |  | 2.3 | 1.6 |  | 1.6 |  | 1.6 | 1.6 | 1.6
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 3.5 | 3.5 | 3.5 |  | 3.5 |  | 3.5 | 3.5 |  | 3.5 |  | 3.5 | 3.5 | 3.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 | 5 | 5
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## BUND
Bulk Summary Information and Peak Load Forecast
Substation |  |  |  | BUND - Bundaberg BSP (132/66kV) | [8 empty] | Supply |  | QGNG - Gin Gin TCP
Description |  |  |  | Region is Wide Bay
Transformer size is 1x132/66kV 36/70MVA ONAN/ONAF;2x132/66kV 40/50/60MVA ON/OFN/OFB
Capacity of commissioned Embedded Generation (with Connection Agreements) is 7.2 MVA
|  | Latest Peak Compensated Load | [5 empty] | 118.5 MVA on 13/02/2023 at 17:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[5 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  | NCC Rating (MVA) |  | 226.4 | 226.4 | 226.4 |  | 226.4 |  | 226.4 | 250.8 |  | 250.8 |  | 250.8 | 250.8 | 250.8
|  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  | 10 PoE Load (MVA) |  | 125 | 123.9 | 123.3 |  | 123.5 |  | 127.8 | 115 |  | 114.3 |  | 113.7 | 113.7 | 116.5
LARn (MVA)
LARn (MW)
|  |  | Power Factor at Peak Load |  | 0.992 | 0.992 | 0.992 |  | 0.992 |  | 0.992 | 0.994 |  | 0.994 |  | 0.994 | 0.994 | 0.994
|  |  | ECC Rating (MVA) |  | 170.2 | 170.2 | 170.2 |  | 170.2 |  | 170.2 | 179.4 |  | 179.4 |  | 179.4 | 179.4 | 179.4
|  |  | 50 PoE Load (MVA) |  | 118.4 | 117.3 | 116.8 |  | 117 |  | 121.2 | 107.3 |  | 106.6 |  | 106.1 | 106.1 | 108.9
|  |  | 50 PoE Load > 95% (MVA) |  | 5.9 | 5.9 | 5.8 |  | 5.9 |  | 6.1 | 5.4 |  | 5.3 |  | 5.3 | 5.3 | 5.4
|  |  | Hours PA > 95% Peak Load |  | 12.5 | 12.5 | 12.5 |  | 12.5 |  | 12.5 | 12.5 |  | 12.5 |  | 12.5 | 12.5 | 12.5
Raw LAR (MVA)
|  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Capacity for Embedded Generation (MVA) |  | 116 | 116 | 116 |  | 116 |  | 116 | 116 |  | 116 |  | 116 | 116 | 116 | -50MVA by 2030
|  |  | Firm Capacity for Embedded Generation (MVA) |  | 76 | 76 | 76 |  | 76 |  | 76 | 76 |  | 76 |  | 76 | 76 | 76
LARc (MVA)
LARc (MW)
|  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## CACI
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | CACI - Cairns City (132/22kV) | [8 empty] | Supply |  | QCNS - Cairns City 132kV TCP
| Description |  |  |  | Region is Far North
Transformer size is 1x132/22kV 55/80MVA ONAN/ODAN;1x132/22kV 64/80MVA ONAN/ODAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.0% W -0.6%2025 S -1.1% W -0.7%2026 S -0.6% W -0.4%2027 S 0.0% W -0.4%
|  |  | Latest Peak Compensated Load | [5 empty] | 49.9 MVA on 24/11/2022 at 12:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 182.3 | 182.3 | 182.3 |  | 182.3 |  | 182.3 | 187.9 |  | 187.9 |  | 187.9 | 187.9 | 187.9
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 53.2 | 52.6 | 52.3 |  | 52.3 |  | 52.8 | 34.8 |  | 34.6 |  | 34.4 | 34.3 | 34.1
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.999 | 0.999 | 0.999 |  | 0.999 |  | 0.999 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | ECC Rating (MVA) |  | 101.6 | 101.6 | 101.6 |  | 101.6 |  | 101.6 | 103.8 |  | 103.8 |  | 103.8 | 103.8 | 103.8
|  |  |  | 50 PoE Load (MVA) |  | 50.5 | 49.9 | 49.6 |  | 49.7 |  | 50.1 | 34 |  | 33.8 |  | 33.6 | 33.4 | 33.3
|  |  |  | 50 PoE Load > 95% (MVA) |  | 2.5 | 2.5 | 2.5 |  | 2.5 |  | 2.5 | 1.7 |  | 1.7 |  | 1.7 | 1.7 | 1.7
|  |  |  | Hours PA > 95% Peak Load |  | 419 | 419 | 419 |  | 419 |  | 419 | 419 |  | 419 |  | 419 | 419 | 419
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 119 | 119 | 119 |  | 119 |  | 119 | 119 |  | 119 |  | 119 | 119 | 119
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 55 | 55 | 55 |  | 55 |  | 55 | 55 |  | 55 |  | 55 | 55 | 55
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## CAFE
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | CAFE - Cape Ferguson (66/11kV) | [8 empty] | Supply |  | TMES - Townsville Mesh
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/11kV 2.3MVA ONAN;1x66/11kV 2MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.7% W -0.1%2025 S -0.4% W 0.3%,2026 S 0.1% W 0.5%, 2027 S 0.8% W 0.6%
|  |  | Latest Peak Compensated Load | [5 empty] | 1.8 MVA on 02/02/2023 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 4.4 | 4.4 | 4.4 |  | 4.4 |  | 4.4 | 4.7 |  | 4.7 |  | 4.7 | 4.7 | 4.7
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 1.8 | 1.8 | 1.8 |  | 1.8 |  | 1.8 | 1.5 |  | 1.5 |  | 1.5 | 1.5 | 1.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.997 | 0.997 | 0.997 |  | 0.997 |  | 0.997 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | ECC Rating (MVA) |  | 2.6 | 2.6 | 2.6 |  | 2.6 |  | 2.6 | 2.7 |  | 2.7 |  | 2.7 | 2.7 | 2.7
|  |  |  | 50 PoE Load (MVA) |  | 1.7 | 1.7 | 1.7 |  | 1.7 |  | 1.7 | 1.4 |  | 1.4 |  | 1.4 | 1.4 | 1.4
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 21.5 | 21.5 | 21.5 |  | 21.5 |  | 21.5 | 21.5 |  | 21.5 |  | 21.5 | 21.5 | 21.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 | 2 | 2
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## CALE
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | CALE - Calen (66/11kV) | [8 empty] | Supply |  | PROS - Proserpine BSP
| Description |  |  |  | Region is Mackay
Transformer size is 2x66/11kV 5MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.7% W -0.7%2025 S -0.4% W -0.5%2026 S 0.0% W -0.2%,2027 S 0.6% W -0.2%
|  |  | Latest Peak Compensated Load | [5 empty] | 2.5 MVA on 16/11/2022 at 19:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 11 | 11 | 11 |  | 11 |  | 11 | 12 |  | 12 |  | 12 | 12 | 12
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 3 | 2.9 | 2.9 |  | 3 |  | 3 | 2.6 |  | 2.6 |  | 2.6 | 2.6 | 2.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.971 | 0.971 | 0.971 |  | 0.971 |  | 0.971 | 0.988 |  | 0.988 |  | 0.988 | 0.988 | 0.988
|  |  |  | ECC Rating (MVA) |  | 6.3 | 6.3 | 6.3 |  | 6.3 |  | 6.3 | 6.5 |  | 6.5 |  | 6.5 | 6.5 | 6.5
|  |  |  | 50 PoE Load (MVA) |  | 2.8 | 2.8 | 2.8 |  | 2.8 |  | 2.8 | 2.4 |  | 2.4 |  | 2.3 | 2.3 | 2.3
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 26 | 26 | 26 |  | 26 |  | 26 | 26 |  | 26 |  | 26 | 26 | 26
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 | 5 | 5
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## CALL
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | CALL - Calliope (66/11kV) | [8 empty] | Supply |  | T019 - Gladstone South BSP
| Description |  |  |  | Region is Capricornia
Transformer size is 1x66/11kV 7.5/10MVA ON/OB;1x66/11kV 7.5/10MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.6% W -0.3%2025 S -0.4% W -0.2%2026 S 0.1% W 0.2%, 2027 S 0.9% W 0.4%
|  |  | Latest Peak Compensated Load | [5 empty] | 9.7 MVA on 13/02/2023 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 26.7 | 26.7 | 26.7 |  | 26.7 |  | 26.7 | 29.9 |  | 29.9 |  | 29.9 | 29.9 | 29.9
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 10.7 | 10.6 | 10.6 |  | 10.7 |  | 10.9 | 8.2 |  | 8.6 |  | 8.6 | 8.6 | 8.6
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.985 | 0.985 | 0.985 |  | 0.985 |  | 0.985 | 0.992 |  | 0.992 |  | 0.992 | 0.992 | 0.992
|  |  |  | ECC Rating (MVA) |  | 14.7 | 14.7 | 14.7 |  | 14.7 |  | 14.7 | 15 |  | 15 |  | 15 | 15 | 15
|  |  |  | 50 PoE Load (MVA) |  | 9.9 | 9.8 | 9.8 |  | 9.9 |  | 10.1 | 7 |  | 7.4 |  | 7.4 | 7.4 | 7.4
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  |  | Hours PA > 95% Peak Load |  | 6 | 6 | 6 |  | 6 |  | 6 | 6 |  | 6 |  | 6 | 6 | 6
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 12.6 | 12.6 | 12.6 |  | 12.6 |  | 12.6 | 12.6 |  | 12.6 |  | 12.6 | 12.6 | 12.6
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 5.1 | 5.1 | 5.1 |  | 5.1 |  | 5.1 | 5.1 |  | 5.1 |  | 5.1 | 5.1 | 5.1
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## CANN
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | CANN - Cannonvale (66/11kV) | [8 empty] | Supply |  | PROS - Proserpine BSP
| Description |  |  |  | Region is Mackay
Transformer size is 2x66/11kV 15MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.4% W -0.3%2025 S -0.5% W -0.6%2026 S -0.0% W -0.2%2027 S 0.8% W 0.6%
|  |  | Latest Peak Compensated Load | [5 empty] | 17.7 MVA on 02/02/2023 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 34.9 | 34.9 | 34.9 |  | 34.9 |  | 34.9 | 37.8 |  | 37.8 |  | 37.8 | 37.8 | 37.8
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 18.1 | 18 | 18 |  | 18.1 |  | 18.5 | 12.5 |  | 12.5 |  | 12.4 | 12.4 | 12.4
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.994 | 0.994 | 0.994 |  | 0.994 |  | 0.994 | 0.999 |  | 0.999 |  | 0.999 | 0.999 | 0.999
|  |  |  | ECC Rating (MVA) |  | 20 | 20 | 20 |  | 20 |  | 20 | 21.9 |  | 21.9 |  | 21.9 | 21.9 | 21.9
|  |  |  | 50 PoE Load (MVA) |  | 17.5 | 17.4 | 17.4 |  | 17.5 |  | 17.9 | 11.7 |  | 11.6 |  | 11.6 | 11.6 | 11.6
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.9 | 0.9 | 0.9 |  | 0.9 |  | 0.9 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  |  | Hours PA > 95% Peak Load |  | 14.5 | 14.5 | 14.5 |  | 14.5 |  | 14.5 | 14.5 |  | 14.5 |  | 14.5 | 14.5 | 14.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 12.6 | 13.6 | 13.6 |  | 13.6 |  | 13.6 | 13.6 |  | 13.6 |  | 13.6 | 13.6 | 13.6
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 6.3 | 6.3 | 6.3 |  | 6.3 |  | 6.3 | 6.3 |  | 6.3 |  | 6.3 | 6.3 | 6.3
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## CANO
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | CANO - Cairns North (132/22kV) | [8 empty] | Supply |  | QWRE - Woree TCP
| Description |  |  |  | Region is Far North
Transformer size is 2x132/22kV 50/63MVA ONAN/ODAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.8% W -0.2%2025 S -1.9% W -0.2%2026 S -0.6% W 0.1%,2027 S 0.1% W 0.4%
|  |  | Latest Peak Compensated Load | [5 empty] | 52.2 MVA on 15/12/2022 at 16:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 142.8 | 142.8 | 142.8 |  | 142.8 |  | 142.8 | 147.1 |  | 147.1 |  | 147.1 | 147.1 | 147.1
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 52.7 | 51.7 | 51.4 |  | 51.5 |  | 51.9 | 35.6 |  | 35.5 |  | 35.5 | 35.5 | 35.6
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 1 | 1 | 1 |  | 1 |  | 1 | 0.999 |  | 0.999 |  | 0.999 | 0.999 | 0.999
|  |  |  | ECC Rating (MVA) |  | 79.4 | 79.4 | 79.4 |  | 79.4 |  | 79.4 | 81.1 |  | 81.1 |  | 81.1 | 81.1 | 81.1
|  |  |  | 50 PoE Load (MVA) |  | 50.6 | 49.6 | 49.3 |  | 49.4 |  | 49.8 | 34.6 |  | 34.5 |  | 34.5 | 34.5 | 34.6
|  |  |  | 50 PoE Load > 95% (MVA) |  | 2.5 | 2.5 | 2.5 |  | 2.5 |  | 2.5 | 1.7 |  | 1.7 |  | 1.7 | 1.7 | 1.7
|  |  |  | Hours PA > 95% Peak Load |  | 6.5 | 6.5 | 6.5 |  | 6.5 |  | 6.5 | 6.5 |  | 6.5 |  | 6.5 | 6.5 | 6.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 100 | 100 | 100 |  | 100 |  | 100 | 100 |  | 100 |  | 100 | 100 | 100
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 50 | 50 | 50 |  | 50 |  | 50 | 50 |  | 50 |  | 50 | 50 | 50
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## CARI
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | CARI - Cape River (66/11kV) | [8 empty] | Supply |  | T095 - Millchester BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/11kV 1MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.0% W -0.5%2025 S -0.8% W -0.2%2026 S -0.4% W 0.0%,2027 S 0.3% W 0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 0.7 MVA on 15/07/2022 at 20:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1.1 |  | 1.1 |  | 1.1 | 1.1 | 1.1
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 0.7 | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.7 | 0.7
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.97 | 0.97 | 0.97 |  | 0.97 |  | 0.97 | 0.966 |  | 0.966 |  | 0.966 | 0.966 | 0.966
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 0.7 | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.7 | 0.7
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 12 | 12 | 12 |  | 12 |  | 12 | 12 |  | 12 |  | 12 | 12 | 12
|  |  |  | Raw LAR (MVA) |  | 0.7 | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.7 | 0.7
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## CARM
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | CARM - Carmila (33/11kV) | [8 empty] | Supply |  | T065 - Alligator Creek BSP
| Description |  |  |  | Region is Mackay
Transformer size is 1x33/11kV 1MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.2% W -1.0%2025 S -1.1% W -0.8%2026 S -0.6% W -0.5%2027 S 0.4% W 0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 0.5 MVA on 04/01/2023 at 19:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 1.3 | 1.3 | 1.3 |  | 1.3 |  | 1.3 | 1.4 |  | 1.4 |  | 1.4 | 1.4 | 1.4
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 0.4 |  | 0.8 |  | 0.8 | 0.8 | 0.8
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.955 | 0.955 | 0.955 |  | 0.955 |  | 0.955 | 0.995 |  | 0.995 |  | 0.995 | 0.995 | 0.995
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 0.9 | 0.9 | 0.9 |  | 0.9 |  | 0.9 | 0.4 |  | 0.8 |  | 0.8 | 0.8 | 0.8
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 11.5 | 11.5 | 11.5 |  | 11.5 |  | 11.5 | 11.5 |  | 11.5 |  | 11.5 | 11.5 | 11.5
|  |  |  | Raw LAR (MVA) |  | 0.9 | 0.9 | 0.9 |  | 0.9 |  | 0.9 | 0.4 |  | 0.8 |  | 0.8 | 0.8 | 0.8
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Mobile Plant Avail (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## CAST
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | CAST - Canning Street (66/11kV) | [8 empty] | Supply |  | RMES - Rockhampton Mesh
| Description |  |  |  | Region is Capricornia
Transformer size is 2x16/20 MVA 66/11 ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.5% W -1.1%2025 S -1.2% W -1.0%2026 S -0.6% W -0.7%2027 S 0.1% W -0.6%
|  |  | Latest Peak Compensated Load | [5 empty] | 22.8 MVA on 13/02/2023 at 17:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 46.3 | 46.3 | 46.3 |  | 46.3 |  | 46.3 | 54.2 |  | 54.2 |  | 54.2 | 54.2 | 54.2
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 22.6 | 22.3 | 22.2 |  | 22.2 |  | 22.4 | 14.8 |  | 14.6 |  | 14.4 | 14.3 | 14.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.985 | 0.985 | 0.985 |  | 0.985 |  | 0.985 | 0.994 |  | 0.994 |  | 0.994 | 0.994 | 0.994
|  |  |  | ECC Rating (MVA) |  | 26.9 | 26.9 | 26.9 |  | 26.9 |  | 26.9 | 29.9 |  | 29.9 |  | 29.9 | 29.9 | 29.9
|  |  |  | 50 PoE Load (MVA) |  | 21.9 | 21.7 | 21.5 |  | 21.6 |  | 21.7 | 13.8 |  | 13.7 |  | 13.5 | 13.4 | 13.4
|  |  |  | 50 PoE Load > 95% (MVA) |  | 1.1 | 1.1 | 1.1 |  | 1.1 |  | 1.1 | 0.7 |  | 0.7 |  | 0.7 | 0.7 | 0.7
|  |  |  | Hours PA > 95% Peak Load |  | 6.5 | 6.5 | 6.5 |  | 6.5 |  | 6.5 | 6.5 |  | 6.5 |  | 6.5 | 6.5 | 6.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 32 | 32 | 32 |  | 32 |  | 32 | 32 |  | 32 |  | 32 | 32 | 32
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 16 | 16 | 16 |  | 16 |  | 16 | 16 |  | 16 |  | 16 | 16 | 16
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## CAWD
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | CAWD - Skid B (Cawdor) (33/11kV) | [8 empty] | Supply |  | T116 - Torrington BSP
| Description |  |  |  | Region is South West
Transformer size is 1x33/11kV 10MVA Skid transformer
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.9% W -0.5%2025 S -0.8% W -0.2%2026 S -0.3% W 0.0%,2027 S 0.5% W 0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 8.1 MVA on 04/07/2022 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 11 | 11 | 11 |  | 11 |  | 11 | 11 |  | 11 |  | 11 | 11 | 11
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 8 | 8 | 7.9 |  | 8 |  | 8.1 | 9.1 |  | 9.1 |  | 9.1 | 9.1 | 9.1
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.926 | 0.926 | 0.926 |  | 0.926 |  | 0.926 | 0.882 |  | 0.882 |  | 0.882 | 0.882 | 0.882
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 7 | 7 | 7 |  | 7 |  | 7.1 | 8.5 |  | 8.5 |  | 8.5 | 8.5 | 8.5
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.4 | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  |  | Hours PA > 95% Peak Load |  | 3.5 | 3.5 | 3.5 |  | 3.5 |  | 3.5 | 3.5 |  | 3.5 |  | 3.5 | 3.5 | 3.5
|  |  |  | Raw LAR (MVA) |  | 7 | 7 | 7 |  | 7 |  | 7.1 | 8.5 |  | 8.5 |  | 8.5 | 8.5 | 8.5
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 3.6 | 3.6 | 3.6 |  | 3.6 |  | 3.6 | 3.6 |  | 3.6 |  | 3.6 | 3.6 | 3.6
|  |  |  | Mobile Plant Avail (MVA) |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## CEPL
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | CEPL - Cecil Plains (33/11kV) | [8 empty] | Supply |  | YARA - Yarranlea BSP
| Description |  |  |  | Region is South West
Transformer size is 2x33/11kV 5MVA ON
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.9% W -0.7%2025 S -0.8% W -0.3%2026 S -0.3% W -0.1%2027 S 0.3% W -0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 4 MVA on 12/07/2022 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 1.6 | 1.6 | 1.6 |  | 1.6 |  | 1.6 | 3.9 |  | 3.9 |  | 3.9 | 3.9 | 3.9
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.998 | 0.998 | 0.998 |  | 0.998 |  | 0.998 | 0.988 |  | 0.988 |  | 0.988 | 0.988 | 0.988
|  |  |  | ECC Rating (MVA) |  | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 | 5 | 5
|  |  |  | 50 PoE Load (MVA) |  | 1.6 | 1.5 | 1.5 |  | 1.5 |  | 1.6 | 3.8 |  | 3.8 |  | 3.8 | 3.8 | 3.8
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 15 | 15 | 15 |  | 15 |  | 15 | 15 |  | 15 |  | 15 | 15 | 15
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 | 5 | 5
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## CHAL
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | CHAL - Skid K (Charlton) (33/11kV) | [8 empty] | Supply |  | T116 - Torrington BSP
| Description |  |  |  | Region is South West
Transformer size is 1x33/11kV 10MVA Skid ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.6% W -0.1%2025 S -0.7% W 0.0%,2026 S -0.2% W 0.3%,2027 S 0.6% W 0.4%
|  |  | Latest Peak Compensated Load | [5 empty] | 4.2 MVA on 21/07/2022 at 08:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 11 | 11 | 11 |  | 11 |  | 11 | 11 |  | 11 |  | 11 | 11 | 11
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 4 | 4 | 4 |  | 4 |  | 4.1 | 4.6 |  | 4.6 |  | 4.6 | 4.6 | 4.6
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.907 | 0.907 | 0.907 |  | 0.907 |  | 0.907 | 0.902 |  | 0.902 |  | 0.902 | 0.902 | 0.902
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 3.8 | 3.8 | 3.8 |  | 3.8 |  | 3.9 | 4.5 |  | 4.4 |  | 4.4 | 4.5 | 4.5
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 | 5 | 5
|  |  |  | Raw LAR (MVA) |  | 3.8 | 3.8 | 3.8 |  | 3.8 |  | 3.9 | 4.5 |  | 4.4 |  | 4.4 | 4.5 | 4.5
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 4.8 | 4.8 | 4.8 |  | 4.8 |  | 4.8 | 4.8 |  | 4.8 |  | 4.8 | 4.8 | 4.8
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | No | No | No |  | No |  | No | No |  | No |  | No | No | No
Return to Index

## CHAR
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | CHAR - Charleville (66/2211kV) | [8 empty] | Supply |  | ROMA - Roma 66kV BSP
| Description |  |  |  | Region is South West
Transformer size is 1x66/11kV 7.5/8.5MVA ONAF;1x66/22kV 7.5/8.5MVA ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.1% W -0.7%2025 S -1.0% W -0.5%2026 S -0.5% W -0.2%2027 S 0.1% W -0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 11.8 MVA on 11/07/2022 at 07:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 18.6 | 18.6 | 18.6 |  | 18.6 |  | 18.6 | 18.6 |  | 18.6 |  | 18.6 | 18.6 | 18.6
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 12.4 | 12.3 | 12.2 |  | 12.2 |  | 12.3 | 10.4 |  | 10.3 |  | 10.3 | 10.3 | 10.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.917 | 0.917 | 0.918 |  | 0.917 |  | 0.917 | 0.968 |  | 0.968 |  | 0.968 | 0.968 | 0.968
|  |  |  | ECC Rating (MVA) |  | 9.3 | 9.3 | 9.3 |  | 9.3 |  | 9.3 | 9.3 |  | 9.3 |  | 9.3 | 9.3 | 9.3
|  |  |  | 50 PoE Load (MVA) |  | 11.3 | 11.2 | 11.2 |  | 11.2 |  | 11.3 | 9.9 |  | 9.8 |  | 9.8 | 9.7 | 9.7
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | Hours PA > 95% Peak Load |  | 18.5 | 18.5 | 18.5 |  | 18.5 |  | 18.5 | 18.5 |  | 18.5 |  | 18.5 | 18.5 | 18.5
|  |  |  | Raw LAR (MVA) |  | 2 | 1.9 | 1.9 |  | 1.9 |  | 2 | 0.6 |  | 0.5 |  | 0.5 | 0.4 | 0.4
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 3.2 | 3.2 | 3.2 |  | 3.2 |  | 3.2 | 3.2 |  | 3.2 |  | 3.2 | 3.2 | 3.2
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 15 | 15 | 15 |  | 15 |  | 15 | 15 |  | 15 |  | 15 | 15 | 15
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 7.5 | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 | 7.5
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## CHIA
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | CHIA - Chillagoe (66/22kV) | [8 empty] | Supply |  | TURK - Turkinje 66kV BSP
| Description |  |  |  | Region is Far North
Transformer size is 1x66/22kV 6.3MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.4% W -1.1%2025 S -1.6% W -1.3%2026 S -1.4% W -1.3%2027 S -1.0% W -0.5
|  |  | Latest Peak Compensated Load | [5 empty] | 0.6 MVA on 16/11/2022 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 8.9 | 8.9 | 8.9 |  | 8.9 |  | 8.9 | 9.2 |  | 9.2 |  | 9.2 | 9.2 | 9.2
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.999 | 0.999 | 0.999 |  | 0.999 |  | 0.999 | 0.889 |  | 0.889 |  | 0.889 | 0.889 | 0.889
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 13 | 13 | 13 |  | 13 |  | 13 | 13 |  | 13 |  | 13 | 13 | 13
|  |  |  | Raw LAR (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Mobile Plant Avail (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 6.3 | 6.3 | 6.3 |  | 6.3 |  | 6.3 | 6.3 |  | 6.3 |  | 6.3 | 6.3 | 6.3
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## CHIL
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | CHIL - Childers (66/11kV) | [8 empty] | Supply |  | ISIS - Isis BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 1x66/11kV 10/7.5MVA ONB/ON;1x66/11kV 7.5/10MVA ON/ONB
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.8% W -0.8%2025 S -0.7% W -0.8%2026 S -0.2% W -0.1%2027 S 0.4% W -0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 7.3 MVA on 13/02/2023 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 20.9 | 20.9 | 20.9 |  | 20.9 |  | 20.9 | 22.4 |  | 22.4 |  | 22.4 | 22.4 | 22.4
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 7.2 | 7.2 | 7.1 |  | 7.2 |  | 7.2 | 6.2 |  | 6.2 |  | 6.1 | 6.1 | 6.1
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.965 | 0.974 | 0.965 |  | 0.974 |  | 0.965 | 0.979 |  | 0.979 |  | 0.979 | 0.979 | 0.979
|  |  |  | ECC Rating (MVA) |  | 11.2 | 11.2 | 11.2 |  | 11.2 |  | 11.2 | 11.2 |  | 11.2 |  | 11.2 | 11.2 | 11.2
|  |  |  | 50 PoE Load (MVA) |  | 7 | 7 | 6.9 |  | 7 |  | 7 | 5.6 |  | 5.6 |  | 5.6 | 5.5 | 5.5
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.4 | 0.4 | 0.3 |  | 0.4 |  | 0.4 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Hours PA > 95% Peak Load |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 15 | 15 | 15 |  | 15 |  | 15 | 15 |  | 15 |  | 15 | 15 | 15
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 7.5 | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 | 7.5
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## CHIN
Bulk Summary Information and Peak Load Forecast
Substation |  |  |  | CHIN - Chinchilla BSP (132/33kV) | [8 empty] | Supply |  | QCHA - Chinchilla TCP
Description |  |  |  | Region is South West
Transformer size is 1x106/33/11kV 20MVA ON;1x132/110kV 30MVA ONAN;1x132/33/11kV 50/63MVA ONAN/ONAF;1x106/33/5kV 20MVA ON(Standby)
Capacity of commissioned Embedded Generation (with Connection Agreements) is 15.3 MVA
|  | Latest Peak Compensated Load | [5 empty] | 17 MVA on 12/02/2023 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[5 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  | NCC Rating (MVA) |  | 62.8 | 62.8 | 62.8 |  | 62.8 |  | 62.8 | 75.9 |  | 75.9 |  | 75.9 | 75.9 | 75.9
|  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | 10 PoE Load (MVA) |  | 17.4 | 17.3 | 17.2 |  | 17.2 |  | 17.3 | 16.3 |  | 16.3 |  | 16.3 | 16.3 | 16.3
LARn (MVA)
LARn (MW)
|  |  | Power Factor at Peak Load |  | 1 | 1 | 1 |  | 1 |  | 1 | 0.996 |  | 0.996 |  | 0.996 | 0.996 | 0.996
|  |  | ECC Rating (MVA) |  | 48 | 48 | 48 |  | 48 |  | 48 | 55.4 |  | 55.4 |  | 55.4 | 55.4 | 55.4
|  |  | 50 PoE Load (MVA) |  | 16.4 | 16.3 | 16.2 |  | 16.2 |  | 16.3 | 15.4 |  | 15.4 |  | 15.4 | 15.5 | 15.5
|  |  | 50 PoE Load > 95% (MVA) |  | 0.8 | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.8 | 0.8
|  |  | Hours PA > 95% Peak Load |  | 55 | 55 | 55 |  | 55 |  | 55 | 55 |  | 55 |  | 55 | 55 | 55
Raw LAR (MVA)
|  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Capacity for Embedded Generation (MVA) |  | 70 | 70 | 70 |  | 70 |  | 70 | 70 |  | 70 |  | 70 | 70 | 70
|  |  | Firm Capacity for Embedded Generation (MVA) |  | 20 | 20 | 20 |  | 20 |  | 20 | 20 |  | 20 |  | 20 | 20 | 20
LARc (MVA)
LARc (MW)
|  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## CHTO
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | CHTO - Charters Towers (66/11kV) | [8 empty] | Supply |  | T095 - Millchester BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 2x66/11kV 8/10MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.9% W -0.7%2025 S -0.8% W -1.1%2026 S -0.3% W -0.7%2027 S 0.3% W -0.6%
|  |  | Latest Peak Compensated Load | [5 empty] | 10.6 MVA on 21/11/2022 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 26.8 | 26.8 | 26.8 |  | 26.8 |  | 26.8 | 29.9 |  | 29.9 |  | 29.9 | 29.9 | 29.9
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 10.7 | 10.6 | 10.5 |  | 10.6 |  | 10.7 | 8.3 |  | 8.2 |  | 8.1 | 8.1 | 8
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.997 | 0.997 | 0.997 |  | 0.997 |  | 0.997 | 0.993 |  | 0.993 |  | 0.993 | 0.993 | 0.993
|  |  |  | ECC Rating (MVA) |  | 15 | 15 | 15 |  | 15 |  | 15 | 15 |  | 15 |  | 15 | 15 | 15
|  |  |  | 50 PoE Load (MVA) |  | 10.4 | 10.3 | 10.2 |  | 10.3 |  | 10.4 | 7.9 |  | 7.8 |  | 7.7 | 7.7 | 7.6
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  |  | Hours PA > 95% Peak Load |  | 14.5 | 14.5 | 14.5 |  | 14.5 |  | 14.5 | 14.5 |  | 14.5 |  | 14.5 | 14.5 | 14.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 15.5 | 15.5 | 15.5 |  | 15.5 |  | 15.5 | 15.5 |  | 15.5 |  | 15.5 | 15.5 | 15.5
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 7.5 | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 | 7.5
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## CHTW
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | CHTW - Chinchilla Town (33/11kV) | [8 empty] | Supply |  | CHIN - Chinchilla BSP
| Description |  |  |  | Region is South West
Transformer size is 2x33/11kV 5MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.5% W -0.2%2025 S -1.7% W 0.1%,2026 S -1.1% W 0.3%,2027 S -0.4% W 0.3%
|  |  | Latest Peak Compensated Load | [5 empty] | 8.6 MVA on 01/03/2023 at 16:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 11 | 11 | 11 |  | 11 |  | 11 | 13 |  | 13 |  | 13 | 13 | 13
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 8.9 | 8.8 | 8.7 |  | 8.6 |  | 8.7 | 7.8 |  | 7.8 |  | 7.8 | 7.8 | 7.9
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.974 | 0.974 | 0.974 |  | 0.974 |  | 0.974 | 0.991 |  | 0.991 |  | 0.991 | 0.991 | 0.991
|  |  |  | ECC Rating (MVA) |  | 5.5 | 5.5 | 5.5 |  | 5.5 |  | 5.5 | 6.5 |  | 6.5 |  | 6.5 | 6.5 | 6.5
|  |  |  | 50 PoE Load (MVA) |  | 8.3 | 8.1 | 8 |  | 8 |  | 8 | 7.3 |  | 7.3 |  | 7.3 | 7.4 | 7.4
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.4 | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  |  | Hours PA > 95% Peak Load |  | 7.5 | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 | 7.5
|  |  |  | Raw LAR (MVA) |  | 2.8 | 2.6 | 2.5 |  | 2.5 |  | 2.5 | 0.8 |  | 0.8 |  | 0.8 | 0.9 | 0.9
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0.7 | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.7 | 0.7
|  |  |  | Mobile Plant Avail (MVA) |  | 2.5 | 2.5 | 2.5 |  | 2.5 |  | 2.5 | 2.5 |  | 2.5 |  | 2.5 | 2.5 | 2.5
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 | 5 | 5
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## CHUM
Bulk Summary Information and Peak Load Forecast
Substation |  |  |  | CHUM - Chumvale BSP (220/66kV) | [8 empty] | Supply |  | QMCH - Mica Creek 220kV TCP
Description |  |  |  | Region is Nth Queensland
Transformer size is 1x220/66kV 30/40MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
|  | Latest Peak Compensated Load | [5 empty] | 7.1 MVA on 08/12/2022 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[5 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  | NCC Rating (MVA) |  | 49.8 | 49.8 | 49.8 |  | 49.8 |  | 49.8 | 59.8 |  | 59.8 |  | 59.8 | 59.8 | 59.8
|  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | 10 PoE Load (MVA) |  | 7.3 | 7.3 | 7.3 |  | 7.3 |  | 7.3 | 4.5 |  | 4.5 |  | 4.5 | 4.4 | 4.4
LARn (MVA)
LARn (MW)
|  |  | Power Factor at Peak Load |  | 0.993 | 0.993 | 0.993 |  | 0.993 |  | 0.993 | 0.998 |  | 0.998 |  | 0.998 | 0.998 | 0.998
|  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | 50 PoE Load (MVA) |  | 7.1 | 7.1 | 7.1 |  | 7.1 |  | 7.1 | 4.3 |  | 4.3 |  | 4.3 | 4.3 | 4.3
|  |  | 50 PoE Load > 95% (MVA) |  | 0.4 | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  | Hours PA > 95% Peak Load |  | 13.5 | 13.5 | 13.5 |  | 13.5 |  | 13.5 | 13.5 |  | 13.5 |  | 13.5 | 13.5 | 13.5
|  |  | Raw LAR (MVA) |  | 7.1 | 7.1 | 7.1 |  | 7.1 |  | 7.1 | 4.3 |  | 4.3 |  | 4.3 | 4.3 | 4.3
|  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Manual Trans Avail (MVA) |  | 6.8 | 6.8 | 6.8 |  | 6.8 |  | 6.8 | 6.8 |  | 6.8 |  | 6.8 | 6.8 | 6.8
|  |  | Mobile Plant Avail (MVA) |  | 1.3 | 1.3 | 1.3 |  | 1.3 |  | 1.3 | 1.3 |  | 1.3 |  | 1.3 | 1.3 | 1.3
|  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Capacity for Embedded Generation (MVA) |  | 30 | 30 | 30 |  | 30 |  | 30 | 30 |  | 30 |  | 30 | 30 | 30
|  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## CLBS
Bulk Summary Information and Peak Load Forecast
Substation |  |  |  | CLBS - Clermont BSP (132/66kV) | [8 empty] | Supply |  | QLCM - Lilyvale (Barcaldine & Clermont) TCP
Description |  |  |  | Region is Capricornia
Transformer size is 2x132/69/11kV 30MVA OFDAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 75.0 MVA
|  | Latest Peak Compensated Load | [5 empty] | 42.6 MVA on 17/03/2023 at 14:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[5 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  | NCC Rating (MVA) |  | 80.9 | 80.9 | 80.9 |  | 80.9 |  | 80.9 | 86.9 |  | 86.9 |  | 86.9 | 86.9 | 86.9
|  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | 10 PoE Load (MVA) |  | 22.7 | 22.6 | 22.6 |  | 22.7 |  | 22.8 | 18.6 |  | 18.5 |  | 18.5 | 18.5 | 18.6
LARn (MVA)
LARn (MW)
|  |  | Power Factor at Peak Load |  | 0.852 | 0.852 | 0.852 |  | 0.852 |  | 0.852 | 0.988 |  | 0.988 |  | 0.988 | 0.988 | 0.988
|  |  | ECC Rating (MVA) |  | 44.9 | 44.9 | 44.9 |  | 44.9 |  | 44.9 | 44.9 |  | 44.9 |  | 44.9 | 44.9 | 44.9
|  |  | 50 PoE Load (MVA) |  | 21.8 | 21.7 | 21.7 |  | 21.7 |  | 21.8 | 18.1 |  | 18.1 |  | 18.1 | 18.1 | 18.1
|  |  | 50 PoE Load > 95% (MVA) |  | 1.1 | 1.1 | 1.1 |  | 1.1 |  | 1.1 | 0.9 |  | 0.9 |  | 0.9 | 0.9 | 0.9
|  |  | Hours PA > 95% Peak Load |  | 6.5 | 6.5 | 6.5 |  | 6.5 |  | 6.5 | 6.5 |  | 6.5 |  | 6.5 | 6.5 | 6.5
Raw LAR (MVA)
|  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
Capacity for Embedded Generation (MVA)
Firm Capacity for Embedded Generation (MVA)
LARc (MVA)
LARc (MW)
|  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## CLER
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | CLER - Clermont (66/22kV) | [8 empty] | Supply |  | CLBS - Clermont BSP
| Description |  |  |  | Region is Capricornia
Transformer size is 1xCLERSS CL-T6 11KV TRANSF 6 7.5/10 MVA;1xCLERSS TRANSF 5 7.5/10MVA
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.8% W -0.4%2025 S -0.7% W -0.1%2026 S -0.2% W 0.2%,2027 S 0.5% W 0.3%
|  |  | Latest Peak Compensated Load | [5 empty] | 9.5 MVA on 13/02/2023 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 22 | 22 | 22 |  | 22 |  | 22 | 22 |  | 22 |  | 22 | 22 | 22
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 10.4 | 10.4 | 10.3 |  | 10.4 |  | 10.5 | 7.8 |  | 7.8 |  | 7.8 | 7.8 | 7.8
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 1 | 1 | 1 |  | 1 |  | 1 | 0.997 |  | 0.997 |  | 0.997 | 0.997 | 0.997
|  |  |  | ECC Rating (MVA) |  | 11.5 | 11.5 | 11.5 |  | 11.5 |  | 11.5 | 13 |  | 13 |  | 13 | 13 | 13
|  |  |  | 50 PoE Load (MVA) |  | 9.8 | 9.7 | 9.7 |  | 9.7 |  | 9.9 | 7.6 |  | 7.6 |  | 7.5 | 7.6 | 7.6
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  |  | Hours PA > 95% Peak Load |  | 14.5 | 14.5 | 14.5 |  | 14.5 |  | 14.5 | 14.5 |  | 14.5 |  | 14.5 | 14.5 | 14.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 15 | 15 | 15 |  | 15 |  | 15 | 15 |  | 15 |  | 15 | 15 | 15
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 7.5 | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 | 7.5
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## CLIF
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | CLIF - Clifton (33/11kV) | [8 empty] | Supply |  | T043 - South Toowoomba BSP
| Description |  |  |  | Region is South West
Transformer size is 2x33/11kV 3MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.2% W -0.4%2025 S -1.4% W -0.3%2026 S -0.8% W 0.0%,2027 S -0.1% W 0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 3.5 MVA on 08/06/2022 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 8 | 8 | 8 |  | 8 |  | 8 | 8.7 |  | 8.7 |  | 8.7 | 8.7 | 8.7
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 4 | 4.5 | 4.8 |  | 4.8 |  | 4.8 | 3.7 |  | 3.9 |  | 4.4 | 4.7 | 4.7
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.997 | 0.997 | 0.997 |  | 0.997 |  | 0.997 | 0.992 |  | 0.992 |  | 0.992 | 0.992 | 0.992
|  |  |  | ECC Rating (MVA) |  | 4.4 | 4.4 | 4.4 |  | 4.4 |  | 4.4 | 4.5 |  | 4.5 |  | 4.5 | 4.5 | 4.5
|  |  |  | 50 PoE Load (MVA) |  | 3.6 | 4.2 | 4.5 |  | 4.5 |  | 4.5 | 3.6 |  | 3.8 |  | 4.3 | 4.5 | 4.5
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 | 5 | 5
|  |  |  | Raw LAR (MVA) |  |  |  | 0.1 |  | 0.1 |  | 0.1
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 6 | 6 | 6 |  | 6 |  | 6 | 6 |  | 6 |  | 6 | 6 | 6
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 3 | 3 | 3 |  | 3 |  | 3 | 3 |  | 3 |  | 3 | 3 | 3
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## CLIN
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | CLIN - Clinton (66/11kV) | [8 empty] | Supply |  | GLNO - Gladstone North BSP
| Description |  |  |  | Region is Capricornia
Transformer size is 2x66/11kV 16/20/25MVA ONAN/ONAF/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -4.4% W -0.1%2025 S -2.5% W -0.1%2026 S -2.1% W 0.3%,2027 S -1.4% W 0.3%
|  |  | Latest Peak Compensated Load | [5 empty] | 16 MVA on 08/12/2022 at 16:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 70.4 | 70.4 | 70.4 |  | 70.4 |  | 70.4 | 74.8 |  | 74.8 |  | 74.8 | 74.8 | 74.8
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 16.5 | 16 | 15.7 |  | 15.5 |  | 15.5 | 10.9 |  | 10.9 |  | 10.9 | 10.9 | 10.9
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.952 | 0.952 | 0.952 |  | 0.952 |  | 0.952 | 0.983 |  | 0.983 |  | 0.983 | 0.983 | 0.983
|  |  |  | ECC Rating (MVA) |  | 37.4 | 37.4 | 37.4 |  | 37.4 |  | 37.4 | 37.4 |  | 37.4 |  | 37.4 | 37.4 | 37.4
|  |  |  | 50 PoE Load (MVA) |  | 15.6 | 15.2 | 14.9 |  | 14.7 |  | 14.7 | 10.6 |  | 10.6 |  | 10.6 | 10.6 | 10.6
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.8 | 0.8 | 0.7 |  | 0.7 |  | 0.7 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | Hours PA > 95% Peak Load |  | 11 | 11 | 11 |  | 11 |  | 11 | 11 |  | 11 |  | 11 | 11 | 11
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 3 | 3 | 3 |  | 3 |  | 3 | 3 |  | 3 |  | 3 | 3 | 3
|  |  |  | Mobile Plant Avail (MVA) |  | 4 | 4 | 4 |  | 4 |  | 4 | 4 |  | 4 |  | 4 | 4 | 4
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 32 | 32 | 32 |  | 32 |  | 32 | 32 |  | 32 |  | 32 | 32 | 32
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 16 | 16 | 16 |  | 16 |  | 16 | 16 |  | 16 |  | 16 | 16 | 16
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## CLON
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | CLON - Cloncurry (66/11kV) | [8 empty] | Supply |  | CHUM - Chumvale BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/11kV 2/2.3MVA ONAN/ONAF;1x66/11kV 3.15MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.3% W -1.3%2025 S -1.3% W -1.7%2026 S -0.9% W -0.7%2027 S -0.0% W -0.5
|  |  | Latest Peak Compensated Load | [5 empty] | 3.5 MVA on 12/12/2022 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 6.7 | 6.7 | 6.7 |  | 6.7 |  | 6.7 | 6.9 |  | 6.9 |  | 6.9 | 6.9 | 6.9
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 3.7 | 3.6 | 3.6 |  | 3.6 |  | 3.6 | 2.4 |  | 2.4 |  | 2.4 | 2.3 | 2.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.986 | 0.986 | 0.986 |  | 0.986 |  | 0.986 | 0.988 |  | 0.988 |  | 0.988 | 0.988 | 0.988
|  |  |  | ECC Rating (MVA) |  | 3.4 | 3.4 | 3.4 |  | 3.4 |  | 3.4 | 3.4 |  | 3.4 |  | 3.4 | 3.4 | 3.4
|  |  |  | 50 PoE Load (MVA) |  | 3.5 | 3.5 | 3.4 |  | 3.4 |  | 3.5 | 2.2 |  | 2.1 |  | 2.1 | 2.1 | 2.1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 51 | 51 | 51 |  | 51 |  | 51 | 51 |  | 51 |  | 51 | 51 | 51
|  |  |  | Raw LAR (MVA) |  | 0.1 | 0.1 |  |  |  |  | 0.1
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 1.7 | 1.7 | 1.7 |  | 1.7 |  | 1.7 | 1.7 |  | 1.7 |  | 1.7 | 1.7 | 1.7
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 5.15 | 5.15 | 5.15 |  | 5.15 |  | 5.15 | 5.15 |  | 5.15 |  | 5.15 | 5.15 | 5.15
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 | 2 | 2
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## CLSO
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | CLSO - Clare South (66/11kV) | [8 empty] | Supply |  | T193 - Clare South BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/11kV 6.3MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.7% W 0.3%,2025 S -1.2% W -0.3%2026 S -0.7% W 0.2%,2027 S -0.1% W 0.2%
|  |  | Latest Peak Compensated Load | [5 empty] | 2.8 MVA on 15/12/2022 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 7.5 | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 8.3 |  | 8.3 |  | 8.3 | 8.3 | 8.3
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 2.8 | 2.8 | 2.8 |  | 2.8 |  | 2.8 | 1.5 |  | 1.5 |  | 1.5 | 1.5 | 1.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.903 | 0.903 | 0.903 |  | 0.903 |  | 0.903 | 0.897 |  | 0.897 |  | 0.897 | 0.897 | 0.897
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 2.8 | 2.7 | 2.7 |  | 2.7 |  | 2.7 | 1.5 |  | 1.5 |  | 1.5 | 1.5 | 1.5
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 12 | 12 | 12 |  | 12 |  | 12 | 12 |  | 12 |  | 12 | 12 | 12
|  |  |  | Raw LAR (MVA) |  | 2.8 | 2.7 | 2.7 |  | 2.7 |  | 2.7 | 1.5 |  | 1.5 |  | 1.5 | 1.5 | 1.5
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 2.2 | 2.2 | 2.2 |  | 2.2 |  | 2.2 | 2.2 |  | 2.2 |  | 2.2 | 2.2 | 2.2
|  |  |  | Mobile Plant Avail (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 6.3 | 6.3 | 6.3 |  | 6.3 |  | 6.3 | 6.3 |  | 6.3 |  | 6.3 | 6.3 | 6.3
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## COLU
Bulk Summary Information and Peak Load Forecast
Substation |  |  |  | COLU - Columboola BSP (132/33kV) | [8 empty] | Supply |  | T194 - Columboola TCP
Description |  |  |  | Region is South West
Transformer size is 1xCOLU 132/3311KV 24/32MVA TRANSF 1
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
|  | Latest Peak Compensated Load | [5 empty] | 14.1 MVA on 13/02/2023 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[5 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  | NCC Rating (MVA) |  | 40.2 | 40.2 | 40.2 |  | 40.2 |  | 40.2 | 47.4 |  | 47.4 |  | 47.4 | 47.4 | 47.4
|  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | 10 PoE Load (MVA) |  | 14.8 | 14.7 | 14.6 |  | 14.6 |  | 14.7 | 14.1 |  | 14.1 |  | 14 | 14 | 14
LARn (MVA)
LARn (MW)
|  |  | Power Factor at Peak Load |  | 0.993 | 0.993 | 0.993 |  | 0.993 |  | 0.993 | 0.996 |  | 0.996 |  | 0.996 | 0.996 | 0.996
|  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | 50 PoE Load (MVA) |  | 14 | 13.9 | 13.8 |  | 13.8 |  | 13.9 | 13.4 |  | 13.3 |  | 13.3 | 13.3 | 13.3
|  |  | 50 PoE Load > 95% (MVA) |  | 0.7 | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.7 | 0.7
|  |  | Hours PA > 95% Peak Load |  | 11.5 | 11.5 | 11.5 |  | 11.5 |  | 11.5 | 11.5 |  | 11.5 |  | 11.5 | 11.5 | 11.5
|  |  | Raw LAR (MVA) |  | 14 | 13.9 | 13.8 |  | 13.8 |  | 13.9 | 13.4 |  | 13.3 |  | 13.3 | 13.3 | 13.3
|  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Manual Trans Avail (MVA) |  | 14 | 14 | 14 |  | 14 |  | 14 | 14 |  | 14 |  | 14 | 14 | 14
|  |  | Mobile Plant Avail (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 | 2 | 2
|  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Capacity for Embedded Generation (MVA) |  | 24 | 24 | 24 |  | 24 |  | 24 | 24 |  | 24 |  | 24 | 24 | 24
|  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## COME
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | COME - Comet (66/22kV) | [8 empty] | Supply |  | T032 - Blackwater BSP
| Description |  |  |  | Region is Capricornia
Transformer size is 1x66/22kV 6.3MVA ON;1x66/22kV 2MVA ON(Standby)
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.3% W -1.0%2025 S -1.3% W -1.3%2026 S -0.9% W -1.2%2027 S -0.3% W -1.5
|  |  | Latest Peak Compensated Load | [5 empty] | 2.8 MVA on 03/01/2023 at 16:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 6.9 | 6.9 | 6.9 |  | 6.9 |  | 6.9 | 6.9 |  | 6.9 |  | 6.9 | 6.9 | 6.9
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 3 | 2.9 | 2.9 |  | 2.9 |  | 2.9 | 1.1 |  | 1.1 |  | 1.1 | 1.1 | 1.1
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.881 | 0.881 | 0.881 |  | 0.881 |  | 0.881 | 0.792 |  | 0.792 |  | 0.792 | 0.792 | 0.792
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 2.7 | 2.7 | 2.7 |  | 2.7 |  | 2.7 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 28.5 | 28.5 | 28.5 |  | 28.5 |  | 28.5 | 28.5 |  | 28.5 |  | 28.5 | 28.5 | 28.5
|  |  |  | Raw LAR (MVA) |  | 2.7 | 2.7 | 2.7 |  | 2.7 |  | 2.7 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 2.4 | 2.4 | 2.4 |  | 2.4 |  | 2.4 | 2.4 |  | 2.4 |  | 2.4 | 2.4 | 2.4
|  |  |  | Mobile Plant Avail (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 6.3 | 6.3 | 6.3 |  | 6.3 |  | 6.3 | 6.3 |  | 6.3 |  | 6.3 | 6.3 | 6.3
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 | 2 | 2
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## COOK
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | COOK - Cooktown (66/22kV) | [8 empty] | Supply |  | T159 - Lakeland BSP
| Description |  |  |  | Region is Far North
Transformer size is 2x66/22kV 8/10MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.7% W -0.2%2025 S -0.7% W -0.1%2026 S -0.1% W 0.2%,2027 S 0.7% W 0.3%
|  |  | Latest Peak Compensated Load | [5 empty] | 4.4 MVA on 02/02/2023 at 16:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 21.5 | 21.5 | 21.5 |  | 21.5 |  | 21.5 | 24.6 |  | 24.6 |  | 24.6 | 24.6 | 24.6
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 4.6 | 4.5 | 4.5 |  | 4.5 |  | 4.6 | 3.9 |  | 3.9 |  | 3.8 | 3.9 | 3.9
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.984 | 0.984 | 0.984 |  | 0.984 |  | 0.984 | 0.987 |  | 0.987 |  | 0.987 | 0.987 | 0.987
|  |  |  | ECC Rating (MVA) |  | 12.6 | 12.6 | 12.6 |  | 12.6 |  | 12.6 | 13.6 |  | 13.6 |  | 13.6 | 13.6 | 13.6
|  |  |  | 50 PoE Load (MVA) |  | 4.4 | 4.4 | 4.4 |  | 4.4 |  | 4.5 | 3.7 |  | 3.7 |  | 3.7 | 3.7 | 3.7
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 26.5 | 26.5 | 26.5 |  | 26.5 |  | 26.5 | 26.5 |  | 26.5 |  | 26.5 | 26.5 | 26.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 16 | 16 | 16 |  | 16 |  | 16 | 16 |  | 16 |  | 16 | 16 | 16
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 8 | 8 | 8 |  | 8 |  | 8 | 8 |  | 8 |  | 8 | 8 | 8
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## COOM
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | COOM - Coominglah (66/22kV) | [8 empty] | Supply |  | T026 - Biloela BSP
| Description |  |  |  | Region is Capricornia
Transformer size is 2x66/22kV 2MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.2% W -0.9%2025 S -0.9% W -0.5%2026 S -0.5% W -0.3%2027 S 0.2% W -0.2%
|  |  | Latest Peak Compensated Load | [5 empty] | 1.6 MVA on 05/07/2022 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 5.3 | 5.3 | 5.3 |  | 5.3 |  | 5.3 | 6 |  | 6 |  | 6 | 6 | 6
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 1.5 | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.6 |  | 1.5 |  | 1.5 | 1.5 | 1.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.929 | 0.929 | 0.929 |  | 0.929 |  | 0.929 | 0.889 |  | 0.889 |  | 0.889 | 0.889 | 0.889
|  |  |  | ECC Rating (MVA) |  | 3 | 3 | 3 |  | 3 |  | 3 | 3 |  | 3 |  | 3 | 3 | 3
|  |  |  | 50 PoE Load (MVA) |  | 1.4 | 1.4 | 1.4 |  | 1.4 |  | 1.4 | 1.5 |  | 1.5 |  | 1.5 | 1.5 | 1.5
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 | 5 | 5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 3 | 3 | 3 |  | 3 |  | 3 | 3 |  | 3 |  | 3 | 3 | 3
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 4 | 4 | 4 |  | 4 |  | 4 | 4 |  | 4 |  | 4 | 4 | 4
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 | 2 | 2
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## CPRE
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | CPRE - Cape River East 132/66kV (66/33kV) | [8 empty] | Supply |  | CRET - Cape River East Transmission Accumulator
| Description |  |  |  | Region is Nth Queensland
Transformer size is 2x132/66/33kV 40/40/27MVA
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 0.0%, 2024 S 0.0% W 0.0%, 2025 S 0.0% W 0.0%, 2026 S 0.0% W 0.0%, 2027 S 0.0% W 0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 35.5 MVA on 20/02/2023 at 11:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 80 | 80 | 80 |  | 80 |  | 80 | 80 |  | 80 |  | 80 | 80 | 80
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 41.5 | 41.5 | 41.5 |  | 41.5 |  | 41.5 | 29.7 |  | 29.7 |  | 29.7 | 29.7 | 29.7
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.703 | 0.703 | 0.703 |  | 0.703 |  | 0.703 | 0.615 |  | 0.615 |  | 0.615 | 0.615 | 0.615
|  |  |  | ECC Rating (MVA) |  | 40 | 40 | 40 |  | 40 |  | 40 | 40 |  | 40 |  | 40 | 40 | 40
|  |  |  | 50 PoE Load (MVA) |  | 40.5 | 40.5 | 40.5 |  | 40.5 |  | 40.5 | 29 |  | 29 |  | 29 | 29 | 29
|  |  |  | 50 PoE Load > 95% (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 1.5 |  | 1.5 |  | 1.5 | 1.5 | 1.5
|  |  |  | Hours PA > 95% Peak Load |  | 110.5 | 110.5 | 110.5 |  | 110.5 |  | 110.5 | 110.5 |  | 110.5 |  | 110.5 | 110.5 | 110.5
|  |  |  | Raw LAR (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | LARc (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5
|  |  |  | LARc (MW) |  | 0.4 | 0.4 | 0.4 |  | 0.4 |  | 0.4
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | No | No | No |  | No |  | No | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## CRAI
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | CRAI - Craiglie (132/22kV) | [8 empty] | Supply |  | QTUH - Turkinje 132kV TCP
| Description |  |  |  | Region is Far North
Transformer size is 2x132/22kV 15/20MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.5% W -0.5%2025 S -1.0% W -0.6%2026 S -0.2% W -0.3%2027 S 0.6% W -0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 16.2 MVA on 01/11/2022 at 16:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 47.1 | 47.1 | 47.1 |  | 47.1 |  | 47.1 | 53.4 |  | 53.4 |  | 53.4 | 53.4 | 53.4
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 17.8 | 17.7 | 17.6 |  | 17.7 |  | 18 | 12.9 |  | 12.9 |  | 12.8 | 12.8 | 12.8
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.995 | 0.995 | 0.995 |  | 0.995 |  | 0.995 | 0.998 |  | 0.998 |  | 0.998 | 0.998 | 0.998
|  |  |  | ECC Rating (MVA) |  | 27.6 | 27.6 | 27.6 |  | 27.6 |  | 27.6 | 29.8 |  | 29.8 |  | 29.8 | 29.8 | 29.8
|  |  |  | 50 PoE Load (MVA) |  | 17.2 | 17 | 17 |  | 17.1 |  | 17.3 | 12.6 |  | 12.6 |  | 12.5 | 12.5 | 12.4
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.9 | 0.9 | 0.9 |  | 0.9 |  | 0.9 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  |  | Hours PA > 95% Peak Load |  | 20 | 20 | 20 |  | 20 |  | 20 | 20 |  | 20 |  | 20 | 20 | 20
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 | 2 | 2
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 | 2 | 2
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 4.2 | 4.2 | 4.2 |  | 4.2 |  | 4.2 | 4.2 |  | 4.2 |  | 4.2 | 4.2 | 4.2
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 2.1 | 2.1 | 2.1 |  | 2.1 |  | 2.1 | 2.1 |  | 2.1 |  | 2.1 | 2.1 | 2.1
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## CRAN
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | CRAN - Cranbrook (66/11kV) | [8 empty] | Supply |  | TMES - Townsville Mesh
| Description |  |  |  | Region is Nth Queensland
Transformer size is 2x66/11kV 15/20/25MVA ONAN/ONAF/OFDAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.1% W -1.3%2025 S -1.2% W -1.2%2026 S -0.7% W 0.1%,2027 S 0.0% W 0.2%
|  |  | Latest Peak Compensated Load | [5 empty] | 13.9 MVA on 15/12/2022 at 17:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 55.6 | 55.6 | 55.6 |  | 55.6 |  | 55.6 | 57.9 |  | 57.9 |  | 57.9 | 57.9 | 57.9
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 14.3 | 14.1 | 14 |  | 14 |  | 14.1 | 8.3 |  | 8.2 |  | 8.1 | 8.1 | 8.1
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.99 | 0.99 | 0.99 |  | 0.99 |  | 0.99 | 0.994 |  | 0.994 |  | 0.994 | 0.994 | 0.994
|  |  |  | ECC Rating (MVA) |  | 30.5 | 30.5 | 30.5 |  | 30.5 |  | 30.5 | 31.9 |  | 31.9 |  | 31.9 | 31.9 | 31.9
|  |  |  | 50 PoE Load (MVA) |  | 13.8 | 13.6 | 13.5 |  | 13.5 |  | 13.6 | 7.9 |  | 7.8 |  | 7.7 | 7.7 | 7.7
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.7 | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  |  | Hours PA > 95% Peak Load |  | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 | 5 | 5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 18.2 | 18.2 | 18.2 |  | 18.2 |  | 18.2 | 18.2 |  | 18.2 |  | 18.2 | 18.2 | 18.2
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 9.1 | 9.1 | 9.1 |  | 9.1 |  | 9.1 | 9.1 |  | 9.1 |  | 9.1 | 9.1 | 9.1
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## CRED
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | CRED - Crediton (66/11kV) | [8 empty] | Supply |  | PIVA - Pioneer Valley BSP
| Description |  |  |  | Region is Mackay
Transformer size is 1x66/11kV 1MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.9% W -0.4%2025 S -0.6% W -0.1%2026 S -0.2% W 0.2%,2027 S 0.6% W 0.4%
|  |  | Latest Peak Compensated Load | [5 empty] | 0.6 MVA on 08/12/2022 at 19:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 1.1 | 1.1 | 1.1 |  | 1.1 |  | 1.1 | 1.1 |  | 1.1 |  | 1.1 | 1.1 | 1.1
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.974 | 0.974 | 0.974 |  | 0.974 |  | 0.974 | 0.986 |  | 0.986 |  | 0.986 | 0.986 | 0.986
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 232 | 232 | 232 |  | 232 |  | 232 | 232 |  | 232 |  | 232 | 232 | 232
|  |  |  | Raw LAR (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## CRNE
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | CRNE - Crows Nest (33/11kV) | [8 empty] | Supply |  | T029 - Postmans Ridge BSP
| Description |  |  |  | Region is South West
Transformer size is 1x33/11kV 6.3MVA ONAN;1x33/11kV 1.5MVA ON(Standby)
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.0% W -0.7%2025 S -0.9% W -0.5%2026 S -0.4% W -0.2%2027 S 0.3% W -0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 5 MVA on 04/07/2022 at 17:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 8.3 | 8.3 | 8.3 |  | 8.3 |  | 8.3 | 9.4 |  | 9.4 |  | 9.4 | 9.4 | 9.4
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 4.4 | 4.4 | 4.3 |  | 4.4 |  | 4.4 | 5.1 |  | 5.1 |  | 5 | 5 | 5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.995 | 0.995 | 0.995 |  | 0.995 |  | 0.995 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 3.9 | 3.9 | 3.9 |  | 3.9 |  | 3.9 | 4.9 |  | 4.9 |  | 4.8 | 4.8 | 4.8
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 4.5 | 4.5 | 4.5 |  | 4.5 |  | 4.5 | 4.5 |  | 4.5 |  | 4.5 | 4.5 | 4.5
|  |  |  | Raw LAR (MVA) |  | 3.9 | 3.9 | 3.9 |  | 3.9 |  | 3.9 | 4.9 |  | 4.9 |  | 4.8 | 4.8 | 4.8
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 1.5 | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.5 | 1.5
|  |  |  | Mobile Plant Avail (MVA) |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 6.3 | 6.3 | 6.3 |  | 6.3 |  | 6.3 | 6.3 |  | 6.3 |  | 6.3 | 6.3 | 6.3
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## CROY
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | CROY - Croydon (66/22kV) | [8 empty] | Supply |  | GEOR - Georgetown BSP
| Description |  |  |  | Region is Far North
Transformer size is 2x66/22kV 2MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.4% W 0.0%,2025 S -0.3% W 0.2%,2026 S 0.2% W 0.5%, 2027 S 0.7% W 0.4%
|  |  | Latest Peak Compensated Load | [5 empty] | 0.6 MVA on 13/12/2022 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 5.1 | 5.1 | 5.1 |  | 5.1 |  | 5.1 | 5.4 |  | 5.4 |  | 5.4 | 5.4 | 5.4
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.982 | 0.982 | 0.982 |  | 0.982 |  | 0.982 | 0.951 |  | 0.951 |  | 0.951 | 0.951 | 0.951
|  |  |  | ECC Rating (MVA) |  | 3 | 3 | 3 |  | 3 |  | 3 | 3 |  | 3 |  | 3 | 3 | 3
|  |  |  | 50 PoE Load (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 77 | 77 | 77 |  | 77 |  | 77 | 77 |  | 77 |  | 77 | 77 | 77
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 4 | 4 | 4 |  | 4 |  | 4 | 4 |  | 4 |  | 4 | 4 | 4
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 | 2 | 2
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## CUNN
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | CUNN - Cunnamulla (66/22kV) | [8 empty] | Supply |  | ROMA - Roma 66kV BSP
| Description |  |  |  | Region is South West
Transformer size is 1x66/11kV 5MVA ONAN;1x66/22kV 5MVA ONAN;1x22/11kV 3MVA ONAN(Standby)
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.5% W -1.1%2025 S -1.4% W -0.9%2026 S -0.9% W -0.6%2027 S -0.2% W -0.4
|  |  | Latest Peak Compensated Load | [5 empty] | 4.9 MVA on 22/06/2022 at 07:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 11.3 | 11.3 | 11.3 |  | 11.3 |  | 11.3 | 13.9 |  | 13.9 |  | 13.9 | 13.9 | 13.9
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 4.4 | 4.4 | 5.5 |  | 5.4 |  | 5.5 | 4.8 |  | 4.7 |  | 5.4 | 5.4 | 5.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.994 | 0.995 | 0.989 |  | 0.989 |  | 0.989 | 0.998 |  | 0.998 |  | 0.996 | 0.996 | 0.996
|  |  |  | ECC Rating (MVA) |  | 6.5 | 6.5 | 6.5 |  | 6.5 |  | 6.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 | 7.5
|  |  |  | 50 PoE Load (MVA) |  | 4.3 | 4.3 | 5.4 |  | 5.4 |  | 5.4 | 4.6 |  | 4.5 |  | 5.2 | 5.2 | 5.1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.3 |  | 0.3 |  | 0.3 | 0.2 |  | 0.2 |  | 0.3 | 0.3 | 0.3
|  |  |  | Hours PA > 95% Peak Load |  | 6 | 6 | 6 |  | 6 |  | 6 | 6 |  | 6 |  | 6 | 6 | 6
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 13 | 13 | 13 |  | 13 |  | 13 | 13 |  | 13 |  | 13 | 13 | 13
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 8 | 8 | 8 |  | 8 |  | 8 | 8 |  | 8 |  | 8 | 8 | 8
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## DACE
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | DACE - Dalby Central (33/11kV) | [8 empty] | Supply |  | T002 - Dalby East BSP
| Description |  |  |  | Region is South West
Transformer size is 2x33/11kV 16/20MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.0% W -0.7%2025 S -1.0% W -0.6%2026 S -0.5% W -0.1%2027 S 0.1% W 0.4%
|  |  | Latest Peak Compensated Load | [5 empty] | 14.5 MVA on 13/02/2023 at 17:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 47.6 | 47.6 | 47.6 |  | 47.6 |  | 47.6 | 50.9 |  | 50.9 |  | 50.9 | 50.9 | 50.9
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 16.3 | 16.1 | 16 |  | 16 |  | 16.2 | 14.6 |  | 14.5 |  | 14.4 | 14.4 | 14.4
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.981 | 0.981 | 0.981 |  | 0.981 |  | 0.981 | 0.99 |  | 0.99 |  | 0.99 | 0.99 | 0.99
|  |  |  | ECC Rating (MVA) |  | 26.4 | 26.4 | 26.4 |  | 26.4 |  | 26.4 | 28.1 |  | 28.1 |  | 28.1 | 28.1 | 28.1
|  |  |  | 50 PoE Load (MVA) |  | 14.9 | 14.8 | 14.7 |  | 14.7 |  | 14.8 | 13.5 |  | 13.4 |  | 13.3 | 13.3 | 13.4
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.7 | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.7 | 0.7
|  |  |  | Hours PA > 95% Peak Load |  | 5.5 | 5.5 | 5.5 |  | 5.5 |  | 5.5 | 5.5 |  | 5.5 |  | 5.5 | 5.5 | 5.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 32 | 32 | 32 |  | 32 |  | 32 | 32 |  | 32 |  | 32 | 32 | 32
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 16 | 16 | 16 |  | 16 |  | 16 | 16 |  | 16 |  | 16 | 16 | 16
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## DAGL
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | DAGL - Dan Gleeson (66/11kV) | [8 empty] | Supply |  | TMES - Townsville Mesh
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/11kV 15/20/25MVA ONAN/ODAN/ODAF;1x66/11kV 15/20/25MVA ONAN/ONAF/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.7% W 0.1%,2025 S -0.6% W 0.4%,2026 S -0.2% W 0.6%,2027 S 0.5% W 0.7%
|  |  | Latest Peak Compensated Load | [5 empty] | 25.1 MVA on 21/11/2022 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 42.6 | 42.6 | 42.6 |  | 42.6 |  | 42.6 | 39.8 |  | 39.8 |  | 39.8 | 39.8 | 39.8
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 30.7 | 30.5 | 30.5 |  | 30.6 |  | 31 | 16.8 |  | 16.8 |  | 16.9 | 17 | 17.1
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.992 | 0.992 | 0.992 |  | 0.992 |  | 0.992 | 0.997 |  | 0.997 |  | 0.997 | 0.997 | 0.997
|  |  |  | ECC Rating (MVA) |  | 28.1 | 28.1 | 28.1 |  | 28.1 |  | 28.1 | 26.3 |  | 26.3 |  | 26.3 | 26.3 | 26.3
|  |  |  | 50 PoE Load (MVA) |  | 29.2 | 29 | 28.9 |  | 29.1 |  | 29.4 | 16.5 |  | 16.5 |  | 16.5 | 16.7 | 16.8
|  |  |  | 50 PoE Load > 95% (MVA) |  | 1.5 | 1.5 | 1.4 |  | 1.5 |  | 1.5 | 0.8 |  | 0.8 |  | 0.8 | 0.8 | 0.8
|  |  |  | Hours PA > 95% Peak Load |  | 11 | 11 | 11 |  | 11 |  | 11 | 11 |  | 11 |  | 11 | 11 | 11
|  |  |  | Raw LAR (MVA) |  | 1.1 | 0.9 | 0.8 |  | 1 |  | 1.3
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 6 | 6 | 6 |  | 6 |  | 6 | 6 |  | 6 |  | 6 | 6 | 6
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 30 | 30 | 30 |  | 30 |  | 30 | 30 |  | 30 |  | 30 | 30 | 30
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 15 | 15 | 15 |  | 15 |  | 15 | 15 |  | 15 |  | 15 | 15 | 15
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## DEGI
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | DEGI - Degilbo (66/11kV) | [8 empty] | Supply |  | ISIS - Isis BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 2x66/11kV 2MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 2.8 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.3% W -1.1%2025 S -1.2% W -1.0%2026 S -0.7% W -0.6%2027 S -0.0% W -0.5
|  |  | Latest Peak Compensated Load | [5 empty] | 2.6 MVA on 13/02/2023 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 5.1 | 5.1 | 5.1 |  | 5.1 |  | 5.1 | 5.9 |  | 5.9 |  | 5.9 | 5.9 | 5.9
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 2.6 | 3.2 | 3.8 |  | 3.8 |  | 3.8 | 2.6 |  | 3 |  | 3.5 | 3.5 | 3.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.983 | 0.983 | 0.983 |  | 0.983 |  | 0.983 | 0.993 |  | 0.993 |  | 0.993 | 0.993 | 0.993
|  |  |  | ECC Rating (MVA) |  | 2.9 | 2.9 | 2.9 |  | 2.9 |  | 2.9 | 3 |  | 3 |  | 3 | 3 | 3
|  |  |  | 50 PoE Load (MVA) |  | 2.5 | 3.1 | 3.7 |  | 3.7 |  | 3.7 | 2.3 |  | 2.8 |  | 3.3 | 3.3 | 3.3
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.1 |  | 0.1 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 7.5 | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 | 7.5
|  |  |  | Raw LAR (MVA) |  |  | 0.2 | 0.8 |  | 0.8 |  | 0.8 |  |  |  |  | 0.3 | 0.3 | 0.3
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 0.8 | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.8 | 0.8
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | LARc (MVA) |  |  |  | 0.2 |  | 0.2 |  | 0.2
|  |  |  | LARc (MW) |  |  |  | 0.2 |  | 0.2 |  | 0.2
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | No |  | No |  | No | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## DIMB
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | DIMB - Dimbulah (66/22kV) | [8 empty] | Supply |  | TURK - Turkinje 66kV BSP
| Description |  |  |  | Region is Far North
Transformer size is 2x66/22kV 10MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.8% W -0.4%2025 S -0.7% W -0.4%2026 S -0.2% W 0.0%,2027 S 0.4% W 0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 4.4 MVA on 15/12/2022 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 24.2 | 24.2 | 24.2 |  | 24.2 |  | 24.2 | 25.9 |  | 25.9 |  | 25.9 | 25.9 | 25.9
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 4.8 | 4.7 | 4.7 |  | 4.7 |  | 4.8 | 3.9 |  | 3.9 |  | 3.9 | 3.9 | 3.9
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.965 | 0.965 | 0.965 |  | 0.965 |  | 0.965 | 0.969 |  | 0.969 |  | 0.969 | 0.969 | 0.969
|  |  |  | ECC Rating (MVA) |  | 13.2 | 13.2 | 13.2 |  | 13.2 |  | 13.2 | 14.4 |  | 14.4 |  | 14.4 | 14.4 | 14.4
|  |  |  | 50 PoE Load (MVA) |  | 4.6 | 4.6 | 4.6 |  | 4.6 |  | 4.7 | 3.8 |  | 3.7 |  | 3.7 | 3.7 | 3.7
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 5.5 | 5.5 | 5.5 |  | 5.5 |  | 5.5 | 5.5 |  | 5.5 |  | 5.5 | 5.5 | 5.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## DISR
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | DISR - Disraeli (66/11kV) | [8 empty] | Supply |  | T193 - Clare South BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/11kV 0.25MVA
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.0% W -0.6%2025 S -0.8% W -0.2%2026 S -0.3% W 0.0%,2027 S 0.3% W 0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 0.1 MVA on 11/11/2022 at 06:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.95 | 0.95 | 0.95 |  | 0.95 |  | 0.95 | 0.95 |  | 0.95 |  | 0.95 | 0.95 | 0.95
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 92.5 | 92.5 | 92.5 |  | 92.5 |  | 92.5 | 92.5 |  | 92.5 |  | 92.5 | 92.5 | 92.5
|  |  |  | Raw LAR (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 0.25 | 0.25 | 0.25 |  | 0.25 |  | 0.25 | 0.25 |  | 0.25 |  | 0.25 | 0.25 | 0.25
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## Duchr2
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | Duchr2 - Duchess Road 11/66kV (11/66kV) | [8 empty] | Supply |  | Duchess Road 66kV accumulator
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1xTR4 11/66kV 6.3MVA
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 0.0%, 2024 S 0.0% W 0.0%, 2025 S 0.0% W 0.0%, 2026 S 0.0% W 0.0%, 2027 S 0.0% W 0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 1.4 MVA on 04/06/2022 at 21:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 7.6 | 7.6 | 7.6 |  | 7.6 |  | 7.6 | 8.8 |  | 8.8 |  | 8.8 | 8.8 | 8.8
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 1.4 | 1.4 | 1.4 |  | 1.4 |  | 1.4 | 1.4 |  | 1.4 |  | 1.4 | 1.4 | 1.4
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.032 | 0.032 | 0.032 |  | 0.032 |  | 0.032 | 0.031 |  | 0.031 |  | 0.031 | 0.031 | 0.031
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 1.4 | 1.4 | 1.4 |  | 1.4 |  | 1.4 | 1.4 |  | 1.4 |  | 1.4 | 1.4 | 1.4
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 50 | 50 | 50 |  | 50 |  | 50 | 50 |  | 50 |  | 50 | 50 | 50
|  |  |  | Raw LAR (MVA) |  | 1.4 | 1.4 | 1.4 |  | 1.4 |  | 1.4 | 1.4 |  | 1.4 |  | 1.4 | 1.4 | 1.4
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 6 | 6 | 6 |  | 6 |  | 6 | 6 |  | 6 |  | 6 | 6 | 6
|  |  |  | Mobile Plant Avail (MVA) |  | 4 | 4 | 4 |  | 4 |  | 4 | 4 |  | 4 |  | 4 | 4 | 4
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## DURO
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | DURO - Duchess Road (132/66kV) | [8 empty] | Supply |  | QMCL - Mica Creek 132kV TCP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 2x132/11kV 40/60MVA ONAN/ONAF;1x66/11kV 5/6.25MVA ONAF(Standby);1x66/11kV 5/6.25MVA ONAN/ONAF(Standby)
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.0% W -0.4%2025 S -0.9% W -0.3%2026 S -0.4% W 0.0%,2027 S 0.4% W 0.2%
|  |  | Latest Peak Compensated Load | [5 empty] | 33.2 MVA on 08/12/2022 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 79.6 | 79.6 | 79.6 |  | 79.6 |  | 79.6 | 84.4 |  | 84.4 |  | 84.4 | 84.4 | 84.4
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 34.3 | 34 | 33.9 |  | 34 |  | 34.4 | 23.4 |  | 23.3 |  | 23.2 | 23.2 | 23.2
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.994 | 0.994 | 0.994 |  | 0.994 |  | 0.994 | 0.997 |  | 0.997 |  | 0.997 | 0.997 | 0.997
|  |  |  | ECC Rating (MVA) |  | 39.8 | 39.8 | 39.8 |  | 39.8 |  | 39.8 | 42.2 |  | 42.2 |  | 42.2 | 42.2 | 42.2
|  |  |  | 50 PoE Load (MVA) |  | 33 | 32.7 | 32.6 |  | 32.7 |  | 33.1 | 21.4 |  | 21.3 |  | 21.3 | 21.3 | 21.3
|  |  |  | 50 PoE Load > 95% (MVA) |  | 1.7 | 1.6 | 1.6 |  | 1.6 |  | 1.7 | 1.1 |  | 1.1 |  | 1.1 | 1.1 | 1.1
|  |  |  | Hours PA > 95% Peak Load |  | 12.5 | 12.5 | 12.5 |  | 12.5 |  | 12.5 | 12.5 |  | 12.5 |  | 12.5 | 12.5 | 12.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 40 | 40 | 40 |  | 40 |  | 40 | 40 |  | 40 |  | 40 | 40 | 40
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 | 5 | 5
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## DYSA
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | DYSA - Dysart (66/22kV) | [8 empty] | Supply |  | T035 - Dysart BSP
| Description |  |  |  | Region is Capricornia
Transformer size is 2x20MVA 66kV Transformer;1x66/22kV 15/20MVA;1x66/22kV15/20MVA
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.0% W -0.6%2025 S -0.9% W -0.4%2026 S -0.4% W -0.1%2027 S 0.4% W 0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 7.5 MVA on 14/02/2023 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 62.3 | 62.3 | 62.3 |  | 62.3 |  | 62.3 | 62.3 |  | 62.3 |  | 62.3 | 62.3 | 62.3
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 7.5 | 7.4 | 7.4 |  | 7.4 |  | 7.5 | 6.1 |  | 6 |  | 6 | 6 | 6
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | ECC Rating (MVA) |  | 46.1 | 46.1 | 46.1 |  | 46.1 |  | 46.1 | 46.1 |  | 46.1 |  | 46.1 | 46.1 | 46.1
|  |  |  | 50 PoE Load (MVA) |  | 7.2 | 7.2 | 7.1 |  | 7.2 |  | 7.3 | 5.7 |  | 5.7 |  | 5.7 | 5.7 | 5.7
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.4 | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Hours PA > 95% Peak Load |  | 4.5 | 4.5 | 4.5 |  | 4.5 |  | 4.5 | 4.5 |  | 4.5 |  | 4.5 | 4.5 | 4.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 20 | 20 | 20 |  | 20 |  | 20 | 20 |  | 20 |  | 20 | 20 | 20
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## EAAY
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | EAAY - East Ayr (66/11kV) | [8 empty] | Supply |  | T193 - Clare South BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 2x66/11kV 15/18/25MVA ONAN/ODAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.7% W -0.1%2025 S -0.6% W 0.0%,2026 S -0.1% W 0.3%,2027 S 0.5% W 0.3%
|  |  | Latest Peak Compensated Load | [5 empty] | 13.3 MVA on 14/12/2022 at 20:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 64.9 | 64.9 | 64.9 |  | 64.9 |  | 64.9 | 69.9 |  | 69.9 |  | 69.9 | 69.9 | 69.9
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 13.9 | 13.8 | 13.8 |  | 13.9 |  | 14 | 9.5 |  | 9.5 |  | 9.5 | 9.6 | 9.6
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 1 | 1 | 1 |  | 1 |  | 1 | 0.984 |  | 0.984 |  | 0.984 | 0.984 | 0.984
|  |  |  | ECC Rating (MVA) |  | 37.1 | 37.1 | 37.1 |  | 37.1 |  | 37.1 | 37.4 |  | 37.4 |  | 37.4 | 37.4 | 37.4
|  |  |  | 50 PoE Load (MVA) |  | 13.5 | 13.4 | 13.4 |  | 13.5 |  | 13.7 | 9.3 |  | 9.3 |  | 9.3 | 9.3 | 9.3
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.7 | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | Hours PA > 95% Peak Load |  | 11.5 | 11.5 | 11.5 |  | 11.5 |  | 11.5 | 11.5 |  | 11.5 |  | 11.5 | 11.5 | 11.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 30 | 30 | 30 |  | 30 |  | 30 | 30 |  | 30 |  | 30 | 30 | 30
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 15 | 15 | 15 |  | 15 |  | 15 | 15 |  | 15 |  | 15 | 15 | 15
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## EABU
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | EABU - East Bundaberg (66/11kV) | [8 empty] | Supply |  | BUND - Bundaberg BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 2x66/11kV 12/16MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 1.8 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.5% W 0.0%,2025 S -0.4% W 0.3%,2026 S 0.1% W 0.5%, 2027 S 0.6% W 0.4%
|  |  | Latest Peak Compensated Load | [5 empty] | 21.9 MVA on 05/07/2022 at 20:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 32.4 | 44 | 44 |  | 44 |  | 44 | 32.4 |  | 44 |  | 44 | 44 | 44
|  |  |  | Contracted non-network (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  |  | 10 PoE Load (MVA) |  | 20.1 | 20 | 20 |  | 20.1 |  | 20.4 | 22.6 |  | 22.6 |  | 22.7 | 22.8 | 22.9
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | ECC Rating (MVA) |  | 16.2 | 23 | 23 |  | 23 |  | 23 | 16.2 |  | 26 |  | 26 | 26 | 26
|  |  |  | 50 PoE Load (MVA) |  | 19.1 | 19 | 19.1 |  | 19.2 |  | 19.4 | 21.7 |  | 21.7 |  | 21.7 | 21.9 | 22
|  |  |  | 50 PoE Load > 95% (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1.1 |  | 1.1 |  | 1.1 | 1.1 | 1.1
|  |  |  | Hours PA > 95% Peak Load |  | 12 | 12 | 12 |  | 12 |  | 12 | 12 |  | 12 |  | 12 | 12 | 12
|  |  |  | Raw LAR (MVA) |  | 2.9 | [6 empty] | 5.5
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 2.1 | 2.1 | 2.1 |  | 2.1 |  | 2.1 | 2.1 |  | 2.1 |  | 2.1 | 2.1 | 2.1
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 24 | 24 | 24 |  | 24 |  | 24 | 24 |  | 24 |  | 24 | 24 | 24
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 12 | 12 | 12 |  | 12 |  | 12 | 12 |  | 12 |  | 12 | 12 | 12
|  |  |  | LARc (MVA) |  | 0.8 | [6 empty] | 3.4
|  |  |  | LARc (MW) |  | 0.8 | [6 empty] | 3.4
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | No | Yes | Yes |  | Yes |  | Yes | No |  | Yes |  | Yes | Yes | Yes
Return to Index

## EATO
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | EATO - East Toowoomba (33/11kV) | [8 empty] | Supply |  | T043 - South Toowoomba BSP
| Description |  |  |  | Region is South West
Transformer size is 2x33/11kV 15/18/25MVA ONAN/OFDAN/OFDAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.1% W -0.5%2025 S -1.1% W -0.3%2026 S -0.5% W 0.0%,2027 S 0.1% W -0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 33.4 MVA on 09/06/2022 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 56.3 | 56.3 | 56.3 |  | 56.3 |  | 56.3 | 66.1 |  | 66.1 |  | 66.1 | 66.1 | 66.1
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 24.7 | 24.5 | 24.3 |  | 24.4 |  | 24.5 | 37.4 |  | 37.2 |  | 37.1 | 37.1 | 37.1
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.989 | 0.989 | 0.989 |  | 0.989 |  | 0.989 | 0.996 |  | 0.996 |  | 0.996 | 0.996 | 0.996
|  |  |  | ECC Rating (MVA) |  | 28.1 | 28.1 | 28.1 |  | 28.1 |  | 28.1 | 34.3 |  | 34.3 |  | 34.3 | 34.3 | 34.3
|  |  |  | 50 PoE Load (MVA) |  | 23.4 | 23.2 | 23.1 |  | 23.1 |  | 23.3 | 34.5 |  | 34.4 |  | 34.3 | 34.3 | 34.2
|  |  |  | 50 PoE Load > 95% (MVA) |  | 1.2 | 1.2 | 1.2 |  | 1.2 |  | 1.2 | 1.7 |  | 1.7 |  | 1.7 | 1.7 | 1.7
|  |  |  | Hours PA > 95% Peak Load |  | 10.5 | 10.5 | 10.5 |  | 10.5 |  | 10.5 | 10.5 |  | 10.5 |  | 10.5 | 10.5 | 10.5
|  |  |  | Raw LAR (MVA) | [8 empty] | 0.2 |  | 0.1
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 5.5 | 5.5 | 5.5 |  | 5.5 |  | 5.5 | 5.5 |  | 5.5 |  | 5.5 | 5.5 | 5.5
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 4.4 | 4.4 | 4.4 |  | 4.4 |  | 4.4 | 4.4 |  | 4.4 |  | 4.4 | 4.4 | 4.4
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 2.2 | 2.2 | 2.2 |  | 2.2 |  | 2.2 | 2.2 |  | 2.2 |  | 2.2 | 2.2 | 2.2
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## EIDS
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | EIDS - Eidsvold (66/11kV) | [8 empty] | Supply |  | ISIS - Isis BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 1x62/11kV 2MVA ON;1x66/11kV 2MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.0% W -0.8%2025 S -0.8% W -0.6%2026 S -0.4% W -0.1%2027 S 0.3% W -0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 1.8 MVA on 13/02/2023 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 4.5 | 4.5 | 4.5 |  | 4.5 |  | 4.5 | 5.3 |  | 5.3 |  | 5.3 | 5.3 | 5.3
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 1.9 | 1.9 | 1.9 |  | 1.9 |  | 1.9 | 1.6 |  | 1.5 |  | 1.5 | 1.5 | 1.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.994 | 0.994 | 0.994 |  | 0.994 |  | 0.994 | 0.996 |  | 0.996 |  | 0.996 | 0.996 | 0.996
|  |  |  | ECC Rating (MVA) |  | 2.7 | 2.7 | 2.7 |  | 2.7 |  | 2.7 | 3 |  | 3 |  | 3 | 3 | 3
|  |  |  | 50 PoE Load (MVA) |  | 1.8 | 1.8 | 1.7 |  | 1.7 |  | 1.8 | 1.5 |  | 1.5 |  | 1.5 | 1.5 | 1.5
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 5.5 | 5.5 | 5.5 |  | 5.5 |  | 5.5 | 5.5 |  | 5.5 |  | 5.5 | 5.5 | 5.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## ELRO
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | ELRO - Ellwoods Road (66/11kV) | [8 empty] | Supply |  | H018 - Tarong BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 2x66/11kV 4.1MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.6% W -0.6%2025 S -0.9% W -0.1%2026 S -0.4% W 0.1%,2027 S 0.2% W 0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 3 MVA on 28/02/2023 at 16:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 10 | 10 | 10 |  | 10 |  | 10 | 11 |  | 11 |  | 11 | 11 | 11
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 3.5 | 3.9 | 3.9 |  | 3.9 |  | 4 | 3.4 |  | 3.9 |  | 3.9 | 3.9 | 3.9
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.949 | 0.949 | 0.949 |  | 0.949 |  | 0.949 | 0.935 |  | 0.935 |  | 0.935 | 0.935 | 0.935
|  |  |  | ECC Rating (MVA) |  | 5.8 | 5.8 | 5.8 |  | 5.8 |  | 5.8 | 6.1 |  | 6.1 |  | 6.1 | 6.1 | 6.1
|  |  |  | 50 PoE Load (MVA) |  | 3.4 | 3.8 | 3.8 |  | 3.8 |  | 3.9 | 3.3 |  | 3.8 |  | 3.8 | 3.8 | 3.8
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 9.5 | 9.5 | 9.5 |  | 9.5 |  | 9.5 | 9.5 |  | 9.5 |  | 9.5 | 9.5 | 9.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 4.1 | 4.1 | 4.1 |  | 4.1 |  | 4.1 | 4.1 |  | 4.1 |  | 4.1 | 4.1 | 4.1
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 8.2 | 8.2 | 8.2 |  | 8.2 |  | 8.2 | 8.2 |  | 8.2 |  | 8.2 | 8.2 | 8.2
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 4.1 | 4.1 | 4.1 |  | 4.1 |  | 4.1 | 4.1 |  | 4.1 |  | 4.1 | 4.1 | 4.1
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## EMER
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | EMER - Emerald (66/22kV) | [8 empty] | Supply |  | H015 - Lilyvale BSP
| Description |  |  |  | Region is Capricornia
Transformer size is 2x66/22kV 15/20MVA ONAN/ONAF;1x66/22kV 16/20MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.8% W -0.3%2025 S -0.8% W -0.3%2026 S -0.3% W 0.1%,2027 S 0.4% W 0.2%
|  |  | Latest Peak Compensated Load | [5 empty] | 34.1 MVA on 13/02/2023 at 17:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 69.6 | 69.6 | 69.6 |  | 69.6 |  | 69.6 | 81.1 |  | 81.1 |  | 81.1 | 81.1 | 81.1
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 39.8 | 39.5 | 40.6 |  | 40.7 |  | 41.2 | 28.3 |  | 28.2 |  | 28.8 | 28.8 | 28.9
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 1 | 1 | 1 |  | 1 |  | 1 | 0.996 |  | 0.996 |  | 0.996 | 0.996 | 0.996
|  |  |  | ECC Rating (MVA) |  | 52.9 | 52.9 | 52.9 |  | 52.9 |  | 52.9 | 58.4 |  | 58.4 |  | 58.4 | 58.4 | 58.4
|  |  |  | 50 PoE Load (MVA) |  | 38 | 37.7 | 38.5 |  | 38.7 |  | 39 | 26.9 |  | 26.9 |  | 27.5 | 27.5 | 27.5
|  |  |  | 50 PoE Load > 95% (MVA) |  | 1.9 | 1.9 | 1.9 |  | 1.9 |  | 2 | 1.3 |  | 1.3 |  | 1.4 | 1.4 | 1.4
|  |  |  | Hours PA > 95% Peak Load |  | 7 | 7 | 7 |  | 7 |  | 7 | 7 |  | 7 |  | 7 | 7 | 7
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 29 | 29 | 29 |  | 29 |  | 29 | 29 |  | 29 |  | 29 | 29 | 29
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 14.5 | 14.5 | 14.5 |  | 14.5 |  | 14.5 | 14.5 |  | 14.5 |  | 14.5 | 14.5 | 14.5
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## ETON
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | ETON - Eton (33/11kV) | [8 empty] | Supply |  | T065 - Alligator Creek BSP
| Description |  |  |  | Region is Mackay
Transformer size is 2x33/11kV 7.5/5MVA ONAF/ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.8% W -0.4%2025 S -0.6% W -0.3%2026 S -0.1% W 0.1%,2027 S 0.7% W 0.6%
|  |  | Latest Peak Compensated Load | [5 empty] | 5.4 MVA on 05/03/2023 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 14.1 | 14.1 | 14.1 |  | 14.1 |  | 14.1 | 15 |  | 15 |  | 15 | 15 | 15
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 5.7 | 5.6 | 5.6 |  | 5.7 |  | 5.7 | 2.9 |  | 2.9 |  | 2.9 | 2.9 | 2.9
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.938 | 0.938 | 0.938 |  | 0.938 |  | 0.938 | 0.972 |  | 0.972 |  | 0.972 | 0.972 | 0.972
|  |  |  | ECC Rating (MVA) |  | 7.5 | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 | 7.5
|  |  |  | 50 PoE Load (MVA) |  | 5.5 | 5.4 | 5.4 |  | 5.5 |  | 5.6 | 2.7 |  | 2.7 |  | 2.7 | 2.7 | 2.7
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 8 | 8 | 8 |  | 8 |  | 8 | 8 |  | 8 |  | 8 | 8 | 8
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 1.5 | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.5 | 1.5
|  |  |  | Mobile Plant Avail (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 13.6 | 13.6 | 13.6 |  | 13.6 |  | 13.6 | 13.6 |  | 13.6 |  | 13.6 | 13.6 | 13.6
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 6.8 | 6.8 | 6.8 |  | 6.8 |  | 6.8 | 6.8 |  | 6.8 |  | 6.8 | 6.8 | 6.8
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## EUDA
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | EUDA - Eungella Dam (66/11kV) | [8 empty] | Supply |  | PIVA - Pioneer Valley BSP
| Description |  |  |  | Region is Mackay
Transformer size is 1x66/11kV 1MVA ONAN;1x66/11kV 5MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 0.0%, 2024 S 0.0% W 0.0%, 2025 S 0.0% W 0.0%, 2026 S 0.0% W 0.0%, 2027 S 0.0% W 0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 0.9 MVA on 01/01/2022 at 17:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6 | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.848 | 0.848 | 0.848 |  | 0.848 |  | 0.848 | 0.848 |  | 0.848 |  | 0.848 | 0.848 | 0.848
|  |  |  | ECC Rating (MVA) |  | 1.1 | 1.1 | 1.1 |  | 1.1 |  | 1.1 | 1.2 |  | 1.2 |  | 1.2 | 1.2 | 1.2
|  |  |  | 50 PoE Load (MVA) |  | 0.9 | 0.9 | 0.9 |  | 0.9 |  | 0.9 | 0.9 |  | 0.9 |  | 0.9 | 0.9 | 0.9
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 6989 | 6989 | 6989 |  | 6989 |  | 6989 | 6989 |  | 6989 |  | 6989 | 6989 | 6989
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 | 5 | 5
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## EVEL
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | EVEL - Evelyn (66/22kV) | [8 empty] | Supply |  | TURK - Turkinje 66kV BSP
| Description |  |  |  | Region is Far North
Transformer size is 1x66/22kV 6.3 MVA
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.1% W -1.4%2025 S -1.1% W -1.3%2026 S -0.6% W -0.8%2027 S 0.1% W -0.5%
|  |  | Latest Peak Compensated Load | [5 empty] | 1.4 MVA on 14/06/2022 at 17:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 9.4 | 9.4 | 9.4 |  | 9.4 |  | 9.4 | 9.4 |  | 9.4 |  | 9.4 | 9.4 | 9.4
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 1.5 | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.6 |  | 1.5 |  | 1.5 | 1.5 | 1.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.98 | 0.98 | 0.98 |  | 0.98 |  | 0.98 | 0.997 |  | 0.997 |  | 0.997 | 0.997 | 0.997
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 1.4 | 1.4 | 1.4 |  | 1.4 |  | 1.4 | 1.5 |  | 1.5 |  | 1.4 | 1.4 | 1.4
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 90.5 | 90.5 | 90.5 |  | 90.5 |  | 90.5 | 90.5 |  | 90.5 |  | 90.5 | 90.5 | 90.5
|  |  |  | Raw LAR (MVA) |  | 1.4 | 1.4 | 1.4 |  | 1.4 |  | 1.4 | 1.5 |  | 1.5 |  | 1.4 | 1.4 | 1.4
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 2.5 | 2.5 | 2.5 |  | 2.5 |  | 2.5 | 2.5 |  | 2.5 |  | 2.5 | 2.5 | 2.5
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 1.3 | 1.3 | 1.3 |  | 1.3 |  | 1.3 | 1.3 |  | 1.3 |  | 1.3 | 1.3 | 1.3
|  |  |  | Capacity for Embedded Generation (MVA) |  | 6.3 | 6.3 | 6.3 |  | 6.3 |  | 6.3 | 6.3 |  | 6.3 |  | 6.3 | 6.3 | 6.3
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## FARL
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | FARL - Farleigh (33/11kV) | [8 empty] | Supply |  | MACK - Mackay BSP
| Description |  |  |  | Region is Mackay
Transformer size is 2x33/11kV 5.5MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 14.4 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.6% W -0.3%2025 S -0.4% W 0.0%,2026 S 0.1% W 0.3%, 2027 S 0.7% W 0.3%
|  |  | Latest Peak Compensated Load | [5 empty] | 4.7 MVA on 21/11/2022 at 16:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 11 | 11 | 11 |  | 11 |  | 11 | 11 |  | 11 |  | 11 | 11 | 11
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 4.7 | 4.6 | 4.6 |  | 4.7 |  | 4.7 | 4.1 |  | 4.1 |  | 4.1 | 4.1 | 4.2
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.991 | 0.991 | 0.991 |  | 0.991 |  | 0.991 | 0.992 |  | 0.992 |  | 0.992 | 0.992 | 0.992
|  |  |  | ECC Rating (MVA) |  | 6 | 6 | 6 |  | 6 |  | 6 | 6 |  | 6 |  | 6 | 6 | 6
|  |  |  | 50 PoE Load (MVA) |  | 4.5 | 4.5 | 4.5 |  | 4.5 |  | 4.6 | 3.8 |  | 3.8 |  | 3.8 | 3.8 | 3.8
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 6.5 | 6.5 | 6.5 |  | 6.5 |  | 6.5 | 6.5 |  | 6.5 |  | 6.5 | 6.5 | 6.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 | 2 | 2
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 | 5 | 5
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## FARN
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | FARN - Farnsfield (66/11kV) | [8 empty] | Supply |  | ISIS - Isis BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 2x66/11kV 10/12.5MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.1% W -0.5%2025 S -0.9% W -0.4%2026 S -0.5% W -0.1%2027 S 0.2% W -0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 7.8 MVA on 13/02/2023 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 28.9 | 28.9 | 28.9 |  | 28.9 |  | 28.9 | 37.4 |  | 37.4 |  | 37.4 | 37.4 | 37.4
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 8.1 | 8.1 | 8 |  | 8.1 |  | 8.1 | 4.3 |  | 4.3 |  | 4.2 | 4.2 | 4.2
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.87 | 0.87 | 0.87 |  | 0.87 |  | 0.87 | 0.837 |  | 0.837 |  | 0.837 | 0.837 | 0.837
|  |  |  | ECC Rating (MVA) |  | 15.9 | 15.9 | 15.9 |  | 15.9 |  | 15.9 | 18.7 |  | 18.7 |  | 18.7 | 18.7 | 18.7
|  |  |  | 50 PoE Load (MVA) |  | 7.7 | 7.6 | 7.6 |  | 7.6 |  | 7.7 | 3.9 |  | 3.9 |  | 3.9 | 3.9 | 3.8
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.4 | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 8 | 8 | 8 |  | 8 |  | 8 | 8 |  | 8 |  | 8 | 8 | 8
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 20 | 20 | 20 |  | 20 |  | 20 | 20 |  | 20 |  | 20 | 20 | 20
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## FREN
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | FREN - Frenchville (66/11kV) | [8 empty] | Supply |  | RMES - Rockhampton Mesh
| Description |  |  |  | Region is Capricornia
Transformer size is 2x66/11kV 15/20MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.3% W -0.1%2025 S -1.2% W 0.3%,2026 S -0.8% W 0.5%,2027 S 0.0% W 0.8%
|  |  | Latest Peak Compensated Load | [5 empty] | 19.3 MVA on 13/02/2023 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 48 | 48 | 48 |  | 48 |  | 48 | 48 |  | 48 |  | 48 | 48 | 48
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 19.4 | 19.2 | 19 |  | 19 |  | 19.1 | 13 |  | 13 |  | 13 | 13.1 | 13.2
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.99 | 0.99 | 0.99 |  | 0.99 |  | 0.99 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | ECC Rating (MVA) |  | 24 | 24 | 24 |  | 24 |  | 24 | 24 |  | 24 |  | 24 | 24 | 24
|  |  |  | 50 PoE Load (MVA) |  | 18.7 | 18.4 | 18.3 |  | 18.3 |  | 18.4 | 12.5 |  | 12.5 |  | 12.5 | 12.6 | 12.7
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.9 | 0.9 | 0.9 |  | 0.9 |  | 0.9 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  |  | Hours PA > 95% Peak Load |  | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 | 2 | 2
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 30 | 30 | 30 |  | 30 |  | 30 | 30 |  | 30 |  | 30 | 30 | 30
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 15 | 15 | 15 |  | 15 |  | 15 | 15 |  | 15 |  | 15 | 15 | 15
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## GARB
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | GARB - Garbutt (66/11kV) | [8 empty] | Supply |  | TMES - Townsville Mesh
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/11kV 21/26.25/35MVA ONAN/ODAN/ODAF;1x66/11kV 21/26.25/35MVA ONAN/ONAF/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.6% W -1.4%2025 S -2.2% W -2.1%2026 S -1.7% W -1.4%2027 S -0.8% W 0.6%
|  |  | Latest Peak Compensated Load | [5 empty] | 26 MVA on 21/11/2022 at 16:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 53.8 | 53.8 | 53.8 |  | 53.8 |  | 53.8 | 54 |  | 54 |  | 54 | 54 | 54
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 27.6 | 27 | 26.5 |  | 26.3 |  | 26.6 | 20.3 |  | 20 |  | 19.6 | 19.3 | 19.4
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.966 | 0.966 | 0.966 |  | 0.966 |  | 0.966 | 0.958 |  | 0.958 |  | 0.958 | 0.958 | 0.958
|  |  |  | ECC Rating (MVA) |  | 29.8 | 29.8 | 29.8 |  | 29.8 |  | 29.8 | 30.8 |  | 30.8 |  | 30.8 | 30.8 | 30.8
|  |  |  | 50 PoE Load (MVA) |  | 26.3 | 25.7 | 25.3 |  | 25.1 |  | 25.4 | 19.5 |  | 19.2 |  | 18.8 | 18.6 | 18.7
|  |  |  | 50 PoE Load > 95% (MVA) |  | 1.3 | 1.3 | 1.3 |  | 1.3 |  | 1.3 | 1 |  | 1 |  | 0.9 | 0.9 | 0.9
|  |  |  | Hours PA > 95% Peak Load |  | 15 | 15 | 15 |  | 15 |  | 15 | 15 |  | 15 |  | 15 | 15 | 15
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 11.8 | 11.8 | 11.8 |  | 11.8 |  | 11.8 | 11.8 |  | 11.8 |  | 11.8 | 11.8 | 11.8
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 6 | 6 | 6 |  | 6 |  | 6 | 6 |  | 6 |  | 6 | 6 | 6
|  |  |  | Capacity for Embedded Generation (MVA) |  | 42 | 42 | 42 |  | 42 |  | 42 | 42 |  | 42 |  | 42 | 42 | 42
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 21 | 21 | 21 |  | 21 |  | 21 | 21 |  | 21 |  | 21 | 21 | 21
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## GAYN
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | GAYN - Gayndah (66/11kV) | [8 empty] | Supply |  | ISIS - Isis BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 2x66/11kV 7.5/10MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.0% W -0.6%2025 S -1.0% W -0.5%2026 S -0.5% W -0.2%2027 S 0.2% W -0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 5.9 MVA on 13/02/2023 at 17:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 24.6 | 24.6 | 24.6 |  | 24.6 |  | 24.6 | 27.1 |  | 27.1 |  | 27.1 | 27.1 | 27.1
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 6.3 | 6.3 | 6.3 |  | 6.3 |  | 6.3 | 4.9 |  | 4.9 |  | 4.8 | 4.8 | 4.8
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.954 | 0.954 | 0.954 |  | 0.954 |  | 0.954 | 0.849 |  | 0.849 |  | 0.849 | 0.849 | 0.849
|  |  |  | ECC Rating (MVA) |  | 14.3 | 14.3 | 14.3 |  | 14.3 |  | 14.3 | 15 |  | 15 |  | 15 | 15 | 15
|  |  |  | 50 PoE Load (MVA) |  | 6 | 6 | 6 |  | 6 |  | 6 | 4.7 |  | 4.7 |  | 4.7 | 4.6 | 4.6
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 7.5 | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 | 7.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 15 | 15 | 15 |  | 15 |  | 15 | 15 |  | 15 |  | 15 | 15 | 15
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 7.5 | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 | 7.5
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## GEOR
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | GEOR - Georgetown (66/22kV) | [8 empty] | Supply |  | GEOR - Georgetown BSP
| Description |  |  |  | Region is Far North
Transformer size is 2x66/22kV 2MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.1% W -1.1%2025 S -0.9% W -0.6%2026 S -0.4% W -0.3%2027 S 0.2% W -0.2%
|  |  | Latest Peak Compensated Load | [5 empty] | 2.3 MVA on 09/12/2022 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 5.5 | 5.5 | 5.5 |  | 5.5 |  | 5.5 | 6 |  | 6 |  | 6 | 6 | 6
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 2.4 | 2.3 | 2.3 |  | 2.3 |  | 2.4 | 1.6 |  | 1.6 |  | 1.6 | 1.6 | 1.6
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.978 | 0.978 | 0.978 |  | 0.978 |  | 0.978 | 0.944 |  | 0.944 |  | 0.944 | 0.944 | 0.944
|  |  |  | ECC Rating (MVA) |  | 3 | 3 | 3 |  | 3 |  | 3 | 3 |  | 3 |  | 3 | 3 | 3
|  |  |  | 50 PoE Load (MVA) |  | 2.3 | 2.3 | 2.3 |  | 2.3 |  | 2.3 | 1.6 |  | 1.6 |  | 1.6 | 1.5 | 1.5
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 46 | 46 | 46 |  | 46 |  | 46 | 46 |  | 46 |  | 46 | 46 | 46
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 4 | 4 | 4 |  | 4 |  | 4 | 4 |  | 4 |  | 4 | 4 | 4
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 | 2 | 2
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## GEOR1
Bulk Summary Information and Peak Load Forecast
Substation |  |  |  | GEOR - Georgetown BSP (132/66kV) | [8 empty] | Supply |  | QROS - Ross (Kidston and Milchester) TCP
Description |  |  |  | Region is Far North
Transformer size is 2x132/66/6.6kV 8MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 5.3 MVA
|  | Latest Peak Compensated Load | [5 empty] | 8.3 MVA on 08/12/2022 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[5 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  | NCC Rating (MVA) |  | 16.7 | 16.7 | 16.7 |  | 16.7 |  | 16.7 | 18 |  | 18 |  | 18 | 18 | 18
|  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | 10 PoE Load (MVA) |  | 8.7 | 8.6 | 8.6 |  | 8.6 |  | 8.7 | 7.6 |  | 7.6 |  | 7.6 | 7.6 | 7.6
LARn (MVA)
LARn (MW)
|  |  | Power Factor at Peak Load |  | 0.905 | 0.905 | 0.905 |  | 0.905 |  | 0.905 | 0.824 |  | 0.824 |  | 0.824 | 0.824 | 0.824
|  |  | ECC Rating (MVA) |  | 9.6 | 9.6 | 9.6 |  | 9.6 |  | 9.6 | 10 |  | 10 |  | 10 | 10 | 10
|  |  | 50 PoE Load (MVA) |  | 8.5 | 8.5 | 8.5 |  | 8.5 |  | 8.6 | 7.4 |  | 7.3 |  | 7.3 | 7.3 | 7.3
|  |  | 50 PoE Load > 95% (MVA) |  | 0.4 | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  | Hours PA > 95% Peak Load |  | 29.5 | 29.5 | 29.5 |  | 29.5 |  | 29.5 | 29.5 |  | 29.5 |  | 29.5 | 29.5 | 29.5
Raw LAR (MVA)
|  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Capacity for Embedded Generation (MVA) |  | 16 | 16 | 16 |  | 16 |  | 16 | 16 |  | 16 |  | 16 | 16 | 16
|  |  | Firm Capacity for Embedded Generation (MVA) |  | 8 | 8 | 8 |  | 8 |  | 8 | 8 |  | 8 |  | 8 | 8 | 8
LARc (MVA)
LARc (MW)
|  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## GIRU
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | GIRU - Giru (66/11kV) | [8 empty] | Supply |  | T193 - Clare South BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 2x66/11kV 4MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.1% W -0.8%2025 S -1.0% W -0.6%2026 S -0.6% W -0.4%2027 S 0.0% W -0.4%
|  |  | Latest Peak Compensated Load | [5 empty] | 1.9 MVA on 16/11/2022 at 20:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 9.5 | 9.5 | 9.5 |  | 9.5 |  | 9.5 | 10.5 |  | 10.5 |  | 10.5 | 10.5 | 10.5
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 2.4 | 2.4 | 2.3 |  | 2.3 |  | 2.4 | 1.4 |  | 1.3 |  | 1.3 | 1.3 | 1.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.916 | 0.916 | 0.916 |  | 0.916 |  | 0.916 | 0.931 |  | 0.931 |  | 0.931 | 0.931 | 0.931
|  |  |  | ECC Rating (MVA) |  | 5 | 5 | 5 |  | 5 |  | 5 | 5.4 |  | 5.4 |  | 5.4 | 5.4 | 5.4
|  |  |  | 50 PoE Load (MVA) |  | 2.2 | 2.2 | 2.2 |  | 2.2 |  | 2.2 | 1.3 |  | 1.3 |  | 1.3 | 1.3 | 1.3
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 6 | 6 | 6 |  | 6 |  | 6 | 6 |  | 6 |  | 6 | 6 | 6
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6 | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 3.3 | 3.3 | 3.3 |  | 3.3 |  | 3.3 | 3.3 |  | 3.3 |  | 3.3 | 3.3 | 3.3
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## GIVE
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | GIVE - Givelda (66/11kV) | [8 empty] | Supply |  | BUND - Bundaberg BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 1x66/11kV 10MVA ONAN;1x66/11kV 7.5/10MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.0% W -0.7%2025 S -0.7% W -0.3%2026 S -0.3% W -0.0%2027 S 0.3% W -0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 5.4 MVA on 13/01/2023 at 09:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 24.4 | 24.4 | 24.4 |  | 24.4 |  | 24.4 | 29.6 |  | 29.6 |  | 29.6 | 29.6 | 29.6
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 5.7 | 5.6 | 5.6 |  | 5.6 |  | 5.7 | 3 |  | 3 |  | 3 | 3 | 3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.869 | 0.869 | 0.869 |  | 0.869 |  | 0.869 | 0.872 |  | 0.872 |  | 0.872 | 0.872 | 0.872
|  |  |  | ECC Rating (MVA) |  | 14.3 | 14.3 | 14.3 |  | 14.3 |  | 14.3 | 15 |  | 15 |  | 15 | 15 | 15
|  |  |  | 50 PoE Load (MVA) |  | 5.2 | 5.2 | 5.1 |  | 5.2 |  | 5.2 | 2.9 |  | 2.9 |  | 2.9 | 2.9 | 2.9
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 72 | 72 | 72 |  | 72 |  | 72 | 72 |  | 72 |  | 72 | 72 | 72
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 15 | 15 | 15 |  | 15 |  | 15 | 15 |  | 15 |  | 15 | 15 | 15
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 | 5 | 5
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## GLEE
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | GLEE - Glenelg (66/33kV) | [8 empty] | Supply |  | T095 - Millchester BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/33kV 0.63MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -1.5% W 2.4%,2025 S 0.6% W 2.4%, 2026 S 1.0% W 2.7%, 2027 S 1.4% W 2.2%
|  |  | Latest Peak Compensated Load | [5 empty] | 0.5 MVA on 02/01/2023 at 20:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 0.7 | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.7 | 0.7
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.93 | 0.93 | 0.93 |  | 0.925 |  | 0.925 | 0.761 |  | 0.761 |  | 0.761 | 0.761 | 0.761
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 2.5 | 2.5 | 2.5 |  | 2.5 |  | 2.5 | 2.5 |  | 2.5 |  | 2.5 | 2.5 | 2.5
|  |  |  | Raw LAR (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 0.63 | 0.63 | 0.63 |  | 0.63 |  | 0.63 | 0.63 |  | 0.63 |  | 0.63 | 0.63 | 0.63
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## GLEL
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | GLEL - Glenella 11kV (66/11kV) | [8 empty] | Supply |  | PIVA - Pioneer Valley BSP
| Description |  |  |  | Region is Mackay
Transformer size is 2x66/11kV 19/26/32MVA ONAN/ODAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.4% W -0.6%2025 S -0.3% W 0.0%,2026 S 0.2% W 0.3%, 2027 S 0.7% W 0.2%
|  |  | Latest Peak Compensated Load | [5 empty] | 12.4 MVA on 02/02/2023 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 75.2 | 75.2 | 75.2 |  | 75.2 |  | 75.2 | 83.8 |  | 83.8 |  | 83.8 | 83.8 | 83.8
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 15.4 | 15.4 | 15.4 |  | 15.5 |  | 15.7 | 8.7 |  | 9 |  | 9 | 9 | 9.1
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.989 | 0.989 | 0.989 |  | 0.989 |  | 0.989 | 0.999 |  | 0.999 |  | 0.999 | 0.999 | 0.999
|  |  |  | ECC Rating (MVA) |  | 41.9 | 41.9 | 41.9 |  | 41.9 |  | 41.9 | 44.7 |  | 44.7 |  | 44.7 | 44.7 | 44.7
|  |  |  | 50 PoE Load (MVA) |  | 14.3 | 14.3 | 14.3 |  | 14.4 |  | 14.6 | 8.3 |  | 8.6 |  | 8.6 | 8.6 | 8.7
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.7 | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  |  | Hours PA > 95% Peak Load |  | 32 | 32 | 32 |  | 32 |  | 32 | 32 |  | 32 |  | 32 | 32 | 32
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 76 | 76 | 76 |  | 76 |  | 76 | 76 |  | 76 |  | 76 | 76 | 76
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 38 | 38 | 38 |  | 38 |  | 38 | 38 |  | 38 |  | 38 | 38 | 38
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## GLEL33
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | GLEL33 - Glenella 33kV (66/33kV) | [8 empty] | Supply |  | PIVA - Pioneer Valley BSP
| Description |  |  |  | Region is Mackay
Transformer size is 2x66/33/6.6kV 38/50/63MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.7% W -0.4%2025 S -0.3% W -0.3%2026 S 0.2% W 0.0%, 2027 S 1.0% W 0.7%
|  |  | Latest Peak Compensated Load | [5 empty] | 45.8 MVA on 02/02/2023 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 153.9 | 153.9 | 153.9 |  | 153.9 |  | 153.9 | 171.5 |  | 171.5 |  | 171.5 | 171.5 | 171.5
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 48.9 | 48.7 | 48.8 |  | 49.3 |  | 50.1 | 32.4 |  | 32.2 |  | 32.1 | 32.2 | 32.4
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.983 | 0.983 | 0.983 |  | 0.983 |  | 0.983 | 0.996 |  | 0.996 |  | 0.996 | 0.996 | 0.996
|  |  |  | ECC Rating (MVA) |  | 85.8 | 85.8 | 85.8 |  | 85.8 |  | 85.8 | 92.1 |  | 92.1 |  | 92.1 | 92.1 | 92.1
|  |  |  | 50 PoE Load (MVA) |  | 46.5 | 46.3 | 46.4 |  | 46.9 |  | 47.7 | 30.3 |  | 30.2 |  | 30.1 | 30.1 | 30.3
|  |  |  | 50 PoE Load > 95% (MVA) |  | 2.3 | 2.3 | 2.3 |  | 2.3 |  | 2.4 | 1.5 |  | 1.5 |  | 1.5 | 1.5 | 1.5
|  |  |  | Hours PA > 95% Peak Load |  | 6.5 | 6.5 | 6.5 |  | 6.5 |  | 6.5 | 6.5 |  | 6.5 |  | 6.5 | 6.5 | 6.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 6 | 6 | 6 |  | 6 |  | 6 | 6 |  | 6 |  | 6 | 6 | 6
|  |  |  | Mobile Plant Avail (MVA) |  | 4 | 4 | 4 |  | 4 |  | 4 | 4 |  | 4 |  | 4 | 4 | 4
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 64 | 64 | 64 |  | 64 |  | 64 | 64 |  | 64 |  | 64 | 64 | 64
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 32 | 32 | 32 |  | 32 |  | 32 | 32 |  | 32 |  | 32 | 32 | 32
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## GLEN
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | GLEN - Glenden (66/11kV) | [8 empty] | Supply |  | NEWL - Newlands BSP
| Description |  |  |  | Region is Mackay
Transformer size is 2x66/11kV 7.5MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.1% W -0.7%2025 S -1.0% W -0.5%2026 S -0.5% W -0.2%2027 S 0.4% W 0.2%
|  |  | Latest Peak Compensated Load | [5 empty] | 1.6 MVA on 05/02/2023 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 15.6 | 15.6 | 15.6 |  | 15.6 |  | 15.6 | 16.7 |  | 16.7 |  | 16.7 | 16.7 | 16.7
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 1.7 | 1.6 | 1.6 |  | 1.6 |  | 1.7 | 1.3 |  | 1.3 |  | 1.3 | 1.3 | 1.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.997 | 0.999 | 0.999 |  | 0.999 |  | 0.997 | 0.998 |  | 0.998 |  | 0.998 | 0.998 | 0.998
|  |  |  | ECC Rating (MVA) |  | 9.7 | 9.7 | 9.7 |  | 9.7 |  | 9.7 | 10.2 |  | 10.2 |  | 10.2 | 10.2 | 10.2
|  |  |  | 50 PoE Load (MVA) |  | 1.6 | 1.5 | 1.5 |  | 1.5 |  | 1.6 | 1.3 |  | 1.3 |  | 1.2 | 1.2 | 1.2
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 26 | 26 | 26 |  | 26 |  | 26 | 26 |  | 26 |  | 26 | 26 | 26
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 7.5 | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 | 7.5
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 15 | 15 | 15 |  | 15 |  | 15 | 15 |  | 15 |  | 15 | 15 | 15
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 7.5 | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 | 7.5
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## GLFS
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | GLFS - Friend Street (66/11kV) | [8 empty] | Supply |  | T019 - Gladstone South BSP
| Description |  |  |  | Region is Capricornia
Transformer size is 1x66/11kV 16/20MVA ONAN/ONAF;1x66/11kV 24/32MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.1% W -0.4%2025 S -1.4% W -0.4%2026 S -0.8% W -0.1%2027 S -0.1% W 0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 18.8 MVA on 16/03/2023 at 15:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 47.4 | 47.4 | 47.4 |  | 47.4 |  | 47.4 | 53.3 |  | 53.3 |  | 53.3 | 53.3 | 53.3
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 18.2 | 18 | 17.8 |  | 17.8 |  | 18 | 16 |  | 16 |  | 15.9 | 15.9 | 15.9
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.999 | 1 | 1 |  | 1 |  | 0.999 | 0.956 |  | 0.956 |  | 0.956 | 0.956 | 0.956
|  |  |  | ECC Rating (MVA) |  | 27.2 | 27.2 | 27.2 |  | 27.2 |  | 27.2 | 29.8 |  | 29.8 |  | 29.8 | 29.8 | 29.8
|  |  |  | 50 PoE Load (MVA) |  | 17.3 | 17 | 16.9 |  | 16.9 |  | 17.1 | 14.3 |  | 14.3 |  | 14.2 | 14.2 | 14.2
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.9 | 0.9 | 0.8 |  | 0.8 |  | 0.9 | 0.7 |  | 0.7 |  | 0.7 | 0.7 | 0.7
|  |  |  | Hours PA > 95% Peak Load |  | 3 | 3 | 3 |  | 3 |  | 3 | 3 |  | 3 |  | 3 | 3 | 3
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 2.2 | 2.2 | 2.2 |  | 2.2 |  | 2.2 | 2.2 |  | 2.2 |  | 2.2 | 2.2 | 2.2
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 40 | 40 | 40 |  | 40 |  | 40 | 40 |  | 40 |  | 40 | 40 | 40
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 16 | 16 | 16 |  | 16 |  | 16 | 16 |  | 16 |  | 16 | 16 | 16
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## GLNO
Bulk Summary Information and Peak Load Forecast
Substation |  |  |  | GLNO - Gladstone North BSP (132/66kV) | [8 empty] | Supply |  | H067 - Calliope River TCP
Description |  |  |  | Region is Capricornia
Transformer size is 2x132/66/11kV 60/80MVA ONAN/ODAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
|  | Latest Peak Compensated Load | [5 empty] | 52 MVA on 08/12/2022 at 16:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[5 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  | NCC Rating (MVA) |  | 184 | 184 | 184 |  | 184 |  | 184 | 208.8 |  | 208.8 |  | 208.8 | 208.8 | 208.8
|  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | 10 PoE Load (MVA) |  | 53 | 52.3 | 51.7 |  | 51.4 |  | 51.4 | 48.6 |  | 48.6 |  | 48.6 | 48.6 | 48.7
LARn (MVA)
LARn (MW)
|  |  | Power Factor at Peak Load |  | 0.997 | 0.997 | 0.997 |  | 0.997 |  | 0.997 | 0.994 |  | 0.994 |  | 0.994 | 0.994 | 0.994
|  |  | ECC Rating (MVA) |  | 105.3 | 105.3 | 105.3 |  | 105.3 |  | 105.3 | 115.9 |  | 115.9 |  | 115.9 | 115.9 | 115.9
|  |  | 50 PoE Load (MVA) |  | 50.4 | 49.7 | 49.2 |  | 48.9 |  | 48.9 | 46.6 |  | 46.6 |  | 46.6 | 46.6 | 46.7
|  |  | 50 PoE Load > 95% (MVA) |  | 2.5 | 2.5 | 2.5 |  | 2.4 |  | 2.4 | 2.3 |  | 2.3 |  | 2.3 | 2.3 | 2.3
|  |  | Hours PA > 95% Peak Load |  | 4.5 | 4.5 | 4.5 |  | 4.5 |  | 4.5 | 4.5 |  | 4.5 |  | 4.5 | 4.5 | 4.5
Raw LAR (MVA)
|  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Capacity for Embedded Generation (MVA) |  | 120 | 120 | 120 |  | 120 |  | 120 | 120 |  | 120 |  | 120 | 120 | 120
|  |  | Firm Capacity for Embedded Generation (MVA) |  | 60 | 60 | 60 |  | 60 |  | 60 | 60 |  | 60 |  | 60 | 60 | 60
LARc (MVA)
LARc (MW)
|  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## GLSO
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | GLSO - Gladstone South (66/11kV) | [8 empty] | Supply |  | T019 - Gladstone South BSP
| Description |  |  |  | Region is Capricornia
Transformer size is 1x66/11kV 15/20 MVA ONAN/ONAF;1x66/11kV 15/20MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.6% W -0.2%2025 S -0.5% W -0.2%2026 S 0.0% W 0.1%, 2027 S 0.7% W 0.3%
|  |  | Latest Peak Compensated Load | [5 empty] | 23 MVA on 13/02/2023 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 54.7 | 54.7 | 54.7 |  | 54.7 |  | 54.7 | 59.8 |  | 59.8 |  | 59.8 | 59.8 | 59.8
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 26.6 | 26.5 | 26.5 |  | 26.7 |  | 27 | 18.8 |  | 18.8 |  | 18.7 | 18.7 | 18.8
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.995 | 0.995 | 0.995 |  | 0.995 |  | 0.995 | 0.999 |  | 0.999 |  | 0.999 | 0.999 | 0.999
|  |  |  | ECC Rating (MVA) |  | 29.6 | 29.6 | 29.6 |  | 29.6 |  | 29.6 | 29.9 |  | 29.9 |  | 29.9 | 29.9 | 29.9
|  |  |  | 50 PoE Load (MVA) |  | 23.9 | 23.8 | 23.8 |  | 24 |  | 24.3 | 18 |  | 18 |  | 17.9 | 18 | 18
|  |  |  | 50 PoE Load > 95% (MVA) |  | 1.2 | 1.2 | 1.2 |  | 1.2 |  | 1.2 | 0.9 |  | 0.9 |  | 0.9 | 0.9 | 0.9
|  |  |  | Hours PA > 95% Peak Load |  | 4 | 4 | 4 |  | 4 |  | 4 | 4 |  | 4 |  | 4 | 4 | 4
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 7.8 | 7.8 | 7.8 |  | 7.8 |  | 7.8 | 7.8 |  | 7.8 |  | 7.8 | 7.8 | 7.8
|  |  |  | Mobile Plant Avail (MVA) |  | 0.8 | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.8 | 0.8
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 30 | 30 | 30 |  | 30 |  | 30 | 30 |  | 30 |  | 30 | 30 | 30
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 15 | 15 | 15 |  | 15 |  | 15 | 15 |  | 15 |  | 15 | 15 | 15
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## GOOB
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | GOOB - Gooburrum (66/11kV) | [8 empty] | Supply |  | BUND - Bundaberg BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 2x66/11kV 5MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.8% W -1.7%2025 S -0.8% W -1.7%2026 S -0.3% W -0.5%2027 S 0.4% W -0.3%
|  |  | Latest Peak Compensated Load | [5 empty] | 3.9 MVA on 04/01/2023 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 14.3 | 14.3 | 14.3 |  | 14.3 |  | 14.3 | 15 |  | 15 |  | 15 | 15 | 15
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 5.4 | 5.4 | 5.3 |  | 5.4 |  | 5.4 | 3 |  | 3 |  | 2.9 | 2.9 | 2.9
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.928 | 0.928 | 0.928 |  | 0.928 |  | 0.928 | 0.97 |  | 0.97 |  | 0.97 | 0.97 | 0.97
|  |  |  | ECC Rating (MVA) |  | 7.5 | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 | 7.5
|  |  |  | 50 PoE Load (MVA) |  | 5.2 | 5.1 | 5.1 |  | 5.1 |  | 5.2 | 2.9 |  | 2.8 |  | 2.8 | 2.8 | 2.8
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 17 | 17 | 17 |  | 17 |  | 17 | 17 |  | 17 |  | 17 | 17 | 17
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 8 | 8 | 8 |  | 8 |  | 8 | 8 |  | 8 |  | 8 | 8 | 8
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## GOOT
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | GOOT - Gootchie (66/11kV) | [8 empty] | Supply |  | MARY - Maryborough BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 1x62/11kV 2MVA ON;1x66/11kV 6.3MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.5% W -1.6%2025 S -1.6% W -0.6%2026 S -1.0% W -0.1%2027 S -0.7% W -0.4
|  |  | Latest Peak Compensated Load | [5 empty] | 4.4 MVA on 13/02/2023 at 17:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 5 | 5 | 5 |  | 5 |  | 5 | 5.8 |  | 5.8 |  | 5.8 | 5.8 | 5.8
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 4.3 | 4.2 | 4.2 |  | 4.2 |  | 4.2 | 3.8 |  | 3.7 |  | 3.7 | 3.7 | 3.7
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.979 | 0.979 | 0.979 |  | 0.979 |  | 0.979 | 0.992 |  | 0.992 |  | 0.992 | 0.992 | 0.992
|  |  |  | ECC Rating (MVA) |  | 2.8 | 2.8 | 2.8 |  | 2.8 |  | 2.8 | 3 |  | 3 |  | 3 | 3 | 3
|  |  |  | 50 PoE Load (MVA) |  | 3.9 | 3.9 | 3.8 |  | 3.8 |  | 3.8 | 3.5 |  | 3.4 |  | 3.4 | 3.4 | 3.4
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 3 | 3 | 3 |  | 3 |  | 3 | 3 |  | 3 |  | 3 | 3 | 3
|  |  |  | Raw LAR (MVA) |  | 1.1 | 1.1 | 1 |  | 1 |  | 1 | 0.5 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 | 2 | 2
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 6.3 | 6.3 | 6.3 |  | 6.3 |  | 6.3 | 6.3 |  | 6.3 |  | 6.3 | 6.3 | 6.3
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## Gracem
Zone Summary Information and Peak Load Forecast
| Substation |  |  | Gracem - Gracemere (66/11kV) | [6 empty] | Supply |  |  | RMES - Rockhampton Mesh
| Description |  |  | Region is Capricornia
Transformer size is 1x20MVA 66kV Transformer
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  | 2023 W 1.8%, 2024 S -2.3% W 0.7%,2025 S -0.1% W 0.8%,2026 S 0.4% W 1.1%, 2027 S 1.2% W 1.4%
No current information, due to be commissioned Winter 2023
Hours PA Exceeding 95% Peak Load
|  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[5 empty] | 2023/24 |  | 2024/25 | 2025/26 | 2026/27 | 2027/28 |  | 2023 | 2024 |  | 2025 | 2026 | 2027
|  |  | NCC Rating (MVA) |  | 22 |  | 22 | 22 | 22 | 22 |  | 22 | 22 |  | 22 | 22 | 22
|  |  | Contracted non-network (MVA) |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0
|  |  | 10 PoE Load (MVA) |  | 7.2 |  | 7.2 | 7.2 | 7.3 | 7.4 |  | 5.8 | 5.9 |  | 5.9 | 6 | 6.1
LARn (MVA)
LARn (MW)
|  |  | Power Factor at Peak Load |  | 0.987 |  | 0.987 | 0.987 | 0.987 | 0.987 |  | 0.998 | 0.998 |  | 0.998 | 0.998 | 0.998
|  |  | ECC Rating (MVA) |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0
|  |  | 50 PoE Load (MVA) |  | 7.2 |  | 7.2 | 7.2 | 7.3 | 7.4 |  | 5.8 | 5.9 |  | 5.9 | 6 | 6.1
|  |  | 50 PoE Load > 95% (MVA) |  | 0.4 |  | 0.4 | 0.4 | 0.4 | 0.4 |  | 0.3 | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  | Hours PA > 95% Peak Load |  | N/A |  | N/A | N/A | N/A | N/A |  | N/A | N/A |  | N/A | N/A | N/A
|  |  | Raw LAR (MVA) |  | 7.2 |  | 7.2 | 7.2 | 7.3 | 7.4 |  | 5.8 | 5.9 |  | 5.9 | 6 | 6.1
|  |  | Auto Trans Avail (MVA) |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0
|  |  | Remote Trans Avail (MVA) |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0
|  |  | Manual Trans Avail (MVA) |  | 10 |  | 10 | 10 | 10 | 10 |  | 10 | 10 |  | 10 | 10 | 10
|  |  | Mobile Plant Avail (MVA) |  | 4 |  | 4 | 4 | 4 | 4 |  | 4 | 4 |  | 4 | 4 | 4
|  |  | Shed(30min) |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0
|  |  | Shed(4Hour) |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0
Capacity for Embedded Generation (MVA)
Firm Capacity for Embedded Generation (MVA)
LARc (MVA)
LARc (MW)
|  |  | Substation Category |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  | Meets Security Standard |  | Yes |  | Yes | Yes | Yes | Yes |  | Yes | Yes |  | Yes | Yes | Yes
Return to Index

## GRCR
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | GRCR - Granite Creek (66/22kV) | [8 empty] | Supply |  | T166 - Granite Creek BSP
| Description |  |  |  | Region is Capricornia
Transformer size is 1xGRCRSS 22/22KV REGULATOR 1 REG 1
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.1% W -1.1%2025 S -0.9% W -0.8%2026 S -0.4% W -0.5%2027 S 0.3% W -0.4%
|  |  | Latest Peak Compensated Load | [5 empty] | 0.3 MVA on 05/07/2022 at 17:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 3.8 | 3.8 | 3.8 |  | 3.8 |  | 3.8 | 3.8 |  | 3.8 |  | 3.8 | 3.8 | 3.8
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.928 | 0.928 | 0.928 |  | 0.928 |  | 0.928 | 0.887 |  | 0.887 |  | 0.887 | 0.887 | 0.887
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 9 | 9 | 9 |  | 9 |  | 9 | 9 |  | 9 |  | 9 | 9 | 9
|  |  |  | Raw LAR (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## GREN
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | GREN - Greenvale (66/11kV) | [8 empty] | Supply |  | T047 - Ingham BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x1.5MVA 66kV Transformer
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.9% W -0.4%2025 S -0.8% W -0.1%2026 S -0.3% W 0.1%,2027 S 0.3% W 0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 0.6 MVA on 19/11/2022 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 1.7 | 1.7 | 1.7 |  | 1.7 |  | 1.7 | 1.7 |  | 1.7 |  | 1.7 | 1.7 | 1.7
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 0.7 | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.5 |  | 0.7 |  | 0.7 | 0.7 | 0.7
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.991 | 0.991 | 0.991 |  | 0.991 |  | 0.991 | 0.993 |  | 0.993 |  | 0.993 | 0.993 | 0.993
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 0.7 | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.5 |  | 0.7 |  | 0.7 | 0.7 | 0.7
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 4 | 4 | 4 |  | 4 |  | 4 | 4 |  | 4 |  | 4 | 4 | 4
|  |  |  | Raw LAR (MVA) |  | 0.7 | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.5 |  | 0.7 |  | 0.7 | 0.7 | 0.7
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## GUML
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | GUML - Gumlu (66/11kV) | [8 empty] | Supply |  | T193 - Clare South BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/11kV 0.5MVA ONAN;1x66/11kV 1MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -5.5% W -3.1%2025 S -4.3% W -2.2%2026 S -4.3% W -1.9%2027 S -3.3% W -1.9
|  |  | Latest Peak Compensated Load | [5 empty] | 1.1 MVA on 02/08/2022 at 17:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 1.7 | 1.7 | 6.9 |  | 6.9 |  | 6.9 | 1.8 |  | 1.8 |  | 6.9 | 6.9 | 6.9
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 1 | 1 | 0.9 |  | 0.9 |  | 0.9 | 1.3 |  | 1.2 |  | 1.2 | 1.2 | 1.2
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.932 | 0.932 | 0.932 |  | 0.932 |  | 0.932 | 0.909 |  | 0.909 |  | 0.909 | 0.909 | 0.909
|  |  |  | ECC Rating (MVA) |  | 0.7 | 0.7 | 0 |  | 0 |  | 0 | 0.8 |  | 0.8 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 1 | 0.9 | 0.9 |  | 0.9 |  | 0.9 | 1.2 |  | 1.1 |  | 1.1 | 1.1 | 1.1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0 | 0 |  | 0 |  | 0 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 177 | 177 | 177 |  | 177 |  | 177 | 177 |  | 177 |  | 177 | 177 | 177
|  |  |  | Raw LAR (MVA) |  | 0.3 | 0.2 | 0.9 |  | 0.9 |  | 0.9 | 0.4 |  | 0.3 |  | 1.1 | 1.1 | 1.1
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | LARc (MVA) | [12 empty] | 0.1 | 0.1 | 0.1
|  |  |  | LARc (MW) | [12 empty] | 0.1 | 0.1 | 0.1
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | No | No | No
Return to Index

## GUTH
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | GUTH - Guthalungra (66/11kV) | [8 empty] | Supply |  | T193 - Clare South BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/11kV 0.5MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.9% W -0.5%2025 S -0.8% W -0.2%2026 S -0.3% W 0.0%,2027 S 0.3% W 0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 0.4 MVA on 31/12/2022 at 20:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 0.4 | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.957 | 0.957 | 0.957 |  | 0.957 |  | 0.957 | 0.96 |  | 0.96 |  | 0.96 | 0.96 | 0.96
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 0.4 | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 9 | 9 | 9 |  | 9 |  | 9 | 9 |  | 9 |  | 9 | 9 | 9
|  |  |  | Raw LAR (MVA) |  | 0.4 | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## HAPU
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | HAPU - Haughton (66/11kV) | [8 empty] | Supply |  | T193 - Clare South BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/11kV 2.5MVA ONAN;1x66/11kV 4MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.3% W 0.7%,2025 S -0.3% W 0.6%,2026 S 0.2% W 1.0%, 2027 S 1.1% W 1.3%
|  |  | Latest Peak Compensated Load | [5 empty] | 4.6 MVA on 16/11/2022 at 15:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 6.2 | 6.2 | 6.2 |  | 6.2 |  | 6.2 | 6.7 |  | 6.7 |  | 6.7 | 6.7 | 6.7
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 4.6 | 4.6 | 4.6 |  | 4.6 |  | 4.7 | 4.8 |  | 4.8 |  | 4.8 | 4.9 | 4.9
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.868 | 0.868 | 0.868 |  | 0.868 |  | 0.868 | 0.869 |  | 0.869 |  | 0.869 | 0.869 | 0.869
|  |  |  | ECC Rating (MVA) |  | 3.7 | 3.7 | 3.7 |  | 3.7 |  | 3.7 | 3.7 |  | 3.7 |  | 3.7 | 3.7 | 3.7
|  |  |  | 50 PoE Load (MVA) |  | 4.4 | 4.4 | 4.4 |  | 4.4 |  | 4.5 | 4.6 |  | 4.6 |  | 4.6 | 4.7 | 4.7
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 181 | 181 | 181 |  | 181 |  | 181 | 181 |  | 181 |  | 181 | 181 | 181
|  |  |  | Raw LAR (MVA) |  | 0.7 | 0.7 | 0.7 |  | 0.7 |  | 0.8 | 0.9 |  | 0.9 |  | 0.9 | 1 | 1
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0.8 | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.8 | 0.8
|  |  |  | Mobile Plant Avail (MVA) |  | 0.7 | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.7 | 0.7
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 2.5 | 2.5 | 2.5 |  | 2.5 |  | 2.5 | 2.5 |  | 2.5 |  | 2.5 | 2.5 | 2.5
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## HELE
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | HELE - Helenvale (66/22kV) | [8 empty] | Supply |  | T159 - Lakeland BSP
| Description |  |  |  | Region is Far North
Transformer size is 1x66/22kV 5MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.3% W -0.9%2025 S -0.9% W -0.3%2026 S -0.5% W -0.0%2027 S 0.2% W -0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 0.8 MVA on 17/01/2023 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 5.7 | 5.7 | 5.7 |  | 5.7 |  | 5.7 | 6.3 |  | 6.3 |  | 6.3 | 6.3 | 6.3
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 0.8 | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.8 | 0.8
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.977 | 0.977 | 0.978 |  | 0.978 |  | 0.977 | 0.946 |  | 0.946 |  | 0.946 | 0.946 | 0.946
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 0.8 | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.8 | 0.8
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 351.5 | 351.5 | 351.5 |  | 351.5 |  | 351.5 | 351.5 |  | 351.5 |  | 351.5 | 351.5 | 351.5
|  |  |  | Raw LAR (MVA) |  | 0.8 | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.8 | 0.8
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 1.2 | 1.2 | 1.2 |  | 1.2 |  | 1.2 | 1.2 |  | 1.2 |  | 1.2 | 1.2 | 1.2
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 | 5 | 5
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## HEPA
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | HEPA - Hermit Park (66/11kV) | [8 empty] | Supply |  | TMES - Townsville Mesh
| Description |  |  |  | Region is Nth Queensland
Transformer size is 2x66/11kV 15/20/25MVA ONAN/ONAF/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.8% W -1.5%2025 S -0.9% W -1.9%2026 S -0.4% W 0.1%,2027 S 0.3% W 0.6%
|  |  | Latest Peak Compensated Load | [5 empty] | 17.7 MVA on 15/12/2022 at 16:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 28.8 | 28.8 | 28.8 |  | 28.8 |  | 28.8 | 40.6 |  | 40.6 |  | 40.6 | 40.6 | 40.6
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 19.9 | 19.7 | 19.6 |  | 19.7 |  | 19.9 | 11.7 |  | 11.6 |  | 11.4 | 11.4 | 11.4
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.986 | 0.986 | 0.986 |  | 0.986 |  | 0.986 | 0.99 |  | 0.99 |  | 0.99 | 0.99 | 0.99
|  |  |  | ECC Rating (MVA) |  | 14.9 | 14.9 | 14.9 |  | 14.9 |  | 14.9 | 20.3 |  | 20.3 |  | 20.3 | 20.3 | 20.3
|  |  |  | 50 PoE Load (MVA) |  | 19.1 | 18.9 | 18.9 |  | 18.9 |  | 19.1 | 11.3 |  | 11.1 |  | 10.9 | 10.9 | 11
|  |  |  | 50 PoE Load > 95% (MVA) |  | 1 | 0.9 | 0.9 |  | 0.9 |  | 1 | 0.6 |  | 0.6 |  | 0.5 | 0.5 | 0.6
|  |  |  | Hours PA > 95% Peak Load |  | 16.5 | 16.5 | 16.5 |  | 16.5 |  | 16.5 | 16.5 |  | 16.5 |  | 16.5 | 16.5 | 16.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 3.5 | 3.5 | 3.5 |  | 3.5 |  | 3.5 | 3.5 |  | 3.5 |  | 3.5 | 3.5 | 3.5
|  |  |  | Mobile Plant Avail (MVA) |  | 1.2 | 1.2 | 1.2 |  | 1.2 |  | 1.2 | 1.2 |  | 1.2 |  | 1.2 | 1.2 | 1.2
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 20 | 20 | 20 |  | 20 |  | 20 | 20 |  | 20 |  | 20 | 20 | 20
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## HIGH
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | HIGH - Highfields (33/11kV) | [8 empty] | Supply |  | T029 - Postmans Ridge BSP
| Description |  |  |  | Region is South West
Transformer size is 1x33/11kV 5MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.0% W -0.6%2025 S -0.9% W -0.4%2026 S -0.4% W -0.1%2027 S 0.3% W 0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 2.4 MVA on 24/08/2022 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 | 5 | 5
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 2.3 | 2.2 | 2.3 |  | 2.3 |  | 2.3 | 2.5 |  | 2.5 |  | 2.5 | 2.5 | 2.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.991 | 0.991 | 0.992 |  | 0.992 |  | 0.991 | 0.997 |  | 0.997 |  | 0.997 | 0.997 | 0.997
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 2.1 | 2.1 | 2.1 |  | 2.1 |  | 2.1 | 2.5 |  | 2.4 |  | 2.4 | 2.4 | 2.4
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 29.5 | 29.5 | 29.5 |  | 29.5 |  | 29.5 | 29.5 |  | 29.5 |  | 29.5 | 29.5 | 29.5
|  |  |  | Raw LAR (MVA) |  | 2.1 | 2.1 | 2.1 |  | 2.1 |  | 2.1 | 2.5 |  | 2.4 |  | 2.4 | 2.4 | 2.4
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 5.5 | 5.5 | 5.5 |  | 5.5 |  | 5.5 | 5.5 |  | 5.5 |  | 5.5 | 5.5 | 5.5
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 | 5 | 5
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## HOHI
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | HOHI - Home Hill (66/11kV) | [8 empty] | Supply |  | T193 - Clare South BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/11kV 15/20/25MVA ONAN/ODAN/ODAF;1x66/11kV 15/20/25MVA ONAN/ONAF/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 15.1 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.0% W -2.2%2025 S -0.9% W -3.0%2026 S -0.5% W -2.5%2027 S 0.1% W -2.2%
|  |  | Latest Peak Compensated Load | [5 empty] | 11.4 MVA on 15/12/2022 at 19:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 59.3 | 59.3 | 59.3 |  | 59.3 |  | 59.3 | 65.1 |  | 65.1 |  | 65.1 | 65.1 | 65.1
|  |  |  | Contracted non-network (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | 10 PoE Load (MVA) |  | 12 | 11.8 | 11.8 |  | 11.8 |  | 11.9 | 8.1 |  | 7.9 |  | 7.6 | 7.4 | 7.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.914 | 0.914 | 0.914 |  | 0.914 |  | 0.914 | 0.935 |  | 0.935 |  | 0.935 | 0.935 | 0.935
|  |  |  | ECC Rating (MVA) |  | 34.6 | 34.6 | 34.6 |  | 34.6 |  | 34.6 | 36.8 |  | 36.8 |  | 36.8 | 36.8 | 36.8
|  |  |  | 50 PoE Load (MVA) |  | 11.5 | 11.4 | 11.4 |  | 11.4 |  | 11.5 | 7.7 |  | 7.5 |  | 7.3 | 7.1 | 7
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  |  | Hours PA > 95% Peak Load |  | 13 | 13 | 13 |  | 13 |  | 13 | 13 |  | 13 |  | 13 | 13 | 13
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 30 | 30 | 30 |  | 30 |  | 30 | 30 |  | 30 |  | 30 | 30 | 30
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 15 | 15 | 15 |  | 15 |  | 15 | 15 |  | 15 |  | 15 | 15 | 15
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## HOWA
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | HOWA - Howard (66/11kV) | [8 empty] | Supply |  | ISIS - Isis BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 1x66/11kV 12.5MVA ONAN;1x62/11kV 7.5MVA ONAN(Standby)
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.0% W -1.6%2025 S -0.8% W -1.5%2026 S -0.3% W -1.2%2027 S 0.4% W -0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 9.7 MVA on 05/07/2022 at 17:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 12.5 | 12.5 | 12.5 |  | 12.5 |  | 12.5 | 12.5 |  | 12.5 |  | 12.5 | 12.5 | 12.5
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 9.3 | 12.2 | 15.1 |  | 15.2 |  | 15.3 | 10 |  | 9.8 |  | 12.3 | 14.9 | 14.9
|  |  |  | LARn (MVA) |  |  |  | 2.6 |  | 2.7 |  | 2.8 | [5 empty] | 2.4 | 2.4
|  |  |  | LARn (MW) |  |  |  | 2.6 |  | 2.7 |  | 2.8 | [5 empty] | 2.4 | 2.4
|  |  |  | Power Factor at Peak Load |  | 0.993 | 0.993 | 0.993 |  | 0.993 |  | 0.993 | 0.996 |  | 0.996 |  | 0.996 | 0.996 | 0.996
|  |  |  | ECC Rating (MVA) |  | 7.5 | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 | 7.5
|  |  |  | 50 PoE Load (MVA) |  | 8.8 | 11.7 | 14.7 |  | 14.7 |  | 14.8 | 9.1 |  | 8.9 |  | 11.4 | 14 | 14
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.4 | 0.6 | 0.7 |  | 0.7 |  | 0.7 | 0.5 |  | 0.4 |  | 0.6 | 0.7 | 0.7
|  |  |  | Hours PA > 95% Peak Load |  | 4 | 4 | 4 |  | 4 |  | 4 | 4 |  | 4 |  | 4 | 4 | 4
|  |  |  | Raw LAR (MVA) |  | 8.8 | 11.7 | 14.7 |  | 14.7 |  | 14.8 | 9.1 |  | 8.9 |  | 11.4 | 14 | 14
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0.9 | 0.9 | 0.9 |  | 0.9 |  | 0.9 | 0.9 |  | 0.9 |  | 0.9 | 0.9 | 0.9
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 8.9 | 8.9 | 8.9 |  | 8.9 |  | 8.9 | 8.9 |  | 8.9 |  | 8.9 | 8.9 | 8.9
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 4 | 4 | 4 |  | 4 |  | 4 | 4 |  | 4 |  | 4 | 4 | 4
|  |  |  | LARc (MVA) |  | 0.4 | 3.3 | 6.3 |  | 6.3 |  | 6.4 | 0.7 |  | 0.5 |  | 3 | 5.6 | 5.6
|  |  |  | LARc (MW) |  | 0.3 | 3.2 | 6.2 |  | 6.2 |  | 6.3 | 0.7 |  | 0.5 |  | 3 | 5.6 | 5.6
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | No | No | No |  | No |  | No | No |  | No |  | No | No | No
Return to Index

## HUGH
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | HUGH - Hughenden (66/33kV) | [8 empty] | Supply |  | T095 - Millchester BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/33/6.6kV 7.5/10MVA ONAF/ONAN;1x66/33/6.6kV7.5/10MVA ONAF/ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 10.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.2% W -1.0%2025 S -1.1% W -0.8%2026 S -0.7% W -0.5%2027 S 0.0% W -0.4%
|  |  | Latest Peak Compensated Load | [5 empty] | 4 MVA on 04/07/2022 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 20 | 20 | 20 |  | 20 |  | 20 | 22.9 |  | 22.9 |  | 22.9 | 22.9 | 22.9
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 4.2 | 4.2 | 4.1 |  | 4.1 |  | 4.2 | 3.5 |  | 3.5 |  | 3.4 | 3.4 | 3.4
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.951 | 0.951 | 0.951 |  | 0.951 |  | 0.951 | 0.866 |  | 0.866 |  | 0.866 | 0.866 | 0.866
|  |  |  | ECC Rating (MVA) |  | 11.4 | 11.4 | 11.4 |  | 11.4 |  | 11.4 | 11.4 |  | 11.4 |  | 11.4 | 11.4 | 11.4
|  |  |  | 50 PoE Load (MVA) |  | 4 | 4 | 4 |  | 4 |  | 4 | 3.3 |  | 3.3 |  | 3.3 | 3.3 | 3.2
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 9 | 9 | 9 |  | 9 |  | 9 | 9 |  | 9 |  | 9 | 9 | 9
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 15 | 15 | 15 |  | 15 |  | 15 | 15 |  | 15 |  | 15 | 15 | 15
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 7.5 | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 | 7.5
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## ILBI
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | ILBI - Ilbilbie (33/11kV) | [8 empty] | Supply |  | T065 - Alligator Creek BSP
| Description |  |  |  | Region is Mackay
Transformer size is 1x33/11kV 1MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.3% W -0.9%2025 S -1.1% W -0.7%2026 S -0.7% W -0.4%2027 S 0.4% W 0.2%
|  |  | Latest Peak Compensated Load | [5 empty] | 0.6 MVA on 16/03/2023 at 19:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 1.2 | 1.2 | 1.2 |  | 1.2 |  | 1.2 | 1.4 |  | 1.4 |  | 1.4 | 1.4 | 1.4
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 0.8 | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.97 | 0.97 | 0.97 |  | 0.97 |  | 0.97 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 0.7 | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 7 | 7 | 7 |  | 7 |  | 7 | 7 |  | 7 |  | 7 | 7 | 7
|  |  |  | Raw LAR (MVA) |  | 0.7 | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0.9 | 0.9 | 0.9 |  | 0.9 |  | 0.9 | 0.9 |  | 0.9 |  | 0.9 | 0.9 | 0.9
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## INGH
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | INGH - Ingham (66/11kV) | [8 empty] | Supply |  | T047 - Ingham BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 2x66/11kV 7.5/10MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.4% W -0.9%2025 S -1.5% W -0.8%2026 S -1.0% W -0.5%2027 S -0.2% W -0.5
|  |  | Latest Peak Compensated Load | [5 empty] | 12 MVA on 21/11/2022 at 16:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 26.7 | 26.7 | 26.7 |  | 26.7 |  | 26.7 | 28.1 |  | 28.1 |  | 28.1 | 28.1 | 28.1
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 12.3 | 12.1 | 12 |  | 12 |  | 12.1 | 8.9 |  | 8.8 |  | 8.8 | 8.7 | 8.7
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.998 | 0.998 | 0.998 |  | 0.998 |  | 0.998 | 0.989 |  | 0.989 |  | 0.989 | 0.989 | 0.989
|  |  |  | ECC Rating (MVA) |  | 14.1 | 14.1 | 14.1 |  | 14.1 |  | 14.1 | 15 |  | 15 |  | 15 | 15 | 15
|  |  |  | 50 PoE Load (MVA) |  | 12 | 11.8 | 11.7 |  | 11.6 |  | 11.7 | 8.5 |  | 8.5 |  | 8.4 | 8.3 | 8.3
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  |  | Hours PA > 95% Peak Load |  | 51.5 | 51.5 | 51.5 |  | 51.5 |  | 51.5 | 51.5 |  | 51.5 |  | 51.5 | 51.5 | 51.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 15 | 15 | 15 |  | 15 |  | 15 | 15 |  | 15 |  | 15 | 15 | 15
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 7.5 | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 | 7.5
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## ISIS
Bulk Summary Information and Peak Load Forecast
Substation |  |  |  | ISIS - Isis BSP (132/66kV) | [8 empty] | Supply |  | QTBC - Teebar Creek TCP
Description |  |  |  | Region is Wide Bay
Transformer size is 1x132/66/11kV 80/100MVA ONAN/ODAN;1x132/66kV 34/42.5/64MVA ONAN/ODAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 91.8 MVA
|  | Latest Peak Compensated Load | [5 empty] | 55 MVA on 13/02/2023 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[5 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  | NCC Rating (MVA) |  | 134 | 134 | 134 |  | 134 |  | 134 | 145 |  | 145 |  | 145 | 145 | 145
|  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 5.7 |  | 5.7 |  | 5.7 | 5.7 | 5.7
|  |  | 10 PoE Load (MVA) |  | 55.6 | 59 | 62.6 |  | 62.7 |  | 63.2 | 43.1 |  | 43.2 |  | 45.5 | 47.5 | 47.5
LARn (MVA)
LARn (MW)
|  |  | Power Factor at Peak Load |  | 0.991 | 0.991 | 0.991 |  | 0.991 |  | 0.991 | 0.999 |  | 0.999 |  | 0.999 | 0.999 | 0.999
|  |  | ECC Rating (MVA) |  | 75.3 | 75.3 | 75.3 |  | 75.3 |  | 75.3 | 77.8 |  | 77.8 |  | 77.8 | 77.8 | 77.8
|  |  | 50 PoE Load (MVA) |  | 53.4 | 56.6 | 60.2 |  | 60.4 |  | 60.8 | 40.5 |  | 40.7 |  | 43 | 45 | 44.9
|  |  | 50 PoE Load > 95% (MVA) |  | 2.7 | 2.8 | 3 |  | 3 |  | 3 | 2 |  | 2 |  | 2.2 | 2.3 | 2.2
|  |  | Hours PA > 95% Peak Load |  | 3.5 | 3.5 | 3.5 |  | 3.5 |  | 3.5 | 3.5 |  | 3.5 |  | 3.5 | 3.5 | 3.5
Raw LAR (MVA)
|  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Capacity for Embedded Generation (MVA) |  | 114 | 114 | 114 |  | 114 |  | 114 | 114 |  | 114 |  | 114 | 114 | 114
|  |  | Firm Capacity for Embedded Generation (MVA) |  | 80 | 80 | 80 |  | 80 |  | 80 | 80 |  | 80 |  | 80 | 80 | 80
LARc (MVA)
LARc (MW)
|  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## JAND
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | JAND - Jandowae (33/11kV) | [8 empty] | Supply |  | CHIN - Chinchilla BSP
| Description |  |  |  | Region is South West
Transformer size is 1x33/11 3.15MVA ONAN;1x33/11kV 0.75MVA ONAN(Standby)
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.7% W -0.6%2025 S -0.5% W -0.4%2026 S 0.0% W 0.1%, 2027 S 0.6% W 0.2%
|  |  | Latest Peak Compensated Load | [5 empty] | 1.1 MVA on 04/07/2022 at 16:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 3.5 | 3.5 | 3.5 |  | 3.5 |  | 3.5 | 3.5 |  | 3.5 |  | 3.5 | 3.5 | 3.5
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 1.1 | 1.1 | 1.1 |  | 1.1 |  | 1.1 | 1.2 |  | 1.2 |  | 1.2 | 1.2 | 1.2
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.99 | 0.99 | 0.99 |  | 0.99 |  | 0.99 | 0.998 |  | 0.998 |  | 0.998 | 0.998 | 0.998
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1.1 | 1.1 |  | 1.1 |  | 1.1 | 1.1 | 1.1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10
|  |  |  | Raw LAR (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1.1 | 1.1 |  | 1.1 |  | 1.1 | 1.1 | 1.1
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0.8 | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.8 | 0.8
|  |  |  | Mobile Plant Avail (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 3.15 | 3.15 | 3.15 |  | 3.15 |  | 3.15 | 3.15 |  | 3.15 |  | 3.15 | 3.15 | 3.15
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0.75 | 0.75 | 0.75 |  | 0.75 |  | 0.75 | 0.75 |  | 0.75 |  | 0.75 | 0.75 | 0.75
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## JARV
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | JARV - Jarvisfield (66/11kV) | [8 empty] | Supply |  | T193 - Clare South BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 2x66/11kV 5MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.2% W -0.2%2025 S -1.1% W -0.4%2026 S -0.5% W -0.0%2027 S 0.2% W 0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 5.1 MVA on 28/02/2023 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 12.1 | 12.1 | 12.1 |  | 12.1 |  | 12.1 | 12.4 |  | 12.4 |  | 12.4 | 12.4 | 12.4
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 6 | 5.9 | 5.9 |  | 5.9 |  | 5.9 | 1.9 |  | 1.9 |  | 1.9 | 1.9 | 1.9
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.868 | 0.868 | 0.868 |  | 0.868 |  | 0.868 | 0.912 |  | 0.912 |  | 0.912 | 0.912 | 0.912
|  |  |  | ECC Rating (MVA) |  | 7 | 7 | 7 |  | 7 |  | 7 | 7.1 |  | 7.1 |  | 7.1 | 7.1 | 7.1
|  |  |  | 50 PoE Load (MVA) |  | 5.6 | 5.5 | 5.5 |  | 5.5 |  | 5.5 | 1.8 |  | 1.8 |  | 1.8 | 1.8 | 1.8
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 8 | 8 | 8 |  | 8 |  | 8 | 8 |  | 8 |  | 8 | 8 | 8
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## JCRK
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | JCRK - Jardine Creek 66/132kV (66/132kV) | [8 empty] | Supply |  | CRET - Cape River East Transmission Accumulator
| Description |  |  |  | Region is Nth Queensland
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 0.0%, 2024 S 0.0% W 0.0%, 2025 S 0.0% W 0.0%, 2026 S 0.0% W 0.0%, 2027 S 0.0% W 0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 13.9 MVA on 17/03/2023 at 20:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
NCC Rating (MVA)
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 15.1 | 15.1 | 15.1 |  | 15.1 |  | 15.1 | 10.7 |  | 10.7 |  | 10.7 | 10.7 | 10.7
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.94 | 0.94 | 0.94 |  | 0.94 |  | 0.94 | 0.968 |  | 0.968 |  | 0.968 | 0.968 | 0.968
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 14.3 | 14.3 | 14.3 |  | 14.3 |  | 14.3 | 10.5 |  | 10.5 |  | 10.5 | 10.5 | 10.5
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.7 | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | Hours PA > 95% Peak Load |  | N/A | N/A | N/A |  | N/A |  | N/A | N/A |  | N/A |  | N/A | N/A | N/A
|  |  |  | Raw LAR (MVA) |  | 14.3 | 14.3 | 14.3 |  | 14.3 |  | 14.3 | 10.5 |  | 10.5 |  | 10.5 | 10.5 | 10.5
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
Capacity for Embedded Generation (MVA)
Firm Capacity for Embedded Generation (MVA)
|  |  |  | LARc (MVA) |  | 14.3 | 14.3 | 14.3 |  | 14.3 |  | 14.3 | 10.5 |  | 10.5 |  | 10.5 | 10.5 | 10.5
|  |  |  | LARc (MW) |  | 13.4 | 13.4 | 13.4 |  | 13.4 |  | 13.4 | 10.2 |  | 10.2 |  | 10.2 | 10.2 | 10.2
|  |  |  | Substation Category |  | Remote | Remote | Remote |  | Remote |  | Remote | Remote |  | Remote |  | Remote | Remote | Remote
|  |  |  | Meets Security Standard |  | No | No | No |  | No |  | No | No |  | No |  | No | No | No
Return to Index

## JUCR
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | JUCR - Julia Creek (66/33kV) | [8 empty] | Supply |  | T095 - Millchester BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/33kV 7.5/6.3MVA ONAF/ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.1% W -0.6%2025 S -1.0% W -0.6%2026 S -0.5% W -0.2%2027 S 0.1% W -0.2%
|  |  | Latest Peak Compensated Load | [5 empty] | 2.6 MVA on 08/12/2022 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 7.4 | 7.4 | 7.4 |  | 7.4 |  | 7.4 | 8.8 |  | 8.8 |  | 8.8 | 8.8 | 8.8
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 2.9 | 2.8 | 4 |  | 4 |  | 4 | 1.8 |  | 1.7 |  | 2.4 | 2.4 | 2.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.981 | 0.981 | 0.981 |  | 0.981 |  | 0.973 | 0.977 |  | 0.977 |  | 0.977 | 0.977 | 0.973
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 2.7 | 2.7 | 3.9 |  | 3.9 |  | 3.9 | 1.7 |  | 1.7 |  | 2.4 | 2.4 | 2.4
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.2 |  | 0.2 |  | 0.2 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 17 | 17 | 17 |  | 17 |  | 17 | 17 |  | 17 |  | 17 | 17 | 17
|  |  |  | Raw LAR (MVA) |  | 2.7 | 2.7 | 3.9 |  | 3.9 |  | 3.9 | 1.7 |  | 1.7 |  | 2.4 | 2.4 | 2.4
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 2.7 | 2.7 | 2.7 |  | 2.7 |  | 2.7 | 2.7 |  | 2.7 |  | 2.7 | 2.7 | 2.7
|  |  |  | Mobile Plant Avail (MVA) |  | 0.4 | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 6.3 | 6.3 | 6.3 |  | 6.3 |  | 6.3 | 6.3 |  | 6.3 |  | 6.3 | 6.3 | 6.3
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | LARc (MVA) |  |  |  | 0.8 |  | 0.8 |  | 0.8
|  |  |  | LARc (MW) |  |  |  | 0.8 |  | 0.8 |  | 0.8
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | No |  | No |  | No | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## JUPO
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | JUPO - Jubilee Pocket (66/11kV) | [8 empty] | Supply |  | PROS - Proserpine BSP
| Description |  |  |  | Region is Mackay
Transformer size is 1x66/11kV 19/26/32MVA ONAN/ODAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.4% W -0.8%2025 S -0.1% W -0.8%2026 S 0.4% W -0.6%,2027 S 1.1% W 0.7%
|  |  | Latest Peak Compensated Load | [5 empty] | 4.7 MVA on 11/01/2023 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 39.6 | 39.6 | 39.6 |  | 39.6 |  | 39.6 | 43.4 |  | 43.4 |  | 43.4 | 43.4 | 43.4
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 4.8 | 4.8 | 4.8 |  | 4.8 |  | 4.9 | 3.4 |  | 3.4 |  | 3.3 | 3.3 | 3.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.996 | 0.996 | 0.996 |  | 0.996 |  | 0.996 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 4.7 | 4.7 | 4.7 |  | 4.7 |  | 4.8 | 3.3 |  | 3.3 |  | 3.2 | 3.2 | 3.2
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 364 | 364 | 364 |  | 364 |  | 364 | 364 |  | 364 |  | 364 | 364 | 364
|  |  |  | Raw LAR (MVA) |  | 4.7 | 4.7 | 4.7 |  | 4.7 |  | 4.8 | 3.3 |  | 3.3 |  | 3.2 | 3.2 | 3.2
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 4.3 | 4.3 | 4.3 |  | 4.3 |  | 4.3 | 4.3 |  | 4.3 |  | 4.3 | 4.3 | 4.3
|  |  |  | Mobile Plant Avail (MVA) |  | 1.5 | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.5 | 1.5
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 19 | 19 | 19 |  | 19 |  | 19 | 19 |  | 19 |  | 19 | 19 | 19
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## KAIM
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | KAIM - Kaimkillenbun (33/11kV) | [8 empty] | Supply |  | T002 - Dalby East BSP
| Description |  |  |  | Region is South West
Transformer size is 1x33/11kV 1MVA ONAN;1x33/11kV 1MVA ONAN(Standby)
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.6% W -0.2%2025 S -0.4% W 0.1%,2026 S 0.1% W 0.3%, 2027 S 0.7% W 0.3%
|  |  | Latest Peak Compensated Load | [5 empty] | 0.9 MVA on 08/07/2022 at 20:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 0.8 | 0.8 | 0.8 |  | 0.8 |  | 0.9 | 1 |  | 1 |  | 1 | 1 | 1
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.983 | 0.983 | 0.983 |  | 0.983 |  | 0.983 | 0.998 |  | 0.998 |  | 0.998 | 0.998 | 0.998
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 0.8 | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.9 |  | 0.9 |  | 0.9 | 0.9 | 0.9
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 8.5 | 8.5 | 8.5 |  | 8.5 |  | 8.5 | 8.5 |  | 8.5 |  | 8.5 | 8.5 | 8.5
|  |  |  | Raw LAR (MVA) |  | 0.8 | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.9 |  | 0.9 |  | 0.9 | 0.9 | 0.9
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 1.1 | 1.1 | 1.1 |  | 1.1 |  | 1.1 | 1.1 |  | 1.1 |  | 1.1 | 1.1 | 1.1
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 | 2 | 2
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## KALA
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | KALA - Kalamia (66/11kV) | [8 empty] | Supply |  | T193 - Clare South BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/11kV 7.5/10MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 11.3 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.1% W -0.7%2025 S -0.8% W -0.2%2026 S -0.4% W 0.0%,2027 S 0.2% W -0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 4.5 MVA on 06/12/2022 at 21:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 7 | 7 | 7 |  | 7 |  | 7 | 8.2 |  | 8.2 |  | 8.2 | 8.2 | 8.2
|  |  |  | Contracted non-network (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  |  | 10 PoE Load (MVA) |  | 4.4 | 4.4 | 4.3 |  | 4.4 |  | 4.4 | 3.5 |  | 3.5 |  | 3.5 | 3.5 | 3.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.885 | 0.885 | 0.885 |  | 0.885 |  | 0.885 | 0.962 |  | 0.962 |  | 0.962 | 0.962 | 0.962
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 4.3 | 4.3 | 4.2 |  | 4.3 |  | 4.3 | 3.6 |  | 3.6 |  | 3.6 | 3.6 | 3.6
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 48.5 | 48.5 | 48.5 |  | 48.5 |  | 48.5 | 48.5 |  | 48.5 |  | 48.5 | 48.5 | 48.5
|  |  |  | Raw LAR (MVA) |  | 4.3 | 4.3 | 4.2 |  | 4.3 |  | 4.3 | 3.6 |  | 3.6 |  | 3.6 | 3.6 | 3.6
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 1.3 | 1.3 | 1.3 |  | 1.3 |  | 1.3 | 1.3 |  | 1.3 |  | 1.3 | 1.3 | 1.3
|  |  |  | Mobile Plant Avail (MVA) |  | 1.8 | 1.8 | 1.8 |  | 1.8 |  | 1.8 | 1.8 |  | 1.8 |  | 1.8 | 1.8 | 1.8
|  |  |  | Shed(30min) |  | 3 | 3 | 3 |  | 3 |  | 3 | 3 |  | 3 |  | 3 | 3 | 3
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 7.5 | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 | 7.5
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## KECE
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | KECE - Kelsey Creek East (66/11kV) | [8 empty] | Supply |  | PROS - Proserpine BSP
| Description |  |  |  | Region is Mackay
Transformer size is 1x66/11kV 12.5/16MVA ONAN/ONAF;1x66/11kV 16/20MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.9% W -0.3%2025 S -1.0% W -0.3%2026 S -0.3% W 0.0%,2027 S 0.5% W 0.3%
|  |  | Latest Peak Compensated Load | [5 empty] | 11.2 MVA on 13/03/2023 at 17:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 36.8 | 36.8 | 36.8 |  | 36.8 |  | 36.8 | 38.4 |  | 38.4 |  | 38.4 | 38.4 | 38.4
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 12.4 | 12.3 | 12.2 |  | 12.3 |  | 12.4 | 8 |  | 8 |  | 7.9 | 7.9 | 8
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.97 | 0.97 | 0.97 |  | 0.97 |  | 0.97 | 0.995 |  | 0.995 |  | 0.995 | 0.995 | 0.995
|  |  |  | ECC Rating (MVA) |  | 18.4 | 18.4 | 18.4 |  | 18.4 |  | 18.4 | 20 |  | 20 |  | 20 | 20 | 20
|  |  |  | 50 PoE Load (MVA) |  | 11.8 | 11.7 | 11.7 |  | 11.7 |  | 11.8 | 7.7 |  | 7.7 |  | 7.7 | 7.7 | 7.7
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  |  | Hours PA > 95% Peak Load |  | 8.5 | 8.5 | 8.5 |  | 8.5 |  | 8.5 | 8.5 |  | 8.5 |  | 8.5 | 8.5 | 8.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Mobile Plant Avail (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 | 2 | 2
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 28.5 | 28.5 | 28.5 |  | 28.5 |  | 28.5 | 28.5 |  | 28.5 |  | 28.5 | 28.5 | 28.5
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 12.5 | 12.5 | 12.5 |  | 12.5 |  | 12.5 | 12.5 |  | 12.5 |  | 12.5 | 12.5 | 12.5
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## KESP
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | KESP - Kearneys Spring (110/11kV) | [8 empty] | Supply |  | QMRG - Middle Ridge (Ergon) TCP
| Description |  |  |  | Region is South West
Transformer size is 2x110/11kV 30/40MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.6% W -0.3%2025 S -0.6% W -0.1%2026 S -0.1% W 0.1%,2027 S 0.6% W 0.2%
|  |  | Latest Peak Compensated Load | [5 empty] | 33.3 MVA on 13/07/2022 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 79.1 | 79.1 | 79.1 |  | 79.1 |  | 79.1 | 89.8 |  | 89.8 |  | 89.8 | 89.8 | 89.8
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 26.8 | 26.6 | 26.6 |  | 26.7 |  | 27.1 | 34.5 |  | 34.3 |  | 34.3 | 34.3 | 34.4
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.995 | 0.995 | 0.995 |  | 0.995 |  | 0.995 | 0.997 |  | 0.997 |  | 0.997 | 0.997 | 0.997
|  |  |  | ECC Rating (MVA) |  | 44.8 | 44.8 | 44.8 |  | 44.8 |  | 44.8 | 49.3 |  | 49.3 |  | 49.3 | 49.3 | 49.3
|  |  |  | 50 PoE Load (MVA) |  | 25.2 | 25 | 25 |  | 25.1 |  | 25.5 | 32.8 |  | 32.7 |  | 32.7 | 32.7 | 32.8
|  |  |  | 50 PoE Load > 95% (MVA) |  | 1.3 | 1.3 | 1.3 |  | 1.3 |  | 1.3 | 1.6 |  | 1.6 |  | 1.6 | 1.6 | 1.6
|  |  |  | Hours PA > 95% Peak Load |  | 4 | 4 | 4 |  | 4 |  | 4 | 4 |  | 4 |  | 4 | 4 | 4
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 60 | 60 | 60 |  | 60 |  | 60 | 60 |  | 60 |  | 60 | 60 | 60
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 30 | 30 | 30 |  | 30 |  | 30 | 30 |  | 30 |  | 30 | 30 | 30
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## KIDS
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | KIDS - Kidston (132/6.6kV) | [8 empty] | Supply |  | QROS - Ross (Kidston and Milchester) TCP
| Description |  |  |  | Region is Far North
Transformer size is 2x132/6.6kV 20MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.1% W -0.6%2025 S -0.8% W -0.2%2026 S -0.4% W 0.0%,2027 S 0.3% W 0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 6.8 MVA on 28/01/2023 at 11:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 42.5 | 42.5 | 42.5 |  | 42.5 |  | 42.5 | 44.9 |  | 44.9 |  | 44.9 | 44.9 | 44.9
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 5.9 | 5.9 | 1.4 |  | 1.4 |  | 1.5 | 5.3 |  | 5.3 |  | 1.5 | 1.5 | 1.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.852 | 0.852 | 0.852 |  | 0.852 |  | 0.852 | 0.854 |  | 0.854 |  | 0.888 | 0.888 | 0.888
|  |  |  | ECC Rating (MVA) |  | 25.4 | 25.4 | 25.4 |  | 25.4 |  | 25.4 | 25.8 |  | 25.8 |  | 25.8 | 25.8 | 25.8
|  |  |  | 50 PoE Load (MVA) |  | 5.4 | 5.3 | 0.9 |  | 0.9 |  | 0.9 | 5.3 |  | 5.2 |  | 1.5 | 1.5 | 1.5
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.3 | 0.3 | 0 |  | 0 |  | 0 | 0.3 |  | 0.3 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 17 | 17 | 17 |  | 17 |  | 17 | 17 |  | 17 |  | 17 | 17 | 17
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 40 | 40 | 40 |  | 40 |  | 40 | 40 |  | 40 |  | 40 | 40 | 40
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 20 | 20 | 20 |  | 20 |  | 20 | 20 |  | 20 |  | 20 | 20 | 20
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## KILK
Bulk Summary Information and Peak Load Forecast
Substation |  |  |  | KILK - Kilkivan BSP (132/66kV) | [8 empty] | Supply |  | QWLN - Woolooga TCP
Description |  |  |  | Region is Wide Bay
Transformer size is 1x132/66/11kV 25/34MVA ONAF;1x132/66kV 15/18MVA ONAF/ONB(Standby)
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
|  | Latest Peak Compensated Load | [5 empty] | 18.5 MVA on 13/02/2023 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[5 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  | NCC Rating (MVA) |  | 34 | 34 | 96 |  | 96 |  | 96 | 34 |  | 34 |  | 102 | 102 | 102
|  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | 10 PoE Load (MVA) |  | 18.8 | 19 | 19 |  | 19 |  | 19.2 | 17.2 |  | 17.5 |  | 17.4 | 17.3 | 17.3
LARn (MVA)
LARn (MW)
|  |  | Power Factor at Peak Load |  | 0.982 | 0.981 | 0.981 |  | 0.981 |  | 0.981 | 0.996 |  | 0.996 |  | 0.996 | 0.996 | 0.996
|  |  | ECC Rating (MVA) |  | 0 | 0 | 68 |  | 68 |  | 68 | 0 |  | 0 |  | 68 | 68 | 68
|  |  | 50 PoE Load (MVA) |  | 17.1 | 17.4 | 17.3 |  | 17.4 |  | 17.6 | 16 |  | 16.3 |  | 16.2 | 16.2 | 16.2
|  |  | 50 PoE Load > 95% (MVA) |  | 0.9 | 0.9 | 0.9 |  | 0.9 |  | 0.9 | 0.8 |  | 0.8 |  | 0.8 | 0.8 | 0.8
|  |  | Hours PA > 95% Peak Load |  | 28 | 28 | 28 |  | 28 |  | 28 | 28 |  | 28 |  | 28 | 28 | 28
|  |  | Raw LAR (MVA) |  | 17.1 | 17.4 | [5 empty] | 16 |  | 16.3
|  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Manual Trans Avail (MVA) |  | 25.7 | 25.7 | 25.7 |  | 25.7 |  | 25.7 | 28.4 |  | 28.4 |  | 28.4 | 28.4 | 28.4
|  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Capacity for Embedded Generation (MVA) |  | 39 | 39 | 39 |  | 39 |  | 39 | 39 |  | 39 |  | 39 | 39 | 39
|  |  | Firm Capacity for Embedded Generation (MVA) |  | 15 | 15 | 15 |  | 15 |  | 15 | 15 |  | 15 |  | 15 | 15 | 15
LARc (MVA)
LARc (MW)
|  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## KILL
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | KILL - Killarney (33/11kV) | [8 empty] | Supply |  | T058 - Warwick BSP
| Description |  |  |  | Region is South West
Transformer size is 2x33/11kV 3MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.8% W -0.5%2025 S -0.7% W -0.2%2026 S -0.2% W 0.0%,2027 S 0.5% W 0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 2.4 MVA on 19/07/2022 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 7.5 | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 8.9 |  | 8.9 |  | 8.9 | 8.9 | 8.9
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2.5 |  | 2.5 |  | 2.5 | 2.5 | 2.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.975 | 0.975 | 0.975 |  | 0.975 |  | 0.975 | 0.98 |  | 0.98 |  | 0.98 | 0.98 | 0.98
|  |  |  | ECC Rating (MVA) |  | 4.3 | 4.3 | 4.3 |  | 4.3 |  | 4.3 | 4.5 |  | 4.5 |  | 4.5 | 4.5 | 4.5
|  |  |  | 50 PoE Load (MVA) |  | 1.9 | 1.9 | 1.9 |  | 1.9 |  | 1.9 | 2.4 |  | 2.4 |  | 2.4 | 2.4 | 2.4
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 12.5 | 12.5 | 12.5 |  | 12.5 |  | 12.5 | 12.5 |  | 12.5 |  | 12.5 | 12.5 | 12.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 6 | 6 | 6 |  | 6 |  | 6 | 6 |  | 6 |  | 6 | 6 | 6
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 3 | 3 | 3 |  | 3 |  | 3 | 3 |  | 3 |  | 3 | 3 | 3
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## KING
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | KING - Kingaroy (66/11kV) | [8 empty] | Supply |  | H018 - Tarong BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 2x66/11kV 20/25/27MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.2% W -0.4%2025 S -1.5% W -0.4%2026 S -0.9% W -0.1%2027 S -0.2% W 0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 24.1 MVA on 13/02/2023 at 16:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 57.4 | 57.4 | 57.4 |  | 57.4 |  | 57.4 | 64.7 |  | 64.7 |  | 64.7 | 64.7 | 64.7
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 23.9 | 23.6 | 23.4 |  | 23.3 |  | 23.5 | 26.8 |  | 26.7 |  | 26.6 | 26.5 | 26.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.971 | 0.971 | 0.971 |  | 0.971 |  | 0.971 | 0.984 |  | 0.984 |  | 0.984 | 0.984 | 0.984
|  |  |  | ECC Rating (MVA) |  | 32.5 | 32.5 | 32.5 |  | 32.5 |  | 32.5 | 36.2 |  | 36.2 |  | 36.2 | 36.2 | 36.2
|  |  |  | 50 PoE Load (MVA) |  | 22.6 | 22.2 | 22 |  | 22 |  | 22.1 | 24.7 |  | 24.6 |  | 24.5 | 24.5 | 24.5
|  |  |  | 50 PoE Load > 95% (MVA) |  | 1.1 | 1.1 | 1.1 |  | 1.1 |  | 1.1 | 1.2 |  | 1.2 |  | 1.2 | 1.2 | 1.2
|  |  |  | Hours PA > 95% Peak Load |  | 3 | 3 | 3 |  | 3 |  | 3 | 3 |  | 3 |  | 3 | 3 | 3
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 40 | 40 | 40 |  | 40 |  | 40 | 40 |  | 40 |  | 40 | 40 | 40
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 20 | 20 | 20 |  | 20 |  | 20 | 20 |  | 20 |  | 20 | 20 | 20
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## KIRK
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | KIRK - Kirknie (66/11kV) | [8 empty] | Supply |  | T193 - Clare South BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/11kV 10MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.7% W -0.9%2025 S -1.6% W -0.6%2026 S -1.3% W -0.4%2027 S -0.8% W -0.5
|  |  | Latest Peak Compensated Load | [5 empty] | 7.4 MVA on 18/11/2022 at 10:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 9.7 | 9.7 | 9.7 |  | 9.7 |  | 9.7 | 10.9 |  | 10.9 |  | 10.9 | 10.9 | 10.9
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 8 | 7.9 | 7.8 |  | 7.7 |  | 7.8 | 5.4 |  | 5.4 |  | 5.3 | 5.3 | 5.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.838 | 0.838 | 0.838 |  | 0.838 |  | 0.838 | 0.788 |  | 0.788 |  | 0.788 | 0.788 | 0.788
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 7.9 | 7.8 | 7.7 |  | 7.6 |  | 7.7 | 5.1 |  | 5.1 |  | 5.1 | 5 | 5
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.4 | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Hours PA > 95% Peak Load |  | 50 | 50 | 50 |  | 50 |  | 50 | 50 |  | 50 |  | 50 | 50 | 50
|  |  |  | Raw LAR (MVA) |  | 7.9 | 7.8 | 7.7 |  | 7.6 |  | 7.7 | 5.1 |  | 5.1 |  | 5.1 | 5 | 5
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 | 2 | 2
|  |  |  | Mobile Plant Avail (MVA) |  | 1.3 | 1.3 | 1.3 |  | 1.3 |  | 1.3 | 1.3 |  | 1.3 |  | 1.3 | 1.3 | 1.3
|  |  |  | Shed(30min) |  | 7 | 7 | 7 |  | 7 |  | 7 | 7 |  | 7 |  | 7 | 7 | 7
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## KITO
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | KITO - Kilkivan Town (66/11kV) | [8 empty] | Supply |  | KILK - Kilkivan BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 2x62/11kV 1MVA ON
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.7% W -0.5%2025 S -0.5% W -0.3%2026 S -0.0% W 0.0%,2027 S 0.6% W 0.2%
|  |  | Latest Peak Compensated Load | [5 empty] | 1.1 MVA on 13/02/2023 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 | 2 | 2
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 1.2 | 1.2 | 1.2 |  | 1.2 |  | 1.2 | 0.8 |  | 0.8 |  | 0.7 | 0.7 | 0.8
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.957 | 0.957 | 0.957 |  | 0.957 |  | 0.957 | 0.984 |  | 0.984 |  | 0.984 | 0.984 | 0.984
|  |  |  | ECC Rating (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | 50 PoE Load (MVA) |  | 1.1 | 1.1 | 1.1 |  | 1.1 |  | 1.1 | 0.7 |  | 0.7 |  | 0.7 | 0.7 | 0.7
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 13 | 13 | 13 |  | 13 |  | 13 | 13 |  | 13 |  | 13 | 13 | 13
|  |  |  | Raw LAR (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 0.8 | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.8 | 0.8
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0.4 | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## KOCR
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | KOCR - Kogan Creek (33/11kV) | [8 empty] | Supply |  | CHIN - Chinchilla BSP
| Description |  |  |  | Region is South West
Transformer size is 1xKOCR TFR1-66/33KV TRANSF 1
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S 1.1% W 3.1%, 2025 S 2.9% W 3.2%, 2026 S 3.4% W 3.3%, 2027 S 3.9% W 3.2%
|  |  | Latest Peak Compensated Load | [5 empty] | 0.3 MVA on 10/07/2022 at 21:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 | 5 | 5
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.2 |  | 0.3 |  | 0.3 | 0.3 | 0.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.929 | 0.929 | 0.969 |  | 0.969 |  | 0.969 | 0.996 |  | 0.996 |  | 0.996 | 0.996 | 0.996
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.2 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 2.5 | 2.5 | 2.5 |  | 2.5 |  | 2.5 | 2.5 |  | 2.5 |  | 2.5 | 2.5 | 2.5
|  |  |  | Raw LAR (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.2 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Mobile Plant Avail (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## KOUM
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | KOUM - Koumala (33/11kV) | [8 empty] | Supply |  | T065 - Alligator Creek BSP
| Description |  |  |  | Region is Mackay
Transformer size is 1x33/11kV 5MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.4% W -0.6%2025 S -0.2% W -0.3%2026 S 0.2% W 0.0%, 2027 S 0.9% W 0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 0.9 MVA on 02/02/2023 at 20:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 7 | 7 | 7 |  | 7 |  | 7 | 7.5 |  | 7.5 |  | 7.5 | 7.5 | 7.5
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 0.8 |  | 0.8 |  | 0.8 | 0.8 | 0.8
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.934 | 0.934 | 0.934 |  | 0.934 |  | 0.934 | 0.941 |  | 0.941 |  | 0.941 | 0.941 | 0.941
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 0.9 | 0.9 | 0.9 |  | 0.9 |  | 0.9 | 0.8 |  | 0.8 |  | 0.8 | 0.8 | 0.8
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 51 | 51 | 51 |  | 51 |  | 51 | 51 |  | 51 |  | 51 | 51 | 51
|  |  |  | Raw LAR (MVA) |  | 0.9 | 0.9 | 0.9 |  | 0.9 |  | 0.9 | 0.8 |  | 0.8 |  | 0.8 | 0.8 | 0.8
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 1.9 | 1.9 | 1.9 |  | 1.9 |  | 1.9 | 1.9 |  | 1.9 |  | 1.9 | 1.9 | 1.9
|  |  |  | Mobile Plant Avail (MVA) |  | 0.4 | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 | 5 | 5
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## LACR
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | LACR - Lakes Creek (66/11kV) | [8 empty] | Supply |  | RMES - Rockhampton Mesh
| Description |  |  |  | Region is Capricornia
Transformer size is 2x66/11kV 16/20MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.0% W -0.6%2025 S -0.7% W -0.2%2026 S -0.3% W 0.1%,2027 S 0.4% W 0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 13.8 MVA on 07/12/2022 at 19:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 45.9 | 45.9 | 45.9 |  | 45.9 |  | 45.9 | 50.9 |  | 50.9 |  | 50.9 | 50.9 | 50.9
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 13.9 | 13.8 | 13.8 |  | 13.8 |  | 14 | 11.8 |  | 11.7 |  | 11.7 | 11.7 | 11.7
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 1 | 1 | 1 |  | 1 |  | 1 | 0.996 |  | 0.996 |  | 0.996 | 0.996 | 0.996
|  |  |  | ECC Rating (MVA) |  | 27 | 27 | 27 |  | 27 |  | 27 | 29.3 |  | 29.3 |  | 29.3 | 29.3 | 29.3
|  |  |  | 50 PoE Load (MVA) |  | 13.3 | 13.2 | 13.2 |  | 13.2 |  | 13.4 | 11.1 |  | 11.1 |  | 11 | 11.1 | 11.1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.7 | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  |  | Hours PA > 95% Peak Load |  | 6.5 | 6.5 | 6.5 |  | 6.5 |  | 6.5 | 6.5 |  | 6.5 |  | 6.5 | 6.5 | 6.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 32 | 32 | 32 |  | 32 |  | 32 | 32 |  | 32 |  | 32 | 32 | 32
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 16 | 16 | 16 |  | 16 |  | 16 | 16 |  | 16 |  | 16 | 16 | 16
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## LAKE
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | LAKE - Lakeland (66/22kV) | [8 empty] | Supply |  | T159 - Lakeland BSP
| Description |  |  |  | Region is Far North
Transformer size is 2x20MVA
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.2% W -0.8%2025 S -1.2% W -0.6%2026 S -0.6% W -0.3%2027 S 0.1% W -0.2%
|  |  | Latest Peak Compensated Load | [5 empty] | 1.5 MVA on 21/11/2022 at 16:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 16 | 16 | 16 |  | 16 |  | 16 | 16 |  | 16 |  | 16 | 16 | 16
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 1.5 | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.6 |  | 1.6 |  | 1.6 | 1.6 | 1.6
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.997 | 0.997 | 0.997 |  | 0.997 |  | 0.997 | 0.993 |  | 0.993 |  | 0.993 | 0.993 | 0.993
|  |  |  | ECC Rating (MVA) |  | 8 | 8 | 8 |  | 8 |  | 8 | 8 |  | 8 |  | 8 | 8 | 8
|  |  |  | 50 PoE Load (MVA) |  | 1.5 | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.5 | 1.5
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 13.5 | 13.5 | 13.5 |  | 13.5 |  | 13.5 | 13.5 |  | 13.5 |  | 13.5 | 13.5 | 13.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 30 | 30 | 30 |  | 30 |  | 30 | 30 |  | 30 |  | 30 | 30 | 30
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 15 | 15 | 15 |  | 15 |  | 15 | 15 |  | 15 |  | 15 | 15 | 15
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## LANN
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | LANN - Lannercost (66/11kV) | [8 empty] | Supply |  | T047 - Ingham BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/11kV 6.3MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.0% W -0.6%2025 S -0.8% W -0.3%2026 S -0.4% W -0.0%2027 S 0.3% W 0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 1.8 MVA on 01/11/2022 at 19:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 8.2 | 8.2 | 8.2 |  | 8.2 |  | 8.2 | 8.7 |  | 8.7 |  | 8.7 | 8.7 | 8.7
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 2.1 | 2.1 | 2.1 |  | 2.1 |  | 2.1 | 1.3 |  | 1.3 |  | 1.3 | 1.3 | 1.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.992 | 0.992 | 0.992 |  | 0.992 |  | 0.992 | 0.997 |  | 0.997 |  | 0.997 | 0.997 | 0.997
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 1.9 | 1.9 | 1.9 |  | 1.9 |  | 1.9 | 1.2 |  | 1.2 |  | 1.2 | 1.2 | 1.2
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 5.5 | 5.5 | 5.5 |  | 5.5 |  | 5.5 | 5.5 |  | 5.5 |  | 5.5 | 5.5 | 5.5
|  |  |  | Raw LAR (MVA) |  | 1.9 | 1.9 | 1.9 |  | 1.9 |  | 1.9 | 1.2 |  | 1.2 |  | 1.2 | 1.2 | 1.2
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 | 2 | 2
|  |  |  | Mobile Plant Avail (MVA) |  | 0.4 | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 6.3 | 6.3 | 6.3 |  | 6.3 |  | 6.3 | 6.3 |  | 6.3 |  | 6.3 | 6.3 | 6.3
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## LAQU
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | LAQU - Laguna Quays (66/11kV) | [8 empty] | Supply |  | PROS - Proserpine BSP
| Description |  |  |  | Region is Mackay
Transformer size is 2x66/11kV 7.5MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -1.6% W 1.3%,2025 S 0.6% W 1.4%, 2026 S 1.1% W 1.7%, 2027 S 1.5% W 1.4%
|  |  | Latest Peak Compensated Load | [5 empty] | 1.6 MVA on 16/11/2022 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 17.6 | 17.6 | 17.6 |  | 17.6 |  | 17.6 | 19 |  | 19 |  | 19 | 19 | 19
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 1.7 | 1.7 | 1.7 |  | 1.8 |  | 1.8 | 1.2 |  | 1.1 |  | 1.2 | 1.2 | 1.2
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.993 | 0.993 | 0.993 |  | 0.993 |  | 0.993 | 0.996 |  | 0.983 |  | 0.996 | 0.996 | 0.996
|  |  |  | ECC Rating (MVA) |  | 9.7 | 9.7 | 9.7 |  | 9.7 |  | 9.7 | 10.3 |  | 10.3 |  | 10.3 | 10.3 | 10.3
|  |  |  | 50 PoE Load (MVA) |  | 1.6 | 1.6 | 1.6 |  | 1.6 |  | 1.7 | 1.1 |  | 1.1 |  | 1.2 | 1.2 | 1.2
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 8 | 8 | 8 |  | 8 |  | 8 | 8 |  | 8 |  | 8 | 8 | 8
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 15 | 15 | 15 |  | 15 |  | 15 | 15 |  | 15 |  | 15 | 15 | 15
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 7.5 | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 | 7.5
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## LARO
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | LARO - Skid D (Landing Road) (66/11kV) | [8 empty] | Supply |  | T130 - Boat Creek BSP
| Description |  |  |  | Region is Capricornia
Transformer size is 1x66/11kV 10MVA Skid Transformer ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.2% W -0.8%2025 S -0.9% W -0.3%2026 S -0.5% W -0.1%2027 S 0.1% W -0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 3.1 MVA on 13/03/2023 at 11:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 11 | 11 | 11 |  | 11 |  | 11 | 11 |  | 11 |  | 11 | 11 | 11
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 4.5 | 4.4 | 6.1 |  | 7.8 |  | 7.8 | 3.8 |  | 3.8 |  | 3.8 | 5.2 | 6.7
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.795 | 0.795 | 0.795 |  | 0.795 |  | 0.795 | 0.793 |  | 0.787 |  | 0.787 | 0.793 | 0.793
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 4.4 | 4.3 | 6 |  | 7.7 |  | 7.8 | 3.8 |  | 3.8 |  | 3.8 | 5.2 | 6.6
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.3 |  | 0.4 |  | 0.4 | 0.2 |  | 0.2 |  | 0.2 | 0.3 | 0.3
|  |  |  | Hours PA > 95% Peak Load |  | 14 | 14 | 14 |  | 14 |  | 14 | 14 |  | 14 |  | 14 | 14 | 14
|  |  |  | Raw LAR (MVA) |  | 4.4 | 4.3 | 6 |  | 7.7 |  | 7.8 | 3.8 |  | 3.8 |  | 3.8 | 5.2 | 6.6
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 2.4 | 2.4 | 2.4 |  | 2.4 |  | 2.4 | 2.4 |  | 2.4 |  | 2.4 | 2.4 | 2.4
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 3.1 | 3.1 | 3.1 |  | 3.1 |  | 3.1 | 3.1 |  | 3.1 |  | 3.1 | 3.1 | 3.1
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | LARc (MVA) |  |  |  | 0.5 |  | 2.2 |  | 2.3 | [6 empty] | 1.1
|  |  |  | LARc (MW) |  |  |  | 0.4 |  | 1.7 |  | 1.8 | [6 empty] | 0.9
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | No |  | No |  | No | Yes |  | Yes |  | Yes | Yes | No
Return to Index

## LITT
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | LITT - Littlemore (66/11kV) | [8 empty] | Supply |  | T019 - Gladstone South BSP
| Description |  |  |  | Region is Capricornia
Transformer size is 1x66/11kV 2MVA ON;1x66/11kV 2MVA ON(Standby)
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -0.6% W 1.0%,2025 S 1.4% W 1.0%, 2026 S 1.8% W 1.3%, 2027 S 3.0% W 1.9%
|  |  | Latest Peak Compensated Load | [5 empty] | 0.4 MVA on 24/06/2022 at 07:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 2.2 | 2.2 | 2.2 |  | 2.2 |  | 2.2 | 2.2 |  | 2.2 |  | 2.2 | 2.2 | 2.2
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.6 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.812 | 0.812 | 0.812 |  | 0.812 |  | 0.812 | 0.862 |  | 0.862 |  | 0.862 | 0.862 | 0.862
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.4 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 4 | 4 | 4 |  | 4 |  | 4 | 4 |  | 4 |  | 4 | 4 | 4
|  |  |  | Raw LAR (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.4 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 | 2 | 2
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## LOCR
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | LOCR - Louisa Creek (33/11kV) | [8 empty] | Supply |  | T176 - Louisa Creek BSP
| Description |  |  |  | Region is Mackay
Transformer size is 1x33/11kV 6.3MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -1.9% W 0.7%,2025 S 0.2% W 0.8%, 2026 S 0.7% W 1.1%, 2027 S 1.4% W 1.2%
|  |  | Latest Peak Compensated Load | [5 empty] | 2.9 MVA on 05/02/2023 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 7.4 | 7.4 | 7.4 |  | 7.4 |  | 7.4 | 7.8 |  | 7.8 |  | 7.8 | 7.8 | 7.8
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 2.9 | 2.9 | 3 |  | 3 |  | 3 | 2.3 |  | 2.4 |  | 2.4 | 2.4 | 2.4
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.998 | 0.998 | 0.998 |  | 0.998 |  | 0.998 | 0.991 |  | 0.991 |  | 0.991 | 0.991 | 0.991
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 2.8 | 2.8 | 2.8 |  | 2.9 |  | 2.9 | 2.2 |  | 2.2 |  | 2.2 | 2.2 | 2.3
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 17 | 17 | 17 |  | 17 |  | 17 | 17 |  | 17 |  | 17 | 17 | 17
|  |  |  | Raw LAR (MVA) |  | 2.8 | 2.8 | 2.8 |  | 2.9 |  | 2.9 | 2.2 |  | 2.2 |  | 2.2 | 2.2 | 2.3
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1.2 |  | 1 |  | 1 | 1 | 1
|  |  |  | Mobile Plant Avail (MVA) |  | 1.6 | 1.6 | 1.6 |  | 1.6 |  | 1.6 | 1.6 |  | 1.6 |  | 1.6 | 1.6 | 1.6
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 6.3 | 6.3 | 6.3 |  | 6.3 |  | 6.3 | 6.3 |  | 6.3 |  | 6.3 | 6.3 | 6.3
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | LARc (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.3 |  | 0.3
|  |  |  | LARc (MW) |  | 0.2 | 0.2 | 0.2 |  | 0.3 |  | 0.3
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | No | No | No |  | No |  | No | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## LONG
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | LONG - Longreach (66/22kV) | [8 empty] | Supply |  | T072 - Barcaldine BSP
| Description |  |  |  | Region is Capricornia
Transformer size is 2x66/22kV 8/10MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.3% W -0.9%2025 S -1.3% W -0.7%2026 S -0.8% W -0.4%2027 S -0.1% W -0.3
|  |  | Latest Peak Compensated Load | [5 empty] | 9 MVA on 07/12/2022 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 24.4 | 24.4 | 24.4 |  | 24.4 |  | 24.4 | 28.6 |  | 28.6 |  | 28.6 | 28.6 | 28.6
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 9.7 | 9.6 | 9.5 |  | 9.5 |  | 9.6 | 8.7 |  | 8.6 |  | 8.6 | 8.5 | 8.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.999 | 0.999 | 0.999 |  | 0.999 |  | 0.999 | 0.995 |  | 0.995 |  | 0.995 | 0.995 | 0.995
|  |  |  | ECC Rating (MVA) |  | 13.9 | 13.9 | 13.9 |  | 13.9 |  | 13.9 | 15 |  | 15 |  | 15 | 15 | 15
|  |  |  | 50 PoE Load (MVA) |  | 9.3 | 9.1 | 9.1 |  | 9.1 |  | 9.1 | 8.2 |  | 8.1 |  | 8.1 | 8 | 8
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  |  | Hours PA > 95% Peak Load |  | 11.5 | 11.5 | 11.5 |  | 11.5 |  | 11.5 | 11.5 |  | 11.5 |  | 11.5 | 11.5 | 11.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 16 | 16 | 16 |  | 16 |  | 16 | 16 |  | 16 |  | 16 | 16 | 16
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 8 | 8 | 8 |  | 8 |  | 8 | 8 |  | 8 |  | 8 | 8 | 8
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## LUCI
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | LUCI - Lucinda (66/11kV) | [8 empty] | Supply |  | T047 - Ingham BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/11kV 5/4MVA ONAF/ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.1% W -0.7%2025 S -0.9% W -0.4%2026 S -0.5% W -0.1%2027 S 0.1% W -0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 2.9 MVA on 06/12/2022 at 20:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 5.9 | 5.9 | 5.9 |  | 5.9 |  | 5.9 | 6 |  | 6 |  | 6 | 6 | 6
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 2.9 | 2.9 | 2.8 |  | 2.8 |  | 2.9 | 3 |  | 3 |  | 3 | 3 | 3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.858 | 0.858 | 0.858 |  | 0.858 |  | 0.858 | 0.909 |  | 0.909 |  | 0.909 | 0.909 | 0.909
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 2.8 | 2.8 | 2.8 |  | 2.8 |  | 2.8 | 2.9 |  | 2.9 |  | 2.9 | 2.9 | 2.9
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 397.5 | 397.5 | 397.5 |  | 397.5 |  | 397.5 | 397.5 |  | 397.5 |  | 397.5 | 397.5 | 397.5
|  |  |  | Raw LAR (MVA) |  | 2.8 | 2.8 | 2.8 |  | 2.8 |  | 2.8 | 2.9 |  | 2.9 |  | 2.9 | 2.9 | 2.9
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 1.1 | 1.1 | 1.1 |  | 1.1 |  | 1.1 | 1.1 |  | 1.1 |  | 1.1 | 1.1 | 1.1
|  |  |  | Mobile Plant Avail (MVA) |  | 0.4 | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  |  | Shed(30min) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 | 2 | 2
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 4 | 4 | 4 |  | 4 |  | 4 | 4 |  | 4 |  | 4 | 4 | 4
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## LYLA
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | LYLA - Lyndley Lane (33/22kV) | [8 empty] | Supply |  | T002 - Dalby East BSP
| Description |  |  |  | Region is South West
Transformer size is 1x33/22kV 0.3MVA ONAN;1x33/22kV 0.75MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.6% W -0.1%2025 S -0.4% W 0.2%,2026 S 0.1% W 0.4%, 2027 S 0.7% W 0.5%
|  |  | Latest Peak Compensated Load | [5 empty] | 0.6 MVA on 27/02/2023 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 1.1 | 1.1 | 1.1 |  | 1.1 |  | 1.1 | 1.1 |  | 1.1 |  | 1.1 | 1.1 | 1.1
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.997 | 0.997 | 0.997 |  | 0.997 |  | 0.997 | 0.987 |  | 0.987 |  | 0.987 | 0.987 | 0.987
|  |  |  | ECC Rating (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | 50 PoE Load (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 16 | 16 | 16 |  | 16 |  | 16 | 16 |  | 16 |  | 16 | 16 | 16
|  |  |  | Raw LAR (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Mobile Plant Avail (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 0.75 | 0.75 | 0.75 |  | 0.75 |  | 0.75 | 0.75 |  | 0.75 |  | 0.75 | 0.75 | 0.75
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MACI
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MACI - Maryborough City (66/11kV) | [8 empty] | Supply |  | MARY - Maryborough BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 2x66/11kV 14/19MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 3.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.0% W -1.2%2025 S -0.9% W -1.3%2026 S -0.4% W -0.6%2027 S 0.3% W 0.2%
|  |  | Latest Peak Compensated Load | [5 empty] | 13.1 MVA on 01/02/2023 at 14:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 39.6 | 39.6 | 39.6 |  | 39.6 |  | 39.6 | 42.7 |  | 42.7 |  | 42.7 | 42.7 | 42.7
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 13.3 | 14.4 | 15.7 |  | 15.7 |  | 15.9 | 9.9 |  | 10.7 |  | 11.8 | 11.7 | 11.7
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.999 | 1 | 1 |  | 1 |  | 1 | 0.971 |  | 1 |  | 0.999 | 0.999 | 0.999
|  |  |  | ECC Rating (MVA) |  | 22.7 | 22.7 | 22.7 |  | 22.7 |  | 22.7 | 24.4 |  | 24.4 |  | 24.4 | 24.4 | 24.4
|  |  |  | 50 PoE Load (MVA) |  | 12.3 | 13.5 | 14.7 |  | 14.7 |  | 14.9 | 9.5 |  | 10.3 |  | 11.4 | 11.3 | 11.3
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.6 | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.5 |  | 0.5 |  | 0.6 | 0.6 | 0.6
|  |  |  | Hours PA > 95% Peak Load |  | 3.5 | 3.5 | 3.5 |  | 3.5 |  | 3.5 | 3.5 |  | 3.5 |  | 3.5 | 3.5 | 3.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 4 | 4 | 4 |  | 4 |  | 4 | 4 |  | 4 |  | 4 | 4 | 4
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 12.6 | 12.6 | 12.6 |  | 12.6 |  | 12.6 | 12.6 |  | 12.6 |  | 12.6 | 12.6 | 12.6
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 6.3 | 6.3 | 6.3 |  | 6.3 |  | 6.3 | 6.3 |  | 6.3 |  | 6.3 | 6.3 | 6.3
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MACN
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MACN - Macknade (66/11kV) | [8 empty] | Supply |  | T047 - Ingham BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x6.3MVA 66kV Transformer;1x66/11kV 8/10MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 8.8 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.1% W -0.7%2025 S -0.9% W -0.4%2026 S -0.5% W -0.1%2027 S 0.2% W -0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 3.8 MVA on 06/06/2022 at 20:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 13.9 | 13.9 | 13.9 |  | 13.9 |  | 13.9 | 13.9 |  | 13.9 |  | 13.9 | 13.9 | 13.9
|  |  |  | Contracted non-network (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 3.2 | 3.2 | 3.2 |  | 3.2 |  | 3.2 | 3.7 |  | 3.7 |  | 3.7 | 3.6 | 3.6
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.95 | 0.95 | 0.95 |  | 0.95 |  | 0.95 | 0.971 |  | 0.971 |  | 0.971 | 0.971 | 0.971
|  |  |  | ECC Rating (MVA) |  | 7.2 | 7.2 | 7.2 |  | 7.2 |  | 7.2 | 8.2 |  | 8.2 |  | 8.2 | 8.2 | 8.2
|  |  |  | 50 PoE Load (MVA) |  | 3.1 | 3.1 | 3 |  | 3 |  | 3.1 | 3.1 |  | 3.1 |  | 3.1 | 3.1 | 3
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 17.5 | 17.5 | 17.5 |  | 17.5 |  | 17.5 | 17.5 |  | 17.5 |  | 17.5 | 17.5 | 17.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 4.5 | 4.5 | 4.5 |  | 4.5 |  | 4.5 | 4.5 |  | 4.5 |  | 4.5 | 4.5 | 4.5
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 8 | 8 | 8 |  | 8 |  | 8 | 8 |  | 8 |  | 8 | 8 | 8
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MACT
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MACT - Mackay City (33/11kV) | [8 empty] | Supply |  | MACK - Mackay BSP
| Description |  |  |  | Region is Mackay
Transformer size is 1x25/32MVA 33/11kV TR94712137;1x25/32MVA 33/11kV TR94712143
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.2% W -0.6%2025 S -1.5% W -0.6%2026 S -0.9% W -0.2%2027 S -0.3% W -0.1
|  |  | Latest Peak Compensated Load | [5 empty] | 17.2 MVA on 02/02/2023 at 16:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 89.6 | 89.6 | 89.6 |  | 89.6 |  | 89.6 | 96 |  | 96 |  | 96 | 96 | 96
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 20 | 19.7 | 19.5 |  | 19.4 |  | 19.5 | 11.5 |  | 11.4 |  | 11.3 | 11.3 | 11.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.961 | 0.961 | 0.961 |  | 0.961 |  | 0.961 | 0.972 |  | 0.972 |  | 0.972 | 0.972 | 0.972
|  |  |  | ECC Rating (MVA) |  | 48 | 48 | 48 |  | 48 |  | 48 | 48 |  | 48 |  | 48 | 48 | 48
|  |  |  | 50 PoE Load (MVA) |  | 18.1 | 17.9 | 17.7 |  | 17.7 |  | 17.7 | 10.3 |  | 10.3 |  | 10.2 | 10.2 | 10.2
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.9 | 0.9 | 0.9 |  | 0.9 |  | 0.9 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | Hours PA > 95% Peak Load |  | 6 | 6 | 6 |  | 6 |  | 6 | 6 |  | 6 |  | 6 | 6 | 6
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 5.5 | 5.5 | 5.5 |  | 5.5 |  | 5.5 | 5.5 |  | 5.5 |  | 5.5 | 5.5 | 5.5
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 50 | 50 | 50 |  | 50 |  | 50 | 50 |  | 50 |  | 50 | 50 | 50
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 25 | 25 | 25 |  | 25 |  | 25 | 25 |  | 25 |  | 25 | 25 | 25
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MAFU
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MAFU - Max Fulton (66/11kV) | [8 empty] | Supply |  | TMES - Townsville Mesh
| Description |  |  |  | Region is Nth Queensland
Transformer size is 2x66/11kV 21/26.25/35MVA ONAN/ODAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.3% W 0.0%,2025 S -1.8% W -0.4%2026 S -1.1% W 0.1%,2027 S 0.2% W 0.3%
|  |  | Latest Peak Compensated Load | [5 empty] | 12 MVA on 16/11/2022 at 17:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 76.3 | 76.3 | 76.3 |  | 76.3 |  | 76.3 | 77.7 |  | 77.7 |  | 77.7 | 77.7 | 77.7
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 13.9 | 15.3 | 15.2 |  | 15.2 |  | 15.5 | 10.2 |  | 11.5 |  | 11.4 | 11.5 | 11.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.989 | 0.989 | 0.989 |  | 0.989 |  | 0.989 | 0.982 |  | 0.982 |  | 0.982 | 0.982 | 0.982
|  |  |  | ECC Rating (MVA) |  | 38.5 | 38.5 | 38.5 |  | 38.5 |  | 38.5 | 39.2 |  | 39.2 |  | 39.2 | 39.2 | 39.2
|  |  |  | 50 PoE Load (MVA) |  | 13.6 | 15.1 | 14.9 |  | 14.9 |  | 15.2 | 9.6 |  | 10.9 |  | 10.8 | 10.8 | 10.9
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.7 | 0.8 | 0.7 |  | 0.7 |  | 0.8 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | Hours PA > 95% Peak Load |  | 203.5 | 203.5 | 203.5 |  | 203.5 |  | 203.5 | 203.5 |  | 203.5 |  | 203.5 | 203.5 | 203.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 42 | 42 | 42 |  | 42 |  | 42 | 42 |  | 42 |  | 42 | 42 | 42
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 21 | 21 | 21 |  | 21 |  | 21 | 21 |  | 21 |  | 21 | 21 | 21
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MAKA
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MAKA - Mary Kathleen (66/11kV) | [8 empty] | Supply |  | Duchess Road 66kV accumulator
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1xMAKA T1-66/11kV0.25MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 0.0%, 2024 S 0.0% W 0.0%, 2025 S 0.0% W 0.0%, 2026 S 0.0% W 0.0%, 2027 S 0.0% W 0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 0.1 MVA on 01/01/2022 at 17:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.85 | 0.85 | 0.85 |  | 0.85 |  | 0.85 | 0.85 |  | 0.85 |  | 0.85 | 0.85 | 0.85
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Raw LAR (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Mobile Plant Avail (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 0.25 | 0.25 | 0.25 |  | 0.25 |  | 0.25 | 0.25 |  | 0.25 |  | 0.25 | 0.25 | 0.25
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MALC
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MALC - Malchi (66/11kV) | [8 empty] | Supply |  | RMES - Rockhampton Mesh
| Description |  |  |  | Region is Capricornia
Transformer size is 2x66/11kV 7.5/10MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.3% W 0.7%,2025 S -0.1% W 0.8%,2026 S 0.4% W 1.1%, 2027 S 1.2% W 1.4%
|  |  | Latest Peak Compensated Load | [5 empty] | 19.3 MVA on 13/02/2023 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 23.8 | 23.8 | 23.8 |  | 23.8 |  | 23.8 | 28.7 |  | 28.7 |  | 28.7 | 28.7 | 28.7
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 14.8 | 14.8 | 14.8 |  | 15 |  | 15.3 | 6.1 |  | 6.1 |  | 6.2 | 6.3 | 6.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.99 | 0.99 | 0.99 |  | 0.99 |  | 0.99 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | ECC Rating (MVA) |  | 13.3 | 13.3 | 13.3 |  | 13.3 |  | 13.3 | 15 |  | 15 |  | 15 | 15 | 15
|  |  |  | 50 PoE Load (MVA) |  | 12.4 | 12.4 | 12.4 |  | 12.6 |  | 12.8 | 4.8 |  | 4.8 |  | 4.8 | 4.9 | 5
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.3
|  |  |  | Hours PA > 95% Peak Load |  | 2.5 | 2.5 | 2.5 |  | 2.5 |  | 2.5 | 2.5 |  | 2.5 |  | 2.5 | 2.5 | 2.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 1.5 | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.5 | 1.5
|  |  |  | Mobile Plant Avail (MVA) |  | 2.5 | 2.5 | 2.5 |  | 2.5 |  | 2.5 | 2.5 |  | 2.5 |  | 2.5 | 2.5 | 2.5
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 15 | 15 | 15 |  | 15 |  | 15 | 15 |  | 15 |  | 15 | 15 | 15
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 7.5 | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 | 7.5
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MARE
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MARE - Mareeba (66/22kV) | [8 empty] | Supply |  | TURK - Turkinje 66kV BSP
| Description |  |  |  | Region is Far North
Transformer size is 2x66/22kV 20/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.1% W 0.3%,2025 S -1.5% W 0.5%,2026 S -0.1% W 0.8%,2027 S 0.8% W 0.8%
|  |  | Latest Peak Compensated Load | [5 empty] | 20.6 MVA on 22/11/2022 at 16:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 57.2 | 57.2 | 57.2 |  | 57.2 |  | 57.2 | 63.6 |  | 63.6 |  | 63.6 | 63.6 | 63.6
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 22.2 | 21.9 | 21.8 |  | 22 |  | 22.4 | 18.5 |  | 18.6 |  | 18.7 | 18.8 | 19
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.998 | 0.998 | 0.997 |  | 0.998 |  | 0.997 | 0.998 |  | 0.998 |  | 0.998 | 0.998 | 0.998
|  |  |  | ECC Rating (MVA) |  | 32.8 | 32.8 | 32.8 |  | 32.8 |  | 32.8 | 35.2 |  | 35.2 |  | 35.2 | 35.2 | 35.2
|  |  |  | 50 PoE Load (MVA) |  | 21.2 | 20.9 | 20.9 |  | 21 |  | 21.4 | 17.5 |  | 17.6 |  | 17.7 | 17.8 | 17.9
|  |  |  | 50 PoE Load > 95% (MVA) |  | 1.1 | 1 | 1 |  | 1.1 |  | 1.1 | 0.9 |  | 0.9 |  | 0.9 | 0.9 | 0.9
|  |  |  | Hours PA > 95% Peak Load |  | 30 | 30 | 30 |  | 30 |  | 30 | 30 |  | 30 |  | 30 | 30 | 30
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 40 | 40 | 40 |  | 40 |  | 40 | 40 |  | 40 |  | 40 | 40 | 40
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 20 | 20 | 20 |  | 20 |  | 20 | 20 |  | 20 |  | 20 | 20 | 20
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MARY
Bulk Summary Information and Peak Load Forecast
Substation |  |  |  | MARY - Maryborough BSP (132/66kV) | [8 empty] | Supply |  | QTBC - Teebar Creek TCP
Description |  |  |  | Region is Wide Bay
Transformer size is 2x132/66/11kV 80/100MVA ONAN/ODAN;1x132/66kV 64/80/90MVA ONAN/ODAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 78.4 MVA
|  | Latest Peak Compensated Load | [5 empty] | 123.2 MVA on 13/02/2023 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[5 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  | NCC Rating (MVA) |  | 356.1 | 356.1 | 356.1 |  | 356.1 |  | 356.1 | 403.7 |  | 403.7 |  | 403.7 | 403.7 | 403.7
|  |  | Contracted non-network (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  | 10 PoE Load (MVA) |  | 124.7 | 126.1 | 127.1 |  | 127.8 |  | 128.8 | 116.3 |  | 118.3 |  | 119.6 | 120.1 | 120.1
LARn (MVA)
LARn (MW)
|  |  | Power Factor at Peak Load |  | 0.995 | 0.995 | 0.995 |  | 0.995 |  | 0.995 | 0.996 |  | 0.996 |  | 0.996 | 0.996 | 0.996
|  |  | ECC Rating (MVA) |  | 266.8 | 266.8 | 266.8 |  | 266.8 |  | 266.8 | 269.1 |  | 269.1 |  | 269.1 | 269.1 | 269.1
|  |  | 50 PoE Load (MVA) |  | 117.9 | 119.3 | 120.4 |  | 121.2 |  | 122 | 109.5 |  | 111.5 |  | 112.9 | 113.3 | 113.4
|  |  | 50 PoE Load > 95% (MVA) |  | 5.9 | 6 | 6 |  | 6.1 |  | 6.1 | 5.5 |  | 5.6 |  | 5.6 | 5.7 | 5.7
|  |  | Hours PA > 95% Peak Load |  | 6 | 6 | 6 |  | 6 |  | 6 | 6 |  | 6 |  | 6 | 6 | 6
Raw LAR (MVA)
|  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Capacity for Embedded Generation (MVA) |  | 100 | 100 | 100 |  | 100 |  | 100 | 100 |  | 100 |  | 100 | 100 | 100
|  |  | Firm Capacity for Embedded Generation (MVA) |  | 24 | 24 | 24 |  | 24 |  | 24 | 24 |  | 24 |  | 24 | 24 | 24
LARc (MVA)
LARc (MW)
|  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MASO
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MASO - Marian South (66/11kV) | [8 empty] | Supply |  | PIVA - Pioneer Valley BSP
| Description |  |  |  | Region is Mackay
Transformer size is 1x66/11kV 8/10MVA ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 23.4 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.1% W -0.6%2025 S -1.1% W -0.3%2026 S -0.6% W 0.0%,2027 S 0.8% W 0.3%
|  |  | Latest Peak Compensated Load | [5 empty] | 7.3 MVA on 16/07/2022 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 15 | 15 | 15 |  | 15 |  | 15 | 15 |  | 15 |  | 15 | 15 | 15
|  |  |  | Contracted non-network (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 2.8 |  | 2.8 |  | 2.8 | 2.8 | 2.8
|  |  |  | 10 PoE Load (MVA) |  | 6.1 | 6 | 6 |  | 6.1 |  | 6.1 | 7.4 |  | 7.4 |  | 7.3 | 7.3 | 7.4
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.978 | 0.978 | 0.978 |  | 0.978 |  | 0.978 | 0.979 |  | 0.979 |  | 0.979 | 0.979 | 0.979
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 5.8 | 5.8 | 5.7 |  | 5.8 |  | 5.9 | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Hours PA > 95% Peak Load |  | 35 | 35 | 35 |  | 35 |  | 35 | 35 |  | 35 |  | 35 | 35 | 35
|  |  |  | Raw LAR (MVA) |  | 5.8 | 5.8 | 5.7 |  | 5.8 |  | 5.9 | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 3.4 | 3.4 | 3.4 |  | 3.4 |  | 3.4 | 3.4 |  | 3.4 |  | 3.4 | 3.4 | 3.4
|  |  |  | Mobile Plant Avail (MVA) |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 2.8 | 2.8 | 2.8 |  | 2.8 |  | 2.8 | 2.8 |  | 2.8 |  | 2.8 | 2.8 | 2.8
|  |  |  | Capacity for Embedded Generation (MVA) |  | 8 | 8 | 8 |  | 8 |  | 8 | 8 |  | 8 |  | 8 | 8 | 8
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MCCR
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MCCR - McKinley Creek (66/11kV) | [8 empty] | Supply |  | PIVA - Pioneer Valley BSP
| Description |  |  |  | Region is Mackay
Transformer size is 1x66/11kV 5/6.3MVA ONAN/ONAF;1xMCCR 66/11KV 5/6.3MVA ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.6% W -0.4%2025 S -0.4% W -0.2%2026 S 0.0% W 0.1%, 2027 S 0.6% W 0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 3.5 MVA on 02/02/2023 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 15.1 | 15.1 | 15.1 |  | 15.1 |  | 15.1 | 15.1 |  | 15.1 |  | 15.1 | 15.1 | 15.1
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 3.8 | 3.8 | 3.8 |  | 3.8 |  | 3.8 | 3.1 |  | 3.1 |  | 3.1 | 3.1 | 3.1
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.989 | 0.989 | 0.989 |  | 0.989 |  | 0.989 | 0.997 |  | 0.997 |  | 0.997 | 0.997 | 0.997
|  |  |  | ECC Rating (MVA) |  | 7.9 | 7.9 | 7.9 |  | 7.9 |  | 7.9 | 8.2 |  | 8.2 |  | 8.2 | 8.2 | 8.2
|  |  |  | 50 PoE Load (MVA) |  | 3.6 | 3.6 | 3.6 |  | 3.6 |  | 3.7 | 2.8 |  | 2.8 |  | 2.8 | 2.8 | 2.8
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 3.5 | 3.5 | 3.5 |  | 3.5 |  | 3.5 | 3.5 |  | 3.5 |  | 3.5 | 3.5 | 3.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 | 5 | 5
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MEAD
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MEAD - Meadowvale (66/11kV) | [8 empty] | Supply |  | BUND - Bundaberg BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 1x66/11kV 12/14MVA ONAN/ONAF;1x62/11kV 7.5MVA ONAN(Standby)
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.9% W -1.4%2025 S -1.0% W -0.4%2026 S -0.5% W 0.3%,2027 S 0.4% W 0.4%
|  |  | Latest Peak Compensated Load | [5 empty] | 8.4 MVA on 13/02/2023 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 15.9 | 15.9 | 15.9 |  | 15.9 |  | 15.9 | 17.3 |  | 17.3 |  | 17.3 | 17.3 | 17.3
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 8.6 | 8.6 | 8.5 |  | 8.6 |  | 8.7 | 8.6 |  | 8.5 |  | 8.5 | 8.5 | 8.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.995 | 0.995 | 0.995 |  | 0.995 |  | 0.995 | 0.991 |  | 0.991 |  | 0.991 | 0.991 | 0.991
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 8.5 | 8.4 | 8.4 |  | 8.4 |  | 8.5 | 8.4 |  | 8.3 |  | 8.2 | 8.3 | 8.3
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.4 | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  |  | Hours PA > 95% Peak Load |  | 8.5 | 8.5 | 8.5 |  | 8.5 |  | 8.5 | 8.5 |  | 8.5 |  | 8.5 | 8.5 | 8.5
|  |  |  | Raw LAR (MVA) |  | 8.5 | 8.4 | 8.4 |  | 8.4 |  | 8.5 | 8.4 |  | 8.3 |  | 8.2 | 8.3 | 8.3
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 11.2 | 11.2 | 11.2 |  | 11.2 |  | 11.2 | 11.2 |  | 11.2 |  | 11.2 | 11.2 | 11.2
|  |  |  | Manual Trans Avail (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 | 2 | 2
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 7.5 | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 | 7.5
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 7.5 | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 | 7.5
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MEAN
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MEAN - Meandarra (33/22kV) | [8 empty] | Supply |  | COLU - Columboola BSP
| Description |  |  |  | Region is South West
Transformer size is 1x33/22/0.415kV 1MVA ONAN;1x33/22/0.415kV 1MVA ONAN(Standby)
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.0% W -0.6%2025 S -0.8% W -0.2%2026 S -0.3% W 0.0%,2027 S 0.3% W 0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 0.7 MVA on 12/02/2023 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1.1 |  | 1.1 |  | 1.1 | 1.1 | 1.1
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 0.9 | 0.9 | 0.9 |  | 0.9 |  | 0.9 | 0.8 |  | 0.8 |  | 0.8 | 0.8 | 0.8
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 0.8 | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.7 |  | 0.7 |  | 0.7 | 0.7 | 0.7
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 5.5 | 5.5 | 5.5 |  | 5.5 |  | 5.5 | 5.5 |  | 5.5 |  | 5.5 | 5.5 | 5.5
|  |  |  | Raw LAR (MVA) |  | 0.8 | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.7 |  | 0.7 |  | 0.7 | 0.7 | 0.7
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 | 2 | 2
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MERI
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MERI - Merinda (66/11kV) | [8 empty] | Supply |  | T181 - Bowen North BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/11kV 6.3MVA ONAN;1x66/11kV 8/10MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.5% W -0.6%2025 S -1.4% W -0.6%2026 S -0.7% W -0.3%2027 S 0.1% W -0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 3.9 MVA on 29/08/2022 at 14:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 16.1 | 16.1 | 16.1 |  | 16.1 |  | 16.1 | 16.6 |  | 16.6 |  | 16.6 | 16.6 | 16.6
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 4.1 | 4 | 4 |  | 4 |  | 4.1 | 5.1 |  | 5 |  | 5 | 5 | 5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.903 | 0.903 | 0.903 |  | 0.903 |  | 0.903 | 0.897 |  | 0.897 |  | 0.897 | 0.897 | 0.897
|  |  |  | ECC Rating (MVA) |  | 9.4 | 9.4 | 9.4 |  | 9.4 |  | 9.4 | 9.4 |  | 9.4 |  | 9.4 | 9.4 | 9.4
|  |  |  | 50 PoE Load (MVA) |  | 4 | 3.9 | 3.9 |  | 3.9 |  | 3.9 | 4.8 |  | 4.8 |  | 4.7 | 4.7 | 4.7
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 173.5 | 173.5 | 173.5 |  | 173.5 |  | 173.5 | 173.5 |  | 173.5 |  | 173.5 | 173.5 | 173.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 11 | 11 | 11 |  | 11 |  | 11 | 11 |  | 11 |  | 11 | 11 | 11
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 14.3 | 14.3 | 14.3 |  | 14.3 |  | 14.3 | 14.3 |  | 14.3 |  | 14.3 | 14.3 | 14.3
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 6.3 | 6.3 | 6.3 |  | 6.3 |  | 6.3 | 6.3 |  | 6.3 |  | 6.3 | 6.3 | 6.3
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MERN
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MERN - Meringandan (33/11kV) | [8 empty] | Supply |  | T116 - Torrington BSP
| Description |  |  |  | Region is South West
Transformer size is 2x33/11kV 6.3MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.5% W -0.2%2025 S -0.6% W -0.2%2026 S 0.2% W 0.0%, 2027 S 1.1% W 0.2%
|  |  | Latest Peak Compensated Load | [5 empty] | 12.9 MVA on 04/07/2022 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 16.9 | 16.9 | 16.9 |  | 16.9 |  | 16.9 | 18.5 |  | 18.5 |  | 18.5 | 18.5 | 18.5
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 11.3 | 11.2 | 11.2 |  | 11.3 |  | 11.5 | 12.8 |  | 12.7 |  | 12.7 | 12.7 | 12.7
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.997 | 0.997 | 0.997 |  | 0.997 |  | 0.997 | 0.999 |  | 0.999 |  | 0.999 | 0.999 | 0.999
|  |  |  | ECC Rating (MVA) |  | 9.2 | 9.2 | 9.2 |  | 9.2 |  | 9.2 | 9.4 |  | 9.4 |  | 9.4 | 9.4 | 9.4
|  |  |  | 50 PoE Load (MVA) |  | 10.4 | 10.4 | 10.4 |  | 10.5 |  | 10.7 | 12.2 |  | 12.1 |  | 12.1 | 12.1 | 12.1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  |  | Hours PA > 95% Peak Load |  | 2.5 | 2.5 | 2.5 |  | 2.5 |  | 2.5 | 2.5 |  | 2.5 |  | 2.5 | 2.5 | 2.5
|  |  |  | Raw LAR (MVA) |  | 1.2 | 1.2 | 1.2 |  | 1.3 |  | 1.5 | 2.8 |  | 2.7 |  | 2.7 | 2.7 | 2.7
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 1.5 | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.5 | 1.5
|  |  |  | Mobile Plant Avail (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 12.6 | 12.6 | 12.6 |  | 12.6 |  | 12.6 | 12.6 |  | 12.6 |  | 12.6 | 12.6 | 12.6
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 6.3 | 6.3 | 6.3 |  | 6.3 |  | 6.3 | 6.3 |  | 6.3 |  | 6.3 | 6.3 | 6.3
|  |  |  | LARc (MVA) | [8 empty] | 0.3 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | LARc (MW) | [8 empty] | 0.3 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | No |  | No |  | No | No | No
Return to Index

## MICO
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MICO - Miles-Condamine (33/22kV) | [8 empty] | Supply |  | COLU - Columboola BSP
| Description |  |  |  | Region is South West
Transformer size is 1x33/22kV 0.75MVA ON;1x33/22kV 0.75MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.0% W -0.6%2025 S -0.8% W -0.2%2026 S -0.4% W 0.0%,2027 S 0.2% W 0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 0.7 MVA on 12/02/2023 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 1.5 | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.6 |  | 1.6 |  | 1.6 | 1.6 | 1.6
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 0.7 | 0.6 | 0.6 |  | 0.6 |  | 0.7 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.995 | 0.994 | 0.994 |  | 0.994 |  | 0.995 | 0.999 |  | 0.999 |  | 0.999 | 0.999 | 0.999
|  |  |  | ECC Rating (MVA) |  | 0.8 | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.8 | 0.8
|  |  |  | 50 PoE Load (MVA) |  | 0.7 | 0.6 | 0.6 |  | 0.6 |  | 0.7 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 3 | 3 | 3 |  | 3 |  | 3 | 3 |  | 3 |  | 3 | 3 | 3
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0.8 | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.8 | 0.8
|  |  |  | Mobile Plant Avail (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 1.5 | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.5 | 1.5
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0.75 | 0.75 | 0.75 |  | 0.75 |  | 0.75 | 0.75 |  | 0.75 |  | 0.75 | 0.75 | 0.75
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MIDD
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MIDD - Middlemount (66/22kV) | [8 empty] | Supply |  | H015 - Lilyvale BSP
| Description |  |  |  | Region is Capricornia
Transformer size is 2x66/22kV 5/7MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.0% W -0.5%2025 S -0.9% W -0.4%2026 S -0.4% W -0.1%2027 S 0.3% W 0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 5 MVA on 13/02/2023 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 15.3 | 15.3 | 15.3 |  | 15.3 |  | 15.3 | 18.6 |  | 18.6 |  | 18.6 | 18.6 | 18.6
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 5.2 | 5.1 | 5.1 |  | 5.1 |  | 5.2 | 3.8 |  | 3.8 |  | 3.8 | 3.8 | 3.8
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.994 | 0.994 | 0.994 |  | 0.994 |  | 0.994 | 0.997 |  | 0.997 |  | 0.997 | 0.997 | 0.997
|  |  |  | ECC Rating (MVA) |  | 8.7 | 8.7 | 8.7 |  | 8.7 |  | 8.7 | 9.3 |  | 9.3 |  | 9.3 | 9.3 | 9.3
|  |  |  | 50 PoE Load (MVA) |  | 5 | 5 | 4.9 |  | 5 |  | 5 | 3.6 |  | 3.6 |  | 3.6 | 3.6 | 3.6
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.3 | 0.3 | 0.2 |  | 0.3 |  | 0.3 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 14.5 | 14.5 | 14.5 |  | 14.5 |  | 14.5 | 14.5 |  | 14.5 |  | 14.5 | 14.5 | 14.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 | 5 | 5
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MILC
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MILC - Millchester (66/11kV) | [8 empty] | Supply |  | T095 - Millchester BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/11kV 10MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.0% W -0.5%2025 S -0.9% W -0.2%2026 S -0.4% W 0.0%,2027 S 0.2% W 0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 5.6 MVA on 21/11/2022 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 10.6 | 10.6 | 10.6 |  | 10.6 |  | 10.6 | 12.2 |  | 12.2 |  | 12.2 | 12.2 | 12.2
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 5.8 | 5.8 | 5.8 |  | 5.8 |  | 5.8 | 4.6 |  | 4.6 |  | 4.6 | 4.6 | 4.6
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.99 | 0.99 | 0.99 |  | 0.99 |  | 0.99 | 0.997 |  | 0.997 |  | 0.997 | 0.997 | 0.997
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 5.5 | 5.5 | 5.5 |  | 5.5 |  | 5.5 | 4.3 |  | 4.3 |  | 4.3 | 4.3 | 4.3
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 8.5 | 8.5 | 8.5 |  | 8.5 |  | 8.5 | 8.5 |  | 8.5 |  | 8.5 | 8.5 | 8.5
|  |  |  | Raw LAR (MVA) |  | 5.5 | 5.5 | 5.5 |  | 5.5 |  | 5.5 | 4.3 |  | 4.3 |  | 4.3 | 4.3 | 4.3
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 6.5 | 6.5 | 6.5 |  | 6.5 |  | 6.5 | 6.5 |  | 6.5 |  | 6.5 | 6.5 | 6.5
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MILE
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MILE - Miles (33/11kV) | [8 empty] | Supply |  | COLU - Columboola BSP
| Description |  |  |  | Region is South West
Transformer size is 1x33/11kV 5/6.3MVA ONAN;1x33/11KV 1.5MVA ONAN(Standby)
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.4% W -0.3%2025 S -1.6% W -0.2%2026 S -0.8% W 0.1%,2027 S 0.0% W 0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 3.4 MVA on 12/02/2023 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 8.1 | 8.1 | 8.1 |  | 8.1 |  | 8.1 | 9.4 |  | 9.4 |  | 9.4 | 9.4 | 9.4
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 3.7 | 3.6 | 3.6 |  | 3.6 |  | 3.7 | 3.4 |  | 3.3 |  | 3.3 | 3.3 | 3.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.989 | 0.989 | 0.989 |  | 0.989 |  | 0.989 | 0.995 |  | 0.995 |  | 0.995 | 0.995 | 0.995
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 3.4 | 3.4 | 3.3 |  | 3.3 |  | 3.4 | 3.2 |  | 3.2 |  | 3.2 | 3.2 | 3.2
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 17 | 17 | 17 |  | 17 |  | 17 | 17 |  | 17 |  | 17 | 17 | 17
|  |  |  | Raw LAR (MVA) |  | 3.4 | 3.4 | 3.3 |  | 3.3 |  | 3.4 | 3.2 |  | 3.2 |  | 3.2 | 3.2 | 3.2
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 1.5 | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.5 | 1.5
|  |  |  | Mobile Plant Avail (MVA) |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 6.5 | 6.5 | 6.5 |  | 6.5 |  | 6.5 | 6.5 |  | 6.5 |  | 6.5 | 6.5 | 6.5
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MILL
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MILL - Millaroo (66/11kV) | [8 empty] | Supply |  | T193 - Clare South BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/11kV 5MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.7% W -0.3%2025 S -0.7% W -0.4%2026 S -0.2% W 0.0%,2027 S 0.4% W 0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 1.7 MVA on 14/12/2022 at 19:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 5.6 | 5.6 | 5.6 |  | 5.6 |  | 5.6 | 6.5 |  | 6.5 |  | 6.5 | 6.5 | 6.5
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 2.1 | 2 | 2 |  | 2 |  | 2 | 1.5 |  | 1.5 |  | 1.5 | 1.5 | 1.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.887 | 0.887 | 0.887 |  | 0.887 |  | 0.877 | 0.891 |  | 0.871 |  | 0.871 | 0.871 | 0.871
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 1.5 |  | 1.4 |  | 1.4 | 1.4 | 1.4
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 41.5 | 41.5 | 41.5 |  | 41.5 |  | 41.5 | 41.5 |  | 41.5 |  | 41.5 | 41.5 | 41.5
|  |  |  | Raw LAR (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 1.5 |  | 1.4 |  | 1.4 | 1.4 | 1.4
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 | 5 | 5
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MILM
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MILM - Millmerran (33/11kV) | [8 empty] | Supply |  | YARA - Yarranlea BSP
| Description |  |  |  | Region is South West
Transformer size is 1x33/11kV 6.3MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.9% W -0.5%2025 S -0.9% W -0.2%2026 S -0.4% W 0.1%,2027 S 0.2% W 0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 4 MVA on 12/02/2023 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 7.6 | 7.6 | 7.6 |  | 7.6 |  | 7.6 | 8.5 |  | 8.5 |  | 8.5 | 8.5 | 8.5
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 3.9 | 3.8 | 3.8 |  | 3.8 |  | 3.9 | 3.5 |  | 3.5 |  | 3.4 | 3.5 | 3.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.994 | 0.994 | 0.994 |  | 0.994 |  | 0.994 | 0.996 |  | 0.996 |  | 0.996 | 0.996 | 0.996
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 3.7 | 3.6 | 3.6 |  | 3.6 |  | 3.7 | 3.3 |  | 3.3 |  | 3.3 | 3.3 | 3.3
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 6.5 | 6.5 | 6.5 |  | 6.5 |  | 6.5 | 6.5 |  | 6.5 |  | 6.5 | 6.5 | 6.5
|  |  |  | Raw LAR (MVA) |  | 3.7 | 3.6 | 3.6 |  | 3.6 |  | 3.7 | 3.3 |  | 3.3 |  | 3.3 | 3.3 | 3.3
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 6.3 | 6.3 | 6.3 |  | 6.3 |  | 6.3 | 6.3 |  | 6.3 |  | 6.3 | 6.3 | 6.3
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MING
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MING - Mingela (66/11kV) | [8 empty] | Supply |  | TMES - Townsville Mesh
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1xMING TX NO 1-66/11KV 0.25MVA
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 0.0%, 2024 S 0.0% W 0.0%, 2025 S 0.0% W 0.0%, 2026 S 0.0% W 0.0%, 2027 S 0.0% W 0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 0.3 MVA on 01/01/2022 at 17:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.85 | 0.85 | 0.85 |  | 0.85 |  | 0.85 | 0.85 |  | 0.85 |  | 0.85 | 0.85 | 0.85
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Raw LAR (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 0.25 | 0.25 | 0.25 |  | 0.25 |  | 0.25 | 0.25 |  | 0.25 |  | 0.25 | 0.25 | 0.25
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MIRA
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MIRA - Mirani (66/11kV) | [8 empty] | Supply |  | PIVA - Pioneer Valley BSP
| Description |  |  |  | Region is Mackay
Transformer size is 1x66/11kV 5MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.5% W 0.1%,2025 S -0.4% W 0.3%,2026 S 0.1% W 0.5%, 2027 S 1.1% W 1.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 2.3 MVA on 13/02/2023 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 6.1 | 6.1 | 6.1 |  | 6.1 |  | 6.1 | 7 |  | 7 |  | 7 | 7 | 7
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 3 | 3 | 3 |  | 3 |  | 3.1 | 1.9 |  | 1.9 |  | 1.9 | 1.9 | 2
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.973 | 0.973 | 0.973 |  | 0.973 |  | 0.973 | 0.984 |  | 0.984 |  | 0.984 | 0.984 | 0.984
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 2.8 | 2.8 | 2.8 |  | 2.9 |  | 2.9 | 1.8 |  | 1.8 |  | 1.8 | 1.8 | 1.8
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 113.5 | 113.5 | 113.5 |  | 113.5 |  | 113.5 | 113.5 |  | 113.5 |  | 113.5 | 113.5 | 113.5
|  |  |  | Raw LAR (MVA) |  | 2.8 | 2.8 | 2.8 |  | 2.9 |  | 2.9 | 1.8 |  | 1.8 |  | 1.8 | 1.8 | 1.8
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 3.2 | 3.2 | 3.2 |  | 3.2 |  | 3.2 | 3.2 |  | 3.2 |  | 3.2 | 3.2 | 3.2
|  |  |  | Mobile Plant Avail (MVA) |  | 1.6 | 1.6 | 1.6 |  | 1.6 |  | 1.6 | 1.6 |  | 1.6 |  | 1.6 | 1.6 | 1.6
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 | 5 | 5
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MITC
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MITC - Mitchell (33/11kV) | [8 empty] | Supply |  | T083 - Roma 33kV BSP
| Description |  |  |  | Region is South West
Transformer size is 3x33/11kV 0.75MVA ON
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.2% W -0.8%2025 S -1.1% W -0.7%2026 S -0.7% W -0.4%2027 S -0.1% W -0.4
|  |  | Latest Peak Compensated Load | [5 empty] | 2.3 MVA on 15/07/2022 at 07:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 2.3 | 3.2 | 3.2 |  | 3.2 |  | 3.2 | 2.3 |  | 3.2 |  | 3.2 | 3.2 | 3.2
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2.5 |  | 2.5 |  | 2.5 | 2.5 | 2.5
|  |  |  | LARn (MVA) | [8 empty] | 0.2
|  |  |  | LARn (MW) | [8 empty] | 0.2
|  |  |  | Power Factor at Peak Load |  | 0.947 | 0.947 | 0.947 |  | 0.947 |  | 0.947 | 0.964 |  | 0.964 |  | 0.964 | 0.964 | 0.964
|  |  |  | ECC Rating (MVA) |  | 1.5 | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.5 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 1.9 | 1.9 | 1.9 |  | 1.9 |  | 1.9 | 2.4 |  | 2.4 |  | 2.4 | 2.3 | 2.3
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 9.5 | 9.5 | 9.5 |  | 9.5 |  | 9.5 | 9.5 |  | 9.5 |  | 9.5 | 9.5 | 9.5
|  |  |  | Raw LAR (MVA) |  | 0.4 | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.9 |  | 2.4 |  | 2.4 | 2.3 | 2.3
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 1 | 13 | 13 |  | 13 |  | 13 | 1 |  | 13 |  | 13 | 13 | 13
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 1.5 | 3.2 | 3.2 |  | 3.2 |  | 3.2 | 1.5 |  | 3.2 |  | 3.2 | 3.2 | 3.2
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0.75 | 0 | 0 |  | 0 |  | 0 | 0.8 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | No |  | Yes |  | Yes | Yes | Yes
Return to Index

## MIVA
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MIVA - Miriam Vale (66/22kV) | [8 empty] | Supply |  | T019 - Gladstone South BSP
| Description |  |  |  | Region is Capricornia
Transformer size is 1x66/22kV 6.3MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.0% W -0.7%2025 S -0.8% W -0.4%2026 S -0.4% W -0.1%2027 S 0.3% W -0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 2.4 MVA on 12/06/2022 at 17:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 9.1 | 9.1 | 9.1 |  | 9.1 |  | 9.1 | 9.4 |  | 9.4 |  | 9.4 | 9.4 | 9.4
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 2.1 | 2 | 2 |  | 2 |  | 2.1 | 2.6 |  | 2.5 |  | 2.5 | 2.5 | 2.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.999 | 0.999 | 0.999 |  | 0.999 |  | 0.999 | 0.996 |  | 0.996 |  | 0.996 | 0.996 | 0.996
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 2 | 2 | 1.9 |  | 2 |  | 2 | 2.4 |  | 2.4 |  | 2.4 | 2.4 | 2.4
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 67 | 67 | 67 |  | 67 |  | 67 | 67 |  | 67 |  | 67 | 67 | 67
|  |  |  | Raw LAR (MVA) |  | 2 | 2 | 1.9 |  | 2 |  | 2 | 2.4 |  | 2.4 |  | 2.4 | 2.4 | 2.4
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 1.6 | 1.6 | 1.6 |  | 1.6 |  | 1.6 | 1.6 |  | 1.6 |  | 1.6 | 1.6 | 1.6
|  |  |  | Manual Trans Avail (MVA) |  | 3.1 | 3.1 | 3.1 |  | 3.1 |  | 3.1 | 3.1 |  | 3.1 |  | 3.1 | 3.1 | 3.1
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 6.3 | 6.3 | 6.3 |  | 6.3 |  | 6.3 | 6.3 |  | 6.3 |  | 6.3 | 6.3 | 6.3
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MOBA
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MOBA - Mt Bassett (33/11kV) | [8 empty] | Supply |  | MACK - Mackay BSP
| Description |  |  |  | Region is Mackay
Transformer size is 1x33/11kV 10MVA ONAN;2x33/11kV 12.5MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.8% W -0.3%2025 S -0.9% W -0.4%2026 S -0.4% W -0.0%2027 S 0.1% W -0.2%
|  |  | Latest Peak Compensated Load | [5 empty] | 12.8 MVA on 02/02/2023 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 39 | 39 | 39 |  | 39 |  | 39 | 42 |  | 42 |  | 42 | 42 | 42
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 13.8 | 13.7 | 13.7 |  | 13.7 |  | 13.8 | 9.1 |  | 9.1 |  | 9 | 9 | 9
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.985 | 0.985 | 0.985 |  | 0.985 |  | 0.985 | 0.988 |  | 0.988 |  | 0.988 | 0.988 | 0.988
|  |  |  | ECC Rating (MVA) |  | 27.9 | 27.9 | 27.9 |  | 27.9 |  | 27.9 | 27.9 |  | 27.9 |  | 27.9 | 27.9 | 27.9
|  |  |  | 50 PoE Load (MVA) |  | 12.8 | 12.7 | 12.6 |  | 12.6 |  | 12.8 | 8.6 |  | 8.6 |  | 8.6 | 8.6 | 8.5
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  |  | Hours PA > 95% Peak Load |  | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 | 5 | 5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 25 | 25 | 25 |  | 25 |  | 25 | 25 |  | 25 |  | 25 | 25 | 25
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 12.5 | 12.5 | 12.5 |  | 12.5 |  | 12.5 | 12.5 |  | 12.5 |  | 12.5 | 12.5 | 12.5
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MODA
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MODA - Monduran Dam (66/11kV) | [8 empty] | Supply |  | BUND - Bundaberg BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 1xMODA TX NO 2-66/11/3.3KV TRANSF 2(Standby);1xMODA TX NO 1-66/11/3.3KV TRANSF 1
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.0% W 0.7%,2025 S -0.7% W 0.7%,2026 S -0.3% W 1.0%,2027 S 0.4% W 1.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 1.4 MVA on 30/12/2022 at 21:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 1.5 | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.5 | 1.5
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 1.2 | 1.2 | 1.2 |  | 1.2 |  | 1.2 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.96 | 0.96 | 0.96 |  | 0.96 |  | 0.96 | 0.979 |  | 0.979 |  | 0.979 | 0.979 | 0.979
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 1.2 | 1.2 | 1.2 |  | 1.2 |  | 1.2 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 8.5 | 8.5 | 8.5 |  | 8.5 |  | 8.5 | 8.5 |  | 8.5 |  | 8.5 | 8.5 | 8.5
|  |  |  | Raw LAR (MVA) |  | 1.2 | 1.2 | 1.2 |  | 1.2 |  | 1.2 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 1.5 | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.5 | 1.5
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 3.1 | 3.1 | 0 |  | 3.1 |  | 3.1 | 3.1 |  | 3.1 |  | 3.1 | 3.1 | 3.1
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MOFO
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MOFO - Mount Fox (66/33kV) | [8 empty] | Supply |  | T047 - Ingham BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/33kV 0.63MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -4.0% W -1.5%2025 S -1.9% W -1.2%2026 S -1.5% W -1.0%2027 S -0.9% W -1.0
|  |  | Latest Peak Compensated Load | [5 empty] | 0.1 MVA on 13/07/2022 at 19:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 0.7 | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.7 | 0.7
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.9 | 0.9 | 0.9 |  | 0.9 |  | 0.9 | 0.756 |  | 0.756 |  | 0.756 | 0.756 | 0.756
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 7 | 7 | 7 |  | 7 |  | 7 | 7 |  | 7 |  | 7 | 7 | 7
|  |  |  | Raw LAR (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 0.63 | 0.63 | 0.63 |  | 0.63 |  | 0.63 | 0.63 |  | 0.63 |  | 0.63 | 0.63 | 0.63
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MOGA
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MOGA - Mt Garnet (66/22kV) | [8 empty] | Supply |  | TURK - Turkinje 66kV BSP
| Description |  |  |  | Region is Far North
Transformer size is 2x66/22kV 4MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.0% W -0.8%2025 S -0.9% W -0.6%2026 S -0.4% W -0.3%2027 S 0.2% W -0.2%
|  |  | Latest Peak Compensated Load | [5 empty] | 1.9 MVA on 15/07/2022 at 07:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 8.5 | 8.5 | 8.5 |  | 8.5 |  | 8.5 | 9.3 |  | 9.3 |  | 9.3 | 9.3 | 9.3
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 1.9 | 1.9 | 1.9 |  | 1.9 |  | 1.9 | 2 |  | 2 |  | 2 | 2 | 2
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.972 | 0.972 | 0.972 |  | 0.972 |  | 0.972 | 0.998 |  | 0.998 |  | 0.998 | 0.998 | 0.998
|  |  |  | ECC Rating (MVA) |  | 4.2 | 4.2 | 4.2 |  | 4.2 |  | 4.2 | 4.7 |  | 4.7 |  | 4.7 | 4.7 | 4.7
|  |  |  | 50 PoE Load (MVA) |  | 1.8 | 1.8 | 1.8 |  | 1.8 |  | 1.8 | 1.9 |  | 1.9 |  | 1.8 | 1.8 | 1.8
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 24 | 24 | 24 |  | 24 |  | 24 | 24 |  | 24 |  | 24 | 24 | 24
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 8 | 8 | 8 |  | 8 |  | 8 | 8 |  | 8 |  | 8 | 8 | 8
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 4 | 4 | 4 |  | 4 |  | 4 | 4 |  | 4 |  | 4 | 4 | 4
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MOLP
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MOLP - Mount Leyshon Pump (66/11kV) | [8 empty] | Supply |  | T095 - Millchester BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/11kV 0.25MVA
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 0.0%, 2024 S 0.0% W 0.0%, 2025 S 0.0% W 0.0%, 2026 S 0.0% W 0.0%, 2027 S 0.0% W 0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 0.1 MVA on 01/01/2022 at 17:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.82 | 0.82 | 0.82 |  | 0.82 |  | 0.82 | 0.85 |  | 0.85 |  | 0.85 | 0.85 | 0.85
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 271 | 271 | 271 |  | 271 |  | 271 | 271 |  | 271 |  | 271 | 271 | 271
|  |  |  | Raw LAR (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 0.25 | 0.25 | 0.25 |  | 0.25 |  | 0.25 | 0.25 |  | 0.25 |  | 0.25 | 0.25 | 0.25
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MOMO
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MOMO - Mt Molloy (66/22kV) | [8 empty] | Supply |  | TURK - Turkinje 66kV BSP
| Description |  |  |  | Region is Far North
Transformer size is 1x66/22kV 10/12.5MVA ONAN/ONAF;1x66/22kV 1.5MVA ONAN(Standby)
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.7% W -0.3%2025 S -0.6% W 0.0%,2026 S -0.1% W 0.2%,2027 S 0.6% W 0.3%
|  |  | Latest Peak Compensated Load | [5 empty] | 1.6 MVA on 05/02/2023 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 16.4 | 16.4 | 16.4 |  | 16.4 |  | 16.4 | 18 |  | 18 |  | 18 | 18 | 18
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 1.6 | 1.6 | 1.6 |  | 1.6 |  | 1.6 | 1.5 |  | 1.5 |  | 1.5 | 1.5 | 1.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.974 | 0.974 | 0.974 |  | 0.974 |  | 0.974 | 0.975 |  | 0.975 |  | 0.975 | 0.975 | 0.975
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 1.6 | 1.6 | 1.6 |  | 1.6 |  | 1.6 | 1.5 |  | 1.5 |  | 1.5 | 1.5 | 1.5
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 11.5 | 11.5 | 11.5 |  | 11.5 |  | 11.5 | 11.5 |  | 11.5 |  | 11.5 | 11.5 | 11.5
|  |  |  | Raw LAR (MVA) |  | 1.6 | 1.6 | 1.6 |  | 1.6 |  | 1.6 | 1.5 |  | 1.5 |  | 1.5 | 1.5 | 1.5
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 2.2 | 2.2 | 2.2 |  | 2.2 |  | 2.2 | 2.2 |  | 2.2 |  | 2.2 | 2.2 | 2.2
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 6.1 | 6.1 | 6.1 |  | 6.1 |  | 6.1 | 6.1 |  | 6.1 |  | 6.1 | 6.1 | 6.1
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 1.5 | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.5 | 1.5
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MOMR
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MOMR - Mt Morgan (66/11kV) | [8 empty] | Supply |  | RMES - Rockhampton Mesh
| Description |  |  |  | Region is Capricornia
Transformer size is 2x66/11kV 5/6.25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.1% W -1.1%2025 S -0.9% W -0.8%2026 S -0.5% W -0.3%2027 S 0.2% W -0.2%
|  |  | Latest Peak Compensated Load | [5 empty] | 3.4 MVA on 13/02/2023 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 15.8 | 15.8 | 15.8 |  | 15.8 |  | 15.8 | 18 |  | 18 |  | 18 | 18 | 18
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 3.7 | 3.6 | 3.6 |  | 3.6 |  | 3.7 | 3.4 |  | 3.4 |  | 3.4 | 3.3 | 3.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.987 | 0.987 | 0.987 |  | 0.987 |  | 0.987 | 0.995 |  | 0.995 |  | 0.995 | 0.995 | 0.995
|  |  |  | ECC Rating (MVA) |  | 8.7 | 8.7 | 8.7 |  | 8.7 |  | 8.7 | 9.3 |  | 9.3 |  | 9.3 | 9.3 | 9.3
|  |  |  | 50 PoE Load (MVA) |  | 3.3 | 3.3 | 3.3 |  | 3.3 |  | 3.3 | 3.2 |  | 3.2 |  | 3.2 | 3.1 | 3.1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 12 | 12 | 12 |  | 12 |  | 12 | 12 |  | 12 |  | 12 | 12 | 12
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 | 5 | 5
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MOMW
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MOMW - Mt Mowbullan (33/11kV) | [8 empty] | Supply |  | T002 - Dalby East BSP
| Description |  |  |  | Region is South West
Transformer size is 1x33/11kV 1MVA ON
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -1.8% W 0.1%,2025 S 0.1% W 0.3%, 2026 S 0.6% W 0.6%, 2027 S 1.3% W 0.6%
|  |  | Latest Peak Compensated Load | [5 empty] | 0.7 MVA on 10/06/2022 at 21:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.7 |  | 0.7 |  | 0.7 | 0.7 | 0.8
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.999 | 0.999 | 0.999 |  | 0.999 |  | 0.998 | 0.999 |  | 0.999 |  | 0.999 | 0.999 | 0.999
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.7 |  | 0.7 |  | 0.7 | 0.7 | 0.7
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 9.5 | 9.5 | 9.5 |  | 9.5 |  | 9.5 | 9.5 |  | 9.5 |  | 9.5 | 9.5 | 9.5
|  |  |  | Raw LAR (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.7 |  | 0.7 |  | 0.7 | 0.7 | 0.7
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MONT
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MONT - Monto (66/11kV) | [8 empty] | Supply |  | T026 - Biloela BSP
| Description |  |  |  | Region is Capricornia
Transformer size is 2x66/11kV 6.25MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.9% W -0.7%2025 S -0.9% W -1.0%2026 S -0.4% W -0.5%2027 S 0.3% W -0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 4.7 MVA on 13/02/2023 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 14 | 14 | 14 |  | 14 |  | 14 | 16.7 |  | 16.7 |  | 16.7 | 16.7 | 16.7
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 5.3 | 5.2 | 5.2 |  | 5.2 |  | 5.3 | 4 |  | 4 |  | 4 | 3.9 | 3.9
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.998 | 0.998 | 0.998 |  | 0.998 |  | 0.998 | 0.982 |  | 0.982 |  | 0.982 | 0.982 | 0.982
|  |  |  | ECC Rating (MVA) |  | 8 | 8 | 8 |  | 8 |  | 8 | 9.3 |  | 9.3 |  | 9.3 | 9.3 | 9.3
|  |  |  | 50 PoE Load (MVA) |  | 4.9 | 4.9 | 4.8 |  | 4.9 |  | 4.9 | 3.8 |  | 3.8 |  | 3.8 | 3.7 | 3.7
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 4.5 | 4.5 | 4.5 |  | 4.5 |  | 4.5 | 4.5 |  | 4.5 |  | 4.5 | 4.5 | 4.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 12.5 | 12.5 | 12.5 |  | 12.5 |  | 12.5 | 12.5 |  | 12.5 |  | 12.5 | 12.5 | 12.5
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 6.25 | 6.25 | 6.25 |  | 6.25 |  | 6.25 | 6.25 |  | 6.25 |  | 6.25 | 6.25 | 6.25
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MOOR
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MOOR - Moorvale (66/11kV) | [8 empty] | Supply |  | T198 - Broadlea BSP
| Description |  |  |  | Region is Mackay
Transformer size is 1x66/11kV 7.5/10MVA ON/OB
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.1% W -0.7%2025 S -0.8% W -0.2%2026 S -0.4% W 0.0%,2027 S 0.3% W 0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 6.1 MVA on 09/01/2023 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 10.5 | 10.5 | 10.5 |  | 10.5 |  | 10.5 | 11 |  | 11 |  | 11 | 11 | 11
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 6.1 | 6 | 6 |  | 6 |  | 6.1 | 6 |  | 5.9 |  | 5.9 | 5.9 | 5.9
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.987 | 0.987 | 0.987 |  | 0.987 |  | 0.987 | 0.99 |  | 0.99 |  | 0.99 | 0.99 | 0.99
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 5.9 | 5.9 | 5.9 |  | 5.9 |  | 5.9 | 5.7 |  | 5.7 |  | 5.7 | 5.7 | 5.7
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Hours PA > 95% Peak Load |  | 21.5 | 21.5 | 21.5 |  | 21.5 |  | 21.5 | 21.5 |  | 21.5 |  | 21.5 | 21.5 | 21.5
|  |  |  | Raw LAR (MVA) |  | 5.9 | 5.9 | 5.9 |  | 5.9 |  | 5.9 | 5.7 |  | 5.7 |  | 5.7 | 5.7 | 5.7
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 11.5 | 11.5 | 11.5 |  | 11.5 |  | 11.5 | 11.5 |  | 11.5 |  | 11.5 | 11.5 | 11.5
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 3.1 | 3.1 | 3.1 |  | 3.1 |  | 3.1 | 3.1 |  | 3.1 |  | 3.1 | 3.1 | 3.1
|  |  |  | Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MOPA
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MOPA - Mona Park (66/11kV) | [8 empty] | Supply |  | T193 - Clare South BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 2x66/11kV 4MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.8% W -0.6%2025 S -1.0% W -1.3%2026 S -0.3% W -0.8%2027 S 0.3% W -0.4%
|  |  | Latest Peak Compensated Load | [5 empty] | 4.3 MVA on 16/11/2022 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 7.6 | 7.6 | 11 |  | 11 |  | 11 | 8 |  | 8 |  | 8 | 11 | 11
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 5.4 | 5.4 | 5.4 |  | 5.4 |  | 5.4 | 2.9 |  | 2.9 |  | 2.9 | 2.9 | 2.8
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.895 | 0.895 | 0.895 |  | 0.895 |  | 0.895 | 0.884 |  | 0.884 |  | 0.884 | 0.884 | 0.884
|  |  |  | ECC Rating (MVA) |  | 4 | 4 | 0 |  | 0 |  | 0 | 4 |  | 4 |  | 4 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 5.3 | 5.2 | 5.2 |  | 5.2 |  | 5.3 | 2.7 |  | 2.7 |  | 2.7 | 2.7 | 2.7
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 136.5 | 136.5 | 136.5 |  | 136.5 |  | 136.5 | 136.5 |  | 136.5 |  | 136.5 | 136.5 | 136.5
|  |  |  | Raw LAR (MVA) |  | 1.3 | 1.2 | 5.2 |  | 5.2 |  | 5.3 | [5 empty] | 2.7 | 2.7
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 2.3 | 2.3 | 2.3 |  | 2.3 |  | 2.3 | 2.3 |  | 2.3 |  | 2.3 | 2.3 | 2.3
|  |  |  | Mobile Plant Avail (MVA) |  | 0.8 | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.8 | 0.8
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | LARc (MVA) |  |  |  | 2.1 |  | 2.1 |  | 2.2
|  |  |  | LARc (MW) |  |  |  | 1.9 |  | 1.9 |  | 2
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | No |  | No |  | No | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MORO
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MORO - Mount Rooper (66/11kV) | [8 empty] | Supply |  | PROS - Proserpine BSP
| Description |  |  |  | Region is Mackay
Transformer size is 1x66/11kV 5MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.9% W -0.4%2025 S -0.9% W -0.4%2026 S -0.5% W -0.2%2027 S 0.1% W -0.2%
|  |  | Latest Peak Compensated Load | [5 empty] | 1.1 MVA on 15/12/2022 at 10:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 5.8 | 5.8 | 5.8 |  | 5.8 |  | 5.8 | 6.4 |  | 6.4 |  | 6.4 | 6.4 | 6.4
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 1.3 | 1.3 | 1.3 |  | 1.3 |  | 1.3 | 0.8 |  | 0.8 |  | 0.8 | 0.8 | 0.8
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.978 | 0.978 | 0.978 |  | 0.978 |  | 0.978 | 0.983 |  | 0.983 |  | 0.983 | 0.983 | 0.983
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 1.1 | 1.1 | 1.1 |  | 1.1 |  | 1.1 | 0.7 |  | 0.7 |  | 0.7 | 0.7 | 0.7
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 18.5 | 18.5 | 18.5 |  | 18.5 |  | 18.5 | 18.5 |  | 18.5 |  | 18.5 | 18.5 | 18.5
|  |  |  | Raw LAR (MVA) |  | 1.1 | 1.1 | 1.1 |  | 1.1 |  | 1.1 | 0.7 |  | 0.7 |  | 0.7 | 0.7 | 0.7
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 1.1 | 1.1 | 1.1 |  | 1.1 |  | 1.1 | 1.1 |  | 1.1 |  | 1.1 | 1.1 | 1.1
|  |  |  | Capacity for Embedded Generation (MVA) |  | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 | 5 | 5
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MOSI
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MOSI - Mt Sibley (33/11kV) | [8 empty] | Supply |  | T043 - South Toowoomba BSP
| Description |  |  |  | Region is South West
Transformer size is 1x33/11kV 3MVA ON;1x33/11KV 5MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.8% W -0.3%2025 S -0.7% W -0.1%2026 S -0.2% W 0.2%,2027 S 0.4% W 0.3%
|  |  | Latest Peak Compensated Load | [5 empty] | 4.2 MVA on 09/01/2023 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 6.3 | 6.3 | 6.3 |  | 6.3 |  | 6.3 | 6.3 |  | 6.3 |  | 6.3 | 6.3 | 6.3
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 5.2 | 5.1 | 5.1 |  | 5.1 |  | 5.2 | 4.2 |  | 4.2 |  | 4.2 | 4.2 | 4.2
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.931 | 0.931 | 0.931 |  | 0.931 |  | 0.931 | 0.946 |  | 0.946 |  | 0.946 | 0.946 | 0.946
|  |  |  | ECC Rating (MVA) |  | 3.3 | 3.3 | 3.3 |  | 3.3 |  | 3.3 | 3.5 |  | 3.5 |  | 3.5 | 3.5 | 3.5
|  |  |  | 50 PoE Load (MVA) |  | 4.5 | 4.4 | 4.4 |  | 4.5 |  | 4.5 | 4.1 |  | 4.1 |  | 4.1 | 4.1 | 4.1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 226 | 226 | 226 |  | 226 |  | 226 | 226 |  | 226 |  | 226 | 226 | 226
|  |  |  | Raw LAR (MVA) |  | 1.2 | 1.1 | 1.1 |  | 1.2 |  | 1.2 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0.8 | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.8 | 0.8
|  |  |  | Mobile Plant Avail (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 3 | 3 | 3 |  | 3 |  | 3 | 3 |  | 3 |  | 3 | 3 | 3
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MOSS
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MOSS - Mossman (66/22kV) | [8 empty] | Supply |  | TURK - Turkinje 66kV BSP
| Description |  |  |  | Region is Far North
Transformer size is 2x66/22kV 10MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 11.3 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.5% W -0.7%2025 S -0.6% W -0.6%2026 S -0.0% W -0.2%2027 S 0.6% W -0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 8.3 MVA on 14/12/2022 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 18.5 | 18.5 | 35.2 |  | 35.2 |  | 35.2 | 20.6 |  | 20.6 |  | 35.2 | 35.2 | 35.2
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 8.4 | 8.4 | 8.4 |  | 8.4 |  | 8.6 | 7.2 |  | 7.1 |  | 7.1 | 7.1 | 7.1
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.996 | 0.996 | 0.996 |  | 0.996 |  | 0.996 | 0.993 |  | 0.993 |  | 0.993 | 0.993 | 0.993
|  |  |  | ECC Rating (MVA) |  | 9.3 | 9.3 | 0 |  | 0 |  | 0 | 10.3 |  | 10.3 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 8 | 8 | 8 |  | 8 |  | 8.2 | 6.9 |  | 6.8 |  | 6.8 | 6.8 | 6.7
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.4 | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Hours PA > 95% Peak Load |  | 141 | 141 | 141 |  | 141 |  | 141 | 141 |  | 141 |  | 141 | 141 | 141
|  |  |  | Raw LAR (MVA) |  |  |  | 8 |  | 8 |  | 8.2 |  |  |  |  | 6.8 | 6.8 | 6.7
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 4 | 4 | 4 |  | 4 |  | 4 | 4 |  | 4 |  | 4 | 4 | 4
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 0 | 0 | 24 |  | 24 |  | 24 | 0 |  | 0 |  | 24 | 24 | 24
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | LARc (MVA) |  |  |  | 4 |  | 4 |  | 4.2 |  |  |  |  | 2.8 | 2.8 | 2.7
|  |  |  | LARc (MW) |  |  |  | 4 |  | 4 |  | 4.2 |  |  |  |  | 2.8 | 2.8 | 2.7
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | No |  | No |  | No | Yes |  | Yes |  | No | No | No
Return to Index

## MOUR
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MOUR - Moura (11/22kV) | [8 empty] | Supply |  | T027 - Moura BSP
| Description |  |  |  | Region is Capricornia
Transformer size is 2x11/22kV 7.5/10 MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.2% W -0.7%2025 S -1.1% W -0.5%2026 S -0.6% W -0.2%2027 S 0.1% W -0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 8.9 MVA on 20/03/2023 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 20 | 20 | 20 |  | 20 |  | 20 | 20 |  | 20 |  | 20 | 20 | 20
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 14.6 | 15 | 14.9 |  | 14.9 |  | 15 | 11.1 |  | 11.6 |  | 12.1 | 12.1 | 12.1
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.987 | 0.987 | 0.987 |  | 0.987 |  | 0.987 | 0.999 |  | 0.999 |  | 0.999 | 0.999 | 0.999
|  |  |  | ECC Rating (MVA) |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10
|  |  |  | 50 PoE Load (MVA) |  | 14 | 14.5 | 14.4 |  | 14.4 |  | 14.5 | 10.6 |  | 11.1 |  | 11.6 | 11.6 | 11.6
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.7 | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.5 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  |  | Hours PA > 95% Peak Load |  | 16 | 16 | 16 |  | 16 |  | 16 | 16 |  | 16 |  | 16 | 16 | 16
|  |  |  | Raw LAR (MVA) |  | 4 | 4.5 | 4.4 |  | 4.4 |  | 4.5 | 0.6 |  | 1.1 |  | 1.6 | 1.6 | 1.6
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
Capacity for Embedded Generation (MVA)
Firm Capacity for Embedded Generation (MVA)
|  |  |  | LARc (MVA) |  | 4 | 4.5 | 4.4 |  | 4.4 |  | 4.5 | 0.6 |  | 1.1 |  | 1.6 | 1.6 | 1.6
|  |  |  | LARc (MW) |  | 3.9 | 4.4 | 4.3 |  | 4.3 |  | 4.4 | 0.6 |  | 1.1 |  | 1.6 | 1.6 | 1.6
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | No | No | No |  | No |  | No | No |  | No |  | No | No | No
Return to Index

## MURG
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MURG - Murgon (66/11kV) | [8 empty] | Supply |  | KILK - Kilkivan BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 2x66/11kV 8.5/12.5MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.0% W -0.6%2025 S -0.8% W -0.4%2026 S -0.3% W -0.1%2027 S 0.3% W -0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 14.2 MVA on 13/02/2023 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 29.6 | 29.6 | 29.6 |  | 29.6 |  | 29.6 | 35.4 |  | 35.4 |  | 35.4 | 35.4 | 35.4
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 14.8 | 15.2 | 15.1 |  | 15.2 |  | 15.3 | 13.5 |  | 13.9 |  | 13.8 | 13.8 | 13.8
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.965 | 0.965 | 0.965 |  | 0.965 |  | 0.965 | 0.979 |  | 0.979 |  | 0.979 | 0.979 | 0.979
|  |  |  | ECC Rating (MVA) |  | 17 | 17 | 17 |  | 17 |  | 17 | 18.7 |  | 18.7 |  | 18.7 | 18.7 | 18.7
|  |  |  | 50 PoE Load (MVA) |  | 13.6 | 14 | 13.9 |  | 14 |  | 14.1 | 12.6 |  | 12.9 |  | 12.9 | 12.9 | 12.9
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.7 | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  |  | Hours PA > 95% Peak Load |  | 3 | 3 | 3 |  | 3 |  | 3 | 3 |  | 3 |  | 3 | 3 | 3
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 12.1 | 12.1 | 12.1 |  | 12.1 |  | 12.1 | 12.1 |  | 12.1 |  | 12.1 | 12.1 | 12.1
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 5.8 | 5.8 | 5.8 |  | 5.8 |  | 5.8 | 5.8 |  | 5.8 |  | 5.8 | 5.8 | 5.8
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MUTA
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MUTA - Mutarnee (66/11kV) | [8 empty] | Supply |  | T047 - Ingham BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/11kV 1MVA ON
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.0% W -0.5%2025 S -0.9% W -0.3%2026 S -0.4% W 0.0%,2027 S 0.3% W 0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 0.4 MVA on 24/11/2022 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 1.1 | 1.1 | 1.1 |  | 1.1 |  | 1.1 | 1.1 |  | 1.1 |  | 1.1 | 1.1 | 1.1
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 0.4 | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.966 | 0.966 | 0.966 |  | 0.966 |  | 0.966 | 0.981 |  | 0.981 |  | 0.981 | 0.981 | 0.981
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 0.4 | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 4 | 4 | 4 |  | 4 |  | 4 | 4 |  | 4 |  | 4 | 4 | 4
|  |  |  | Raw LAR (MVA) |  | 0.4 | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MUTO
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MUTO - Mundubbera Town (66/11kV) | [8 empty] | Supply |  | ISIS - Isis BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 1x66/11kV 16/20MVA ONAN/ONAF;1xMUTO 66/11kV 16/20MVA ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.9% W -0.5%2025 S -0.9% W -0.4%2026 S -0.4% W -0.1%2027 S 0.3% W 0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 6.1 MVA on 13/02/2023 at 17:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 49.4 | 49.4 | 49.4 |  | 49.4 |  | 49.4 | 54.6 |  | 54.6 |  | 54.6 | 54.6 | 54.6
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 6.3 | 6.3 | 6.3 |  | 6.3 |  | 6.3 | 5 |  | 5 |  | 4.9 | 4.9 | 4.9
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.995 | 0.996 | 0.996 |  | 0.996 |  | 0.995 | 0.893 |  | 0.893 |  | 0.893 | 0.893 | 0.893
|  |  |  | ECC Rating (MVA) |  | 28.4 | 28.4 | 28.4 |  | 28.4 |  | 28.4 | 29.9 |  | 29.9 |  | 29.9 | 29.9 | 29.9
|  |  |  | 50 PoE Load (MVA) |  | 6 | 6 | 6 |  | 6 |  | 6 | 4.7 |  | 4.7 |  | 4.6 | 4.6 | 4.6
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 12.5 | 12.5 | 12.5 |  | 12.5 |  | 12.5 | 12.5 |  | 12.5 |  | 12.5 | 12.5 | 12.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 32 | 32 | 32 |  | 32 |  | 32 | 32 |  | 32 |  | 32 | 32 | 32
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 16 | 16 | 16 |  | 16 |  | 16 | 16 |  | 16 |  | 16 | 16 | 16
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## NANA
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | NANA - Nanango (66/11kV) | [8 empty] | Supply |  | H018 - Tarong BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 2x66/11kV 5/6.25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.8% W -0.5%2025 S -0.8% W -0.5%2026 S -0.3% W -0.1%2027 S 0.4% W -0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 7 MVA on 12/02/2023 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 13.7 | 13.7 | 13.7 |  | 13.7 |  | 13.7 | 15.6 |  | 15.6 |  | 15.6 | 15.6 | 15.6
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 7.3 | 7.3 | 7.2 |  | 7.3 |  | 7.3 | 7 |  | 6.9 |  | 6.9 | 6.9 | 6.9
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.986 | 0.986 | 0.986 |  | 0.986 |  | 0.986 | 0.993 |  | 0.993 |  | 0.993 | 0.993 | 0.993
|  |  |  | ECC Rating (MVA) |  | 6.8 | 6.8 | 6.8 |  | 6.8 |  | 6.8 | 7.8 |  | 7.8 |  | 7.8 | 7.8 | 7.8
|  |  |  | 50 PoE Load (MVA) |  | 6.9 | 6.8 | 6.8 |  | 6.8 |  | 6.9 | 6.5 |  | 6.5 |  | 6.4 | 6.4 | 6.4
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Hours PA > 95% Peak Load |  | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 | 5 | 5
|  |  |  | Raw LAR (MVA) |  | 0.1 | [5 empty] | 0.1
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0.8 | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.8 | 0.8
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 | 5 | 5
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## NAND
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | NAND - Nandi (33/11kV) | [8 empty] | Supply |  | T002 - Dalby East BSP
| Description |  |  |  | Region is South West
Transformer size is 1x33/11 3.15MVA ON;1x33/11kV 1MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.9% W -0.2%2025 S -0.8% W -0.2%2026 S -0.3% W 0.1%,2027 S 0.3% W 0.2%
|  |  | Latest Peak Compensated Load | [5 empty] | 1.3 MVA on 01/03/2023 at 17:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 | 2 | 2
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 1.3 | 1.3 | 1.3 |  | 1.3 |  | 1.3 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.919 | 0.919 | 0.919 |  | 0.919 |  | 0.919 | 0.973 |  | 0.973 |  | 0.973 | 0.973 | 0.973
|  |  |  | ECC Rating (MVA) |  | 1.1 | 1.1 | 1.1 |  | 1.1 |  | 1.1 | 1.1 |  | 1.1 |  | 1.1 | 1.1 | 1.1
|  |  |  | 50 PoE Load (MVA) |  | 1.2 | 1.2 | 1.2 |  | 1.2 |  | 1.2 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 | 5 | 5
|  |  |  | Raw LAR (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 3.15 | 3.15 | 3.15 |  | 3.15 |  | 3.15 | 3.15 |  | 3.15 |  | 3.15 | 3.15 | 3.15
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## NEBO
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | NEBO - Nebo (132/11kV) | [8 empty] | Supply |  | QNEB - Nebo TCP
| Description |  |  |  | Region is Mackay
Transformer size is 1xNEBOSS 3T 132/11KV TRANSF 3 3T;1xNEBOSS TRANSF 4
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.9% W -0.5%2025 S -0.9% W -0.3%2026 S -0.4% W -0.0%2027 S 0.4% W 0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 3.5 MVA on 13/02/2023 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 3.6 | 3.6 | 3.5 |  | 3.6 |  | 3.6 | 3.1 |  | 3.1 |  | 3.1 | 3.1 | 3.1
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.993 | 0.993 | 0.993 |  | 0.993 |  | 0.993 | 0.999 |  | 0.999 |  | 0.999 | 0.999 | 0.999
|  |  |  | ECC Rating (MVA) |  | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 | 5 | 5
|  |  |  | 50 PoE Load (MVA) |  | 3.5 | 3.4 | 3.4 |  | 3.4 |  | 3.5 | 2.9 |  | 2.9 |  | 2.9 | 2.9 | 2.9
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 5.5 | 5.5 | 5.5 |  | 5.5 |  | 5.5 | 5.5 |  | 5.5 |  | 5.5 | 5.5 | 5.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
Capacity for Embedded Generation (MVA)
Firm Capacity for Embedded Generation (MVA)
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## NESM
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | NESM - Neil Smith (66/11kV) | [8 empty] | Supply |  | TMES - Townsville Mesh
| Description |  |  |  | Region is Nth Queensland
Transformer size is 2x66/11kV 15/20/25MVA ON/OB/OFB
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.6% W 0.0%,2025 S -0.8% W -0.4%2026 S -0.3% W 0.1%,2027 S 0.6% W 0.5%
|  |  | Latest Peak Compensated Load | [5 empty] | 15.4 MVA on 16/03/2023 at 13:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 65.5 | 65.5 | 65.5 |  | 65.5 |  | 65.5 | 68 |  | 68 |  | 68 | 68 | 68
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 15.7 | 15.5 | 15.5 |  | 15.6 |  | 15.8 | 10.1 |  | 10.1 |  | 10.4 | 10.4 | 10.2
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.993 | 0.993 | 0.993 |  | 0.993 |  | 0.993 | 1 |  | 1 |  | 0.97 | 0.97 | 1
|  |  |  | ECC Rating (MVA) |  | 36.8 | 36.8 | 36.8 |  | 36.8 |  | 36.8 | 37.4 |  | 37.4 |  | 37.4 | 37.4 | 37.4
|  |  |  | 50 PoE Load (MVA) |  | 15 | 14.8 | 14.8 |  | 14.9 |  | 15.1 | 10.1 |  | 10.1 |  | 10.1 | 10.1 | 10.1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.8 | 0.7 | 0.7 |  | 0.7 |  | 0.8 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | Hours PA > 95% Peak Load |  | 28.5 | 28.5 | 28.5 |  | 28.5 |  | 28.5 | 28.5 |  | 28.5 |  | 28.5 | 28.5 | 28.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 18.4 | 18.4 | 18.4 |  | 18.4 |  | 18.4 | 18.4 |  | 18.4 |  | 18.4 | 18.4 | 18.4
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 9.2 | 9.2 | 9.2 |  | 9.2 |  | 9.2 | 9.2 |  | 9.2 |  | 9.2 | 9.2 | 9.2
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## NOCL
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | NOCL - North Cloncurry (66/11kV) | [8 empty] | Supply |  | CHUM - Chumvale BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/11kV 5/6.5MVA ONAN/ONAF;1x66/11kV 6.5/5MVA ONAF/ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.5% W -0.8%2025 S -1.5% W -0.7%2026 S -1.1% W -0.5%2027 S -0.5% W -0.3
|  |  | Latest Peak Compensated Load | [5 empty] | 3.5 MVA on 07/12/2022 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 10.8 | 10.8 | 10.8 |  | 10.8 |  | 10.8 | 13.1 |  | 13.1 |  | 13.1 | 13.1 | 13.1
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 3.9 | 3.8 | 3.8 |  | 3.8 |  | 3.8 | 2.4 |  | 2.4 |  | 2.3 | 2.3 | 2.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.997 | 0.997 | 0.997 |  | 0.997 |  | 0.997 | 0.999 |  | 0.999 |  | 0.999 | 0.999 | 0.999
|  |  |  | ECC Rating (MVA) |  | 6.2 | 6.2 | 6.2 |  | 6.2 |  | 6.2 | 7.2 |  | 7.2 |  | 7.2 | 7.2 | 7.2
|  |  |  | 50 PoE Load (MVA) |  | 3.6 | 3.6 | 3.5 |  | 3.5 |  | 3.5 | 2.3 |  | 2.3 |  | 2.2 | 2.2 | 2.2
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 446 | 446 | 446 |  | 446 |  | 446 | 446 |  | 446 |  | 446 | 446 | 446
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 11 | 11 | 11 |  | 11 |  | 11 | 11 |  | 11 |  | 11 | 11 | 11
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 | 5 | 5
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## NOMA
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | NOMA - North Mackay (33/11kV) | [8 empty] | Supply |  | GZSA - Glenella ZS Accumulator
| Description |  |  |  | Region is Mackay
Transformer size is 2x33/11kV 15/20MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.8% W 0.0%,2025 S -0.7% W 0.3%,2026 S -0.2% W 0.6%,2027 S 0.6% W 0.5%
|  |  | Latest Peak Compensated Load | [5 empty] | 24.8 MVA on 02/02/2023 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 47.7 | 47.7 | 47.7 |  | 47.7 |  | 47.7 | 53.1 |  | 53.1 |  | 53.1 | 53.1 | 53.1
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 25.1 | 24.9 | 24.9 |  | 25 |  | 25.3 | 17.7 |  | 17.7 |  | 17.8 | 17.9 | 17.9
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.999 | 0.999 | 0.999 |  | 0.999 |  | 0.999 | 0.999 |  | 0.999 |  | 0.999 | 0.999 | 0.999
|  |  |  | ECC Rating (MVA) |  | 26.9 | 26.9 | 26.9 |  | 26.9 |  | 26.9 | 29.1 |  | 29.1 |  | 29.1 | 29.1 | 29.1
|  |  |  | 50 PoE Load (MVA) |  | 24 | 23.8 | 23.8 |  | 23.9 |  | 24.2 | 16.7 |  | 16.7 |  | 16.7 | 16.8 | 16.9
|  |  |  | 50 PoE Load > 95% (MVA) |  | 1.2 | 1.2 | 1.2 |  | 1.2 |  | 1.2 | 0.8 |  | 0.8 |  | 0.8 | 0.8 | 0.8
|  |  |  | Hours PA > 95% Peak Load |  | 6.5 | 6.5 | 6.5 |  | 6.5 |  | 6.5 | 6.5 |  | 6.5 |  | 6.5 | 6.5 | 6.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 30 | 30 | 30 |  | 30 |  | 30 | 30 |  | 30 |  | 30 | 30 | 30
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 15 | 15 | 15 |  | 15 |  | 15 | 15 |  | 15 |  | 15 | 15 | 15
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## NORM
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | NORM - Normanton (66/22kV) | [8 empty] | Supply |  | GEOR - Georgetown BSP
| Description |  |  |  | Region is Far North
Transformer size is 2xNORM 66/22/6.6KV 5MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 5.3 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.8% W -0.3%2025 S -0.7% W -0.2%2026 S -0.2% W 0.1%,2027 S 0.5% W 0.2%
|  |  | Latest Peak Compensated Load | [5 empty] | 4.7 MVA on 16/11/2022 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 10.2 | 10.2 | 10.2 |  | 10.2 |  | 10.2 | 10.2 |  | 10.2 |  | 10.2 | 10.2 | 10.2
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 4.7 | 4.7 | 4.7 |  | 4.7 |  | 4.7 | 4.2 |  | 4.2 |  | 4.2 | 4.2 | 4.2
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.998 | 0.998 | 0.998 |  | 0.998 |  | 0.998 | 0.998 |  | 0.998 |  | 0.998 | 0.998 | 0.998
|  |  |  | ECC Rating (MVA) |  | 5.2 | 5.2 | 5.2 |  | 5.2 |  | 5.2 | 5.8 |  | 5.8 |  | 5.8 | 5.8 | 5.8
|  |  |  | 50 PoE Load (MVA) |  | 4.6 | 4.6 | 4.6 |  | 4.6 |  | 4.7 | 4.1 |  | 4.1 |  | 4.1 | 4.1 | 4.1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 28.5 | 28.5 | 28.5 |  | 28.5 |  | 28.5 | 28.5 |  | 28.5 |  | 28.5 | 28.5 | 28.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 1.3 | 1.3 | 1.3 |  | 1.3 |  | 1.3 | 1.3 |  | 1.3 |  | 1.3 | 1.3 | 1.3
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 1.3 | 1.3 | 1.3 |  | 1.3 |  | 1.3 | 1.3 |  | 1.3 |  | 1.3 | 1.3 | 1.3
|  |  |  | Capacity for Embedded Generation (MVA) |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 | 5 | 5
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## NORW
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | NORW - Norwin (33/11kV) | [8 empty] | Supply |  | YARA - Yarranlea BSP
| Description |  |  |  | Region is South West
Transformer size is 2x33/11kV 3MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.0% W -0.3%2025 S -0.8% W -0.2%2026 S -0.3% W 0.1%,2027 S 0.3% W 0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 4 MVA on 06/02/2023 at 11:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 6.9 | 6.9 | 6.9 |  | 6.9 |  | 6.9 | 7.9 |  | 7.9 |  | 7.9 | 7.9 | 7.9
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 3.4 | 3.4 | 3.4 |  | 3.4 |  | 3.4 | 1 |  | 1 |  | 1 | 1 | 1
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.812 | 0.812 | 0.812 |  | 0.812 |  | 0.812 | 0.956 |  | 0.956 |  | 0.956 | 0.956 | 0.956
|  |  |  | ECC Rating (MVA) |  | 4 | 4 | 4 |  | 4 |  | 4 | 4.5 |  | 4.5 |  | 4.5 | 4.5 | 4.5
|  |  |  | 50 PoE Load (MVA) |  | 3.1 | 3 | 3 |  | 3 |  | 3.1 | 0.9 |  | 0.9 |  | 0.9 | 0.9 | 0.9
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 15 | 15 | 15 |  | 15 |  | 15 | 15 |  | 15 |  | 15 | 15 | 15
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 6 | 6 | 6 |  | 6 |  | 6 | 6 |  | 6 |  | 6 | 6 | 6
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 3 | 3 | 3 |  | 3 |  | 3 | 3 |  | 3 |  | 3 | 3 | 3
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## NOST
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | NOST - North Street (33/11kV) | [8 empty] | Supply |  | T116 - Torrington BSP
| Description |  |  |  | Region is South West
Transformer size is 3x33/11kV 10MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.9% W -0.6%2025 S -1.0% W -0.4%2026 S -0.4% W -0.1%2027 S 0.1% W -0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 23.2 MVA on 04/07/2022 at 17:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 31.1 | 31.1 | 31.1 |  | 51.9 |  | 51.9 | 34.5 |  | 34.5 |  | 34.5 | 57.5 | 57.5
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 18.3 | 18.1 | 18.1 |  | 22.6 |  | 27.4 | 26.5 |  | 26.3 |  | 26.2 | 29.2 | 32.8
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.928 | 0.928 | 0.928 |  | 0.924 |  | 0.924 | 0.901 |  | 0.901 |  | 0.901 | 0.907 | 0.907
|  |  |  | ECC Rating (MVA) |  | 23.6 | 23.6 | 23.6 |  | 47.3 |  | 47.3 | 26.5 |  | 26.5 |  | 26.5 | 52.9 | 52.9
|  |  |  | 50 PoE Load (MVA) |  | 17.3 | 17.1 | 17.1 |  | 21.6 |  | 26.4 | 24.6 |  | 24.5 |  | 24.4 | 27.4 | 31
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.9 | 0.9 | 0.9 |  | 1.1 |  | 1.3 | 1.2 |  | 1.2 |  | 1.2 | 1.4 | 1.6
|  |  |  | Hours PA > 95% Peak Load |  | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 | 5 | 5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 10 | 10 | 10 |  | 30 |  | 30 | 10 |  | 10 |  | 10 | 30 | 30
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 15 |  | 15 | 0 |  | 0 |  | 0 | 15 | 15
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## OAKE
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | OAKE - Oakey (33/11kV) | [8 empty] | Supply |  | T189 - Oakey BSP
| Description |  |  |  | Region is South West
Transformer size is 2x33/11kV 20/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.0% W -0.6%2025 S -0.9% W -0.4%2026 S -0.4% W -0.1%2027 S 0.2% W -0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 15 MVA on 13/02/2023 at 17:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 49.7 | 49.7 | 49.7 |  | 49.7 |  | 49.7 | 56.3 |  | 56.3 |  | 56.3 | 56.3 | 56.3
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 15.6 | 15.4 | 15.4 |  | 15.4 |  | 15.6 | 15.6 |  | 15.6 |  | 15.5 | 15.5 | 15.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 1 | 1 | 1 |  | 1 |  | 1 | 0.999 |  | 0.999 |  | 0.999 | 0.999 | 0.999
|  |  |  | ECC Rating (MVA) |  | 28.4 | 28.4 | 28.4 |  | 28.4 |  | 28.4 | 32.3 |  | 32.3 |  | 32.3 | 32.3 | 32.3
|  |  |  | 50 PoE Load (MVA) |  | 15.8 | 15.7 | 15.6 |  | 15.6 |  | 15.8 | 14.9 |  | 14.8 |  | 14.7 | 14.7 | 14.7
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.8 | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.7 |  | 0.7 |  | 0.7 | 0.7 | 0.7
|  |  |  | Hours PA > 95% Peak Load |  | 8 | 8 | 8 |  | 8 |  | 8 | 8 |  | 8 |  | 8 | 8 | 8
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 40 | 40 | 40 |  | 40 |  | 40 | 40 |  | 40 |  | 40 | 40 | 40
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 20 | 20 | 20 |  | 20 |  | 20 | 20 |  | 20 |  | 20 | 20 | 20
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## OONN
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | OONN - Oonoonba (66/11kV) | [8 empty] | Supply |  | TMES - Townsville Mesh
| Description |  |  |  | Region is Nth Queensland
Transformer size is 2x66/11kV 19/26/32MVA ONAN/ODAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.0% W 1.2%,2025 S 0.1% W 1.3%, 2026 S 0.8% W 1.6%, 2027 S 0.8% W 0.8%
|  |  | Latest Peak Compensated Load | [5 empty] | 14.2 MVA on 14/03/2023 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 74.2 | 74.2 | 74.2 |  | 74.2 |  | 74.2 | 77.6 |  | 77.6 |  | 77.6 | 77.6 | 77.6
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 14.5 | 14.6 | 14.7 |  | 14.8 |  | 15 | 9.9 |  | 10.1 |  | 10.2 | 10.3 | 10.4
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.996 | 0.996 | 0.996 |  | 0.996 |  | 0.996 | 0.997 |  | 0.997 |  | 0.997 | 0.997 | 0.997
|  |  |  | ECC Rating (MVA) |  | 41.2 | 41.2 | 41.2 |  | 41.2 |  | 41.2 | 42.8 |  | 42.8 |  | 42.8 | 42.8 | 42.8
|  |  |  | 50 PoE Load (MVA) |  | 14 | 14.1 | 14.2 |  | 14.3 |  | 14.5 | 9.6 |  | 9.7 |  | 9.8 | 10 | 10.1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.7 | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | Hours PA > 95% Peak Load |  | 10.5 | 10.5 | 10.5 |  | 10.5 |  | 10.5 | 10.5 |  | 10.5 |  | 10.5 | 10.5 | 10.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 38 | 38 | 38 |  | 38 |  | 38 | 38 |  | 38 |  | 38 | 38 | 38
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 19 | 19 | 19 |  | 19 |  | 19 | 19 |  | 19 |  | 19 | 19 | 19
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## OWAN
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | OWAN - Owanyilla (66/11kV) | [8 empty] | Supply |  | MARY - Maryborough BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 1x66/11kV 10MVA ONAN;1xOWAN 66/11kV 10 MVA ONAN RG91765711
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.1% W -1.0%2025 S -1.0% W -1.0%2026 S -0.3% W -0.5%2027 S 0.4% W -0.5%
|  |  | Latest Peak Compensated Load | [5 empty] | 4.6 MVA on 13/02/2023 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 22 | 22 | 22 |  | 22 |  | 22 | 22 |  | 22 |  | 22 | 22 | 22
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 5.1 | 5.1 | 5.7 |  | 6.3 |  | 6.4 | 3.6 |  | 3.6 |  | 4.2 | 4.9 | 4.9
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.967 | 0.967 | 0.967 |  | 0.967 |  | 0.967 | 0.99 |  | 0.977 |  | 0.977 | 0.977 | 0.977
|  |  |  | ECC Rating (MVA) |  | 12 | 12 | 12 |  | 12 |  | 12 | 13 |  | 13 |  | 13 | 13 | 13
|  |  |  | 50 PoE Load (MVA) |  | 4.9 | 4.8 | 5.5 |  | 6.1 |  | 6.2 | 3.5 |  | 3.4 |  | 4.1 | 4.7 | 4.7
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.3 |  | 0.3 |  | 0.3 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 14 | 14 | 14 |  | 14 |  | 14 | 14 |  | 14 |  | 14 | 14 | 14
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 18 | 18 | 18 |  | 18 |  | 18 | 18 |  | 18 |  | 18 | 18 | 18
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 8 | 8 | 8 |  | 8 |  | 8 | 8 |  | 8 |  | 8 | 8 | 8
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## PAMP
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | PAMP - Pampas (33/11kV) | [8 empty] | Supply |  | YARA - Yarranlea BSP
| Description |  |  |  | Region is South West
Transformer size is 2x33/11kV 5MVA ON
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.9% W -0.3%2025 S -0.8% W -0.8%2026 S -0.3% W -0.4%2027 S 0.3% W -0.3%
|  |  | Latest Peak Compensated Load | [5 empty] | 7.1 MVA on 03/02/2023 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 7.4 | 7.3 | 7.3 |  | 7.3 |  | 7.4 | 3.7 |  | 3.7 |  | 3.7 | 3.6 | 3.6
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.869 | 0.869 | 0.869 |  | 0.869 |  | 0.869 | 0.869 |  | 0.869 |  | 0.854 | 0.869 | 0.869
|  |  |  | ECC Rating (MVA) |  | 5.5 | 5.5 | 5.5 |  | 5.5 |  | 5.5 | 5.5 |  | 5.5 |  | 5.5 | 5.5 | 5.5
|  |  |  | 50 PoE Load (MVA) |  | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6 | 3.5 |  | 3.5 |  | 3.5 | 3.4 | 3.4
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 3 | 3 | 3 |  | 3 |  | 3 | 3 |  | 3 |  | 3 | 3 | 3
|  |  |  | Raw LAR (MVA) |  | 1.1 | 1.1 | 1.1 |  | 1.1 |  | 1.1
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## PAND
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | PAND - Pandoin (66/22kV) | [8 empty] | Supply |  | RMES - Rockhampton Mesh
| Description |  |  |  | Region is Capricornia
Transformer size is 2x66/22kV 8/10MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.0% W -0.6%2025 S -0.8% W -0.3%2026 S -0.4% W -0.1%2027 S 0.3% W 0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 11.5 MVA on 12/02/2023 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 23.2 | 23.2 | 23.2 |  | 23.2 |  | 23.2 | 26.6 |  | 26.6 |  | 26.6 | 26.6 | 26.6
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 11.8 | 11.7 | 11.7 |  | 11.7 |  | 11.8 | 9.4 |  | 9.4 |  | 9.3 | 9.3 | 9.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.985 | 0.985 | 0.985 |  | 0.985 |  | 0.985 | 0.998 |  | 0.998 |  | 0.998 | 0.998 | 0.998
|  |  |  | ECC Rating (MVA) |  | 13.6 | 13.6 | 13.6 |  | 13.6 |  | 13.6 | 14.5 |  | 14.5 |  | 14.5 | 14.5 | 14.5
|  |  |  | 50 PoE Load (MVA) |  | 10.7 | 10.6 | 10.6 |  | 10.6 |  | 10.7 | 8.5 |  | 8.4 |  | 8.4 | 8.4 | 8.4
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  |  | Hours PA > 95% Peak Load |  | 3.5 | 3.5 | 3.5 |  | 3.5 |  | 3.5 | 3.5 |  | 3.5 |  | 3.5 | 3.5 | 3.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 16 | 16 | 16 |  | 16 |  | 16 | 16 |  | 16 |  | 16 | 16 | 16
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 8 | 8 | 8 |  | 8 |  | 8 | 8 |  | 8 |  | 8 | 8 | 8
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## PARK
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | PARK - Parkhurst (66/11kV) | [8 empty] | Supply |  | RMES - Rockhampton Mesh
| Description |  |  |  | Region is Capricornia
Transformer size is 2x66/11kV 15/20MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -1.8% W 0.9%,2025 S 0.4% W 1.1%, 2026 S 0.8% W 1.3%, 2027 S 1.4% W 1.2%
|  |  | Latest Peak Compensated Load | [5 empty] | 15.5 MVA on 02/02/2023 at 15:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 48.3 | 48.3 | 48.3 |  | 48.3 |  | 48.3 | 55.4 |  | 55.4 |  | 55.4 | 55.4 | 55.4
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 18.6 | 18.7 | 18.8 |  | 19.1 |  | 19.5 | 11.8 |  | 11.9 |  | 12 | 12.1 | 12.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.998 | 0.998 | 0.998 |  | 0.998 |  | 0.997 | 0.971 |  | 0.971 |  | 0.971 | 0.971 | 0.971
|  |  |  | ECC Rating (MVA) |  | 28 | 28 | 28 |  | 28 |  | 28 | 29.9 |  | 29.9 |  | 29.9 | 29.9 | 29.9
|  |  |  | 50 PoE Load (MVA) |  | 16.3 | 16.4 | 16.5 |  | 16.7 |  | 17.1 | 11 |  | 11.1 |  | 11.2 | 11.4 | 11.5
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.8 | 0.8 | 0.8 |  | 0.8 |  | 0.9 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  |  | Hours PA > 95% Peak Load |  | 6 | 6 | 6 |  | 6 |  | 6 | 6 |  | 6 |  | 6 | 6 | 6
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 30 | 30 | 30 |  | 30 |  | 30 | 30 |  | 30 |  | 30 | 30 | 30
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 15 | 15 | 15 |  | 15 |  | 15 | 15 |  | 15 |  | 15 | 15 | 15
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## PEAR
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | PEAR - Peter Arlett (66/11kV) | [8 empty] | Supply |  | TMES - Townsville Mesh
| Description |  |  |  | Region is Nth Queensland
Transformer size is 2x66/11kV 21/26.25/35MVA ONAN/ODAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.7% W 0.0%,2025 S -0.4% W 0.4%,2026 S 0.0% W 0.6%, 2027 S 0.4% W 0.4%
|  |  | Latest Peak Compensated Load | [5 empty] | 21.1 MVA on 15/12/2022 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 78.9 | 78.9 | 78.9 |  | 78.9 |  | 78.9 | 87.4 |  | 87.4 |  | 87.4 | 87.4 | 87.4
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 24 | 23.9 | 23.9 |  | 24 |  | 24.2 | 16.6 |  | 16.6 |  | 16.7 | 16.8 | 16.9
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.985 | 0.985 | 0.985 |  | 0.985 |  | 0.985 | 0.991 |  | 0.991 |  | 0.991 | 0.991 | 0.991
|  |  |  | ECC Rating (MVA) |  | 44.4 | 44.4 | 44.4 |  | 44.4 |  | 44.4 | 47.1 |  | 47.1 |  | 47.1 | 47.1 | 47.1
|  |  |  | 50 PoE Load (MVA) |  | 22.7 | 22.6 | 22.6 |  | 22.7 |  | 22.9 | 15.3 |  | 15.3 |  | 15.4 | 15.5 | 15.5
|  |  |  | 50 PoE Load > 95% (MVA) |  | 1.1 | 1.1 | 1.1 |  | 1.1 |  | 1.1 | 0.8 |  | 0.8 |  | 0.8 | 0.8 | 0.8
|  |  |  | Hours PA > 95% Peak Load |  | 28 | 28 | 28 |  | 28 |  | 28 | 28 |  | 28 |  | 28 | 28 | 28
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 41 | 41 | 41 |  | 41 |  | 41 | 41 |  | 41 |  | 41 | 41 | 41
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 21 | 21 | 21 |  | 21 |  | 21 | 21 |  | 21 |  | 21 | 21 | 21
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## PERA
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | PERA - Peranga (33/11kV) | [8 empty] | Supply |  | T189 - Oakey BSP
| Description |  |  |  | Region is South West
Transformer size is 1x33/11kV 0.75MVA ON;1x33/11kV 3MVA ON
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.9% W -0.6%2025 S -0.9% W -0.4%2026 S -0.4% W -0.1%2027 S 0.3% W -0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 1.7 MVA on 04/07/2022 at 17:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 4.7 | 4.7 | 4.7 |  | 4.7 |  | 4.7 | 5.1 |  | 5.1 |  | 5.1 | 5.1 | 5.1
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 1.7 | 1.6 | 1.6 |  | 1.6 |  | 1.7 | 1.8 |  | 1.8 |  | 1.8 | 1.8 | 1.8
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.937 | 0.937 | 0.911 |  | 0.937 |  | 0.937 | 0.911 |  | 0.946 |  | 0.946 | 0.946 | 0.946
|  |  |  | ECC Rating (MVA) |  | 0.8 | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.8 | 0.8
|  |  |  | 50 PoE Load (MVA) |  | 1.6 | 1.6 | 1.5 |  | 1.6 |  | 1.6 | 1.7 |  | 1.7 |  | 1.7 | 1.7 | 1.7
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 4 | 4 | 4 |  | 4 |  | 4 | 4 |  | 4 |  | 4 | 4 | 4
|  |  |  | Raw LAR (MVA) |  | 0.8 | 0.8 | 0.7 |  | 0.8 |  | 0.8 | 0.9 |  | 0.9 |  | 0.9 | 0.9 | 0.9
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 3 | 3 | 3 |  | 3 |  | 3 | 3 |  | 3 |  | 3 | 3 | 3
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## PIAL
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | PIAL - Pialba (66/11kV) | [8 empty] | Supply |  | MARY - Maryborough BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 2x66/11kV 12.5/16MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.4 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.5% W -1.6%2025 S -1.6% W -1.3%2026 S -1.2% W -1.0%2027 S -0.5% W -0.9
|  |  | Latest Peak Compensated Load | [5 empty] | 18.9 MVA on 02/02/2023 at 16:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 33.2 | 33.2 | 33.2 |  | 33.2 |  |  | 37.2 |  | 37.2 |  | 37.2 | 37.2
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 18.9 | 18.6 | 18.4 |  | 18.3 |  |  | 17.1 |  | 16.9 |  | 16.6 | 16.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.999 | 0.999 | 0.999 |  | 0.999 |  |  | 0.998 |  | 0.998 |  | 0.998 | 0.998
|  |  |  | ECC Rating (MVA) |  | 19.1 | 19.1 | 19.1 |  | 19.1 |  |  | 21 |  | 21 |  | 21 | 21
|  |  |  | 50 PoE Load (MVA) |  | 17.6 | 17.4 | 17.1 |  | 17.1 |  |  | 15.2 |  | 15 |  | 14.8 | 14.7
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.9 | 0.9 | 0.9 |  | 0.9 |  |  | 0.8 |  | 0.8 |  | 0.7 | 0.7
|  |  |  | Hours PA > 95% Peak Load |  | 4.5 | 4.5 | 4.5 |  | 4.5 |  |  | 4.5 |  | 4.5 |  | 4.5 | 4.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 4 | 4 | 4 |  | 4 |  |  | 4 |  | 4 |  | 4 | 4
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  |  | 0 |  | 0 |  | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 25 | 25 | 25 |  | 25 |  |  | 25 |  | 25 |  | 25 | 25
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 12.5 | 12.5 | 12.5 |  | 12.5 |  |  | 12.5 |  | 12.5 |  | 12.5 | 12.5
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  |  | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  |  | Yes |  | Yes |  | Yes | Yes
Return to Index

## PISO
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | PISO - Pialba South (66/11kV) | [8 empty] | Supply |  | MARY - Maryborough BSP
| Description |  |  |  | Region is Wide Bay (Note: PIAL is being rebuilt as Pialba South)
Transformer size is 2x66/11kV 15/20MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.4 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.5% W -1.6%2025 S -1.6% W -1.3%2026 S -1.2% W -1.0%2027 S -0.5% W -0.9
|  |  | Latest Peak Compensated Load | [5 empty] | 18.9 MVA on 02/02/2023 at 16:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) | [7 empty] | 40 | [6 empty] | 40
|  |  |  | Contracted non-network (MVA) | [7 empty] | 0 | [6 empty] | 0
|  |  |  | 10 PoE Load (MVA) | [7 empty] | 18.3 | [6 empty] | 16.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load | [7 empty] | 0.999 | [6 empty] | 0.998
|  |  |  | ECC Rating (MVA) | [7 empty] | 20 | [6 empty] | 20
|  |  |  | 50 PoE Load (MVA) | [7 empty] | 17.1 | [6 empty] | 14.5
|  |  |  | 50 PoE Load > 95% (MVA) | [7 empty] | 0.9 | [6 empty] | 0.7
|  |  |  | Hours PA > 95% Peak Load | [7 empty] | 4.5 | [6 empty] | 4.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) | [7 empty] | 0 | [6 empty] | 0
|  |  |  | Remote Trans Avail (MVA) | [7 empty] | 0 | [6 empty] | 0
|  |  |  | Manual Trans Avail (MVA) | [7 empty] | 4 | [6 empty] | 4
|  |  |  | Mobile Plant Avail (MVA) | [7 empty] | 0 | [6 empty] | 0
|  |  |  | Shed(30min) | [7 empty] | 0 | [6 empty] | 0
|  |  |  | Shed(4Hour) | [7 empty] | 0 | [6 empty] | 0
|  |  |  | Capacity for Embedded Generation (MVA) | [7 empty] | 25 | [6 empty] | 25
|  |  |  | Firm Capacity for Embedded Generation (MVA) | [7 empty] | 12.5 | [6 empty] | 12.5
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## PINN
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | PINN - Pinnacle (66/11kV) | [8 empty] | Supply |  | PIVA - Pioneer Valley BSP
| Description |  |  |  | Region is Mackay
Transformer size is 2x66/11kV 5MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.5% W -0.1%2025 S -0.3% W 0.2%,2026 S 0.1% W 0.5%, 2027 S 1.2% W 0.9%
|  |  | Latest Peak Compensated Load | [5 empty] | 2.3 MVA on 23/11/2022 at 20:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 11 | 11 | 11 |  | 11 |  | 11 | 12 |  | 12 |  | 12 | 12 | 12
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 2.8 | 2.8 | 2.8 |  | 2.8 |  | 2.8 | 2.3 |  | 2.3 |  | 2.3 | 2.3 | 2.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.956 | 0.956 | 0.956 |  | 0.956 |  | 0.956 | 0.997 |  | 0.997 |  | 0.997 | 0.997 | 0.997
|  |  |  | ECC Rating (MVA) |  | 6.3 | 6.3 | 6.3 |  | 6.3 |  | 6.3 | 6.5 |  | 6.5 |  | 6.5 | 6.5 | 6.5
|  |  |  | 50 PoE Load (MVA) |  | 2.6 | 2.6 | 2.6 |  | 2.6 |  | 2.7 | 2.1 |  | 2.1 |  | 2.1 | 2.1 | 2.1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 12.5 | 12.5 | 12.5 |  | 12.5 |  | 12.5 | 12.5 |  | 12.5 |  | 12.5 | 12.5 | 12.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 | 5 | 5
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## PIRR
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | PIRR - Pirrinuan (33/11kV) | [8 empty] | Supply |  | T002 - Dalby East BSP
| Description |  |  |  | Region is South West
Transformer size is 1x33/11kV 3.15MVA ONAN;1x33/11kV 1MVA ON(Standby)
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.0% W -0.0%2025 S -1.4% W 0.1%,2026 S -0.8% W 0.4%,2027 S -0.1% W 0.4%
|  |  | Latest Peak Compensated Load | [5 empty] | 1.9 MVA on 14/02/2023 at 14:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 3.2 | 3.2 | 3.2 |  | 3.2 |  | 3.2 | 3.2 |  | 3.2 |  | 3.2 | 3.2 | 3.2
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 1.8 | 1.8 | 1.8 |  | 1.8 |  | 1.8 | 2 |  | 2 |  | 2 | 2 | 2
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.866 | 0.866 | 0.866 |  | 0.866 |  | 0.866 | 0.718 |  | 0.718 |  | 0.718 | 0.718 | 0.718
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 1.7 | 1.6 | 1.6 |  | 1.6 |  | 1.6 | 1.9 |  | 1.9 |  | 1.9 | 1.9 | 1.9
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10
|  |  |  | Raw LAR (MVA) |  | 1.7 | 1.6 | 1.6 |  | 1.6 |  | 1.6 | 1.9 |  | 1.9 |  | 1.9 | 1.9 | 1.9
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 1.4 | 1.4 | 1.4 |  | 1.4 |  | 1.4 | 1.5 |  | 1.5 |  | 1.5 | 1.5 | 1.5
|  |  |  | Mobile Plant Avail (MVA) |  | 1.5 | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.5 | 1.5
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 3.15 | 3.15 | 3.15 |  | 3.15 |  | 3.15 | 3.15 |  | 3.15 |  | 3.15 | 3.15 | 3.15
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## PLAN
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | PLAN - Planella (33/11kV) | [8 empty] | Supply |  | GZSA - Glenella ZS Accumulator
| Description |  |  |  | Region is Mackay
Transformer size is 2x33/11kV 13/15MVA ONAN/ONAF (Both transformers have rating limited to 13.3MVA by transformer LV bushing, not upgradable)
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.2% W -0.2%2025 S 0.0% W 0.0%, 2026 S 0.5% W 0.4%, 2027 S 1.6% W 1.3%
|  |  | Latest Peak Compensated Load | [5 empty] | 19.1 MVA on 02/02/2023 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 26.6 | 26.6 | 26.6 |  | 26.6 |  | 26.6 | 26.6 |  | 26.6 |  | 26.6 | 26.6 | 26.6
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 19.3 | 19.3 | 19.3 |  | 19.6 |  | 20.1 | 11.4 |  | 11.4 |  | 11.4 | 11.5 | 11.6
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.998 | 0.998 | 0.998 |  | 0.998 |  | 0.998 | 0.999 |  | 0.999 |  | 0.999 | 0.999 | 0.999
|  |  |  | ECC Rating (MVA) |  | 13.3 | 13.3 | 13.3 |  | 13.3 |  | 13.3 | 13.3 |  | 13.3 |  | 13.3 | 13.3 | 13.3
|  |  |  | 50 PoE Load (MVA) |  | 18.4 | 18.4 | 18.5 |  | 18.8 |  | 19.2 | 11 |  | 11 |  | 11 | 11 | 11.1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.9 | 0.9 | 0.9 |  | 0.9 |  | 1 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  |  | Hours PA > 95% Peak Load |  | 6.5 | 6.5 | 6.5 |  | 6.5 |  | 6.5 | 6.5 |  | 6.5 |  | 6.5 | 6.5 | 6.5
|  |  |  | Raw LAR (MVA) |  | 5.1 | 5.1 | 5.2 |  | 5.5 |  | 5.9
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 2.3 | 2.3 | 2.3 |  | 2.3 |  | 2.3 | 2.3 |  | 2.3 |  | 2.3 | 2.3 | 2.3
|  |  |  | Mobile Plant Avail (MVA) |  | 1.5 | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.5 | 1.5
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 15.6 | 15.6 | 15.6 |  | 15.6 |  | 15.6 | 15.6 |  | 15.6 |  | 15.6 | 15.6 | 15.6
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 7.8 | 7.8 | 7.8 |  | 7.8 |  | 7.8 | 7.8 |  | 7.8 |  | 7.8 | 7.8 | 7.8
|  |  |  | LARc (MVA) |  | 1.3 | 1.3 | 1.4 |  | 1.3 |  | 2.1
|  |  |  | LARc (MW) |  | 1.3 | 1.3 | 1.4 |  | 1.3 |  | 2.1
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | No | No | No |  | No |  | No | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## PLEY
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | PLEY - Pleystowe (33/11kV) | [8 empty] | Supply |  | MACK - Mackay BSP
| Description |  |  |  | Region is Mackay
Transformer size is 3x33/11kV 5MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.0% W -0.8%2025 S -0.9% W -0.6%2026 S -0.4% W -0.3%2027 S 0.3% W -0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 7.2 MVA on 02/02/2023 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 13.5 | 13.5 | 13.5 |  | 13.5 |  | 13.5 | 13.5 |  | 13.5 |  | 13.5 | 13.5 | 13.5
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 7.8 | 7.7 | 7.7 |  | 7.7 |  | 7.8 | 5 |  | 5 |  | 5 | 4.9 | 4.9
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.992 | 0.992 | 0.992 |  | 0.992 |  | 0.992 | 0.999 |  | 0.999 |  | 0.999 | 0.999 | 0.999
|  |  |  | ECC Rating (MVA) |  | 9 | 9 | 9 |  | 9 |  | 9 | 9 |  | 9 |  | 9 | 9 | 9
|  |  |  | 50 PoE Load (MVA) |  | 7.3 | 7.2 | 7.2 |  | 7.2 |  | 7.3 | 4.8 |  | 4.8 |  | 4.7 | 4.7 | 4.7
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.4 | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 6.5 | 6.5 | 6.5 |  | 6.5 |  | 6.5 | 6.5 |  | 6.5 |  | 6.5 | 6.5 | 6.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 | 2 | 2
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 | 5 | 5
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## POVE
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | POVE - Point Vernon (66/11kV) | [8 empty] | Supply |  | MARY - Maryborough BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 2x66/11kV 25/32MVA ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -4.4% W -2.0%2025 S -3.0% W -1.1%2026 S -1.1% W -0.7%2027 S -0.1% W -0.5
|  |  | Latest Peak Compensated Load | [5 empty] | 22 MVA on 02/02/2023 at 16:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 84.6 | 84.6 | 84.6 |  | 84.6 |  | 84.6 | 95.7 |  | 95.7 |  | 95.7 | 95.7 | 95.7
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 21.8 | 21.1 | 20.9 |  | 20.8 |  | 20.9 | 18.7 |  | 18.4 |  | 18.1 | 18 | 17.9
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.999 | 0.999 | 0.999 |  | 0.999 |  | 0.999 | 0.998 |  | 0.998 |  | 0.998 | 0.998 | 0.998
|  |  |  | ECC Rating (MVA) |  | 47.6 | 47.6 | 47.6 |  | 47.6 |  | 47.6 | 47.8 |  | 47.8 |  | 47.8 | 47.8 | 47.8
|  |  |  | 50 PoE Load (MVA) |  | 20.3 | 19.7 | 19.5 |  | 19.5 |  | 19.6 | 17.9 |  | 17.5 |  | 17.3 | 17.2 | 17.1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 0.9 |  | 0.9 |  | 0.9 | 0.9 | 0.9
|  |  |  | Hours PA > 95% Peak Load |  | 3.5 | 3.5 | 3.5 |  | 3.5 |  | 3.5 | 3.5 |  | 3.5 |  | 3.5 | 3.5 | 3.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 50 | 50 | 50 |  | 50 |  | 50 | 50 |  | 50 |  | 50 | 50 | 50
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 25 | 25 | 25 |  | 25 |  | 25 | 25 |  | 25 |  | 25 | 25 | 25
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## POZI
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | POZI - Pozieres (33/11kV) | [8 empty] | Supply |  | STAN - Stanthorpe BSP
| Description |  |  |  | Region is South West
Transformer size is 2x33/11kV 3MVA ON
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.6% W 0.0%,2025 S -0.6% W 0.0%,2026 S -0.1% W 0.3%,2027 S 0.5% W 0.3%
|  |  | Latest Peak Compensated Load | [5 empty] | 3 MVA on 04/01/2023 at 15:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 7.1 | 7.1 | 7.1 |  | 7.1 |  | 7.1 | 7.5 |  | 7.5 |  | 7.5 | 7.5 | 7.5
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 3.1 | 3 | 3 |  | 3 |  | 3.1 | 2.5 |  | 2.5 |  | 2.5 | 2.5 | 2.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.894 | 0.894 | 0.894 |  | 0.894 |  | 0.894 | 0.969 |  | 0.969 |  | 0.969 | 0.969 | 0.969
|  |  |  | ECC Rating (MVA) |  | 3.9 | 3.9 | 3.9 |  | 3.9 |  | 3.9 | 4 |  | 4 |  | 4 | 4 | 4
|  |  |  | 50 PoE Load (MVA) |  | 2.9 | 2.9 | 2.9 |  | 2.9 |  | 2.9 | 2.4 |  | 2.4 |  | 2.4 | 2.4 | 2.4
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 34 | 34 | 34 |  | 34 |  | 34 | 34 |  | 34 |  | 34 | 34 | 34
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 6 | 6 | 6 |  | 6 |  | 6 | 6 |  | 6 |  | 6 | 6 | 6
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 3 | 3 | 3 |  | 3 |  | 3 | 3 |  | 3 |  | 3 | 3 | 3
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## PRMI
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | PRMI - Proserpine Mill (66/11kV) | [8 empty] | Supply |  | PROS - Proserpine BSP
| Description |  |  |  | Region is Mackay
Transformer size is 1x66/11kV 10/12.5MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 20.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.0% W -0.9%2025 S -0.8% W -0.7%2026 S -0.4% W -0.4%2027 S 0.3% W -0.4%
|  |  | Latest Peak Compensated Load | [5 empty] | 5.3 MVA on 16/11/2022 at 11:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 14.4 | 14.4 | 14.4 |  | 14.4 |  | 14.4 | 15.2 |  | 15.2 |  | 15.2 | 15.2 | 15.2
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 5.7 | 5.6 | 5.6 |  | 5.6 |  | 5.7 | 4.4 |  | 4.4 |  | 4.3 | 4.3 | 4.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.873 | 0.873 | 0.873 |  | 0.873 |  | 0.873 | 0.926 |  | 0.926 |  | 0.926 | 0.926 | 0.926
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 5.5 | 5.5 | 5.5 |  | 5.5 |  | 5.5 | 4.3 |  | 4.3 |  | 4.2 | 4.2 | 4.2
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 8.5 | 8.5 | 8.5 |  | 8.5 |  | 8.5 | 8.5 |  | 8.5 |  | 8.5 | 8.5 | 8.5
|  |  |  | Raw LAR (MVA) |  | 5.5 | 5.5 | 5.5 |  | 5.5 |  | 5.5 | 4.3 |  | 4.3 |  | 4.2 | 4.2 | 4.2
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 1.8 | 1.8 | 1.8 |  | 1.8 |  | 1.8 | 1.8 |  | 1.8 |  | 1.8 | 1.8 | 1.8
|  |  |  | Mobile Plant Avail (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 2.3 | 2.3 | 2.3 |  | 2.3 |  | 2.3 | 2.3 |  | 2.3 |  | 2.3 | 2.3 | 2.3
|  |  |  | Capacity for Embedded Generation (MVA) |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | LARc (MVA) |  | 0.4 | 0.4 | 0.4 |  | 0.4 |  | 0.4
|  |  |  | LARc (MW) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | No | No | No |  | No |  | No | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## PROT
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | PROT - Proston (66/11kV) | [8 empty] | Supply |  | KILK - Kilkivan BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 1x66/11kV 2.3MVA ONAN;1x66/11kV 2MVA ON
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.9% W -0.7%2025 S -0.7% W -0.4%2026 S -0.2% W -0.1%2027 S 0.4% W -0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 2 MVA on 13/02/2023 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 5.4 | 5.4 | 5.4 |  | 5.4 |  | 5.4 | 6 |  | 6 |  | 6 | 6 | 6
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 1.8 | 1.8 | 1.8 |  | 1.8 |  | 1.8 | 1.8 |  | 1.7 |  | 1.7 | 1.7 | 1.7
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.986 | 0.986 | 0.986 |  | 0.986 |  | 0.986 | 0.997 |  | 0.997 |  | 0.997 | 0.997 | 0.997
|  |  |  | ECC Rating (MVA) |  | 3 | 3 | 3 |  | 3 |  | 3 | 3 |  | 3 |  | 3 | 3 | 3
|  |  |  | 50 PoE Load (MVA) |  | 1.6 | 1.6 | 1.6 |  | 1.6 |  | 1.7 | 1.6 |  | 1.6 |  | 1.6 | 1.6 | 1.6
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 4.5 | 4.5 | 4.5 |  | 4.5 |  | 4.5 | 4.5 |  | 4.5 |  | 4.5 | 4.5 | 4.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## PURR
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | PURR - Purrawunda (33/11kV) | [8 empty] | Supply |  | T116 - Torrington BSP
| Description |  |  |  | Region is South West
Transformer size is 2x33/11kV 6.25MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.0% W -0.6%2025 S -0.8% W -0.2%2026 S -0.3% W 0.0%,2027 S 0.3% W 0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 5.8 MVA on 10/01/2023 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 14 | 14 | 14 |  | 14 |  | 14 | 15.5 |  | 15.5 |  | 15.5 | 15.5 | 15.5
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 6.3 | 6.2 | 6.2 |  | 6.2 |  | 6.3 | 6 |  | 6 |  | 5.9 | 5.9 | 5.9
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.992 | 0.992 | 0.992 |  | 0.992 |  | 0.992 | 0.984 |  | 0.984 |  | 0.984 | 0.984 | 0.984
|  |  |  | ECC Rating (MVA) |  | 8.2 | 8.2 | 8.2 |  | 8.2 |  | 8.2 | 8.8 |  | 8.8 |  | 8.8 | 8.8 | 8.8
|  |  |  | 50 PoE Load (MVA) |  | 6.1 | 6.1 | 6 |  | 6.1 |  | 6.1 | 5.8 |  | 5.8 |  | 5.8 | 5.8 | 5.8
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Hours PA > 95% Peak Load |  | 100.5 | 100.5 | 100.5 |  | 100.5 |  | 100.5 | 100.5 |  | 100.5 |  | 100.5 | 100.5 | 100.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 12.5 | 12.5 | 12.5 |  | 12.5 |  | 12.5 | 12.5 |  | 12.5 |  | 12.5 | 12.5 | 12.5
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 6.25 | 6.25 | 6.25 |  | 6.25 |  | 6.25 | 6.25 |  | 6.25 |  | 6.25 | 6.25 | 6.25
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## QUIL
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | QUIL - Quilpie (66/11kV) | [8 empty] | Supply |  | ROMA - Roma 66kV BSP
| Description |  |  |  | Region is South West
Transformer size is 2x66/11kV 3MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.9% W -1.2%2025 S -1.8% W -0.9%2026 S -1.3% W -0.6%2027 S -0.4% W -0.5
|  |  | Latest Peak Compensated Load | [5 empty] | 2.3 MVA on 28/02/2023 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 6.3 | 6.3 | 6.3 |  | 6.3 |  | 6.3 | 7.4 |  | 7.4 |  | 7.4 | 7.4 | 7.4
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 2.4 | 2.3 | 2.3 |  | 2.3 |  | 2.3 | 2.1 |  | 2 |  | 2 | 2 | 2
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.962 | 0.962 | 0.962 |  | 0.962 |  | 0.962 | 0.874 |  | 0.874 |  | 0.874 | 0.874 | 0.874
|  |  |  | ECC Rating (MVA) |  | 3.7 | 3.7 | 3.7 |  | 3.7 |  | 3.7 | 4.3 |  | 4.3 |  | 4.3 | 4.3 | 4.3
|  |  |  | 50 PoE Load (MVA) |  | 2.3 | 2.2 | 2.2 |  | 2.2 |  | 2.2 | 2 |  | 1.9 |  | 1.9 | 1.9 | 1.9
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 13 | 13 | 13 |  | 13 |  | 13 | 13 |  | 13 |  | 13 | 13 | 13
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 6 | 6 | 6 |  | 6 |  | 6 | 6 |  | 6 |  | 6 | 6 | 6
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 3 | 3 | 3 |  | 3 |  | 3 | 3 |  | 3 |  | 3 | 3 | 3
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## RAGL
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | RAGL - Raglan (66/22kV) | [8 empty] | Supply |  | RMES - Rockhampton Mesh
| Description |  |  |  | Region is Capricornia
Transformer size is 2x66/22kV 5MVA ON
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.6% W 0.0%,2025 S -0.6% W 0.1%,2026 S -0.1% W 0.4%,2027 S 0.6% W 0.5%
|  |  | Latest Peak Compensated Load | [5 empty] | 3.9 MVA on 13/02/2023 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 12.5 | 12.5 | 12.5 |  | 12.5 |  | 12.5 | 14 |  | 14 |  | 14 | 14 | 14
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 4 | 4 | 4 |  | 4 |  | 4.1 | 3.3 |  | 3.3 |  | 3.3 | 3.3 | 3.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.994 | 0.994 | 0.994 |  | 0.994 |  | 0.994 | 0.984 |  | 0.984 |  | 0.984 | 0.984 | 0.984
|  |  |  | ECC Rating (MVA) |  | 7.5 | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 | 7.5
|  |  |  | 50 PoE Load (MVA) |  | 3.8 | 3.8 | 3.8 |  | 3.8 |  | 3.8 | 3.1 |  | 3.1 |  | 3.1 | 3.1 | 3.1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 2.5 | 2.5 | 2.5 |  | 2.5 |  | 2.5 | 2.5 |  | 2.5 |  | 2.5 | 2.5 | 2.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 | 5 | 5
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## RASM
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | RASM - Rasmussen (66/11kV) | [8 empty] | Supply |  | TMES - Townsville Mesh
| Description |  |  |  | Region is Nth Queensland
Transformer size is 2x66/11kV 19/26/32MVA ONAN/ODAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.6% W 0.1%,2025 S -0.3% W 0.4%,2026 S 0.1% W 0.7%, 2027 S 0.9% W 0.9%
|  |  | Latest Peak Compensated Load | [5 empty] | 18.1 MVA on 14/12/2022 at 20:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 80.4 | 80.4 | 80.4 |  | 80.4 |  | 80.4 | 84.4 |  | 84.4 |  | 84.4 | 84.4 | 84.4
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 20.4 | 20.4 | 20.4 |  | 20.6 |  | 20.9 | 12.1 |  | 12.1 |  | 12.2 | 12.3 | 12.4
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.996 | 0.996 | 0.996 |  | 0.996 |  | 0.996 | 0.999 |  | 0.999 |  | 0.999 | 0.999 | 0.999
|  |  |  | ECC Rating (MVA) |  | 42.9 | 42.9 | 42.9 |  | 42.9 |  | 42.9 | 45 |  | 45 |  | 45 | 45 | 45
|  |  |  | 50 PoE Load (MVA) |  | 19.1 | 19.1 | 19.1 |  | 19.2 |  | 19.5 | 11.8 |  | 11.8 |  | 11.8 | 11.9 | 12
|  |  |  | 50 PoE Load > 95% (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  |  | Hours PA > 95% Peak Load |  | 12 | 12 | 12 |  | 12 |  | 12 | 12 |  | 12 |  | 12 | 12 | 12
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 38 | 38 | 38 |  | 38 |  | 38 | 38 |  | 38 |  | 38 | 38 | 38
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 19 | 19 | 19 |  | 19 |  | 19 | 19 |  | 19 |  | 19 | 19 | 19
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## RAVE
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | RAVE - Ravenshoe (66/22kV) | [8 empty] | Supply |  | TURK - Turkinje 66kV BSP
| Description |  |  |  | Region is Far North
Transformer size is 1x66/22kV 12/15MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 12.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.1% W -0.5%2025 S -1.1% W -0.3%2026 S -0.5% W 0.0%,2027 S 0.2% W 0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 2.6 MVA on 15/07/2022 at 07:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 19.6 | 19.6 | 19.6 |  | 19.6 |  | 19.6 | 22.3 |  | 22.3 |  | 22.3 | 22.3 | 22.3
|  |  |  | Contracted non-network (MVA) |  | 4.9 | 4.9 | 4.9 |  | 4.9 |  | 4.9 | 4.9 |  | 4.9 |  | 4.9 | 4.9 | 4.9
|  |  |  | 10 PoE Load (MVA) |  | 2.1 | 2 | 2 |  | 2 |  | 2 | 2.8 |  | 2.7 |  | 2.7 | 2.7 | 2.7
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.913 | 0.913 | 0.913 |  | 0.913 |  | 0.913 | 0.972 |  | 0.972 |  | 0.972 | 0.972 | 0.972
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2.5 |  | 2.5 |  | 2.5 | 2.5 | 2.5
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 23 | 23 | 23 |  | 23 |  | 23 | 23 |  | 23 |  | 23 | 23 | 23
|  |  |  | Raw LAR (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2.5 |  | 2.5 |  | 2.5 | 2.5 | 2.5
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 3.9 | 3.9 | 3.9 |  | 3.9 |  | 3.9 | 3.9 |  | 3.9 |  | 3.9 | 3.9 | 3.9
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 12 | 12 | 12 |  | 12 |  | 12 | 12 |  | 12 |  | 12 | 12 | 12
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## RAVN
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | RAVN - Ravenswood (66/11kV) | [8 empty] | Supply |  | T193 - Clare South BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/11kV 2.5MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.3% W -0.4%2025 S -1.7% W -0.4%2026 S -1.0% W 0.0%,2027 S -0.2% W 0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 0.8 MVA on 09/06/2022 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 2.5 | 2.5 | 2.5 |  | 2.5 |  | 2.5 | 2.5 |  | 2.5 |  | 2.5 | 2.5 | 2.5
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 0.8 | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.9 |  | 0.9 |  | 0.9 | 0.9 | 0.9
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.919 | 0.872 | 0.872 |  | 0.872 |  | 0.872 | 0.904 |  | 0.904 |  | 0.904 | 0.904 | 0.904
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 0.8 | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.8 | 0.8
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 8 | 8 | 8 |  | 8 |  | 8 | 8 |  | 8 |  | 8 | 8 | 8
|  |  |  | Raw LAR (MVA) |  | 0.8 | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.8 | 0.8
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 | 2 | 2
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 2.5 | 2.5 | 2.5 |  | 2.5 |  | 2.5 | 2.5 |  | 2.5 |  | 2.5 | 2.5 | 2.5
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## RICH
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | RICH - Richmond (66/33kV) | [8 empty] | Supply |  | T095 - Millchester BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/33kV 6.3MVA ONAN;1x66/33kV 7.5/6.3MVA ONAF/ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.2% W -1.1%2025 S -1.1% W -0.6%2026 S -0.6% W -0.2%2027 S 0.0% W -0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 2.3 MVA on 13/12/2022 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 14.6 | 14.6 | 14.6 |  | 14.6 |  | 14.6 | 16.3 |  | 16.3 |  | 16.3 | 16.3 | 16.3
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 2.4 | 2.4 | 3.6 |  | 3.6 |  | 3.7 | 1.9 |  | 1.8 |  | 2.6 | 2.6 | 2.6
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.984 | 0.984 | 0.985 |  | 0.985 |  | 0.985 | 0.935 |  | 0.904 |  | 0.904 | 0.904 | 0.904
|  |  |  | ECC Rating (MVA) |  | 8.5 | 8.5 | 8.5 |  | 8.5 |  | 8.5 | 9.4 |  | 9.4 |  | 9.4 | 9.4 | 9.4
|  |  |  | 50 PoE Load (MVA) |  | 2.4 | 2.3 | 3.6 |  | 3.6 |  | 3.6 | 1.8 |  | 1.7 |  | 2.4 | 2.4 | 2.4
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.2 |  | 0.2 |  | 0.2 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 84.5 | 84.5 | 84.5 |  | 84.5 |  | 84.5 | 84.5 |  | 84.5 |  | 84.5 | 84.5 | 84.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 12 | 12 | 12 |  | 12 |  | 12 | 12 |  | 12 |  | 12 | 12 | 12
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 6.3 | 6.3 | 6.3 |  | 6.3 |  | 6.3 | 6.3 |  | 6.3 |  | 6.3 | 6.3 | 6.3
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## ROEA
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | ROEA - Roma East (33/11kV) | [8 empty] | Supply |  | T083 - Roma 33kV BSP
| Description |  |  |  | Region is South West
Transformer size is 2x33/11kV 6.3MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.0% W -0.5%2025 S -1.1% W -0.4%2026 S -0.6% W -0.1%2027 S 0.1% W -0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 9 MVA on 01/03/2023 at 15:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 14 | 14 | 14 |  | 14 |  | 14 | 17.5 |  | 17.5 |  | 17.5 | 17.5 | 17.5
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 10.2 | 10.1 | 11.5 |  | 11.5 |  | 11.6 | 9.6 |  | 9.5 |  | 10.1 | 10.1 | 10.1
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.975 | 0.975 | 0.975 |  | 0.975 |  | 0.975 | 0.991 |  | 0.991 |  | 0.991 | 0.991 | 0.991
|  |  |  | ECC Rating (MVA) |  | 8 | 8 | 8 |  | 8 |  | 8 | 9.4 |  | 9.4 |  | 9.4 | 9.4 | 9.4
|  |  |  | 50 PoE Load (MVA) |  | 9.6 | 9.5 | 10.9 |  | 10.9 |  | 11 | 9.1 |  | 9.1 |  | 9.7 | 9.7 | 9.7
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.6 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | Hours PA > 95% Peak Load |  | 18 | 18 | 18 |  | 18 |  | 18 | 18 |  | 18 |  | 18 | 18 | 18
|  |  |  | Raw LAR (MVA) |  | 1.6 | 1.5 | 2.9 |  | 2.9 |  | 3 |  |  |  |  | 0.3 | 0.3 | 0.3
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 | 2 | 2
|  |  |  | Mobile Plant Avail (MVA) |  | 11.5 | 11.5 | 11.5 |  | 11.5 |  | 11.5 | 11.5 |  | 11.5 |  | 11.5 | 11.5 | 11.5
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 12.6 | 12.6 | 12.6 |  | 12.6 |  | 12.6 | 12.6 |  | 12.6 |  | 12.6 | 12.6 | 12.6
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 6.3 | 6.3 | 6.3 |  | 6.3 |  | 6.3 | 6.3 |  | 6.3 |  | 6.3 | 6.3 | 6.3
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## ROGL
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | ROGL - Rockhampton Glenmore (66/11kV) | [8 empty] | Supply |  | RMES - Rockhampton Mesh
| Description |  |  |  | Region is Capricornia
Transformer size is 2x66/11kV 20/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.6% W -0.1%2025 S -0.6% W -0.1%2026 S -0.1% W 0.3%,2027 S 0.5% W 0.3%
|  |  | Latest Peak Compensated Load | [5 empty] | 21.4 MVA on 02/02/2023 at 15:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 54.3 | 54.3 | 54.3 |  | 54.3 |  | 54.3 | 64.5 |  | 64.5 |  | 64.5 | 64.5 | 64.5
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 22.7 | 22.5 | 22.5 |  | 22.6 |  | 22.9 | 13.8 |  | 13.8 |  | 13.8 | 13.9 | 13.9
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.998 | 0.998 | 0.998 |  | 0.998 |  | 0.998 | 0.983 |  | 0.983 |  | 0.983 | 0.983 | 0.983
|  |  |  | ECC Rating (MVA) |  | 32 | 32 | 32 |  | 32 |  | 32 | 35.9 |  | 35.9 |  | 35.9 | 35.9 | 35.9
|  |  |  | 50 PoE Load (MVA) |  | 20.9 | 20.8 | 20.8 |  | 20.9 |  | 21.1 | 13.2 |  | 13.2 |  | 13.2 | 13.2 | 13.2
|  |  |  | 50 PoE Load > 95% (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1.1 | 0.7 |  | 0.7 |  | 0.7 | 0.7 | 0.7
|  |  |  | Hours PA > 95% Peak Load |  | 7 | 7 | 7 |  | 7 |  | 7 | 7 |  | 7 |  | 7 | 7 | 7
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 14 | 14 | 14 |  | 14 |  | 14 | 14 |  | 14 |  | 14 | 14 | 14
|  |  |  | Mobile Plant Avail (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 | 2 | 2
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 40 | 40 | 40 |  | 40 |  | 40 | 40 |  | 40 |  | 40 | 40 | 40
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 20 | 20 | 20 |  | 20 |  | 20 | 20 |  | 20 |  | 20 | 20 | 20
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## ROLE
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | ROLE - Rolleston (66/22kV) | [8 empty] | Supply |  | T163 - Rolleston BSP
| Description |  |  |  | Region is Capricornia
Transformer size is 2x132/66/22kV 30/40/50MVA ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.0% W -0.6%2025 S -0.8% W -0.2%2026 S -0.3% W 0.0%,2027 S 0.3% W 0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 6.7 MVA on 14/02/2023 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 89.3 | 89.3 | 89.3 |  | 89.3 |  | 89.3 | 97.7 |  | 97.7 |  | 97.7 | 97.7 | 97.7
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 6.8 | 6.8 | 7.8 |  | 7.9 |  | 7.9 | 6.2 |  | 6.2 |  | 6.8 | 6.8 | 6.8
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.998 | 0.998 | 0.998 |  | 0.998 |  | 0.998 | 0.999 |  | 0.999 |  | 0.999 | 0.999 | 0.999
|  |  |  | ECC Rating (MVA) |  | 52.3 | 52.3 | 52.3 |  | 52.3 |  | 52.3 | 56.1 |  | 56.1 |  | 56.1 | 56.1 | 56.1
|  |  |  | 50 PoE Load (MVA) |  | 6.6 | 6.5 | 7.6 |  | 7.6 |  | 7.7 | 6 |  | 6 |  | 6.6 | 6.6 | 6.6
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.3 | 0.3 | 0.4 |  | 0.4 |  | 0.4 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Hours PA > 95% Peak Load |  | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 | 5 | 5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 60 | 60 | 60 |  | 60 |  | 60 | 60 |  | 60 |  | 60 | 60 | 60
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 30 | 30 | 30 |  | 30 |  | 30 | 30 |  | 30 |  | 30 | 30 | 30
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## ROLL
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | ROLL - Rollingstone (66/11kV) | [8 empty] | Supply |  | TMES - Townsville Mesh
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/11kV 2.5/2.9MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.5% W 0.1%,2025 S -0.3% W 0.4%,2026 S 0.2% W 0.6%, 2027 S 1.0% W 0.9%
|  |  | Latest Peak Compensated Load | [5 empty] | 1.5 MVA on 14/12/2022 at 20:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 4.3 | 4.3 | 4.3 |  | 4.3 |  | 4.3 | 4.3 |  | 4.3 |  | 4.3 | 4.3 | 4.3
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 1.7 | 1.7 | 1.7 |  | 1.7 |  | 1.7 | 1.3 |  | 1.3 |  | 1.3 | 1.3 | 1.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.993 | 0.993 | 0.993 |  | 0.993 |  | 0.993 | 0.989 |  | 0.989 |  | 0.989 | 0.989 | 0.989
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 1.6 | 1.6 | 1.6 |  | 1.6 |  | 1.6 | 1.2 |  | 1.2 |  | 1.2 | 1.2 | 1.2
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 4 | 4 | 4 |  | 4 |  | 4 | 4 |  | 4 |  | 4 | 4 | 4
|  |  |  | Raw LAR (MVA) |  | 1.6 | 1.6 | 1.6 |  | 1.6 |  | 1.6 | 1.2 |  | 1.2 |  | 1.2 | 1.2 | 1.2
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 | 2 | 2
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 2.5 | 2.5 | 2.5 |  | 2.5 |  | 2.5 | 2.5 |  | 2.5 |  | 2.5 | 2.5 | 2.5
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## ROMA
Bulk Summary Information and Peak Load Forecast
Substation |  |  |  | ROMA - Roma 66kV BSP (132/66kV) | [8 empty] | Supply |  | T194 - Columboola TCP
Description |  |  |  | Region is South West
Transformer size is 1x132/66/11kV 60/80MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
|  | Latest Peak Compensated Load | [5 empty] | 33.8 MVA on 14/07/2022 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[5 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  | NCC Rating (MVA) |  | 101.4 | 101.4 | 101.4 |  | 101.4 |  | 101.4 | 119.6 |  | 119.6 |  | 119.6 | 119.6 | 119.6
|  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | 10 PoE Load (MVA) |  | 35 | 34.6 | 36.9 |  | 36.9 |  | 37.1 | 35.3 |  | 35.1 |  | 36.4 | 36.3 | 36.3
LARn (MVA)
LARn (MW)
|  |  | Power Factor at Peak Load |  | 0.992 | 0.992 | 0.992 |  | 0.992 |  | 0.992 | 0.977 |  | 0.977 |  | 0.977 | 0.977 | 0.977
|  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | 50 PoE Load (MVA) |  | 33.1 | 32.8 | 35.1 |  | 35.1 |  | 35.3 | 33.9 |  | 33.6 |  | 35 | 34.9 | 34.8
|  |  | 50 PoE Load > 95% (MVA) |  | 1.7 | 1.6 | 1.8 |  | 1.8 |  | 1.8 | 1.7 |  | 1.7 |  | 1.8 | 1.7 | 1.7
|  |  | Hours PA > 95% Peak Load |  | 16 | 16 | 16 |  | 16 |  | 16 | 16 |  | 16 |  | 16 | 16 | 16
|  |  | Raw LAR (MVA) |  | 33.1 | 32.8 | 35.1 |  | 35.1 |  | 35.3 | 33.9 |  | 33.6 |  | 35 | 34.9 | 34.8
|  |  | Auto Trans Avail (MVA) |  | 50 | 50 | 50 |  | 50 |  | 50 | 50 |  | 50 |  | 50 | 50 | 50
|  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Capacity for Embedded Generation (MVA) |  | 40 | 40 | 40 |  | 40 |  | 40 | 40 |  | 40 |  | 40 | 40 | 40
|  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## ROPL
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | ROPL - Ross Plains (66/11kV) | [8 empty] | Supply |  | TMES - Townsville Mesh
| Description |  |  |  | Region is Nth Queensland
Transformer size is 2x66/11kV 12/15MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.1% W -0.7%2025 S -1.0% W -0.6%2026 S -0.5% W -0.3%2027 S 0.1% W -0.2%
|  |  | Latest Peak Compensated Load | [5 empty] | 13.3 MVA on 02/02/2023 at 17:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 33 | 33 | 33 |  | 33 |  | 33 | 37.8 |  | 37.8 |  | 37.8 | 37.8 | 37.8
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 15.9 | 15.7 | 15.6 |  | 15.6 |  | 15.8 | 8.4 |  | 8.4 |  | 8.3 | 8.3 | 8.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.994 | 0.994 | 0.994 |  | 0.994 |  | 0.994 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | ECC Rating (MVA) |  | 19.2 | 19.2 | 19.2 |  | 19.2 |  | 19.2 | 20.8 |  | 20.8 |  | 20.8 | 20.8 | 20.8
|  |  |  | 50 PoE Load (MVA) |  | 15.2 | 15 | 14.9 |  | 14.9 |  | 15.1 | 8.2 |  | 8.1 |  | 8.1 | 8 | 8
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.8 | 0.8 | 0.7 |  | 0.7 |  | 0.8 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  |  | Hours PA > 95% Peak Load |  | 4.5 | 4.5 | 4.5 |  | 4.5 |  | 4.5 | 4.5 |  | 4.5 |  | 4.5 | 4.5 | 4.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 10.2 | 10.2 | 10.2 |  | 10.2 |  | 10.2 | 10.2 |  | 10.2 |  | 10.2 | 10.2 | 10.2
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 5.1 | 5.1 | 5.1 |  | 5.1 |  | 5.1 | 5.1 |  | 5.1 |  | 5.1 | 5.1 | 5.1
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## ROSE
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | ROSE - Rosella (33/11kV) | [8 empty] | Supply |  | T065 - Alligator Creek BSP
| Description |  |  |  | Region is Mackay
Transformer size is 2x33/11kV 4.5MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.4% W 0.2%,2025 S -0.2% W 0.4%,2026 S 0.2% W 0.6%, 2027 S 1.0% W 0.9%
|  |  | Latest Peak Compensated Load | [5 empty] | 5.4 MVA on 21/11/2022 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 11.5 | 11.5 | 11.5 |  | 11.5 |  | 11.5 | 12.3 |  | 12.3 |  | 12.3 | 12.3 | 12.3
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 5.5 | 5.5 | 5.5 |  | 5.6 |  | 5.6 | 5 |  | 5 |  | 5 | 5.1 | 5.1
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.969 | 0.969 | 0.969 |  | 0.969 |  | 0.969 | 0.969 |  | 0.969 |  | 0.969 | 0.969 | 0.969
|  |  |  | ECC Rating (MVA) |  | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6 | 6.7 |  | 6.7 |  | 6.7 | 6.7 | 6.7
|  |  |  | 50 PoE Load (MVA) |  | 5.3 | 5.3 | 5.3 |  | 5.4 |  | 5.5 | 4.6 |  | 4.6 |  | 4.6 | 4.6 | 4.7
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 9 | 9 | 9 |  | 9 |  | 9 | 9 |  | 9 |  | 9 | 9 | 9
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 1.6 | 1.6 | 1.6 |  | 1.6 |  | 1.6 | 1.6 |  | 1.6 |  | 1.6 | 1.6 | 1.6
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 1.2 | 1.2 | 1.2 |  | 1.2 |  | 1.2 | 1.2 |  | 1.2 |  | 1.2 | 1.2 | 1.2
|  |  |  | Capacity for Embedded Generation (MVA) |  | 9 | 9 | 9 |  | 9 |  | 9 | 9 |  | 9 |  | 9 | 9 | 9
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 4.5 | 4.5 | 4.5 |  | 4.5 |  | 4.5 | 4.5 |  | 4.5 |  | 4.5 | 4.5 | 4.5
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## ROSO
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | ROSO - Rockhampton South (66/11kV) | [8 empty] | Supply |  | RMES - Rockhampton Mesh
| Description |  |  |  | Region is Capricornia
Transformer size is 2x66/11kV 15/20MVA ONAN/OFDAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.7% W -1.6%2025 S -2.6% W -1.5%2026 S -2.2% W -0.9%2027 S -1.8% W -1.0
|  |  | Latest Peak Compensated Load | [5 empty] | 12.6 MVA on 02/02/2023 at 15:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 32.7 | 32.7 | 32.7 |  | 32.7 |  | 32.7 | 32.7 |  | 32.7 |  | 32.7 | 32.7 | 32.7
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 12.9 | 12.6 | 12.3 |  | 12.1 |  | 11.9 | 8.9 |  | 8.7 |  | 8.6 | 8.5 | 8.4
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.933 | 0.933 | 0.933 |  | 0.933 |  | 0.933 | 0.937 |  | 0.937 |  | 0.937 | 0.937 | 0.937
|  |  |  | ECC Rating (MVA) |  | 16.5 | 16.5 | 16.5 |  | 16.5 |  | 16.5 | 18 |  | 18 |  | 18 | 18 | 18
|  |  |  | 50 PoE Load (MVA) |  | 12.5 | 12.1 | 11.9 |  | 11.6 |  | 11.5 | 8.1 |  | 7.9 |  | 7.8 | 7.7 | 7.7
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  |  | Hours PA > 95% Peak Load |  | 7.5 | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 | 7.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 30 | 30 | 30 |  | 30 |  | 30 | 30 |  | 30 |  | 30 | 30 | 30
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 15 | 15 | 15 |  | 15 |  | 15 | 15 |  | 15 |  | 15 | 15 | 15
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## ROST
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | ROST - Rocky Street (66/11kV) | [8 empty] | Supply |  | MARY - Maryborough BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 2x66/11kV 15/20/25MVA ONAN/ONAF/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.1% W -0.4%2025 S -1.1% W -0.0%2026 S -0.6% W 0.2%,2027 S 0.1% W 0.2%
|  |  | Latest Peak Compensated Load | [5 empty] | 22.4 MVA on 13/02/2023 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 57.5 | 57.5 | 57.5 |  | 57.5 |  | 57.5 | 64.3 |  | 64.3 |  | 64.3 | 64.3 | 64.3
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 22.2 | 21.9 | 21.8 |  | 21.8 |  | 22 | 21.2 |  | 21.1 |  | 21.1 | 21.1 | 21.2
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.999 | 0.999 | 0.999 |  | 0.999 |  | 0.999 | 0.993 |  | 0.993 |  | 0.993 | 0.993 | 0.993
|  |  |  | ECC Rating (MVA) |  | 32.1 | 32.1 | 32.1 |  | 32.1 |  | 32.1 | 36.1 |  | 36.1 |  | 36.1 | 36.1 | 36.1
|  |  |  | 50 PoE Load (MVA) |  | 20.7 | 20.4 | 20.3 |  | 20.3 |  | 20.5 | 19.3 |  | 19.3 |  | 19.3 | 19.3 | 19.3
|  |  |  | 50 PoE Load > 95% (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Hours PA > 95% Peak Load |  | 4.5 | 4.5 | 4.5 |  | 4.5 |  | 4.5 | 4.5 |  | 4.5 |  | 4.5 | 4.5 | 4.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 21.6 | 21.6 | 21.6 |  | 21.6 |  | 21.6 | 21.6 |  | 21.6 |  | 21.6 | 21.6 | 21.6
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 10.8 | 10.8 | 10.8 |  | 10.8 |  | 10.8 | 10.8 |  | 10.8 |  | 10.8 | 10.8 | 10.8
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## ROWE
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | ROWE - Roma West (33/11kV) | [8 empty] | Supply |  | T083 - Roma 33kV BSP
| Description |  |  |  | Region is South West
Transformer size is 2x33/11kV 3.15MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.3% W -0.6%2025 S -1.1% W -0.4%2026 S -0.4% W -0.1%2027 S 0.3% W -0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 4.3 MVA on 01/03/2023 at 15:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 6.3 | 6.3 | 6.3 |  | 6.3 |  | 6.3 | 6.3 |  | 6.3 |  | 6.3 | 6.3 | 6.3
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 4.7 | 4.7 | 4.6 |  | 4.7 |  | 4.7 | 4.5 |  | 4.5 |  | 4.5 | 4.4 | 4.4
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.978 | 0.978 | 0.978 |  | 0.978 |  | 0.978 | 0.992 |  | 0.992 |  | 0.992 | 0.992 | 0.992
|  |  |  | ECC Rating (MVA) |  | 3.2 | 3.2 | 3.2 |  | 3.2 |  | 3.2 | 3.2 |  | 3.2 |  | 3.2 | 3.2 | 3.2
|  |  |  | 50 PoE Load (MVA) |  | 4.5 | 4.4 | 4.4 |  | 4.4 |  | 4.4 | 4.3 |  | 4.3 |  | 4.2 | 4.2 | 4.2
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 28.5 | 28.5 | 28.5 |  | 28.5 |  | 28.5 | 28.5 |  | 28.5 |  | 28.5 | 28.5 | 28.5
|  |  |  | Raw LAR (MVA) |  | 1.3 | 1.2 | 1.2 |  | 1.2 |  | 1.2 | 1.1 |  | 1.1 |  | 1 | 1 | 1
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 4 | 4 | 4 |  | 4 |  | 4 | 4 |  | 4 |  | 4 | 4 | 4
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 6.3 | 6.3 | 6.3 |  | 6.3 |  | 6.3 | 6.3 |  | 6.3 |  | 6.3 | 6.3 | 6.3
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 3.15 | 3.15 | 3.15 |  | 3.15 |  | 3.15 | 3.15 |  | 3.15 |  | 3.15 | 3.15 | 3.15
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## ROWO
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | ROWO - Roo Works (33/11kV) | [8 empty] | Supply |  | SGZA - St George ZS Accumulator
| Description |  |  |  | Region is South West
Transformer size is 1x33/11kV 2MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -4.6% W -0.7%2025 S -2.5% W -0.4%2026 S -1.9% W -0.1%2027 S -1.2% W -0.1
|  |  | Latest Peak Compensated Load | [5 empty] | 1 MVA on 03/01/2023 at 17:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 2.4 | 2.4 | 2.4 |  | 2.4 |  | 2.4 | 2.4 |  | 2.4 |  | 2.4 | 2.4 | 2.4
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 1 | 1 | 0.9 |  | 0.9 |  | 0.9 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.942 | 0.942 | 0.942 |  | 0.942 |  | 0.942 | 0.982 |  | 0.982 |  | 0.982 | 0.982 | 0.982
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 0.9 | 0.9 | 0.9 |  | 0.9 |  | 0.9 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 71.5 | 71.5 | 71.5 |  | 71.5 |  | 71.5 | 71.5 |  | 71.5 |  | 71.5 | 71.5 | 71.5
|  |  |  | Raw LAR (MVA) |  | 0.9 | 0.9 | 0.9 |  | 0.9 |  | 0.9 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 1.2 | 1.2 | 1.2 |  | 1.2 |  | 1.2 | 1.2 |  | 1.2 |  | 1.2 | 1.2 | 1.2
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 | 2 | 2
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## SAGE
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | SAGE - St. George (66/33kV) | [8 empty] | Supply |  | ROMA - Roma 66kV BSP
| Description |  |  |  | Region is South West
Transformer size is 2x66/33/11kV 20MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.1% W -0.7%2025 S -0.9% W -0.3%2026 S -0.5% W -0.1%2027 S 0.2% W -0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 14.4 MVA on 14/07/2022 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 48.7 | 48.7 | 48.7 |  | 48.7 |  | 48.7 | 55.9 |  | 55.9 |  | 55.9 | 55.9 | 55.9
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 12.6 | 12.5 | 13.5 |  | 13.5 |  | 13.6 | 14.6 |  | 14.5 |  | 15.1 | 15.1 | 15.1
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.975 | 0.975 | 0.975 |  | 0.975 |  | 0.975 | 0.976 |  | 0.976 |  | 0.976 | 0.976 | 0.976
|  |  |  | ECC Rating (MVA) |  | 27.6 | 27.6 | 27.6 |  | 27.6 |  | 27.6 | 29.9 |  | 29.9 |  | 29.9 | 29.9 | 29.9
|  |  |  | 50 PoE Load (MVA) |  | 12.1 | 12 | 13 |  | 13 |  | 13.1 | 14.1 |  | 14 |  | 14.6 | 14.6 | 14.6
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.6 | 0.6 | 0.7 |  | 0.7 |  | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.7 | 0.7
|  |  |  | Hours PA > 95% Peak Load |  | 7.5 | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 | 7.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 40 | 40 | 40 |  | 40 |  | 40 | 40 |  | 40 |  | 40 | 40 | 40
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 20 | 20 | 20 |  | 20 |  | 20 | 20 |  | 20 |  | 20 | 20 | 20
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## SAGT
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | SAGT - St. George Town (33/11kV) | [8 empty] | Supply |  | SGZA - St George ZS Accumulator
| Description |  |  |  | Region is South West
Transformer size is 2x33/11kV 3MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.1% W -0.7%2025 S -1.0% W -0.5%2026 S -0.5% W -0.2%2027 S 0.1% W -0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 4.9 MVA on 14/03/2023 at 17:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6 | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 5.2 | 5.1 | 5.1 |  | 5.1 |  | 5.2 | 4.3 |  | 4.2 |  | 4.2 | 4.2 | 4.2
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.971 | 0.971 | 0.971 |  | 0.971 |  | 0.971 | 0.987 |  | 0.987 |  | 0.987 | 0.987 | 0.987
|  |  |  | ECC Rating (MVA) |  | 3.5 | 3.5 | 3.5 |  | 3.5 |  | 3.5 | 3.6 |  | 3.6 |  | 3.6 | 3.6 | 3.6
|  |  |  | 50 PoE Load (MVA) |  | 4.9 | 4.9 | 4.9 |  | 4.9 |  | 4.9 | 4.1 |  | 4 |  | 4 | 4 | 4
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 19 | 19 | 19 |  | 19 |  | 19 | 19 |  | 19 |  | 19 | 19 | 19
|  |  |  | Raw LAR (MVA) |  | 1.4 | 1.4 | 1.4 |  | 1.4 |  | 1.4 | 0.5 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0.8 | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.8 | 0.8
|  |  |  | Mobile Plant Avail (MVA) |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 6 | 6 | 6 |  | 6 |  | 6 | 6 |  | 6 |  | 6 | 6 | 6
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 3 | 3 | 3 |  | 3 |  | 3 | 3 |  | 3 |  | 3 | 3 | 3
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## SARI
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | SARI - Sarina (33/11kV) | [8 empty] | Supply |  | T065 - Alligator Creek BSP
| Description |  |  |  | Region is Mackay
Transformer size is 2x33/11kV 10/12.5MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 17.5 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.5% W -0.2%2025 S -0.4% W -0.1%2026 S 0.1% W 0.2%, 2027 S 0.7% W 0.3%
|  |  | Latest Peak Compensated Load | [5 empty] | 14.6 MVA on 02/02/2023 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 27.6 | 27.6 | 27.6 |  | 27.6 |  | 27.6 | 27.6 |  | 27.6 |  | 27.6 | 27.6 | 27.6
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 16 | 15.9 | 16 |  | 16.1 |  | 16.3 | 13.5 |  | 13.5 |  | 13.4 | 13.5 | 13.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.957 | 0.957 | 0.957 |  | 0.957 |  | 0.957 | 0.974 |  | 0.974 |  | 0.974 | 0.974 | 0.974
|  |  |  | ECC Rating (MVA) |  | 14.4 | 14.4 | 14.4 |  | 14.4 |  | 14.4 | 16.3 |  | 16.3 |  | 16.3 | 16.3 | 16.3
|  |  |  | 50 PoE Load (MVA) |  | 15.3 | 15.2 | 15.2 |  | 15.3 |  | 15.6 | 12.5 |  | 12.5 |  | 12.5 | 12.5 | 12.6
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.8 | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  |  | Hours PA > 95% Peak Load |  | 6.5 | 6.5 | 6.5 |  | 6.5 |  | 6.5 | 6.5 |  | 6.5 |  | 6.5 | 6.5 | 6.5
|  |  |  | Raw LAR (MVA) |  | 0.9 | 0.8 | 0.8 |  | 0.9 |  | 1.2
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1.1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Mobile Plant Avail (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 20 | 20 | 20 |  | 20 |  | 20 | 20 |  | 20 |  | 20 | 20 | 20
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## SAUN
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | SAUN - Saunders (66/11kV) | [8 empty] | Supply |  | TMES - Townsville Mesh
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/11kV 4MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.6% W -0.6%2025 S -0.5% W -0.4%2026 S -0.1% W -0.1%2027 S 0.6% W 0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 1.6 MVA on 16/12/2022 at 15:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 5.1 | 5.1 | 5.1 |  | 5.1 |  | 5.1 | 5.4 |  | 5.4 |  | 5.4 | 5.4 | 5.4
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 1.6 | 1.6 | 1.6 |  | 1.6 |  | 1.6 | 1.5 |  | 1.5 |  | 1.5 | 1.5 | 1.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.924 | 0.924 | 0.924 |  | 0.924 |  | 0.924 | 0.907 |  | 0.907 |  | 0.907 | 0.907 | 0.907
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 1.5 | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.4 |  | 1.4 |  | 1.4 | 1.4 | 1.4
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 44 | 44 | 44 |  | 44 |  | 44 | 44 |  | 44 |  | 44 | 44 | 44
|  |  |  | Raw LAR (MVA) |  | 1.5 | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.4 |  | 1.4 |  | 1.4 | 1.4 | 1.4
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 2.7 | 2.7 | 2.7 |  | 2.7 |  | 2.7 | 2.7 |  | 2.7 |  | 2.7 | 2.7 | 2.7
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 3.6 | 3.6 | 3.6 |  | 3.6 |  | 3.6 | 3.6 |  | 3.6 |  | 3.6 | 3.6 | 3.6
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## SHUT
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | SHUT - Shutehaven (66/22kV) | [8 empty] | Supply |  | PROS - Proserpine BSP
| Description |  |  |  | Region is Mackay
Transformer size is 1x66/22kV 15/20/25MVA ONAN/ONAF/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.1% W -0.7%2025 S -0.8% W -0.2%2026 S -0.4% W 0.0%,2027 S 0.2% W -0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 9.6 MVA on 14/12/2022 at 15:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 30.4 | 30.4 | 30.4 |  | 30.4 |  | 30.4 | 33.2 |  | 33.2 |  | 33.2 | 33.2 | 33.2
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 9.5 | 9.4 | 9.4 |  | 9.4 |  | 9.5 | 6.4 |  | 6.4 |  | 6.4 | 6.4 | 6.4
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.994 | 0.994 | 0.994 |  | 0.994 |  | 0.994 | 0.99 |  | 0.99 |  | 0.99 | 0.99 | 0.99
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 9.2 | 9.2 | 9.1 |  | 9.1 |  | 9.2 | 6.2 |  | 6.2 |  | 6.2 | 6.2 | 6.2
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Hours PA > 95% Peak Load |  | 13.5 | 13.5 | 13.5 |  | 13.5 |  | 13.5 | 13.5 |  | 13.5 |  | 13.5 | 13.5 | 13.5
|  |  |  | Raw LAR (MVA) |  | 9.2 | 9.2 | 9.1 |  | 9.1 |  | 9.2 | 6.2 |  | 6.2 |  | 6.2 | 6.2 | 6.2
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 13.3 | 13.3 | 13.3 |  | 13.3 |  | 13.3 | 13.3 |  | 13.3 |  | 13.3 | 13.3 | 13.3
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 15 | 15 | 15 |  | 15 |  | 15 | 15 |  | 15 |  | 15 | 15 | 15
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## SKIE
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | SKIE - Skid E (Chinchilla) (33/11kV) | [8 empty] | Supply |  | CHIN - Chinchilla BSP
| Description |  |  |  | Region is South West
Transformer size is 1x33/11kV 5MVA Skid ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.8% W -0.2%2025 S -0.7% W 0.0%,2026 S -0.2% W 0.4%,2027 S 0.4% W 0.4%
|  |  | Latest Peak Compensated Load | [5 empty] | 4.1 MVA on 12/02/2023 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 5.5 | 5.5 | 5.5 |  | 5.5 |  | 5.5 | 5.5 |  | 5.5 |  | 5.5 | 5.5 | 5.5
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 4.1 | 4.1 | 4.1 |  | 4.1 |  | 4.2 | 4 |  | 4 |  | 4 | 4 | 4.1
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.985 | 0.985 | 0.985 |  | 0.985 |  | 0.985 | 0.993 |  | 0.993 |  | 0.993 | 0.993 | 0.993
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 4 | 3.9 | 3.9 |  | 4 |  | 4 | 3.8 |  | 3.8 |  | 3.8 | 3.8 | 3.9
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 8.5 | 8.5 | 8.5 |  | 8.5 |  | 8.5 | 8.5 |  | 8.5 |  | 8.5 | 8.5 | 8.5
|  |  |  | Raw LAR (MVA) |  | 4 | 3.9 | 3.9 |  | 4 |  | 4 | 3.8 |  | 3.8 |  | 3.8 | 3.8 | 3.9
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 2.2 | 2.2 | 2.2 |  | 2.2 |  | 2.2 | 2.2 |  | 2.2 |  | 2.2 | 2.2 | 2.2
|  |  |  | Mobile Plant Avail (MVA) |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 | 5 | 5
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## SOBL
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | SOBL - South Blackwater (66/22kV) | [8 empty] | Supply |  | T032 - Blackwater BSP
| Description |  |  |  | Region is Capricornia
Transformer size is 1x66/22kV 0.3MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -4.5% W -2.1%2025 S -2.3% W -1.9%2026 S -1.9% W -1.6%2027 S -0.5% W -0.8
|  |  | Latest Peak Compensated Load | [5 empty] | 0.4 MVA on 13/02/2023 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 0.4 | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | LARn (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1
|  |  |  | LARn (MW) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1
|  |  |  | Power Factor at Peak Load |  | 0.847 | 0.847 | 0.847 |  | 0.847 |  | 0.847 | 0.843 |  | 0.843 |  | 0.843 | 0.843 | 0.843
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 0.4 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 | 2 | 2
|  |  |  | Raw LAR (MVA) |  | 0.4 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Mobile Plant Avail (MVA) |  | 0.4 | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | No | No | No |  | No |  | No | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## SOBU
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | SOBU - South Bundaberg (66/11kV) | [8 empty] | Supply |  | BUND - Bundaberg BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 2x66/11kV 14/19MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.7% W -0.0%2025 S -0.6% W 0.2%,2026 S -0.1% W 0.5%,2027 S 0.4% W 0.4%
|  |  | Latest Peak Compensated Load | [5 empty] | 13 MVA on 13/02/2023 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 42.4 | 42.4 | 42.4 |  | 42.4 |  | 42.4 | 46.6 |  | 46.6 |  | 46.6 | 46.6 | 46.6
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 17.1 | 17.1 | 17 |  | 17.1 |  | 17.3 | 14.4 |  | 14.4 |  | 14.4 | 14.5 | 14.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.996 | 0.996 | 0.996 |  | 0.996 |  | 0.996 | 0.997 |  | 0.997 |  | 0.997 | 0.997 | 0.997
|  |  |  | ECC Rating (MVA) |  | 24.2 | 24.2 | 24.2 |  | 24.2 |  | 24.2 | 25.4 |  | 25.4 |  | 25.4 | 25.4 | 25.4
|  |  |  | 50 PoE Load (MVA) |  | 16 | 15.9 | 15.9 |  | 16 |  | 16.1 | 13.6 |  | 13.6 |  | 13.6 | 13.6 | 13.7
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.8 | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.7 |  | 0.7 |  | 0.7 | 0.7 | 0.7
|  |  |  | Hours PA > 95% Peak Load |  | 3 | 3 | 3 |  | 3 |  | 3 | 3 |  | 3 |  | 3 | 3 | 3
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 12.6 | 12.6 | 12.6 |  | 12.6 |  | 12.6 | 12.6 |  | 12.6 |  | 12.6 | 12.6 | 12.6
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 6.3 | 6.3 | 6.3 |  | 6.3 |  | 6.3 | 6.3 |  | 6.3 |  | 6.3 | 6.3 | 6.3
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## SOKO
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | SOKO - South Kolan (66/11kV) | [8 empty] | Supply |  | BUND - Bundaberg BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 2x66/11kV 7.5/10MVA ON/ONB
Capacity of commissioned Embedded Generation (with Connection Agreements) is 1.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.7% W -0.6%2025 S -0.5% W -0.4%2026 S -0.1% W 0.0%,2027 S 0.6% W 0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 5.4 MVA on 30/01/2023 at 20:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 27.5 | 27.5 | 27.5 |  | 27.5 |  | 27.5 | 29.9 |  | 29.9 |  | 29.9 | 29.9 | 29.9
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 5.4 | 5.4 | 5.4 |  | 5.4 |  | 5.5 | 4.5 |  | 4.5 |  | 4.5 | 4.5 | 4.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.971 | 0.971 | 0.971 |  | 0.971 |  | 0.971 | 0.985 |  | 0.985 |  | 0.985 | 0.985 | 0.985
|  |  |  | ECC Rating (MVA) |  | 15 | 15 | 15 |  | 15 |  | 15 | 15 |  | 15 |  | 15 | 15 | 15
|  |  |  | 50 PoE Load (MVA) |  | 5.1 | 5.1 | 5.1 |  | 5.1 |  | 5.2 | 4.1 |  | 4.1 |  | 4.1 | 4.1 | 4.1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 8.5 | 8.5 | 8.5 |  | 8.5 |  | 8.5 | 8.5 |  | 8.5 |  | 8.5 | 8.5 | 8.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 15 | 15 | 15 |  | 15 |  | 15 | 15 |  | 15 |  | 15 | 15 | 15
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 7.5 | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 | 7.5
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## SOMA
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | SOMA - South Mackay (33/11kV) | [8 empty] | Supply |  | MACK - Mackay BSP
| Description |  |  |  | Region is Mackay
Transformer size is 2x33/11kV 12.5/15/20MVA ONAN/ONAF/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 2.4 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -4.6% W -0.9%2025 S -2.2% W -1.1%2026 S -0.9% W -0.7%2027 S -0.3% W -0.7
|  |  | Latest Peak Compensated Load | [5 empty] | 20.4 MVA on 01/02/2023 at 14:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 40 | 40 | 40 |  | 40 |  | 40 | 40 |  | 40 |  | 40 | 40 | 40
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 18.5 | 18.1 | 17.9 |  | 17.9 |  | 18 | 16.1 |  | 15.9 |  | 15.7 | 15.6 | 15.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 1 | 1 | 1 |  | 1 |  | 1 | 0.97 |  | 0.97 |  | 0.97 | 0.97 | 0.97
|  |  |  | ECC Rating (MVA) |  | 21 | 21 | 21 |  | 21 |  | 21 | 22 |  | 22 |  | 22 | 22 | 22
|  |  |  | 50 PoE Load (MVA) |  | 17.9 | 17.5 | 17.3 |  | 17.3 |  | 17.4 | 15.6 |  | 15.4 |  | 15.2 | 15.1 | 15
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.9 | 0.9 | 0.9 |  | 0.9 |  | 0.9 | 0.8 |  | 0.8 |  | 0.8 | 0.8 | 0.8
|  |  |  | Hours PA > 95% Peak Load |  | 21.5 | 21.5 | 21.5 |  | 21.5 |  | 21.5 | 21.5 |  | 21.5 |  | 21.5 | 21.5 | 21.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 1.8 | 1.8 | 1.8 |  | 1.8 |  | 1.8 | 1.8 |  | 1.8 |  | 1.8 | 1.8 | 1.8
|  |  |  | Mobile Plant Avail (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 | 2 | 2
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 25 | 25 | 25 |  | 25 |  | 25 | 25 |  | 25 |  | 25 | 25 | 25
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 12.5 | 12.5 | 12.5 |  | 12.5 |  | 12.5 | 12.5 |  | 12.5 |  | 12.5 | 12.5 | 12.5
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## SOTO
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | SOTO - South Toowoomba (33/11kV) | [8 empty] | Supply |  | T043 - South Toowoomba BSP
| Description |  |  |  | Region is South West
Transformer size is 3x33/11kV 11.5MVA ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.9% W -0.4%2025 S -1.3% W -0.3%2026 S -0.7% W 0.0%,2027 S 0.0% W 0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 21.2 MVA on 04/07/2022 at 17:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 37.4 | 37.4 | 37.4 |  | 37.4 |  | 37.4 | 42.4 |  | 42.4 |  | 42.4 | 42.4 | 42.4
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 16 | 15.8 | 15.7 |  | 15.7 |  | 15.9 | 22 |  | 21.9 |  | 21.8 | 21.8 | 21.8
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.977 | 0.977 | 0.977 |  | 0.977 |  | 0.977 | 0.992 |  | 0.992 |  | 0.992 | 0.992 | 0.992
|  |  |  | ECC Rating (MVA) |  | 28.3 | 28.3 | 28.3 |  | 28.3 |  | 28.3 | 31.2 |  | 31.2 |  | 31.2 | 31.2 | 31.2
|  |  |  | 50 PoE Load (MVA) |  | 15.1 | 14.9 | 14.8 |  | 14.8 |  | 14.9 | 21 |  | 21 |  | 20.9 | 20.9 | 20.9
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.8 | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 1.1 |  | 1.1 |  | 1 | 1 | 1
|  |  |  | Hours PA > 95% Peak Load |  | 20.5 | 20.5 | 20.5 |  | 20.5 |  | 20.5 | 20.5 |  | 20.5 |  | 20.5 | 20.5 | 20.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 10.8 | 10.8 | 10.8 |  | 10.8 |  | 10.8 | 10.8 |  | 10.8 |  | 10.8 | 10.8 | 10.8
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## STAM
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | STAM - Stamford (66/33kV) | [8 empty] | Supply |  | T095 - Millchester BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/33/19kV 0.63MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.9% W -0.5%2025 S -0.8% W -0.3%2026 S -0.3% W 0.0%,2027 S 0.3% W 0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 0.3 MVA on 07/12/2022 at 20:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 0.7 | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.7 | 0.7
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 |  | 0.3 |  | 0.2 | 0.2 | 0.2
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.925 | 0.925 | 0.925 |  | 0.925 |  | 0.925 | 0.888 |  | 0.888 |  | 0.888 | 0.888 | 0.888
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 8.5 | 8.5 | 8.5 |  | 8.5 |  | 8.5 | 8.5 |  | 8.5 |  | 8.5 | 8.5 | 8.5
|  |  |  | Raw LAR (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 0.63 | 0.63 | 0.63 |  | 0.63 |  | 0.63 | 0.63 |  | 0.63 |  | 0.63 | 0.63 | 0.63
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## STAN
Bulk Summary Information and Peak Load Forecast
Substation |  |  |  | STAN - Stanthorpe BSP (110/33kV) | [8 empty] | Supply |  | QMRG - Middle Ridge (Ergon) TCP
Description |  |  |  | Region is South West
Transformer size is 2x103/33kV 20/30MVA ON/OB
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
|  | Latest Peak Compensated Load | [5 empty] | 14.2 MVA on 04/07/2022 at 20:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[5 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  | NCC Rating (MVA) |  | 71.3 | 71.3 | 71.3 |  | 71.3 |  | 71.3 | 80.4 |  | 80.4 |  | 80.4 | 80.4 | 80.4
|  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | 10 PoE Load (MVA) |  | 13.4 | 13.8 | 13.8 |  | 13.9 |  | 14 | 15.1 |  | 15.6 |  | 16.1 | 16.1 | 16.1
LARn (MVA)
LARn (MW)
|  |  | Power Factor at Peak Load |  | 0.979 | 0.979 | 0.979 |  | 0.979 |  | 0.979 | 0.997 |  | 0.997 |  | 0.997 | 0.997 | 0.997
|  |  | ECC Rating (MVA) |  | 40.5 | 40.5 | 40.5 |  | 40.5 |  | 40.5 | 43.8 |  | 43.8 |  | 43.8 | 43.8 | 43.8
|  |  | 50 PoE Load (MVA) |  | 12.5 | 12.8 | 12.8 |  | 12.9 |  | 13 | 14.7 |  | 15.1 |  | 15.6 | 15.7 | 15.7
|  |  | 50 PoE Load > 95% (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.7 | 0.7 |  | 0.8 |  | 0.8 | 0.8 | 0.8
|  |  | Hours PA > 95% Peak Load |  | 19 | 19 | 19 |  | 19 |  | 19 | 19 |  | 19 |  | 19 | 19 | 19
Raw LAR (MVA)
|  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Capacity for Embedded Generation (MVA) |  | 4.3 | 4.3 | 4.3 |  | 4.3 |  | 4.3 | 4.3 |  | 4.3 |  | 4.3 | 4.3 | 4.3
|  |  | Firm Capacity for Embedded Generation (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 | 2 | 2
LARc (MVA)
LARc (MW)
|  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## STTO
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | STTO - Stanthorpe Town (33/11kV) | [8 empty] | Supply |  | STAN - Stanthorpe BSP
| Description |  |  |  | Region is South West
Transformer size is 2x33/11kV 10MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.7% W -0.4%2025 S -0.6% W -0.1%2026 S -0.1% W 0.2%,2027 S 0.5% W 0.2%
|  |  | Latest Peak Compensated Load | [5 empty] | 11.9 MVA on 08/07/2022 at 20:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 23.4 | 23.4 | 23.4 |  | 23.4 |  | 23.4 | 25.3 |  | 25.3 |  | 25.3 | 25.3 | 25.3
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 11 | 11.4 | 11.4 |  | 11.4 |  | 11.5 | 12.5 |  | 13 |  | 13.5 | 13.5 | 13.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.983 | 0.983 | 0.983 |  | 0.983 |  | 0.983 | 0.994 |  | 0.994 |  | 0.994 | 0.994 | 0.994
|  |  |  | ECC Rating (MVA) |  | 13 | 13 | 13 |  | 13 |  | 13 | 14 |  | 14 |  | 14 | 14 | 14
|  |  |  | 50 PoE Load (MVA) |  | 10.1 | 10.5 | 10.5 |  | 10.5 |  | 10.7 | 12.2 |  | 12.6 |  | 13.1 | 13.2 | 13.2
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.6 |  | 0.6 |  | 0.7 | 0.7 | 0.7
|  |  |  | Hours PA > 95% Peak Load |  | 16 | 16 | 16 |  | 16 |  | 16 | 16 |  | 16 |  | 16 | 16 | 16
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 20 | 20 | 20 |  | 20 |  | 20 | 20 |  | 20 |  | 20 | 20 | 20
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## STUA
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | STUA - Stuart (66/11kV) | [8 empty] | Supply |  | TMES - Townsville Mesh
| Description |  |  |  | Region is Nth Queensland
Transformer size is 2x66/11kV 21/26/35MVA ONAN/ODAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -1.9% W 0.7%,2025 S 0.2% W 1.1%, 2026 S 0.6% W 1.3%, 2027 S 1.6% W 1.6%
|  |  | Latest Peak Compensated Load | [5 empty] | 27.2 MVA on 02/02/2023 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 76.7 | 76.7 | 76.7 |  | 76.7 |  | 76.7 | 81.6 |  | 81.6 |  | 81.6 | 81.6 | 81.6
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 27.3 | 27.4 | 13.8 |  | 14.2 |  | 14.9 | 26.3 |  | 26.5 |  | 26.8 | 12.5 | 13
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.97 | 0.97 | 0.97 |  | 0.97 |  | 0.97 | 0.964 |  | 0.964 |  | 0.964 | 0.964 | 0.964
|  |  |  | ECC Rating (MVA) |  | 45.5 | 45.5 | 45.5 |  | 45.5 |  | 45.5 | 47.2 |  | 47.2 |  | 47.2 | 47.2 | 47.2
|  |  |  | 50 PoE Load (MVA) |  | 26.7 | 26.7 | 13.1 |  | 13.5 |  | 14.2 | 25.3 |  | 25.5 |  | 25.8 | 11.5 | 12
|  |  |  | 50 PoE Load > 95% (MVA) |  | 1.3 | 1.3 | 0.7 |  | 0.7 |  | 0.7 | 1.3 |  | 1.3 |  | 1.3 | 0.6 | 0.6
|  |  |  | Hours PA > 95% Peak Load |  | 46.5 | 46.5 | 46.5 |  | 46.5 |  | 46.5 | 46.5 |  | 46.5 |  | 46.5 | 46.5 | 46.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 42 | 42 | 42 |  | 42 |  | 42 | 42 |  | 42 |  | 42 | 42 | 42
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 21 | 21 | 21 |  | 21 |  | 21 | 21 |  | 21 |  | 21 | 21 | 21
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## T002
Bulk Summary Information and Peak Load Forecast
Substation |  |  |  | T002 - Dalby East BSP (110/33kV) | [8 empty] | Supply |  | QTKM - Tangkam TCP
Description |  |  |  | Region is South West
Transformer size is 2x110/33kV 50/63MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 5.4 MVA
|  | Latest Peak Compensated Load | [5 empty] | 29.7 MVA on 10/06/2022 at 07:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[5 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  | NCC Rating (MVA) |  | 130.3 | 130.3 | 130.3 |  | 130.3 |  | 130.3 | 149.7 |  | 149.7 |  | 149.7 | 149.7 | 149.7
|  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | 10 PoE Load (MVA) |  | 32.2 | 33.1 | 33 |  | 33 |  | 33.2 | 32.2 |  | 34.1 |  | 34.8 | 34.8 | 34.9
LARn (MVA)
LARn (MW)
|  |  | Power Factor at Peak Load |  | 0.985 | 0.985 | 0.985 |  | 0.985 |  | 0.985 | 0.99 |  | 0.989 |  | 0.989 | 0.989 | 0.989
|  |  | ECC Rating (MVA) |  | 74.4 | 74.4 | 74.4 |  | 74.4 |  | 74.4 | 85.5 |  | 85.5 |  | 85.5 | 85.5 | 85.5
|  |  | 50 PoE Load (MVA) |  | 30.3 | 31.2 | 31.1 |  | 31.1 |  | 31.3 | 30.3 |  | 32.2 |  | 32.9 | 32.9 | 33
|  |  | 50 PoE Load > 95% (MVA) |  | 1.5 | 1.6 | 1.6 |  | 1.6 |  | 1.6 | 1.5 |  | 1.6 |  | 1.6 | 1.6 | 1.7
|  |  | Hours PA > 95% Peak Load |  | 6.5 | 6.5 | 6.5 |  | 6.5 |  | 6.5 | 6.5 |  | 6.5 |  | 6.5 | 6.5 | 6.5
Raw LAR (MVA)
|  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Capacity for Embedded Generation (MVA) |  | 100 | 100 | 100 |  | 100 |  | 100 | 100 |  | 100 |  | 100 | 100 | 100
|  |  | Firm Capacity for Embedded Generation (MVA) |  | 50 | 50 | 50 |  | 50 |  | 50 | 50 |  | 50 |  | 50 | 50 | 50
LARc (MVA)
LARc (MW)
|  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## T019
Bulk Summary Information and Peak Load Forecast
Substation |  |  |  | T019 - Gladstone South BSP (132/66kV) | [8 empty] | Supply |  | QGST - Gladstone South TCP
Description |  |  |  | Region is Capricornia
Transformer size is 1xGLSO 3 TRANSFORMER-132/66/11KV TRANSF 3;1xGLSO 6 TRANSFORMER-132/66/11 TRANSF 6
Capacity of commissioned Embedded Generation (with Connection Agreements) is 1.1 MVA
|  | Latest Peak Compensated Load | [5 empty] | 49.2 MVA on 13/02/2023 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[5 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  | NCC Rating (MVA) |  | 120 | 120 | 120 |  | 120 |  | 120 | 120 |  | 120 |  | 120 | 120 | 120
|  |  | Contracted non-network (MVA) |  | 1.5 | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.5 | 1.5
|  |  | 10 PoE Load (MVA) |  | 48.7 | 49 | 49 |  | 49.2 |  | 49.8 | 36.8 |  | 37.6 |  | 37.5 | 37.6 | 37.7
LARn (MVA)
LARn (MW)
|  |  | Power Factor at Peak Load |  | 0.928 | 0.928 | 0.928 |  | 0.928 |  | 0.928 | 0.948 |  | 0.948 |  | 0.948 | 0.948 | 0.948
|  |  | ECC Rating (MVA) |  | 80 | 80 | 80 |  | 80 |  | 80 | 80 |  | 80 |  | 80 | 80 | 80
|  |  | 50 PoE Load (MVA) |  | 45.7 | 46.1 | 46 |  | 46.2 |  | 46.8 | 34.1 |  | 35 |  | 34.9 | 35 | 35
|  |  | 50 PoE Load > 95% (MVA) |  | 2.3 | 2.3 | 2.3 |  | 2.3 |  | 2.3 | 1.7 |  | 1.8 |  | 1.7 | 1.8 | 1.8
|  |  | Hours PA > 95% Peak Load |  | 13.5 | 13.5 | 13.5 |  | 13.5 |  | 13.5 | 13.5 |  | 13.5 |  | 13.5 | 13.5 | 13.5
Raw LAR (MVA)
|  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Manual Trans Avail (MVA) |  | 6 | 6 | 6 |  | 6 |  | 6 | 6 |  | 6 |  | 6 | 6 | 6
|  |  | Mobile Plant Avail (MVA) |  | 4 | 4 | 4 |  | 4 |  | 4 | 4 |  | 4 |  | 4 | 4 | 4
|  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Capacity for Embedded Generation (MVA) |  | 30 | 30 | 30 |  | 30 |  | 30 | 30 |  | 30 |  | 30 | 30 | 30
|  |  | Firm Capacity for Embedded Generation (MVA) |  | 15 | 15 | 15 |  | 15 |  | 15 | 15 |  | 15 |  | 15 | 15 | 15
LARc (MVA)
LARc (MW)
|  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## T032
Bulk Summary Information and Peak Load Forecast
Substation |  |  |  | T032 - Blackwater BSP (132/66kV) | [8 empty] | Supply |  | QBWL - Blackwater 66kV TCP
Description |  |  |  | Region is Capricornia
Transformer size is 1xBLAC TX NO 1-132/66KV TRANSF 1;1xBLAC TX NO 2-132/66KV TRANSF 2;1xBLACSS TRANSFORMER
Capacity of commissioned Embedded Generation (with Connection Agreements) is 70.0 MVA
|  | Latest Peak Compensated Load | [5 empty] | 99 MVA on 11/08/2022 at 09:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[5 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  | NCC Rating (MVA) |  | 120 | 120 | 120 |  | 120 |  | 120 | 120 |  | 120 |  | 120 | 120 | 120
|  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | 10 PoE Load (MVA) |  | 100.1 | 99.9 | 101.2 |  | 101.2 |  | 101.4 | 101.7 |  | 101.6 |  | 102.2 | 102.2 | 102.1
LARn (MVA)
LARn (MW)
|  |  | Power Factor at Peak Load |  | 0.985 | 0.985 | 0.985 |  | 0.985 |  | 0.985 | 0.999 |  | 0.999 |  | 0.999 | 0.999 | 0.999
|  |  | ECC Rating (MVA) |  | 104 | 104 | 104 |  | 104 |  | 104 | 104 |  | 104 |  | 104 | 104 | 104
|  |  | 50 PoE Load (MVA) |  | 96.8 | 96.6 | 97.9 |  | 97.9 |  | 98.1 | 98.2 |  | 98.1 |  | 98.7 | 98.7 | 98.6
|  |  | 50 PoE Load > 95% (MVA) |  | 4.8 | 4.8 | 4.9 |  | 4.9 |  | 4.9 | 4.9 |  | 4.9 |  | 4.9 | 4.9 | 4.9
|  |  | Hours PA > 95% Peak Load |  | 8.5 | 8.5 | 8.5 |  | 8.5 |  | 8.5 | 8.5 |  | 8.5 |  | 8.5 | 8.5 | 8.5
Raw LAR (MVA)
|  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Manual Trans Avail (MVA) |  | 6 | 6 | 6 |  | 6 |  | 6 | 6 |  | 6 |  | 6 | 6 | 6
|  |  | Mobile Plant Avail (MVA) |  | 4 | 4 | 4 |  | 4 |  | 4 | 4 |  | 4 |  | 4 | 4 | 4
|  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
Capacity for Embedded Generation (MVA)
Firm Capacity for Embedded Generation (MVA)
LARc (MVA)
LARc (MW)
|  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## T043
Bulk Summary Information and Peak Load Forecast
Substation |  |  |  | T043 - South Toowoomba BSP (110/33kV) | [8 empty] | Supply |  | QMRG - Middle Ridge (Ergon) TCP
Description |  |  |  | Region is South West
Transformer size is 1x106/33kV 35/60MVA ON/OFB;1x106/33kV 37/48/60MVA ON/OB/OFB
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
|  | Latest Peak Compensated Load | [5 empty] | 62.7 MVA on 04/07/2022 at 17:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[5 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  | NCC Rating (MVA) |  | 144.9 | 144.9 | 144.9 |  | 144.9 |  | 144.9 | 163.6 |  | 163.6 |  | 163.6 | 163.6 | 163.6
|  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | 10 PoE Load (MVA) |  | 48.3 | 48.3 | 48.4 |  | 48.4 |  | 48.8 | 67.4 |  | 67.3 |  | 67.6 | 67.9 | 67.9
LARn (MVA)
LARn (MW)
|  |  | Power Factor at Peak Load |  | 0.982 | 0.982 | 0.982 |  | 0.982 |  | 0.982 | 0.987 |  | 0.987 |  | 0.987 | 0.987 | 0.987
|  |  | ECC Rating (MVA) |  | 81.4 | 81.4 | 81.4 |  | 81.4 |  | 81.4 | 89.3 |  | 89.3 |  | 89.3 | 89.3 | 89.3
|  |  | 50 PoE Load (MVA) |  | 45.1 | 45.2 | 45.2 |  | 45.3 |  | 45.7 | 63.3 |  | 63.2 |  | 63.6 | 63.9 | 63.9
|  |  | 50 PoE Load > 95% (MVA) |  | 2.3 | 2.3 | 2.3 |  | 2.3 |  | 2.3 | 3.2 |  | 3.2 |  | 3.2 | 3.2 | 3.2
|  |  | Hours PA > 95% Peak Load |  | 120 | 120 | 120 |  | 120 |  | 120 | 120 |  | 120 |  | 120 | 120 | 120
Raw LAR (MVA)
|  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Capacity for Embedded Generation (MVA) |  | 72 | 72 | 72 |  | 72 |  | 72 | 72 |  | 72 |  | 72 | 72 | 72
|  |  | Firm Capacity for Embedded Generation (MVA) |  | 35 | 35 | 35 |  | 35 |  | 35 | 35 |  | 35 |  | 35 | 35 | 35
LARc (MVA)
LARc (MW)
|  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## T047
Bulk Summary Information and Peak Load Forecast
Substation |  |  |  | T047 - Ingham BSP (132/66kV) | [8 empty] | Supply |  | QING - Ingham TCP
Description |  |  |  | Region is Nth Queensland
Transformer size is 1x132/66kV 34 MVA;1xINSOSS 1T 132KV 1 TRANSF TFMR-1
Capacity of commissioned Embedded Generation (with Connection Agreements) is 38.8 MVA
|  | Latest Peak Compensated Load | [5 empty] | 17.8 MVA on 02/02/2023 at 17:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[5 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  | NCC Rating (MVA) |  | 68 | 68 | 68 |  | 68 |  | 68 | 68 |  | 68 |  | 68 | 68 | 68
|  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  | 10 PoE Load (MVA) |  | 18.6 | 18.5 | 18.3 |  | 18.3 |  | 18.5 | 15.6 |  | 15.6 |  | 15.5 | 15.5 | 15.4
LARn (MVA)
LARn (MW)
|  |  | Power Factor at Peak Load |  | 0.999 | 0.999 | 0.999 |  | 0.999 |  | 0.999 | 0.994 |  | 0.994 |  | 0.994 | 0.994 | 0.994
|  |  | ECC Rating (MVA) |  | 34 | 34 | 34 |  | 34 |  | 34 | 34 |  | 34 |  | 34 | 34 | 34
|  |  | 50 PoE Load (MVA) |  | 18 | 17.8 | 17.7 |  | 17.7 |  | 17.8 | 14.7 |  | 14.7 |  | 14.6 | 14.6 | 14.6
|  |  | 50 PoE Load > 95% (MVA) |  | 0.9 | 0.9 | 0.9 |  | 0.9 |  | 0.9 | 0.7 |  | 0.7 |  | 0.7 | 0.7 | 0.7
|  |  | Hours PA > 95% Peak Load |  | 12.5 | 12.5 | 12.5 |  | 12.5 |  | 12.5 | 12.5 |  | 12.5 |  | 12.5 | 12.5 | 12.5
Raw LAR (MVA)
|  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Manual Trans Avail (MVA) |  | 6 | 6 | 6 |  | 6 |  | 6 | 6 |  | 6 |  | 6 | 6 | 6
|  |  | Mobile Plant Avail (MVA) |  | 4 | 4 | 4 |  | 4 |  | 4 | 4 |  | 4 |  | 4 | 4 | 4
|  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Capacity for Embedded Generation (MVA) |  | 34 | 34 | 34 |  | 34 |  | 34 | 34 |  | 34 |  | 34 | 34 | 34
|  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## T058
Bulk Summary Information and Peak Load Forecast
Substation |  |  |  | T058 - Warwick BSP (110/33kV) | [8 empty] | Supply |  | QMRG - Middle Ridge (Ergon) TCP
Description |  |  |  | Region is South West
Transformer size is 2x110/33/11kV 40/50MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
|  | Latest Peak Compensated Load | [5 empty] | 41.6 MVA on 13/07/2022 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[5 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  | NCC Rating (MVA) |  | 118.5 | 118.5 | 118.5 |  | 118.5 |  | 118.5 | 135.6 |  | 135.6 |  | 135.6 | 135.6 | 135.6
|  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | 10 PoE Load (MVA) |  | 41.2 | 40.9 | 40.7 |  | 40.8 |  | 41.3 | 43.4 |  | 43.2 |  | 43.2 | 43.2 | 43.3
LARn (MVA)
LARn (MW)
|  |  | Power Factor at Peak Load |  | 0.998 | 0.998 | 0.998 |  | 0.998 |  | 0.998 | 1 |  | 1 |  | 1 | 1 | 1
|  |  | ECC Rating (MVA) |  | 68 | 68 | 68 |  | 68 |  | 68 | 74.8 |  | 74.8 |  | 74.8 | 74.8 | 74.8
|  |  | 50 PoE Load (MVA) |  | 38.6 | 38.3 | 38.1 |  | 38.2 |  | 38.6 | 41.9 |  | 41.8 |  | 41.7 | 41.8 | 41.8
|  |  | 50 PoE Load > 95% (MVA) |  | 1.9 | 1.9 | 1.9 |  | 1.9 |  | 1.9 | 2.1 |  | 2.1 |  | 2.1 | 2.1 | 2.1
|  |  | Hours PA > 95% Peak Load |  | 9 | 9 | 9 |  | 9 |  | 9 | 9 |  | 9 |  | 9 | 9 | 9
Raw LAR (MVA)
|  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Capacity for Embedded Generation (MVA) |  | 80 | 80 | 80 |  | 80 |  | 80 | 80 |  | 80 |  | 80 | 80 | 80
|  |  | Firm Capacity for Embedded Generation (MVA) |  | 40 | 40 | 40 |  | 40 |  | 40 | 40 |  | 40 |  | 40 | 40 | 40
LARc (MVA)
LARc (MW)
|  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## T072
Bulk Summary Information and Peak Load Forecast
Substation |  |  |  | T072 - Barcaldine BSP (132/66kV) | [8 empty] | Supply |  | QLCM - Lilyvale (Barcaldine & Clermont) TCP
Description |  |  |  | Region is Capricornia
Transformer size is 1x132/66/11kV 15+5MVA ONAN;1x132/69/11kV 24MVA ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 43.4 MVA
|  | Latest Peak Compensated Load | [5 empty] | 21.5 MVA on 07/12/2022 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[5 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  | NCC Rating (MVA) |  | 26.6 | 48 | 48 |  | 48 |  | 48 | 26.6 |  | 26.6 |  | 48 | 48 | 48
|  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  | 10 PoE Load (MVA) |  | 22.1 | 21.9 | 21.8 |  | 21.8 |  | 22 | 20.1 |  | 20 |  | 19.9 | 19.8 | 19.8
LARn (MVA)
LARn (MW)
|  |  | Power Factor at Peak Load |  | 0.985 | 0.985 | 0.985 |  | 0.985 |  | 0.985 | 0.947 |  | 0.947 |  | 0.947 | 0.947 | 0.947
|  |  | ECC Rating (MVA) |  | 13.3 | 24 | 24 |  | 24 |  | 24 | 14.6 |  | 14.6 |  | 24 | 24 | 24
|  |  | 50 PoE Load (MVA) |  | 21.1 | 20.8 | 20.7 |  | 20.7 |  | 20.9 | 19.1 |  | 19 |  | 18.9 | 18.9 | 18.9
|  |  | 50 PoE Load > 95% (MVA) |  | 1.1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 0.9 | 0.9 | 0.9
|  |  | Hours PA > 95% Peak Load |  | 104.5 | 104.5 | 104.5 |  | 104.5 |  | 104.5 | 104.5 |  | 104.5 |  | 104.5 | 104.5 | 104.5
|  |  | Raw LAR (MVA) |  | 7.8 | [6 empty] | 4.5 |  | 4.4
|  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Remote Trans Avail (MVA) |  | 6.7 | 6.7 | 6.7 |  | 6.7 |  | 6.7 | 6.7 |  | 6.7 |  | 6.7 | 6.7 | 6.7
|  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Mobile Plant Avail (MVA) |  | 0.7 | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.7 | 0.7
|  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | LARc (MVA) |  | 0.4
|  |  | LARc (MW) |  | 0.4
|  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  | Meets Security Standard |  | No | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## T083
Bulk Summary Information and Peak Load Forecast
Substation |  |  |  | T083 - Roma 33kV BSP (132/33kV) | [8 empty] | Supply |  | T194 - Columboola TCP
Description |  |  |  | Region is South West
Transformer size is 1x132/33/11KV 60/80MVA ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 1.0 MVA
|  | Latest Peak Compensated Load | [5 empty] | 25 MVA on 15/07/2022 at 07:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[5 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  | NCC Rating (MVA) |  | 97.8 | 97.8 | 97.8 |  | 97.8 |  | 97.8 | 115.2 |  | 115.2 |  | 115.2 | 115.2 | 115.2
|  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | 10 PoE Load (MVA) |  | 26.1 | 25.9 | 27 |  | 27 |  | 27.2 | 27 |  | 26.9 |  | 27.5 | 27.4 | 27.4
LARn (MVA)
LARn (MW)
|  |  | Power Factor at Peak Load |  | 0.997 | 0.997 | 0.997 |  | 0.997 |  | 0.997 | 0.999 |  | 0.999 |  | 0.999 | 0.999 | 0.999
|  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | 50 PoE Load (MVA) |  | 24.6 | 24.5 | 25.6 |  | 25.6 |  | 25.7 | 25.6 |  | 25.6 |  | 26.1 | 26.1 | 26.1
|  |  | 50 PoE Load > 95% (MVA) |  | 1.2 | 1.2 | 1.3 |  | 1.3 |  | 1.3 | 1.3 |  | 1.3 |  | 1.3 | 1.3 | 1.3
|  |  | Hours PA > 95% Peak Load |  | 1323 | 1323 | 1323 |  | 1323 |  | 1323 | 1323 |  | 1323 |  | 1323 | 1323 | 1323
|  |  | Raw LAR (MVA) |  | 24.6 | 24.5 | 25.6 |  | 25.6 |  | 25.7 | 25.6 |  | 25.6 |  | 26.1 | 26.1 | 26.1
|  |  | Auto Trans Avail (MVA) |  | 50 | 50 | 50 |  | 50 |  | 50 | 50 |  | 50 |  | 50 | 50 | 50
|  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
Capacity for Embedded Generation (MVA)
Firm Capacity for Embedded Generation (MVA)
LARc (MVA)
LARc (MW)
|  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## T095
Bulk Summary Information and Peak Load Forecast
Substation |  |  |  | T095 - Millchester BSP (132/66kV) | [8 empty] | Supply |  | QROS - Ross (Kidston and Milchester) TCP
Description |  |  |  | Region is Nth Queensland
Transformer size is 1x132/66/11kV 25/34/40MVA ONAN/ONAF/ODAF;1x132/66kV 25/34MVA ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 55.0 MVA
|  | Latest Peak Compensated Load | [5 empty] | 41 MVA on 18/03/2023 at 20:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[5 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  | NCC Rating (MVA) |  | 68 | 68 | 68 |  | 68 |  | 68 | 68 |  | 68 |  | 68 | 68 | 68
|  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | 10 PoE Load (MVA) |  | 41.9 | 41.7 | 42.8 |  | 42.8 |  | 43 | 34.2 |  | 34 |  | 34.7 | 34.6 | 34.6
LARn (MVA)
LARn (MW)
|  |  | Power Factor at Peak Load |  | 0.998 | 0.998 | 0.998 |  | 0.998 |  | 0.998 | 0.989 |  | 0.989 |  | 0.989 | 0.989 | 0.989
|  |  | ECC Rating (MVA) |  | 37.4 | 37.4 | 37.4 |  | 37.4 |  | 37.4 | 37.4 |  | 37.4 |  | 37.4 | 37.4 | 37.4
|  |  | 50 PoE Load (MVA) |  | 40.8 | 40.6 | 41.7 |  | 41.7 |  | 41.8 | 32.9 |  | 32.8 |  | 33.4 | 33.4 | 33.3
|  |  | 50 PoE Load > 95% (MVA) |  | 2 | 2 | 2.1 |  | 2.1 |  | 2.1 | 1.6 |  | 1.6 |  | 1.7 | 1.7 | 1.7
|  |  | Hours PA > 95% Peak Load |  | 8.5 | 8.5 | 8.5 |  | 8.5 |  | 8.5 | 8.5 |  | 8.5 |  | 8.5 | 8.5 | 8.5
|  |  | Raw LAR (MVA) |  | 3.4 | 3.2 | 4.3 |  | 4.3 |  | 4.4
|  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Manual Trans Avail (MVA) |  | 19.1 | 19.1 | 19.1 |  | 19.1 |  | 19.1 | 19.1 |  | 19.1 |  | 19.1 | 19.1 | 19.1
|  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(30min) |  | 7.9 | 7.9 | 7.9 |  | 7.9 |  | 7.9 | 7.9 |  | 7.9 |  | 7.9 | 7.9 | 7.9
|  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Capacity for Embedded Generation (MVA) |  | 50 | 50 | 50 |  | 50 |  | 50 | 50 |  | 50 |  | 50 | 50 | 50
|  |  | Firm Capacity for Embedded Generation (MVA) |  | 25 | 25 | 25 |  | 25 |  | 25 | 25 |  | 25 |  | 25 | 25 | 25
LARc (MVA)
LARc (MW)
|  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## T116
Bulk Summary Information and Peak Load Forecast
Substation |  |  |  | T116 - Torrington BSP (110/33kV) | [8 empty] | Supply |  | QMRG - Middle Ridge (Ergon) TCP
Description |  |  |  | Region is South West
Transformer size is 2x110/33/11kV 64/80/106MVA ONAN/ODAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 4.4 MVA
|  | Latest Peak Compensated Load | [5 empty] | 108.3 MVA on 04/07/2022 at 17:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[5 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  | NCC Rating (MVA) |  | 239 | 239 | 239 |  | 239 |  | 239 | 286.2 |  | 286.2 |  | 286.2 | 286.2 | 286.2
|  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | 10 PoE Load (MVA) |  | 88.8 | 88.1 | 88 |  | 92.4 |  | 97.5 | 111.4 |  | 111 |  | 110.8 | 113.5 | 116.4
LARn (MVA)
LARn (MW)
|  |  | Power Factor at Peak Load |  | 0.989 | 0.989 | 0.989 |  | 0.989 |  | 0.989 | 0.989 |  | 0.989 |  | 0.989 | 0.989 | 0.989
|  |  | ECC Rating (MVA) |  | 132.3 | 132.3 | 132.3 |  | 132.3 |  | 132.3 | 157.1 |  | 157.1 |  | 157.1 | 157.1 | 157.1
|  |  | 50 PoE Load (MVA) |  | 83 | 82.4 | 82.2 |  | 86.6 |  | 91.6 | 106.2 |  | 105.8 |  | 105.6 | 108.4 | 111.2
|  |  | 50 PoE Load > 95% (MVA) |  | 4.2 | 4.1 | 4.1 |  | 4.3 |  | 4.6 | 5.3 |  | 5.3 |  | 5.3 | 5.4 | 5.6
|  |  | Hours PA > 95% Peak Load |  | 4.5 | 4.5 | 4.5 |  | 4.5 |  | 4.5 | 4.5 |  | 4.5 |  | 4.5 | 4.5 | 4.5
Raw LAR (MVA)
|  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Capacity for Embedded Generation (MVA) |  | 128 | 128 | 128 |  | 128 |  | 128 | 128 |  | 128 |  | 128 | 128 | 128
|  |  | Firm Capacity for Embedded Generation (MVA) |  | 64 | 64 | 64 |  | 64 |  | 64 | 64 |  | 64 |  | 64 | 64 | 64
LARc (MVA)
LARc (MW)
|  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## T130
Bulk Summary Information and Peak Load Forecast
Substation |  |  |  | T130 - Boat Creek BSP (132/66kV) | [8 empty] | Supply |  | QYAE - Boat Creek TCP
Description |  |  |  | Region is Capricornia
Transformer size is 2x132/66/11kV 60/80MVA ONAN/ODAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
|  | Latest Peak Compensated Load | [5 empty] | 48.9 MVA on 12/12/2022 at 11:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[5 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  | NCC Rating (MVA) |  | 151.2 | 151.2 | 151.2 |  | 151.2 |  | 151.2 | 162 |  | 162 |  | 162 | 162 | 162
|  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | 10 PoE Load (MVA) |  | 50 | 50 | 51.3 |  | 52.5 |  | 52.6 | 44.6 |  | 44.6 |  | 44.6 | 45.8 | 46.9
LARn (MVA)
LARn (MW)
|  |  | Power Factor at Peak Load |  | 0.942 | 0.942 | 0.942 |  | 0.942 |  | 0.942 | 0.941 |  | 0.941 |  | 0.941 | 0.941 | 0.941
|  |  | ECC Rating (MVA) |  | 90.9 | 90.9 | 90.9 |  | 90.9 |  | 90.9 | 95.7 |  | 95.7 |  | 95.7 | 95.7 | 95.7
|  |  | 50 PoE Load (MVA) |  | 49.2 | 49.2 | 50.5 |  | 51.8 |  | 51.8 | 43.9 |  | 43.9 |  | 43.9 | 45.1 | 46.2
|  |  | 50 PoE Load > 95% (MVA) |  | 2.5 | 2.5 | 2.5 |  | 2.6 |  | 2.6 | 2.2 |  | 2.2 |  | 2.2 | 2.3 | 2.3
|  |  | Hours PA > 95% Peak Load |  | 100.5 | 100.5 | 100.5 |  | 100.5 |  | 100.5 | 100.5 |  | 100.5 |  | 100.5 | 100.5 | 100.5
Raw LAR (MVA)
|  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Capacity for Embedded Generation (MVA) |  | 120 | 120 | 120 |  | 120 |  | 120 | 120 |  | 120 |  | 120 | 120 | 120
|  |  | Firm Capacity for Embedded Generation (MVA) |  | 60 | 60 | 60 |  | 60 |  | 60 | 60 |  | 60 |  | 60 | 60 | 60
LARc (MVA)
LARc (MW)
|  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## T156
Bulk Summary Information and Peak Load Forecast
Substation |  |  |  | T156 - Waggamba BSP (132/66kV) | [8 empty] | Supply |  | QBLK - Bulli Creek TCP
Description |  |  |  | Region is South West
Transformer size is 1x132/66/33KV 33/40/55MVA ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
|  | Latest Peak Compensated Load | [5 empty] | 24.1 MVA on 05/07/2022 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[5 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  | NCC Rating (MVA) |  | 71.3 | 71.3 | 71.3 |  | 71.3 |  | 71.3 | 80.1 |  | 80.1 |  | 80.1 | 80.1 | 80.1
|  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | 10 PoE Load (MVA) |  | 20.8 | 20.8 | 21.8 |  | 21.8 |  | 21.8 | 25.1 |  | 25.1 |  | 25.7 | 25.7 | 25.7
LARn (MVA)
LARn (MW)
|  |  | Power Factor at Peak Load |  | 0.999 | 0.999 | 0.999 |  | 0.999 |  | 0.999 | 0.994 |  | 0.994 |  | 0.994 | 0.994 | 0.994
|  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | 50 PoE Load (MVA) |  | 19.7 | 19.7 | 20.7 |  | 20.7 |  | 20.7 | 23.8 |  | 23.8 |  | 24.5 | 24.5 | 24.5
|  |  | 50 PoE Load > 95% (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1.2 |  | 1.2 |  | 1.2 | 1.2 | 1.2
|  |  | Hours PA > 95% Peak Load |  | 10.5 | 10.5 | 10.5 |  | 10.5 |  | 10.5 | 10.5 |  | 10.5 |  | 10.5 | 10.5 | 10.5
|  |  | Raw LAR (MVA) |  | 19.7 | 19.7 | 20.7 |  | 20.7 |  | 20.7 | 23.8 |  | 23.8 |  | 24.5 | 24.5 | 24.5
|  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Remote Trans Avail (MVA) |  | 30 | 30 | 30 |  | 30 |  | 30 | 30 |  | 30 |  | 30 | 30 | 30
|  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## T159
Bulk Summary Information and Peak Load Forecast
Substation |  |  |  | T159 - Lakeland BSP (132/66kV) | [8 empty] | Supply |  | QTUH - Turkinje 132kV TCP
Description |  |  |  | Region is Far North
Transformer size is 2x132/66/22kV 15/20MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 10.5 MVA
|  | Latest Peak Compensated Load | [5 empty] | 6.5 MVA on 01/11/2022 at 17:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[5 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  | NCC Rating (MVA) |  | 49.8 | 49.8 | 49.8 |  | 49.8 |  | 49.8 | 55.8 |  | 55.8 |  | 55.8 | 55.8 | 55.8
|  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | 10 PoE Load (MVA) |  | 6.7 | 6.6 | 6.6 |  | 6.6 |  | 6.7 | 5.8 |  | 5.8 |  | 5.8 | 5.8 | 5.8
LARn (MVA)
LARn (MW)
|  |  | Power Factor at Peak Load |  | 0.997 | 0.997 | 0.997 |  | 0.997 |  | 0.997 | 0.988 |  | 0.988 |  | 0.988 | 0.988 | 0.988
|  |  | ECC Rating (MVA) |  | 29.4 | 29.4 | 29.4 |  | 29.4 |  | 29.4 | 29.9 |  | 29.9 |  | 29.9 | 29.9 | 29.9
|  |  | 50 PoE Load (MVA) |  | 6.5 | 6.4 | 6.4 |  | 6.4 |  | 6.5 | 5.5 |  | 5.5 |  | 5.5 | 5.5 | 5.5
|  |  | 50 PoE Load > 95% (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  | Hours PA > 95% Peak Load |  | 15 | 15 | 15 |  | 15 |  | 15 | 15 |  | 15 |  | 15 | 15 | 15
Raw LAR (MVA)
|  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Capacity for Embedded Generation (MVA) |  | 30 | 30 | 30 |  | 30 |  | 30 | 30 |  | 30 |  | 30 | 30 | 30
|  |  | Firm Capacity for Embedded Generation (MVA) |  | 15 | 15 | 15 |  | 15 |  | 15 | 15 |  | 15 |  | 15 | 15 | 15
LARc (MVA)
LARc (MW)
|  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## T163
Bulk Summary Information and Peak Load Forecast
Substation |  |  |  | T163 - Rolleston BSP (132/66kV) | [8 empty] | Supply |  | QBWH - Blackwater 132kV TCP
Description |  |  |  | Region is Capricornia
Transformer size is 2x132/66/22kV 30/40/37.5MVA ONAN/ODAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
|  | Latest Peak Compensated Load | [5 empty] | 20.8 MVA on 14/03/2023 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[5 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  | NCC Rating (MVA) |  | 89.3 | 89.3 | 89.3 |  | 89.3 |  | 89.3 | 97.7 |  | 97.7 |  | 97.7 | 97.7 | 97.7
|  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | 10 PoE Load (MVA) |  | 21.2 | 21.1 | 22.1 |  | 22.2 |  | 22.2 | 20.1 |  | 20 |  | 20.6 | 20.6 | 20.6
LARn (MVA)
LARn (MW)
|  |  | Power Factor at Peak Load |  | 0.973 | 0.973 | 0.973 |  | 0.973 |  | 0.973 | 0.955 |  | 0.955 |  | 0.955 | 0.955 | 0.955
|  |  | ECC Rating (MVA) |  | 52.3 | 52.3 | 52.3 |  | 52.3 |  | 52.3 | 56.1 |  | 56.1 |  | 56.1 | 56.1 | 56.1
|  |  | 50 PoE Load (MVA) |  | 20.4 | 20.3 | 21.4 |  | 21.4 |  | 21.4 | 19.3 |  | 19.2 |  | 19.8 | 19.8 | 19.8
|  |  | 50 PoE Load > 95% (MVA) |  | 1 | 1 | 1.1 |  | 1.1 |  | 1.1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  | Hours PA > 95% Peak Load |  | 4.5 | 4.5 | 4.5 |  | 4.5 |  | 4.5 | 4.5 |  | 4.5 |  | 4.5 | 4.5 | 4.5
Raw LAR (MVA)
|  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Capacity for Embedded Generation (MVA) |  | 60 | 60 | 60 |  | 60 |  | 60 | 60 |  | 60 |  | 60 | 60 | 60
|  |  | Firm Capacity for Embedded Generation (MVA) |  | 30 | 30 | 30 |  | 30 |  | 30 | 30 |  | 30 |  | 30 | 30 | 30
LARc (MVA)
LARc (MW)
|  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## T166
Bulk Summary Information and Peak Load Forecast
Substation |  |  |  | T166 - Granite Creek BSP (132/66kV) | [8 empty] | Supply |  | QGNG - Gin Gin TCP
Description |  |  |  | Region is Capricornia
Transformer size is 1xGRCR TRANSF 1-132/66/22KV TRANSF 1;1xGRCR TRANSF 2-132/66/11KV TRANSF 2(Standby)
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
|  | Latest Peak Compensated Load | [5 empty] | 7.7 MVA on 05/07/2022 at 17:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[5 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  | NCC Rating (MVA) |  | 32 | 32 | 32 |  | 32 |  | 32 | 32 |  | 32 |  | 32 | 32 | 32
|  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | 10 PoE Load (MVA) |  | 6.8 | 6.8 | 6.8 |  | 6.8 |  | 6.9 | 7.7 |  | 7.6 |  | 7.5 | 7.4 | 7.3
LARn (MVA)
LARn (MW)
|  |  | Power Factor at Peak Load |  | 0.871 | 0.872 | 0.872 |  | 0.871 |  | 0.869 | 0.888 |  | 0.889 |  | 0.891 | 0.892 | 0.892
|  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | 50 PoE Load (MVA) |  | 6.5 | 6.4 | 6.4 |  | 6.5 |  | 6.6 | 6.9 |  | 6.8 |  | 6.7 | 6.6 | 6.6
|  |  | 50 PoE Load > 95% (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  | Hours PA > 95% Peak Load |  | 12 | 12 | 12 |  | 12 |  | 12 | 12 |  | 12 |  | 12 | 12 | 12
|  |  | Raw LAR (MVA) |  | 6.5 | 6.4 | 6.4 |  | 6.5 |  | 6.6 | 6.9 |  | 6.8 |  | 6.7 | 6.6 | 6.6
|  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Manual Trans Avail (MVA) |  | 15 | 15 | 15 |  | 15 |  | 15 | 15 |  | 15 |  | 15 | 15 | 15
|  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Capacity for Embedded Generation (MVA) |  | 25 | 25 | 25 |  | 25 |  | 25 | 25 |  | 25 |  | 25 | 25 | 25
|  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## T176
Bulk Summary Information and Peak Load Forecast
Substation |  |  |  | T176 - Louisa Creek BSP (132/33kV) | [8 empty] | Supply |  | QALH - Alligator Creek 132kV TCP
Description |  |  |  | Region is Mackay
Transformer size is 2x132/33/11kV 60/80MVA ONAN/ODAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
|  | Latest Peak Compensated Load | [5 empty] | 41.3 MVA on 17/06/2022 at 03:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[5 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  | NCC Rating (MVA) |  | 175.8 | 175.8 | 175.8 |  | 175.8 |  | 175.8 | 185.2 |  | 185.2 |  | 185.2 | 185.2 | 185.2
|  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | 10 PoE Load (MVA) |  | 42.6 | 42.6 | 42.6 |  | 42.7 |  | 42.7 | 42.6 |  | 42.6 |  | 42.7 | 42.7 | 42.7
LARn (MVA)
LARn (MW)
|  |  | Power Factor at Peak Load |  | 0.962 | 0.962 | 0.962 |  | 0.962 |  | 0.962 | 0.963 |  | 0.963 |  | 0.963 | 0.963 | 0.963
|  |  | ECC Rating (MVA) |  | 100.4 | 100.4 | 100.4 |  | 100.4 |  | 100.4 | 105.5 |  | 105.5 |  | 105.5 | 105.5 | 105.5
|  |  | 50 PoE Load (MVA) |  | 40.9 | 40.9 | 40.9 |  | 40.9 |  | 41 | 41 |  | 41 |  | 41 | 41 | 41.1
|  |  | 50 PoE Load > 95% (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2.1 | 2.1 |  | 2.1 |  | 2.1 | 2.1 | 2.1
|  |  | Hours PA > 95% Peak Load |  | 37 | 37 | 37 |  | 37 |  | 37 | 37 |  | 37 |  | 37 | 37 | 37
Raw LAR (MVA)
|  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Capacity for Embedded Generation (MVA) |  | 120 | 120 | 120 |  | 120 |  | 120 | 120 |  | 120 |  | 120 | 120 | 120
|  |  | Firm Capacity for Embedded Generation (MVA) |  | 60 | 60 | 60 |  | 60 |  | 60 | 60 |  | 60 |  | 60 | 60 | 60
LARc (MVA)
LARc (MW)
|  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## T188
Bulk Summary Information and Peak Load Forecast
Substation |  |  |  | T188 - Daandine BSP (110/33kV) | [8 empty] | Supply |  | QTKM - Tangkam TCP
Description |  |  |  | Region is South West
Transformer size is 1x110/33/11kV 24/32MVA ONAN/ODAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 30.0 MVA
|  | Latest Peak Compensated Load | [5 empty] | 5.3 MVA on 12/02/2023 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[5 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  | NCC Rating (MVA) |  | 37.3 | 37.3 | 37.3 |  | 37.3 |  | 37.3 | 40.5 |  | 40.5 |  | 40.5 | 40.5 | 40.5
|  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 2.7 |  | 2.7 |  | 2.7 | 2.7 | 2.7
|  |  | 10 PoE Load (MVA) |  | 7.6 | 9.1 | 9.1 |  | 9.1 |  | 9.1 | 7.7 |  | 9.3 |  | 9.3 | 9.3 | 9.3
LARn (MVA)
LARn (MW)
|  |  | Power Factor at Peak Load |  | 0.895 | 0.895 | 0.895 |  | 0.895 |  | 0.895 | 0.898 |  | 0.898 |  | 0.898 | 0.898 | 0.898
|  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | 50 PoE Load (MVA) |  | 7.2 | 8.7 | 8.7 |  | 8.7 |  | 8.7 | 7.4 |  | 9 |  | 9 | 9 | 9
|  |  | 50 PoE Load > 95% (MVA) |  | 0.4 | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.4 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  | Hours PA > 95% Peak Load |  | 4.5 | 4.5 | 4.5 |  | 4.5 |  | 4.5 | 4.5 |  | 4.5 |  | 4.5 | 4.5 | 4.5
|  |  | Raw LAR (MVA) |  | 7.2 | 8.7 | 8.7 |  | 8.7 |  | 8.7 | 7.4 |  | 9 |  | 9 | 9 | 9
|  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Manual Trans Avail (MVA) |  | 3.6 | 3.6 | 3.6 |  | 3.6 |  | 3.6 | 3.6 |  | 3.6 |  | 3.6 | 3.6 | 3.6
|  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | LARc (MVA) |  | 3.6 | 5.1 | 5.1 |  | 5.1 |  | 5.1 | 3.8 |  | 5.4 |  | 5.4 | 5.4 | 5.4
|  |  | LARc (MW) |  | 3.2 | 4.6 | 4.6 |  | 4.6 |  | 4.6 | 3.4 |  | 4.8 |  | 4.8 | 4.8 | 4.8
|  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  | Meets Security Standard |  | No | No | No |  | No |  | No | No |  | No |  | No | No | No
Return to Index

## T189
Bulk Summary Information and Peak Load Forecast
Substation |  |  |  | T189 - Oakey BSP (110/33kV) | [8 empty] | Supply |  | QOKT - Oakey TCP
Description |  |  |  | Region is South West
Transformer size is 2x110/33/11kV 48/63MVA ONAN/ODAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 27.5 MVA
|  | Latest Peak Compensated Load | [5 empty] | 17.9 MVA on 13/02/2023 at 16:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[5 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  | NCC Rating (MVA) |  | 147.2 | 147.2 | 147.2 |  | 147.2 |  | 147.2 | 165.2 |  | 165.2 |  | 165.2 | 165.2 | 165.2
|  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | 10 PoE Load (MVA) |  | 19.3 | 19.1 | 19 |  | 19.1 |  | 19.2 | 19.1 |  | 19 |  | 19 | 19 | 18.9
LARn (MVA)
LARn (MW)
|  |  | Power Factor at Peak Load |  | 0.928 | 0.928 | 0.928 |  | 0.928 |  | 0.928 | 0.984 |  | 0.984 |  | 0.984 | 0.984 | 0.984
|  |  | ECC Rating (MVA) |  | 82 | 82 | 82 |  | 82 |  | 82 | 92.5 |  | 92.5 |  | 92.5 | 92.5 | 92.5
|  |  | 50 PoE Load (MVA) |  | 18.4 | 18.2 | 18.1 |  | 18.2 |  | 18.3 | 18.2 |  | 18.1 |  | 18.1 | 18.1 | 18.1
|  |  | 50 PoE Load > 95% (MVA) |  | 0.9 | 0.9 | 0.9 |  | 0.9 |  | 0.9 | 0.9 |  | 0.9 |  | 0.9 | 0.9 | 0.9
|  |  | Hours PA > 95% Peak Load |  | 29 | 29 | 29 |  | 29 |  | 29 | 29 |  | 29 |  | 29 | 29 | 29
Raw LAR (MVA)
|  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Capacity for Embedded Generation (MVA) |  | 96 | 96 | 96 |  | 96 |  | 96 | 96 |  | 96 |  | 96 | 96 | 96
|  |  | Firm Capacity for Embedded Generation (MVA) |  | 48 | 48 | 48 |  | 48 |  | 48 | 48 |  | 48 |  | 48 | 48 | 48
LARc (MVA)
LARc (MW)
|  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## T198
Bulk Summary Information and Peak Load Forecast
Substation |  |  |  | T198 - Broadlea BSP (132/66kV) | [8 empty] | Supply |  | QMRH - Moranbah 132kV TCP
Description |  |  |  | Region is Mackay
Transformer size is 2x132/66/11kV 80/100MVA ONAN/ODAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
|  | Latest Peak Compensated Load | [5 empty] | 49.1 MVA on 29/08/2022 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[5 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  | NCC Rating (MVA) |  | 223.1 | 223.1 | 223.1 |  | 223.1 |  | 223.1 | 241.4 |  | 241.4 |  | 241.4 | 241.4 | 241.4
|  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | 10 PoE Load (MVA) |  | 61.8 | 59.6 | 59.6 |  | 59.6 |  | 59.7 | 62.7 |  | 61.1 |  | 61 | 61 | 61
LARn (MVA)
LARn (MW)
|  |  | Power Factor at Peak Load |  | 0.968 | 0.968 | 0.968 |  | 0.968 |  | 0.968 | 0.978 |  | 0.978 |  | 0.978 | 0.978 | 0.978
|  |  | ECC Rating (MVA) |  | 132.4 | 132.4 | 132.4 |  | 132.4 |  | 132.4 | 140.1 |  | 140.1 |  | 140.1 | 140.1 | 140.1
|  |  | 50 PoE Load (MVA) |  | 60.6 | 58.5 | 58.5 |  | 58.5 |  | 58.5 | 61.4 |  | 59.8 |  | 59.7 | 59.7 | 59.7
|  |  | 50 PoE Load > 95% (MVA) |  | 3 | 2.9 | 2.9 |  | 2.9 |  | 2.9 | 3.1 |  | 3 |  | 3 | 3 | 3
|  |  | Hours PA > 95% Peak Load |  | 137.5 | 137.5 | 137.5 |  | 137.5 |  | 137.5 | 137.5 |  | 137.5 |  | 137.5 | 137.5 | 137.5
Raw LAR (MVA)
|  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Capacity for Embedded Generation (MVA) |  | 160 | 160 | 160 |  | 160 |  | 160 | 160 |  | 160 |  | 160 | 160 | 160
|  |  | Firm Capacity for Embedded Generation (MVA) |  | 80 | 80 | 80 |  | 80 |  | 80 | 80 |  | 80 |  | 80 | 80 | 80
LARc (MVA)
LARc (MW)
|  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## TANB
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | TANB - Tanby (66/22kV) | [8 empty] | Supply |  | RMES - Rockhampton Mesh
| Description |  |  |  | Region is Capricornia
Transformer size is 2x66/22kV 15/20MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 4.4 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -1.8% W 0.5%,2025 S 0.3% W 0.6%, 2026 S 0.7% W 0.9%, 2027 S 2.1% W 1.8%
|  |  | Latest Peak Compensated Load | [5 empty] | 13.1 MVA on 03/02/2023 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 50.4 | 50.4 | 50.4 |  | 50.4 |  | 50.4 | 56.6 |  | 56.6 |  | 56.6 | 56.6 | 56.6
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 14.8 | 14.8 | 14.9 |  | 15.3 |  | 15.7 | 11.4 |  | 11.5 |  | 11.6 | 11.7 | 11.9
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.973 | 0.973 | 0.973 |  | 0.973 |  | 0.973 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | ECC Rating (MVA) |  | 27.4 | 27.4 | 27.4 |  | 27.4 |  | 27.4 | 29.9 |  | 29.9 |  | 29.9 | 29.9 | 29.9
|  |  |  | 50 PoE Load (MVA) |  | 13.4 | 13.4 | 13.5 |  | 13.8 |  | 14.2 | 10 |  | 10 |  | 10.1 | 10.2 | 10.3
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.7 | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | Hours PA > 95% Peak Load |  | 4 | 4 | 4 |  | 4 |  | 4 | 4 |  | 4 |  | 4 | 4 | 4
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 30 | 30 | 30 |  | 30 |  | 30 | 30 |  | 30 |  | 30 | 30 | 30
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 15 | 15 | 15 |  | 15 |  | 15 | 15 |  | 15 |  | 15 | 15 | 15
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## TARA
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | TARA - Tara (33/11kV) | [8 empty] | Supply |  | COLU - Columboola BSP
| Description |  |  |  | Region is South West
Transformer size is 1x33/11kV 1.5MVA ON;1x33/11kV 1MVA ON
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.2% W -0.6%2025 S -1.1% W -0.2%2026 S -0.6% W 0.0%,2027 S 0.1% W 0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 1.3 MVA on 11/07/2022 at 07:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 | 2 | 2
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 1.4 | 1.4 | 1.3 |  | 1.3 |  | 1.4 | 1.4 |  | 1.4 |  | 1.4 | 1.4 | 1.4
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.965 | 0.965 | 0.965 |  | 0.965 |  | 0.965 | 0.994 |  | 0.994 |  | 0.994 | 0.994 | 0.994
|  |  |  | ECC Rating (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | 50 PoE Load (MVA) |  | 1.3 | 1.3 | 1.3 |  | 1.3 |  | 1.3 | 1.3 |  | 1.3 |  | 1.3 | 1.3 | 1.3
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 8 | 8 | 8 |  | 8 |  | 8 | 8 |  | 8 |  | 8 | 8 | 8
|  |  |  | Raw LAR (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## THEO
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | THEO - Theodore (66/22kV) | [8 empty] | Supply |  | T027 - Moura BSP
| Description |  |  |  | Region is Capricornia
Transformer size is 2x66/22kV 5MVA ON;1x66/22kV 5MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.3% W -0.9%2025 S -1.1% W -0.5%2026 S -0.7% W -0.3%2027 S 0.0% W -0.2%
|  |  | Latest Peak Compensated Load | [5 empty] | 13.5 MVA on 12/02/2023 at 17:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 16.6 | 16.6 | 16.6 |  | 16.6 |  | 16.6 | 18.2 |  | 18.2 |  | 18.2 | 18.2 | 18.2
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 12.8 | 12.7 | 12.6 |  | 12.6 |  | 12.7 | 10.7 |  | 10.6 |  | 10.6 | 10.5 | 10.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.982 | 0.982 | 0.982 |  | 0.982 |  | 0.982 | 0.999 |  | 0.999 |  | 0.999 | 0.999 | 0.999
|  |  |  | ECC Rating (MVA) |  | 11.4 | 11.4 | 11.4 |  | 11.4 |  | 11.4 | 12.5 |  | 12.5 |  | 12.5 | 12.5 | 12.5
|  |  |  | 50 PoE Load (MVA) |  | 12.4 | 12.3 | 12.2 |  | 12.2 |  | 12.3 | 10.5 |  | 10.4 |  | 10.3 | 10.3 | 10.3
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | Hours PA > 95% Peak Load |  | 26 | 26 | 26 |  | 26 |  | 26 | 26 |  | 26 |  | 26 | 26 | 26
|  |  |  | Raw LAR (MVA) |  | 1 | 0.9 | 0.8 |  | 0.8 |  | 0.9
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 5.2 | 5.2 | 5.2 |  | 5.2 |  | 5.2 | 5.2 |  | 5.2 |  | 5.2 | 5.2 | 5.2
|  |  |  | Shed(4Hour) |  | 1.8 | 1.8 | 1.8 |  | 1.8 |  | 1.8 | 1.8 |  | 1.8 |  | 1.8 | 1.8 | 1.8
|  |  |  | Capacity for Embedded Generation (MVA) |  | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 | 5 | 5
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 | 5 | 5
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## TIER
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | TIER - Tieri (66/22kV) | [8 empty] | Supply |  | H015 - Lilyvale BSP
| Description |  |  |  | Region is Capricornia
Transformer size is 2x66/22kV 5MVA ON
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.0% W -0.6%2025 S -0.9% W -0.4%2026 S -0.4% W -0.1%2027 S 0.5% W 0.2%
|  |  | Latest Peak Compensated Load | [5 empty] | 2 MVA on 13/02/2023 at 17:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 11 | 11 | 11 |  | 11 |  | 11 | 11 |  | 11 |  | 11 | 11 | 11
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 1.4 |  | 1.4 |  | 1.4 | 1.4 | 1.4
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.996 | 0.996 | 0.996 |  | 0.996 |  | 0.996 | 0.996 |  | 0.996 |  | 0.996 | 0.996 | 0.996
|  |  |  | ECC Rating (MVA) |  | 6 | 6 | 6 |  | 6 |  | 6 | 6.8 |  | 6.8 |  | 6.8 | 6.8 | 6.8
|  |  |  | 50 PoE Load (MVA) |  | 1.9 | 1.9 | 1.9 |  | 1.9 |  | 1.9 | 1.4 |  | 1.4 |  | 1.3 | 1.3 | 1.3
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 6 | 6 | 6 |  | 6 |  | 6 | 6 |  | 6 |  | 6 | 6 | 6
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 | 5 | 5
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## TOPO
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | TOPO - Townsville Port (66/11kV) | [8 empty] | Supply |  | TMES - Townsville Mesh
| Description |  |  |  | Region is Nth Queensland
Transformer size is 2x66/11kV 19.2/24/32MVA ONAN/ODAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.9% W -0.4%2025 S -0.8% W -0.2%2026 S -0.3% W 0.1%,2027 S 0.3% W 0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 11.1 MVA on 01/11/2022 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 83.2 | 83.2 | 83.2 |  | 83.2 |  | 83.2 | 83.2 |  | 83.2 |  | 83.2 | 83.2 | 83.2
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 10.9 | 10.8 | 10.8 |  | 10.8 |  | 10.9 | 8.8 |  | 8.8 |  | 8.7 | 8.8 | 8.8
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.979 | 0.979 | 0.979 |  | 0.979 |  | 0.979 | 0.979 |  | 0.979 |  | 0.979 | 0.979 | 0.979
|  |  |  | ECC Rating (MVA) |  | 41.6 | 41.6 | 41.6 |  | 41.6 |  | 41.6 | 41.6 |  | 41.6 |  | 41.6 | 41.6 | 41.6
|  |  |  | 50 PoE Load (MVA) |  | 10.7 | 10.6 | 10.5 |  | 10.6 |  | 10.7 | 8.5 |  | 8.5 |  | 8.4 | 8.5 | 8.5
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  |  | Hours PA > 95% Peak Load |  | 37 | 37 | 37 |  | 37 |  | 37 | 37 |  | 37 |  | 37 | 37 | 37
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 38 | 38 | 38 |  | 38 |  | 38 | 38 |  | 38 |  | 38 | 38 | 38
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 19 | 19 | 19 |  | 19 |  | 19 | 19 |  | 19 |  | 19 | 19 | 19
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## TORQ
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | TORQ - Torquay (66/11kV) | [8 empty] | Supply |  | MARY - Maryborough BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 2x66/11kV 21/26.25/35MVA ONAN/ODAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.5% W 0.4%,2025 S -0.5% W 0.6%,2026 S -0.0% W 0.9%,2027 S 0.7% W 1.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 30.4 MVA on 16/03/2023 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 91.1 | 91.1 | 91.1 |  | 91.1 |  | 91.1 | 99 |  | 99 |  | 99 | 99 | 99
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 30.7 | 30.5 | 30.5 |  | 30.8 |  | 31.2 | 23.3 |  | 23.4 |  | 23.6 | 23.8 | 24
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.988 | 0.988 | 0.988 |  | 0.988 |  | 0.988 | 0.997 |  | 0.997 |  | 0.997 | 0.997 | 0.997
|  |  |  | ECC Rating (MVA) |  | 48.8 | 48.8 | 48.8 |  | 48.8 |  | 48.8 | 52.3 |  | 52.3 |  | 52.3 | 52.3 | 52.3
|  |  |  | 50 PoE Load (MVA) |  | 29.6 | 29.4 | 29.4 |  | 29.6 |  | 30 | 22.6 |  | 22.7 |  | 22.8 | 23 | 23.2
|  |  |  | 50 PoE Load > 95% (MVA) |  | 1.5 | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.1 |  | 1.1 |  | 1.1 | 1.2 | 1.2
|  |  |  | Hours PA > 95% Peak Load |  | 12.5 | 12.5 | 12.5 |  | 12.5 |  | 12.5 | 12.5 |  | 12.5 |  | 12.5 | 12.5 | 12.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 42 | 42 | 42 |  | 42 |  | 42 | 42 |  | 42 |  | 42 | 42 | 42
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 21 | 21 | 21 |  | 21 |  | 21 | 21 |  | 21 |  | 21 | 21 | 21
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## TORR
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | TORR - Torrington (33/11kV) | [8 empty] | Supply |  | T116 - Torrington BSP
| Description |  |  |  | Region is South West
Transformer size is 2x33/11kV 15/18.5/25 ONAN/ODAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 4.4 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -1.8% W 0.2%,2025 S -0.1% W 0.2%,2026 S 0.5% W 0.6%, 2027 S 1.5% W 0.8%
|  |  | Latest Peak Compensated Load | [5 empty] | 26.9 MVA on 04/07/2022 at 17:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 56.7 | 56.7 | 56.7 |  | 56.7 |  | 56.7 | 67.5 |  | 67.5 |  | 67.5 | 67.5 | 67.5
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 22.6 | 22.5 | 22.6 |  | 23 |  | 23.5 | 28.1 |  | 28.2 |  | 28.2 | 28.4 | 28.6
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.989 | 0.989 | 0.989 |  | 0.989 |  | 0.989 | 0.997 |  | 0.997 |  | 0.997 | 0.997 | 0.997
|  |  |  | ECC Rating (MVA) |  | 31.6 | 31.6 | 31.6 |  | 31.6 |  | 31.6 | 37.4 |  | 37.4 |  | 37.4 | 37.4 | 37.4
|  |  |  | 50 PoE Load (MVA) |  | 20.5 | 20.5 | 20.6 |  | 20.9 |  | 21.4 | 27.2 |  | 27.2 |  | 27.3 | 27.5 | 27.7
|  |  |  | 50 PoE Load > 95% (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1.1 | 1.4 |  | 1.4 |  | 1.4 | 1.4 | 1.4
|  |  |  | Hours PA > 95% Peak Load |  | 2.5 | 2.5 | 2.5 |  | 2.5 |  | 2.5 | 2.5 |  | 2.5 |  | 2.5 | 2.5 | 2.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 30 | 30 | 30 |  | 30 |  | 30 | 30 |  | 30 |  | 30 | 30 | 30
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 15 | 15 | 15 |  | 15 |  | 15 | 15 |  | 15 |  | 15 | 15 | 15
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## TUAN
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | TUAN - Tuan (66/11kV) | [8 empty] | Supply |  | MARY - Maryborough BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 1x66/11kV 7.5/10MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.9% W -0.5%2025 S -0.6% W 0.0%,2026 S -0.2% W 0.2%,2027 S 0.4% W 0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 8.1 MVA on 13/02/2023 at 20:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 10.8 | 10.8 | 10.8 |  | 10.8 |  | 10.8 | 11.4 |  | 11.4 |  | 11.4 | 11.4 | 11.4
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 8.4 | 8.3 | 8.3 |  | 8.4 |  | 8.4 | 8.4 |  | 8.4 |  | 8.4 | 8.4 | 8.4
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.861 | 0.861 | 0.861 |  | 0.861 |  | 0.861 | 0.855 |  | 0.855 |  | 0.855 | 0.855 | 0.855
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 8.2 | 8.1 | 8.1 |  | 8.2 |  | 8.2 | 8.2 |  | 8.2 |  | 8.2 | 8.2 | 8.2
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.4 | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  |  | Hours PA > 95% Peak Load |  | 17.5 | 17.5 | 17.5 |  | 17.5 |  | 17.5 | 17.5 |  | 17.5 |  | 17.5 | 17.5 | 17.5
|  |  |  | Raw LAR (MVA) |  | 8.2 | 8.1 | 8.1 |  | 8.2 |  | 8.2 | 8.2 |  | 8.2 |  | 8.2 | 8.2 | 8.2
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 2.1 | 2.1 | 2.1 |  | 2.1 |  | 2.1 | 2.1 |  | 2.1 |  | 2.1 | 2.1 | 2.1
|  |  |  | Mobile Plant Avail (MVA) |  | 1.6 | 1.6 | 1.6 |  | 1.6 |  | 1.6 | 1.6 |  | 1.6 |  | 1.6 | 1.6 | 1.6
|  |  |  | Shed(30min) |  | 6 | 6 | 6 |  | 6 |  | 6 | 6 |  | 6 |  | 6 | 6 | 6
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 | 5 | 5
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## TWCE
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | TWCE - Toowoomba Central (110/11kV) | [8 empty] | Supply |  | QMRG - Middle Ridge (Ergon) TCP
| Description |  |  |  | Region is South West
Transformer size is 2x110/11kV 32/40MVA ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.3% W -0.9%2025 S -1.8% W -1.5%2026 S -1.4% W -1.3%2027 S -1.0% W -1.5
|  |  | Latest Peak Compensated Load | [5 empty] | 19.8 MVA on 03/02/2023 at 13:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 88 | 88 | 88 |  | 88 |  | 88 | 88 |  | 88 |  | 88 | 88 | 88
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 21.7 | 21.3 | 21 |  | 20.8 |  | 20.7 | 19.2 |  | 19 |  | 18.7 | 18.5 | 18.2
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.975 | 0.975 | 0.975 |  | 0.975 |  | 0.975 | 0.99 |  | 0.99 |  | 0.99 | 0.99 | 0.99
|  |  |  | ECC Rating (MVA) |  | 46 | 46 | 46 |  | 46 |  | 46 | 52 |  | 52 |  | 52 | 52 | 52
|  |  |  | 50 PoE Load (MVA) |  | 20.7 | 20.3 | 20 |  | 19.8 |  | 19.7 | 18.6 |  | 18.4 |  | 18.1 | 17.9 | 17.6
|  |  |  | 50 PoE Load > 95% (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 0.9 |  | 0.9 |  | 0.9 | 0.9 | 0.9
|  |  |  | Hours PA > 95% Peak Load |  | 13 | 13 | 13 |  | 13 |  | 13 | 13 |  | 13 |  | 13 | 13 | 13
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 64 | 64 | 64 |  | 64 |  | 64 | 64 |  | 64 |  | 64 | 64 | 64
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 32 | 32 | 32 |  | 32 |  | 32 | 32 |  | 32 |  | 32 | 32 | 32
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## VERM
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | VERM - Vermont (66/22kV) | [8 empty] | Supply |  | T035 - Dysart BSP
| Description |  |  |  | Region is Capricornia
Transformer size is 2x66/22kV 10MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 0.0%, 2024 S 0.0% W 0.0%, 2025 S 0.0% W 0.0%, 2026 S 0.0% W 0.0%, 2027 S 0.0% W 0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 11.3 MVA on 29/03/2023 at 11:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 22.1 | 22.1 | 22.1 |  | 22.1 |  | 22.1 | 24.3 |  | 24.3 |  | 24.3 | 24.3 | 24.3
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 11.5 | 11.5 | 11.5 |  | 11.5 |  | 11.5 | 10.4 |  | 10.4 |  | 10.4 | 10.4 | 10.4
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.934 | 0.934 | 0.934 |  | 0.934 |  | 0.934 | 0.931 |  | 0.931 |  | 0.931 | 0.931 | 0.931
|  |  |  | ECC Rating (MVA) |  | 13.7 | 13.7 | 13.7 |  | 13.7 |  | 13.7 | 14.7 |  | 14.7 |  | 14.7 | 14.7 | 14.7
|  |  |  | 50 PoE Load (MVA) |  | 11.3 | 11.3 | 11.3 |  | 11.3 |  | 11.3 | 10.4 |  | 10.4 |  | 10.4 | 10.4 | 10.4
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | Hours PA > 95% Peak Load |  | 305 | 305 | 305 |  | 305 |  | 305 | 305 |  | 305 |  | 305 | 305 | 305
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 20 | 20 | 20 |  | 20 |  | 20 | 20 |  | 20 |  | 20 | 20 | 20
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## WAEA
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | WAEA - Warwick East (33/11kV) | [8 empty] | Supply |  | T058 - Warwick BSP
| Description |  |  |  | Region is South West
Transformer size is 2x33/11kV 25/32MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.8% W -0.3%2025 S -1.2% W -0.1%2026 S -0.6% W 0.1%,2027 S 0.0% W 0.2%
|  |  | Latest Peak Compensated Load | [5 empty] | 20.9 MVA on 09/06/2022 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 69.6 | 69.6 | 69.6 |  | 69.6 |  | 69.6 | 79.2 |  | 79.2 |  | 79.2 | 79.2 | 79.2
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 18.8 | 18.6 | 18.5 |  | 18.5 |  | 18.7 | 21.8 |  | 21.7 |  | 21.7 | 21.7 | 21.8
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.998 | 0.998 | 0.998 |  | 0.998 |  | 0.998 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | ECC Rating (MVA) |  | 38.8 | 38.8 | 38.8 |  | 38.8 |  | 38.8 | 42.2 |  | 42.2 |  | 42.2 | 42.2 | 42.2
|  |  |  | 50 PoE Load (MVA) |  | 17.8 | 17.6 | 17.5 |  | 17.5 |  | 17.6 | 21.2 |  | 21.1 |  | 21.1 | 21.1 | 21.1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.9 | 0.9 | 0.9 |  | 0.9 |  | 0.9 | 1.1 |  | 1.1 |  | 1.1 | 1.1 | 1.1
|  |  |  | Hours PA > 95% Peak Load |  | 5.5 | 5.5 | 5.5 |  | 5.5 |  | 5.5 | 5.5 |  | 5.5 |  | 5.5 | 5.5 | 5.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 50 | 50 | 50 |  | 50 |  | 50 | 50 |  | 50 |  | 50 | 50 | 50
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 25 | 25 | 25 |  | 25 |  | 25 | 25 |  | 25 |  | 25 | 25 | 25
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## WAGG
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | WAGG - Waggamba 132/33kV (66/33kV) | [8 empty] | Supply |  | T156 - Waggamba BSP
| Description |  |  |  | Region is South West
Transformer size is 1x132/33kV 15 MVA
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 0.0%, 2024 S 0.0% W 0.0%, 2025 S 0.0% W 0.0%, 2026 S 0.0% W 0.0%, 2027 S 0.0% W 0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 5.6 MVA on 12/02/2023 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 15 | 15 | 15 |  | 15 |  | 15 | 15 |  | 15 |  | 15 | 15 | 15
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 6.9 | 6.9 | 8 |  | 8 |  | 8 | 5.5 |  | 5.5 |  | 6.1 | 6.1 | 6.1
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.997 | 0.997 | 0.997 |  | 0.997 |  | 0.997 | 0.98 |  | 0.98 |  | 0.98 | 0.98 | 0.98
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 6.4 | 6.4 | 7.5 |  | 7.5 |  | 7.5 | 5.2 |  | 5.2 |  | 5.9 | 5.9 | 5.9
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.3 | 0.3 | 0.4 |  | 0.4 |  | 0.4 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Hours PA > 95% Peak Load |  | 7.5 | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 | 7.5
|  |  |  | Raw LAR (MVA) |  | 6.4 | 6.4 | 7.5 |  | 7.5 |  | 7.5 | 5.2 |  | 5.2 |  | 5.9 | 5.9 | 5.9
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Mobile Plant Avail (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 | 2 | 2
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
Capacity for Embedded Generation (MVA)
Firm Capacity for Embedded Generation (MVA)
|  |  |  | LARc (MVA) |  | 3.4 | 3.4 | 4.5 |  | 4.5 |  | 4.5 | 2.2 |  | 2.2 |  | 2.9 | 2.9 | 2.9
|  |  |  | LARc (MW) |  | 3.4 | 3.4 | 4.5 |  | 4.5 |  | 4.5 | 2.2 |  | 2.2 |  | 2.8 | 2.8 | 2.8
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | No | No | No |  | No |  | No | No |  | No |  | No | No | No
Return to Index

## WALL
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | WALL - Wallaville (66/11kV) | [8 empty] | Supply |  | BUND - Bundaberg BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 2x66/11kV 8/10MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.9% W -1.5%2025 S -0.7% W -1.9%2026 S -0.2% W -1.0%2027 S 0.5% W 0.3%
|  |  | Latest Peak Compensated Load | [5 empty] | 7 MVA on 13/02/2023 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 25.6 | 25.6 | 25.6 |  | 25.6 |  | 25.6 | 27 |  | 27 |  | 27 | 27 | 27
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 7.1 | 7 | 7 |  | 7.1 |  | 7.2 | 5.7 |  | 5.6 |  | 5.5 | 5.4 | 5.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.991 | 0.991 | 0.991 |  | 0.991 |  | 0.991 | 0.977 |  | 0.977 |  | 0.977 | 0.977 | 0.977
|  |  |  | ECC Rating (MVA) |  | 14.7 | 14.7 | 14.7 |  | 14.7 |  | 14.7 | 15 |  | 15 |  | 15 | 15 | 15
|  |  |  | 50 PoE Load (MVA) |  | 6.7 | 6.7 | 6.6 |  | 6.7 |  | 6.8 | 5.3 |  | 5.2 |  | 5.1 | 5.1 | 5.1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Hours PA > 95% Peak Load |  | 7.5 | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 | 7.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10 | tapchanger limited to 5MVA
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 | 5 | 5 | -3.1MVA by 2030 | RPF 2.2
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## WAND
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | WAND - Wandoan (33/22kV) | [8 empty] | Supply |  | COLU - Columboola BSP
| Description |  |  |  | Region is South West
Transformer size is 2x33/22kV 5MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.1% W -0.7%2025 S -1.0% W -0.5%2026 S -0.5% W -0.2%2027 S 0.1% W -0.2%
|  |  | Latest Peak Compensated Load | [5 empty] | 3.1 MVA on 12/02/2023 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 12.2 | 12.2 | 12.2 |  | 12.2 |  | 12.2 | 14.5 |  | 14.5 |  | 14.5 | 14.5 | 14.5
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 3.1 | 3.1 | 3.1 |  | 3.1 |  | 3.1 | 3.1 |  | 3.1 |  | 3.1 | 3.1 | 3.1
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.991 | 0.991 | 0.991 |  | 0.991 |  | 0.991 | 0.999 |  | 0.999 |  | 0.999 | 0.999 | 0.999
|  |  |  | ECC Rating (MVA) |  | 7.1 | 7.1 | 7.1 |  | 7.1 |  | 7.1 | 7.5 |  | 7.5 |  | 7.5 | 7.5 | 7.5
|  |  |  | 50 PoE Load (MVA) |  | 2.9 | 2.9 | 2.9 |  | 2.9 |  | 2.9 | 2.9 |  | 2.9 |  | 2.9 | 2.9 | 2.9
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 32 | 32 | 32 |  | 32 |  | 32 | 32 |  | 32 |  | 32 | 32 | 32
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 | 5 | 5
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## WEBU
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | WEBU - West Bundaberg (66/11kV) | [8 empty] | Supply |  | BUND - Bundaberg BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 2x66/11kV 15/18/25MVA ONAN/ODAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.5% W -1.2%2025 S -1.9% W -1.6%2026 S -1.4% W -0.9%2027 S -0.8% W 0.3%
|  |  | Latest Peak Compensated Load | [5 empty] | 28.3 MVA on 13/02/2023 at 16:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 61.3 | 61.3 | 61.3 |  | 61.3 |  | 61.3 | 65 |  | 65 |  | 65 | 65 | 65
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 28.2 | 28.1 | 27.7 |  | 27.5 |  | 27.5 | 27.5 |  | 27.1 |  | 26.7 | 26.5 | 26.6
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 1 | 0.984 | 0.984 |  | 0.984 |  | 0.984 | 0.991 |  | 0.991 |  | 0.991 | 0.991 | 0.991
|  |  |  | ECC Rating (MVA) |  | 34.3 | 34.3 | 34.3 |  | 34.3 |  | 34.3 | 36.5 |  | 36.5 |  | 36.5 | 36.5 | 36.5
|  |  |  | 50 PoE Load (MVA) |  | 27.1 | 26.6 | 26.2 |  | 26 |  | 26 | 24.7 |  | 24.4 |  | 24 | 23.8 | 23.8
|  |  |  | 50 PoE Load > 95% (MVA) |  | 1.4 | 1.3 | 1.3 |  | 1.3 |  | 1.3 | 1.2 |  | 1.2 |  | 1.2 | 1.2 | 1.2
|  |  |  | Hours PA > 95% Peak Load |  | 8 | 8 | 8 |  | 8 |  | 8 | 8 |  | 8 |  | 8 | 8 | 8
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 30 | 30 | 30 |  | 30 |  | 30 | 30 |  | 30 |  | 30 | 30 | 30
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 15 | 15 | 15 |  | 15 |  | 15 | 15 |  | 15 |  | 15 | 15 | 15
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## WEDA
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | WEDA - West Dalby (33/11kV) | [8 empty] | Supply |  | T002 - Dalby East BSP
| Description |  |  |  | Region is South West
Transformer size is 1x33/11KV 6.25MVA ONAN;1x33/11KV 6.3MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.4% W -0.3%2025 S -1.6% W -0.2%2026 S -0.9% W 0.1%,2027 S -0.2% W 0.2%
|  |  | Latest Peak Compensated Load | [5 empty] | 5.1 MVA on 01/03/2023 at 16:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 14.6 | 14.6 | 14.6 |  | 14.6 |  | 14.6 | 17.5 |  | 17.5 |  | 17.5 | 17.5 | 17.5
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 5.2 | 5.1 | 5 |  | 5 |  | 5 | 5.2 |  | 5.2 |  | 5.2 | 5.2 | 5.2
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.962 | 0.962 | 0.962 |  | 0.962 |  | 0.962 | 0.973 |  | 0.973 |  | 0.973 | 0.973 | 0.973
|  |  |  | ECC Rating (MVA) |  | 8.2 | 8.2 | 8.2 |  | 8.2 |  | 8.2 | 9.3 |  | 9.3 |  | 9.3 | 9.3 | 9.3
|  |  |  | 50 PoE Load (MVA) |  | 4.8 | 4.7 | 4.7 |  | 4.6 |  | 4.7 | 4.9 |  | 4.9 |  | 4.8 | 4.8 | 4.9
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 1.5 | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.5 | 1.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 12.55 | 12.55 | 12.55 |  | 12.55 |  | 12.55 | 12.55 |  | 12.55 |  | 12.55 | 12.55 | 12.55
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 6.25 | 6.25 | 6.25 |  | 6.25 |  | 6.25 | 6.25 |  | 6.25 |  | 6.25 | 6.25 | 6.25
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## WEMA
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | WEMA - West Mackay (33/11kV) | [8 empty] | Supply |  | MACK - Mackay BSP
| Description |  |  |  | Region is Mackay
Transformer size is 2x33/11kV 15/20MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.0% W -0.8%2025 S -1.0% W -0.6%2026 S -0.5% W -0.1%2027 S 0.2% W 0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 18 MVA on 02/02/2023 at 17:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 38.7 | 38.7 | 38.7 |  | 38.7 |  | 38.7 | 40.9 |  | 40.9 |  | 40.9 | 40.9 | 40.9
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 21 | 20.8 | 20.7 |  | 20.7 |  | 20.9 | 11.5 |  | 11.4 |  | 11.3 | 11.3 | 11.4
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.988 | 0.988 | 0.988 |  | 0.988 |  | 0.988 | 0.996 |  | 0.996 |  | 0.996 | 0.996 | 0.996
|  |  |  | ECC Rating (MVA) |  | 22.3 | 22.3 | 22.3 |  | 22.3 |  | 22.3 | 23.4 |  | 23.4 |  | 23.4 | 23.4 | 23.4
|  |  |  | 50 PoE Load (MVA) |  | 18.8 | 18.6 | 18.6 |  | 18.6 |  | 18.8 | 11.2 |  | 11.1 |  | 11.1 | 11.1 | 11.1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.9 | 0.9 | 0.9 |  | 0.9 |  | 0.9 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  |  | Hours PA > 95% Peak Load |  | 7.5 | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 | 7.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 30 | 30 | 30 |  | 30 |  | 30 | 30 |  | 30 |  | 30 | 30 | 30
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 15 | 15 | 15 |  | 15 |  | 15 | 15 |  | 15 |  | 15 | 15 | 15
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## WETO
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | WETO - West Toowoomba (33/11kV) | [8 empty] | Supply |  | T116 - Torrington BSP
| Description |  |  |  | Region is South West
Transformer size is 3x33/11kV 10MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.2% W -0.8%2025 S -1.3% W -0.6%2026 S -0.7% W -0.3%2027 S -0.1% W -0.3
|  |  | Latest Peak Compensated Load | [5 empty] | 22.4 MVA on 04/07/2022 at 17:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 31.4 | 31.4 | 31.4 |  | 31.4 |  | 31.4 | 36.2 |  | 36.2 |  | 36.2 | 36.2 | 36.2
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 19.3 | 19 | 18.9 |  | 18.9 |  | 19 | 23.2 |  | 23 |  | 22.9 | 22.8 | 22.8
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.98 | 0.98 | 0.98 |  | 0.98 |  | 0.98 | 0.993 |  | 0.993 |  | 0.993 | 0.993 | 0.993
|  |  |  | ECC Rating (MVA) |  | 23.8 | 23.8 | 23.8 |  | 23.8 |  | 23.8 | 26.9 |  | 26.9 |  | 26.9 | 26.9 | 26.9
|  |  |  | 50 PoE Load (MVA) |  | 18.5 | 18.3 | 18.1 |  | 18.1 |  | 18.2 | 22.2 |  | 22 |  | 21.9 | 21.8 | 21.8
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.9 | 0.9 | 0.9 |  | 0.9 |  | 0.9 | 1.1 |  | 1.1 |  | 1.1 | 1.1 | 1.1
|  |  |  | Hours PA > 95% Peak Load |  | 7.5 | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 | 7.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 6 | 6 | 6 |  | 6 |  | 6 | 6 |  | 6 |  | 6 | 6 | 6
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 24.9 | 24.9 | 24.9 |  | 24.9 |  | 24.9 | 24.9 |  | 24.9 |  | 24 | 24.9 | 24.9
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 16.6 | 16.6 | 16.6 |  | 16.6 |  | 16.6 | 16.6 |  | 16.6 |  | 16.6 | 16.6 | 16.6
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## WEWA
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | WEWA - West Warwick (33/11kV) | [8 empty] | Supply |  | T058 - Warwick BSP
| Description |  |  |  | Region is South West
Transformer size is 2x33/11kV 10/12.5MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.8% W -0.5%2025 S -0.6% W -0.1%2026 S -0.1% W 0.2%,2027 S 0.5% W 0.2%
|  |  | Latest Peak Compensated Load | [5 empty] | 12.8 MVA on 13/07/2022 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 27 | 27 | 27 |  | 27 |  | 27 | 30 |  | 30 |  | 30 | 30 | 30
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 11.6 | 11.6 | 11.5 |  | 11.6 |  | 11.7 | 13.3 |  | 13.2 |  | 13.2 | 13.3 | 13.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.983 | 0.983 | 0.983 |  | 0.983 |  | 0.983 | 0.986 |  | 0.986 |  | 0.986 | 0.986 | 0.986
|  |  |  | ECC Rating (MVA) |  | 15.2 | 15.2 | 15.2 |  | 15.2 |  | 15.2 | 16.9 |  | 16.9 |  | 16.9 | 16.9 | 16.9
|  |  |  | 50 PoE Load (MVA) |  | 10.6 | 10.6 | 10.5 |  | 10.6 |  | 10.7 | 12.8 |  | 12.7 |  | 12.7 | 12.7 | 12.8
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  |  | Hours PA > 95% Peak Load |  | 2.5 | 2.5 | 2.5 |  | 2.5 |  | 2.5 | 2.5 |  | 2.5 |  | 2.5 | 2.5 | 2.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 30 | 30 | 30 |  | 30 |  | 30 | 30 |  | 30 |  | 30 | 30 | 30
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 15 | 15 | 15 |  | 15 |  | 15 | 15 |  | 15 |  | 15 | 15 | 15
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## WINT
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | WINT - Winton (66/11kV) | [8 empty] | Supply |  | T095 - Millchester BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 2x66/11kV 4MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.7% W -1.4%2025 S -1.7% W -1.3%2026 S -1.2% W -1.0%2027 S -0.5% W -0.8
|  |  | Latest Peak Compensated Load | [5 empty] | 2.9 MVA on 08/12/2022 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 9.4 | 9.4 | 9.4 |  | 9.4 |  | 9.4 | 10.9 |  | 10.9 |  | 10.9 | 10.9 | 10.9
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 3 | 2.9 | 2.9 |  | 2.9 |  | 2.9 | 2.5 |  | 2.4 |  | 2.4 | 2.4 | 2.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.997 | 0.997 | 0.997 |  | 0.997 |  | 0.997 | 0.989 |  | 0.989 |  | 0.989 | 0.989 | 0.989
|  |  |  | ECC Rating (MVA) |  | 5.4 | 5.4 | 5.4 |  | 5.4 |  | 5.4 | 6 |  | 6 |  | 6 | 6 | 6
|  |  |  | 50 PoE Load (MVA) |  | 3 | 2.9 | 2.9 |  | 2.9 |  | 2.9 | 2.3 |  | 2.3 |  | 2.2 | 2.2 | 2.2
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 11.5 | 11.5 | 11.5 |  | 11.5 |  | 11.5 | 11.5 |  | 11.5 |  | 11.5 | 11.5 | 11.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 3 | 3 | 3 |  | 3 |  | 3 | 3 |  | 3 |  | 3 | 3 | 3
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 1.5 | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.5 | 1.5
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## WIRR
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | WIRR - Wirralie (66/33kV) | [8 empty] | Supply |  | NEWL - Newlands BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/33KV 0.63MVA ONAN WIRRSS
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.9% W -0.8%2025 S -0.8% W -0.5%2026 S -0.3% W -0.1%2027 S 0.3% W 0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 0.4 MVA on 23/11/2022 at 19:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 0.7 | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.7 | 0.7
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 0.4 | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.892 | 0.892 | 0.892 |  | 0.892 |  | 0.892 | 0.81 |  | 0.81 |  | 0.81 | 0.81 | 0.81
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 0.4 | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 7.5 | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 | 7.5
|  |  |  | Raw LAR (MVA) |  | 0.4 | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | Mobile Plant Avail (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 0.63 | 0.63 | 0.63 |  | 0.63 |  | 0.63 | 0.63 |  | 0.63 |  | 0.63 | 0.63 | 0.63
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## WOOD
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | WOOD - Woodhouse Station (66/11kV) | [8 empty] | Supply |  | T193 - Clare South BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/11kV 0.25MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 0.0%, 2024 S 0.0% W 0.0%, 2025 S 0.0% W 0.0%, 2026 S 0.0% W 0.0%, 2027 S 0.0% W 0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 0.1 MVA on 01/01/2022 at 17:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.85 | 0.85 | 0.85 |  | 0.85 |  | 0.85 | 0.85 |  | 0.85 |  | 0.85 | 0.85 | 0.85
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 8589.5 | 8589.5 | 8589.5 |  | 8589.5 |  | 8589.5 | 8589.5 |  | 8589.5 |  | 8589.5 | 8589.5 | 8589.5
|  |  |  | Raw LAR (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 0.25 | 0.25 | 0.25 |  | 0.25 |  | 0.25 | 0.25 |  | 0.25 |  | 0.25 | 0.25 | 0.25
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## WOOG
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | WOOG - Woodgate (66/11kV) | [8 empty] | Supply |  | ISIS - Isis BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 1x66/11kV 5MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -1.9% W -0.1%2025 S 0.1% W -0.2%,2026 S 0.7% W 0.2%, 2027 S 1.5% W 0.2%
|  |  | Latest Peak Compensated Load | [5 empty] | 2.7 MVA on 05/07/2022 at 17:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 5.3 | 5.3 | 5.3 |  | 5.3 |  | 5.3 | 5.3 |  | 5.3 |  | 5.3 | 5.3 | 5.3
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 2.6 | 2.6 | 2.6 |  | 2.6 |  | 2.7 | 2.7 |  | 2.7 |  | 2.7 | 2.7 | 2.7
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.991 | 0.991 | 0.991 |  | 0.991 |  | 0.991 | 0.995 |  | 0.995 |  | 0.995 | 0.995 | 0.995
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 2.4 | 2.4 | 2.4 |  | 2.5 |  | 2.5 | 2.4 |  | 2.4 |  | 2.4 | 2.4 | 2.4
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 | 5 | 5
|  |  |  | Raw LAR (MVA) |  | 2.4 | 2.4 | 2.4 |  | 2.5 |  | 2.5 | 2.4 |  | 2.4 |  | 2.4 | 2.4 | 2.4
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 2.2 | 2.2 | 2.2 |  | 2.2 |  | 2.2 | 2.2 |  | 2.2 |  | 2.2 | 2.2 | 2.2
|  |  |  | Mobile Plant Avail (MVA) |  | 0.7 | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.7 | 0.7
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## WOOL
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | WOOL - Woolooga (66/11kV) | [8 empty] | Supply |  | KILK - Kilkivan BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 2x66/11kV 5/6.25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.2% W -1.3%2025 S -1.1% W -1.2%2026 S -0.6% W -0.4%2027 S 0.0% W -0.3%
|  |  | Latest Peak Compensated Load | [5 empty] | 4.9 MVA on 12/02/2023 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 17.7 | 17.7 | 17.7 |  | 17.7 |  | 17.7 | 18.7 |  | 18.7 |  | 18.7 | 18.7 | 18.7
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 5 | 5 | 4.9 |  | 4.9 |  | 5 | 4.1 |  | 4 |  | 4 | 4 | 4
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.974 | 0.974 | 0.974 |  | 0.974 |  | 0.974 | 0.986 |  | 0.986 |  | 0.986 | 0.986 | 0.986
|  |  |  | ECC Rating (MVA) |  | 9.3 | 9.3 | 9.3 |  | 9.3 |  | 9.3 | 9.3 |  | 9.3 |  | 9.3 | 9.3 | 9.3
|  |  |  | 50 PoE Load (MVA) |  | 4.4 | 4.4 | 4.4 |  | 4.4 |  | 4.4 | 3.8 |  | 3.8 |  | 3.7 | 3.7 | 3.7
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 3.5 | 3.5 | 3.5 |  | 3.5 |  | 3.5 | 3.5 |  | 3.5 |  | 3.5 | 3.5 | 3.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 | 5 | 5
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## WOSO
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | WOSO - Woodstock South (66/11kV) | [8 empty] | Supply |  | TMES - Townsville Mesh
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/11kV 6.3MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.6% W -0.4%2025 S -0.4% W -0.2%2026 S 0.0% W 0.1%, 2027 S 0.7% W 0.3%
|  |  | Latest Peak Compensated Load | [5 empty] | 1.2 MVA on 21/11/2022 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 8.6 | 8.6 | 8.6 |  | 8.6 |  | 8.6 | 9.4 |  | 9.4 |  | 9.4 | 9.4 | 9.4
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 1.3 | 1.3 | 1.3 |  | 1.3 |  | 1.4 | 1 |  | 1 |  | 1 | 1 | 1
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.986 | 0.986 | 0.986 |  | 0.986 |  | 0.986 | 0.971 |  | 0.971 |  | 0.971 | 0.971 | 0.971
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 1.3 | 1.3 | 1.3 |  | 1.3 |  | 1.3 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 11.5 | 11.5 | 11.5 |  | 11.5 |  | 11.5 | 11.5 |  | 11.5 |  | 11.5 | 11.5 | 11.5
|  |  |  | Raw LAR (MVA) |  | 1.3 | 1.3 | 1.3 |  | 1.3 |  | 1.3 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 3 | 3 | 3 |  | 3 |  | 3 | 3 |  | 3 |  | 3 | 3 | 3
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 6.3 | 6.3 | 6.3 |  | 6.3 |  | 6.3 | 6.3 |  | 6.3 |  | 6.3 | 6.3 | 6.3
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## WOWA
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | WOWA - Wowan (66/22kV) | [8 empty] | Supply |  | T026 - Biloela BSP
| Description |  |  |  | Region is Capricornia
Transformer size is 2x66/22kV 5/6.3MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.1% W -0.7%2025 S -1.0% W -0.5%2026 S -0.5% W -0.2%2027 S 0.2% W -0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 5.4 MVA on 13/02/2023 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 16.1 | 16.1 | 16.1 |  | 16.1 |  | 16.1 | 18 |  | 18 |  | 18 | 18 | 18
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 5.8 | 5.7 | 5.7 |  | 5.7 |  | 5.8 | 4.9 |  | 4.9 |  | 4.9 | 4.9 | 4.9
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.978 | 0.978 | 0.978 |  | 0.978 |  | 0.978 | 0.998 |  | 0.998 |  | 0.998 | 0.998 | 0.998
|  |  |  | ECC Rating (MVA) |  | 9 | 9 | 9 |  | 9 |  | 9 | 9.4 |  | 9.4 |  | 9.4 | 9.4 | 9.4
|  |  |  | 50 PoE Load (MVA) |  | 5.4 | 5.4 | 5.4 |  | 5.4 |  | 5.4 | 4.6 |  | 4.6 |  | 4.6 | 4.6 | 4.6
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 33 | 33 | 33 |  | 33 |  | 33 | 33 |  | 33 |  | 33 | 33 | 33
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 | 5 | 5
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## YARA
Bulk Summary Information and Peak Load Forecast
Substation |  |  |  | YARA - Yarranlea BSP (110/33kV) | [8 empty] | Supply |  | QMRG - Middle Ridge (Ergon) TCP
Description |  |  |  | Region is South West
Transformer size is 2x110/33/11kV 25/32MVA ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 27.3 MVA
|  | Latest Peak Compensated Load | [5 empty] | 24.4 MVA on 13/02/2023 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[5 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  | NCC Rating (MVA) |  | 64 | 64 | 64 |  | 64 |  | 64 | 64 |  | 64 |  | 64 | 64 | 64
|  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | 10 PoE Load (MVA) |  | 26.1 | 26.5 | 26.4 |  | 26.5 |  | 26.7 | 22.3 |  | 22.7 |  | 22.7 | 22.6 | 22.6
LARn (MVA)
LARn (MW)
|  |  | Power Factor at Peak Load |  | 0.935 | 0.935 | 0.935 |  | 0.935 |  | 0.935 | 0.974 |  | 0.974 |  | 0.974 | 0.974 | 0.974
|  |  | ECC Rating (MVA) |  | 32 | 32 | 32 |  | 32 |  | 32 | 32 |  | 32 |  | 32 | 32 | 32
|  |  | 50 PoE Load (MVA) |  | 24 | 24.4 | 24.3 |  | 24.4 |  | 24.6 | 21.2 |  | 21.7 |  | 21.6 | 21.6 | 21.6
|  |  | 50 PoE Load > 95% (MVA) |  | 1.2 | 1.2 | 1.2 |  | 1.2 |  | 1.2 | 1.1 |  | 1.1 |  | 1.1 | 1.1 | 1.1
|  |  | Hours PA > 95% Peak Load |  | 12 | 12 | 12 |  | 12 |  | 12 | 12 |  | 12 |  | 12 | 12 | 12
Raw LAR (MVA)
|  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Remote Trans Avail (MVA) |  | 7 | 7 | 7 |  | 7 |  | 7 | 7 |  | 7 |  | 7 | 7 | 7
|  |  | Manual Trans Avail (MVA) |  | 1.7 | 1.7 | 1.7 |  | 1.7 |  | 1.7 | 1.7 |  | 1.7 |  | 1.7 | 1.7 | 1.7
|  |  | Mobile Plant Avail (MVA) |  | 2.5 | 2.5 | 2.5 |  | 2.5 |  | 2.5 | 2.5 |  | 2.5 |  | 2.5 | 2.5 | 2.5
|  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Capacity for Embedded Generation (MVA) |  | 50 | 50 | 50 |  | 50 |  | 50 | 50 |  | 50 |  | 50 | 50 | 50
|  |  | Firm Capacity for Embedded Generation (MVA) |  | 25 | 25 | 25 |  | 25 |  | 25 | 25 |  | 25 |  | 25 | 25 | 25
LARc (MVA)
LARc (MW)
|  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## YARR
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | YARR - Yarraman (66/11kV) | [8 empty] | Supply |  | H018 - Tarong BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 2x66/11kV 5/6MVA ON/ONB
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.6% W -0.3%2025 S -0.6% W -0.3%2026 S -0.1% W 0.0%,2027 S 0.6% W 0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 4.5 MVA on 12/02/2023 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 15.5 | 15.5 | 15.5 |  | 15.5 |  | 15.5 | 17.9 |  | 17.9 |  | 17.9 | 17.9 | 17.9
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 4.8 | 4.8 | 4.8 |  | 4.8 |  | 4.8 | 4.9 |  | 4.8 |  | 4.8 | 4.8 | 4.8
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.982 | 0.982 | 0.982 |  | 0.982 |  | 0.982 | 0.99 |  | 0.99 |  | 0.99 | 0.99 | 0.99
|  |  |  | ECC Rating (MVA) |  | 8.5 | 8.5 | 8.5 |  | 8.5 |  | 8.5 | 9 |  | 9 |  | 9 | 9 | 9
|  |  |  | 50 PoE Load (MVA) |  | 4.4 | 4.4 | 4.4 |  | 4.4 |  | 4.4 | 4.5 |  | 4.5 |  | 4.5 | 4.5 | 4.5
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 6.5 | 6.5 | 6.5 |  | 6.5 |  | 6.5 | 6.5 |  | 6.5 |  | 6.5 | 6.5 | 6.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 | 5 | 5
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## YASO
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | YASO - Yarranlea South (33/11kV) | [8 empty] | Supply |  | YARA - Yarranlea BSP
| Description |  |  |  | Region is South West
Transformer size is 1x33/11kV 1.5MVA ONAN;1x33/11kV 1MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.9% W -0.4%2025 S -0.9% W -0.4%2026 S -0.4% W -0.0%2027 S 0.3% W 0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 1.5 MVA on 13/02/2023 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 2.8 | 2.8 | 2.8 |  | 2.8 |  | 2.8 | 2.8 |  | 2.8 |  | 2.8 | 2.8 | 2.8
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 1.5 | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.1 |  | 1.1 |  | 1.1 | 1.1 | 1.1
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.85 | 0.85 | 0.85 |  | 0.85 |  | 0.85 | 0.85 |  | 0.85 |  | 0.85 | 0.85 | 0.85
|  |  |  | ECC Rating (MVA) |  | 1.2 | 1.2 | 1.2 |  | 1.2 |  | 1.2 | 1.3 |  | 1.3 |  | 1.3 | 1.3 | 1.3
|  |  |  | 50 PoE Load (MVA) |  | 1.5 | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.1 |  | 1.1 |  | 1.1 | 1.1 | 1.1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 8.5 | 8.5 | 8.5 |  | 8.5 |  | 8.5 | 8.5 |  | 8.5 |  | 8.5 | 8.5 | 8.5
|  |  |  | Raw LAR (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 1.2 | 1.2 | 1.2 |  | 1.2 |  | 1.2 | 1.2 |  | 1.2 |  | 1.2 | 1.2 | 1.2
|  |  |  | Mobile Plant Avail (MVA) |  | 0.4 | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## YEPP
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | YEPP - Yeppoon (66/11kV) | [8 empty] | Supply |  | RMES - Rockhampton Mesh
| Description |  |  |  | Region is Capricornia
Transformer size is 2x66/11kV 16/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.5% W -0.2%2025 S -0.5% W 0.0%,2026 S -0.1% W 0.3%,2027 S 0.8% W 0.6%
|  |  | Latest Peak Compensated Load | [5 empty] | 25.8 MVA on 13/02/2023 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 59 | 59 | 59 |  | 59 |  | 59 | 67.8 |  | 67.8 |  | 67.8 | 67.8 | 67.8
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 30.1 | 30 | 30 |  | 30.2 |  | 30.6 | 21.2 |  | 21.1 |  | 21.1 | 21.2 | 21.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.994 | 0.994 | 0.994 |  | 0.994 |  | 0.994 | 0.999 |  | 0.999 |  | 0.999 | 0.999 | 0.999
|  |  |  | ECC Rating (MVA) |  | 32.3 | 32.3 | 32.3 |  | 32.3 |  | 32.3 | 36.3 |  | 36.3 |  | 36.3 | 36.3 | 36.3
|  |  |  | 50 PoE Load (MVA) |  | 26.5 | 26.4 | 26.4 |  | 26.6 |  | 26.9 | 19.2 |  | 19.2 |  | 19.2 | 19.3 | 19.4
|  |  |  | 50 PoE Load > 95% (MVA) |  | 1.3 | 1.3 | 1.3 |  | 1.3 |  | 1.3 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Hours PA > 95% Peak Load |  | 6 | 6 | 6 |  | 6 |  | 6 | 6 |  | 6 |  | 6 | 6 | 6
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 1.5 | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.5 | 1.5
|  |  |  | Capacity for Embedded Generation (MVA) |  | 32 | 32 | 32 |  | 32 |  | 32 | 32 |  | 32 |  | 32 | 32 | 32
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 16 | 16 | 16 |  | 16 |  | 16 | 16 |  | 16 |  | 16 | 16 | 16
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## Z1313
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | Z1313 - Charleville 11kV (66/11kV) | [8 empty] | Supply |  | Z1796 - Charleville Tx Accumulator
| Description |  |  |  | Region is South West
Transformer size is 1x66/11kV 7.5/8.5MVA ONAF;1x22/11kV 6MVA ONAN(Standby)
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.4% W -0.7%2025 S -1.4% W -0.5%2026 S -0.9% W -0.2%2027 S -0.1% W -0.2
|  |  | Latest Peak Compensated Load | [5 empty] | 7.1 MVA on 07/12/2022 at 16:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 9.4 | 9.4 | 9.4 |  | 9.4 |  | 9.4 | 10.3 |  | 10.3 |  | 10.3 | 10.3 | 10.3
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 6.3 | 6.2 | 6.1 |  | 6.1 |  | 6.2 | 6 |  | 6 |  | 6 | 5.9 | 5.9
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.937 | 0.938 | 0.939 |  | 0.939 |  | 0.938 | 0.986 |  | 0.986 |  | 0.986 | 0.986 | 0.986
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 5.9 | 5.8 | 5.7 |  | 5.7 |  | 5.8 | 5.6 |  | 5.6 |  | 5.6 | 5.5 | 5.5
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Hours PA > 95% Peak Load |  | 56 | 56 | 56 |  | 56 |  | 56 | 56 |  | 56 |  | 56 | 56 | 56
|  |  |  | Raw LAR (MVA) |  | 5.9 | 5.8 | 5.7 |  | 5.7 |  | 5.8 | 5.6 |  | 5.6 |  | 5.6 | 5.5 | 5.5
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 6 | 6 | 6 |  | 6 |  | 6 | 6 |  | 6 |  | 6 | 6 | 6
|  |  |  | Mobile Plant Avail (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 | 2 | 2
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 7.5 | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 | 7.5
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## Z1314
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | Z1314 - Charleville 22kV (66/22kV) | [8 empty] | Supply |  | Z1796 - Charleville Tx Accumulator
| Description |  |  |  | Region is South West
Transformer size is 1x66/22kV 7.5/8.5MVA ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.0% W -0.6%2025 S -0.8% W -0.4%2026 S -0.4% W -0.1%2027 S 0.3% W -0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 4.9 MVA on 07/12/2022 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 9.3 | 9.3 | 9.3 |  | 9.3 |  | 9.3 | 9.3 |  | 9.3 |  | 9.3 | 9.3 | 9.3
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 5.3 | 5.3 | 5.3 |  | 5.3 |  | 5.3 | 4.4 |  | 4.4 |  | 4.3 | 4.3 | 4.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.968 | 0.968 | 0.968 |  | 0.968 |  | 0.968 | 0.994 |  | 0.994 |  | 0.994 | 0.994 | 0.994
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 5 | 5 | 5 |  | 5 |  | 5 | 4.2 |  | 4.2 |  | 4.2 | 4.2 | 4.2
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 65 | 65 | 65 |  | 65 |  | 65 | 65 |  | 65 |  | 65 | 65 | 65
|  |  |  | Raw LAR (MVA) |  | 5 | 5 | 5 |  | 5 |  | 5 | 4.2 |  | 4.2 |  | 4.2 | 4.2 | 4.2
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 6 | 6 | 6 |  | 6 |  | 6 | 6 |  | 6 |  | 6 | 6 | 6
|  |  |  | Mobile Plant Avail (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 | 2 | 2
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 7.5 | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 | 7.5
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## Z1326
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | Z1326 - Cunnamulla 11kV (66/11kV) | [8 empty] | Supply |  | CUTA - Cunnamulla Tx Accumulator
| Description |  |  |  | Region is South West
Transformer size is 1x66/11kV 5MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.5% W -1.2%2025 S -1.3% W -0.9%2026 S -0.9% W -0.6%2027 S -0.2% W -0.5
|  |  | Latest Peak Compensated Load | [5 empty] | 2 MVA on 20/07/2022 at 17:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 5.6 | 5.6 | 5.6 |  | 5.6 |  | 5.6 | 7.2 |  | 7.2 |  | 7.2 | 7.2 | 7.2
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 2.4 | 2.3 | 2.3 |  | 2.3 |  | 2.3 | 2.1 |  | 2 |  | 2 | 2 | 2
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.889 | 0.889 | 0.889 |  | 0.889 |  | 0.889 | 0.99 |  | 0.99 |  | 0.99 | 0.99 | 0.99
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 2.3 | 2.2 | 2.2 |  | 2.2 |  | 2.2 | 1.9 |  | 1.9 |  | 1.9 | 1.9 | 1.9
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 13 | 13 | 13 |  | 13 |  | 13 | 13 |  | 13 |  | 13 | 13 | 13
|  |  |  | Raw LAR (MVA) |  | 2.3 | 2.2 | 2.2 |  | 2.2 |  | 2.2 | 1.9 |  | 1.9 |  | 1.9 | 1.9 | 1.9
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Mobile Plant Avail (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 | 2 | 2
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
Capacity for Embedded Generation (MVA)
Firm Capacity for Embedded Generation (MVA)
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## Z1327
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | Z1327 - Cunnamulla 22kV (66/22kV) | [8 empty] | Supply |  | CUTA - Cunnamulla Tx Accumulator
| Description |  |  |  | Region is South West
Transformer size is 1x66/22kV 5MVA ONAN;1x22/11kV 3MVA ONAN(Standby)
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -3.5% W -0.9%2025 S -1.3% W -0.6%2026 S -0.8% W -0.3%2027 S -0.2% W -0.3
|  |  | Latest Peak Compensated Load | [5 empty] | 2.7 MVA on 20/03/2023 at 17:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 5.6 | 5.6 | 5.6 |  | 5.6 |  | 5.6 | 6.9 |  | 6.9 |  | 6.9 | 6.9 | 6.9
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 2.7 | 2.7 | 2.6 |  | 2.6 |  | 2.6 | 2.7 |  | 2.6 |  | 2.6 | 2.6 | 2.6
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.962 | 0.962 | 0.962 |  | 0.962 |  | 0.962 | 0.911 |  | 0.89 |  | 0.89 | 0.89 | 0.89
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 2.6 | 2.6 | 2.5 |  | 2.5 |  | 2.6 | 2.6 |  | 2.5 |  | 2.5 | 2.5 | 2.5
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 24.5 | 24.5 | 24.5 |  | 24.5 |  | 24.5 | 24.5 |  | 24.5 |  | 24.5 | 24.5 | 24.5
|  |  |  | Raw LAR (MVA) |  | 2.6 | 2.6 | 2.5 |  | 2.5 |  | 2.6 | 2.6 |  | 2.5 |  | 2.5 | 2.5 | 2.5
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Mobile Plant Avail (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 | 2 | 2
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 | 5 | 5
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 3 | 3 | 3 |  | 3 |  | 3 | 3 |  | 3 |  | 3 | 3 | 3
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## Z1350
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | Z1350 - Gooburrum 3.3kV (66/3.3kV) | [8 empty] | Supply |  | BUND - Bundaberg BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 1x66/3.3/11kV 3MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 0.0%, 2024 S 0.0% W 0.0%, 2025 S 0.0% W 0.0%, 2026 S 0.0% W 0.0%, 2027 S 0.0% W 0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 1.5 MVA on 24/02/2023 at 21:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 4.4 | 4.4 | 4.4 |  | 4.4 |  | 4.4 | 4.5 |  | 4.5 |  | 4.5 | 4.5 | 4.5
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 1.5 | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 0.8 |  | 0.8 |  | 0.8 | 0.8 | 0.8
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.863 | 0.863 | 0.863 |  | 0.863 |  | 0.863 | 0.863 |  | 0.863 |  | 0.863 | 0.863 | 0.863
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 1.5 | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 0.8 |  | 0.8 |  | 0.8 | 0.8 | 0.8
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 1215.5 | 1215.5 | 1215.5 |  | 1215.5 |  | 1215.5 | 1215.5 |  | 1215.5 |  | 1215.5 | 1215.5 | 1215.5
|  |  |  | Raw LAR (MVA) |  | 1.5 | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 0.8 |  | 0.8 |  | 0.8 | 0.8 | 0.8
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Mobile Plant Avail (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 | 2 | 2
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 3 | 3 | 3 |  | 3 |  | 3 | 3 |  | 3 |  | 3 | 3 | 3
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## Z300
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | Z300 - Monduran Dam DNR (66/3.3kV) | [8 empty] | Supply |  | BUND - Bundaberg BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 1xMODA TX NO 1-66/11/3.3KV TRANSF 1;1xMODA TX NO 2-66/11/3.3KV TRANSF 2(Standby)
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 0.0%, 2024 S 0.0% W 0.0%, 2025 S 0.0% W 0.0%, 2026 S 0.0% W 0.0%, 2027 S 0.0% W 0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 1.2 MVA on 13/01/2023 at 11:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 3 | 3 | 3 |  | 3 |  | 3 | 3 |  | 3 |  | 3 | 3 | 3
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 1.2 | 1.2 | 1.2 |  | 1.2 |  | 1.2 | 0.9 |  | 0.9 |  | 0.9 | 0.9 | 0.9
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.821 | 0.821 | 0.821 |  | 0.821 |  | 0.821 | 0.822 |  | 0.822 |  | 0.822 | 0.822 | 0.822
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 1.2 | 1.2 | 1.2 |  | 1.2 |  | 1.2 | 0.9 |  | 0.9 |  | 0.9 | 0.9 | 0.9
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 19.5 | 19.5 | 19.5 |  | 19.5 |  | 19.5 | 19.5 |  | 19.5 |  | 19.5 | 19.5 | 19.5
|  |  |  | Raw LAR (MVA) |  | 1.2 | 1.2 | 1.2 |  | 1.2 |  | 1.2 | 0.9 |  | 0.9 |  | 0.9 | 0.9 | 0.9
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 3 | 3 | 3 |  | 3 |  | 3 | 3 |  | 3 |  | 3 | 3 | 3
|  |  |  | Mobile Plant Avail (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 | 2 | 2
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## Z454
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | Z454 - Waggamba 132/66kV (66/66kV) | [8 empty] | Supply |  | T156 - Waggamba BSP
| Description |  |  |  | Region is South West
Transformer size is 1xWAGG TFR3-33/0.415KV TRANSF 3(Standby);1xWAGG TFR1-132/66/33KV TRANSF 1
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 0.0%, 2024 S 0.0% W 0.0%, 2025 S 0.0% W 0.0%, 2026 S 0.0% W 0.0%, 2027 S 0.0% W 0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 19.1 MVA on 05/07/2022 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 33 | 33 | 33 |  | 33 |  | 33 | 33 |  | 33 |  | 33 | 33 | 33
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 14.5 | 14.5 | 14.5 |  | 14.5 |  | 14.5 | 19.7 |  | 19.7 |  | 19.7 | 19.7 | 19.7
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.999 | 0.999 | 0.999 |  | 0.999 |  | 0.999 | 0.997 |  | 0.997 |  | 0.997 | 0.997 | 0.997
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 13.9 | 13.9 | 13.9 |  | 13.9 |  | 13.9 | 18.7 |  | 18.7 |  | 18.7 | 18.7 | 18.7
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.7 | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.9 |  | 0.9 |  | 0.9 | 0.9 | 0.9
|  |  |  | Hours PA > 95% Peak Load |  | 8 | 8 | 8 |  | 8 |  | 8 | 8 |  | 8 |  | 8 | 8 | 8
|  |  |  | Raw LAR (MVA) |  | 13.9 | 13.9 | 13.9 |  | 13.9 |  | 13.9 | 18.7 |  | 18.7 |  | 18.7 | 18.7 | 18.7
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Mobile Plant Avail (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 | 2 | 2
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
Capacity for Embedded Generation (MVA)
Firm Capacity for Embedded Generation (MVA)
|  |  |  | LARc (MVA) |  | 10.9 | 10.9 | 10.9 |  | 10.9 |  | 10.9 | 15.7 |  | 15.7 |  | 15.7 | 15.7 | 15.7
|  |  |  | LARc (MW) |  | 10.9 | 10.9 | 10.9 |  | 10.9 |  | 10.9 | 15.7 |  | 15.7 |  | 15.7 | 15.7 | 15.7
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | No | No | No |  | No |  | No | No |  | No |  | No | No | No
Return to Index

## Z1553
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | Z1553 - Yeppoon 11/22kv (11/22kV) | [8 empty] | Supply |  | YACC - Yeppoon 22kV Accumulator
| Description |  |  |  | Region is Capricornia
Transformer size is 1x11/22KV 10MVA ONAN;1x11/22KV 10MVA ONAN YEPP(Standby)
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2023 W 1.8%, 2024 S -2.3% W 0.6%,2025 S -0.3% W 0.8%,2026 S 0.2% W 1.0%, 2027 S 1.1% W 1.3%
|  |  | Latest Peak Compensated Load | [5 empty] | 1.9 MVA on 13/02/2023 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2023/24 | 2024/25 | 2025/26 |  | 2026/27 |  | 2027/28 | 2023 |  | 2024 |  | 2025 | 2026 | 2027
|  |  |  | NCC Rating (MVA) |  | 11 | 11 | 11 |  | 11 |  | 11 | 11 |  | 11 |  | 11 | 11 | 11
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 2.1 | 2.1 | 2.1 |  | 2.1 |  | 2.2 | 1.6 |  | 1.6 |  | 1.7 | 1.7 | 1.7
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.997 | 0.997 | 0.997 |  | 0.997 |  | 0.997 | 0.999 |  | 0.999 |  | 0.999 | 0.999 | 0.999
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 1.5 |  | 1.5 |  | 1.5 | 1.6 | 1.6
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 8.5 | 8.5 | 8.5 |  | 8.5 |  | 8.5 | 8.5 |  | 8.5 |  | 8.5 | 8.5 | 8.5
|  |  |  | Raw LAR (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 1.5 |  | 1.5 |  | 1.5 | 1.6 | 1.6
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 6 | 6 | 6 |  | 6 |  | 6 | 6 |  | 6 |  | 6 | 6 | 6
|  |  |  | Mobile Plant Avail (MVA) |  | 4 | 4 | 4 |  | 4 |  | 4 | 4 |  | 4 |  | 4 | 4 | 4
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Capacity for Embedded Generation (MVA) |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10
|  |  |  | Firm Capacity for Embedded Generation (MVA) |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index