## Disclaimer & Introduction
1. Disclaimer and Introduction
1.1 Disclaimer
These set of Subtransmission load flow studies results are prepared and made available solely for information purposes as part of the Distribution Annual Planning Report (DAPR). Whilst care was taken in the preparation of the information in this report, and it is provided with the best intentions and good faith, the Network Modelling Team accepts no responsibility or liability (including without limitation, liability to any person by reason of negligence or negligent mis-statement) for any loss or damage that may be incurred by any person acting in reliance on this information or assumptions drawn from it, except to the extent that liability under any applicable Queensland or Commonwealth of Australia statute cannot be excluded.
Ergon Energy makes no representation or warranty as to the accuracy, reliability, completeness or suitability for any particular purpose of the information in this document. All information should be independently investigated, reviewed, analysed, and verified, and must not be relied upon in connection with any investment proposal or decision. The information contained in this report is subject to annual review.
The Known Issues section below outlines some factors that could affect the accuracy of the results presented in this studies summary and should be considered when making network augmentation or financial decisions based on these values. The basis of the disclosed studies results are the network demand forecasts obtained from the SIFT system/database. The Network Modelling Team obtain these forecast values as populated by the Strategic Forecasting Team following quality assurance processes for accuracy.
1.2 Introduction and Methodology
This load flow studies summary is prepared to provide a reference for Strategic Planners during the preparation of the DAPR. Engineers should carry out their own due diligence on the information provided by this summary prior to applying it to engineering activities. The results of these studies contained herein are produced as per the methodology described below.
In preparing the load flow summary results:
· The subtransmission network model was developed and prepared using Power Factory 2021 SP4. The results were calculated in Power Factory 2023 SP4.
· For the Ergon Energy network the model is connected to the Powerlink TAPR model at the common coupling points.
· All approved projects (in the form of variations) and new connection load/generators are incorporated into the model
· Obtain 10 and 50 PoE demand forecasts from SIFT and minimum demand forecast from Tableau
· Using Python automation to pull demand forecasts into Power Factory model
· Run Load Flow studies for each of the following scenarios and document result summaries:
Ergon Energy Network (EE)
a) Time of Day conditions with SIFT 10% PoE profile (10PoE_EE_NNC);
b) Static normal conditions with minimum demand profile (MinLoad_EE_NNC);
c) N-1 conditions with SIFT 50% PoE profile (50PoE_EE_N-1);
d) N-1 conditions with minimum demand profile (MinLoad_EE_N-1);
1.3 High level Process Summary
1. Derive Master Model, Pack External Objects and Export
2. Activate Model
3. Activate Load Characteristic Application Study Case (ie. 2023TransLF-ErgonSubtrans-WithVars for EE, EnergexST_AppPrjs[DAPR2023] for EX)
4. Run Forecast Load script for required conditions (e.g. 10PoE Day SUMWIN for 10PoE peak conditions)
5. Run Power Factory Information Producer (ie. a Report Nearly Anything Sequential Creator and Task Automation of Report Nearly anything Scripts or SubtransFeederForecastProducer for 10PoE_EE_NNC)
6. Repeat steps 3-5 for other Load Characteristic Configurations if required
8. Run a Python Interpreter that reads the output files and produces the formatted document
1.4 Definition of Terms Feeder Capacity and Forecast Tables
Term | Definition
10 PoE Load (A) | Peak load forecast with 10% probability of being exceeded (one in every 10 years will be exceeded). Based on normal expected growth rates and weather corrected starting loads.
50 PoE Load (A) | Peak load forecast with 50% probability of being exceeded (one in every two years will be exceeded). Based on normal expected growth rates & weather corrected starting loads. This is the worst case (highest) load forecast beween summer day and summer night.
NNC | Normal Network Configuration, Outages labelled "_NNC" indicate the limitations for the feeder were identical or worse under the Normal Network Configuration.
NCC Rating (A) | Normal Cyclic Capacity - the total capacity with all network components and equipment intact. This is the maximum permissible peak daily loading for a given load cycle that a feeder can supply each day of its life. For overhead feeders, the NCC is the conductor rating with an assumed 1m/s wind, orthogonal to the line. For underground cables, the NCC assumes that there are sufficient temperature and current operating margins from the thermal inertia of the cable and its surroundings.
Power Factor (System Normal) | Lowest power factor along the feeder at 10 PoE Peak Load. Where the Power Factor is either 0 or blank, the feeder is a normally open feeder that does not have load under System Normal conditions.
Security Standard | For security standard application, the general type of customer a sub-transmission, or transmission feeder is supplying.
Transfers | This is the total amount of load transfers that are available following the worst case network contingency. This includes automatic transfers that are controlled automatically through SCADA and are generally implemented within a minute, load transfers that can be implemented through screen switching by a network controller, manual transfers that are deployed via manually controlled switchgear locally by field staff, and mobile generation which can be deployed by field staff by moving generation to specific sites.
Note: It should be noted under the Safety Net in the Distribution Authority, it is generally assumed that 4MVA (70A) of generation is available for Urban feeders and 10MVA (170A) for Rural feeders to meet specific criteria. These values have been used as a default in the forecast tables where these are sufficient to reduce the 50PoE load below the ECC rating. Where the load is still above the ECC rating, specific load transfers have been calculated for the feeder to determine whether the Safety Net criteria is met.

## Important Info-10PoE_EE_NCC
2. Important Information
2.1 Study Information - 10PoE_EE_NNC
A summary of most information used as inputs is given in the Study Info Worksheet referenced below. This includes what Project Version was used, Study times, Variations, what Generators are included etc.
2.2 Results
The results of this study are referenced in the documented versions disclosed below.
Result Version: | 10PoE_EE_NNC_20231014_0920 10PoE_EE_NNC_20231017_1055
2.3 Known Issues and Limitations
· The List of Subtransmission Projects to be stored as Variations has been produced manually from Copperleaf and SIFT for the next 10 years.
· Automatic Outage Switching is not incorporated for both Ergon Energy and Energex N-1 Studies
· Ratings are the NCC (Normal Cyclic Capacity) Rating and do not consider increased capacity due to the outage (eg. Parallel cable runs where no load in another feeder increases trench capacity for the remaining feeders)
· N-1 Outages modelled take the entire feeder out of service.
· N-1 Outages that do not produce convergent results are ignored. The list of these can be seen in the Study Info worksheet.
· North West Power System (ie. The Network around Mount Isa) has been reported in a separate Spreadsheet this year.
· The Report is not suitable to determine "directionality" of the real or reactive power-flows due to the use of absolute value functions prior to the limits being calculated.
3. Additional Information
2.1 Information About Variables
The Values for a given timeslot shown are calculated as follows. All of the values will be for the line element in Power Factory with the Loading Constraint.
This means that the Power Factor and Voltage values are recorded at the line that is considered the most "limited" not the minimum voltage on the feeder or the minimum Power Factor on the feeder.
For each Contingency Event the values for each line are recorded with them eventually ending up in the following fields
% of Rated A: The % Utilisation called "loading" in Power Factory [c:loading]
Loading (A): Absolute Maximum Current for Both Ends in kA
Loading (MVA): Absolute Maximum Apparent Power for Both Ends in MVA
Loading (MW): Absolute Maximum Real Power for Both Ends in MW
Power Factor: Absolute Min Power Factor for Both Ends
Rating (A): Line Nominal Rating using [e:Inom_a]
Min Voltage at Constrained Conductor: Min Voltage seen on both sides of the feeder line
Once they are calculated for each feeder and Timeslot the Limiting entry is determined. This will be the values for a single line limited in the following order.
At each step all lines that share the "limiting" value will be recorded, provided their float representative is identical.
Minor differences in the float representation will result in the Min or Max value being utilised even if the value when considering real life significant figures are otherwise identical.
1. % of Rated A - Max
2. Rating (A) - Min
3. Loading (MVA) - Max
The following limit calculations are applied to ensure only 1 line's values are recorded even if all entries have the same electrical loading characteristics.
4. Contingency Outage: Alphabetical Max
Note that "_NNC" is used with is a "Normal Network Configuration" contingency where nothing is taken out of service. If it is displayed, then taking a feeder out of service did not make a recordable difference to the feeder loading.
If multiple feeder outage contingencies have the same effect on the feeder, then the higher alphabetical name will be recorded.
5. Limiting Line Name: Alphabetical Min: This is to ensure there is a unique value
6. Current Study Case Time: Alphabetical Min: This is a stopgap to ensure there is a unique value

## 10PoE_EE_NNC
Region | ECORP ID | Operational Number | Feeder Name | Operational Name | Variable | 2024 SD | 2024 SE | 2024 SNM | 2025 SD | 2025 SE | 2025 SNM | 2026 SD | 2026 SE | 2026 SNM | 2027 SD | 2027 SE | 2027 SNM | 2028 SD | 2028 SE | 2028 SNM
CA | 40000958 | 6074 | From LCSS to TANB | 6074_Lakes Creek - Tanby 66 kV | % of Rated A | 43.0222 | 47.1036 | 37.9541 | 43.2312 | 47.0088 | 38.1212 | 43.0061 | 47.0707 | 38.2263 | 43.622 | 47.578 | 38.7225 | 44.5104 | 48.7272 | 39.5948
CA | 40000958 | 6074 | From LCSS to TANB | 6074_Lakes Creek - Tanby 66 kV | Limiting Line Name | TR_LINE 19802_1 | TR_LINE 19802_1 | TR_LINE 19802_1 | TR_LINE 19802_1 | TR_LINE 19802_1 | TR_LINE 19802_1 | TR_LINE 19802_1 | TR_LINE 19802_1 | TR_LINE 19802_1 | TR_LINE 19802_1 | TR_LINE 19802_1 | TR_LINE 19802_1 | TR_LINE 19802_1 | TR_LINE 19802_1 | TR_LINE 19802_1
CA | 40000958 | 6074 | From LCSS to TANB | 6074_Lakes Creek - Tanby 66 kV | Loading (A) | 171.6587 | 195.48 | 140.4303 | 172.4926 | 195.0865 | 141.0483 | 171.5945 | 195.3432 | 141.4373 | 174.0519 | 197.4488 | 143.2731 | 177.5967 | 202.218 | 146.5006
CA | 40000958 | 6074 | From LCSS to TANB | 6074_Lakes Creek - Tanby 66 kV | Loading (MVA) | 20.2207 | 22.8502 | 16.6063 | 20.193 | 22.8175 | 16.5788 | 20.1621 | 22.8328 | 16.6179 | 20.3716 | 23.2047 | 16.8775 | 20.8307 | 23.7325 | 17.2426
CA | 40000958 | 6074 | From LCSS to TANB | 6074_Lakes Creek - Tanby 66 kV | Loading (MW) | 19.6127 | 22.0549 | 16.246 | 19.5943 | 22.0272 | 16.2267 | 19.5592 | 22.0432 | 16.2639 | 19.7634 | 22.3905 | 16.5076 | 20.1861 | 22.869 | 16.8489
CA | 40000958 | 6074 | From LCSS to TANB | 6074_Lakes Creek - Tanby 66 kV | Power Factor | 0.96993 | 0.96519 | 0.97831 | 0.97035 | 0.96537 | 0.97876 | 0.9701 | 0.96542 | 0.97869 | 0.97014 | 0.96491 | 0.97808 | 0.96905 | 0.96362 | 0.97717
CA | 40000958 | 6074 | From LCSS to TANB | 6074_Lakes Creek - Tanby 66 kV | Rating (A) | 399 | 415 | 370 | 399 | 415 | 370 | 399 | 415 | 370 | 399 | 415 | 370 | 399 | 415 | 370
CA | 40000958 | 6074 | From LCSS to TANB | 6074_Lakes Creek - Tanby 66 kV | Time | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00
CA | 40000958 | 6074 | From LCSS to TANB | 6074_Lakes Creek - Tanby 66 kV | Voltage at Constrained Conductor | 68.0097 | 67.4881 | 68.2732 | 67.5881 | 67.5273 | 67.8617 | 67.8379 | 67.4839 | 67.8347 | 67.5751 | 67.8518 | 68.0116 | 67.7187 | 67.7583 | 67.9519
CA | 40000980 | 6047 | Coominglah Sub Tee | 6047_Coominglah Sub Tee 66 kV | % of Rated A | 7.8161 | 6.4403 | 5.5708 | 7.8107 | 6.4347 | 5.5674 | 7.8103 | 6.4344 | 5.5672 | 7.8104 | 6.4344 | 5.5683 | 7.8179 | 6.44 | 5.5718
CA | 40000980 | 6047 | Coominglah Sub Tee | 6047_Coominglah Sub Tee 66 kV | Limiting Line Name | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1
CA | 40000980 | 6047 | Coominglah Sub Tee | 6047_Coominglah Sub Tee 66 kV | Loading (A) | 12.0369 | 13.3314 | 11.0858 | 12.0284 | 13.3199 | 11.0791 | 12.0278 | 13.3192 | 11.0787 | 12.028 | 13.3191 | 11.081 | 12.0395 | 13.3309 | 11.0878
CA | 40000980 | 6047 | Coominglah Sub Tee | 6047_Coominglah Sub Tee 66 kV | Loading (MVA) | 1.3921 | 1.5332 | 1.3061 | 1.3921 | 1.5332 | 1.306 | 1.3921 | 1.5332 | 1.306 | 1.3921 | 1.5332 | 1.3061 | 1.3922 | 1.5332 | 1.3061
CA | 40000980 | 6047 | Coominglah Sub Tee | 6047_Coominglah Sub Tee 66 kV | Loading (MW) | 1.2743 | 1.4009 | 1.1968 | 1.2743 | 1.4009 | 1.1968 | 1.2743 | 1.4009 | 1.1968 | 1.2743 | 1.4009 | 1.1968 | 1.2743 | 1.4009 | 1.1969
CA | 40000980 | 6047 | Coominglah Sub Tee | 6047_Coominglah Sub Tee 66 kV | Power Factor | 0.91534 | 0.91371 | 0.91637 | 0.91536 | 0.91373 | 0.91639 | 0.91536 | 0.91374 | 0.91639 | 0.91536 | 0.91374 | 0.91638 | 0.91533 | 0.91371 | 0.91637
CA | 40000980 | 6047 | Coominglah Sub Tee | 6047_Coominglah Sub Tee 66 kV | Rating (A) | 154 | 207 | 199 | 154 | 207 | 199 | 154 | 207 | 199 | 154 | 207 | 199 | 154 | 207 | 199
CA | 40000980 | 6047 | Coominglah Sub Tee | 6047_Coominglah Sub Tee 66 kV | Time | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00
CA | 40000980 | 6047 | Coominglah Sub Tee | 6047_Coominglah Sub Tee 66 kV | Voltage at Constrained Conductor | 66.7745 | 66.4008 | 68.0206 | 66.8195 | 66.4553 | 68.0602 | 66.8227 | 66.4589 | 68.0628 | 66.8217 | 66.4592 | 68.0492 | 66.7602 | 66.4031 | 68.0089
CA | 40000983 | 6026 | From T27 to THSS | 6026_Moura - Theodore 66 kV | % of Rated A | 15.0239 | 14.3585 | 13.6709 | 14.9006 | 14.2403 | 13.5593 | 14.7757 | 14.1206 | 13.4466 | 14.7757 | 14.1206 | 13.4466 | 14.9008 | 14.2404 | 13.5593
CA | 40000983 | 6026 | From T27 to THSS | 6026_Moura - Theodore 66 kV | Limiting Line Name | TR_LINE 59682_1 | TR_LINE 59682_1 | TR_LINE 59682_1 | TR_LINE 59682_1 | TR_LINE 59682_1 | TR_LINE 59682_1 | TR_LINE 59682_1 | TR_LINE 59682_1 | TR_LINE 59682_1 | TR_LINE 59682_1 | TR_LINE 59682_1 | TR_LINE 59682_1 | TR_LINE 59682_1 | TR_LINE 59682_1 | TR_LINE 59682_1
CA | 40000983 | 6026 | From T27 to THSS | 6026_Moura - Theodore 66 kV | Loading (A) | 109.5227 | 112.4253 | 97.0616 | 108.6238 | 111.4996 | 96.2691 | 107.7134 | 110.5628 | 95.4691 | 107.7135 | 110.5629 | 95.4691 | 108.6249 | 111.5007 | 96.2692
CA | 40000983 | 6026 | From T27 to THSS | 6026_Moura - Theodore 66 kV | Loading (MVA) | 12.6943 | 12.8213 | 11.1536 | 12.5934 | 12.7193 | 11.0651 | 12.4924 | 12.6174 | 10.9766 | 12.4924 | 12.6174 | 10.9766 | 12.5934 | 12.7193 | 11.0651
CA | 40000983 | 6026 | From T27 to THSS | 6026_Moura - Theodore 66 kV | Loading (MW) | 12.3323 | 12.4531 | 10.8493 | 12.2355 | 12.3554 | 10.7642 | 12.1387 | 12.2576 | 10.6791 | 12.1387 | 12.2576 | 10.6791 | 12.2355 | 12.3554 | 10.7642
CA | 40000983 | 6026 | From T27 to THSS | 6026_Moura - Theodore 66 kV | Power Factor | 0.97148 | 0.97128 | 0.97272 | 0.97158 | 0.97139 | 0.9728 | 0.97169 | 0.97149 | 0.97289 | 0.97169 | 0.97149 | 0.97289 | 0.97158 | 0.97139 | 0.9728
CA | 40000983 | 6026 | From T27 to THSS | 6026_Moura - Theodore 66 kV | Rating (A) | 729 | 783 | 710 | 729 | 783 | 710 | 729 | 783 | 710 | 729 | 783 | 710 | 729 | 783 | 710
CA | 40000983 | 6026 | From T27 to THSS | 6026_Moura - Theodore 66 kV | Time | 16:30 | 17:30 | 22:30 | 16:30 | 17:30 | 22:30 | 16:30 | 17:30 | 22:30 | 16:30 | 17:30 | 22:30 | 16:30 | 17:30 | 22:30
CA | 40000983 | 6026 | From T27 to THSS | 6026_Moura - Theodore 66 kV | Voltage at Constrained Conductor | 66.9181 | 65.8427 | 66.3447 | 66.9355 | 65.8614 | 66.3604 | 66.9603 | 65.8869 | 66.3814 | 66.9602 | 65.8868 | 66.3814 | 66.9349 | 65.8608 | 66.3602
CA | 40000986 | 6056 | From EMSS to CMSS | 6056_Comet - Emerald 66 kV | % of Rated A | 51.9599 | 49.7091 | 37.6004 | 51.6269 | 49.3685 | 37.4113 | 52.7903 | 50.6377 | 37.9652 | 52.9189 | 50.7637 | 38.0387 | 53.5313 | 51.3921 | 38.3641
CA | 40000986 | 6056 | From EMSS to CMSS | 6056_Comet - Emerald 66 kV | Limiting Line Name | TR_LINE 22146_1 | TR_LINE 22146_1 | TR_LINE 22146_1 | TR_LINE 22146_1 | TR_LINE 22146_1 | TR_LINE 22146_1 | TR_LINE 22146_1 | TR_LINE 22146_1 | TR_LINE 22146_1 | TR_LINE 22146_1 | TR_LINE 22146_1 | TR_LINE 22146_1 | TR_LINE 22146_1 | TR_LINE 22146_1 | TR_LINE 22146_1
CA | 40000986 | 6056 | From EMSS to CMSS | 6056_Comet - Emerald 66 kV | Loading (A) | 143.9289 | 146.6418 | 98.8891 | 143.0065 | 145.6371 | 98.3917 | 146.2291 | 149.3811 | 99.8485 | 146.5853 | 149.753 | 100.0417 | 148.2817 | 151.6067 | 100.8976
CA | 40000986 | 6056 | From EMSS to CMSS | 6056_Comet - Emerald 66 kV | Loading (MVA) | 17.0866 | 17.3189 | 11.8697 | 16.9891 | 17.2133 | 11.8152 | 17.3463 | 17.6373 | 12.0231 | 17.3863 | 17.6787 | 12.0456 | 17.5753 | 17.8842 | 12.1445
CA | 40000986 | 6056 | From EMSS to CMSS | 6056_Comet - Emerald 66 kV | Loading (MW) | 15.3544 | 15.9868 | 9.561 | 15.2383 | 15.8652 | 9.4953 | 15.6886 | 16.3121 | 9.186 | 15.7368 | 16.361 | 9.2165 | 15.968 | 16.6044 | 9.356
CA | 40000986 | 6056 | From EMSS to CMSS | 6056_Comet - Emerald 66 kV | Power Factor | 0.89862 | 0.92308 | 0.80549 | 0.89694 | 0.92169 | 0.80365 | 0.90443 | 0.92486 | 0.76403 | 0.90513 | 0.92547 | 0.76514 | 0.90855 | 0.92844 | 0.77039
CA | 40000986 | 6056 | From EMSS to CMSS | 6056_Comet - Emerald 66 kV | Rating (A) | 277 | 295 | 263 | 277 | 295 | 263 | 277 | 295 | 263 | 277 | 295 | 263 | 277 | 295 | 263
CA | 40000986 | 6056 | From EMSS to CMSS | 6056_Comet - Emerald 66 kV | Time | 16:30 | 18:00 | 8:00 | 16:30 | 18:00 | 8:00 | 16:30 | 18:00 | 8:00 | 16:30 | 18:00 | 8:00 | 16:30 | 18:00 | 8:00
CA | 40000986 | 6056 | From EMSS to CMSS | 6056_Comet - Emerald 66 kV | Voltage at Constrained Conductor | 68.5403 | 68.1872 | 69.2998 | 68.589 | 68.2388 | 69.33 | 68.4877 | 68.1673 | 69.5208 | 68.4786 | 68.1576 | 69.5162 | 68.4313 | 68.1069 | 69.4926
CA | 40000987 | 6065 | From H15 to TMSS | 6065_Lilyvale - Tieri Tee 66 kV | % of Rated A | 44.69 | 39.4898 | 34.7674 | 44.3035 | 39.1465 | 34.5326 | 44.3169 | 39.1592 | 34.538 | 44.3184 | 39.1606 | 34.5386 | 44.7071 | 39.5033 | 34.7737
CA | 40000987 | 6065 | From H15 to TMSS | 6065_Lilyvale - Tieri Tee 66 kV | Limiting Line Name | TR_LINE 155365_2 | TR_LINE 155365_2 | TR_LINE 155365_2 | TR_LINE 155365_2 | TR_LINE 155365_2 | TR_LINE 155365_2 | TR_LINE 155365_2 | TR_LINE 155365_2 | TR_LINE 155365_2 | TR_LINE 155365_2 | TR_LINE 155365_2 | TR_LINE 155365_2 | TR_LINE 155365_2 | TR_LINE 155365_2 | TR_LINE 155365_2
CA | 40000987 | 6065 | From H15 to TMSS | 6065_Lilyvale - Tieri Tee 66 kV | Loading (A) | 108.4338 | 107.2514 | 86.0621 | 107.4952 | 106.3179 | 85.4799 | 107.5277 | 106.3525 | 85.4934 | 107.5314 | 106.3564 | 85.4948 | 108.4754 | 107.2883 | 86.0778
CA | 40000987 | 6065 | From H15 to TMSS | 6065_Lilyvale - Tieri Tee 66 kV | Loading (MVA) | 12.9225 | 12.8134 | 10.2187 | 12.8126 | 12.7039 | 10.1504 | 12.813 | 12.7043 | 10.1506 | 12.813 | 12.7044 | 10.1506 | 12.9231 | 12.8132 | 10.2189
CA | 40000987 | 6065 | From H15 to TMSS | 6065_Lilyvale - Tieri Tee 66 kV | Loading (MW) | 12.6701 | 12.5706 | 10.0254 | 12.5638 | 12.4647 | 9.9588 | 12.564 | 12.4649 | 9.9589 | 12.564 | 12.4649 | 9.9589 | 12.6704 | 12.5707 | 10.0255
CA | 40000987 | 6065 | From H15 to TMSS | 6065_Lilyvale - Tieri Tee 66 kV | Power Factor | 0.98047 | 0.98105 | 0.98108 | 0.98058 | 0.98117 | 0.98112 | 0.98057 | 0.98115 | 0.98112 | 0.98057 | 0.98115 | 0.98111 | 0.98045 | 0.98108 | 0.98107
CA | 40000987 | 6065 | From H15 to TMSS | 6065_Lilyvale - Tieri Tee 66 kV | Rating (A) | 243 | 272 | 248 | 243 | 272 | 248 | 243 | 272 | 248 | 243 | 272 | 248 | 243 | 272 | 248
CA | 40000987 | 6065 | From H15 to TMSS | 6065_Lilyvale - Tieri Tee 66 kV | Time | 16:00 | 18:30 | 22:00 | 16:00 | 18:30 | 22:00 | 16:00 | 18:30 | 22:00 | 16:00 | 18:30 | 22:00 | 16:00 | 18:30 | 22:00
CA | 40000987 | 6065 | From H15 to TMSS | 6065_Lilyvale - Tieri Tee 66 kV | Voltage at Constrained Conductor | 68.8054 | 68.9765 | 68.5524 | 68.8156 | 68.9874 | 68.5582 | 68.797 | 68.9674 | 68.5485 | 68.7949 | 68.9652 | 68.5474 | 68.7819 | 68.9518 | 68.5412
CA | 40000988 | 6067 | Emerald | 6067 Lilyvale - Emerald 66 kV | % of Rated A | 61.1053 | 48.3842 | 36.4755 | 60.6567 | 48.0095 | 36.274 | 62.3471 | 49.3341 | 36.9908 | 62.475 | 49.4424 | 37.0496 | 63.1431 | 50.0049 | 37.3466
CA | 40000988 | 6067 | Emerald | 6067 Lilyvale - Emerald 66 kV | Limiting Line Name | TR_LINE 17480_1 | TR_LINE 17480_1 | TR_LINE 17480_1 | TR_LINE 17480_1 | TR_LINE 17480_1 | TR_LINE 17480_1 | TR_LINE 17480_1 | TR_LINE 17480_1 | TR_LINE 17480_1 | TR_LINE 17480_1 | TR_LINE 17480_1 | TR_LINE 17480_1 | TR_LINE 17480_1 | TR_LINE 17480_1 | TR_LINE 17480_1
CA | 40000988 | 6067 | Emerald | 6067 Lilyvale - Emerald 66 kV | Loading (A) | 208.3691 | 218.213 | 157.574 | 206.8395 | 216.5229 | 156.7037 | 212.6037 | 222.4968 | 159.8002 | 213.0396 | 222.9852 | 160.0542 | 215.318 | 225.522 | 161.3372
CA | 40000988 | 6067 | Emerald | 6067 Lilyvale - Emerald 66 kV | Loading (MVA) | 24.7823 | 26.3201 | 18.72 | 24.604 | 26.1202 | 18.6181 | 25.2858 | 26.8327 | 18.9833 | 25.3369 | 26.8906 | 19.0132 | 25.6032 | 27.1915 | 19.164
CA | 40000988 | 6067 | Emerald | 6067 Lilyvale - Emerald 66 kV | Loading (MW) | 24.6573 | 26.2717 | 17.4648 | 24.4657 | 26.0629 | 17.329 | 25.167 | 26.7994 | 17.7846 | 25.2214 | 26.8592 | 17.8224 | 25.5036 | 27.1687 | 18.0125
CA | 40000988 | 6067 | Emerald | 6067 Lilyvale - Emerald 66 kV | Power Factor | 0.99496 | 0.99816 | 0.93295 | 0.99438 | 0.99781 | 0.93076 | 0.9953 | 0.99876 | 0.93686 | 0.99544 | 0.99883 | 0.93737 | 0.99611 | 0.99916 | 0.93992
CA | 40000988 | 6067 | Emerald | 6067 Lilyvale - Emerald 66 kV | Rating (A) | 341 | 451 | 432 | 341 | 451 | 432 | 341 | 451 | 432 | 341 | 451 | 432 | 341 | 451 | 432
CA | 40000988 | 6067 | Emerald | 6067 Lilyvale - Emerald 66 kV | Time | 15:30 | 17:30 | 22:00 | 15:30 | 17:30 | 22:00 | 15:30 | 17:30 | 22:00 | 15:30 | 17:30 | 22:00 | 15:30 | 17:30 | 22:00
CA | 40000988 | 6067 | Emerald | 6067 Lilyvale - Emerald 66 kV | Voltage at Constrained Conductor | 68.6668 | 69.6381 | 68.59 | 68.6769 | 69.6485 | 68.5955 | 68.6666 | 69.6273 | 68.5858 | 68.6645 | 69.6249 | 68.5847 | 68.652 | 69.6119 | 68.5788
CA | 40000997 | 7153 | Lilyvale - Clermont 132 kV | 7153_Lilyvale - Clermont 132 kV | % of Rated A | 25.6426 | 24.9704 | 23.1799 | 25.5407 | 24.8782 | 23.1455 | 25.4492 | 24.7857 | 23.0737 | 25.494 | 24.833 | 23.0988 | 25.6259 | 24.9556 | 23.2104
CA | 40000997 | 7153 | Lilyvale - Clermont 132 kV | 7153_Lilyvale - Clermont 132 kV | Limiting Line Name | TR_LINE 52800_1 | TR_LINE 52800_1 | TR_LINE 52800_1 | TR_LINE 52800_1 | TR_LINE 52800_1 | TR_LINE 52800_1 | TR_LINE 52800_1 | TR_LINE 52800_1 | TR_LINE 52800_1 | TR_LINE 52800_1 | TR_LINE 52800_1 | TR_LINE 52800_1 | TR_LINE 52800_1 | TR_LINE 52800_1 | TR_LINE 52800_1
CA | 40000997 | 7153 | Lilyvale - Clermont 132 kV | 7153_Lilyvale - Clermont 132 kV | Loading (A) | 181.5498 | 180.7859 | 147.6561 | 180.828 | 180.1178 | 147.4369 | 180.1805 | 179.4481 | 146.9794 | 180.4976 | 179.791 | 147.1395 | 181.4312 | 180.6786 | 147.8504
CA | 40000997 | 7153 | Lilyvale - Clermont 132 kV | 7153_Lilyvale - Clermont 132 kV | Loading (MVA) | 44.2017 | 43.9872 | 35.9799 | 44.0276 | 43.8265 | 35.9273 | 43.8687 | 43.6621 | 35.8155 | 43.9455 | 43.7452 | 35.8544 | 44.1708 | 43.9592 | 36.0269
CA | 40000997 | 7153 | Lilyvale - Clermont 132 kV | 7153_Lilyvale - Clermont 132 kV | Loading (MW) | 42.4187 | 42.0889 | 30.988 | 42.1838 | 41.8514 | 30.8496 | 41.9731 | 41.6331 | 30.7238 | 42.0625 | 41.7307 | 30.7755 | 42.3615 | 42.0155 | 31.0052
CA | 40000997 | 7153 | Lilyvale - Clermont 132 kV | 7153_Lilyvale - Clermont 132 kV | Power Factor | 0.95966 | 0.95684 | 0.86126 | 0.95812 | 0.95493 | 0.85867 | 0.95679 | 0.95353 | 0.85784 | 0.95715 | 0.95395 | 0.85835 | 0.95904 | 0.95578 | 0.86061
CA | 40000997 | 7153 | Lilyvale - Clermont 132 kV | 7153_Lilyvale - Clermont 132 kV | Rating (A) | 708 | 724 | 637 | 708 | 724 | 637 | 708 | 724 | 637 | 708 | 724 | 637 | 708 | 724 | 637
CA | 40000997 | 7153 | Lilyvale - Clermont 132 kV | 7153_Lilyvale - Clermont 132 kV | Time | 16:00 | 17:00 | 8:30 | 16:00 | 17:00 | 8:30 | 16:00 | 17:00 | 8:30 | 16:00 | 17:00 | 8:30 | 16:00 | 17:00 | 8:30
CA | 40000997 | 7153 | Lilyvale - Clermont 132 kV | 7153_Lilyvale - Clermont 132 kV | Voltage at Constrained Conductor | 140.5667 | 140.4758 | 140.6851 | 140.5718 | 140.4815 | 140.6883 | 140.5678 | 140.4771 | 140.6871 | 140.5668 | 140.4759 | 140.6865 | 140.5604 | 140.4695 | 140.6836
CA | 40001012 | 6011 | From T32 to CMSS | 6011_Blackwater - Comet 66 kV | % of Rated A | 57.7784 | 55.7512 | 41.879 | 57.2374 | 55.1939 | 41.5459 | 58.4918 | 56.5024 | 41.7639 | 58.6289 | 56.6364 | 41.8457 | 59.2835 | 57.3043 | 42.2111
CA | 40001012 | 6011 | From T32 to CMSS | 6011_Blackwater - Comet 66 kV | Limiting Line Name | TR_LINE 22148_1 | TR_LINE 22148_1 | TR_LINE 22148_1 | TR_LINE 22148_1 | TR_LINE 22148_1 | TR_LINE 22148_1 | TR_LINE 22148_1 | TR_LINE 22148_1 | TR_LINE 22148_1 | TR_LINE 22148_1 | TR_LINE 22148_1 | TR_LINE 22148_1 | TR_LINE 22148_1 | TR_LINE 22148_1 | TR_LINE 22148_1
CA | 40001012 | 6011 | From T32 to CMSS | 6011_Blackwater - Comet 66 kV | Loading (A) | 160.0462 | 164.4661 | 110.1419 | 158.5475 | 162.822 | 109.2658 | 162.0223 | 166.6821 | 109.839 | 162.402 | 167.0774 | 110.0541 | 164.2153 | 169.0477 | 111.0152
CA | 40001012 | 6011 | From T32 to CMSS | 6011_Blackwater - Comet 66 kV | Loading (MVA) | 19.3428 | 19.8568 | 13.2958 | 19.1636 | 19.6604 | 13.1909 | 19.5794 | 20.1231 | 13.2627 | 19.6252 | 20.1707 | 13.2886 | 19.843 | 20.4072 | 13.4043
CA | 40001012 | 6011 | From T32 to CMSS | 6011_Blackwater - Comet 66 kV | Loading (MW) | 18.5464 | 19.3345 | 11.9439 | 18.3334 | 19.1105 | 11.8041 | 18.8135 | 19.5912 | 11.4975 | 18.865 | 19.6437 | 11.5292 | 19.112 | 19.9048 | 11.6745
CA | 40001012 | 6011 | From T32 to CMSS | 6011_Blackwater - Comet 66 kV | Power Factor | 0.95882 | 0.9737 | 0.89832 | 0.95668 | 0.97203 | 0.89487 | 0.96088 | 0.97357 | 0.8669 | 0.96126 | 0.97387 | 0.8676 | 0.96316 | 0.97538 | 0.87095
CA | 40001012 | 6011 | From T32 to CMSS | 6011_Blackwater - Comet 66 kV | Rating (A) | 277 | 295 | 263 | 277 | 295 | 263 | 277 | 295 | 263 | 277 | 295 | 263 | 277 | 295 | 263
CA | 40001012 | 6011 | From T32 to CMSS | 6011_Blackwater - Comet 66 kV | Time | 16:30 | 18:00 | 8:00 | 16:30 | 18:00 | 8:00 | 16:30 | 18:00 | 8:00 | 16:30 | 18:00 | 8:00 | 16:30 | 18:00 | 8:00
CA | 40001012 | 6011 | From T32 to CMSS | 6011_Blackwater - Comet 66 kV | Voltage at Constrained Conductor | 69.7772 | 69.7065 | 69.6949 | 69.7843 | 69.7138 | 69.6995 | 69.7693 | 69.7021 | 69.7131 | 69.7689 | 69.7016 | 69.7129 | 69.7644 | 69.6968 | 69.7107
CA | 40001013 | 6012 | From T32 to BFSS | 6012_Blackwater - Bedford Weir 66 kV | % of Rated A | 36.8014 | 37.5664 | 33.5522 | 36.4807 | 37.2456 | 33.2883 | 36.5024 | 37.2714 | 33.3009 | 36.5026 | 37.2717 | 33.301 | 36.8072 | 37.5746 | 33.5534
CA | 40001013 | 6012 | From T32 to BFSS | 6012_Blackwater - Bedford Weir 66 kV | Limiting Line Name | TR_LINE 22155_1 | TR_LINE 22155_1 | TR_LINE 22155_1 | TR_LINE 22155_1 | TR_LINE 22155_1 | TR_LINE 22155_1 | TR_LINE 22155_1 | TR_LINE 22155_1 | TR_LINE 22155_1 | TR_LINE 22155_1 | TR_LINE 22155_1 | TR_LINE 22155_1 | TR_LINE 22155_1 | TR_LINE 22155_1 | TR_LINE 22155_1
CA | 40001013 | 6012 | From T32 to BFSS | 6012_Blackwater - Bedford Weir 66 kV | Loading (A) | 102.3034 | 111.1919 | 88.5733 | 101.4119 | 110.2425 | 87.8769 | 101.4722 | 110.3188 | 87.9101 | 101.4727 | 110.3196 | 87.9103 | 102.3196 | 111.2162 | 88.5765
CA | 40001013 | 6012 | From T32 to BFSS | 6012_Blackwater - Bedford Weir 66 kV | Loading (MVA) | 12.1053 | 13.1379 | 10.5168 | 12.0043 | 13.031 | 10.4371 | 12.0079 | 13.0354 | 10.4394 | 12.0079 | 13.0354 | 10.4394 | 12.1054 | 13.1381 | 10.5168
CA | 40001013 | 6012 | From T32 to BFSS | 6012_Blackwater - Bedford Weir 66 kV | Loading (MW) | 11.478 | 12.4312 | 9.9957 | 11.4103 | 12.3599 | 9.9417 | 11.3864 | 12.3348 | 9.9226 | 11.3864 | 12.3348 | 9.9226 | 11.4781 | 12.4312 | 9.9957
CA | 40001013 | 6012 | From T32 to BFSS | 6012_Blackwater - Bedford Weir 66 kV | Power Factor | 0.94818 | 0.9462 | 0.95045 | 0.95052 | 0.9485 | 0.95253 | 0.94824 | 0.94626 | 0.9505 | 0.94824 | 0.94625 | 0.9505 | 0.94817 | 0.94619 | 0.95045
CA | 40001013 | 6012 | From T32 to BFSS | 6012_Blackwater - Bedford Weir 66 kV | Rating (A) | 278 | 296 | 264 | 278 | 296 | 264 | 278 | 296 | 264 | 278 | 296 | 264 | 278 | 296 | 264
CA | 40001013 | 6012 | From T32 to BFSS | 6012_Blackwater - Bedford Weir 66 kV | Time | 13:30 | 18:30 | 22:30 | 13:30 | 18:30 | 22:30 | 13:30 | 18:30 | 22:30 | 13:30 | 18:30 | 22:30 | 13:30 | 18:30 | 22:30
CA | 40001013 | 6012 | From T32 to BFSS | 6012_Blackwater - Bedford Weir 66 kV | Voltage at Constrained Conductor | 68.3165 | 68.2171 | 68.552 | 68.3421 | 68.2447 | 68.5719 | 68.3216 | 68.2204 | 68.5609 | 68.3213 | 68.2199 | 68.5608 | 68.3064 | 68.2032 | 68.5498
CA | 40001019 | 6058 | From BFSS to BGSS | 6058_Bedford Weir - Bingegang 66 kV | % of Rated A | 13.1468 | 13.4174 | 13.4673 | 13.1418 | 13.4114 | 13.4634 | 13.1456 | 13.5377 | 13.4662 | 13.1457 | 13.5378 | 13.4663 | 13.1485 | 13.5414 | 13.4684
CA | 40001019 | 6058 | From BFSS to BGSS | 6058_Bedford Weir - Bingegang 66 kV | Limiting Line Name | TR_LINE 99926_1 | TR_LINE 99926_1 | TR_LINE 99926_1 | TR_LINE 99926_1 | TR_LINE 99926_1 | TR_LINE 99926_1 | TR_LINE 99926_1 | TR_LINE 99926_1 | TR_LINE 99926_1 | TR_LINE 99926_1 | TR_LINE 99926_1 | TR_LINE 99926_1 | TR_LINE 99926_1 | TR_LINE 99926_1 | TR_LINE 99926_1
CA | 40001019 | 6058 | From BFSS to BGSS | 6058_Bedford Weir - Bingegang 66 kV | Loading (A) | 36.5481 | 39.7156 | 35.5537 | 36.5343 | 39.6977 | 35.5435 | 36.5449 | 40.0715 | 35.5508 | 36.545 | 40.0718 | 35.5509 | 36.5529 | 40.0824 | 35.5565
CA | 40001019 | 6058 | From BFSS to BGSS | 6058_Bedford Weir - Bingegang 66 kV | Loading (MVA) | 4.2807 | 4.6357 | 4.1825 | 4.2805 | 4.6355 | 4.1824 | 4.2806 | 4.6151 | 4.1825 | 4.2806 | 4.6151 | 4.1825 | 4.2807 | 4.6152 | 4.1825
CA | 40001019 | 6058 | From BFSS to BGSS | 6058_Bedford Weir - Bingegang 66 kV | Loading (MW) | 3.8515 | 4.2271 | 3.8198 | 3.8515 | 4.2271 | 3.8198 | 3.8515 | 4.207 | 3.8198 | 3.8515 | 4.207 | 3.8198 | 3.8515 | 4.207 | 3.8198
CA | 40001019 | 6058 | From BFSS to BGSS | 6058_Bedford Weir - Bingegang 66 kV | Power Factor | 0.89975 | 0.91187 | 0.91328 | 0.89977 | 0.9119 | 0.9133 | 0.89975 | 0.91157 | 0.91329 | 0.89975 | 0.91157 | 0.91329 | 0.89974 | 0.91155 | 0.91328
CA | 40001019 | 6058 | From BFSS to BGSS | 6058_Bedford Weir - Bingegang 66 kV | Rating (A) | 278 | 296 | 264 | 278 | 296 | 264 | 278 | 296 | 264 | 278 | 296 | 264 | 278 | 296 | 264
CA | 40001019 | 6058 | From BFSS to BGSS | 6058_Bedford Weir - Bingegang 66 kV | Time | 11:00 | 18:30 | 23:30 | 11:00 | 18:30 | 23:30 | 11:00 | 19:00 | 23:30 | 11:00 | 19:00 | 23:30 | 11:00 | 19:00 | 23:30
CA | 40001019 | 6058 | From BFSS to BGSS | 6058_Bedford Weir - Bingegang 66 kV | Voltage at Constrained Conductor | 67.6217 | 67.389 | 67.919 | 67.6452 | 67.4173 | 67.937 | 67.6272 | 66.4947 | 67.924 | 67.627 | 66.4943 | 67.9239 | 67.6136 | 66.4779 | 67.9141
CA | 40001027 | 6085 | From TMSS to TISS | 6085_Tieri Tee - Tieri 66 kV | % of Rated A | 6.7481 | 6.2259 | 4.4135 | 6.7467 | 6.2246 | 4.4129 | 6.7485 | 6.2257 | 4.4135 | 6.7487 | 6.2259 | 4.4136 | 6.7505 | 6.2276 | 4.4142
CA | 40001027 | 6085 | From TMSS to TISS | 6085_Tieri Tee - Tieri 66 kV | Limiting Line Name | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1
CA | 40001027 | 6085 | From TMSS to TISS | 6085_Tieri Tee - Tieri 66 kV | Loading (A) | 16.3979 | 16.9344 | 10.9454 | 16.3944 | 16.9308 | 10.944 | 16.3989 | 16.9339 | 10.9456 | 16.3994 | 16.9345 | 10.9458 | 16.4036 | 16.939 | 10.9472
CA | 40001027 | 6085 | From TMSS to TISS | 6085_Tieri Tee - Tieri 66 kV | Loading (MVA) | 1.9388 | 2.004 | 1.2916 | 1.9388 | 2.004 | 1.2916 | 1.9388 | 2.004 | 1.2916 | 1.9388 | 2.004 | 1.2916 | 1.9388 | 2.004 | 1.2916
CA | 40001027 | 6085 | From TMSS to TISS | 6085_Tieri Tee - Tieri 66 kV | Loading (MW) | 1.9291 | 1.994 | 1.2859 | 1.9291 | 1.994 | 1.2859 | 1.9291 | 1.994 | 1.2859 | 1.9291 | 1.994 | 1.2859 | 1.9291 | 1.994 | 1.2859
CA | 40001027 | 6085 | From TMSS to TISS | 6085_Tieri Tee - Tieri 66 kV | Power Factor | 0.99503 | 0.99499 | 0.99554 | 0.99503 | 0.99499 | 0.99554 | 0.99503 | 0.99499 | 0.99554 | 0.99503 | 0.99499 | 0.99554 | 0.99503 | 0.99499 | 0.99554
CA | 40001027 | 6085 | From TMSS to TISS | 6085_Tieri Tee - Tieri 66 kV | Rating (A) | 243 | 272 | 248 | 243 | 272 | 248 | 243 | 272 | 248 | 243 | 272 | 248 | 243 | 272 | 248
CA | 40001027 | 6085 | From TMSS to TISS | 6085_Tieri Tee - Tieri 66 kV | Time | 16:00 | 18:00 | 22:00 | 16:00 | 18:00 | 22:00 | 16:00 | 18:00 | 22:00 | 16:00 | 18:00 | 22:00 | 16:00 | 18:00 | 22:00
CA | 40001027 | 6085 | From TMSS to TISS | 6085_Tieri Tee - Tieri 66 kV | Voltage at Constrained Conductor | 68.2613 | 68.3244 | 68.1318 | 68.2758 | 68.3387 | 68.1401 | 68.2571 | 68.3263 | 68.1303 | 68.255 | 68.324 | 68.1293 | 68.2376 | 68.306 | 68.1205
CA | 40001028 | 6086 | From TMSS to MDSS | 6086_Tieri Tee - Middlemount 66 kV | % of Rated A | 38.5606 | 35.9314 | 31.001 | 38.1758 | 35.5693 | 30.7618 | 38.1873 | 35.5809 | 30.7631 | 38.1887 | 35.5822 | 30.7637 | 38.5754 | 35.9428 | 31.0032
CA | 40001028 | 6086 | From TMSS to MDSS | 6086_Tieri Tee - Middlemount 66 kV | Limiting Line Name | TR_LINE 17095_1 | TR_CABLE 10487_1 | TR_LINE 17095_1 | TR_LINE 17095_1 | TR_CABLE 10487_1 | TR_LINE 17095_1 | TR_LINE 17095_1 | TR_CABLE 10487_1 | TR_LINE 17095_1 | TR_LINE 17095_1 | TR_CABLE 10487_1 | TR_LINE 17095_1 | TR_LINE 17095_1 | TR_CABLE 10487_1 | TR_LINE 17095_1
CA | 40001028 | 6086 | From TMSS to MDSS | 6086_Tieri Tee - Middlemount 66 kV | Loading (A) | 93.433 | 92.3437 | 76.5979 | 92.4972 | 91.4131 | 76.0039 | 92.5253 | 91.443 | 76.0073 | 92.5285 | 91.4463 | 76.0086 | 93.4689 | 92.3729 | 76.6034
CA | 40001028 | 6086 | From TMSS to MDSS | 6086_Tieri Tee - Middlemount 66 kV | Loading (MVA) | 10.8255 | 10.731 | 8.9455 | 10.7217 | 10.6275 | 8.8785 | 10.7219 | 10.6277 | 8.8785 | 10.7219 | 10.6277 | 8.8785 | 10.8257 | 10.7303 | 8.9456
CA | 40001028 | 6086 | From TMSS to MDSS | 6086_Tieri Tee - Middlemount 66 kV | Loading (MW) | 10.4907 | 10.4048 | 8.6463 | 10.3891 | 10.3035 | 8.5801 | 10.3891 | 10.3036 | 8.5801 | 10.3892 | 10.3036 | 8.5801 | 10.4908 | 10.4047 | 8.6463
CA | 40001028 | 6086 | From TMSS to MDSS | 6086_Tieri Tee - Middlemount 66 kV | Power Factor | 0.96907 | 0.96961 | 0.96655 | 0.96898 | 0.96951 | 0.96639 | 0.96897 | 0.9695 | 0.96639 | 0.96897 | 0.9695 | 0.96639 | 0.96906 | 0.96966 | 0.96655
CA | 40001028 | 6086 | From TMSS to MDSS | 6086_Tieri Tee - Middlemount 66 kV | Rating (A) | 243 | 257 | 248 | 243 | 257 | 248 | 243 | 257 | 248 | 243 | 257 | 248 | 243 | 257 | 248
CA | 40001028 | 6086 | From TMSS to MDSS | 6086_Tieri Tee - Middlemount 66 kV | Time | 16:00 | 18:30 | 8:30 | 16:00 | 18:30 | 8:30 | 16:00 | 18:30 | 8:30 | 16:00 | 18:30 | 8:30 | 16:00 | 18:30 | 8:30
CA | 40001028 | 6086 | From TMSS to MDSS | 6086_Tieri Tee - Middlemount 66 kV | Voltage at Constrained Conductor | 66.8939 | 67.0919 | 67.4261 | 66.9229 | 67.1216 | 67.4436 | 66.9037 | 67.1009 | 67.4408 | 66.9015 | 67.0985 | 67.4397 | 66.8695 | 67.0669 | 67.4215
CA | 40001036 | 6019 | From GFSS to T19 | 6019_Gladstone South - Friend St 66 kV | % of Rated A | 32.3369 | 18.7986 | 26.7834 | 33.1612 | 18.7887 | 12.0107 | 33.0748 | 18.9329 | 11.9029 | 32.8653 | 19.329 | 12.2235 | 31.7456 | 20.0701 | 27.3726
CA | 40001036 | 6019 | From GFSS to T19 | 6019_Gladstone South - Friend St 66 kV | Limiting Line Name | TR_LINE 22252_1 | TR_LINE 21764_1 | TR_LINE 22252_1 | TR_LINE 22252_1 | TR_LINE 21764_1 | TR_LINE 21764_1 | TR_LINE 22252_1 | TR_LINE 21764_1 | TR_LINE 22252_1 | TR_LINE 22252_1 | TR_LINE 21764_1 | TR_LINE 22252_1 | TR_LINE 22252_1 | TR_LINE 21764_1 | TR_LINE 22252_1
CA | 40001036 | 6019 | From GFSS to T19 | 6019_Gladstone South - Friend St 66 kV | Loading (A) | 79.2253 | 64.2914 | 76.3327 | 81.2449 | 64.2575 | 34.2306 | 81.0333 | 64.7505 | 33.9227 | 80.52 | 66.1053 | 34.8367 | 77.7767 | 68.6397 | 78.012
CA | 40001036 | 6019 | From GFSS to T19 | 6019_Gladstone South - Friend St 66 kV | Loading (MVA) | 9.353 | 7.6245 | 9.0072 | 9.5945 | 7.6264 | 4.0687 | 9.5693 | 7.6841 | 4.009 | 9.5073 | 7.8454 | 4.1173 | 9.1788 | 8.1399 | 9.204
CA | 40001036 | 6019 | From GFSS to T19 | 6019_Gladstone South - Friend St 66 kV | Loading (MW) | 4.7914 | 5.4047 | 1.4816 | 4.4994 | 5.8132 | 3.9671 | 4.329 | 5.9719 | 4.0063 | 4.2347 | 6.1323 | 4.1162 | 4.2127 | 6.338 | 2.0011
CA | 40001036 | 6019 | From GFSS to T19 | 6019_Gladstone South - Friend St 66 kV | Power Factor | 0.51229 | 0.70886 | 0.16449 | 0.46896 | 0.76225 | 0.97502 | 0.45238 | 0.77718 | 0.99933 | 0.44542 | 0.78164 | 0.99973 | 0.45896 | 0.77864 | 0.21742
CA | 40001036 | 6019 | From GFSS to T19 | 6019_Gladstone South - Friend St 66 kV | Rating (A) | 245 | 342 | 285 | 245 | 342 | 285 | 245 | 342 | 285 | 245 | 342 | 285 | 245 | 342 | 285
CA | 40001036 | 6019 | From GFSS to T19 | 6019_Gladstone South - Friend St 66 kV | Time | 11:00 | 19:00 | 7:00 | 11:00 | 19:30 | 8:30 | 11:00 | 19:30 | 22:30 | 11:00 | 19:30 | 22:30 | 11:00 | 19:30 | 7:00
CA | 40001036 | 6019 | From GFSS to T19 | 6019_Gladstone South - Friend St 66 kV | Voltage at Constrained Conductor | 68.1595 | 68.4701 | 68.1269 | 68.1813 | 68.5227 | 68.625 | 68.1799 | 68.5158 | 68.2317 | 68.1701 | 68.5201 | 68.236 | 68.1359 | 68.4669 | 68.117
CA | 40001047 | 6020 | GLSO - BORT 6020 | 6020_Gladstone South - BORE 66 kV | % of Rated A | 53.6956 | 48.891 | 42.5753 | 56.0909 | 50.457 | 43.8091 | 56.0312 | 50.4673 | 43.8026 | 56.438 | 50.7514 | 44.0547 | 56.6921 | 51.5699 | 44.7212
CA | 40001047 | 6020 | GLSO - BORT 6020 | 6020_Gladstone South - BORE 66 kV | Limiting Line Name | TR_LINE 215688_1 | TR_LINE 215688_1 | TR_LINE 215688_1 | TR_LINE 215688_1 | TR_LINE 215688_1 | TR_LINE 215688_1 | TR_LINE 215688_1 | TR_LINE 215688_1 | TR_LINE 215688_1 | TR_LINE 215688_1 | TR_LINE 215688_1 | TR_LINE 215688_1 | TR_LINE 215688_1 | TR_LINE 215688_1 | TR_LINE 215688_1
CA | 40001047 | 6020 | GLSO - BORT 6020 | 6020_Gladstone South - BORE 66 kV | Loading (A) | 113.2946 | 144.2216 | 104.3053 | 118.3477 | 148.8409 | 107.3274 | 118.2206 | 148.8703 | 107.3106 | 119.0801 | 149.7093 | 107.929 | 119.6149 | 152.1228 | 109.5612
CA | 40001047 | 6020 | GLSO - BORT 6020 | 6020_Gladstone South - BORE 66 kV | Loading (MVA) | 13.2925 | 16.9699 | 12.2543 | 13.8821 | 17.5108 | 12.6087 | 13.8641 | 17.51 | 12.6045 | 13.9671 | 17.6111 | 12.6761 | 14.1444 | 17.8721 | 12.8583
CA | 40001047 | 6020 | GLSO - BORT 6020 | 6020_Gladstone South - BORE 66 kV | Loading (MW) | 13.2832 | 16.9184 | 12.2393 | 13.8661 | 17.4482 | 12.5891 | 13.8382 | 17.4311 | 12.5775 | 13.9506 | 17.5475 | 12.656 | 14.1179 | 17.7875 | 12.8286
CA | 40001047 | 6020 | GLSO - BORT 6020 | 6020_Gladstone South - BORE 66 kV | Power Factor | 0.99931 | 0.99696 | 0.99877 | 0.99884 | 0.99642 | 0.99844 | 0.99814 | 0.99549 | 0.99785 | 0.99882 | 0.99639 | 0.99842 | 0.99813 | 0.99527 | 0.99769
CA | 40001047 | 6020 | GLSO - BORT 6020 | 6020_Gladstone South - BORE 66 kV | Rating (A) | 211 | 295 | 245 | 211 | 295 | 245 | 211 | 295 | 245 | 211 | 295 | 245 | 211 | 295 | 245
CA | 40001047 | 6020 | GLSO - BORT 6020 | 6020_Gladstone South - BORE 66 kV | Time | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00
CA | 40001047 | 6020 | GLSO - BORT 6020 | 6020_Gladstone South - BORE 66 kV | Voltage at Constrained Conductor | 67.7385 | 67.9343 | 67.83 | 67.7229 | 67.9241 | 67.8266 | 67.7074 | 67.9075 | 67.8147 | 67.7184 | 67.9168 | 67.8088 | 68.2712 | 67.8299 | 67.759
CA | 40001055 | 6079 | From T72 to LRSS | 6079_Barcaldine - Longreach 66 kV | % of Rated A | 80.8588 | 84.8392 | 57.1584 | 79.8038 | 84.1245 | 56.5161 | 78.8066 | 82.6257 | 56.7304 | 78.8173 | 82.6387 | 56.7341 | 79.8794 | 84.1506 | 56.5314
CA | 40001055 | 6079 | From T72 to LRSS | 6079_Barcaldine - Longreach 66 kV | Limiting Line Name | TR_CABLE 562_1 | TR_CABLE 562_1 | TR_CABLE 562_1 | TR_CABLE 562_1 | TR_CABLE 562_1 | TR_CABLE 562_1 | TR_CABLE 562_1 | TR_CABLE 562_1 | TR_CABLE 562_1 | TR_CABLE 562_1 | TR_CABLE 562_1 | TR_CABLE 562_1 | TR_CABLE 562_1 | TR_CABLE 562_1 | TR_CABLE 562_1
CA | 40001055 | 6079 | From T72 to LRSS | 6079_Barcaldine - Longreach 66 kV | Loading (A) | 80.8588 | 84.8392 | 57.1584 | 79.8038 | 84.1245 | 56.5161 | 78.8066 | 82.6257 | 56.7304 | 78.8173 | 82.6387 | 56.7341 | 79.8794 | 84.1506 | 56.5314
CA | 40001055 | 6079 | From T72 to LRSS | 6079_Barcaldine - Longreach 66 kV | Loading (MVA) | 9.6118 | 10.2053 | 6.9161 | 9.5055 | 9.9944 | 6.8457 | 9.4002 | 9.9783 | 6.7733 | 9.4003 | 9.9784 | 6.7733 | 9.5064 | 9.9947 | 6.8457
CA | 40001055 | 6079 | From T72 to LRSS | 6079_Barcaldine - Longreach 66 kV | Loading (MW) | 9.6118 | 10.205 | 6.8606 | 9.5052 | 9.994 | 6.7873 | 9.3995 | 9.9783 | 6.7202 | 9.3996 | 9.9784 | 6.7202 | 9.5061 | 9.9943 | 6.7874
CA | 40001055 | 6079 | From T72 to LRSS | 6079_Barcaldine - Longreach 66 kV | Power Factor | 1 | 0.99996 | 0.99197 | 0.99997 | 0.99996 | 0.99146 | 0.99992 | 1 | 0.99216 | 0.99992 | 1 | 0.99217 | 0.99997 | 0.99996 | 0.99149
CA | 40001055 | 6079 | From T72 to LRSS | 6079_Barcaldine - Longreach 66 kV | Rating (A) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
CA | 40001055 | 6079 | From T72 to LRSS | 6079_Barcaldine - Longreach 66 kV | Time | 16:00 | 18:30 | 22:00 | 16:00 | 18:00 | 22:00 | 16:00 | 18:30 | 22:00 | 16:00 | 18:30 | 22:00 | 16:00 | 18:00 | 22:00
CA | 40001055 | 6079 | From T72 to LRSS | 6079_Barcaldine - Longreach 66 kV | Voltage at Constrained Conductor | 68.6307 | 69.4496 | 69.859 | 68.7688 | 68.5919 | 69.9339 | 68.8675 | 69.7236 | 68.9322 | 68.859 | 69.7137 | 68.9276 | 68.7099 | 68.573 | 69.9145
CA | 40001056 | 7154 | Barcaldine | 7154_Clermont - Barcaldine 132 kV | % of Rated A | 28.2254 | 24.6768 | 26.4177 | 28.1187 | 24.5715 | 26.3852 | 28.0591 | 24.5214 | 26.3034 | 28.0591 | 24.5211 | 26.3036 | 28.1927 | 24.6108 | 26.441
CA | 40001056 | 7154 | Barcaldine | 7154_Clermont - Barcaldine 132 kV | Limiting Line Name | TR_LINE 52329_1 | TR_LINE 52329_1 | TR_LINE 52329_1 | TR_LINE 52329_1 | TR_LINE 52329_1 | TR_LINE 52329_1 | TR_LINE 52329_1 | TR_LINE 52329_1 | TR_LINE 52329_1 | TR_LINE 52329_1 | TR_LINE 52329_1 | TR_LINE 52329_1 | TR_LINE 52329_1 | TR_LINE 52329_1 | TR_LINE 52329_1
CA | 40001056 | 7154 | Barcaldine | 7154_Clermont - Barcaldine 132 kV | Loading (A) | 101.6114 | 96.4863 | 92.7261 | 101.2273 | 96.0744 | 92.612 | 101.0127 | 95.8788 | 92.3248 | 101.0127 | 95.8774 | 92.3258 | 101.4936 | 96.2281 | 92.8079
CA | 40001056 | 7154 | Barcaldine | 7154_Clermont - Barcaldine 132 kV | Loading (MVA) | 24.858 | 23.5247 | 22.9687 | 24.7784 | 23.4373 | 22.9478 | 24.7333 | 23.3972 | 22.8771 | 24.7313 | 23.3944 | 22.8764 | 24.8357 | 23.4678 | 22.9913
CA | 40001056 | 7154 | Barcaldine | 7154_Clermont - Barcaldine 132 kV | Loading (MW) | 21.5093 | 19.7096 | 17.0208 | 21.2926 | 19.4798 | 16.8846 | 21.1812 | 19.3625 | 16.813 | 21.1814 | 19.3628 | 16.8131 | 21.3973 | 19.5441 | 16.9863
CA | 40001056 | 7154 | Barcaldine | 7154_Clermont - Barcaldine 132 kV | Power Factor | 0.86529 | 0.83783 | 0.74104 | 0.85932 | 0.83114 | 0.73579 | 0.85638 | 0.82756 | 0.73493 | 0.85646 | 0.82767 | 0.73495 | 0.86155 | 0.8328 | 0.73881
CA | 40001056 | 7154 | Barcaldine | 7154_Clermont - Barcaldine 132 kV | Rating (A) | 360 | 391 | 351 | 360 | 391 | 351 | 360 | 391 | 351 | 360 | 391 | 351 | 360 | 391 | 351
CA | 40001056 | 7154 | Barcaldine | 7154_Clermont - Barcaldine 132 kV | Time | 14:30 | 17:00 | 8:30 | 14:30 | 17:00 | 8:30 | 14:30 | 17:00 | 8:30 | 14:30 | 17:00 | 8:30 | 14:30 | 17:00 | 8:30
CA | 40001056 | 7154 | Barcaldine | 7154_Clermont - Barcaldine 132 kV | Voltage at Constrained Conductor | 141.2419 | 140.7659 | 143.0124 | 141.324 | 140.8443 | 143.0581 | 141.3664 | 140.8902 | 143.0612 | 141.3547 | 140.8754 | 143.0551 | 141.2789 | 140.8025 | 143.0272
CA | 40001069 | 6077 | Farnborough - Capricorn Resort 66kV | 6077_Farnborough - Capricorn Resort 66kV | % of Rated A | 0.066887 | 0.059848 | 0.076893 | 0.066827 | 0.059877 | 0.076911 | 0.067115 | 0.059849 | 0.076876 | 0.067159 | 0.059982 | 0.076782 | 0.066843 | 0.059869 | 0.076806
CA | 40001069 | 6077 | Farnborough - Capricorn Resort 66kV | 6077_Farnborough - Capricorn Resort 66kV | Limiting Line Name | TR_LINE FARB-FARE | TR_LINE FARB-FARE | TR_LINE FARB-FARE | TR_LINE FARB-FARE | TR_LINE FARB-FARE | TR_LINE FARB-FARE | TR_LINE FARB-FARE | TR_LINE FARB-FARE | TR_LINE FARB-FARE | TR_LINE FARB-FARE | TR_LINE FARB-FARE | TR_LINE FARB-FARE | TR_LINE FARB-FARE | TR_LINE FARB-FARE | TR_LINE FARB-FARE
CA | 40001069 | 6077 | Farnborough - Capricorn Resort 66kV | 6077_Farnborough - Capricorn Resort 66kV | Loading (A) | 0.25417 | 0.25017 | 0.26067 | 0.25394 | 0.25029 | 0.26073 | 0.25504 | 0.25017 | 0.26061 | 0.25521 | 0.25072 | 0.26029 | 0.254 | 0.25025 | 0.26037
CA | 40001069 | 6077 | Farnborough - Capricorn Resort 66kV | 6077_Farnborough - Capricorn Resort 66kV | Loading (MVA) | 0.029229 | 0.028316 | 0.030742 | 0.029177 | 0.028343 | 0.030757 | 0.029429 | 0.028316 | 0.030729 | 0.029468 | 0.028442 | 0.030654 | 0.029191 | 0.028335 | 0.030673
CA | 40001069 | 6077 | Farnborough - Capricorn Resort 66kV | 6077_Farnborough - Capricorn Resort 66kV | Loading (MW) | 4.1329e-08 | 4.0037e-08 | 4.3469e-08 | 4.1255e-08 | 4.0076e-08 | 4.3489e-08 | 4.1611e-08 | 4.0038e-08 | 4.3449e-08 | 4.1666e-08 | 4.0215e-08 | 4.3344e-08 | 4.1274e-08 | 4.0064e-08 | 4.3371e-08
CA | 40001069 | 6077 | Farnborough - Capricorn Resort 66kV | 6077_Farnborough - Capricorn Resort 66kV | Power Factor | 1.414e-06 | 1.414e-06 | 1.414e-06 | 1.414e-06 | 1.414e-06 | 1.414e-06 | 1.414e-06 | 1.4139e-06 | 1.414e-06 | 1.414e-06 | 1.414e-06 | 1.414e-06 | 1.414e-06 | 1.414e-06 | 1.414e-06
CA | 40001069 | 6077 | Farnborough - Capricorn Resort 66kV | 6077_Farnborough - Capricorn Resort 66kV | Rating (A) | 380 | 418 | 339 | 380 | 418 | 339 | 380 | 418 | 339 | 380 | 418 | 339 | 380 | 418 | 339
CA | 40001069 | 6077 | Farnborough - Capricorn Resort 66kV | 6077_Farnborough - Capricorn Resort 66kV | Time | 10:30 | 21:30 | 4:00 | 9:30 | 21:30 | 4:00 | 9:30 | 21:30 | 4:00 | 9:30 | 21:30 | 5:00 | 9:30 | 21:30 | 4:30
CA | 40001069 | 6077 | Farnborough - Capricorn Resort 66kV | 6077_Farnborough - Capricorn Resort 66kV | Voltage at Constrained Conductor | 66.3946 | 65.3485 | 68.0914 | 66.335 | 65.3798 | 68.1074 | 66.6207 | 65.3495 | 68.0763 | 66.6649 | 65.494 | 67.9933 | 66.3509 | 65.3705 | 68.0143
CA | 40001070 | 6023 | From GFSS to CISS | 6023_Friend St-Clinton Industrial 66 kV | % of Rated A | 34.101 | 39.3269 | 35.6722 | 34.9166 | 39.7632 | 36.1689 | 34.8534 | 39.7148 | 36.0841 | 35.2139 | 40.0186 | 36.3571 | 37.3292 | 40.2551 | 36.6505
CA | 40001070 | 6023 | From GFSS to CISS | 6023_Friend St-Clinton Industrial 66 kV | Limiting Line Name | TR_LINE 22275_1 | TR_LINE 22275_1 | TR_LINE 22275_1 | TR_LINE 22275_1 | TR_LINE 22275_1 | TR_LINE 22275_1 | TR_LINE 22275_1 | TR_LINE 22275_1 | TR_LINE 22275_1 | TR_LINE 22275_1 | TR_LINE 22275_1 | TR_LINE 22275_1 | TR_LINE 22275_1 | TR_LINE 22275_1 | TR_LINE 22275_1
CA | 40001070 | 6023 | From GFSS to CISS | 6023_Friend St-Clinton Industrial 66 kV | Loading (A) | 149.7036 | 188.7691 | 138.765 | 153.2839 | 190.8632 | 140.6972 | 153.0062 | 190.6308 | 140.3671 | 154.5889 | 192.0891 | 141.4292 | 163.8753 | 193.2246 | 142.5703
CA | 40001070 | 6023 | From GFSS to CISS | 6023_Friend St-Clinton Industrial 66 kV | Loading (MVA) | 17.6541 | 22.3738 | 16.3978 | 18.0836 | 22.6329 | 16.6317 | 18.0501 | 22.6047 | 16.5918 | 18.2389 | 22.7773 | 16.7154 | 19.4478 | 22.895 | 16.84
CA | 40001070 | 6023 | From GFSS to CISS | 6023_Friend St-Clinton Industrial 66 kV | Loading (MW) | 16.4486 | 19.83 | 15.4044 | 16.8164 | 19.9813 | 15.5738 | 16.8253 | 19.9897 | 15.558 | 16.9996 | 20.1421 | 15.6704 | 15.7981 | 20.5119 | 15.9229
CA | 40001070 | 6023 | From GFSS to CISS | 6023_Friend St-Clinton Industrial 66 kV | Power Factor | 0.93172 | 0.88631 | 0.93942 | 0.92993 | 0.88284 | 0.9364 | 0.93215 | 0.88432 | 0.93769 | 0.93205 | 0.8843 | 0.93748 | 0.81233 | 0.89591 | 0.94554
CA | 40001070 | 6023 | From GFSS to CISS | 6023_Friend St-Clinton Industrial 66 kV | Rating (A) | 439 | 480 | 389 | 439 | 480 | 389 | 439 | 480 | 389 | 439 | 480 | 389 | 439 | 480 | 389
CA | 40001070 | 6023 | From GFSS to CISS | 6023_Friend St-Clinton Industrial 66 kV | Time | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00
CA | 40001070 | 6023 | From GFSS to CISS | 6023_Friend St-Clinton Industrial 66 kV | Voltage at Constrained Conductor | 68.0851 | 68.4302 | 68.2252 | 68.1126 | 68.4634 | 68.2479 | 68.1097 | 68.4612 | 68.2444 | 68.1179 | 68.4604 | 68.2364 | 68.5166 | 68.4096 | 68.1949
CA | 40001073 | 6001 | From T23 to PHSS | 6001_Glenmore - Parkhurst 66 kV | % of Rated A | 17.3655 | 18.2176 | 19.0443 | 17.5215 | 18.2848 | 18.6529 | 17.5333 | 18.2694 | 18.5907 | 17.2584 | 19.029 | 19.3316 | 17.6211 | 19.358 | 19.645
CA | 40001073 | 6001 | From T23 to PHSS | 6001_Glenmore - Parkhurst 66 kV | Limiting Line Name | TR_LINE 21203_1 | TR_LINE 21203_1 | TR_LINE 21203_1 | TR_LINE 21203_1 | TR_LINE 21203_1 | TR_LINE 21203_1 | TR_LINE 21203_1 | TR_LINE 21203_1 | TR_LINE 21203_1 | TR_LINE 21203_1 | TR_LINE 21203_1 | TR_LINE 21203_1 | TR_LINE 21203_1 | TR_LINE 21203_1 | TR_LINE 21203_1
CA | 40001073 | 6001 | From T23 to PHSS | 6001_Glenmore - Parkhurst 66 kV | Loading (A) | 69.3483 | 75.9856 | 70.6655 | 69.9728 | 76.2666 | 69.2642 | 69.9816 | 76.2041 | 69.1105 | 68.8912 | 79.2712 | 71.7403 | 70.339 | 80.6408 | 72.8989
CA | 40001073 | 6001 | From T23 to PHSS | 6001_Glenmore - Parkhurst 66 kV | Loading (MVA) | 8.2147 | 8.9638 | 8.4076 | 8.2921 | 9.0005 | 8.231 | 8.3035 | 8.9901 | 8.1649 | 8.1518 | 9.4145 | 8.5049 | 8.3163 | 9.571 | 8.6366
CA | 40001073 | 6001 | From T23 to PHSS | 6001_Glenmore - Parkhurst 66 kV | Loading (MW) | 7.9586 | 8.8743 | 8.3098 | 8.0317 | 8.9108 | 8.1861 | 7.966 | 8.9027 | 8.1595 | 7.8433 | 9.1547 | 8.4115 | 7.9865 | 9.294 | 8.5331
CA | 40001073 | 6001 | From T23 to PHSS | 6001_Glenmore - Parkhurst 66 kV | Power Factor | 0.96883 | 0.99001 | 0.98837 | 0.9686 | 0.99004 | 0.99454 | 0.95935 | 0.99028 | 0.99933 | 0.96216 | 0.97241 | 0.98902 | 0.96035 | 0.97106 | 0.98801
CA | 40001073 | 6001 | From T23 to PHSS | 6001_Glenmore - Parkhurst 66 kV | Rating (A) | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372
CA | 40001073 | 6001 | From T23 to PHSS | 6001_Glenmore - Parkhurst 66 kV | Time | 15:30 | 20:30 | 22:00 | 15:30 | 20:30 | 22:30 | 15:30 | 20:30 | 22:00 | 15:30 | 20:30 | 22:00 | 15:30 | 20:30 | 22:00
CA | 40001073 | 6001 | From T23 to PHSS | 6001_Glenmore - Parkhurst 66 kV | Voltage at Constrained Conductor | 68.3901 | 68.1085 | 68.6916 | 68.4184 | 68.1352 | 68.6092 | 68.5038 | 68.1124 | 68.2099 | 68.3168 | 68.5678 | 68.4453 | 68.2612 | 68.5238 | 68.4007
CA | 40001074 | 6003 | From RGBS to BERS | 6003_Glenmore - Berserker 66 kV | % of Rated A | 73.8361 | 71.4226 | 58.5017 | 73.1238 | 70.771 | 58.2444 | 73.4491 | 71.1722 | 58.0594 | 74.5775 | 72.3696 | 57.8712 | 75.1866 | 72.3353 | 58.4117
CA | 40001074 | 6003 | From RGBS to BERS | 6003_Glenmore - Berserker 66 kV | Limiting Line Name | TR_LINE 22137_1 | TR_LINE 22137_1 | TR_LINE 22137_1 | TR_LINE 22137_1 | TR_LINE 22137_1 | TR_LINE 22137_1 | TR_LINE 22137_1 | TR_LINE 22137_1 | TR_LINE 22137_1 | TR_LINE 22137_1 | TR_LINE 22137_1 | TR_LINE 22137_1 | TR_LINE 22137_1 | TR_LINE 22137_1 | TR_LINE 22137_1
CA | 40001074 | 6003 | From RGBS to BERS | 6003_Glenmore - Berserker 66 kV | Loading (A) | 296.0829 | 298.5467 | 217.6263 | 293.2266 | 295.8227 | 216.6691 | 294.5309 | 297.4997 | 215.9809 | 299.0558 | 302.5051 | 215.2807 | 301.4981 | 302.3614 | 217.2916
CA | 40001074 | 6003 | From RGBS to BERS | 6003_Glenmore - Berserker 66 kV | Loading (MVA) | 35.2066 | 35.4968 | 25.8935 | 34.629 | 34.9291 | 25.6063 | 34.9526 | 35.2981 | 25.5174 | 35.381 | 35.7748 | 25.5226 | 35.7783 | 36.0794 | 25.7442
CA | 40001074 | 6003 | From RGBS to BERS | 6003_Glenmore - Berserker 66 kV | Loading (MW) | 34.959 | 35.2896 | 25.2173 | 34.2838 | 34.6375 | 24.7325 | 34.7403 | 35.1259 | 24.6567 | 35.2219 | 35.6545 | 24.8644 | 35.6896 | 35.9546 | 25.1152
CA | 40001074 | 6003 | From RGBS to BERS | 6003_Glenmore - Berserker 66 kV | Power Factor | 0.99297 | 0.99416 | 0.97388 | 0.99003 | 0.99165 | 0.96588 | 0.99393 | 0.99512 | 0.96627 | 0.9955 | 0.99664 | 0.97421 | 0.99752 | 0.99654 | 0.97557
CA | 40001074 | 6003 | From RGBS to BERS | 6003_Glenmore - Berserker 66 kV | Rating (A) | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372
CA | 40001074 | 6003 | From RGBS to BERS | 6003_Glenmore - Berserker 66 kV | Time | 16:30 | 17:00 | 22:00 | 16:30 | 17:00 | 22:00 | 16:30 | 17:00 | 22:00 | 16:30 | 17:00 | 22:00 | 16:30 | 17:00 | 22:00
CA | 40001074 | 6003 | From RGBS to BERS | 6003_Glenmore - Berserker 66 kV | Voltage at Constrained Conductor | 68.6515 | 68.6461 | 68.694 | 68.183 | 68.1703 | 68.2321 | 68.5154 | 68.5021 | 68.2119 | 68.3057 | 68.2785 | 68.4477 | 68.5133 | 68.8925 | 68.4031
CA | 40001075 | 6004 | From T23 to RSSS | 6004_Glenmore - Rockhampton South 66 kV | % of Rated A | 15.3188 | 8.136 | 12.9377 | 13.615 | 6.4873 | 13.0173 | 18.2717 | 11.0728 | 12.8926 | 19.7293 | 14.5718 | 16.2241 | 18.9819 | 14.1473 | 15.8799
CA | 40001075 | 6004 | From T23 to RSSS | 6004_Glenmore - Rockhampton South 66 kV | Limiting Line Name | TR_LINE 139201_1 | TR_CABLE 301_1 | TR_LINE 139203_1 | TR_LINE 139201_1 | TR_CABLE 301_1 | TR_LINE 139203_1 | TR_LINE 139201_1 | TR_CABLE 301_1 | TR_LINE 22131_1 | TR_LINE 139201_1 | TR_CABLE 301_1 | TR_LINE 139201_1 | TR_LINE 139201_1 | TR_CABLE 301_1 | TR_LINE 139201_1
CA | 40001075 | 6004 | From T23 to RSSS | 6004_Glenmore - Rockhampton South 66 kV | Loading (A) | 56.2201 | 30.2659 | 43.7293 | 49.967 | 24.1329 | 43.9985 | 67.0571 | 41.191 | 47.7025 | 72.4064 | 54.2073 | 54.8375 | 69.6637 | 52.628 | 53.6739
CA | 40001075 | 6004 | From T23 to RSSS | 6004_Glenmore - Rockhampton South 66 kV | Loading (MVA) | 6.6764 | 3.598 | 5.1802 | 5.9166 | 2.8493 | 5.2131 | 7.9618 | 4.8862 | 5.6447 | 8.5883 | 6.4087 | 6.5059 | 8.264 | 6.278 | 6.3654
CA | 40001075 | 6004 | From T23 to RSSS | 6004_Glenmore - Rockhampton South 66 kV | Loading (MW) | 5.1918 | 3.2688 | 0.77356 | 4.4057 | 2.8021 | 0.81392 | 6.3392 | 4.4092 | 0.73142 | 6.843 | 5.7489 | 5.7664 | 6.5344 | 5.6525 | 5.6497
CA | 40001075 | 6004 | From T23 to RSSS | 6004_Glenmore - Rockhampton South 66 kV | Power Factor | 0.77764 | 0.90851 | 0.14933 | 0.74464 | 0.98343 | 0.15613 | 0.7962 | 0.90238 | 0.12958 | 0.79678 | 0.89705 | 0.88634 | 0.79071 | 0.90036 | 0.88756
CA | 40001075 | 6004 | From T23 to RSSS | 6004_Glenmore - Rockhampton South 66 kV | Rating (A) | 367 | 372 | 338 | 367 | 372 | 338 | 367 | 372 | 370 | 367 | 372 | 338 | 367 | 372 | 338
CA | 40001075 | 6004 | From T23 to RSSS | 6004_Glenmore - Rockhampton South 66 kV | Time | 14:00 | 17:00 | 0:30 | 11:00 | 17:00 | 0:30 | 13:30 | 17:00 | 0:30 | 12:30 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30
CA | 40001075 | 6004 | From T23 to RSSS | 6004_Glenmore - Rockhampton South 66 kV | Voltage at Constrained Conductor | 68.5633 | 68.6353 | 68.3935 | 68.3636 | 68.1669 | 68.406 | 68.5501 | 68.4867 | 68.3188 | 68.481 | 68.2576 | 68.4965 | 68.4891 | 68.8723 | 68.4708
CA | 40001076 | 6006 | From T23 to FVSS | 6006_Glenmore - Frenchville 66 kV | % of Rated A | 29.0615 | 35.113 | 30.906 | 28.5392 | 34.9508 | 30.4109 | 28.5004 | 34.7343 | 30.2547 | 28.296 | 35.2346 | 30.8808 | 29.3539 | 35.6241 | 31.2313
CA | 40001076 | 6006 | From T23 to FVSS | 6006_Glenmore - Frenchville 66 kV | Limiting Line Name | TR_LINE 22209_1 | TR_LINE 22209_1 | TR_LINE 22209_1 | TR_LINE 22209_1 | TR_LINE 22209_1 | TR_LINE 22209_1 | TR_LINE 22209_1 | TR_LINE 22209_1 | TR_LINE 22209_1 | TR_LINE 22209_1 | TR_LINE 22209_1 | TR_LINE 22209_1 | TR_LINE 22209_1 | TR_LINE 22209_1 | TR_LINE 22209_1
CA | 40001076 | 6006 | From T23 to FVSS | 6006_Glenmore - Frenchville 66 kV | Loading (A) | 116.535 | 146.7711 | 114.9693 | 114.4409 | 146.0932 | 113.1279 | 114.2853 | 145.188 | 112.5466 | 113.4657 | 147.2792 | 114.8755 | 117.7073 | 148.9071 | 116.1793
CA | 40001076 | 6006 | From T23 to FVSS | 6006_Glenmore - Frenchville 66 kV | Loading (MVA) | 13.7813 | 17.201 | 13.6101 | 13.4467 | 17.129 | 13.3075 | 13.4902 | 17.0179 | 13.2356 | 13.3533 | 17.3721 | 13.5503 | 13.8873 | 17.5511 | 13.694
CA | 40001076 | 6006 | From T23 to FVSS | 6006_Glenmore - Frenchville 66 kV | Loading (MW) | 13.4466 | 16.9437 | 13.4213 | 13.2639 | 16.8745 | 13.2292 | 13.1789 | 16.7686 | 13.1596 | 13.0623 | 16.9789 | 13.3695 | 13.3977 | 17.1434 | 13.5037
CA | 40001076 | 6006 | From T23 to FVSS | 6006_Glenmore - Frenchville 66 kV | Power Factor | 0.97571 | 0.98504 | 0.98613 | 0.98641 | 0.98515 | 0.99412 | 0.97692 | 0.98535 | 0.99426 | 0.97821 | 0.97736 | 0.98666 | 0.96474 | 0.97677 | 0.9861
CA | 40001076 | 6006 | From T23 to FVSS | 6006_Glenmore - Frenchville 66 kV | Rating (A) | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372
CA | 40001076 | 6006 | From T23 to FVSS | 6006_Glenmore - Frenchville 66 kV | Time | 16:30 | 20:30 | 22:00 | 16:30 | 20:30 | 22:00 | 16:30 | 20:30 | 22:00 | 16:30 | 20:30 | 22:00 | 16:30 | 20:30 | 22:00
CA | 40001076 | 6006 | From T23 to FVSS | 6006_Glenmore - Frenchville 66 kV | Voltage at Constrained Conductor | 68.277 | 67.6634 | 68.3467 | 67.8381 | 67.6925 | 67.915 | 68.1504 | 67.6731 | 67.897 | 67.9458 | 68.1005 | 68.1021 | 68.1168 | 68.0499 | 68.052
CA | 40001077 | 6044 | From RLSS to EQSS - YWSS | 6044_Raglan-East End Quarry/Yarwun 66 kV | % of Rated A | 1.4845 | 1.1673 | 1.248 | 1.485 | 1.1677 | 1.2482 | 1.4874 | 1.1703 | 1.2474 | 1.4877 | 1.1693 | 1.2467 | 1.486 | 1.1679 | 1.2464
CA | 40001077 | 6044 | From RLSS to EQSS - YWSS | 6044_Raglan-East End Quarry/Yarwun 66 kV | Limiting Line Name | TR_LINE 22122_1 | TR_LINE 22122_1 | TR_LINE 22122_1 | TR_LINE 22122_1 | TR_LINE 22122_1 | TR_LINE 22122_1 | TR_LINE 22122_1 | TR_LINE 22122_1 | TR_LINE 22122_1 | TR_LINE 22122_1 | TR_LINE 22122_1 | TR_LINE 22122_1 | TR_LINE 22122_1 | TR_LINE 22122_1 | TR_LINE 22122_1
CA | 40001077 | 6044 | From RLSS to EQSS - YWSS | 6044_Raglan-East End Quarry/Yarwun 66 kV | Loading (A) | 1.9596 | 1.9493 | 1.9843 | 1.9602 | 1.95 | 1.9846 | 1.9633 | 1.9544 | 1.9833 | 1.9638 | 1.9527 | 1.9822 | 1.9615 | 1.9504 | 1.9818
CA | 40001077 | 6044 | From RLSS to EQSS - YWSS | 6044_Raglan-East End Quarry/Yarwun 66 kV | Loading (MVA) | 0.23141 | 0.229 | 0.23729 | 0.23154 | 0.22915 | 0.23735 | 0.23229 | 0.23018 | 0.23705 | 0.2324 | 0.2298 | 0.23678 | 0.23185 | 0.22926 | 0.23669
CA | 40001077 | 6044 | From RLSS to EQSS - YWSS | 6044_Raglan-East End Quarry/Yarwun 66 kV | Loading (MW) | 3.4446e-05 | 3.4087e-05 | 3.5321e-05 | 3.4467e-05 | 3.411e-05 | 3.5331e-05 | 3.4578e-05 | 3.4264e-05 | 3.5286e-05 | 3.4593e-05 | 3.4207e-05 | 3.5245e-05 | 3.4513e-05 | 3.4126e-05 | 3.5232e-05
CA | 40001077 | 6044 | From RLSS to EQSS - YWSS | 6044_Raglan-East End Quarry/Yarwun 66 kV | Power Factor | 0.00014886 | 0.00014886 | 0.00014886 | 0.00014886 | 0.00014886 | 0.00014886 | 0.00014886 | 0.00014886 | 0.00014886 | 0.00014886 | 0.00014886 | 0.00014886 | 0.00014886 | 0.00014886 | 0.00014886
CA | 40001077 | 6044 | From RLSS to EQSS - YWSS | 6044_Raglan-East End Quarry/Yarwun 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
CA | 40001077 | 6044 | From RLSS to EQSS - YWSS | 6044_Raglan-East End Quarry/Yarwun 66 kV | Time | 9:00 | 20:00 | 4:00 | 9:00 | 20:00 | 4:00 | 9:00 | 21:00 | 4:00 | 9:00 | 21:00 | 5:00 | 12:30 | 21:00 | 4:30
CA | 40001077 | 6044 | From RLSS to EQSS - YWSS | 6044_Raglan-East End Quarry/Yarwun 66 kV | Voltage at Constrained Conductor | 68.1793 | 67.8234 | 69.0402 | 68.1999 | 67.8459 | 69.0495 | 68.3096 | 67.9985 | 69.0053 | 68.3252 | 67.942 | 68.9659 | 68.2452 | 67.8619 | 68.9532
CA | 40001079 | 6050 | From FVSS to PHSS | 6050_Parkhurst - Frenchville 66 kV | % of Rated A | 4.9132 | 6.7804 | 5.902 | 4.835 | 6.509 | 6.3479 | 5.439 | 6.3175 | 6.004 | 5.0739 | 6.209 | 5.0353 | 5.8095 | 6.0403 | 5.243
CA | 40001079 | 6050 | From FVSS to PHSS | 6050_Parkhurst - Frenchville 66 kV | Limiting Line Name | TR_LINE 13284_1 | TR_LINE 22210_1 | TR_LINE 13284_1 | TR_LINE 13284_1 | TR_LINE 22210_1 | TR_LINE 13284_1 | TR_LINE 13284_1 | TR_LINE 22210_1 | TR_LINE 13284_1 | TR_LINE 13284_1 | TR_LINE 22210_1 | TR_LINE 13284_1 | TR_LINE 13284_1 | TR_LINE 22210_1 | TR_LINE 13284_1
CA | 40001079 | 6050 | From FVSS to PHSS | 6050_Parkhurst - Frenchville 66 kV | Loading (A) | 19.7018 | 28.3422 | 21.9556 | 19.3885 | 27.2077 | 23.614 | 21.8103 | 26.4073 | 22.335 | 20.3464 | 25.9537 | 18.7313 | 23.2959 | 25.2484 | 19.5039
CA | 40001079 | 6050 | From FVSS to PHSS | 6050_Parkhurst - Frenchville 66 kV | Loading (MVA) | 2.329 | 3.3436 | 2.6176 | 2.2855 | 3.2111 | 2.8122 | 2.5815 | 3.1159 | 2.6627 | 2.4002 | 3.0602 | 2.2081 | 2.7491 | 2.9742 | 2.2996
CA | 40001079 | 6050 | From FVSS to PHSS | 6050_Parkhurst - Frenchville 66 kV | Loading (MW) | 1.9063 | 3.163 | 2.1516 | 2.21 | 3.0339 | 2.3641 | 2.2278 | 2.9376 | 2.2109 | 1.8922 | 2.8786 | 2.1951 | 2.2636 | 2.8094 | 2.2816
CA | 40001079 | 6050 | From FVSS to PHSS | 6050_Parkhurst - Frenchville 66 kV | Power Factor | 0.8185 | 0.946 | 0.82198 | 0.96696 | 0.94482 | 0.84067 | 0.86298 | 0.94277 | 0.83033 | 0.78834 | 0.94066 | 0.99411 | 0.82339 | 0.94457 | 0.99216
CA | 40001079 | 6050 | From FVSS to PHSS | 6050_Parkhurst - Frenchville 66 kV | Rating (A) | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372
CA | 40001079 | 6050 | From FVSS to PHSS | 6050_Parkhurst - Frenchville 66 kV | Time | 11:30 | 20:00 | 3:00 | 9:00 | 20:00 | 1:30 | 9:00 | 20:00 | 3:00 | 10:30 | 20:00 | 1:00 | 9:00 | 20:00 | 1:30
CA | 40001079 | 6050 | From FVSS to PHSS | 6050_Parkhurst - Frenchville 66 kV | Voltage at Constrained Conductor | 68.2488 | 68.1105 | 68.8335 | 68.058 | 68.139 | 68.7565 | 68.336 | 68.1242 | 68.8296 | 68.1071 | 68.0753 | 68.0589 | 68.1314 | 68.011 | 68.0725
CA | 40001081 | 6024 | CALLIOPE | 6024_Awoonga - Calliope 66kV | % of Rated A | 16.4837 | 8.6226 | 6.4204 | 19.2122 | 10.4129 | 7.182 | 19.3633 | 10.6616 | 7.2958 | 19.2402 | 10.4241 | 7.1925 | 19.381 | 10.6873 | 7.2678
CA | 40001081 | 6024 | CALLIOPE | 6024_Awoonga - Calliope 66kV | Limiting Line Name | TR_LINE 181307_1 | TR_LINE 181307_1 | TR_LINE 181307_1 | TR_LINE 181307_1 | TR_LINE 181307_1 | TR_LINE 181307_1 | TR_LINE 181307_1 | TR_LINE 181307_1 | TR_LINE 181307_1 | TR_LINE 181307_1 | TR_LINE 181307_1 | TR_LINE 181307_1 | TR_LINE 181307_1 | TR_LINE 181307_1 | TR_LINE 181307_1
CA | 40001081 | 6024 | CALLIOPE | 6024_Awoonga - Calliope 66kV | Loading (A) | 27.8574 | 20.6942 | 15.0238 | 32.4686 | 24.9909 | 16.8058 | 32.724 | 25.5878 | 17.0723 | 32.5159 | 25.0178 | 16.8304 | 32.7538 | 25.6495 | 17.0067
CA | 40001081 | 6024 | CALLIOPE | 6024_Awoonga - Calliope 66kV | Loading (MVA) | 3.2591 | 2.4103 | 1.7736 | 3.7947 | 2.9241 | 1.9834 | 3.823 | 2.9927 | 2.0153 | 3.7998 | 2.9268 | 1.9869 | 3.823 | 2.9789 | 2.0066
CA | 40001081 | 6024 | CALLIOPE | 6024_Awoonga - Calliope 66kV | Loading (MW) | 2.4259 | 1.1689 | 0.96468 | 2.9579 | 1.7589 | 1.2117 | 2.8889 | 1.685 | 1.1849 | 2.9605 | 1.7568 | 1.2117 | 2.8727 | 1.6437 | 1.16
CA | 40001081 | 6024 | CALLIOPE | 6024_Awoonga - Calliope 66kV | Power Factor | 0.74435 | 0.48496 | 0.5439 | 0.7795 | 0.60151 | 0.61092 | 0.75567 | 0.56304 | 0.58798 | 0.77913 | 0.60022 | 0.60982 | 0.75144 | 0.55179 | 0.57811
CA | 40001081 | 6024 | CALLIOPE | 6024_Awoonga - Calliope 66kV | Rating (A) | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234
CA | 40001081 | 6024 | CALLIOPE | 6024_Awoonga - Calliope 66kV | Time | 15:30 | 17:00 | 6:00 | 15:30 | 17:00 | 6:00 | 15:30 | 17:00 | 6:00 | 15:30 | 17:00 | 6:00 | 15:30 | 17:00 | 6:00
CA | 40001081 | 6024 | CALLIOPE | 6024_Awoonga - Calliope 66kV | Voltage at Constrained Conductor | 67.545 | 67.2455 | 68.1593 | 67.4757 | 67.5539 | 68.1383 | 67.4493 | 67.5249 | 68.1521 | 67.4686 | 67.5445 | 68.1603 | 67.3875 | 67.0519 | 68.1198
CA | 40001083 | 6090 | From EHBS to RLSS | 6090_Egan's Hill - Raglan 66 kV | % of Rated A | 23.5481 | 20.5187 | 15.9619 | 23.6751 | 20.5099 | 16.0256 | 23.6361 | 20.5367 | 16.0345 | 23.7545 | 20.4492 | 16.0112 | 24.3317 | 20.9987 | 16.421
CA | 40001083 | 6090 | From EHBS to RLSS | 6090_Egan's Hill - Raglan 66 kV | Limiting Line Name | TR_LINE 22121_1 | TR_LINE 22121_1 | TR_LINE 160589_1 | TR_LINE 22121_1 | TR_LINE 22121_1 | TR_LINE 160589_1 | TR_LINE 22121_1 | TR_LINE 22121_1 | TR_LINE 160589_1 | TR_LINE 22121_1 | TR_LINE 22121_1 | TR_LINE 160589_1 | TR_LINE 22121_1 | TR_LINE 22121_1 | TR_LINE 160589_1
CA | 40001083 | 6090 | From EHBS to RLSS | 6090_Egan's Hill - Raglan 66 kV | Loading (A) | 31.0828 | 34.2653 | 25.3795 | 31.2504 | 34.2507 | 25.4808 | 31.1989 | 34.2955 | 25.4948 | 31.3552 | 34.1493 | 25.4579 | 32.1171 | 35.067 | 26.1094
CA | 40001083 | 6090 | From EHBS to RLSS | 6090_Egan's Hill - Raglan 66 kV | Loading (MVA) | 3.6537 | 3.9966 | 3.0134 | 3.6537 | 3.9966 | 3.0214 | 3.6536 | 3.9967 | 3.0214 | 3.6539 | 3.9964 | 3.0214 | 3.7459 | 4.0973 | 3.0965
CA | 40001083 | 6090 | From EHBS to RLSS | 6090_Egan's Hill - Raglan 66 kV | Loading (MW) | 3.6445 | 3.9841 | 3.0046 | 3.6444 | 3.9841 | 3.0129 | 3.6444 | 3.9841 | 3.0128 | 3.6445 | 3.9841 | 3.0128 | 3.7357 | 4.0839 | 3.089
CA | 40001083 | 6090 | From EHBS to RLSS | 6090_Egan's Hill - Raglan 66 kV | Power Factor | 0.99749 | 0.99687 | 0.99708 | 0.99747 | 0.99688 | 0.99718 | 0.99749 | 0.99686 | 0.99717 | 0.99743 | 0.99692 | 0.99715 | 0.99728 | 0.99673 | 0.99758
CA | 40001083 | 6090 | From EHBS to RLSS | 6090_Egan's Hill - Raglan 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
CA | 40001083 | 6090 | From EHBS to RLSS | 6090_Egan's Hill - Raglan 66 kV | Time | 16:30 | 18:30 | 22:30 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00
CA | 40001083 | 6090 | From EHBS to RLSS | 6090_Egan's Hill - Raglan 66 kV | Voltage at Constrained Conductor | 67.8656 | 67.3408 | 68.5514 | 67.5015 | 67.3692 | 68.4594 | 67.6111 | 67.2827 | 68.421 | 67.2794 | 67.5658 | 68.5217 | 67.338 | 67.4588 | 68.4721
CA | 40001084 | 6091 | From EHBS to GASS / MASS&MLSS | 6091_Egan's Hill - Gavial 66 kV | % of Rated A | 29.5567 | 30.7186 | 22.1206 | 29.7137 | 30.705 | 22.2389 | 42.2816 | 42.4581 | 28.0257 | 56.5587 | 56.5127 | 43.6079 | 57.1027 | 56.5876 | 43.9048
CA | 40001084 | 6091 | From EHBS to GASS / MASS&MLSS | 6091_Egan's Hill - Gavial 66 kV | Limiting Line Name | TR_LINE 13465_1 | TR_LINE 13465_1 | TR_LINE 13465_1 | TR_LINE 13465_1 | TR_LINE 13465_1 | TR_LINE 13465_1 | TR_LINE 13465_1 | TR_LINE 13465_1 | TR_LINE 13465_1 | TR_LINE 13465_1 | TR_LINE 13465_1 | TR_LINE 13465_1 | TR_LINE 13465_1 | TR_LINE 13465_1 | TR_LINE 13465_1
CA | 40001084 | 6091 | From EHBS to GASS / MASS&MLSS | 6091_Egan's Hill - Gavial 66 kV | Loading (A) | 117.9312 | 127.4823 | 81.8463 | 118.5576 | 127.4259 | 82.284 | 168.7037 | 176.2013 | 103.6951 | 225.6692 | 234.5278 | 161.3492 | 227.8399 | 234.8385 | 162.4477
CA | 40001084 | 6091 | From EHBS to GASS / MASS&MLSS | 6091_Egan's Hill - Gavial 66 kV | Loading (MVA) | 14.0838 | 15.1352 | 9.7763 | 14.0853 | 15.1346 | 9.7788 | 20.0743 | 20.9552 | 12.3188 | 26.7259 | 27.7536 | 19.186 | 27.0185 | 28.041 | 19.3093
CA | 40001084 | 6091 | From EHBS to GASS / MASS&MLSS | 6091_Egan's Hill - Gavial 66 kV | Loading (MW) | 13.9394 | 14.9657 | 9.7452 | 13.9403 | 14.9655 | 9.7463 | 19.2194 | 20.0487 | 11.6646 | 24.8418 | 25.7904 | 17.4002 | 25.1242 | 26.0759 | 17.5225
CA | 40001084 | 6091 | From EHBS to GASS / MASS&MLSS | 6091_Egan's Hill - Gavial 66 kV | Power Factor | 0.98975 | 0.98881 | 0.99681 | 0.98971 | 0.98882 | 0.99667 | 0.95741 | 0.95674 | 0.94689 | 0.9295 | 0.92926 | 0.90692 | 0.92989 | 0.92992 | 0.90746
CA | 40001084 | 6091 | From EHBS to GASS / MASS&MLSS | 6091_Egan's Hill - Gavial 66 kV | Rating (A) | 399 | 415 | 370 | 399 | 415 | 370 | 399 | 415 | 370 | 399 | 415 | 370 | 399 | 415 | 370
CA | 40001084 | 6091 | From EHBS to GASS / MASS&MLSS | 6091_Egan's Hill - Gavial 66 kV | Time | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 17:00 | 8:30 | 16:30 | 17:00 | 8:30 | 16:30 | 17:00 | 8:30
CA | 40001084 | 6091 | From EHBS to GASS / MASS&MLSS | 6091_Egan's Hill - Gavial 66 kV | Voltage at Constrained Conductor | 68.9492 | 68.5451 | 68.9631 | 68.5925 | 68.5731 | 68.6135 | 68.6997 | 68.663 | 68.5882 | 68.3754 | 68.3226 | 68.6526 | 68.4655 | 68.9388 | 68.6265
CA | 40001085 | 6093 | GASS - MLSS | 6093_Gavial - Mt Morgan 66 kV | % of Rated A | 4.2224 | 3.6655 | 3.9076 | 4.224 | 3.6664 | 3.9329 | 41.3018 | 32.7803 | 35.2911 | 84.7302 | 67.301 | 71.9576 | 84.7903 | 66.603 | 71.9939
CA | 40001085 | 6093 | GASS - MLSS | 6093_Gavial - Mt Morgan 66 kV | Limiting Line Name | TR_LINE 19113_1 | TR_LINE 19767_1 | TR_LINE 19767_1 | TR_LINE 19113_1 | TR_LINE 19767_1 | TR_LINE 19767_1 | TR_LINE 19767_1 | TR_LINE 19767_1 | TR_LINE 19767_1 | TR_LINE 19767_1 | TR_LINE 19767_1 | TR_LINE 19767_1 | TR_LINE 19767_1 | TR_LINE 19767_1 | TR_LINE 19767_1
CA | 40001085 | 6093 | GASS - MLSS | 6093_Gavial - Mt Morgan 66 kV | Loading (A) | 6.0381 | 6.1214 | 6.2131 | 6.0403 | 6.1228 | 6.2534 | 54.5183 | 54.7431 | 56.1129 | 111.2188 | 111.7701 | 113.7844 | 111.2986 | 110.5993 | 113.8423
CA | 40001085 | 6093 | GASS - MLSS | 6093_Gavial - Mt Morgan 66 kV | Loading (MVA) | 0.71781 | 0.72472 | 0.74096 | 0.71829 | 0.72506 | 0.75038 | 6.3359 | 6.3382 | 6.5108 | 12.843 | 12.8497 | 13.1929 | 12.8439 | 12.8353 | 13.1936
CA | 40001085 | 6093 | GASS - MLSS | 6093_Gavial - Mt Morgan 66 kV | Loading (MW) | 0.22112 | 0.033301 | 0.025106 | 0.22112 | 0.033301 | 0.025119 | 5.4811 | 5.4812 | 5.6249 | 10.8742 | 10.8767 | 11.164 | 10.8745 | 10.8713 | 11.1643
CA | 40001085 | 6093 | GASS - MLSS | 6093_Gavial - Mt Morgan 66 kV | Power Factor | 0.30804 | 0.04595 | 0.033884 | 0.30784 | 0.045929 | 0.033475 | 0.86509 | 0.86479 | 0.86394 | 0.8467 | 0.84646 | 0.84621 | 0.84667 | 0.84699 | 0.84619
CA | 40001085 | 6093 | GASS - MLSS | 6093_Gavial - Mt Morgan 66 kV | Rating (A) | 143 | 167 | 159 | 143 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
CA | 40001085 | 6093 | GASS - MLSS | 6093_Gavial - Mt Morgan 66 kV | Time | 9:30 | 21:00 | 0:30 | 9:30 | 21:00 | 1:30 | 13:30 | 17:00 | 8:30 | 13:30 | 17:00 | 8:30 | 13:30 | 17:00 | 8:30
CA | 40001085 | 6093 | GASS - MLSS | 6093_Gavial - Mt Morgan 66 kV | Voltage at Constrained Conductor | 68.6354 | 68.3537 | 68.8526 | 68.6561 | 68.3692 | 69.2802 | 67.0973 | 66.8462 | 66.9902 | 66.6693 | 66.3755 | 66.9419 | 66.6267 | 67.0029 | 66.9115
CA | 40001086 | 6094 | From GASS to MASS T | 6094_Malchi Tee - Malchi 66 kV | % of Rated A | 69.4311 | 53.5472 | 35.3548 | 69.7889 | 53.5237 | 35.5427 | 69.9674 | 53.3139 | 35.5865 | 71.5977 | 54.269 | 36.046 | 72.9743 | 55.3976 | 36.8074
CA | 40001086 | 6094 | From GASS to MASS T | 6094_Malchi Tee - Malchi 66 kV | Limiting Line Name | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1
CA | 40001086 | 6094 | From GASS to MASS T | 6094_Malchi Tee - Malchi 66 kV | Loading (A) | 117.1283 | 128.2991 | 82.5401 | 117.7348 | 128.2428 | 82.9802 | 118.0367 | 127.739 | 83.0827 | 120.7931 | 130.0336 | 84.1571 | 123.118 | 132.7378 | 85.9379
CA | 40001086 | 6094 | From GASS to MASS T | 6094_Malchi Tee - Malchi 66 kV | Loading (MVA) | 13.9163 | 15.1465 | 9.828 | 13.9152 | 15.1461 | 9.8299 | 13.917 | 15.1428 | 9.8303 | 14.1121 | 15.1899 | 9.9654 | 14.4013 | 15.6737 | 10.1689
CA | 40001086 | 6094 | From GASS to MASS T | 6094_Malchi Tee - Malchi 66 kV | Loading (MW) | 13.6486 | 14.8372 | 9.6802 | 13.649 | 14.837 | 9.681 | 13.6498 | 14.8355 | 9.6812 | 13.8383 | 14.8784 | 9.813 | 14.1181 | 15.3452 | 10.0111
CA | 40001086 | 6094 | From GASS to MASS T | 6094_Malchi Tee - Malchi 66 kV | Power Factor | 0.98076 | 0.97958 | 0.98496 | 0.98086 | 0.97959 | 0.98486 | 0.98079 | 0.97971 | 0.98483 | 0.98059 | 0.97949 | 0.98471 | 0.98033 | 0.97904 | 0.98449
CA | 40001086 | 6094 | From GASS to MASS T | 6094_Malchi Tee - Malchi 66 kV | Rating (A) | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234
CA | 40001086 | 6094 | From GASS to MASS T | 6094_Malchi Tee - Malchi 66 kV | Time | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 17:30 | 22:00 | 16:30 | 18:00 | 22:00
CA | 40001086 | 6094 | From GASS to MASS T | 6094_Malchi Tee - Malchi 66 kV | Voltage at Constrained Conductor | 68.5964 | 68.1599 | 68.7447 | 68.2378 | 68.1881 | 68.3932 | 68.0721 | 68.4421 | 68.312 | 67.4513 | 67.4434 | 68.3665 | 67.5336 | 68.1737 | 68.3168
CA | 40001087 | 6095 | From EHBS to RSSS | 6095_Egan's Hill-Rockhampton South 66 kV | % of Rated A | 31.3819 | 22.6943 | 35.7644 | 29.4238 | 24.3107 | 35.4455 | 25.2471 | 22.1023 | 32.653 | 19.678 | 21.2846 | 31.2309 | 19.5793 | 21.234 | 30.9859
CA | 40001087 | 6095 | From EHBS to RSSS | 6095_Egan's Hill-Rockhampton South 66 kV | Limiting Line Name | TR_LINE 20972_1 | TR_LINE 20972_1 | TR_LINE 20972_1 | TR_LINE 20972_1 | TR_LINE 20972_1 | TR_LINE 20972_1 | TR_LINE 20972_1 | TR_LINE 20972_1 | TR_LINE 20972_1 | TR_LINE 20972_1 | TR_LINE 20972_1 | TR_LINE 20972_1 | TR_LINE 20972_1 | TR_LINE 20972_1 | TR_LINE 20972_1
CA | 40001087 | 6095 | From EHBS to RSSS | 6095_Egan's Hill-Rockhampton South 66 kV | Loading (A) | 77.743 | 56.7358 | 78.5507 | 72.8829 | 60.6847 | 77.8484 | 62.5169 | 55.2558 | 71.6988 | 48.8015 | 53.2115 | 68.7081 | 48.5566 | 53.085 | 68.1689
CA | 40001087 | 6095 | From EHBS to RSSS | 6095_Egan's Hill-Rockhampton South 66 kV | Loading (MVA) | 9.2153 | 6.7049 | 9.33 | 8.6625 | 7.1828 | 9.2491 | 7.4326 | 6.5689 | 8.523 | 5.7849 | 6.3218 | 8.1466 | 5.7534 | 6.3022 | 8.0819
CA | 40001087 | 6095 | From EHBS to RSSS | 6095_Egan's Hill-Rockhampton South 66 kV | Loading (MW) | 8.1101 | 5.6377 | 6.2911 | 7.521 | 6.1369 | 6.1975 | 6.2623 | 5.4638 | 5.3717 | 4.7923 | 5.2339 | 4.6314 | 4.749 | 5.1973 | 4.5247
CA | 40001087 | 6095 | From EHBS to RSSS | 6095_Egan's Hill-Rockhampton South 66 kV | Power Factor | 0.88007 | 0.84083 | 0.67429 | 0.86823 | 0.85438 | 0.67006 | 0.84255 | 0.83177 | 0.63026 | 0.82842 | 0.82792 | 0.5685 | 0.82543 | 0.82468 | 0.55986
CA | 40001087 | 6095 | From EHBS to RSSS | 6095_Egan's Hill-Rockhampton South 66 kV | Rating (A) | 248 | 250 | 220 | 248 | 250 | 220 | 248 | 250 | 220 | 248 | 250 | 220 | 248 | 250 | 220
CA | 40001087 | 6095 | From EHBS to RSSS | 6095_Egan's Hill-Rockhampton South 66 kV | Time | 14:30 | 18:00 | 7:30 | 14:00 | 17:00 | 7:30 | 11:30 | 21:00 | 7:00 | 10:30 | 21:00 | 0:00 | 10:30 | 21:00 | 0:30
CA | 40001087 | 6095 | From EHBS to RSSS | 6095_Egan's Hill-Rockhampton South 66 kV | Voltage at Constrained Conductor | 68.4364 | 68.2293 | 68.5758 | 68.6206 | 68.3368 | 68.5949 | 68.6411 | 68.6367 | 68.6311 | 68.4386 | 68.5921 | 68.4556 | 68.4089 | 68.5428 | 68.4488
CA | 40001089 | 6097 | From EHBS To CNSS | 6097_Egan's Hill - Canning 66 kV | % of Rated A | 38.9551 | 34.0857 | 38.7277 | 36.8098 | 34.41 | 38.3259 | 31.8248 | 31.8883 | 35.3455 | 27.5354 | 30.0506 | 33.0501 | 27.7109 | 30.1953 | 32.7729
CA | 40001089 | 6097 | From EHBS To CNSS | 6097_Egan's Hill - Canning 66 kV | Limiting Line Name | TR_LINE 21003_1 | TR_LINE 21003_1 | TR_LINE 21003_1 | TR_LINE 21003_1 | TR_LINE 21003_1 | TR_LINE 21003_1 | TR_LINE 21003_1 | TR_LINE 21003_1 | TR_LINE 21003_1 | TR_LINE 21003_1 | TR_LINE 21003_1 | TR_LINE 21003_1 | TR_LINE 21003_1 | TR_LINE 21003_1 | TR_LINE 21003_1
CA | 40001089 | 6097 | From EHBS To CNSS | 6097_Egan's Hill - Canning 66 kV | Loading (A) | 96.5553 | 85.1621 | 85.0912 | 91.2358 | 85.9734 | 84.2064 | 78.878 | 79.671 | 77.6447 | 68.284 | 75.0711 | 72.5823 | 68.7181 | 75.4324 | 71.9714
CA | 40001089 | 6097 | From EHBS To CNSS | 6097_Egan's Hill - Canning 66 kV | Loading (MVA) | 11.4461 | 10.0774 | 10.1101 | 10.808 | 10.1733 | 10.0078 | 9.331 | 9.4323 | 9.2323 | 8.083 | 8.9299 | 8.6243 | 8.1277 | 8.9662 | 8.5506
CA | 40001089 | 6097 | From EHBS To CNSS | 6097_Egan's Hill - Canning 66 kV | Loading (MW) | 11.0636 | 9.7564 | 8.597 | 10.4602 | 9.8558 | 8.4891 | 9.0849 | 9.1597 | 7.6979 | 8.0818 | 8.6117 | 6.8179 | 8.1257 | 8.64 | 6.7199
CA | 40001089 | 6097 | From EHBS To CNSS | 6097_Egan's Hill - Canning 66 kV | Power Factor | 0.96659 | 0.96815 | 0.85034 | 0.96782 | 0.9688 | 0.84825 | 0.97362 | 0.9711 | 0.8338 | 0.99985 | 0.96436 | 0.79054 | 0.99975 | 0.96362 | 0.78589
CA | 40001089 | 6097 | From EHBS To CNSS | 6097_Egan's Hill - Canning 66 kV | Rating (A) | 248 | 250 | 220 | 248 | 250 | 220 | 248 | 250 | 220 | 248 | 250 | 220 | 248 | 250 | 220
CA | 40001089 | 6097 | From EHBS To CNSS | 6097_Egan's Hill - Canning 66 kV | Time | 14:30 | 18:30 | 7:30 | 16:00 | 17:00 | 7:30 | 15:00 | 19:00 | 7:00 | 15:30 | 21:00 | 0:00 | 15:30 | 21:00 | 0:30
CA | 40001089 | 6097 | From EHBS To CNSS | 6097_Egan's Hill - Canning 66 kV | Voltage at Constrained Conductor | 68.4415 | 68.3188 | 68.5979 | 68.3941 | 68.3182 | 68.617 | 68.2989 | 68.353 | 68.6498 | 68.3428 | 68.6774 | 68.6014 | 68.2871 | 68.6263 | 68.5927
CA | 40001092 | 6029 | From LMSS to MVSS | 6029_Littlemore - Miriam Vale 66 kV | % of Rated A | 11.0225 | 10.928 | 7.5249 | 10.5041 | 10.395 | 7.1742 | 10.5073 | 10.3975 | 7.1757 | 10.5052 | 10.3973 | 7.1762 | 10.9468 | 10.9515 | 7.5384
CA | 40001092 | 6029 | From LMSS to MVSS | 6029_Littlemore - Miriam Vale 66 kV | Limiting Line Name | TR_LINE 16162_1 | TR_LINE 16031_1 | TR_LINE 16162_1 | TR_LINE 16162_1 | TR_LINE 16031_1 | TR_LINE 16162_1 | TR_LINE 16162_1 | TR_LINE 16031_1 | TR_LINE 16162_1 | TR_LINE 16162_1 | TR_LINE 16031_1 | TR_LINE 16162_1 | TR_LINE 16162_1 | TR_LINE 16031_1 | TR_LINE 16162_1
CA | 40001092 | 6029 | From LMSS to MVSS | 6029_Littlemore - Miriam Vale 66 kV | Loading (A) | 14.5497 | 18.2497 | 11.9646 | 13.8655 | 17.3596 | 11.4069 | 13.8696 | 17.3637 | 11.4094 | 13.8668 | 17.3635 | 11.4102 | 14.4498 | 18.2891 | 11.986
CA | 40001092 | 6029 | From LMSS to MVSS | 6029_Littlemore - Miriam Vale 66 kV | Loading (MVA) | 1.6959 | 2.1062 | 1.3946 | 1.6163 | 2.0056 | 1.33 | 1.6163 | 2.0056 | 1.33 | 1.6163 | 2.0056 | 1.33 | 1.6963 | 2.1062 | 1.3945
CA | 40001092 | 6029 | From LMSS to MVSS | 6029_Littlemore - Miriam Vale 66 kV | Loading (MW) | 1.6877 | 2.1013 | 1.3811 | 1.6069 | 2.0011 | 1.315 | 1.6069 | 2.0011 | 1.315 | 1.6069 | 2.0011 | 1.315 | 1.6875 | 2.1013 | 1.3811
CA | 40001092 | 6029 | From LMSS to MVSS | 6029_Littlemore - Miriam Vale 66 kV | Power Factor | 0.99513 | 0.9977 | 0.99032 | 0.99416 | 0.99778 | 0.98872 | 0.99417 | 0.99778 | 0.98874 | 0.99416 | 0.99778 | 0.98874 | 0.99486 | 0.99769 | 0.99043
CA | 40001092 | 6029 | From LMSS to MVSS | 6029_Littlemore - Miriam Vale 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
CA | 40001092 | 6029 | From LMSS to MVSS | 6029_Littlemore - Miriam Vale 66 kV | Time | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00
CA | 40001092 | 6029 | From LMSS to MVSS | 6029_Littlemore - Miriam Vale 66 kV | Voltage at Constrained Conductor | 67.2967 | 66.631 | 67.2962 | 67.3031 | 66.7011 | 67.3187 | 67.2823 | 66.6853 | 67.3032 | 67.2963 | 66.6863 | 67.2986 | 67.7751 | 66.4886 | 67.1692
CA | 40001103 | 6031 | From CPSS to LMSS | 6031_Calliope - Littlemore 66 kV | % of Rated A | 16.6513 | 14.8608 | 12.6202 | 16.2785 | 14.4499 | 12.3998 | 16.2783 | 14.4506 | 12.3991 | 16.2784 | 14.4506 | 12.3988 | 16.7729 | 15.0246 | 12.6597
CA | 40001103 | 6031 | From CPSS to LMSS | 6031_Calliope - Littlemore 66 kV | Limiting Line Name | TR_LINE 13872_1 | TR_LINE 13872_1 | TR_LINE 13872_1 | TR_LINE 13872_1 | TR_LINE 13872_1 | TR_LINE 13872_1 | TR_LINE 13872_1 | TR_LINE 13872_1 | TR_LINE 13872_1 | TR_LINE 13872_1 | TR_LINE 13872_1 | TR_LINE 13872_1 | TR_LINE 13872_1 | TR_LINE 13872_1 | TR_LINE 13872_1
CA | 40001103 | 6031 | From CPSS to LMSS | 6031_Calliope - Littlemore 66 kV | Loading (A) | 21.9797 | 24.8175 | 20.0661 | 21.4876 | 24.1313 | 19.7157 | 21.4874 | 24.1325 | 19.7145 | 21.4875 | 24.1325 | 19.7141 | 22.1402 | 25.0911 | 20.129
CA | 40001103 | 6031 | From CPSS to LMSS | 6031_Calliope - Littlemore 66 kV | Loading (MVA) | 2.5695 | 2.8959 | 2.3401 | 2.5111 | 2.8163 | 2.2991 | 2.5103 | 2.8158 | 2.2984 | 2.5108 | 2.8158 | 2.2982 | 2.6078 | 2.9238 | 2.3442
CA | 40001103 | 6031 | From CPSS to LMSS | 6031_Calliope - Littlemore 66 kV | Loading (MW) | 2.0201 | 2.4745 | 1.6399 | 1.9378 | 2.3708 | 1.5728 | 1.9378 | 2.3708 | 1.5728 | 1.9378 | 2.3708 | 1.5728 | 2.0815 | 2.5408 | 1.6876
CA | 40001103 | 6031 | From CPSS to LMSS | 6031_Calliope - Littlemore 66 kV | Power Factor | 0.78617 | 0.85448 | 0.70078 | 0.77169 | 0.84183 | 0.68411 | 0.77194 | 0.84198 | 0.6843 | 0.77177 | 0.84197 | 0.68436 | 0.79819 | 0.869 | 0.71993
CA | 40001103 | 6031 | From CPSS to LMSS | 6031_Calliope - Littlemore 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
CA | 40001103 | 6031 | From CPSS to LMSS | 6031_Calliope - Littlemore 66 kV | Time | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00
CA | 40001103 | 6031 | From CPSS to LMSS | 6031_Calliope - Littlemore 66 kV | Voltage at Constrained Conductor | 67.4952 | 67.3707 | 67.33 | 67.4699 | 67.3804 | 67.3265 | 67.4495 | 67.3651 | 67.3112 | 67.4632 | 67.3661 | 67.3067 | 68.0033 | 67.2768 | 67.2372
CA | 40001125 | 6039 | From CISS to BCSS | 6039_Clinton Industrial - Beecher 66 kV | % of Rated A | 5.3282 | 3.5505 | 4.3165 | 5.3255 | 3.57 | 4.3141 | 5.3264 | 3.57 | 4.3137 | 5.3259 | 3.5694 | 4.3136 | 5.3287 | 3.5515 | 4.3156
CA | 40001125 | 6039 | From CISS to BCSS | 6039_Clinton Industrial - Beecher 66 kV | Limiting Line Name | TR_LINE 33766_1 | TR_LINE 16739_1 | TR_LINE 16739_1 | TR_LINE 33766_1 | TR_LINE 16739_1 | TR_LINE 16739_1 | TR_LINE 33766_1 | TR_LINE 16739_1 | TR_LINE 16739_1 | TR_LINE 33766_1 | TR_LINE 16739_1 | TR_LINE 16739_1 | TR_LINE 33766_1 | TR_LINE 16739_1 | TR_LINE 16739_1
CA | 40001125 | 6039 | From CISS to BCSS | 6039_Clinton Industrial - Beecher 66 kV | Loading (A) | 13.0542 | 9.7993 | 10.0144 | 13.0475 | 9.8532 | 10.0086 | 13.0498 | 9.8532 | 10.0079 | 13.0485 | 9.8515 | 10.0076 | 13.0554 | 9.8021 | 10.0123
CA | 40001125 | 6039 | From CISS to BCSS | 6039_Clinton Industrial - Beecher 66 kV | Loading (MVA) | 1.5492 | 1.1662 | 1.1877 | 1.5489 | 1.1676 | 1.1875 | 1.549 | 1.1676 | 1.1874 | 1.5489 | 1.1676 | 1.1874 | 1.5492 | 1.1663 | 1.1876
CA | 40001125 | 6039 | From CISS to BCSS | 6039_Clinton Industrial - Beecher 66 kV | Loading (MW) | 1.3682 | 1.1024 | 1.1184 | 1.3682 | 1.1024 | 1.1184 | 1.3682 | 1.1024 | 1.1184 | 1.3682 | 1.1024 | 1.1184 | 1.3682 | 1.1024 | 1.1184
CA | 40001125 | 6039 | From CISS to BCSS | 6039_Clinton Industrial - Beecher 66 kV | Power Factor | 0.88319 | 0.94528 | 0.94164 | 0.88332 | 0.9441 | 0.9418 | 0.88328 | 0.9441 | 0.94182 | 0.8833 | 0.94414 | 0.94183 | 0.88317 | 0.9452 | 0.9417
CA | 40001125 | 6039 | From CISS to BCSS | 6039_Clinton Industrial - Beecher 66 kV | Rating (A) | 245 | 276 | 232 | 245 | 276 | 232 | 245 | 276 | 232 | 245 | 276 | 232 | 245 | 276 | 232
CA | 40001125 | 6039 | From CISS to BCSS | 6039_Clinton Industrial - Beecher 66 kV | Time | 11:30 | 17:00 | 8:30 | 11:30 | 17:00 | 8:30 | 11:30 | 17:00 | 8:30 | 11:30 | 17:00 | 8:30 | 11:30 | 17:00 | 8:30
CA | 40001125 | 6039 | From CISS to BCSS | 6039_Clinton Industrial - Beecher 66 kV | Voltage at Constrained Conductor | 68.5147 | 68.7078 | 68.4719 | 68.5391 | 68.4183 | 68.4992 | 68.5307 | 68.4184 | 68.5029 | 68.5353 | 68.4266 | 68.5044 | 68.5105 | 68.6939 | 68.4819
CA | 40001136 | 6041 | From YWSS to BCSS | 6041_Yarwun - Boat Creek 66 kV | % of Rated A | 11.8565 | 7.2353 | 7.7435 | 11.8519 | 7.2655 | 7.7399 | 11.8535 | 7.2655 | 7.7394 | 11.8526 | 7.2645 | 7.7392 | 11.8573 | 7.237 | 7.7422
CA | 40001136 | 6041 | From YWSS to BCSS | 6041_Yarwun - Boat Creek 66 kV | Limiting Line Name | TR_LINE 21443_1 | TR_LINE 135844_1 | TR_LINE 135844_1 | TR_LINE 21443_1 | TR_LINE 135844_1 | TR_LINE 135844_1 | TR_LINE 21443_1 | TR_LINE 135844_1 | TR_LINE 135844_1 | TR_LINE 21443_1 | TR_LINE 135844_1 | TR_LINE 135844_1 | TR_LINE 21443_1 | TR_LINE 135844_1 | TR_LINE 135844_1
CA | 40001136 | 6041 | From YWSS to BCSS | 6041_Yarwun - Boat Creek 66 kV | Loading (A) | 15.8878 | 12.0829 | 12.3122 | 15.8815 | 12.1335 | 12.3064 | 15.8837 | 12.1334 | 12.3056 | 15.8825 | 12.1317 | 12.3053 | 15.8888 | 12.0858 | 12.3101
CA | 40001136 | 6041 | From YWSS to BCSS | 6041_Yarwun - Boat Creek 66 kV | Loading (MVA) | 1.8682 | 1.4295 | 1.4514 | 1.8682 | 1.4294 | 1.4513 | 1.8682 | 1.4294 | 1.4513 | 1.8682 | 1.4294 | 1.4513 | 1.8682 | 1.4296 | 1.4514
CA | 40001136 | 6041 | From YWSS to BCSS | 6041_Yarwun - Boat Creek 66 kV | Loading (MW) | 1.3567 | 1.0967 | 1.1125 | 1.3567 | 1.0967 | 1.1125 | 1.3567 | 1.0967 | 1.1125 | 1.3567 | 1.0967 | 1.1125 | 1.3567 | 1.0967 | 1.1125
CA | 40001136 | 6041 | From YWSS to BCSS | 6041_Yarwun - Boat Creek 66 kV | Power Factor | 0.7262 | 0.76718 | 0.76646 | 0.72622 | 0.76723 | 0.76651 | 0.72622 | 0.76723 | 0.76652 | 0.72622 | 0.76724 | 0.76652 | 0.7262 | 0.76715 | 0.76648
CA | 40001136 | 6041 | From YWSS to BCSS | 6041_Yarwun - Boat Creek 66 kV | Rating (A) | 134 | 167 | 159 | 134 | 167 | 159 | 134 | 167 | 159 | 134 | 167 | 159 | 134 | 167 | 159
CA | 40001136 | 6041 | From YWSS to BCSS | 6041_Yarwun - Boat Creek 66 kV | Time | 11:30 | 17:00 | 8:30 | 11:30 | 17:00 | 8:30 | 11:30 | 17:00 | 8:30 | 11:30 | 17:00 | 8:30 | 11:30 | 17:00 | 8:30
CA | 40001136 | 6041 | From YWSS to BCSS | 6041_Yarwun - Boat Creek 66 kV | Voltage at Constrained Conductor | 67.8903 | 68.3066 | 68.0617 | 67.9151 | 68.0149 | 68.0892 | 67.9065 | 68.015 | 68.093 | 67.9112 | 68.0233 | 68.0945 | 67.8861 | 68.2925 | 68.0718
CA | 40001150 | 6005 | From T23 to CNSS | 6005_Rockhampton Glenmore-Canning 66 kV | % of Rated A | 25.4788 | 26.0303 | 23.8709 | 25.0807 | 25.5533 | 23.7253 | 27.7601 | 28.2959 | 23.9291 | 30.717 | 31.2371 | 26.5844 | 32.041 | 31.2741 | 26.834
CA | 40001150 | 6005 | From T23 to CNSS | 6005_Rockhampton Glenmore-Canning 66 kV | Limiting Line Name | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1
CA | 40001150 | 6005 | From T23 to CNSS | 6005_Rockhampton Glenmore-Canning 66 kV | Loading (A) | 101.6606 | 108.0259 | 88.3223 | 100.0718 | 106.0461 | 87.7834 | 110.7629 | 117.4279 | 88.5377 | 122.5595 | 129.6318 | 98.3624 | 127.8367 | 129.785 | 99.2859
CA | 40001150 | 6005 | From T23 to CNSS | 6005_Rockhampton Glenmore-Canning 66 kV | Loading (MVA) | 12.0882 | 12.8441 | 10.4458 | 11.8181 | 12.5213 | 10.385 | 13.1445 | 13.9327 | 10.515 | 14.4999 | 15.3305 | 11.6532 | 15.1702 | 15.4866 | 11.7585
CA | 40001150 | 6005 | From T23 to CNSS | 6005_Rockhampton Glenmore-Canning 66 kV | Loading (MW) | 12.0339 | 12.8142 | 8.0621 | 11.5339 | 12.3064 | 7.9496 | 13.1353 | 13.9312 | 10.2153 | 14.497 | 15.3192 | 11.5041 | 15.0686 | 15.4746 | 11.6149
CA | 40001150 | 6005 | From T23 to CNSS | 6005_Rockhampton Glenmore-Canning 66 kV | Power Factor | 0.9955 | 0.99767 | 0.77181 | 0.97595 | 0.98284 | 0.76549 | 0.9993 | 0.99989 | 0.97149 | 0.9998 | 0.99926 | 0.9872 | 0.9933 | 0.99922 | 0.98779
CA | 40001150 | 6005 | From T23 to CNSS | 6005_Rockhampton Glenmore-Canning 66 kV | Rating (A) | 399 | 415 | 370 | 399 | 415 | 370 | 399 | 415 | 370 | 399 | 415 | 370 | 399 | 415 | 370
CA | 40001150 | 6005 | From T23 to CNSS | 6005_Rockhampton Glenmore-Canning 66 kV | Time | 16:30 | 17:00 | 7:30 | 16:30 | 17:00 | 7:30 | 16:30 | 17:00 | 8:00 | 16:30 | 17:00 | 8:00 | 16:30 | 17:00 | 8:00
CA | 40001150 | 6005 | From T23 to CNSS | 6005_Rockhampton Glenmore-Canning 66 kV | Voltage at Constrained Conductor | 68.6515 | 68.6461 | 68.2827 | 68.183 | 68.1703 | 68.3023 | 68.5154 | 68.5021 | 68.5681 | 68.3057 | 68.2785 | 68.4001 | 68.5133 | 68.8925 | 68.3761
CA | 40001151 | 6053 | PDBS to PHSS | 6053_Parkhurst - Pandoin 66 kV | % of Rated A | 58.7255 | 50.4531 | 44.3464 | 58.2895 | 50.5448 | 45.8151 | 58.6455 | 50.5878 | 45.9405 | 60.4106 | 52.2981 | 44.7954 | 61.1191 | 52.44 | 45.3892
CA | 40001151 | 6053 | PDBS to PHSS | 6053_Parkhurst - Pandoin 66 kV | Limiting Line Name | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1
CA | 40001151 | 6053 | PDBS to PHSS | 6053_Parkhurst - Pandoin 66 kV | Loading (A) | 307.0984 | 298.6291 | 242.0597 | 304.8186 | 299.1776 | 250.0085 | 306.7009 | 299.4801 | 250.6917 | 315.9208 | 309.5959 | 244.5097 | 319.622 | 310.4331 | 247.7477
CA | 40001151 | 6053 | PDBS to PHSS | 6053_Parkhurst - Pandoin 66 kV | Loading (MVA) | 36.3989 | 35.3179 | 28.8114 | 36.1393 | 35.3964 | 29.6286 | 36.3845 | 35.5143 | 29.7024 | 37.3985 | 36.6423 | 28.9998 | 37.8069 | 37.0686 | 29.3655
CA | 40001151 | 6053 | PDBS to PHSS | 6053_Parkhurst - Pandoin 66 kV | Loading (MW) | 36.345 | 35.2136 | 28.6736 | 36.0877 | 35.3121 | 29.0936 | 36.3705 | 35.514 | 29.1561 | 37.3646 | 36.6351 | 28.8544 | 37.7622 | 37.0589 | 29.2015
CA | 40001151 | 6053 | PDBS to PHSS | 6053_Parkhurst - Pandoin 66 kV | Power Factor | 0.99852 | 0.99704 | 0.99522 | 0.99857 | 0.99762 | 0.98194 | 0.99962 | 0.99999 | 0.98161 | 0.9991 | 0.99981 | 0.99499 | 0.99882 | 0.99974 | 0.99442
CA | 40001151 | 6053 | PDBS to PHSS | 6053_Parkhurst - Pandoin 66 kV | Rating (A) | 523 | 592 | 546 | 523 | 592 | 546 | 523 | 592 | 546 | 523 | 592 | 546 | 523 | 592 | 546
CA | 40001151 | 6053 | PDBS to PHSS | 6053_Parkhurst - Pandoin 66 kV | Time | 15:30 | 18:00 | 22:00 | 15:30 | 17:00 | 22:00 | 15:30 | 17:30 | 22:00 | 15:30 | 17:00 | 22:00 | 15:30 | 17:00 | 22:00
CA | 40001151 | 6053 | PDBS to PHSS | 6053_Parkhurst - Pandoin 66 kV | Voltage at Constrained Conductor | 68.4305 | 68.2814 | 68.7196 | 68.4506 | 68.3076 | 68.422 | 68.4921 | 68.4659 | 68.4055 | 68.3463 | 68.3323 | 68.4761 | 68.2926 | 68.9411 | 68.4332
CA | 40001158 | 6066 | BOCOOLIMA TEE WOODERSON | 6066_Bocoolima Tee -Wooderson 66 kV | % of Rated A | 6.7452 | 30.1804 | 30.8765 | 6.7478 | 29.7895 | 30.4718 | 6.7498 | 29.8002 | 30.4796 | 6.7484 | 29.7945 | 30.4819 | 6.6937 | 30.2506 | 30.9249
CA | 40001158 | 6066 | BOCOOLIMA TEE WOODERSON | 6066_Bocoolima Tee -Wooderson 66 kV | Limiting Line Name | TR_LINE 21599_1 | TR_LINE 223719_1 | TR_LINE 223719_1 | TR_LINE 21599_1 | TR_LINE 223719_1 | TR_LINE 223719_1 | TR_LINE 21599_1 | TR_LINE 223719_1 | TR_LINE 223719_1 | TR_LINE 21599_1 | TR_LINE 223719_1 | TR_LINE 223719_1 | TR_LINE 21599_1 | TR_LINE 223719_1 | TR_LINE 223719_1
CA | 40001158 | 6066 | BOCOOLIMA TEE WOODERSON | 6066_Bocoolima Tee -Wooderson 66 kV | Loading (A) | 11.3994 | 71.5148 | 71.333 | 11.4037 | 70.58 | 70.3894 | 11.4072 | 70.606 | 70.4078 | 11.4049 | 70.5922 | 70.4132 | 11.3123 | 71.6844 | 71.447
CA | 40001158 | 6066 | BOCOOLIMA TEE WOODERSON | 6066_Bocoolima Tee -Wooderson 66 kV | Loading (MVA) | 1.3298 | 8.3283 | 8.3113 | 1.3298 | 8.2179 | 8.2011 | 1.3299 | 8.2183 | 8.2014 | 1.3299 | 8.2181 | 8.2014 | 1.3297 | 8.331 | 8.3131
CA | 40001158 | 6066 | BOCOOLIMA TEE WOODERSON | 6066_Bocoolima Tee -Wooderson 66 kV | Loading (MW) | 1.2247 | 7.6446 | 7.6303 | 1.2247 | 7.5493 | 7.5352 | 1.2247 | 7.5494 | 7.5353 | 1.2247 | 7.5494 | 7.5353 | 1.2247 | 7.6453 | 7.6307
CA | 40001158 | 6066 | BOCOOLIMA TEE WOODERSON | 6066_Bocoolima Tee -Wooderson 66 kV | Power Factor | 0.92097 | 0.9179 | 0.91806 | 0.92096 | 0.91864 | 0.91881 | 0.92096 | 0.91861 | 0.91879 | 0.92096 | 0.91862 | 0.91878 | 0.92107 | 0.91769 | 0.91791
CA | 40001158 | 6066 | BOCOOLIMA TEE WOODERSON | 6066_Bocoolima Tee -Wooderson 66 kV | Rating (A) | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234
CA | 40001158 | 6066 | BOCOOLIMA TEE WOODERSON | 6066_Bocoolima Tee -Wooderson 66 kV | Time | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00
CA | 40001158 | 6066 | BOCOOLIMA TEE WOODERSON | 6066_Bocoolima Tee -Wooderson 66 kV | Voltage at Constrained Conductor | 67.3532 | 67.236 | 67.2698 | 67.3279 | 67.2234 | 67.2671 | 67.3075 | 67.202 | 67.2519 | 67.3212 | 67.2133 | 67.2474 | 67.8633 | 67.0984 | 67.1769
CA | 40001159 | 6051 | From PHSS to KESS | 6051_Parkhurst - Keppel 66 kV | % of Rated A | 98.4561 | 78.3832 | 65.5165 | 98.8169 | 78.0797 | 65.7518 | 98.8899 | 78.1429 | 65.9252 | 100.7704 | 79.5225 | 66.523 | 102.4111 | 80.4922 | 67.8935
CA | 40001159 | 6051 | From PHSS to KESS | 6051_Parkhurst - Keppel 66 kV | Limiting Line Name | TR_LINE 19655_1 | TR_LINE 19655_1 | TR_LINE 19655_1 | TR_LINE 19655_1 | TR_LINE 19655_1 | TR_LINE 19655_1 | TR_LINE 19655_1 | TR_LINE 19655_1 | TR_LINE 19655_1 | TR_LINE 19655_1 | TR_LINE 19655_1 | TR_LINE 19655_1 | TR_LINE 19655_1 | TR_LINE 19655_1 | TR_LINE 19655_1
CA | 40001159 | 6051 | From PHSS to KESS | 6051_Parkhurst - Keppel 66 kV | Loading (A) | 208.7051 | 231.9868 | 161.1574 | 209.4703 | 231.0887 | 161.7366 | 209.6242 | 231.2756 | 162.1629 | 213.6102 | 235.3584 | 163.6333 | 217.0881 | 238.2282 | 167.0034
CA | 40001159 | 6051 | From PHSS to KESS | 6051_Parkhurst - Keppel 66 kV | Loading (MVA) | 23.5 | 25.7471 | 18.4024 | 23.4328 | 25.6669 | 18.3538 | 23.5488 | 25.6701 | 18.3939 | 23.8952 | 26.124 | 18.602 | 24.3103 | 26.5059 | 18.9507
CA | 40001159 | 6051 | From PHSS to KESS | 6051_Parkhurst - Keppel 66 kV | Loading (MW) | 23.429 | 25.6204 | 18.3829 | 23.3623 | 25.5419 | 18.3347 | 23.473 | 25.5431 | 18.374 | 23.8133 | 25.9866 | 18.5811 | 24.2236 | 26.3628 | 18.9257
CA | 40001159 | 6051 | From PHSS to KESS | 6051_Parkhurst - Keppel 66 kV | Power Factor | 0.99698 | 0.99508 | 0.99894 | 0.99699 | 0.99513 | 0.99896 | 0.99678 | 0.99505 | 0.99891 | 0.99657 | 0.99474 | 0.99888 | 0.99643 | 0.9946 | 0.99868
CA | 40001159 | 6051 | From PHSS to KESS | 6051_Parkhurst - Keppel 66 kV | Rating (A) | 212 | 296 | 246 | 212 | 296 | 246 | 212 | 296 | 246 | 212 | 296 | 246 | 212 | 296 | 246
CA | 40001159 | 6051 | From PHSS to KESS | 6051_Parkhurst - Keppel 66 kV | Time | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 17:30 | 22:00 | 16:30 | 18:00 | 22:00
CA | 40001159 | 6051 | From PHSS to KESS | 6051_Parkhurst - Keppel 66 kV | Voltage at Constrained Conductor | 65.0091 | 64.0774 | 65.9271 | 64.5864 | 64.1259 | 65.5174 | 64.8586 | 64.082 | 65.4881 | 64.5845 | 64.0839 | 65.6339 | 64.6538 | 64.2376 | 65.5149
CA | 40001161 | 6082 | From KESS to YPSS | 6082_Farnborough Tee - Yeppoon 66 kV | % of Rated A | 98.5105 | 78.4317 | 65.5462 | 98.8708 | 78.128 | 65.7809 | 98.946 | 78.1916 | 65.955 | 100.8278 | 79.5727 | 66.5533 | 102.4697 | 80.5431 | 67.926
CA | 40001161 | 6082 | From KESS to YPSS | 6082_Farnborough Tee - Yeppoon 66 kV | Limiting Line Name | TR_LINE 22238_1 | TR_LINE 22238_1 | TR_LINE 22238_1 | TR_LINE 22238_1 | TR_LINE 22238_1 | TR_LINE 22238_1 | TR_LINE 22238_1 | TR_LINE 22238_1 | TR_LINE 22238_1 | TR_LINE 22238_1 | TR_LINE 22238_1 | TR_LINE 22238_1 | TR_LINE 22238_1 | TR_LINE 22238_1 | TR_LINE 22238_1
CA | 40001161 | 6082 | From KESS to YPSS | 6082_Farnborough Tee - Yeppoon 66 kV | Loading (A) | 208.8414 | 232.1569 | 161.243 | 209.6053 | 231.258 | 161.8206 | 209.7646 | 231.4462 | 162.2487 | 213.7541 | 235.5342 | 163.7206 | 217.2348 | 238.4066 | 167.0974
CA | 40001161 | 6082 | From KESS to YPSS | 6082_Farnborough Tee - Yeppoon 66 kV | Loading (MVA) | 23.2671 | 25.4514 | 18.2697 | 23.1979 | 25.3737 | 18.2199 | 23.3134 | 25.3762 | 18.2593 | 23.6496 | 25.8184 | 18.4648 | 24.056 | 26.1922 | 18.8073
CA | 40001161 | 6082 | From KESS to YPSS | 6082_Farnborough Tee - Yeppoon 66 kV | Loading (MW) | 23.2054 | 25.3441 | 18.2496 | 23.137 | 25.2678 | 18.2004 | 23.2474 | 25.2685 | 18.239 | 23.5791 | 25.7022 | 18.4437 | 23.9817 | 26.0715 | 18.7825
CA | 40001161 | 6082 | From KESS to YPSS | 6082_Farnborough Tee - Yeppoon 66 kV | Power Factor | 0.99735 | 0.99578 | 0.9989 | 0.99738 | 0.99583 | 0.99893 | 0.99717 | 0.99576 | 0.99889 | 0.99702 | 0.9955 | 0.99886 | 0.99691 | 0.99539 | 0.99868
CA | 40001161 | 6082 | From KESS to YPSS | 6082_Farnborough Tee - Yeppoon 66 kV | Rating (A) | 212 | 296 | 246 | 212 | 296 | 246 | 212 | 296 | 246 | 212 | 296 | 246 | 212 | 296 | 246
CA | 40001161 | 6082 | From KESS to YPSS | 6082_Farnborough Tee - Yeppoon 66 kV | Time | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 17:30 | 22:00 | 16:30 | 18:00 | 22:00
CA | 40001161 | 6082 | From KESS to YPSS | 6082_Farnborough Tee - Yeppoon 66 kV | Voltage at Constrained Conductor | 64.3227 | 63.295 | 65.4167 | 63.8978 | 63.347 | 65.0056 | 64.1671 | 63.3018 | 64.9743 | 63.8778 | 63.287 | 65.1149 | 63.9342 | 63.4298 | 64.9825
CA | 40001163 | 6075 | KESS to FBSS | 6075_Keppel - Farnborough 66 kV | % of Rated A | 0.30327 | 0.27188 | 0.34886 | 0.303 | 0.27201 | 0.34894 | 0.3043 | 0.27188 | 0.34878 | 0.3045 | 0.27248 | 0.34836 | 0.30307 | 0.27197 | 0.34847
CA | 40001163 | 6075 | KESS to FBSS | 6075_Keppel - Farnborough 66 kV | Limiting Line Name | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2
CA | 40001163 | 6075 | KESS to FBSS | 6075_Keppel - Farnborough 66 kV | Loading (A) | 1.1464 | 1.1283 | 1.1757 | 1.1453 | 1.1288 | 1.1759 | 1.1503 | 1.1283 | 1.1754 | 1.151 | 1.1308 | 1.174 | 1.1456 | 1.1287 | 1.1743
CA | 40001163 | 6075 | KESS to FBSS | 6075_Keppel - Farnborough 66 kV | Loading (MVA) | 0.13182 | 0.1277 | 0.13865 | 0.13159 | 0.12782 | 0.13871 | 0.13272 | 0.1277 | 0.13858 | 0.1329 | 0.12827 | 0.13825 | 0.13165 | 0.12779 | 0.13833
CA | 40001163 | 6075 | KESS to FBSS | 6075_Keppel - Farnborough 66 kV | Loading (MW) | 3.2848e-06 | 3.1821e-06 | 3.4549e-06 | 3.2789e-06 | 3.1851e-06 | 3.4565e-06 | 3.3073e-06 | 3.1822e-06 | 3.4533e-06 | 3.3115e-06 | 3.1963e-06 | 3.4448e-06 | 3.2805e-06 | 3.1842e-06 | 3.447e-06
CA | 40001163 | 6075 | KESS to FBSS | 6075_Keppel - Farnborough 66 kV | Power Factor | 2.4918e-05 | 2.4918e-05 | 2.4919e-05 | 2.4918e-05 | 2.4918e-05 | 2.4919e-05 | 2.4919e-05 | 2.4918e-05 | 2.4918e-05 | 2.4918e-05 | 2.4919e-05 | 2.4918e-05 | 2.4919e-05 | 2.4918e-05 | 2.4918e-05
CA | 40001163 | 6075 | KESS to FBSS | 6075_Keppel - Farnborough 66 kV | Rating (A) | 378 | 415 | 337 | 378 | 415 | 337 | 378 | 415 | 337 | 378 | 415 | 337 | 378 | 415 | 337
CA | 40001163 | 6075 | KESS to FBSS | 6075_Keppel - Farnborough 66 kV | Time | 10:30 | 21:30 | 4:00 | 9:30 | 21:30 | 4:00 | 9:30 | 21:30 | 4:00 | 9:30 | 21:30 | 5:00 | 9:30 | 21:30 | 4:30
CA | 40001163 | 6075 | KESS to FBSS | 6075_Keppel - Farnborough 66 kV | Voltage at Constrained Conductor | 66.3906 | 65.3446 | 68.0873 | 66.331 | 65.3759 | 68.1033 | 66.6167 | 65.3456 | 68.0723 | 66.6609 | 65.4901 | 67.9893 | 66.3469 | 65.3666 | 68.0103
CA | 40001218 | 6032 | Boyne Residental Tee to Awoonga | 6032_Boyne Residential Tee-Awoonga 66 kV | % of Rated A | 16.5326 | 18.1865 | 16.916 | 19.1154 | 20.2578 | 18.3505 | 18.6339 | 19.9553 | 18.0996 | 19.1291 | 20.265 | 18.3612 | 18.9507 | 20.4275 | 18.536
CA | 40001218 | 6032 | Boyne Residental Tee to Awoonga | 6032_Boyne Residential Tee-Awoonga 66 kV | Limiting Line Name | TR_LINE 69280_1 | TR_LINE 22220_1 | TR_LINE 69280_1 | TR_LINE 69280_1 | TR_LINE 22220_1 | TR_LINE 22220_1 | TR_LINE 69280_1 | TR_LINE 22220_1 | TR_LINE 22220_1 | TR_LINE 69280_1 | TR_LINE 22220_1 | TR_LINE 22220_1 | TR_LINE 69280_1 | TR_LINE 22220_1 | TR_LINE 22220_1
CA | 40001218 | 6032 | Boyne Residental Tee to Awoonga | 6032_Boyne Residential Tee-Awoonga 66 kV | Loading (A) | 34.8838 | 53.65 | 41.4441 | 40.3335 | 59.7602 | 44.9586 | 39.3176 | 58.8678 | 44.3438 | 40.3624 | 59.7814 | 44.9848 | 39.986 | 60.2607 | 45.4129
CA | 40001218 | 6032 | Boyne Residental Tee to Awoonga | 6032_Boyne Residential Tee-Awoonga 66 kV | Loading (MVA) | 4.0705 | 6.2605 | 4.8442 | 4.7038 | 6.9644 | 5.237 | 4.5838 | 6.8572 | 5.1639 | 4.7067 | 6.966 | 5.2385 | 4.7005 | 7.0125 | 5.2828
CA | 40001218 | 6032 | Boyne Residental Tee to Awoonga | 6032_Boyne Residential Tee-Awoonga 66 kV | Loading (MW) | 4.0287 | 6.2588 | 4.8422 | 4.6863 | 6.9568 | 5.2366 | 4.5775 | 6.8383 | 5.1608 | 4.6888 | 6.9587 | 5.2381 | 4.6942 | 6.992 | 5.279
CA | 40001218 | 6032 | Boyne Residental Tee to Awoonga | 6032_Boyne Residential Tee-Awoonga 66 kV | Power Factor | 0.98974 | 0.99974 | 0.99958 | 0.99629 | 0.99891 | 0.99992 | 0.99862 | 0.99724 | 0.9994 | 0.99621 | 0.99894 | 0.99992 | 0.99867 | 0.99708 | 0.99928
CA | 40001218 | 6032 | Boyne Residental Tee to Awoonga | 6032_Boyne Residential Tee-Awoonga 66 kV | Rating (A) | 211 | 295 | 245 | 211 | 295 | 245 | 211 | 295 | 245 | 211 | 295 | 245 | 211 | 295 | 245
CA | 40001218 | 6032 | Boyne Residental Tee to Awoonga | 6032_Boyne Residential Tee-Awoonga 66 kV | Time | 16:30 | 20:30 | 22:00 | 16:30 | 20:30 | 22:00 | 16:30 | 20:30 | 22:00 | 16:30 | 20:30 | 22:00 | 16:30 | 20:30 | 22:00
CA | 40001218 | 6032 | Boyne Residental Tee to Awoonga | 6032_Boyne Residential Tee-Awoonga 66 kV | Voltage at Constrained Conductor | 67.3695 | 67.3715 | 67.4842 | 67.3319 | 67.2841 | 67.2531 | 67.31 | 67.2522 | 67.233 | 67.3248 | 67.2759 | 67.2332 | 67.8691 | 67.1859 | 67.1622
CA | 40001219 | 6034 | Boyne Residental Tee to Boyne Residental | 6034_Boyne Residential Tee - BORE 66 kV | % of Rated A | 48.1306 | 44.3585 | 34.3846 | 47.7306 | 43.9688 | 34.0885 | 48.1742 | 44.3764 | 34.4016 | 48.1634 | 44.3723 | 34.4034 | 48.616 | 45.217 | 35.045
CA | 40001219 | 6034 | Boyne Residental Tee to Boyne Residental | 6034_Boyne Residential Tee - BORE 66 kV | Limiting Line Name | TR_LINE 22222_1 | TR_LINE 22222_1 | TR_LINE 22222_1 | TR_LINE 22222_1 | TR_LINE 22222_1 | TR_LINE 22222_1 | TR_LINE 22222_1 | TR_LINE 22222_1 | TR_LINE 22222_1 | TR_LINE 22222_1 | TR_LINE 22222_1 | TR_LINE 22222_1 | TR_LINE 22222_1 | TR_LINE 22222_1 | TR_LINE 22222_1
CA | 40001219 | 6034 | Boyne Residental Tee to Boyne Residental | 6034_Boyne Residential Tee - BORE 66 kV | Loading (A) | 79.4136 | 98.9175 | 63.2659 | 78.7536 | 98.0485 | 62.7212 | 79.4855 | 98.9573 | 63.2972 | 79.4677 | 98.9483 | 63.3006 | 80.2145 | 100.8318 | 64.4811
CA | 40001219 | 6034 | Boyne Residental Tee to Boyne Residental | 6034_Boyne Residential Tee - BORE 66 kV | Loading (MVA) | 9.2316 | 11.5069 | 7.3729 | 9.15 | 11.4049 | 7.3079 | 9.2317 | 11.507 | 7.373 | 9.2317 | 11.507 | 7.373 | 9.3937 | 11.7114 | 7.5033
CA | 40001219 | 6034 | Boyne Residental Tee to Boyne Residental | 6034_Boyne Residential Tee - BORE 66 kV | Loading (MW) | 9.1554 | 11.3973 | 7.3196 | 9.0749 | 11.2969 | 7.2552 | 9.1555 | 11.3973 | 7.3196 | 9.1555 | 11.3973 | 7.3196 | 9.3161 | 11.5982 | 7.4483
CA | 40001219 | 6034 | Boyne Residental Tee to Boyne Residental | 6034_Boyne Residential Tee - BORE 66 kV | Power Factor | 0.99176 | 0.99047 | 0.99276 | 0.99179 | 0.99053 | 0.99279 | 0.99175 | 0.99047 | 0.99276 | 0.99175 | 0.99047 | 0.99276 | 0.99174 | 0.99033 | 0.99268
CA | 40001219 | 6034 | Boyne Residental Tee to Boyne Residental | 6034_Boyne Residential Tee - BORE 66 kV | Rating (A) | 165 | 223 | 184 | 165 | 223 | 184 | 165 | 223 | 184 | 165 | 223 | 184 | 165 | 223 | 184
CA | 40001219 | 6034 | Boyne Residental Tee to Boyne Residental | 6034_Boyne Residential Tee - BORE 66 kV | Time | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00
CA | 40001219 | 6034 | Boyne Residental Tee to Boyne Residental | 6034_Boyne Residential Tee - BORE 66 kV | Voltage at Constrained Conductor | 67.115 | 67.1622 | 67.2838 | 67.0796 | 67.1569 | 67.2693 | 67.0553 | 67.1358 | 67.2509 | 67.0701 | 67.1418 | 67.2474 | 67.6121 | 67.058 | 67.1826
CA | 40001229 | 6101 ICI-T4 | 6101 ICI-T4 | 6101_Boat Creek - Orica 66 kV | % of Rated A | 16.2252 | 10.5446 | 17.22 | 16.2243 | 10.5441 | 17.2192 | 16.2371 | 10.5529 | 17.3621 | 16.2517 | 10.5613 | 17.3755 | 16.2521 | 10.5612 | 17.3756
CA | 40001229 | 6101 ICI-T4 | 6101 ICI-T4 | 6101_Boat Creek - Orica 66 kV | Limiting Line Name | TR_LINE pole4158700 to ORIC | TR_LINE pole4158700 to ORIC | TR_LINE pole4158700 to ORIC | TR_LINE pole4158700 to ORIC | TR_LINE pole4158700 to ORIC | TR_LINE pole4158700 to ORIC | TR_LINE pole4158700 to ORIC | TR_LINE pole4158700 to ORIC | TR_LINE pole4158700 to ORIC | TR_LINE pole4158700 to ORIC | TR_LINE pole4158700 to ORIC | TR_LINE pole4158700 to ORIC | TR_LINE pole4158700 to ORIC | TR_LINE pole4158700 to ORIC | TR_LINE pole4158700 to ORIC
CA | 40001229 | 6101 ICI-T4 | 6101 ICI-T4 | 6101_Boat Creek - Orica 66 kV | Loading (A) | 120.0548 | 85.0949 | 113.9846 | 120.0481 | 85.0908 | 113.9791 | 120.1426 | 85.1621 | 114.9252 | 120.2504 | 85.2294 | 115.0141 | 120.2538 | 85.229 | 115.0146
CA | 40001229 | 6101 ICI-T4 | 6101 ICI-T4 | 6101_Boat Creek - Orica 66 kV | Loading (MVA) | 14.1013 | 10.011 | 13.3861 | 14.1013 | 10.011 | 13.3861 | 14.1013 | 10.011 | 13.3862 | 14.1013 | 10.011 | 13.3862 | 14.1013 | 10.011 | 13.3862
CA | 40001229 | 6101 ICI-T4 | 6101 ICI-T4 | 6101_Boat Creek - Orica 66 kV | Loading (MW) | 12.8886 | 9.1501 | 12.2351 | 12.8886 | 9.1501 | 12.2351 | 12.8886 | 9.1501 | 12.2351 | 12.8886 | 9.1501 | 12.2351 | 12.8886 | 9.1501 | 12.2351
CA | 40001229 | 6101 ICI-T4 | 6101 ICI-T4 | 6101_Boat Creek - Orica 66 kV | Power Factor | 0.914 | 0.914 | 0.91401 | 0.914 | 0.914 | 0.91401 | 0.914 | 0.914 | 0.91401 | 0.914 | 0.914 | 0.91401 | 0.914 | 0.914 | 0.91401
CA | 40001229 | 6101 ICI-T4 | 6101 ICI-T4 | 6101_Boat Creek - Orica 66 kV | Rating (A) | 740 | 807 | 662 | 740 | 807 | 662 | 740 | 807 | 662 | 740 | 807 | 662 | 740 | 807 | 662
CA | 40001229 | 6101 ICI-T4 | 6101 ICI-T4 | 6101_Boat Creek - Orica 66 kV | Time | 16:00 | 20:30 | 6:00 | 16:00 | 20:30 | 6:00 | 16:00 | 20:30 | 6:00 | 16:00 | 20:30 | 6:00 | 16:00 | 20:30 | 6:00
CA | 40001229 | 6101 ICI-T4 | 6101 ICI-T4 | 6101_Boat Creek - Orica 66 kV | Voltage at Constrained Conductor | 67.8138 | 67.9224 | 67.8029 | 67.8176 | 67.9258 | 67.8062 | 67.7643 | 67.8688 | 67.2483 | 67.7035 | 67.8152 | 67.1964 | 67.7016 | 67.8156 | 67.1961
CA | 40001235 | 6102 | BOAT CREEK TO YARWUN | 6102_Boat Creek - Yarwun 66 kV | % of Rated A | 5.5461 | 4.1623 | 5.333 | 5.4246 | 4.0717 | 5.2169 | 7.5047 | 5.6249 | 7.2084 | 9.6283 | 7.2018 | 9.23 | 9.6286 | 7.202 | 9.2301
CA | 40001235 | 6102 | BOAT CREEK TO YARWUN | 6102_Boat Creek - Yarwun 66 kV | Limiting Line Name | TR_LINE 16861_2 | TR_LINE 16861_2 | TR_LINE 16861_2 | TR_LINE 16861_2 | TR_LINE 16861_2 | TR_LINE 16861_2 | TR_LINE 16861_2 | TR_LINE 16861_2 | TR_LINE 16861_2 | TR_LINE 16861_2 | TR_LINE 16861_2 | TR_LINE 16861_2 | TR_LINE 16861_2 | TR_LINE 16861_2 | TR_LINE 16861_2
CA | 40001235 | 6102 | BOAT CREEK TO YARWUN | 6102_Boat Creek - Yarwun 66 kV | Loading (A) | 41.0412 | 33.5896 | 35.3046 | 40.1422 | 32.8587 | 34.536 | 55.5347 | 45.3932 | 47.7195 | 71.2493 | 58.1182 | 61.1027 | 71.2515 | 58.1199 | 61.1033
CA | 40001235 | 6102 | BOAT CREEK TO YARWUN | 6102_Boat Creek - Yarwun 66 kV | Loading (MVA) | 4.8156 | 3.9505 | 4.1468 | 4.7105 | 3.8648 | 4.0568 | 6.5076 | 5.3325 | 5.5985 | 8.3362 | 6.8191 | 7.1612 | 8.3362 | 6.8191 | 7.1612
CA | 40001235 | 6102 | BOAT CREEK TO YARWUN | 6102_Boat Creek - Yarwun 66 kV | Loading (MW) | 3.7597 | 3.0999 | 3.2499 | 3.6798 | 3.0342 | 3.181 | 5.0395 | 4.1529 | 4.3535 | 6.4019 | 5.2733 | 5.5277 | 6.4019 | 5.2733 | 5.5277
CA | 40001235 | 6102 | BOAT CREEK TO YARWUN | 6102_Boat Creek - Yarwun 66 kV | Power Factor | 0.78074 | 0.7847 | 0.78371 | 0.78118 | 0.78508 | 0.7841 | 0.77441 | 0.7788 | 0.77761 | 0.76797 | 0.77331 | 0.77189 | 0.76797 | 0.77331 | 0.77189
CA | 40001235 | 6102 | BOAT CREEK TO YARWUN | 6102_Boat Creek - Yarwun 66 kV | Rating (A) | 740 | 807 | 662 | 740 | 807 | 662 | 740 | 807 | 662 | 740 | 807 | 662 | 740 | 807 | 662
CA | 40001235 | 6102 | BOAT CREEK TO YARWUN | 6102_Boat Creek - Yarwun 66 kV | Time | 15:00 | 18:30 | 7:30 | 15:00 | 18:30 | 7:30 | 15:00 | 18:30 | 7:30 | 15:00 | 18:30 | 7:30 | 15:00 | 18:30 | 7:30
CA | 40001235 | 6102 | BOAT CREEK TO YARWUN | 6102_Boat Creek - Yarwun 66 kV | Voltage at Constrained Conductor | 67.7432 | 67.9024 | 67.814 | 67.75 | 67.9077 | 67.8196 | 67.6542 | 67.8236 | 67.7357 | 67.5499 | 67.7417 | 67.6652 | 67.548 | 67.7398 | 67.6645
CA | 40001238 | 6007 | From T26 to COSS | 6007_Biloela - Coominglah Tee 66 kV | % of Rated A | 39.226 | 35.9453 | 30.1953 | 38.6363 | 35.3834 | 29.7621 | 38.6336 | 35.3816 | 29.7612 | 38.6347 | 35.3814 | 29.7661 | 39.2311 | 35.9441 | 30.1997
CA | 40001238 | 6007 | From T26 to COSS | 6007_Biloela - Coominglah Tee 66 kV | Limiting Line Name | TR_LINE 18121_1 | TR_LINE 18121_1 | TR_LINE 18121_1 | TR_LINE 18121_1 | TR_LINE 18121_1 | TR_LINE 18121_1 | TR_LINE 18121_1 | TR_LINE 18121_1 | TR_LINE 18121_1 | TR_LINE 18121_1 | TR_LINE 18121_1 | TR_LINE 18121_1 | TR_LINE 18121_1 | TR_LINE 18121_1 | TR_LINE 18121_1
CA | 40001238 | 6007 | From T26 to COSS | 6007_Biloela - Coominglah Tee 66 kV | Loading (A) | 51.7783 | 60.0286 | 48.0105 | 50.9999 | 59.0903 | 47.3218 | 50.9963 | 59.0873 | 47.3202 | 50.9978 | 59.087 | 47.3281 | 51.785 | 60.0266 | 48.0175
CA | 40001238 | 6007 | From T26 to COSS | 6007_Biloela - Coominglah Tee 66 kV | Loading (MVA) | 6.1472 | 7.1283 | 5.7857 | 6.0553 | 7.0178 | 5.7032 | 6.0554 | 7.0178 | 5.7032 | 6.0554 | 7.0178 | 5.7031 | 6.1472 | 7.1283 | 5.7856
CA | 40001238 | 6007 | From T26 to COSS | 6007_Biloela - Coominglah Tee 66 kV | Loading (MW) | 6.0719 | 7.0977 | 5.6808 | 5.9749 | 6.9837 | 5.5926 | 5.9749 | 6.9836 | 5.5926 | 5.9749 | 6.9836 | 5.5927 | 6.072 | 7.0977 | 5.6808
CA | 40001238 | 6007 | From T26 to COSS | 6007_Biloela - Coominglah Tee 66 kV | Power Factor | 0.98774 | 0.9957 | 0.98186 | 0.98672 | 0.99513 | 0.98061 | 0.98671 | 0.99513 | 0.98061 | 0.98672 | 0.99513 | 0.98064 | 0.98776 | 0.9957 | 0.98189
CA | 40001238 | 6007 | From T26 to COSS | 6007_Biloela - Coominglah Tee 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
CA | 40001238 | 6007 | From T26 to COSS | 6007_Biloela - Coominglah Tee 66 kV | Time | 15:30 | 19:00 | 22:00 | 15:30 | 19:00 | 22:00 | 15:30 | 19:00 | 22:00 | 15:30 | 19:00 | 22:00 | 15:30 | 19:00 | 22:00
CA | 40001238 | 6007 | From T26 to COSS | 6007_Biloela - Coominglah Tee 66 kV | Voltage at Constrained Conductor | 68.5444 | 68.5599 | 69.5763 | 68.5502 | 68.5686 | 69.5821 | 68.5553 | 68.5719 | 69.5846 | 68.5532 | 68.5722 | 69.5716 | 68.5351 | 68.5621 | 69.5652
CA | 40001239 | 6008 | From T26 to WNSS | 6008_Biloela - Wowan 66 kV | % of Rated A | 38.5752 | 30.2412 | 21.8853 | 37.8538 | 29.6753 | 21.4857 | 37.8518 | 29.6743 | 21.485 | 37.8525 | 29.675 | 21.485 | 38.5841 | 30.2481 | 21.8848
CA | 40001239 | 6008 | From T26 to WNSS | 6008_Biloela - Wowan 66 kV | Limiting Line Name | TR_LINE 14892_1 | TR_LINE 14892_1 | TR_LINE 14892_1 | TR_LINE 14892_1 | TR_LINE 14892_1 | TR_LINE 14892_1 | TR_LINE 14892_1 | TR_LINE 14892_1 | TR_LINE 14892_1 | TR_LINE 14892_1 | TR_LINE 14892_1 | TR_LINE 14892_1 | TR_LINE 14892_1 | TR_LINE 14892_1 | TR_LINE 14892_1
CA | 40001239 | 6008 | From T26 to WNSS | 6008_Biloela - Wowan 66 kV | Loading (A) | 50.7951 | 50.3792 | 34.7061 | 49.8444 | 49.4358 | 34.0727 | 49.8418 | 49.4341 | 34.0715 | 49.8426 | 49.4352 | 34.0716 | 50.8068 | 50.3908 | 34.7053
CA | 40001239 | 6008 | From T26 to WNSS | 6008_Biloela - Wowan 66 kV | Loading (MVA) | 5.8754 | 5.8286 | 4.1221 | 5.7693 | 5.7234 | 4.0486 | 5.7692 | 5.7233 | 4.0486 | 5.7692 | 5.7234 | 4.0486 | 5.8755 | 5.8287 | 4.1221
CA | 40001239 | 6008 | From T26 to WNSS | 6008_Biloela - Wowan 66 kV | Loading (MW) | 5.7796 | 5.7347 | 4.0904 | 5.6778 | 5.6338 | 4.019 | 5.6778 | 5.6338 | 4.019 | 5.6778 | 5.6338 | 4.019 | 5.7796 | 5.7348 | 4.0904
CA | 40001239 | 6008 | From T26 to WNSS | 6008_Biloela - Wowan 66 kV | Power Factor | 0.98369 | 0.98389 | 0.99231 | 0.98415 | 0.98435 | 0.99268 | 0.98415 | 0.98435 | 0.99268 | 0.98415 | 0.98435 | 0.99268 | 0.98368 | 0.98388 | 0.99231
CA | 40001239 | 6008 | From T26 to WNSS | 6008_Biloela - Wowan 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
CA | 40001239 | 6008 | From T26 to WNSS | 6008_Biloela - Wowan 66 kV | Time | 16:30 | 17:00 | 8:30 | 16:30 | 17:00 | 8:30 | 16:30 | 17:00 | 8:30 | 16:30 | 17:00 | 8:30 | 16:30 | 17:00 | 8:30
CA | 40001239 | 6008 | From T26 to WNSS | 6008_Biloela - Wowan 66 kV | Voltage at Constrained Conductor | 66.7814 | 66.7967 | 68.5734 | 66.8257 | 66.8419 | 68.6024 | 66.829 | 66.8439 | 68.6045 | 66.8279 | 66.8426 | 68.6044 | 66.7673 | 66.7826 | 68.5748
CA | 40001243 | 6030 | From LMSS to MTSS | 6030_Littlemore - Monto 66 kV | % of Rated A | 5.276 | 4.108 | 4.3827 | 5.2793 | 4.1084 | 4.3853 | 5.2793 | 4.107 | 4.3852 | 5.2781 | 4.1071 | 4.3851 | 5.2713 | 4.0981 | 4.3796
CA | 40001243 | 6030 | From LMSS to MTSS | 6030_Littlemore - Monto 66 kV | Limiting Line Name | TR_LINE 19505_1 | TR_LINE 19505_1 | TR_LINE 19505_1 | TR_LINE 19505_1 | TR_LINE 19505_1 | TR_LINE 19505_1 | TR_LINE 19505_1 | TR_LINE 19505_1 | TR_LINE 19505_1 | TR_LINE 19505_1 | TR_LINE 19505_1 | TR_LINE 19505_1 | TR_LINE 19505_1 | TR_LINE 19505_1 | TR_LINE 19505_1
CA | 40001243 | 6030 | From LMSS to MTSS | 6030_Littlemore - Monto 66 kV | Loading (A) | 6.9644 | 6.8603 | 6.9685 | 6.9687 | 6.861 | 6.9725 | 6.9687 | 6.8587 | 6.9725 | 6.9671 | 6.8588 | 6.9723 | 6.9582 | 6.8438 | 6.9635
CA | 40001243 | 6030 | From LMSS to MTSS | 6030_Littlemore - Monto 66 kV | Loading (MVA) | 0.82916 | 0.80456 | 0.83015 | 0.83019 | 0.80472 | 0.8311 | 0.83018 | 0.80419 | 0.83109 | 0.82981 | 0.80421 | 0.83104 | 0.82768 | 0.80069 | 0.82895
CA | 40001243 | 6030 | From LMSS to MTSS | 6030_Littlemore - Monto 66 kV | Loading (MW) | 0.0015162 | 0.0014713 | 0.001518 | 0.0015181 | 0.0014715 | 0.0015198 | 0.0015181 | 0.0014706 | 0.0015198 | 0.0015174 | 0.0014706 | 0.0015197 | 0.0015135 | 0.0014642 | 0.0015159
CA | 40001243 | 6030 | From LMSS to MTSS | 6030_Littlemore - Monto 66 kV | Power Factor | 0.0018286 | 0.0018286 | 0.0018286 | 0.0018286 | 0.0018286 | 0.0018286 | 0.0018286 | 0.0018286 | 0.0018286 | 0.0018286 | 0.0018286 | 0.0018286 | 0.0018286 | 0.0018286 | 0.0018286
CA | 40001243 | 6030 | From LMSS to MTSS | 6030_Littlemore - Monto 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
CA | 40001243 | 6030 | From LMSS to MTSS | 6030_Littlemore - Monto 66 kV | Time | 9:00 | 21:30 | 8:30 | 9:00 | 21:30 | 8:30 | 9:00 | 21:30 | 8:30 | 9:00 | 21:30 | 8:30 | 9:00 | 21:30 | 8:30
CA | 40001243 | 6030 | From LMSS to MTSS | 6030_Littlemore - Monto 66 kV | Voltage at Constrained Conductor | 68.7376 | 67.7104 | 68.7786 | 68.7803 | 67.7169 | 68.8182 | 68.78 | 67.6947 | 68.8178 | 68.7647 | 67.6955 | 68.8155 | 68.6763 | 67.5473 | 68.729
CA | 40001244 | 6045 | From MTSS to COSS | 6045_Coominglah Tee - Monto 66 kV | % of Rated A | 31.6768 | 28.845 | 23.9488 | 31.099 | 28.2963 | 23.5265 | 31.0968 | 28.2949 | 23.5258 | 31.0977 | 28.2947 | 23.5296 | 31.6809 | 28.8441 | 23.9522
CA | 40001244 | 6045 | From MTSS to COSS | 6045_Coominglah Tee - Monto 66 kV | Limiting Line Name | TR_LINE 75765_1 | TR_LINE 75765_1 | TR_LINE 75765_1 | TR_LINE 75765_1 | TR_LINE 75765_1 | TR_LINE 75765_1 | TR_LINE 75765_1 | TR_LINE 75765_1 | TR_LINE 75765_1 | TR_LINE 75765_1 | TR_LINE 75765_1 | TR_LINE 75765_1 | TR_LINE 75765_1 | TR_LINE 75765_1 | TR_LINE 75765_1
CA | 40001244 | 6045 | From MTSS to COSS | 6045_Coominglah Tee - Monto 66 kV | Loading (A) | 41.8134 | 48.1712 | 38.0786 | 41.0506 | 47.2548 | 37.4072 | 41.0478 | 47.2524 | 37.406 | 41.0489 | 47.2522 | 37.4121 | 41.8187 | 48.1697 | 38.084
CA | 40001244 | 6045 | From MTSS to COSS | 6045_Coominglah Tee - Monto 66 kV | Loading (MVA) | 4.8381 | 5.5442 | 4.4863 | 4.7529 | 5.4432 | 4.4097 | 4.753 | 5.4432 | 4.4098 | 4.753 | 5.4432 | 4.4096 | 4.838 | 5.5442 | 4.4861
CA | 40001244 | 6045 | From MTSS to COSS | 6045_Coominglah Tee - Monto 66 kV | Loading (MW) | 4.7204 | 5.4648 | 4.3323 | 4.6288 | 5.3582 | 4.2486 | 4.6288 | 5.3581 | 4.2486 | 4.6288 | 5.3581 | 4.2487 | 4.7204 | 5.4647 | 4.3323
CA | 40001244 | 6045 | From MTSS to COSS | 6045_Coominglah Tee - Monto 66 kV | Power Factor | 0.97567 | 0.98568 | 0.96568 | 0.97389 | 0.98438 | 0.96347 | 0.97388 | 0.98437 | 0.96346 | 0.97388 | 0.98437 | 0.9635 | 0.97569 | 0.98567 | 0.96572
CA | 40001244 | 6045 | From MTSS to COSS | 6045_Coominglah Tee - Monto 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
CA | 40001244 | 6045 | From MTSS to COSS | 6045_Coominglah Tee - Monto 66 kV | Time | 15:30 | 18:30 | 22:00 | 15:30 | 18:30 | 22:00 | 15:30 | 18:30 | 22:00 | 15:30 | 18:30 | 22:00 | 15:30 | 18:30 | 22:00
CA | 40001244 | 6045 | From MTSS to COSS | 6045_Coominglah Tee - Monto 66 kV | Voltage at Constrained Conductor | 66.803 | 66.449 | 68.0213 | 66.847 | 66.5037 | 68.061 | 66.8523 | 66.5073 | 68.0636 | 66.8502 | 66.5076 | 68.05 | 66.7933 | 66.4512 | 68.0097
CA | 40216264 | 6080 | BBBS TO BKSS | 6080_Barcaldine - Blackall 66 kV | % of Rated A | 10.3327 | 10.7818 | 8.852 | 10.0883 | 10.5401 | 8.6853 | 10.0765 | 10.5285 | 8.6852 | 10.0778 | 10.5298 | 8.6856 | 10.0957 | 10.5452 | 8.6869
CA | 40216264 | 6080 | BBBS TO BKSS | 6080_Barcaldine - Blackall 66 kV | Limiting Line Name | TR_LINE 225287_1 | TR_LINE 22558_1 | TR_LINE 22558_1 | TR_LINE 225287_1 | TR_LINE 22558_1 | TR_LINE 22558_1 | TR_LINE 225287_1 | TR_LINE 22558_1 | TR_LINE 22558_1 | TR_LINE 225287_1 | TR_LINE 22558_1 | TR_LINE 22558_1 | TR_LINE 225287_1 | TR_LINE 22558_1 | TR_LINE 22558_1
CA | 40216264 | 6080 | BBBS TO BKSS | 6080_Barcaldine - Blackall 66 kV | Loading (A) | 38.6443 | 41.941 | 29.9199 | 37.7303 | 41.001 | 29.3563 | 37.6862 | 40.9559 | 29.3561 | 37.691 | 40.961 | 29.3575 | 37.7579 | 41.0209 | 29.3618
CA | 40216264 | 6080 | BBBS TO BKSS | 6080_Barcaldine - Blackall 66 kV | Loading (MVA) | 4.4714 | 4.9301 | 3.5254 | 4.3772 | 4.8307 | 3.4626 | 4.3773 | 4.8312 | 3.4626 | 4.3773 | 4.8312 | 3.4625 | 4.3772 | 4.8305 | 3.4623
CA | 40216264 | 6080 | BBBS TO BKSS | 6080_Barcaldine - Blackall 66 kV | Loading (MW) | 4.4475 | 4.847 | 3.3202 | 4.3509 | 4.7399 | 3.248 | 4.3507 | 4.7395 | 3.248 | 4.3507 | 4.7395 | 3.248 | 4.351 | 4.74 | 3.248
CA | 40216264 | 6080 | BBBS TO BKSS | 6080_Barcaldine - Blackall 66 kV | Power Factor | 0.99466 | 0.98313 | 0.9418 | 0.99398 | 0.9812 | 0.93803 | 0.99391 | 0.98101 | 0.93802 | 0.99392 | 0.98103 | 0.93805 | 0.99402 | 0.98128 | 0.93812
CA | 40216264 | 6080 | BBBS TO BKSS | 6080_Barcaldine - Blackall 66 kV | Rating (A) | 374 | 389 | 338 | 374 | 389 | 338 | 374 | 389 | 338 | 374 | 389 | 338 | 374 | 389 | 338
CA | 40216264 | 6080 | BBBS TO BKSS | 6080_Barcaldine - Blackall 66 kV | Time | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00
CA | 40216264 | 6080 | BBBS TO BKSS | 6080_Barcaldine - Blackall 66 kV | Voltage at Constrained Conductor | 66.8032 | 67.8671 | 68.0279 | 66.9806 | 68.0227 | 68.0985 | 67.0606 | 68.1053 | 68.0993 | 67.0519 | 68.0959 | 68.0948 | 66.9307 | 67.9864 | 68.0801
CA | 40218335 | 6046 | MMLS-MMSS-WOWA | 6046_Mt Morgan - Wowan 66 kV | % of Rated A | 3.5389 | 2.9373 | 3.1368 | 3.536 | 2.938 | 3.1573 | 43.2821 | 34.3405 | 36.9355 | 86.7166 | 68.8643 | 73.6136 | 86.7755 | 68.1809 | 73.6492
CA | 40218335 | 6046 | MMLS-MMSS-WOWA | 6046_Mt Morgan - Wowan 66 kV | Limiting Line Name | TR_LINE 15219_3 | TR_LINE 22233_1 | TR_LINE 22233_1 | TR_LINE 15219_3 | TR_LINE 22233_1 | TR_LINE 22233_1 | TR_LINE 76097_1 | TR_LINE 76097_1 | TR_LINE 76097_1 | TR_LINE 76097_1 | TR_LINE 76097_1 | TR_LINE 76097_1 | TR_LINE 76097_1 | TR_LINE 76097_1 | TR_LINE 76097_1
CA | 40218335 | 6046 | MMLS-MMSS-WOWA | 6046_Mt Morgan - Wowan 66 kV | Loading (A) | 4.6714 | 4.9053 | 4.9875 | 4.6675 | 4.9065 | 5.02 | 57.1323 | 57.3486 | 58.7275 | 114.4635 | 115.001 | 117.0433 | 114.5413 | 113.8597 | 117.0998
CA | 40218335 | 6046 | MMLS-MMSS-WOWA | 6046_Mt Morgan - Wowan 66 kV | Loading (MVA) | 0.55694 | 0.58114 | 0.5952 | 0.55602 | 0.58142 | 0.60281 | 6.6256 | 6.6257 | 6.7993 | 12.8776 | 12.8778 | 13.215 | 12.8776 | 12.8773 | 13.215
CA | 40218335 | 6046 | MMLS-MMSS-WOWA | 6046_Mt Morgan - Wowan 66 kV | Loading (MW) | 0.00044363 | 0.032796 | 0.024585 | 0.00044289 | 0.032796 | 0.024591 | 5.4703 | 5.4703 | 5.6136 | 10.6266 | 10.6268 | 10.905 | 10.6267 | 10.6265 | 10.905
CA | 40218335 | 6046 | MMLS-MMSS-WOWA | 6046_Mt Morgan - Wowan 66 kV | Power Factor | 0.00079654 | 0.056433 | 0.041306 | 0.00079654 | 0.056407 | 0.040794 | 0.82564 | 0.82563 | 0.82561 | 0.82521 | 0.8252 | 0.8252 | 0.82521 | 0.82521 | 0.8252
CA | 40218335 | 6046 | MMLS-MMSS-WOWA | 6046_Mt Morgan - Wowan 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
CA | 40218335 | 6046 | MMLS-MMSS-WOWA | 6046_Mt Morgan - Wowan 66 kV | Time | 11:30 | 21:00 | 0:30 | 12:00 | 21:00 | 1:30 | 13:30 | 17:00 | 8:30 | 13:30 | 17:00 | 8:30 | 13:30 | 17:00 | 8:30
CA | 40218335 | 6046 | MMLS-MMSS-WOWA | 6046_Mt Morgan - Wowan 66 kV | Voltage at Constrained Conductor | 68.8332 | 68.4003 | 68.9008 | 68.7762 | 68.4159 | 69.3286 | 66.9547 | 66.703 | 66.8436 | 64.9539 | 64.6516 | 65.1869 | 64.91 | 65.2971 | 65.1556
CA | 82575918 | 6109 | 6109 CLINTON INDUSTRIAL 66KV FEEDER | 6109_Gladstone North - Clinton 66 kV | % of Rated A | 65.9699 | 46.6148 | 40.8501 | 65.8245 | 46.2348 | 40.8279 | 65.3384 | 45.9412 | 40.6089 | 65.3287 | 45.9786 | 40.6611 | 64.4058 | 46.5502 | 40.9315
CA | 82575918 | 6109 | 6109 CLINTON INDUSTRIAL 66KV FEEDER | 6109_Gladstone North - Clinton 66 kV | Limiting Line Name | TR_LINE 60722_1 | TR_LINE 61921_1 | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 61921_1 | TR_LINE 60722_1
CA | 82575918 | 6109 | 6109 CLINTON INDUSTRIAL 66KV FEEDER | 6109_Gladstone North - Clinton 66 kV | Loading (A) | 239.4708 | 254.0426 | 188.3192 | 238.9429 | 251.9798 | 188.2165 | 237.1783 | 250.3797 | 187.2072 | 237.1433 | 250.5832 | 187.4478 | 233.7929 | 253.691 | 188.694
CA | 82575918 | 6109 | 6109 CLINTON INDUSTRIAL 66KV FEEDER | 6109_Gladstone North - Clinton 66 kV | Loading (MVA) | 28.314 | 30.283 | 22.2984 | 28.2608 | 29.8688 | 22.2914 | 28.052 | 29.6788 | 22.1713 | 28.051 | 29.7058 | 22.1971 | 27.7261 | 30.2347 | 22.3375
CA | 82575918 | 6109 | 6109 CLINTON INDUSTRIAL 66KV FEEDER | 6109_Gladstone North - Clinton 66 kV | Loading (MW) | 28.2372 | 30.2392 | 21.9463 | 28.1567 | 29.2305 | 21.8963 | 27.9462 | 29.0353 | 21.7763 | 27.9348 | 29.0397 | 21.7902 | 27.0378 | 30.1957 | 21.9817
CA | 82575918 | 6109 | 6109 CLINTON INDUSTRIAL 66KV FEEDER | 6109_Gladstone North - Clinton 66 kV | Power Factor | 0.99729 | 0.99855 | 0.98421 | 0.99632 | 0.97863 | 0.98228 | 0.99623 | 0.97832 | 0.98219 | 0.99586 | 0.97758 | 0.98167 | 0.97518 | 0.99871 | 0.98407
CA | 82575918 | 6109 | 6109 CLINTON INDUSTRIAL 66KV FEEDER | 6109_Gladstone North - Clinton 66 kV | Rating (A) | 363 | 545 | 461 | 363 | 545 | 461 | 363 | 545 | 461 | 363 | 545 | 461 | 363 | 545 | 461
CA | 82575918 | 6109 | 6109 CLINTON INDUSTRIAL 66KV FEEDER | 6109_Gladstone North - Clinton 66 kV | Time | 16:30 | 17:00 | 22:00 | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00 | 16:30 | 17:00 | 22:00
CA | 82575918 | 6109 | 6109 CLINTON INDUSTRIAL 66KV FEEDER | 6109_Gladstone North - Clinton 66 kV | Voltage at Constrained Conductor | 68.2634 | 68.8228 | 68.3625 | 68.2856 | 68.4372 | 68.3784 | 68.2856 | 68.4364 | 68.3766 | 68.2932 | 68.443 | 68.3683 | 68.4694 | 68.8081 | 68.3463
CA | 82588694 | 7290 | Boat Creek - Yarwun 132 kV | 7290_Boat Creek - Yarwun 132 kV | % of Rated A | 12.0401 | 9.9298 | 12.5101 | 12.0152 | 9.912 | 12.4918 | 12.4371 | 10.2122 | 12.8487 | 12.868 | 10.5164 | 13.2239 | 12.8684 | 10.5184 | 13.224
CA | 82588694 | 7290 | Boat Creek - Yarwun 132 kV | 7290_Boat Creek - Yarwun 132 kV | Limiting Line Name | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1
CA | 82588694 | 7290 | Boat Creek - Yarwun 132 kV | 7290_Boat Creek - Yarwun 132 kV | Loading (A) | 107.0363 | 97.7094 | 104.96 | 106.8154 | 97.5341 | 104.8058 | 110.5661 | 100.4878 | 107.8006 | 114.3969 | 103.481 | 110.9483 | 114.4002 | 103.5015 | 110.9492
CA | 82588694 | 7290 | Boat Creek - Yarwun 132 kV | 7290_Boat Creek - Yarwun 132 kV | Loading (MVA) | 25.4425 | 23.2382 | 24.9435 | 25.3909 | 23.1982 | 24.9073 | 26.274 | 23.8919 | 25.6138 | 27.1733 | 24.5955 | 26.3552 | 27.1733 | 24.5958 | 26.3552
CA | 82588694 | 7290 | Boat Creek - Yarwun 132 kV | 7290_Boat Creek - Yarwun 132 kV | Loading (MW) | 23.2769 | 21.3756 | 22.9216 | 23.2369 | 21.3438 | 22.8929 | 23.9175 | 21.8856 | 23.4018 | 24.5997 | 22.4285 | 23.9705 | 24.5998 | 22.4285 | 23.9705
CA | 82588694 | 7290 | Boat Creek - Yarwun 132 kV | 7290_Boat Creek - Yarwun 132 kV | Power Factor | 0.91488 | 0.91985 | 0.91894 | 0.91517 | 0.92006 | 0.91912 | 0.91031 | 0.91603 | 0.91364 | 0.90529 | 0.91189 | 0.90952 | 0.90529 | 0.91188 | 0.90952
CA | 82588694 | 7290 | Boat Creek - Yarwun 132 kV | 7290_Boat Creek - Yarwun 132 kV | Rating (A) | 889 | 984 | 839 | 889 | 984 | 839 | 889 | 984 | 839 | 889 | 984 | 839 | 889 | 984 | 839
CA | 82588694 | 7290 | Boat Creek - Yarwun 132 kV | 7290_Boat Creek - Yarwun 132 kV | Time | 15:00 | 17:00 | 6:30 | 15:00 | 17:00 | 6:30 | 15:00 | 17:00 | 7:00 | 15:00 | 17:00 | 7:00 | 15:00 | 17:00 | 7:00
CA | 82588694 | 7290 | Boat Creek - Yarwun 132 kV | 7290_Boat Creek - Yarwun 132 kV | Voltage at Constrained Conductor | 137.236 | 137.3107 | 137.2058 | 137.241 | 137.3209 | 137.2085 | 137.1966 | 137.2704 | 137.1806 | 137.1408 | 137.2255 | 137.1463 | 137.1371 | 137.1996 | 137.1453
CA | 82588698 | 7291 | Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | % of Rated A | 12.0968 | 9.9766 | 12.569 | 12.0718 | 9.9587 | 12.5506 | 12.4957 | 10.2602 | 12.9092 | 12.9286 | 10.5659 | 13.2861 | 12.929 | 10.568 | 13.2862
CA | 82588698 | 7291 | Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | Limiting Line Name | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1
CA | 82588698 | 7291 | Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | Loading (A) | 107.5402 | 98.1694 | 105.4541 | 107.3182 | 97.9932 | 105.2992 | 111.0865 | 100.9609 | 108.3081 | 114.9354 | 103.9682 | 111.4706 | 114.9387 | 103.9887 | 111.4715
CA | 82588698 | 7291 | Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | Loading (MVA) | 25.5629 | 23.3481 | 25.0615 | 25.5111 | 23.3079 | 25.0252 | 26.3984 | 24.005 | 25.7351 | 27.302 | 24.7119 | 26.48 | 27.302 | 24.7122 | 26.48
CA | 82588698 | 7291 | Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | Loading (MW) | 23.3847 | 21.4746 | 23.0277 | 23.3445 | 21.4426 | 22.9989 | 24.0282 | 21.9869 | 23.5101 | 24.7135 | 22.5322 | 24.0814 | 24.7135 | 22.5322 | 24.0814
CA | 82588698 | 7291 | Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | Power Factor | 0.91479 | 0.91976 | 0.91885 | 0.91507 | 0.91997 | 0.91903 | 0.91021 | 0.91593 | 0.91354 | 0.90519 | 0.91179 | 0.90942 | 0.90519 | 0.91179 | 0.90942
CA | 82588698 | 7291 | Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | Rating (A) | 889 | 984 | 839 | 889 | 984 | 839 | 889 | 984 | 839 | 889 | 984 | 839 | 889 | 984 | 839
CA | 82588698 | 7291 | Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | Time | 15:00 | 17:00 | 6:30 | 15:00 | 17:00 | 6:30 | 15:00 | 17:00 | 7:00 | 15:00 | 17:00 | 7:00 | 15:00 | 17:00 | 7:00
CA | 82588698 | 7291 | Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | Voltage at Constrained Conductor | 137.2395 | 137.3139 | 137.2093 | 137.2445 | 137.3241 | 137.212 | 137.2004 | 137.2737 | 137.1843 | 137.1448 | 137.229 | 137.1501 | 137.1411 | 137.2031 | 137.1491
CA | 82747684 | 6274 | MINIERE MINING | 6274 Miniere Mining | % of Rated A | 0.084642 | 0.057428 | 0.058202 | 0.084651 | 0.057432 | 0.058206 | 0.084633 | 0.057423 | 0.0582 | 0.084632 | 0.057423 | 0.0582 | 0.084626 | 0.057424 | 0.058198
CA | 82747684 | 6274 | MINIERE MINING | 6274 Miniere Mining | Limiting Line Name | TR_LINE 22572_1 | TR_LINE 22572_1 | TR_LINE 22572_1 | TR_LINE 22572_1 | TR_LINE 22572_1 | TR_LINE 22572_1 | TR_LINE 22572_1 | TR_LINE 22572_1 | TR_LINE 22572_1 | TR_LINE 22572_1 | TR_LINE 22572_1 | TR_LINE 22572_1 | TR_LINE 22572_1 | TR_LINE 22572_1 | TR_LINE 22572_1
CA | 82747684 | 6274 | MINIERE MINING | 6274 Miniere Mining | Loading (A) | 0.12104 | 0.12117 | 0.12106 | 0.12105 | 0.12118 | 0.12107 | 0.12102 | 0.12116 | 0.12106 | 0.12102 | 0.12116 | 0.12106 | 0.12102 | 0.12116 | 0.12105
CA | 82747684 | 6274 | MINIERE MINING | 6274 Miniere Mining | Loading (MVA) | 0.014431 | 0.014463 | 0.014436 | 0.014434 | 0.014465 | 0.014438 | 0.014427 | 0.01446 | 0.014435 | 0.014427 | 0.01446 | 0.014435 | 0.014425 | 0.014461 | 0.014434
CA | 82747684 | 6274 | MINIERE MINING | 6274 Miniere Mining | Loading (MW) | 6.4317e-08 | 6.4441e-08 | 6.4324e-08 | 6.4323e-08 | 6.4439e-08 | 6.4341e-08 | 6.426e-08 | 6.4414e-08 | 6.4326e-08 | 6.43e-08 | 6.4463e-08 | 6.4331e-08 | 6.4277e-08 | 6.4412e-08 | 6.4308e-08
CA | 82747684 | 6274 | MINIERE MINING | 6274 Miniere Mining | Power Factor | 4.4569e-06 | 4.4557e-06 | 4.4558e-06 | 4.4564e-06 | 4.4548e-06 | 4.4565e-06 | 4.454e-06 | 4.4545e-06 | 4.4563e-06 | 4.4569e-06 | 4.4579e-06 | 4.4567e-06 | 4.4558e-06 | 4.4543e-06 | 4.4553e-06
CA | 82747684 | 6274 | MINIERE MINING | 6274 Miniere Mining | Rating (A) | 143 | 211 | 208 | 143 | 211 | 208 | 143 | 211 | 208 | 143 | 211 | 208 | 143 | 211 | 208
CA | 82747684 | 6274 | MINIERE MINING | 6274 Miniere Mining | Time | 16:30 | 21:00 | 23:30 | 16:30 | 21:00 | 23:30 | 16:30 | 21:00 | 23:30 | 16:30 | 21:00 | 23:30 | 16:30 | 21:00 | 23:30
CA | 82747684 | 6274 | MINIERE MINING | 6274 Miniere Mining | Voltage at Constrained Conductor | 68.8341 | 68.9103 | 68.8465 | 68.8413 | 68.9159 | 68.8509 | 68.8261 | 68.9049 | 68.8436 | 68.8257 | 68.9046 | 68.8435 | 68.8211 | 68.9054 | 68.8416
CA | 82860724 | 6022 | GSBS TO CALLIOPE | 6022_Gladstone South - Calliope 66 kV | % of Rated A | 18.6165 | 25.958 | 22.0639 | 19.2211 | 26.4039 | 22.3616 | 19.1589 | 26.3751 | 22.3362 | 19.3327 | 26.5301 | 22.4582 | 19.498 | 27.0629 | 22.8817
CA | 82860724 | 6022 | GSBS TO CALLIOPE | 6022_Gladstone South - Calliope 66 kV | Limiting Line Name | TR_LINE 72664_1 | TR_LINE 72664_1 | TR_LINE 72664_1 | TR_LINE 72664_1 | TR_LINE 72664_1 | TR_LINE 72664_1 | TR_LINE 72664_1 | TR_LINE 72664_1 | TR_LINE 72664_1 | TR_LINE 72664_1 | TR_LINE 72664_1 | TR_LINE 72664_1 | TR_LINE 72664_1 | TR_LINE 72664_1 | TR_LINE 72664_1
CA | 82860724 | 6022 | GSBS TO CALLIOPE | 6022_Gladstone South - Calliope 66 kV | Loading (A) | 115.9798 | 172.3588 | 132.1608 | 119.7464 | 175.3198 | 133.9438 | 119.3588 | 175.1282 | 133.7915 | 120.4416 | 176.1575 | 134.5227 | 121.4714 | 179.6957 | 137.0593
CA | 82860724 | 6022 | GSBS TO CALLIOPE | 6022_Gladstone South - Calliope 66 kV | Loading (MVA) | 13.5591 | 20.0914 | 15.4131 | 13.9942 | 20.4325 | 15.6202 | 13.9447 | 20.4037 | 15.5989 | 14.074 | 20.5271 | 15.6831 | 14.308 | 20.9039 | 15.9624
CA | 82860724 | 6022 | GSBS TO CALLIOPE | 6022_Gladstone South - Calliope 66 kV | Loading (MW) | 13.3939 | 19.3524 | 14.9007 | 13.8037 | 19.6699 | 15.0964 | 13.7301 | 19.6011 | 15.0494 | 13.8805 | 19.7596 | 15.1563 | 14.0823 | 20.0603 | 15.3839
CA | 82860724 | 6022 | GSBS TO CALLIOPE | 6022_Gladstone South - Calliope 66 kV | Power Factor | 0.98782 | 0.96322 | 0.96676 | 0.98639 | 0.96268 | 0.96647 | 0.98461 | 0.96066 | 0.96477 | 0.98625 | 0.96261 | 0.96641 | 0.98423 | 0.95964 | 0.96376
CA | 82860724 | 6022 | GSBS TO CALLIOPE | 6022_Gladstone South - Calliope 66 kV | Rating (A) | 623 | 664 | 599 | 623 | 664 | 599 | 623 | 664 | 599 | 623 | 664 | 599 | 623 | 664 | 599
CA | 82860724 | 6022 | GSBS TO CALLIOPE | 6022_Gladstone South - Calliope 66 kV | Time | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00
CA | 82860724 | 6022 | GSBS TO CALLIOPE | 6022_Gladstone South - Calliope 66 kV | Voltage at Constrained Conductor | 67.4973 | 67.3001 | 67.3327 | 67.472 | 67.2868 | 67.3293 | 67.4517 | 67.2654 | 67.3141 | 67.4654 | 67.2768 | 67.3096 | 68.0056 | 67.163 | 67.2402
CA | 82999218 | 6103 | FISHERMANS LANDING | 6103_Fisherman Landing-Boat Creek 66 kV | % of Rated A | 83.124 | 76.3809 | 85.788 | 83.1197 | 76.3727 | 85.7838 | 83.193 | 76.4452 | 86.0125 | 83.2638 | 76.5161 | 86.0799 | 83.2871 | 76.5312 | 86.0803
CA | 82999218 | 6103 | FISHERMANS LANDING | 6103_Fisherman Landing-Boat Creek 66 kV | Limiting Line Name | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1
CA | 82999218 | 6103 | FISHERMANS LANDING | 6103_Fisherman Landing-Boat Creek 66 kV | Loading (A) | 232.746 | 234.4881 | 235.9157 | 232.7338 | 234.4627 | 235.9041 | 232.939 | 234.6856 | 236.5329 | 233.1374 | 234.9031 | 236.7185 | 233.2025 | 234.9493 | 236.7196
CA | 82999218 | 6103 | FISHERMANS LANDING | 6103_Fisherman Landing-Boat Creek 66 kV | Loading (MVA) | 27.1709 | 27.3827 | 27.5037 | 27.1709 | 27.3827 | 27.5037 | 27.1709 | 27.3827 | 27.347 | 27.1709 | 27.3827 | 27.347 | 27.1709 | 27.3827 | 27.347
CA | 82999218 | 6103 | FISHERMANS LANDING | 6103_Fisherman Landing-Boat Creek 66 kV | Loading (MW) | 26.0565 | 26.2596 | 26.3757 | 26.0565 | 26.2596 | 26.3757 | 26.0565 | 26.2596 | 26.2254 | 26.0565 | 26.2596 | 26.2254 | 26.0565 | 26.2596 | 26.2254
CA | 82999218 | 6103 | FISHERMANS LANDING | 6103_Fisherman Landing-Boat Creek 66 kV | Power Factor | 0.95898 | 0.95898 | 0.95898 | 0.95898 | 0.95898 | 0.95898 | 0.95898 | 0.95898 | 0.95898 | 0.95898 | 0.95898 | 0.95898 | 0.95898 | 0.95898 | 0.95898
CA | 82999218 | 6103 | FISHERMANS LANDING | 6103_Fisherman Landing-Boat Creek 66 kV | Rating (A) | 280 | 307 | 275 | 280 | 307 | 275 | 280 | 307 | 275 | 280 | 307 | 275 | 280 | 307 | 275
CA | 82999218 | 6103 | FISHERMANS LANDING | 6103_Fisherman Landing-Boat Creek 66 kV | Time | 16:30 | 17:00 | 6:30 | 16:30 | 17:00 | 6:30 | 16:30 | 17:00 | 6:00 | 16:30 | 17:00 | 6:00 | 16:30 | 17:00 | 6:00
CA | 82999218 | 6103 | FISHERMANS LANDING | 6103_Fisherman Landing-Boat Creek 66 kV | Voltage at Constrained Conductor | 67.4002 | 67.4209 | 67.3092 | 67.4037 | 67.4282 | 67.3125 | 67.3443 | 67.3642 | 66.751 | 67.287 | 67.3018 | 66.6987 | 67.2683 | 67.2886 | 66.6984
CA | 83878739 | 6298 | TANB to YPSS | 6298_Tanby - Yeppoon 66 kV | % of Rated A | 15.7881 | 14.9121 | 13.165 | 15.8142 | 14.8456 | 12.97 | 15.4926 | 14.6304 | 13.0178 | 15.187 | 14.3521 | 12.8537 | 15.3249 | 14.4683 | 12.9557
CA | 83878739 | 6298 | TANB to YPSS | 6298_Tanby - Yeppoon 66 kV | Limiting Line Name | TR_LINE 22239_1 | TR_LINE 22239_1 | TR_LINE 22239_1 | TR_LINE 22239_1 | TR_LINE 22239_1 | TR_LINE 112499_1 | TR_LINE 22239_1 | TR_LINE 22239_1 | TR_LINE 22239_1 | TR_LINE 22239_1 | TR_LINE 22239_1 | TR_LINE 22239_1 | TR_LINE 22239_1 | TR_LINE 22239_1 | TR_LINE 22239_1
CA | 83878739 | 6298 | TANB to YPSS | 6298_Tanby - Yeppoon 66 kV | Loading (A) | 59.6786 | 61.8847 | 44.366 | 59.7771 | 61.6086 | 43.7089 | 58.5616 | 60.7158 | 43.8697 | 57.4065 | 59.5608 | 43.3168 | 57.9276 | 60.0431 | 43.6608
CA | 83878739 | 6298 | TANB to YPSS | 6298_Tanby - Yeppoon 66 kV | Loading (MVA) | 6.6478 | 6.8318 | 5.0062 | 6.6148 | 6.8066 | 4.9559 | 6.5076 | 6.6874 | 4.9499 | 6.3504 | 6.5277 | 4.8799 | 6.4137 | 6.5959 | 4.9088
CA | 83878739 | 6298 | TANB to YPSS | 6298_Tanby - Yeppoon 66 kV | Loading (MW) | 6.6051 | 6.7927 | 5.0039 | 6.5794 | 6.7698 | 4.9559 | 6.4705 | 6.6536 | 4.9482 | 6.3235 | 6.4988 | 4.8789 | 6.3834 | 6.5658 | 4.9076
CA | 83878739 | 6298 | TANB to YPSS | 6298_Tanby - Yeppoon 66 kV | Power Factor | 0.99358 | 0.99428 | 0.99954 | 0.99465 | 0.99459 | 0.99999 | 0.99431 | 0.99495 | 0.99967 | 0.99576 | 0.99558 | 0.99979 | 0.99528 | 0.99543 | 0.99974
CA | 83878739 | 6298 | TANB to YPSS | 6298_Tanby - Yeppoon 66 kV | Rating (A) | 378 | 415 | 337 | 378 | 415 | 337 | 378 | 415 | 337 | 378 | 415 | 337 | 378 | 415 | 337
CA | 83878739 | 6298 | TANB to YPSS | 6298_Tanby - Yeppoon 66 kV | Time | 16:30 | 17:30 | 22:30 | 16:30 | 17:30 | 22:30 | 16:30 | 17:30 | 22:30 | 16:30 | 17:30 | 22:30 | 16:30 | 18:30 | 22:30
CA | 83878739 | 6298 | TANB to YPSS | 6298_Tanby - Yeppoon 66 kV | Voltage at Constrained Conductor | 64.3131 | 63.7366 | 65.1476 | 63.8881 | 63.7863 | 65.4625 | 64.1573 | 63.5905 | 65.1429 | 63.8677 | 63.2756 | 65.0424 | 63.9239 | 63.4234 | 64.9123
CA | 83966216 | 6310 | LAKES CREEK | 6310_Lakes Creek - Berserker 66 kV | % of Rated A | 32.2975 | 38.3698 | 27.7564 | 32.2823 | 38.418 | 28.3991 | 34.1277 | 39.3024 | 28.1898 | 36.2931 | 41.425 | 28.864 | 37.6995 | 41.9675 | 29.5688
CA | 83966216 | 6310 | LAKES CREEK | 6310_Lakes Creek - Berserker 66 kV | Limiting Line Name | TR_CABLE 51_1 | TR_CABLE 51_1 | TR_LINE 20950_1 | TR_CABLE 51_1 | TR_CABLE 51_1 | TR_CABLE 51_1 | TR_CABLE 51_1 | TR_CABLE 51_1 | TR_LINE 20950_1 | TR_CABLE 51_1 | TR_CABLE 51_1 | TR_LINE 20950_1 | TR_CABLE 51_1 | TR_CABLE 51_1 | TR_LINE 20950_1
CA | 83966216 | 6310 | LAKES CREEK | 6310_Lakes Creek - Berserker 66 kV | Loading (A) | 120.1468 | 142.7358 | 103.254 | 120.09 | 142.9151 | 105.6448 | 126.955 | 146.2048 | 104.8662 | 135.0103 | 154.1011 | 107.3739 | 140.2422 | 156.119 | 109.9958
CA | 83966216 | 6310 | LAKES CREEK | 6310_Lakes Creek - Berserker 66 kV | Loading (MVA) | 14.153 | 16.685 | 12.1938 | 14.0587 | 16.7157 | 12.47 | 14.9172 | 17.1523 | 12.384 | 15.8023 | 18.01 | 12.671 | 16.4495 | 18.4118 | 12.9712
CA | 83966216 | 6310 | LAKES CREEK | 6310_Lakes Creek - Berserker 66 kV | Loading (MW) | 14.1452 | 16.6753 | 12.1482 | 14.0561 | 16.7061 | 12.4538 | 14.8916 | 17.0809 | 12.3458 | 15.7454 | 17.8941 | 12.6434 | 16.3005 | 18.294 | 12.9499
CA | 83966216 | 6310 | LAKES CREEK | 6310_Lakes Creek - Berserker 66 kV | Power Factor | 0.99945 | 0.99942 | 0.99626 | 0.99982 | 0.99943 | 0.9987 | 0.99828 | 0.99584 | 0.99692 | 0.9964 | 0.99357 | 0.99782 | 0.99094 | 0.9936 | 0.99836
CA | 83966216 | 6310 | LAKES CREEK | 6310_Lakes Creek - Berserker 66 kV | Rating (A) | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372
CA | 83966216 | 6310 | LAKES CREEK | 6310_Lakes Creek - Berserker 66 kV | Time | 16:30 | 18:00 | 22:30 | 16:30 | 18:00 | 22:30 | 16:30 | 17:30 | 22:30 | 16:30 | 17:30 | 22:30 | 16:30 | 17:30 | 22:30
CA | 83966216 | 6310 | LAKES CREEK | 6310_Lakes Creek - Berserker 66 kV | Voltage at Constrained Conductor | 68.0105 | 67.489 | 68.1823 | 67.5891 | 67.5282 | 68.1489 | 67.8387 | 67.7331 | 68.1812 | 67.5759 | 67.4757 | 68.1322 | 67.7195 | 68.0893 | 68.0838
CA | 84873218 | 7450 | ROLLESTON | 7450_Memooloo - Rolleston 132 kV | % of Rated A | 10.8402 | 10.9862 | 12.7563 | 10.8402 | 10.9862 | 12.7563 | 11.2745 | 11.466 | 13.075 | 11.3181 | 11.5141 | 13.1069 | 11.3181 | 11.5141 | 13.1069
CA | 84873218 | 7450 | ROLLESTON | 7450_Memooloo - Rolleston 132 kV | Limiting Line Name | TR_LINE 200891_1 | TR_LINE 200891_1 | TR_LINE 200891_1 | TR_LINE 200891_1 | TR_LINE 200891_1 | TR_LINE 200891_1 | TR_LINE 200891_1 | TR_LINE 200891_1 | TR_LINE 200891_1 | TR_LINE 200891_1 | TR_LINE 200891_1 | TR_LINE 200891_1 | TR_LINE 200891_1 | TR_LINE 200891_1 | TR_LINE 200891_1
CA | 84873218 | 7450 | ROLLESTON | 7450_Memooloo - Rolleston 132 kV | Loading (A) | 76.4235 | 80.7485 | 83.1711 | 76.4235 | 80.7485 | 83.1711 | 79.4856 | 84.275 | 85.249 | 79.7924 | 84.6285 | 85.4571 | 79.7924 | 84.6285 | 85.4571
CA | 84873218 | 7450 | ROLLESTON | 7450_Memooloo - Rolleston 132 kV | Loading (MVA) | 18.3328 | 19.3322 | 19.8845 | 18.3328 | 19.3322 | 19.8845 | 19.0537 | 20.1594 | 20.3713 | 19.1259 | 20.2423 | 20.42 | 19.1259 | 20.2423 | 20.42
CA | 84873218 | 7450 | ROLLESTON | 7450_Memooloo - Rolleston 132 kV | Loading (MW) | 17.6266 | 18.6111 | 18.9619 | 17.6266 | 18.6111 | 18.9619 | 18.3512 | 19.4409 | 19.4541 | 18.4236 | 19.5238 | 19.5033 | 18.4236 | 19.5238 | 19.5033
CA | 84873218 | 7450 | ROLLESTON | 7450_Memooloo - Rolleston 132 kV | Power Factor | 0.96148 | 0.9627 | 0.9536 | 0.96148 | 0.9627 | 0.9536 | 0.96313 | 0.96436 | 0.95498 | 0.96328 | 0.96451 | 0.95511 | 0.96328 | 0.96451 | 0.95511
CA | 84873218 | 7450 | ROLLESTON | 7450_Memooloo - Rolleston 132 kV | Rating (A) | 705 | 735 | 652 | 705 | 735 | 652 | 705 | 735 | 652 | 705 | 735 | 652 | 705 | 735 | 652
CA | 84873218 | 7450 | ROLLESTON | 7450_Memooloo - Rolleston 132 kV | Time | 13:30 | 20:30 | 1:00 | 13:30 | 20:30 | 1:00 | 13:30 | 20:30 | 1:00 | 13:30 | 20:30 | 1:00 | 13:30 | 20:30 | 1:00
CA | 84873218 | 7450 | ROLLESTON | 7450_Memooloo - Rolleston 132 kV | Voltage at Constrained Conductor | 138.4975 | 138.2247 | 138.0324 | 138.4975 | 138.2247 | 138.0324 | 138.3984 | 138.1081 | 137.9648 | 138.3884 | 138.0963 | 137.958 | 138.3884 | 138.0963 | 137.958
FN | 10020664 | 7200 | 7200 - CRAIGLIE NO 2 | 7200_Craiglie No 2 132 kV | % of Rated A | 16.645 | 16.008 | 15.2881 | 16.5616 | 15.9446 | 15.2452 | 15.4795 | 15.2277 | 13.587 | 15.5177 | 15.2658 | 13.6132 | 15.7346 | 15.4851 | 13.7654
FN | 10020664 | 7200 | 7200 - CRAIGLIE NO 2 | 7200_Craiglie No 2 132 kV | Limiting Line Name | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1
FN | 10020664 | 7200 | 7200 - CRAIGLIE NO 2 | 7200_Craiglie No 2 132 kV | Loading (A) | 75.2356 | 76.1983 | 65.2803 | 74.8586 | 75.8962 | 65.0968 | 69.9674 | 72.4838 | 58.0166 | 70.1402 | 72.6653 | 58.1284 | 71.1206 | 73.7092 | 58.7781
FN | 10020664 | 7200 | 7200 - CRAIGLIE NO 2 | 7200_Craiglie No 2 132 kV | Loading (MVA) | 17.9689 | 18.1902 | 15.717 | 17.8866 | 18.1071 | 15.6809 | 16.7048 | 17.3054 | 14.0176 | 16.747 | 17.3494 | 14.0452 | 16.9818 | 17.6033 | 14.2149
FN | 10020664 | 7200 | 7200 - CRAIGLIE NO 2 | 7200_Craiglie No 2 132 kV | Loading (MW) | 14.6604 | 15.018 | 10.6105 | 14.5169 | 14.8681 | 10.5105 | 15.4858 | 16.1993 | 11.9558 | 15.5357 | 16.2507 | 11.9923 | 15.8183 | 16.5492 | 12.21
FN | 10020664 | 7200 | 7200 - CRAIGLIE NO 2 | 7200_Craiglie No 2 132 kV | Power Factor | 0.81588 | 0.82561 | 0.6751 | 0.81161 | 0.82112 | 0.67027 | 0.92703 | 0.93608 | 0.85292 | 0.92767 | 0.93667 | 0.85383 | 0.93149 | 0.94012 | 0.85896
FN | 10020664 | 7200 | 7200 - CRAIGLIE NO 2 | 7200_Craiglie No 2 132 kV | Rating (A) | 452 | 476 | 427 | 452 | 476 | 427 | 452 | 476 | 427 | 452 | 476 | 427 | 452 | 476 | 427
FN | 10020664 | 7200 | 7200 - CRAIGLIE NO 2 | 7200_Craiglie No 2 132 kV | Time | 16:30 | 17:00 | 22:00 | 16:30 | 17:00 | 22:00 | 16:30 | 17:00 | 22:00 | 16:30 | 17:00 | 22:00 | 16:30 | 17:00 | 22:00
FN | 10020664 | 7200 | 7200 - CRAIGLIE NO 2 | 7200_Craiglie No 2 132 kV | Voltage at Constrained Conductor | 137.8912 | 137.8263 | 139.0035 | 137.9509 | 137.7428 | 139.0756 | 137.8429 | 137.8415 | 139.4954 | 137.8506 | 137.8467 | 139.5017 | 137.8566 | 137.8834 | 139.6269
FN | 10020665 | 7201 | 7201 - CRAIGLIE NO 1 | 7201_Craiglie No 1 132 kV | % of Rated A | 10.461 | 11.0116 | 9.2074 | 10.3962 | 10.9545 | 9.155 | 16.8311 | 18.7199 | 15.9105 | 16.8854 | 18.7755 | 15.9564 | 17.2233 | 19.1905 | 16.2621
FN | 10020665 | 7201 | 7201 - CRAIGLIE NO 1 | 7201_Craiglie No 1 132 kV | Limiting Line Name | TR_LINE 38738_1 | TR_LINE 38738_1 | TR_LINE 38738_1 | TR_LINE 38738_1 | TR_LINE 38738_1 | TR_LINE 38738_1 | TR_LINE 38738_a | TR_LINE 38738_a | TR_LINE 38738_a | TR_LINE 38738_a | TR_LINE 38738_a | TR_LINE 38738_a | TR_LINE 38738_a | TR_LINE 38738_a | TR_LINE 38738_a
FN | 10020665 | 7201 | 7201 - CRAIGLIE NO 1 | 7201_Craiglie No 1 132 kV | Loading (A) | 39.6474 | 40.7431 | 29.6477 | 39.4017 | 40.5315 | 29.4789 | 63.7835 | 69.2559 | 51.231 | 63.989 | 69.4615 | 51.3786 | 65.2695 | 70.9965 | 52.3626
FN | 10020665 | 7201 | 7201 - CRAIGLIE NO 1 | 7201_Craiglie No 1 132 kV | Loading (MVA) | 9.4472 | 9.7016 | 7.1355 | 9.3933 | 9.6458 | 7.0988 | 15.1887 | 16.4654 | 12.3819 | 15.238 | 16.5134 | 12.4178 | 15.54 | 16.8487 | 12.6652
FN | 10020665 | 7201 | 7201 - CRAIGLIE NO 1 | 7201_Craiglie No 1 132 kV | Loading (MW) | 9.3897 | 9.6524 | 6.9501 | 9.3333 | 9.5946 | 6.9093 | 15.1772 | 16.4476 | 12.3818 | 15.2261 | 16.4952 | 12.4177 | 15.5263 | 16.8277 | 12.6648
FN | 10020665 | 7201 | 7201 - CRAIGLIE NO 1 | 7201_Craiglie No 1 132 kV | Power Factor | 0.99391 | 0.99493 | 0.97402 | 0.99361 | 0.99468 | 0.9733 | 0.99924 | 0.99892 | 0.99999 | 0.99922 | 0.9989 | 0.99999 | 0.99912 | 0.99875 | 0.99997
FN | 10020665 | 7201 | 7201 - CRAIGLIE NO 1 | 7201_Craiglie No 1 132 kV | Rating (A) | 379 | 370 | 322 | 379 | 370 | 322 | 379 | 370 | 322 | 379 | 370 | 322 | 379 | 370 | 322
FN | 10020665 | 7201 | 7201 - CRAIGLIE NO 1 | 7201_Craiglie No 1 132 kV | Time | 16:30 | 17:00 | 22:00 | 16:30 | 17:00 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00
FN | 10020665 | 7201 | 7201 - CRAIGLIE NO 1 | 7201_Craiglie No 1 132 kV | Voltage at Constrained Conductor | 137.5715 | 137.4771 | 138.9542 | 137.6386 | 137.3999 | 139.0315 | 137.4841 | 137.2635 | 139.5388 | 137.4866 | 137.2565 | 139.5415 | 137.4613 | 137.0152 | 139.6462
FN | 10020666 | 7216 | 4GEO (GEORGETOWN) | 7216_4GEO (Georgetown) 132 kV | % of Rated A | 11.4245 | 10.7305 | 9.1214 | 11.3329 | 10.6356 | 9.0552 | 11.3208 | 10.6014 | 9.1456 | 11.3208 | 10.6014 | 9.1456 | 11.3961 | 10.6837 | 9.1933
FN | 10020666 | 7216 | 4GEO (GEORGETOWN) | 7216_4GEO (Georgetown) 132 kV | Limiting Line Name | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1
FN | 10020666 | 7216 | 4GEO (GEORGETOWN) | 7216_4GEO (Georgetown) 132 kV | Loading (A) | 34.0449 | 36.9128 | 31.1951 | 33.7719 | 36.5866 | 30.9687 | 33.736 | 36.4688 | 31.278 | 33.7359 | 36.4688 | 31.2779 | 33.9604 | 36.7519 | 31.4411
FN | 10020666 | 7216 | 4GEO (GEORGETOWN) | 7216_4GEO (Georgetown) 132 kV | Loading (MVA) | 8.2189 | 8.8913 | 7.5382 | 8.1551 | 8.8154 | 7.4853 | 8.2566 | 8.9067 | 7.6678 | 8.2566 | 8.9067 | 7.6678 | 8.3083 | 8.9718 | 7.7048
FN | 10020666 | 7216 | 4GEO (GEORGETOWN) | 7216_4GEO (Georgetown) 132 kV | Loading (MW) | 6.9645 | 7.9113 | 6.027 | 6.8768 | 7.8135 | 5.9458 | 6.8764 | 7.8129 | 5.9457 | 6.8764 | 7.8129 | 5.9457 | 6.9641 | 7.9107 | 6.0268
FN | 10020666 | 7216 | 4GEO (GEORGETOWN) | 7216_4GEO (Georgetown) 132 kV | Power Factor | 0.84737 | 0.88978 | 0.79953 | 0.84325 | 0.88635 | 0.79434 | 0.83284 | 0.87719 | 0.77541 | 0.83284 | 0.87719 | 0.77541 | 0.83821 | 0.88172 | 0.78222
FN | 10020666 | 7216 | 4GEO (GEORGETOWN) | 7216_4GEO (Georgetown) 132 kV | Rating (A) | 298 | 344 | 342 | 298 | 344 | 342 | 298 | 344 | 342 | 298 | 344 | 342 | 298 | 344 | 342
FN | 10020666 | 7216 | 4GEO (GEORGETOWN) | 7216_4GEO (Georgetown) 132 kV | Time | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00
FN | 10020666 | 7216 | 4GEO (GEORGETOWN) | 7216_4GEO (Georgetown) 132 kV | Voltage at Constrained Conductor | 139.3801 | 139.0675 | 139.5147 | 139.4157 | 139.1105 | 139.5485 | 141.3014 | 141.0046 | 141.5373 | 141.3014 | 141.0046 | 141.5373 | 141.2464 | 140.9421 | 141.4819
FN | 10020667 | 3AT2 | ATHERTON NO 2 | 3AT2_Atherton No 2 66 kV | % of Rated A | 17.9984 | 21.8083 | 16.5973 | 17.8747 | 21.6647 | 16.4807 | 17.9419 | 21.7437 | 16.5597 | 18.058 | 21.8947 | 16.6622 | 18.3021 | 21.9556 | 16.8899
FN | 10020667 | 3AT2 | ATHERTON NO 2 | 3AT2_Atherton No 2 66 kV | Limiting Line Name | TR_LINE 4672_1 | TR_CABLE 14_1 | TR_LINE 4672_1 | TR_LINE 4672_1 | TR_CABLE 14_1 | TR_LINE 4672_1 | TR_LINE 4672_1 | TR_CABLE 14_1 | TR_LINE 4672_1 | TR_LINE 4672_1 | TR_CABLE 14_1 | TR_LINE 4672_1 | TR_LINE 4672_1 | TR_CABLE 14_1 | TR_LINE 4672_1
FN | 10020667 | 3AT2 | ATHERTON NO 2 | 3AT2_Atherton No 2 66 kV | Loading (A) | 98.6311 | 122.1263 | 86.4718 | 97.9534 | 121.3221 | 85.8643 | 98.3218 | 121.7648 | 86.2762 | 98.958 | 122.6106 | 86.81 | 100.2958 | 122.9516 | 87.9965
FN | 10020667 | 3AT2 | ATHERTON NO 2 | 3AT2_Atherton No 2 66 kV | Loading (MVA) | 11.7785 | 14.5406 | 10.3203 | 11.7026 | 14.4596 | 10.2535 | 11.7434 | 14.5107 | 10.2874 | 11.8216 | 14.6129 | 10.3526 | 11.9768 | 14.8147 | 10.4827
FN | 10020667 | 3AT2 | ATHERTON NO 2 | 3AT2_Atherton No 2 66 kV | Loading (MW) | 11.7577 | 14.5388 | 10.2856 | 11.686 | 14.4572 | 10.2163 | 11.7213 | 14.5086 | 10.248 | 11.8003 | 14.6111 | 10.3142 | 11.9628 | 14.8125 | 10.4469
FN | 10020667 | 3AT2 | ATHERTON NO 2 | 3AT2_Atherton No 2 66 kV | Power Factor | 0.99823 | 0.99988 | 0.99664 | 0.99858 | 0.99984 | 0.99637 | 0.99812 | 0.99985 | 0.99617 | 0.9982 | 0.99987 | 0.99629 | 0.99883 | 0.99985 | 0.99658
FN | 10020667 | 3AT2 | ATHERTON NO 2 | 3AT2_Atherton No 2 66 kV | Rating (A) | 548 | 560 | 521 | 548 | 560 | 521 | 548 | 560 | 521 | 548 | 560 | 521 | 548 | 560 | 521
FN | 10020667 | 3AT2 | ATHERTON NO 2 | 3AT2_Atherton No 2 66 kV | Time | 16:30 | 18:30 | 7:00 | 16:30 | 18:30 | 7:00 | 16:30 | 18:30 | 7:00 | 16:30 | 18:30 | 7:00 | 16:30 | 18:30 | 7:00
FN | 10020667 | 3AT2 | ATHERTON NO 2 | 3AT2_Atherton No 2 66 kV | Voltage at Constrained Conductor | 68.9472 | 68.7405 | 68.9057 | 68.9769 | 68.8104 | 68.9441 | 68.9579 | 68.8028 | 68.8423 | 68.9707 | 68.8096 | 68.8527 | 68.9442 | 69.5663 | 68.7778
FN | 10020668 | 4KID | ROSS - KIDSTON | 4KID_Ross - Kidston 132 kV | % of Rated A | 20.7733 | 19.8739 | 20.5773 | 20.7119 | 19.8062 | 20.9955 | 21.0373 | 19.9999 | 20.8864 | 21.0373 | 19.9999 | 20.8865 | 21.0966 | 20.0667 | 20.9407
FN | 10020668 | 4KID | ROSS - KIDSTON | 4KID_Ross - Kidston 132 kV | Limiting Line Name | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1
FN | 10020668 | 4KID | ROSS - KIDSTON | 4KID_Ross - Kidston 132 kV | Loading (A) | 73.7453 | 76.5144 | 71.4033 | 73.5271 | 76.2539 | 72.8544 | 74.6823 | 76.9996 | 72.4759 | 74.6824 | 76.9997 | 72.476 | 74.8929 | 77.2567 | 72.6643
FN | 10020668 | 4KID | ROSS - KIDSTON | 4KID_Ross - Kidston 132 kV | Loading (MVA) | 17.7046 | 18.3693 | 17.1421 | 17.6518 | 18.3068 | 17.4905 | 17.9293 | 18.4861 | 17.3998 | 17.9293 | 18.4861 | 17.3998 | 17.9803 | 18.5477 | 17.445
FN | 10020668 | 4KID | ROSS - KIDSTON | 4KID_Ross - Kidston 132 kV | Loading (MW) | 9.9335 | 10.9585 | 9.2285 | 9.8393 | 10.8526 | 8.6001 | 7.9421 | 8.9445 | 7.0231 | 7.9421 | 8.9445 | 7.0231 | 8.0779 | 9.0921 | 7.1562
FN | 10020668 | 4KID | ROSS - KIDSTON | 4KID_Ross - Kidston 132 kV | Power Factor | 0.56107 | 0.59656 | 0.53835 | 0.55741 | 0.59282 | 0.4917 | 0.44297 | 0.48385 | 0.40363 | 0.44297 | 0.48385 | 0.40363 | 0.44926 | 0.4902 | 0.41022
FN | 10020668 | 4KID | ROSS - KIDSTON | 4KID_Ross - Kidston 132 kV | Rating (A) | 355 | 385 | 347 | 355 | 385 | 347 | 355 | 385 | 347 | 355 | 385 | 347 | 355 | 385 | 347
FN | 10020668 | 4KID | ROSS - KIDSTON | 4KID_Ross - Kidston 132 kV | Time | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 23:30 | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00
FN | 10020668 | 4KID | ROSS - KIDSTON | 4KID_Ross - Kidston 132 kV | Voltage at Constrained Conductor | 138.609 | 138.6085 | 138.6069 | 138.6056 | 138.6086 | 138.6075 | 138.6072 | 138.6102 | 138.6086 | 138.6071 | 138.6101 | 138.6086 | 138.6105 | 138.6099 | 138.6085
FN | 10020672 | 3CRO | CROYDON | 3CRO_Croydon 66 kV | % of Rated A | 10.5583 | 11.0787 | 8.9368 | 10.55 | 11.0695 | 8.929 | 10.5175 | 11.0377 | 8.8785 | 10.5175 | 11.0377 | 8.8785 | 10.5291 | 11.05 | 8.89
FN | 10020672 | 3CRO | CROYDON | 3CRO_Croydon 66 kV | Limiting Line Name | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1
FN | 10020672 | 3CRO | CROYDON | 3CRO_Croydon 66 kV | Loading (A) | 48.2516 | 53.9531 | 42.1815 | 48.2136 | 53.9083 | 42.1448 | 48.0648 | 53.7535 | 41.9067 | 48.0648 | 53.7535 | 41.9067 | 48.118 | 53.8134 | 41.9607
FN | 10020672 | 3CRO | CROYDON | 3CRO_Croydon 66 kV | Loading (MVA) | 5.7519 | 6.4219 | 5.0314 | 5.7486 | 6.4182 | 5.028 | 5.7357 | 6.4054 | 5.0061 | 5.7357 | 6.4054 | 5.0061 | 5.7403 | 6.4103 | 5.011
FN | 10020672 | 3CRO | CROYDON | 3CRO_Croydon 66 kV | Loading (MW) | 4.8512 | 5.5606 | 4.0688 | 4.851 | 5.5603 | 4.0687 | 4.8502 | 5.5592 | 4.0677 | 4.8502 | 5.5592 | 4.0677 | 4.8505 | 5.5596 | 4.0679
FN | 10020672 | 3CRO | CROYDON | 3CRO_Croydon 66 kV | Power Factor | 0.84341 | 0.86588 | 0.8087 | 0.84386 | 0.86633 | 0.80921 | 0.84562 | 0.86789 | 0.81256 | 0.84562 | 0.86789 | 0.81256 | 0.84499 | 0.86729 | 0.8118
FN | 10020672 | 3CRO | CROYDON | 3CRO_Croydon 66 kV | Rating (A) | 457 | 487 | 472 | 457 | 487 | 472 | 457 | 487 | 472 | 457 | 487 | 472 | 457 | 487 | 472
FN | 10020672 | 3CRO | CROYDON | 3CRO_Croydon 66 kV | Time | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00
FN | 10020672 | 3CRO | CROYDON | 3CRO_Croydon 66 kV | Voltage at Constrained Conductor | 68.8243 | 68.7204 | 68.8657 | 68.8389 | 68.7379 | 68.8794 | 68.8964 | 68.7983 | 68.9687 | 68.8963 | 68.7983 | 68.9687 | 68.8758 | 68.7749 | 68.9484
FN | 10020676 | 3NOR | NORMANTON | 3NOR_Normanton 66 kV | % of Rated A | 8.1563 | 8.7624 | 6.6102 | 8.151 | 8.7561 | 6.6057 | 8.1306 | 8.7347 | 6.5767 | 8.1306 | 8.7347 | 6.5767 | 8.1379 | 8.743 | 6.5832
FN | 10020676 | 3NOR | NORMANTON | 3NOR_Normanton 66 kV | Limiting Line Name | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1
FN | 10020676 | 3NOR | NORMANTON | 3NOR_Normanton 66 kV | Loading (A) | 37.2741 | 42.6727 | 31.2 | 37.2501 | 42.6423 | 31.1787 | 37.1568 | 42.5379 | 31.0421 | 37.1568 | 42.5379 | 31.0421 | 37.1901 | 42.5782 | 31.0728
FN | 10020676 | 3NOR | NORMANTON | 3NOR_Normanton 66 kV | Loading (MVA) | 4.466 | 5.1001 | 3.7452 | 4.4637 | 5.0973 | 3.7431 | 4.4549 | 5.0877 | 3.7297 | 4.4549 | 5.0877 | 3.7297 | 4.458 | 5.0914 | 3.7327
FN | 10020676 | 3NOR | NORMANTON | 3NOR_Normanton 66 kV | Loading (MW) | 4.2331 | 4.8201 | 3.553 | 4.2331 | 4.82 | 3.553 | 4.233 | 4.8198 | 3.553 | 4.233 | 4.8198 | 3.553 | 4.233 | 4.8199 | 3.553
FN | 10020676 | 3NOR | NORMANTON | 3NOR_Normanton 66 kV | Power Factor | 0.94787 | 0.9451 | 0.9487 | 0.94834 | 0.9456 | 0.94923 | 0.95018 | 0.94734 | 0.95261 | 0.95018 | 0.94734 | 0.95261 | 0.94952 | 0.94667 | 0.95185
FN | 10020676 | 3NOR | NORMANTON | 3NOR_Normanton 66 kV | Rating (A) | 457 | 487 | 472 | 457 | 487 | 472 | 457 | 487 | 472 | 457 | 487 | 472 | 457 | 487 | 472
FN | 10020676 | 3NOR | NORMANTON | 3NOR_Normanton 66 kV | Time | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00
FN | 10020676 | 3NOR | NORMANTON | 3NOR_Normanton 66 kV | Voltage at Constrained Conductor | 69.1749 | 69.0034 | 69.3033 | 69.1842 | 69.0145 | 69.312 | 69.2209 | 69.0533 | 69.3687 | 69.2209 | 69.0533 | 69.3687 | 69.2078 | 69.0383 | 69.3558
FN | 10020678 | 3AT1 | ATHERTON NO 1 | 3AT1_Atherton No 1 66 kV | % of Rated A | 17.9994 | 21.8098 | 16.5981 | 17.8758 | 21.6662 | 16.4814 | 17.9429 | 21.7452 | 16.5605 | 18.0591 | 21.8963 | 16.663 | 18.3032 | 21.9572 | 16.8907
FN | 10020678 | 3AT1 | ATHERTON NO 1 | 3AT1_Atherton No 1 66 kV | Limiting Line Name | TR_LINE 4407_1 | TR_CABLE 15_1 | TR_LINE 4407_1 | TR_LINE 4407_1 | TR_CABLE 15_1 | TR_LINE 4407_1 | TR_LINE 4407_1 | TR_CABLE 15_1 | TR_LINE 4407_1 | TR_LINE 4407_1 | TR_CABLE 15_1 | TR_LINE 4407_1 | TR_LINE 4407_1 | TR_CABLE 15_1 | TR_LINE 4407_1
FN | 10020678 | 3AT1 | ATHERTON NO 1 | 3AT1_Atherton No 1 66 kV | Loading (A) | 98.6367 | 122.1349 | 86.4759 | 97.9591 | 121.3306 | 85.8683 | 98.3273 | 121.7733 | 86.2801 | 98.9637 | 122.6192 | 86.8141 | 100.3018 | 122.9602 | 88.0007
FN | 10020678 | 3AT1 | ATHERTON NO 1 | 3AT1_Atherton No 1 66 kV | Loading (MVA) | 11.7792 | 14.5416 | 10.3207 | 11.7033 | 14.4606 | 10.2539 | 11.7441 | 14.5117 | 10.2879 | 11.8223 | 14.614 | 10.3531 | 11.9775 | 14.8158 | 10.4832
FN | 10020678 | 3AT1 | ATHERTON NO 1 | 3AT1_Atherton No 1 66 kV | Loading (MW) | 11.7586 | 14.5399 | 10.2863 | 11.6868 | 14.4583 | 10.217 | 11.7222 | 14.5096 | 10.2488 | 11.8012 | 14.6122 | 10.315 | 11.9637 | 14.8135 | 10.4476
FN | 10020678 | 3AT1 | ATHERTON NO 1 | 3AT1_Atherton No 1 66 kV | Power Factor | 0.99825 | 0.99988 | 0.99666 | 0.99859 | 0.99984 | 0.9964 | 0.99813 | 0.99986 | 0.9962 | 0.99822 | 0.99988 | 0.99631 | 0.99884 | 0.99985 | 0.9966
FN | 10020678 | 3AT1 | ATHERTON NO 1 | 3AT1_Atherton No 1 66 kV | Rating (A) | 548 | 560 | 521 | 548 | 560 | 521 | 548 | 560 | 521 | 548 | 560 | 521 | 548 | 560 | 521
FN | 10020678 | 3AT1 | ATHERTON NO 1 | 3AT1_Atherton No 1 66 kV | Time | 16:30 | 18:30 | 7:00 | 16:30 | 18:30 | 7:00 | 16:30 | 18:30 | 7:00 | 16:30 | 18:30 | 7:00 | 16:30 | 18:30 | 7:00
FN | 10020678 | 3AT1 | ATHERTON NO 1 | 3AT1_Atherton No 1 66 kV | Voltage at Constrained Conductor | 68.9472 | 68.7405 | 68.9057 | 68.9769 | 68.8104 | 68.9441 | 68.9579 | 68.8028 | 68.8423 | 68.9707 | 68.8096 | 68.8527 | 68.9442 | 69.5663 | 68.7778
FN | 10020733 | 3EVE | EVELYN | 3EVE_Evelyn 66 kV | % of Rated A | 14.6004 | 11.0063 | 9.6454 | 14.0894 | 10.7062 | 9.3628 | 14.1035 | 10.709 | 9.3776 | 14.1022 | 10.7091 | 9.3768 | 14.096 | 10.5826 | 9.3896
FN | 10020733 | 3EVE | EVELYN | 3EVE_Evelyn 66 kV | Limiting Line Name | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1
FN | 10020733 | 3EVE | EVELYN | 3EVE_Evelyn 66 kV | Loading (A) | 24.6747 | 26.5252 | 22.6667 | 23.8111 | 25.802 | 22.0027 | 23.8348 | 25.8087 | 22.0375 | 23.8327 | 25.8089 | 22.0355 | 23.8223 | 25.5041 | 22.0655
FN | 10020733 | 3EVE | EVELYN | 3EVE_Evelyn 66 kV | Loading (MVA) | 2.9172 | 3.095 | 2.6665 | 2.8173 | 3.0151 | 2.5907 | 2.8175 | 3.0152 | 2.591 | 2.8174 | 3.0152 | 2.591 | 2.8174 | 3.0133 | 2.5912
FN | 10020733 | 3EVE | EVELYN | 3EVE_Evelyn 66 kV | Loading (MW) | 2.8266 | 3.0186 | 2.6065 | 2.7348 | 2.9448 | 2.5363 | 2.7348 | 2.9448 | 2.5363 | 2.7348 | 2.9448 | 2.5363 | 2.7348 | 2.9448 | 2.5363
FN | 10020733 | 3EVE | EVELYN | 3EVE_Evelyn 66 kV | Power Factor | 0.96892 | 0.9753 | 0.97751 | 0.97072 | 0.97667 | 0.97898 | 0.97065 | 0.97666 | 0.97889 | 0.97066 | 0.97666 | 0.97889 | 0.97069 | 0.97725 | 0.97882
FN | 10020733 | 3EVE | EVELYN | 3EVE_Evelyn 66 kV | Rating (A) | 169 | 241 | 235 | 169 | 241 | 235 | 169 | 241 | 235 | 169 | 241 | 235 | 169 | 241 | 235
FN | 10020733 | 3EVE | EVELYN | 3EVE_Evelyn 66 kV | Time | 15:30 | 18:00 | 7:00 | 15:30 | 18:00 | 7:00 | 15:30 | 18:00 | 7:00 | 15:30 | 18:00 | 7:00 | 15:30 | 18:00 | 7:00
FN | 10020733 | 3EVE | EVELYN | 3EVE_Evelyn 66 kV | Voltage at Constrained Conductor | 68.2583 | 67.3669 | 67.9191 | 68.3105 | 67.4671 | 67.981 | 68.2472 | 67.4508 | 67.8803 | 68.2528 | 67.4501 | 67.886 | 68.2807 | 68.214 | 67.7994
FN | 10020762 | 3MTG | MT GARNET | 3MTG_Mt Garnet 66 kV | % of Rated A | 10.974 | 5.8289 | 7.295 | 10.9638 | 5.8248 | 7.29 | 10.977 | 5.8254 | 7.3008 | 10.9761 | 5.8254 | 7.3002 | 10.9993 | 5.7868 | 7.3096
FN | 10020762 | 3MTG | MT GARNET | 3MTG_Mt Garnet 66 kV | Limiting Line Name | TR_LINE 4482_2 | TR_LINE 169447_1 | TR_LINE 4482_2 | TR_LINE 4482_2 | TR_LINE 169447_1 | TR_LINE 4482_2 | TR_LINE 4482_2 | TR_LINE 169447_1 | TR_LINE 4482_2 | TR_LINE 4482_2 | TR_LINE 169447_1 | TR_LINE 4482_2 | TR_LINE 4482_2 | TR_LINE 169447_1 | TR_LINE 4482_2
FN | 10020762 | 3MTG | MT GARNET | 3MTG_Mt Garnet 66 kV | Loading (A) | 18.5461 | 14.0476 | 17.1432 | 18.5288 | 14.0377 | 17.1315 | 18.5511 | 14.0392 | 17.1568 | 18.5496 | 14.0393 | 17.1555 | 18.5889 | 13.9462 | 17.1776
FN | 10020762 | 3MTG | MT GARNET | 3MTG_Mt Garnet 66 kV | Loading (MVA) | 2.1804 | 1.6501 | 2.0094 | 2.1803 | 1.6509 | 2.0093 | 2.1804 | 1.6508 | 2.0092 | 2.1804 | 1.6508 | 2.0092 | 2.1805 | 1.6582 | 2.0092
FN | 10020762 | 3MTG | MT GARNET | 3MTG_Mt Garnet 66 kV | Loading (MW) | 2.1145 | 1.5549 | 1.9505 | 2.1145 | 1.5549 | 1.9505 | 2.1145 | 1.5549 | 1.9505 | 2.1145 | 1.5549 | 1.9505 | 2.1145 | 1.5547 | 1.9505
FN | 10020762 | 3MTG | MT GARNET | 3MTG_Mt Garnet 66 kV | Power Factor | 0.96979 | 0.9423 | 0.97072 | 0.9698 | 0.94184 | 0.97074 | 0.96978 | 0.94191 | 0.97078 | 0.96978 | 0.94191 | 0.97078 | 0.96974 | 0.93755 | 0.97075
FN | 10020762 | 3MTG | MT GARNET | 3MTG_Mt Garnet 66 kV | Rating (A) | 169 | 241 | 235 | 169 | 241 | 235 | 169 | 241 | 235 | 169 | 241 | 235 | 169 | 241 | 235
FN | 10020762 | 3MTG | MT GARNET | 3MTG_Mt Garnet 66 kV | Time | 16:00 | 18:30 | 7:30 | 16:00 | 18:30 | 7:30 | 16:00 | 18:30 | 7:30 | 16:00 | 18:30 | 7:30 | 16:00 | 18:30 | 7:30
FN | 10020762 | 3MTG | MT GARNET | 3MTG_Mt Garnet 66 kV | Voltage at Constrained Conductor | 67.8757 | 67.8185 | 67.6714 | 67.938 | 67.8984 | 67.7165 | 67.858 | 67.8865 | 67.6119 | 67.8631 | 67.8857 | 67.6169 | 67.7228 | 68.6479 | 67.5316
FN | 10020819 | 7206 | 7206 CAIRNS CITY | 7206 Woree-Cairns Terminal-Cairns City | % of Rated A | 26.319 | 21.8643 | 22.8796 | 26.014 | 21.6149 | 22.6161 | 25.8625 | 21.4904 | 22.4851 | 25.8648 | 21.4907 | 22.4869 | 26.3852 | 21.699 | 22.7086
FN | 10020819 | 7206 | 7206 CAIRNS CITY | 7206 Woree-Cairns Terminal-Cairns City | Limiting Line Name | TR_LINE 3958_1 | TR_LINE 3958_1 | TR_LINE 3958_1 | TR_LINE 3958_1 | TR_LINE 3958_1 | TR_LINE 3958_1 | TR_LINE 3958_1 | TR_LINE 3958_1 | TR_LINE 3958_1 | TR_LINE 3958_1 | TR_LINE 3958_1 | TR_LINE 3958_1 | TR_LINE 3958_1 | TR_LINE 3958_1 | TR_LINE 3958_1
FN | 10020819 | 7206 | 7206 CAIRNS CITY | 7206 Woree-Cairns Terminal-Cairns City | Loading (A) | 109.9413 | 98.3294 | 93.2915 | 108.6674 | 97.2082 | 92.2173 | 108.0346 | 96.6482 | 91.6834 | 108.0444 | 96.6499 | 91.6906 | 110.2191 | 97.5864 | 92.5943
FN | 10020819 | 7206 | 7206 CAIRNS CITY | 7206 Woree-Cairns Terminal-Cairns City | Loading (MVA) | 26.8468 | 23.5973 | 22.8181 | 26.5396 | 23.3283 | 22.5581 | 26.3862 | 23.194 | 22.4283 | 26.3866 | 23.1944 | 22.4286 | 26.6457 | 23.419 | 22.6457
FN | 10020819 | 7206 | 7206 CAIRNS CITY | 7206 Woree-Cairns Terminal-Cairns City | Loading (MW) | 26.7153 | 23.5165 | 22.75 | 26.4138 | 23.2512 | 22.4934 | 26.2631 | 23.1187 | 22.3651 | 26.2634 | 23.1191 | 22.3654 | 26.5165 | 23.3407 | 22.5798
FN | 10020819 | 7206 | 7206 CAIRNS CITY | 7206 Woree-Cairns Terminal-Cairns City | Power Factor | 0.9951 | 0.99658 | 0.99701 | 0.99526 | 0.9967 | 0.99713 | 0.99533 | 0.99675 | 0.99719 | 0.99533 | 0.99675 | 0.99718 | 0.99515 | 0.99665 | 0.99709
FN | 10020819 | 7206 | 7206 CAIRNS CITY | 7206 Woree-Cairns Terminal-Cairns City | Rating (A) | 418 | 450 | 408 | 418 | 450 | 408 | 418 | 450 | 408 | 418 | 450 | 408 | 418 | 450 | 408
FN | 10020819 | 7206 | 7206 CAIRNS CITY | 7206 Woree-Cairns Terminal-Cairns City | Time | 12:30 | 17:00 | 8:30 | 12:30 | 17:00 | 8:30 | 12:30 | 17:00 | 8:30 | 12:30 | 17:00 | 8:30 | 12:30 | 17:00 | 8:30
FN | 10020819 | 7206 | 7206 CAIRNS CITY | 7206 Woree-Cairns Terminal-Cairns City | Voltage at Constrained Conductor | 140.9844 | 138.5535 | 141.2138 | 141.005 | 138.5542 | 141.231 | 141.0109 | 138.5545 | 141.2355 | 141.0003 | 138.5545 | 141.2267 | 139.5756 | 138.554 | 141.2022
FN | 10020851 | 3MO2 | MOSSMAN NO 2 | 3MO2_Mossman No 2 66 kV | % of Rated A | 23.2214 | 22.8371 | 17.9092 | 23.2109 | 22.8122 | 17.8981 | 3.6949 | 2.6072 | 2.6806 | 3.6956 | 2.6076 | 2.6785 | 3.6849 | 2.608 | 2.6777
FN | 10020851 | 3MO2 | MOSSMAN NO 2 | 3MO2_Mossman No 2 66 kV | Limiting Line Name | TR_LINE 1063_1 | TR_LINE 1063_1 | TR_LINE 167072_1 | TR_LINE 1063_1 | TR_LINE 1063_1 | TR_LINE 167072_1 | TR_LINE 2062_3 | TR_LINE 2062_3 | TR_LINE 2062_3 | TR_LINE 2062_3 | TR_LINE 2062_3 | TR_LINE 2062_3 | TR_LINE 2062_3 | TR_LINE 2062_3 | TR_LINE 2062_3
FN | 10020851 | 3MO2 | MOSSMAN NO 2 | 3MO2_Mossman No 2 66 kV | Loading (A) | 30.6368 | 38.0961 | 28.4756 | 30.6231 | 38.0547 | 28.458 | 6.2444 | 6.2312 | 6.2459 | 6.2455 | 6.2321 | 6.241 | 6.2275 | 6.2332 | 6.2391
FN | 10020851 | 3MO2 | MOSSMAN NO 2 | 3MO2_Mossman No 2 66 kV | Loading (MVA) | 3.629 | 4.4883 | 3.3746 | 3.629 | 4.4881 | 3.3746 | 0.75405 | 0.75086 | 0.7544 | 0.75432 | 0.75108 | 0.75322 | 0.74997 | 0.75133 | 0.75276
FN | 10020851 | 3MO2 | MOSSMAN NO 2 | 3MO2_Mossman No 2 66 kV | Loading (MW) | 3.629 | 4.4846 | 3.3719 | 3.6289 | 4.4845 | 3.3719 | 0.0005959 | 0.00059338 | 0.00059617 | 0.00059611 | 0.00059354 | 0.00059524 | 0.00059267 | 0.00059375 | 0.00059487
FN | 10020851 | 3MO2 | MOSSMAN NO 2 | 3MO2_Mossman No 2 66 kV | Power Factor | 0.99998 | 0.99918 | 0.9992 | 0.99998 | 0.99919 | 0.99919 | 0.00079026 | 0.00079026 | 0.00079026 | 0.00079026 | 0.00079026 | 0.00079026 | 0.00079026 | 0.00079026 | 0.00079026
FN | 10020851 | 3MO2 | MOSSMAN NO 2 | 3MO2_Mossman No 2 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233
FN | 10020851 | 3MO2 | MOSSMAN NO 2 | 3MO2_Mossman No 2 66 kV | Time | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 12:00 | 21:30 | 22:30 | 12:00 | 21:30 | 3:00 | 15:00 | 18:30 | 22:30
FN | 10020851 | 3MO2 | MOSSMAN NO 2 | 3MO2_Mossman No 2 66 kV | Voltage at Constrained Conductor | 68.3891 | 68.021 | 68.421 | 68.4192 | 68.0919 | 68.4633 | 69.7185 | 69.5709 | 69.7345 | 69.7309 | 69.5808 | 69.6802 | 69.5297 | 69.5926 | 69.6586
FN | 10020852 | 3MO1 | MOSSMAN NO 1 | 3MO1_Mossman No 1 66 kV | % of Rated A | 71.3974 | 56.4182 | 42.4717 | 70.463 | 55.7973 | 41.9718 | 70.5926 | 55.8012 | 41.9228 | 71.4509 | 56.4805 | 42.4774 | 72.4314 | 57.2384 | 42.8666
FN | 10020852 | 3MO1 | MOSSMAN NO 1 | 3MO1_Mossman No 1 66 kV | Limiting Line Name | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1
FN | 10020852 | 3MO1 | MOSSMAN NO 1 | 3MO1_Mossman No 1 66 kV | Loading (A) | 94.2445 | 94.2183 | 67.53 | 93.0112 | 93.1814 | 66.7352 | 93.1822 | 93.188 | 66.6573 | 94.3152 | 94.3224 | 67.5391 | 95.6094 | 95.5881 | 68.1578
FN | 10020852 | 3MO1 | MOSSMAN NO 1 | 3MO1_Mossman No 1 66 kV | Loading (MVA) | 11.2035 | 11.1896 | 8.0208 | 11.0626 | 11.0649 | 7.9317 | 11.0912 | 11.0911 | 7.9566 | 11.2285 | 11.2283 | 8.0631 | 11.3761 | 11.3764 | 8.1418
FN | 10020852 | 3MO1 | MOSSMAN NO 1 | 3MO1_Mossman No 1 66 kV | Loading (MW) | 10.9397 | 10.9249 | 7.4555 | 10.7883 | 10.7666 | 7.3516 | 10.8678 | 10.8682 | 7.4364 | 10.9787 | 10.9791 | 7.5125 | 11.1704 | 11.1707 | 7.6438
FN | 10020852 | 3MO1 | MOSSMAN NO 1 | 3MO1_Mossman No 1 66 kV | Power Factor | 0.97645 | 0.97634 | 0.92952 | 0.97521 | 0.97304 | 0.92687 | 0.97986 | 0.97991 | 0.93462 | 0.97775 | 0.97781 | 0.93171 | 0.98192 | 0.98192 | 0.93884
FN | 10020852 | 3MO1 | MOSSMAN NO 1 | 3MO1_Mossman No 1 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
FN | 10020852 | 3MO1 | MOSSMAN NO 1 | 3MO1_Mossman No 1 66 kV | Time | 16:30 | 17:00 | 22:00 | 16:30 | 17:00 | 22:00 | 16:30 | 17:00 | 22:00 | 16:30 | 17:00 | 22:00 | 16:30 | 17:00 | 22:00
FN | 10020852 | 3MO1 | MOSSMAN NO 1 | 3MO1_Mossman No 1 66 kV | Voltage at Constrained Conductor | 68.6338 | 68.5675 | 68.5741 | 68.669 | 68.5578 | 68.6197 | 68.7204 | 68.7154 | 68.9161 | 68.7353 | 68.7288 | 68.9269 | 68.6959 | 68.7133 | 68.9674
FN | 10020859 | 3DIM | DIMBULAH | 3DIM_Dimbulah 66 kV | % of Rated A | 46.4803 | 39.2835 | 37.9154 | 46.0801 | 38.8937 | 37.706 | 46.0955 | 38.8988 | 37.7597 | 46.0851 | 38.894 | 37.7543 | 46.4827 | 38.7205 | 37.9927
FN | 10020859 | 3DIM | DIMBULAH | 3DIM_Dimbulah 66 kV | Limiting Line Name | TR_LINE 2161_1 | TR_LINE 2161_1 | TR_LINE 2161_1 | TR_LINE 2161_1 | TR_LINE 2161_1 | TR_LINE 2161_1 | TR_LINE 2161_1 | TR_LINE 2161_1 | TR_LINE 2161_1 | TR_LINE 2161_1 | TR_LINE 2161_1 | TR_LINE 2161_1 | TR_LINE 2161_1 | TR_LINE 2161_1 | TR_LINE 2161_1
FN | 10020859 | 3DIM | DIMBULAH | 3DIM_Dimbulah 66 kV | Loading (A) | 101.282 | 105.6277 | 95.8747 | 100.4098 | 104.5793 | 95.345 | 100.4434 | 104.5932 | 95.4807 | 100.4206 | 104.5801 | 95.4671 | 101.2874 | 104.1136 | 96.0704
FN | 10020859 | 3DIM | DIMBULAH | 3DIM_Dimbulah 66 kV | Loading (MVA) | 11.9604 | 12.4345 | 11.3608 | 11.8638 | 12.3253 | 11.3031 | 11.8644 | 12.3255 | 11.3056 | 11.864 | 12.3253 | 11.3053 | 11.9605 | 12.4079 | 11.3643
FN | 10020859 | 3DIM | DIMBULAH | 3DIM_Dimbulah 66 kV | Loading (MW) | 11.5138 | 11.9699 | 10.8108 | 11.4234 | 11.8685 | 10.7567 | 11.4236 | 11.8686 | 10.7573 | 11.4234 | 11.8685 | 10.7572 | 11.5139 | 11.9611 | 10.8116
FN | 10020859 | 3DIM | DIMBULAH | 3DIM_Dimbulah 66 kV | Power Factor | 0.96266 | 0.96264 | 0.95158 | 0.96287 | 0.96294 | 0.95166 | 0.96284 | 0.96293 | 0.9515 | 0.96286 | 0.96294 | 0.95152 | 0.96266 | 0.96399 | 0.95137
FN | 10020859 | 3DIM | DIMBULAH | 3DIM_Dimbulah 66 kV | Rating (A) | 218 | 269 | 253 | 218 | 269 | 253 | 218 | 269 | 253 | 218 | 269 | 253 | 218 | 269 | 253
FN | 10020859 | 3DIM | DIMBULAH | 3DIM_Dimbulah 66 kV | Time | 16:30 | 18:30 | 0:00 | 16:30 | 18:30 | 0:00 | 16:30 | 18:30 | 0:00 | 16:30 | 18:30 | 0:00 | 16:30 | 18:30 | 0:00
FN | 10020859 | 3DIM | DIMBULAH | 3DIM_Dimbulah 66 kV | Voltage at Constrained Conductor | 68.1794 | 67.9656 | 68.4142 | 68.2163 | 68.044 | 68.4445 | 68.197 | 68.0363 | 68.3623 | 68.2101 | 68.0435 | 68.3705 | 68.1764 | 68.8065 | 68.2954
FN | 10129304 | 3RA1 | RAVENSHOE NO 1 | 3RA1_Ravenshoe No 1 66 kV | % of Rated A | 10.2469 | 5.811 | 5.6128 | 9.7316 | 5.5136 | 5.3286 | 9.7414 | 5.5151 | 5.3372 | 9.7405 | 5.5151 | 5.3368 | 9.7362 | 5.4593 | 5.3442
FN | 10129304 | 3RA1 | RAVENSHOE NO 1 | 3RA1_Ravenshoe No 1 66 kV | Limiting Line Name | TR_LINE 4408_1 | TR_LINE 4408_1 | TR_LINE 4408_1 | TR_LINE 4408_1 | TR_LINE 4408_1 | TR_LINE 4408_1 | TR_LINE 4408_1 | TR_LINE 4408_1 | TR_LINE 4408_1 | TR_LINE 4408_1 | TR_LINE 4408_1 | TR_LINE 4408_1 | TR_LINE 4408_1 | TR_LINE 4408_1 | TR_LINE 4408_1
FN | 10129304 | 3RA1 | RAVENSHOE NO 1 | 3RA1_Ravenshoe No 1 66 kV | Loading (A) | 17.3172 | 14.0044 | 13.1901 | 16.4465 | 13.2878 | 12.5223 | 16.463 | 13.2914 | 12.5425 | 16.4615 | 13.2915 | 12.5414 | 16.4542 | 13.1569 | 12.5588
FN | 10129304 | 3RA1 | RAVENSHOE NO 1 | 3RA1_Ravenshoe No 1 66 kV | Loading (MVA) | 2.043 | 1.6313 | 1.5492 | 1.942 | 1.5503 | 1.4723 | 1.9421 | 1.5503 | 1.4725 | 1.9421 | 1.5503 | 1.4724 | 1.942 | 1.5369 | 1.4726
FN | 10129304 | 3RA1 | RAVENSHOE NO 1 | 3RA1_Ravenshoe No 1 66 kV | Loading (MW) | 1.92 | 1.5445 | 1.4707 | 1.8285 | 1.4709 | 1.4007 | 1.8285 | 1.4709 | 1.4007 | 1.8285 | 1.4709 | 1.4007 | 1.8285 | 1.4588 | 1.4007
FN | 10129304 | 3RA1 | RAVENSHOE NO 1 | 3RA1_Ravenshoe No 1 66 kV | Power Factor | 0.93979 | 0.94678 | 0.94934 | 0.94156 | 0.9488 | 0.95138 | 0.9415 | 0.94878 | 0.95126 | 0.9415 | 0.94878 | 0.95127 | 0.94153 | 0.94922 | 0.95116
FN | 10129304 | 3RA1 | RAVENSHOE NO 1 | 3RA1_Ravenshoe No 1 66 kV | Rating (A) | 169 | 241 | 235 | 169 | 241 | 235 | 169 | 241 | 235 | 169 | 241 | 235 | 169 | 241 | 235
FN | 10129304 | 3RA1 | RAVENSHOE NO 1 | 3RA1_Ravenshoe No 1 66 kV | Time | 15:30 | 18:00 | 7:00 | 15:30 | 18:00 | 7:00 | 15:30 | 18:00 | 7:00 | 15:30 | 18:00 | 7:00 | 15:30 | 17:30 | 7:00
FN | 10129304 | 3RA1 | RAVENSHOE NO 1 | 3RA1_Ravenshoe No 1 66 kV | Voltage at Constrained Conductor | 68.1121 | 67.2518 | 67.8118 | 68.1725 | 67.3588 | 67.8801 | 68.109 | 67.3424 | 67.7791 | 68.1147 | 67.3417 | 67.7849 | 68.1426 | 67.441 | 67.698
FN | 10131933 | 3MA2 | 3MA2 | 3MA2_Mareeba No 2 66 kV | % of Rated A | 57.0952 | 40.0967 | 29.6108 | 56.3655 | 39.6924 | 29.2697 | 55.3407 | 38.7962 | 28.6099 | 56.0073 | 39.2644 | 28.9824 | 56.7643 | 39.7831 | 29.2431
FN | 10131933 | 3MA2 | 3MA2 | 3MA2_Mareeba No 2 66 kV | Limiting Line Name | TR_LINE 5351_1 | TR_LINE 5351_1 | TR_LINE 5351_1 | TR_LINE 5351_1 | TR_LINE 5351_1 | TR_LINE 5351_1 | TR_LINE 5351_1 | TR_LINE 5351_1 | TR_LINE 5351_1 | TR_LINE 5351_1 | TR_LINE 5351_1 | TR_LINE 5351_1 | TR_LINE 5351_1 | TR_LINE 5351_1 | TR_LINE 5351_1
FN | 10131933 | 3MA2 | 3MA2 | 3MA2_Mareeba No 2 66 kV | Loading (A) | 96.491 | 96.633 | 69.5853 | 95.2577 | 95.6586 | 68.7838 | 93.5258 | 93.4988 | 67.2332 | 94.6524 | 94.6273 | 68.1087 | 95.9317 | 95.8773 | 68.7213
FN | 10131933 | 3MA2 | 3MA2 | 3MA2_Mareeba No 2 66 kV | Loading (MVA) | 11.523 | 11.5303 | 8.2876 | 11.3806 | 11.4109 | 8.1971 | 11.1706 | 11.1662 | 8.0393 | 11.3073 | 11.3029 | 8.1451 | 11.4557 | 11.4517 | 8.2241
FN | 10131933 | 3MA2 | 3MA2 | 3MA2_Mareeba No 2 66 kV | Loading (MW) | 11.3421 | 11.3528 | 7.8417 | 11.1909 | 11.2078 | 7.7383 | 10.987 | 10.9822 | 7.5679 | 11.1004 | 11.0956 | 7.6456 | 11.2889 | 11.284 | 7.7745
FN | 10131933 | 3MA2 | 3MA2 | 3MA2_Mareeba No 2 66 kV | Power Factor | 0.98431 | 0.98461 | 0.9462 | 0.98334 | 0.9822 | 0.94402 | 0.98357 | 0.98352 | 0.94137 | 0.98171 | 0.98166 | 0.93868 | 0.98544 | 0.98536 | 0.94533
FN | 10131933 | 3MA2 | 3MA2 | 3MA2_Mareeba No 2 66 kV | Rating (A) | 169 | 241 | 235 | 169 | 241 | 235 | 169 | 241 | 235 | 169 | 241 | 235 | 169 | 241 | 235
FN | 10131933 | 3MA2 | 3MA2 | 3MA2_Mareeba No 2 66 kV | Time | 16:30 | 17:00 | 22:00 | 16:30 | 17:00 | 22:00 | 16:30 | 17:00 | 22:00 | 16:30 | 17:00 | 22:00 | 16:30 | 17:00 | 22:00
FN | 10131933 | 3MA2 | 3MA2 | 3MA2_Mareeba No 2 66 kV | Voltage at Constrained Conductor | 68.9472 | 68.8897 | 68.7624 | 68.9769 | 68.8709 | 68.8042 | 68.9579 | 68.9509 | 69.0357 | 68.9707 | 68.9622 | 69.045 | 68.9442 | 68.9594 | 69.0935
FN | 10132678 | 4LAK | 7285 LAKELAND 132kV | 7285_4LAK (Lakeland) 132kV | % of Rated A | 8.3417 | 7.8084 | 8.3354 | 8.3135 | 7.8008 | 8.3265 | 8.3193 | 7.7864 | 8.2885 | 8.3194 | 7.7864 | 8.2888 | 8.3462 | 7.8149 | 8.3282
FN | 10132678 | 4LAK | 7285 LAKELAND 132kV | 7285_4LAK (Lakeland) 132kV | Limiting Line Name | TR_LINE 37686_1 | TR_LINE 37686_1 | TR_LINE 37686_1 | TR_LINE 37686_1 | TR_LINE 37686_1 | TR_LINE 37686_1 | TR_LINE 37686_1 | TR_LINE 37686_1 | TR_LINE 37686_1 | TR_LINE 37686_1 | TR_LINE 37686_1 | TR_LINE 37686_1 | TR_LINE 37686_1 | TR_LINE 37686_1 | TR_LINE 37686_1
FN | 10132678 | 4LAK | 7285 LAKELAND 132kV | 7285_4LAK (Lakeland) 132kV | Loading (A) | 42.3759 | 42.478 | 40.0097 | 42.2325 | 42.4362 | 39.9671 | 42.2623 | 42.358 | 39.7848 | 42.2626 | 42.3579 | 39.7862 | 42.3986 | 42.5133 | 39.9753
FN | 10132678 | 4LAK | 7285 LAKELAND 132kV | 7285_4LAK (Lakeland) 132kV | Loading (MVA) | 10.1492 | 10.1656 | 9.7069 | 10.1206 | 10.1511 | 9.7026 | 10.0679 | 10.0849 | 9.5959 | 10.0682 | 10.0849 | 9.5967 | 10.0987 | 10.1222 | 9.6434
FN | 10132678 | 4LAK | 7285 LAKELAND 132kV | 7285_4LAK (Lakeland) 132kV | Loading (MW) | 6.6028 | 6.7068 | 4.7878 | 6.5024 | 6.6009 | 4.7192 | 6.5021 | 6.6026 | 4.7203 | 6.5021 | 6.6026 | 4.7203 | 6.6019 | 6.7056 | 4.7873
FN | 10132678 | 4LAK | 7285 LAKELAND 132kV | 7285_4LAK (Lakeland) 132kV | Power Factor | 0.65057 | 0.65975 | 0.49324 | 0.64249 | 0.65026 | 0.48638 | 0.64583 | 0.6547 | 0.49191 | 0.64581 | 0.6547 | 0.49187 | 0.65374 | 0.66246 | 0.49643
FN | 10132678 | 4LAK | 7285 LAKELAND 132kV | 7285_4LAK (Lakeland) 132kV | Rating (A) | 508 | 544 | 480 | 508 | 544 | 480 | 508 | 544 | 480 | 508 | 544 | 480 | 508 | 544 | 480
FN | 10132678 | 4LAK | 7285 LAKELAND 132kV | 7285_4LAK (Lakeland) 132kV | Time | 16:30 | 17:00 | 23:00 | 16:30 | 17:00 | 23:00 | 16:30 | 17:00 | 23:00 | 16:30 | 17:00 | 23:00 | 16:30 | 17:00 | 23:00
FN | 10132678 | 4LAK | 7285 LAKELAND 132kV | 7285_4LAK (Lakeland) 132kV | Voltage at Constrained Conductor | 138.2771 | 138.1681 | 140.0724 | 138.356 | 138.1071 | 140.1603 | 137.5389 | 137.4605 | 139.2542 | 137.5415 | 137.4604 | 139.2612 | 137.5159 | 137.4644 | 139.277
FN | 80076156 | 3HLA | 3HLA | 3HLA_Helenvale 66 kV | % of Rated A | 11.467 | 11.2487 | 8.6546 | 11.2346 | 10.9044 | 8.4892 | 11.1626 | 10.9456 | 8.5123 | 11.1624 | 10.9457 | 8.5121 | 11.3872 | 11.164 | 8.6643
FN | 80076156 | 3HLA | 3HLA | 3HLA_Helenvale 66 kV | Limiting Line Name | TR_LINE 39200_1 | TR_LINE 39200_1 | TR_LINE 68493_1 | TR_LINE 39200_1 | TR_LINE 39200_1 | TR_LINE 68493_1 | TR_LINE 39200_1 | TR_LINE 39200_1 | TR_LINE 68493_1 | TR_LINE 39200_1 | TR_LINE 39200_1 | TR_LINE 68493_1 | TR_LINE 39200_1 | TR_LINE 39200_1 | TR_LINE 68493_1
FN | 80076156 | 3HLA | 3HLA | 3HLA_Helenvale 66 kV | Loading (A) | 43.3453 | 44.8804 | 32.0219 | 42.4668 | 43.5086 | 31.4102 | 42.1945 | 43.6731 | 31.4889 | 42.1937 | 43.6732 | 31.4883 | 43.0436 | 44.5443 | 32.058
FN | 80076156 | 3HLA | 3HLA | 3HLA_Helenvale 66 kV | Loading (MVA) | 5.0939 | 5.2678 | 3.7442 | 4.9949 | 5.1108 | 3.6766 | 4.9949 | 5.1647 | 3.6773 | 4.9949 | 5.1647 | 3.6773 | 5.093 | 5.2663 | 3.7443
FN | 80076156 | 3HLA | 3HLA | 3HLA_Helenvale 66 kV | Loading (MW) | 5.0935 | 5.2678 | 3.7364 | 4.9941 | 5.1105 | 3.6696 | 4.9935 | 5.1644 | 3.6711 | 4.9935 | 5.1644 | 3.6711 | 5.0923 | 5.2663 | 3.7364
FN | 80076156 | 3HLA | 3HLA | 3HLA_Helenvale 66 kV | Power Factor | 0.99993 | 1 | 0.99791 | 0.99983 | 0.99994 | 0.99812 | 0.99973 | 0.99993 | 0.99831 | 0.99973 | 0.99993 | 0.99831 | 0.99988 | 0.99999 | 0.99789
FN | 80076156 | 3HLA | 3HLA | 3HLA_Helenvale 66 kV | Rating (A) | 378 | 399 | 370 | 378 | 399 | 370 | 378 | 399 | 370 | 378 | 399 | 370 | 378 | 399 | 370
FN | 80076156 | 3HLA | 3HLA | 3HLA_Helenvale 66 kV | Time | 16:30 | 17:00 | 22:00 | 16:30 | 17:30 | 22:00 | 16:30 | 17:00 | 22:00 | 16:30 | 17:00 | 22:00 | 16:30 | 17:00 | 22:00
FN | 80076156 | 3HLA | 3HLA | 3HLA_Helenvale 66 kV | Voltage at Constrained Conductor | 67.8492 | 67.7655 | 67.5077 | 67.908 | 67.8196 | 67.5786 | 68.3452 | 68.277 | 67.4235 | 68.3466 | 68.2769 | 67.4249 | 68.3127 | 68.2582 | 67.4338
FN | 83003861 | 3CHI | CHILLAGOE FDR | 3CHI_Chillagoe 66 kV | % of Rated A | 9.0808 | 8.6223 | 9.3452 | 9.0724 | 8.6096 | 9.3368 | 9.0754 | 8.6121 | 9.3539 | 9.0733 | 8.6106 | 9.3524 | 9.0813 | 8.5966 | 9.3667
FN | 83003861 | 3CHI | CHILLAGOE FDR | 3CHI_Chillagoe 66 kV | Limiting Line Name | TR_LINE 104013_1 | TR_LINE 104013_1 | TR_LINE 104013_1 | TR_LINE 104013_1 | TR_LINE 104013_1 | TR_LINE 104013_1 | TR_LINE 104013_1 | TR_LINE 104013_1 | TR_LINE 104013_1 | TR_LINE 104013_1 | TR_LINE 104013_1 | TR_LINE 104013_1 | TR_LINE 104013_1 | TR_LINE 104013_1 | TR_LINE 104013_1
FN | 83003861 | 3CHI | CHILLAGOE FDR | 3CHI_Chillagoe 66 kV | Loading (A) | 49.7629 | 49.9233 | 48.6887 | 49.7165 | 49.8498 | 48.6449 | 49.7332 | 49.8638 | 48.7339 | 49.7219 | 49.8553 | 48.7258 | 49.7655 | 49.7744 | 48.8003
FN | 83003861 | 3CHI | CHILLAGOE FDR | 3CHI_Chillagoe 66 kV | Loading (MVA) | 5.573 | 5.5778 | 5.4875 | 5.5728 | 5.5775 | 5.4873 | 5.5729 | 5.5776 | 5.4877 | 5.5728 | 5.5776 | 5.4876 | 5.573 | 5.5773 | 5.4879
FN | 83003861 | 3CHI | CHILLAGOE FDR | 3CHI_Chillagoe 66 kV | Loading (MW) | 5.259 | 5.2714 | 5.1541 | 5.259 | 5.2714 | 5.1541 | 5.259 | 5.2714 | 5.1541 | 5.259 | 5.2714 | 5.1541 | 5.259 | 5.2713 | 5.1542
FN | 83003861 | 3CHI | CHILLAGOE FDR | 3CHI_Chillagoe 66 kV | Power Factor | 0.94366 | 0.94507 | 0.93925 | 0.94368 | 0.94511 | 0.93927 | 0.94367 | 0.9451 | 0.93922 | 0.94368 | 0.94511 | 0.93923 | 0.94366 | 0.94515 | 0.93919
FN | 83003861 | 3CHI | CHILLAGOE FDR | 3CHI_Chillagoe 66 kV | Rating (A) | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521
FN | 83003861 | 3CHI | CHILLAGOE FDR | 3CHI_Chillagoe 66 kV | Time | 16:30 | 19:30 | 7:30 | 16:30 | 19:30 | 7:30 | 16:30 | 19:30 | 7:30 | 16:30 | 19:30 | 7:30 | 16:30 | 19:30 | 7:30
FN | 83003861 | 3CHI | CHILLAGOE FDR | 3CHI_Chillagoe 66 kV | Voltage at Constrained Conductor | 64.658 | 64.5059 | 65.0706 | 64.7164 | 64.598 | 65.1273 | 64.6954 | 64.5804 | 65.0123 | 64.7096 | 64.5911 | 65.0228 | 64.6547 | 64.6929 | 64.9268
FN | 83031299 | MUNGANA | MUNGANA | Mungana 66 kV | % of Rated A | 10.2406 | 9.4081 | 10.0146 | 10.2306 | 9.414 | 10.0058 | 10.1956 | 9.3974 | 10.0237 | 10.1937 | 9.3956 | 10.022 | 10.1882 | 9.4195 | 10.037
FN | 83031299 | MUNGANA | MUNGANA | Mungana 66 kV | Limiting Line Name | TR_LINE 104003_1 | TR_LINE 104003_1 | TR_LINE 104003_1 | TR_LINE 104003_1 | TR_LINE 104003_1 | TR_LINE 104003_1 | TR_LINE 104003_1 | TR_LINE 104003_1 | TR_LINE 104003_1 | TR_LINE 104003_1 | TR_LINE 104003_1 | TR_LINE 104003_1 | TR_LINE 104003_1 | TR_LINE 104003_1 | TR_LINE 104003_1
FN | 83031299 | MUNGANA | MUNGANA | Mungana 66 kV | Loading (A) | 46.7994 | 45.8175 | 47.2688 | 46.754 | 45.8461 | 47.2272 | 46.5938 | 45.7652 | 47.3117 | 46.5853 | 45.7564 | 47.304 | 46.5601 | 45.8728 | 47.3747
FN | 83031299 | MUNGANA | MUNGANA | Mungana 66 kV | Loading (MVA) | 5.2309 | 5.0931 | 5.2998 | 5.2309 | 5.1397 | 5.2998 | 5.2309 | 5.1397 | 5.2998 | 5.2309 | 5.0931 | 5.2998 | 5.2309 | 5.1397 | 5.2998
FN | 83031299 | MUNGANA | MUNGANA | Mungana 66 kV | Loading (MW) | 4.8335 | 4.7062 | 4.8972 | 4.8335 | 4.7493 | 4.8972 | 4.8335 | 4.7493 | 4.8972 | 4.8335 | 4.7062 | 4.8972 | 4.8335 | 4.7493 | 4.8972
FN | 83031299 | MUNGANA | MUNGANA | Mungana 66 kV | Power Factor | 0.92404 | 0.92404 | 0.92404 | 0.92404 | 0.92404 | 0.92404 | 0.92404 | 0.92404 | 0.92404 | 0.92404 | 0.92404 | 0.92404 | 0.92404 | 0.92404 | 0.92404
FN | 83031299 | MUNGANA | MUNGANA | Mungana 66 kV | Rating (A) | 457 | 487 | 472 | 457 | 487 | 472 | 457 | 487 | 472 | 457 | 487 | 472 | 457 | 487 | 472
FN | 83031299 | MUNGANA | MUNGANA | Mungana 66 kV | Time | 14:30 | 19:30 | 7:30 | 14:30 | 20:30 | 7:30 | 14:30 | 20:30 | 7:30 | 14:30 | 19:30 | 7:30 | 14:30 | 20:30 | 7:30
FN | 83031299 | MUNGANA | MUNGANA | Mungana 66 kV | Voltage at Constrained Conductor | 64.5322 | 64.1787 | 64.7328 | 64.5947 | 64.726 | 64.7898 | 64.8168 | 64.8403 | 64.6742 | 64.8287 | 64.2643 | 64.6847 | 64.8638 | 64.6883 | 64.5881
FN | 83842085 | FDR 7333 | 132KV CANO 7333 FDR | 7333_Cairns North 132 kV | % of Rated A | 23.2958 | 21.3482 | 18.5506 | 22.8923 | 20.9818 | 18.2584 | 22.7714 | 20.8721 | 18.1712 | 22.8117 | 20.9086 | 18.2012 | 22.9729 | 21.055 | 18.3195
FN | 83842085 | FDR 7333 | 132KV CANO 7333 FDR | 7333_Cairns North 132 kV | Limiting Line Name | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2
FN | 83842085 | FDR 7333 | 132KV CANO 7333 FDR | 7333_Cairns North 132 kV | Loading (A) | 110.1893 | 106.1008 | 82.7358 | 108.2804 | 104.2796 | 81.4326 | 107.7086 | 103.7341 | 81.0436 | 107.8992 | 103.9159 | 81.1772 | 108.6618 | 104.6434 | 81.7051
FN | 83842085 | FDR 7333 | 132KV CANO 7333 FDR | 7333_Cairns North 132 kV | Loading (MVA) | 26.4523 | 25.4708 | 20.2441 | 25.994 | 25.0336 | 19.9273 | 25.8568 | 24.9026 | 19.8324 | 25.9025 | 24.9463 | 19.8635 | 26.0856 | 25.1209 | 19.9889
FN | 83842085 | FDR 7333 | 132KV CANO 7333 FDR | 7333_Cairns North 132 kV | Loading (MW) | 25.8012 | 24.7489 | 18.8858 | 25.3106 | 24.2784 | 18.527 | 25.1634 | 24.1372 | 18.4194 | 25.2125 | 24.1843 | 18.4552 | 25.4087 | 24.3725 | 18.5987
FN | 83842085 | FDR 7333 | 132KV CANO 7333 FDR | 7333_Cairns North 132 kV | Power Factor | 0.97539 | 0.97166 | 0.9329 | 0.97371 | 0.96983 | 0.92973 | 0.97318 | 0.96926 | 0.92875 | 0.97336 | 0.96945 | 0.9291 | 0.97405 | 0.97021 | 0.93045
FN | 83842085 | FDR 7333 | 132KV CANO 7333 FDR | 7333_Cairns North 132 kV | Rating (A) | 473 | 497 | 446 | 473 | 497 | 446 | 473 | 497 | 446 | 473 | 497 | 446 | 473 | 497 | 446
FN | 83842085 | FDR 7333 | 132KV CANO 7333 FDR | 7333_Cairns North 132 kV | Time | 16:00 | 17:00 | 23:00 | 16:00 | 17:00 | 23:00 | 16:00 | 17:00 | 23:00 | 16:00 | 17:00 | 23:00 | 16:00 | 17:00 | 23:00
FN | 83842085 | FDR 7333 | 132KV CANO 7333 FDR | 7333_Cairns North 132 kV | Voltage at Constrained Conductor | 138.6 | 138.6 | 141.2682 | 138.6 | 138.6 | 141.283 | 138.6 | 138.6 | 141.2849 | 138.6 | 138.6 | 141.2733 | 138.6 | 138.6 | 141.2472
FN | 83842089 | 7332 | Cairns North 132 kV | 7332_Cairns North 132 kV | % of Rated A | 24.4238 | 22.3808 | 19.4383 | 24.0002 | 21.9961 | 19.1313 | 23.8733 | 21.8809 | 19.0397 | 23.9156 | 21.9193 | 19.0712 | 24.0848 | 22.073 | 19.1955
FN | 83842089 | 7332 | Cairns North 132 kV | 7332_Cairns North 132 kV | Limiting Line Name | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2
FN | 83842089 | 7332 | Cairns North 132 kV | 7332_Cairns North 132 kV | Loading (A) | 115.5247 | 111.2326 | 86.6946 | 113.5208 | 109.3206 | 85.3258 | 112.9205 | 108.748 | 84.9172 | 113.1206 | 108.9388 | 85.0576 | 113.9212 | 109.7026 | 85.612
FN | 83842089 | 7332 | Cairns North 132 kV | 7332_Cairns North 132 kV | Loading (MVA) | 27.7331 | 26.7027 | 21.2128 | 27.252 | 26.2437 | 20.88 | 27.108 | 26.1063 | 20.7803 | 27.156 | 26.1521 | 20.813 | 27.3482 | 26.3355 | 20.9448
FN | 83842089 | 7332 | Cairns North 132 kV | 7332_Cairns North 132 kV | Loading (MW) | 27.0558 | 25.9518 | 19.8004 | 26.5411 | 25.4581 | 19.424 | 26.3866 | 25.31 | 19.3111 | 26.4381 | 25.3594 | 19.3488 | 26.644 | 25.5569 | 19.4993
FN | 83842089 | 7332 | Cairns North 132 kV | 7332_Cairns North 132 kV | Power Factor | 0.97558 | 0.97188 | 0.93342 | 0.97391 | 0.97006 | 0.93027 | 0.97339 | 0.9695 | 0.9293 | 0.97357 | 0.96969 | 0.92965 | 0.97425 | 0.97044 | 0.93099
FN | 83842089 | 7332 | Cairns North 132 kV | 7332_Cairns North 132 kV | Rating (A) | 473 | 497 | 446 | 473 | 497 | 446 | 473 | 497 | 446 | 473 | 497 | 446 | 473 | 497 | 446
FN | 83842089 | 7332 | Cairns North 132 kV | 7332_Cairns North 132 kV | Time | 16:00 | 17:00 | 23:00 | 16:00 | 17:00 | 23:00 | 16:00 | 17:00 | 23:00 | 16:00 | 17:00 | 23:00 | 16:00 | 17:00 | 23:00
FN | 83842089 | 7332 | Cairns North 132 kV | 7332_Cairns North 132 kV | Voltage at Constrained Conductor | 138.6 | 138.6 | 141.2682 | 138.6 | 138.6 | 141.283 | 138.6 | 138.6 | 141.2849 | 138.6 | 138.6 | 141.2733 | 138.6 | 138.6 | 141.2472
FN | 84463555 | 3COO | COOKTOWN FEEDER | 3COO_Cooktown 66 kV | % of Rated A | 15.7077 | 16.2464 | 10.8808 | 15.3413 | 15.674 | 10.6311 | 15.2368 | 15.7548 | 10.7021 | 15.2364 | 15.7548 | 10.7016 | 15.5965 | 16.1213 | 10.9587
FN | 84463555 | 3COO | COOKTOWN FEEDER | 3COO_Cooktown 66 kV | Limiting Line Name | TR_CABLE 12_1 | TR_CABLE 12_1 | TR_CABLE 12_1 | TR_CABLE 12_1 | TR_CABLE 12_1 | TR_CABLE 12_1 | TR_CABLE 12_1 | TR_CABLE 12_1 | TR_CABLE 12_1 | TR_CABLE 12_1 | TR_CABLE 12_1 | TR_CABLE 12_1 | TR_CABLE 12_1 | TR_CABLE 12_1 | TR_CABLE 12_1
FN | 84463555 | 3COO | COOKTOWN FEEDER | 3COO_Cooktown 66 kV | Loading (A) | 38.955 | 40.2912 | 26.9844 | 38.0465 | 38.8716 | 26.3651 | 37.7872 | 39.0719 | 26.5412 | 37.7864 | 39.072 | 26.54 | 38.6793 | 39.9808 | 27.1775
FN | 84463555 | 3COO | COOKTOWN FEEDER | 3COO_Cooktown 66 kV | Loading (MVA) | 4.4841 | 4.6277 | 3.1507 | 4.386 | 4.5258 | 3.0819 | 4.3857 | 4.526 | 3.082 | 4.3857 | 4.526 | 3.082 | 4.4844 | 4.6273 | 3.1508
FN | 84463555 | 3COO | COOKTOWN FEEDER | 3COO_Cooktown 66 kV | Loading (MW) | 4.3935 | 4.5333 | 3.0911 | 4.2978 | 4.4345 | 3.0238 | 4.2977 | 4.4345 | 3.0239 | 4.2977 | 4.4345 | 3.0239 | 4.3935 | 4.5332 | 3.0911
FN | 84463555 | 3COO | COOKTOWN FEEDER | 3COO_Cooktown 66 kV | Power Factor | 0.97978 | 0.97961 | 0.98109 | 0.97989 | 0.97983 | 0.98116 | 0.97994 | 0.97978 | 0.98113 | 0.97994 | 0.97978 | 0.98113 | 0.97973 | 0.97967 | 0.98105
FN | 84463555 | 3COO | COOKTOWN FEEDER | 3COO_Cooktown 66 kV | Rating (A) | 248 | 248 | 248 | 248 | 248 | 248 | 248 | 248 | 248 | 248 | 248 | 248 | 248 | 248 | 248
FN | 84463555 | 3COO | COOKTOWN FEEDER | 3COO_Cooktown 66 kV | Time | 16:30 | 17:00 | 7:00 | 16:30 | 17:00 | 7:00 | 16:30 | 17:00 | 7:00 | 16:30 | 17:00 | 7:00 | 16:30 | 17:00 | 7:00
FN | 84463555 | 3COO | COOKTOWN FEEDER | 3COO_Cooktown 66 kV | Voltage at Constrained Conductor | 66.4592 | 66.3118 | 67.4111 | 66.5569 | 67.22 | 67.4878 | 67.0093 | 66.8794 | 67.043 | 67.0107 | 66.8793 | 67.046 | 66.9371 | 66.8211 | 66.9353
FN | 85352673 | 7455 | 7455 SOLAR 132KV FDR | Kidston Solar Farm (Genex) | % of Rated A | 0.028281 | 0.027987 | 0.028399 | 0.028285 | 0.027993 | 0.028403 | 0.028485 | 0.028395 | 0.028518 | 0.028485 | 0.028395 | 0.028518 | 0.028476 | 0.028384 | 0.028511
FN | 85352673 | 7455 | 7455 SOLAR 132KV FDR | Kidston Solar Farm (Genex) | Limiting Line Name | Genex_Interconnection | Genex_Interconnection | Genex_Interconnection | Genex_Interconnection | Genex_Interconnection | Genex_Interconnection | Genex_Interconnection | Genex_Interconnection | Genex_Interconnection | Genex_Interconnection | Genex_Interconnection | Genex_Interconnection | Genex_Interconnection | Genex_Interconnection | Genex_Interconnection
FN | 85352673 | 7455 | 7455 SOLAR 132KV FDR | Kidston Solar Farm (Genex) | Loading (A) | 0.28281 | 0.27987 | 0.28399 | 0.28285 | 0.27993 | 0.28403 | 0.28485 | 0.28395 | 0.28518 | 0.28485 | 0.28395 | 0.28518 | 0.28476 | 0.28384 | 0.28511
FN | 85352673 | 7455 | 7455 SOLAR 132KV FDR | Kidston Solar Farm (Genex) | Loading (MVA) | 0.06968 | 0.068241 | 0.070263 | 0.0697 | 0.068269 | 0.070284 | 0.070687 | 0.070245 | 0.070853 | 0.070687 | 0.070245 | 0.070853 | 0.070646 | 0.070187 | 0.07082
FN | 85352673 | 7455 | 7455 SOLAR 132KV FDR | Kidston Solar Farm (Genex) | Loading (MW) | 5.0637e-08 | 4.9588e-08 | 5.1062e-08 | 5.0646e-08 | 4.9607e-08 | 5.1074e-08 | 5.1366e-08 | 5.1047e-08 | 5.1484e-08 | 5.1362e-08 | 5.1046e-08 | 5.1486e-08 | 5.1336e-08 | 5.1001e-08 | 5.1464e-08
FN | 85352673 | 7455 | 7455 SOLAR 132KV FDR | Kidston Solar Farm (Genex) | Power Factor | 7.267e-07 | 7.2666e-07 | 7.2673e-07 | 7.2662e-07 | 7.2663e-07 | 7.2668e-07 | 7.2667e-07 | 7.267e-07 | 7.2664e-07 | 7.2661e-07 | 7.2669e-07 | 7.2665e-07 | 7.2667e-07 | 7.2664e-07 | 7.2669e-07
FN | 85352673 | 7455 | 7455 SOLAR 132KV FDR | Kidston Solar Farm (Genex) | Rating (A) | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000
FN | 85352673 | 7455 | 7455 SOLAR 132KV FDR | Kidston Solar Farm (Genex) | Time | 9:00 | 20:30 | 4:00 | 9:00 | 20:30 | 4:00 | 9:00 | 21:30 | 4:00 | 9:00 | 21:30 | 4:00 | 9:00 | 21:30 | 4:00
FN | 85352673 | 7455 | 7455 SOLAR 132KV FDR | Kidston Solar Farm (Genex) | Voltage at Constrained Conductor | 142.2503 | 140.773 | 142.8438 | 142.2706 | 140.8026 | 142.8652 | 143.2739 | 142.8251 | 143.4423 | 143.2738 | 142.825 | 143.4423 | 143.2324 | 142.7668 | 143.4087
MK | 20011116 | NL-WR-1 | Newlands-Wirralie | NL-WR-1_Newlands-Wirralie 1 66 kV | % of Rated A | 4.7256 | 4.3305 | 4.961 | 4.7261 | 4.331 | 4.895 | 4.7261 | 4.331 | 4.895 | 4.7261 | 4.331 | 4.895 | 4.7256 | 4.3305 | 4.961
MK | 20011116 | NL-WR-1 | Newlands-Wirralie | NL-WR-1_Newlands-Wirralie 1 66 kV | Limiting Line Name | TR_LINE 180753_1 | TR_LINE 180753_1 | TR_LINE 180753_1 | TR_LINE 180753_1 | TR_LINE 180753_1 | TR_LINE 180753_1 | TR_LINE 180753_1 | TR_LINE 180753_1 | TR_LINE 180753_1 | TR_LINE 180753_1 | TR_LINE 180753_1 | TR_LINE 180753_1 | TR_LINE 180753_1 | TR_LINE 180753_1 | TR_LINE 180753_1
MK | 20011116 | NL-WR-1 | Newlands-Wirralie | NL-WR-1_Newlands-Wirralie 1 66 kV | Loading (A) | 8.8841 | 8.8775 | 9.1778 | 8.885 | 8.8786 | 9.0558 | 8.885 | 8.8786 | 9.0558 | 8.885 | 8.8786 | 9.0558 | 8.884 | 8.8775 | 9.1778
MK | 20011116 | NL-WR-1 | Newlands-Wirralie | NL-WR-1_Newlands-Wirralie 1 66 kV | Loading (MVA) | 1.0538 | 1.0656 | 1.1143 | 1.054 | 1.0659 | 1.0866 | 1.054 | 1.0659 | 1.0866 | 1.054 | 1.0659 | 1.0866 | 1.0538 | 1.0656 | 1.1143
MK | 20011116 | NL-WR-1 | Newlands-Wirralie | NL-WR-1_Newlands-Wirralie 1 66 kV | Loading (MW) | 0.22555 | 0.2723 | 0.20718 | 0.22555 | 0.2723 | 0.20711 | 0.22555 | 0.2723 | 0.20711 | 0.22555 | 0.2723 | 0.20711 | 0.22555 | 0.2723 | 0.20718
MK | 20011116 | NL-WR-1 | Newlands-Wirralie | NL-WR-1_Newlands-Wirralie 1 66 kV | Power Factor | 0.21404 | 0.25553 | 0.18593 | 0.214 | 0.25547 | 0.1906 | 0.214 | 0.25547 | 0.1906 | 0.214 | 0.25548 | 0.1906 | 0.21404 | 0.25553 | 0.18593
MK | 20011116 | NL-WR-1 | Newlands-Wirralie | NL-WR-1_Newlands-Wirralie 1 66 kV | Rating (A) | 188 | 205 | 185 | 188 | 205 | 185 | 188 | 205 | 185 | 188 | 205 | 185 | 188 | 205 | 185
MK | 20011116 | NL-WR-1 | Newlands-Wirralie | NL-WR-1_Newlands-Wirralie 1 66 kV | Time | 9:30 | 21:30 | 2:30 | 9:30 | 21:30 | 2:30 | 9:30 | 21:30 | 2:30 | 9:30 | 21:30 | 2:30 | 9:30 | 21:30 | 2:30
MK | 20011116 | NL-WR-1 | Newlands-Wirralie | NL-WR-1_Newlands-Wirralie 1 66 kV | Voltage at Constrained Conductor | 68.4809 | 69.3031 | 70.0955 | 68.4874 | 69.3106 | 69.2761 | 68.4875 | 69.3106 | 69.2761 | 68.4874 | 69.3105 | 69.276 | 68.4808 | 69.3029 | 70.0954
MK | 30053795 | 3045 | SARINA 1 | 3045_Sarina No 1 33 kV | % of Rated A | 38.2654 | 45.378 | 34.1886 | 38.0621 | 45.0024 | 33.8845 | 38.2911 | 45.1507 | 33.9926 | 38.4951 | 45.527 | 34.2951 | 38.9544 | 45.8242 | 34.5122
MK | 30053795 | 3045 | SARINA 1 | 3045_Sarina No 1 33 kV | Limiting Line Name | TR_LINE 136720_1 | TR_CABLE 6966_1 | TR_CABLE 6966_1 | TR_LINE 136720_1 | TR_CABLE 6966_1 | TR_CABLE 6966_1 | TR_LINE 136720_1 | TR_CABLE 6966_1 | TR_CABLE 6966_1 | TR_LINE 136720_1 | TR_CABLE 6966_1 | TR_CABLE 6966_1 | TR_LINE 136720_1 | TR_CABLE 6966_1 | TR_CABLE 6966_1
MK | 30053795 | 3045 | SARINA 1 | 3045_Sarina No 1 33 kV | Loading (A) | 144.642 | 283.6126 | 213.6706 | 143.8737 | 281.2649 | 211.7704 | 144.7392 | 282.1916 | 212.4459 | 145.5103 | 284.5437 | 214.3359 | 147.2466 | 286.4012 | 215.692
MK | 30053795 | 3045 | SARINA 1 | 3045_Sarina No 1 33 kV | Loading (MVA) | 8.3051 | 16.9298 | 12.7833 | 8.2639 | 16.7898 | 12.6704 | 8.3112 | 16.8444 | 12.7104 | 8.3524 | 16.9845 | 12.8227 | 8.4471 | 17.094 | 12.9031
MK | 30053795 | 3045 | SARINA 1 | 3045_Sarina No 1 33 kV | Loading (MW) | 7.6538 | 16.6943 | 12.7502 | 7.6167 | 16.5484 | 12.6414 | 7.6597 | 16.5988 | 12.6802 | 7.6967 | 16.7448 | 12.7886 | 7.7825 | 16.8458 | 12.8662
MK | 30053795 | 3045 | SARINA 1 | 3045_Sarina No 1 33 kV | Power Factor | 0.92157 | 0.98609 | 0.99741 | 0.92168 | 0.98562 | 0.99772 | 0.9216 | 0.98542 | 0.99762 | 0.92149 | 0.98589 | 0.99734 | 0.92132 | 0.98548 | 0.99714
MK | 30053795 | 3045 | SARINA 1 | 3045_Sarina No 1 33 kV | Rating (A) | 378 | 625 | 625 | 378 | 625 | 625 | 378 | 625 | 625 | 378 | 625 | 625 | 378 | 625 | 625
MK | 30053795 | 3045 | SARINA 1 | 3045_Sarina No 1 33 kV | Time | 16:30 | 18:30 | 22:30 | 16:30 | 18:30 | 22:30 | 16:30 | 18:30 | 22:30 | 16:30 | 18:30 | 22:30 | 16:30 | 18:30 | 22:30
MK | 30053795 | 3045 | SARINA 1 | 3045_Sarina No 1 33 kV | Voltage at Constrained Conductor | 33.1506 | 34.4641 | 34.5412 | 33.1624 | 34.4643 | 34.5433 | 33.1526 | 34.4629 | 34.5423 | 33.1405 | 34.4622 | 34.5401 | 33.121 | 34.4594 | 34.5382
MK | 30053796 | 3046 | ROSELLA | 3046_Rosella 33 kV | % of Rated A | 9.7054 | 11.5077 | 10.3741 | 9.705 | 11.5076 | 10.3734 | 9.7052 | 11.5081 | 10.3737 | 9.8831 | 11.7225 | 10.567 | 9.8835 | 11.7235 | 10.5676
MK | 30053796 | 3046 | ROSELLA | 3046_Rosella 33 kV | Limiting Line Name | TR_CABLE 7121_1 | TR_CABLE 7121_1 | TR_CABLE 7121_1 | TR_CABLE 7121_1 | TR_CABLE 7121_1 | TR_CABLE 7121_1 | TR_CABLE 7121_1 | TR_CABLE 7121_1 | TR_CABLE 7121_1 | TR_CABLE 7121_1 | TR_CABLE 7121_1 | TR_CABLE 7121_1 | TR_CABLE 7121_1 | TR_CABLE 7121_1 | TR_CABLE 7121_1
MK | 30053796 | 3046 | ROSELLA | 3046_Rosella 33 kV | Loading (A) | 39.6949 | 47.0663 | 42.4299 | 39.6936 | 47.066 | 42.4272 | 39.6944 | 47.068 | 42.4285 | 40.4218 | 47.9451 | 43.2191 | 40.4234 | 47.9492 | 43.2216
MK | 30053796 | 3046 | ROSELLA | 3046_Rosella 33 kV | Loading (MVA) | 2.3587 | 2.7805 | 2.5148 | 2.3587 | 2.7805 | 2.5148 | 2.3587 | 2.7805 | 2.5148 | 2.4015 | 2.8316 | 2.561 | 2.4015 | 2.8317 | 2.561
MK | 30053796 | 3046 | ROSELLA | 3046_Rosella 33 kV | Loading (MW) | 2.2678 | 2.6696 | 2.4169 | 2.2678 | 2.6696 | 2.4169 | 2.2678 | 2.6696 | 2.4169 | 2.309 | 2.7183 | 2.4609 | 2.309 | 2.7183 | 2.4609
MK | 30053796 | 3046 | ROSELLA | 3046_Rosella 33 kV | Power Factor | 0.96145 | 0.96014 | 0.96109 | 0.96145 | 0.96014 | 0.96109 | 0.96145 | 0.96014 | 0.96109 | 0.9615 | 0.95996 | 0.96093 | 0.9615 | 0.95996 | 0.96093
MK | 30053796 | 3046 | ROSELLA | 3046_Rosella 33 kV | Rating (A) | 409 | 409 | 409 | 409 | 409 | 409 | 409 | 409 | 409 | 409 | 409 | 409 | 409 | 409 | 409
MK | 30053796 | 3046 | ROSELLA | 3046_Rosella 33 kV | Time | 13:00 | 18:30 | 22:30 | 13:00 | 18:30 | 22:30 | 13:00 | 18:30 | 22:30 | 13:00 | 18:30 | 22:30 | 13:00 | 18:30 | 22:30
MK | 30053796 | 3046 | ROSELLA | 3046_Rosella 33 kV | Voltage at Constrained Conductor | 34.307 | 34.1073 | 34.2187 | 34.3082 | 34.1075 | 34.2208 | 34.3075 | 34.1061 | 34.2198 | 34.3005 | 34.0984 | 34.2114 | 34.2991 | 34.0956 | 34.2094
MK | 30053797 | 3047 | SARINA 2 | 3047_Sarina No 2 33 kV | % of Rated A | 41.5798 | 43.6769 | 33.1568 | 41.3159 | 43.3973 | 32.9489 | 41.5489 | 43.6391 | 33.125 | 41.8136 | 43.9198 | 33.3251 | 42.2809 | 44.4053 | 33.6779
MK | 30053797 | 3047 | SARINA 2 | 3047_Sarina No 2 33 kV | Limiting Line Name | TR_LINE 11717_1 | TR_LINE 11717_1 | TR_LINE 11717_1 | TR_LINE 11717_1 | TR_LINE 11717_1 | TR_LINE 11717_1 | TR_LINE 11717_1 | TR_LINE 11717_1 | TR_LINE 11717_1 | TR_LINE 11717_1 | TR_LINE 11717_1 | TR_LINE 11717_1 | TR_LINE 11717_1 | TR_LINE 11717_1 | TR_LINE 11717_1
MK | 30053797 | 3047 | SARINA 2 | 3047_Sarina No 2 33 kV | Loading (A) | 157.9969 | 182.5628 | 139.2527 | 156.9942 | 181.3941 | 138.3792 | 157.8795 | 182.4052 | 139.1189 | 158.8852 | 183.5782 | 139.9593 | 160.6612 | 185.6078 | 141.441
MK | 30053797 | 3047 | SARINA 2 | 3047_Sarina No 2 33 kV | Loading (MVA) | 9.1297 | 10.4726 | 8.0885 | 9.0746 | 10.4094 | 8.0399 | 9.1234 | 10.4643 | 8.0812 | 9.1786 | 10.5276 | 8.128 | 9.2765 | 10.6376 | 8.2107
MK | 30053797 | 3047 | SARINA 2 | 3047_Sarina No 2 33 kV | Loading (MW) | 8.6778 | 9.9198 | 7.7338 | 8.6275 | 9.8625 | 7.689 | 8.6719 | 9.912 | 7.7269 | 8.7222 | 9.9693 | 7.7714 | 8.8111 | 10.0684 | 7.8472
MK | 30053797 | 3047 | SARINA 2 | 3047_Sarina No 2 33 kV | Power Factor | 0.95051 | 0.94721 | 0.95614 | 0.95073 | 0.94746 | 0.95635 | 0.95051 | 0.94722 | 0.95615 | 0.95028 | 0.94697 | 0.95613 | 0.94983 | 0.94649 | 0.95574
MK | 30053797 | 3047 | SARINA 2 | 3047_Sarina No 2 33 kV | Rating (A) | 380 | 418 | 420 | 380 | 418 | 420 | 380 | 418 | 420 | 380 | 418 | 420 | 380 | 418 | 420
MK | 30053797 | 3047 | SARINA 2 | 3047_Sarina No 2 33 kV | Time | 16:30 | 18:00 | 22:30 | 16:30 | 18:00 | 22:30 | 16:30 | 18:00 | 22:30 | 16:30 | 18:00 | 22:30 | 16:30 | 18:00 | 22:30
MK | 30053797 | 3047 | SARINA 2 | 3047_Sarina No 2 33 kV | Voltage at Constrained Conductor | 33.3617 | 33.1192 | 33.5353 | 33.3719 | 33.1316 | 33.5444 | 33.3635 | 33.1218 | 33.5375 | 33.3529 | 33.109 | 33.529 | 33.3359 | 33.0892 | 33.5152
MK | 30053798 | 231 | Carmila | 231_Carmila 33 kV | % of Rated A | 29.0034 | 37.5358 | 31.5394 | 28.9916 | 37.5161 | 31.5287 | 29.0014 | 37.5311 | 31.5367 | 29.0136 | 37.5515 | 31.5478 | 29.0335 | 37.5818 | 31.5639
MK | 30053798 | 231 | Carmila | 231_Carmila 33 kV | Limiting Line Name | TR_LINE 11379_1 | TR_CABLE 34_1 | TR_CABLE 34_1 | TR_LINE 11379_1 | TR_CABLE 34_1 | TR_CABLE 34_1 | TR_LINE 11379_1 | TR_CABLE 34_1 | TR_CABLE 34_1 | TR_LINE 11379_1 | TR_CABLE 34_1 | TR_CABLE 34_1 | TR_LINE 11379_1 | TR_CABLE 34_1 | TR_CABLE 34_1
MK | 30053798 | 231 | Carmila | 231_Carmila 33 kV | Loading (A) | 44.0746 | 57.0544 | 47.9399 | 44.0566 | 57.0245 | 47.9237 | 44.0716 | 57.0473 | 47.9358 | 44.0902 | 57.0783 | 47.9527 | 44.1204 | 57.1244 | 47.9771
MK | 30053798 | 231 | Carmila | 231_Carmila 33 kV | Loading (MVA) | 2.4651 | 3.1825 | 2.7271 | 2.4651 | 3.1822 | 2.727 | 2.4651 | 3.1824 | 2.7271 | 2.4652 | 3.1827 | 2.7272 | 2.4654 | 3.183 | 2.7274
MK | 30053798 | 231 | Carmila | 231_Carmila 33 kV | Loading (MW) | 2.3344 | 3.012 | 2.5886 | 2.3343 | 3.0119 | 2.5886 | 2.3344 | 3.012 | 2.5886 | 2.3344 | 3.0121 | 2.5887 | 2.3344 | 3.0123 | 2.5887
MK | 30053798 | 231 | Carmila | 231_Carmila 33 kV | Power Factor | 0.94695 | 0.94645 | 0.94921 | 0.94697 | 0.94648 | 0.94923 | 0.94696 | 0.94646 | 0.94922 | 0.94694 | 0.94642 | 0.9492 | 0.9469 | 0.94638 | 0.94917
MK | 30053798 | 231 | Carmila | 231_Carmila 33 kV | Rating (A) | 152 | 152 | 152 | 152 | 152 | 152 | 152 | 152 | 152 | 152 | 152 | 152 | 152 | 152 | 152
MK | 30053798 | 231 | Carmila | 231_Carmila 33 kV | Time | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00
MK | 30053798 | 231 | Carmila | 231_Carmila 33 kV | Voltage at Constrained Conductor | 32.2918 | 32.2043 | 32.8432 | 32.304 | 32.2188 | 32.8531 | 32.2939 | 32.2077 | 32.8457 | 32.2814 | 32.1927 | 32.8355 | 32.2611 | 32.1704 | 32.8207
MK | 30053799 | 232 | Newlands-Glenden | 232_Newlands-Glenden 66 kV | % of Rated A | 11.5303 | 8.8141 | 6.3334 | 10.9163 | 8.3336 | 6.0228 | 10.9163 | 8.3336 | 6.0228 | 10.9163 | 8.3337 | 6.0228 | 11.5303 | 8.8143 | 6.3334
MK | 30053799 | 232 | Newlands-Glenden | 232_Newlands-Glenden 66 kV | Limiting Line Name | TR_LINE 10187_1 | TR_LINE 10187_1 | TR_LINE 10181_1 | TR_LINE 10181_1 | TR_LINE 10181_1 | TR_LINE 10181_1 | TR_LINE 10181_1 | TR_LINE 10181_1 | TR_LINE 10181_1 | TR_LINE 10181_1 | TR_LINE 10181_1 | TR_LINE 10181_1 | TR_LINE 10187_1 | TR_LINE 10187_1 | TR_LINE 10181_1
MK | 30053799 | 232 | Newlands-Glenden | 232_Newlands-Glenden 66 kV | Loading (A) | 13.3751 | 14.1026 | 9.8801 | 12.6629 | 13.3337 | 9.3956 | 12.6629 | 13.3337 | 9.3956 | 12.6629 | 13.3339 | 9.3956 | 13.3752 | 14.103 | 9.8801
MK | 30053799 | 232 | Newlands-Glenden | 232_Newlands-Glenden 66 kV | Loading (MVA) | 1.6011 | 1.7039 | 1.186 | 1.5208 | 1.6167 | 1.1279 | 1.5208 | 1.6167 | 1.1279 | 1.5208 | 1.6167 | 1.1279 | 1.6011 | 1.7039 | 1.186
MK | 30053799 | 232 | Newlands-Glenden | 232_Newlands-Glenden 66 kV | Loading (MW) | 1.5941 | 1.6963 | 1.1714 | 1.5078 | 1.6047 | 1.1045 | 1.5078 | 1.6047 | 1.1045 | 1.5078 | 1.6047 | 1.1045 | 1.5941 | 1.6963 | 1.1714
MK | 30053799 | 232 | Newlands-Glenden | 232_Newlands-Glenden 66 kV | Power Factor | 0.99567 | 0.99557 | 0.98767 | 0.99142 | 0.99259 | 0.97922 | 0.99142 | 0.99259 | 0.97922 | 0.99142 | 0.99259 | 0.97922 | 0.99567 | 0.99557 | 0.98767
MK | 30053799 | 232 | Newlands-Glenden | 232_Newlands-Glenden 66 kV | Rating (A) | 116 | 160 | 156 | 116 | 160 | 156 | 116 | 160 | 156 | 116 | 160 | 156 | 116 | 160 | 156
MK | 30053799 | 232 | Newlands-Glenden | 232_Newlands-Glenden 66 kV | Time | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00
MK | 30053799 | 232 | Newlands-Glenden | 232_Newlands-Glenden 66 kV | Voltage at Constrained Conductor | 69.1111 | 69.7557 | 69.3038 | 69.3413 | 70.0014 | 69.3109 | 69.3413 | 70.0015 | 69.3109 | 69.3412 | 70.0007 | 69.3108 | 69.1109 | 69.754 | 69.3037
MK | 30053850 | 340 | MK3-1 Farleigh | 340_MK3-1 Farleigh 33 kV | % of Rated A | 2.2573 | 1.6405 | 1.7139 | 2.2382 | 1.643 | 1.715 | 2.2388 | 1.6434 | 1.7152 | 2.2381 | 1.642 | 1.7148 | 2.2544 | 1.6407 | 1.7141
MK | 30053850 | 340 | MK3-1 Farleigh | 340_MK3-1 Farleigh 33 kV | Limiting Line Name | TR_LINE 11332_1 | TR_LINE 11330_1 | TR_LINE 11330_1 | TR_LINE 11332_1 | TR_LINE 11330_1 | TR_LINE 11330_1 | TR_LINE 11332_1 | TR_LINE 11330_1 | TR_LINE 11330_1 | TR_LINE 11332_1 | TR_LINE 11330_1 | TR_LINE 11330_1 | TR_LINE 11332_1 | TR_LINE 11330_1 | TR_LINE 11330_1
MK | 30053850 | 340 | MK3-1 Farleigh | 340_MK3-1 Farleigh 33 kV | Loading (A) | 3.8826 | 3.6912 | 3.8047 | 3.8496 | 3.6968 | 3.8073 | 3.8507 | 3.6976 | 3.8078 | 3.8495 | 3.6945 | 3.8069 | 3.8776 | 3.6915 | 3.8053
MK | 30053850 | 340 | MK3-1 Farleigh | 340_MK3-1 Farleigh 33 kV | Loading (MVA) | 0.23135 | 0.2126 | 0.22588 | 0.22744 | 0.21325 | 0.22618 | 0.22757 | 0.21334 | 0.22624 | 0.22742 | 0.21298 | 0.22613 | 0.23076 | 0.21263 | 0.22594
MK | 30053850 | 340 | MK3-1 Farleigh | 340_MK3-1 Farleigh 33 kV | Loading (MW) | 0.0042508 | 0.0039517 | 0.0041986 | 0.0041789 | 0.0039638 | 0.0042042 | 0.0041813 | 0.0039655 | 0.0042054 | 0.0041786 | 0.0039589 | 0.0042033 | 0.0042398 | 0.0039523 | 0.0041997
MK | 30053850 | 340 | MK3-1 Farleigh | 340_MK3-1 Farleigh 33 kV | Power Factor | 0.018374 | 0.018588 | 0.018588 | 0.018374 | 0.018588 | 0.018588 | 0.018374 | 0.018588 | 0.018588 | 0.018374 | 0.018588 | 0.018588 | 0.018374 | 0.018588 | 0.018588
MK | 30053850 | 340 | MK3-1 Farleigh | 340_MK3-1 Farleigh 33 kV | Rating (A) | 172 | 225 | 222 | 172 | 225 | 222 | 172 | 225 | 222 | 172 | 225 | 222 | 172 | 225 | 222
MK | 30053850 | 340 | MK3-1 Farleigh | 340_MK3-1 Farleigh 33 kV | Time | 9:00 | 21:00 | 5:00 | 10:00 | 21:00 | 5:00 | 10:00 | 21:00 | 5:00 | 10:00 | 21:00 | 5:00 | 9:30 | 21:30 | 5:00
MK | 30053850 | 340 | MK3-1 Farleigh | 340_MK3-1 Farleigh 33 kV | Voltage at Constrained Conductor | 34.4028 | 33.2528 | 34.2758 | 34.1107 | 33.3036 | 34.2986 | 34.1205 | 33.3106 | 34.3034 | 34.1093 | 33.283 | 34.2952 | 34.3584 | 33.2553 | 34.2804
MK | 30053851 | 341 | TENNYSON ST 2 | 341_Tennyson St No 2 33 kV | % of Rated A | 65.5789 | 61.902 | 54.202 | 64.6478 | 61.046 | 53.457 | 64.1908 | 60.6504 | 53.0959 | 64.0196 | 60.516 | 52.959 | 64.4956 | 60.9836 | 53.3454
MK | 30053851 | 341 | TENNYSON ST 2 | 341_Tennyson St No 2 33 kV | Limiting Line Name | TR_CABLE 29_1 | TR_CABLE 29_1 | TR_CABLE 29_1 | TR_CABLE 29_1 | TR_CABLE 29_1 | TR_CABLE 29_1 | TR_CABLE 29_1 | TR_CABLE 29_1 | TR_CABLE 29_1 | TR_CABLE 29_1 | TR_CABLE 29_1 | TR_CABLE 29_1 | TR_CABLE 29_1 | TR_CABLE 29_1 | TR_CABLE 29_1
MK | 30053851 | 341 | TENNYSON ST 2 | 341_Tennyson St No 2 33 kV | Loading (A) | 229.5262 | 216.6568 | 189.707 | 226.2672 | 213.661 | 187.0996 | 224.6679 | 212.2762 | 185.8358 | 224.0685 | 211.8059 | 185.3565 | 225.7345 | 213.4425 | 186.7088
MK | 30053851 | 341 | TENNYSON ST 2 | 341_Tennyson St No 2 33 kV | Loading (MVA) | 13.5951 | 12.7896 | 11.3891 | 13.4153 | 12.6246 | 11.2405 | 13.3259 | 12.547 | 11.1679 | 13.2892 | 12.5167 | 11.1387 | 13.3795 | 12.6041 | 11.2146
MK | 30053851 | 341 | TENNYSON ST 2 | 341_Tennyson St No 2 33 kV | Loading (MW) | 13.4629 | 12.6883 | 11.3307 | 13.2901 | 12.5291 | 11.1862 | 13.2043 | 12.4542 | 11.1158 | 13.169 | 12.4249 | 11.0873 | 13.256 | 12.5092 | 11.1613
MK | 30053851 | 341 | TENNYSON ST 2 | 341_Tennyson St No 2 33 kV | Power Factor | 0.99027 | 0.99208 | 0.99488 | 0.99067 | 0.99244 | 0.99518 | 0.99088 | 0.99261 | 0.99533 | 0.99095 | 0.99266 | 0.99539 | 0.99076 | 0.99247 | 0.99524
MK | 30053851 | 341 | TENNYSON ST 2 | 341_Tennyson St No 2 33 kV | Rating (A) | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350
MK | 30053851 | 341 | TENNYSON ST 2 | 341_Tennyson St No 2 33 kV | Time | 14:00 | 17:00 | 8:30 | 14:00 | 17:00 | 8:30 | 14:00 | 17:00 | 8:30 | 14:00 | 17:00 | 8:30 | 14:00 | 17:00 | 8:30
MK | 30053851 | 341 | TENNYSON ST 2 | 341_Tennyson St No 2 33 kV | Voltage at Constrained Conductor | 34.1972 | 34.0819 | 34.6612 | 34.2308 | 34.114 | 34.6857 | 34.2447 | 34.1253 | 34.6962 | 34.2419 | 34.1187 | 34.6948 | 34.2202 | 34.0933 | 34.6784
MK | 30053852 | 342 | SOUTH MACKAY | 342_South Mackay 33 kV | % of Rated A | 112.5828 | 61.9524 | 72.0671 | 110.7657 | 61.159 | 70.9863 | 109.8695 | 60.7692 | 70.4518 | 110.0289 | 60.8717 | 70.5466 | 110.5064 | 61.0773 | 70.8245
MK | 30053852 | 342 | SOUTH MACKAY | 342_South Mackay 33 kV | Limiting Line Name | TR_LINE 12122806_1 | TR_LINE 12122806_1 | TR_LINE 12122806_1 | TR_LINE 12122806_1 | TR_LINE 12122806_1 | TR_LINE 12122806_1 | TR_LINE 12122806_1 | TR_LINE 12122806_1 | TR_LINE 12122806_1 | TR_LINE 12122806_1 | TR_LINE 12122806_1 | TR_LINE 12122806_1 | TR_LINE 12122806_1 | TR_LINE 12122806_1 | TR_LINE 12122806_1
MK | 30053852 | 342 | SOUTH MACKAY | 342_South Mackay 33 kV | Loading (A) | 380.5297 | 303.5638 | 353.847 | 374.386 | 299.6759 | 348.54 | 371.3568 | 297.7661 | 345.9159 | 371.8954 | 298.2681 | 346.3814 | 373.5096 | 299.276 | 347.7458
MK | 30053852 | 342 | SOUTH MACKAY | 342_South Mackay 33 kV | Loading (MVA) | 22.6124 | 17.9758 | 21.2983 | 22.2681 | 17.7614 | 20.9929 | 22.0964 | 17.6537 | 20.8407 | 22.1264 | 17.6799 | 20.8678 | 22.2089 | 17.7269 | 20.9405
MK | 30053852 | 342 | SOUTH MACKAY | 342_South Mackay 33 kV | Loading (MW) | 21.0207 | 15.4667 | 19.2968 | 20.6033 | 15.1809 | 18.9207 | 20.3974 | 15.0381 | 18.7327 | 20.4372 | 15.0804 | 18.7702 | 20.5403 | 15.1519 | 18.8643
MK | 30053852 | 342 | SOUTH MACKAY | 342_South Mackay 33 kV | Power Factor | 0.92961 | 0.86042 | 0.90603 | 0.92524 | 0.85471 | 0.90129 | 0.92311 | 0.85184 | 0.89885 | 0.92366 | 0.85297 | 0.89948 | 0.92487 | 0.85474 | 0.90085
MK | 30053852 | 342 | SOUTH MACKAY | 342_South Mackay 33 kV | Rating (A) | 338 | 490 | 491 | 338 | 490 | 491 | 338 | 490 | 491 | 338 | 490 | 491 | 338 | 490 | 491
MK | 30053852 | 342 | SOUTH MACKAY | 342_South Mackay 33 kV | Time | 14:00 | 17:00 | 8:30 | 14:00 | 17:00 | 8:30 | 14:00 | 17:00 | 8:30 | 14:00 | 17:00 | 8:30 | 14:00 | 17:00 | 8:30
MK | 30053852 | 342 | SOUTH MACKAY | 342_South Mackay 33 kV | Voltage at Constrained Conductor | 34.3082 | 34.1883 | 34.7511 | 34.3403 | 34.2188 | 34.7743 | 34.3534 | 34.2294 | 34.7841 | 34.3502 | 34.2225 | 34.7825 | 34.3293 | 34.198 | 34.7668
MK | 30053853 | 343 | PLEYSTOWE | 343_Pleystowe 33 kV | % of Rated A | 47.4369 | 57.6705 | 41.3731 | 46.5501 | 56.6258 | 40.6472 | 46.5327 | 56.6085 | 40.6399 | 47.0392 | 57.1359 | 41.0205 | 47.4176 | 57.6717 | 41.3708
MK | 30053853 | 343 | PLEYSTOWE | 343_Pleystowe 33 kV | Limiting Line Name | TR_CABLE 4169_1 | TR_CABLE 4169_1 | TR_CABLE 4169_1 | TR_CABLE 4169_1 | TR_CABLE 4169_1 | TR_CABLE 4169_1 | TR_CABLE 4169_1 | TR_CABLE 4169_1 | TR_CABLE 4169_1 | TR_CABLE 4169_1 | TR_CABLE 4169_1 | TR_CABLE 4169_1 | TR_CABLE 4169_1 | TR_CABLE 4169_1 | TR_CABLE 4169_1
MK | 30053853 | 343 | PLEYSTOWE | 343_Pleystowe 33 kV | Loading (A) | 104.3612 | 126.8751 | 91.0208 | 102.4103 | 124.5769 | 89.4239 | 102.3719 | 124.5388 | 89.4078 | 103.4862 | 125.6989 | 90.2451 | 104.3188 | 126.8777 | 91.0157
MK | 30053853 | 343 | PLEYSTOWE | 343_Pleystowe 33 kV | Loading (MVA) | 6.0175 | 7.2545 | 5.2932 | 5.9136 | 7.1345 | 5.2055 | 5.9135 | 7.1344 | 5.2054 | 5.9752 | 7.1961 | 5.2519 | 6.0174 | 7.2546 | 5.2931
MK | 30053853 | 343 | PLEYSTOWE | 343_Pleystowe 33 kV | Loading (MW) | 5.9513 | 7.1666 | 5.2462 | 5.8501 | 7.0499 | 5.1603 | 5.8501 | 7.0498 | 5.1603 | 5.9098 | 7.1095 | 5.2056 | 5.9512 | 7.1667 | 5.2462
MK | 30053853 | 343 | PLEYSTOWE | 343_Pleystowe 33 kV | Power Factor | 0.989 | 0.98788 | 0.99113 | 0.98926 | 0.98814 | 0.99133 | 0.98927 | 0.98815 | 0.99133 | 0.98906 | 0.98796 | 0.99119 | 0.98901 | 0.98788 | 0.99113
MK | 30053853 | 343 | PLEYSTOWE | 343_Pleystowe 33 kV | Rating (A) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
MK | 30053853 | 343 | PLEYSTOWE | 343_Pleystowe 33 kV | Time | 16:00 | 18:30 | 22:00 | 16:00 | 18:30 | 22:00 | 16:00 | 18:30 | 22:00 | 16:00 | 18:30 | 22:00 | 16:00 | 18:30 | 22:00
MK | 30053853 | 343 | PLEYSTOWE | 343_Pleystowe 33 kV | Voltage at Constrained Conductor | 33.2901 | 33.0121 | 33.5748 | 33.3387 | 33.0647 | 33.6082 | 33.3507 | 33.0744 | 33.614 | 33.3355 | 33.0524 | 33.5996 | 33.303 | 33.0115 | 33.5766
MK | 30053854 | 344 | WEST MACKAY 2 | 344_West Mackay 2 33 kV | % of Rated A | 28.7366 | 25.9981 | 21.2211 | 28.4305 | 25.7228 | 21.002 | 28.2801 | 25.5889 | 20.8937 | 28.2829 | 25.5942 | 20.8947 | 28.5792 | 25.8647 | 21.109
MK | 30053854 | 344 | WEST MACKAY 2 | 344_West Mackay 2 33 kV | Limiting Line Name | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1
MK | 30053854 | 344 | WEST MACKAY 2 | 344_West Mackay 2 33 kV | Loading (A) | 179.604 | 162.488 | 132.6316 | 177.6904 | 160.7672 | 131.2627 | 176.7509 | 159.9305 | 130.5859 | 176.7678 | 159.9638 | 130.5921 | 178.6199 | 161.6546 | 131.9313
MK | 30053854 | 344 | WEST MACKAY 2 | 344_West Mackay 2 33 kV | Loading (MVA) | 10.6702 | 9.619 | 7.9815 | 10.5663 | 9.5257 | 7.9044 | 10.5145 | 9.479 | 7.8659 | 10.5145 | 9.4791 | 7.8659 | 10.6182 | 9.5724 | 7.943
MK | 30053854 | 344 | WEST MACKAY 2 | 344_West Mackay 2 33 kV | Loading (MW) | 10.41 | 9.3972 | 7.8152 | 10.3105 | 9.3074 | 7.7405 | 10.2607 | 9.2625 | 7.7032 | 10.2607 | 9.2625 | 7.7032 | 10.3602 | 9.3523 | 7.7778
MK | 30053854 | 344 | WEST MACKAY 2 | 344_West Mackay 2 33 kV | Power Factor | 0.97562 | 0.97694 | 0.97915 | 0.97579 | 0.97709 | 0.97927 | 0.97587 | 0.97716 | 0.97932 | 0.97586 | 0.97715 | 0.97932 | 0.97571 | 0.97701 | 0.97921
MK | 30053854 | 344 | WEST MACKAY 2 | 344_West Mackay 2 33 kV | Rating (A) | 625 | 625 | 625 | 625 | 625 | 625 | 625 | 625 | 625 | 625 | 625 | 625 | 625 | 625 | 625
MK | 30053854 | 344 | WEST MACKAY 2 | 344_West Mackay 2 33 kV | Time | 14:00 | 17:00 | 8:30 | 14:00 | 17:00 | 8:30 | 14:00 | 17:00 | 8:30 | 14:00 | 17:00 | 8:30 | 14:00 | 17:00 | 8:30
MK | 30053854 | 344 | WEST MACKAY 2 | 344_West Mackay 2 33 kV | Voltage at Constrained Conductor | 34.3002 | 34.1783 | 34.744 | 34.332 | 34.2087 | 34.7671 | 34.3451 | 34.2193 | 34.7768 | 34.3419 | 34.2124 | 34.7752 | 34.3211 | 34.1879 | 34.7595
MK | 30053855 | 3053 | MT BASSETT | 3053_Mt Bassett 33 kV | % of Rated A | 37.6911 | 27.9751 | 22.7875 | 37.3589 | 27.7213 | 22.8919 | 37.3116 | 27.691 | 22.8645 | 37.3003 | 27.6908 | 22.8576 | 37.5895 | 27.9219 | 22.7284
MK | 30053855 | 3053 | MT BASSETT | 3053_Mt Bassett 33 kV | Limiting Line Name | TR_LINE 11627_1 | TR_LINE 11627_1 | TR_LINE 11627_1 | TR_LINE 11627_1 | TR_LINE 11627_1 | TR_LINE 11627_1 | TR_LINE 11627_1 | TR_LINE 11627_1 | TR_LINE 11627_1 | TR_LINE 11627_1 | TR_LINE 11627_1 | TR_LINE 11627_1 | TR_LINE 11627_1 | TR_LINE 11627_1 | TR_LINE 11627_1
MK | 30053855 | 3053 | MT BASSETT | 3053_Mt Bassett 33 kV | Loading (A) | 88.5275 | 90.8727 | 73.5587 | 87.7467 | 90.0482 | 73.8965 | 87.6357 | 89.9496 | 73.808 | 87.6091 | 89.9491 | 73.7856 | 88.2888 | 90.7 | 73.3679
MK | 30053855 | 3053 | MT BASSETT | 3053_Mt Bassett 33 kV | Loading (MVA) | 5.1986 | 5.334 | 4.4033 | 5.1559 | 5.2907 | 4.3678 | 5.1509 | 5.2864 | 4.3638 | 5.1489 | 5.2848 | 4.3622 | 5.1866 | 5.3239 | 4.3937
MK | 30053855 | 3053 | MT BASSETT | 3053_Mt Bassett 33 kV | Loading (MW) | 4.9863 | 5.1202 | 4.2431 | 4.9459 | 5.08 | 4.2088 | 4.9416 | 5.0763 | 4.2053 | 4.9399 | 5.0749 | 4.2039 | 4.976 | 5.1114 | 4.2346
MK | 30053855 | 3053 | MT BASSETT | 3053_Mt Bassett 33 kV | Power Factor | 0.95915 | 0.9599 | 0.9636 | 0.95927 | 0.96018 | 0.96359 | 0.95937 | 0.96026 | 0.96368 | 0.9594 | 0.96028 | 0.96372 | 0.95939 | 0.96007 | 0.96381
MK | 30053855 | 3053 | MT BASSETT | 3053_Mt Bassett 33 kV | Rating (A) | 235 | 325 | 323 | 235 | 325 | 323 | 235 | 325 | 323 | 235 | 325 | 323 | 235 | 325 | 323
MK | 30053855 | 3053 | MT BASSETT | 3053_Mt Bassett 33 kV | Time | 16:30 | 18:30 | 7:30 | 16:30 | 18:30 | 7:30 | 16:30 | 18:30 | 7:30 | 16:30 | 18:30 | 7:30 | 16:30 | 18:30 | 7:30
MK | 30053855 | 3053 | MT BASSETT | 3053_Mt Bassett 33 kV | Voltage at Constrained Conductor | 33.9038 | 33.8893 | 34.5611 | 33.9247 | 33.9217 | 34.1256 | 33.9345 | 33.9314 | 34.1349 | 33.9319 | 33.9214 | 34.1326 | 33.917 | 33.8894 | 34.5748
MK | 30053856 | 346 | RITCHIES RD | 346_Ritchies Rd 33 kV | % of Rated A | 35.4621 | 31.1917 | 22.4585 | 34.7997 | 30.6271 | 22.0648 | 34.7867 | 30.6178 | 22.0609 | 35.1652 | 30.9029 | 22.2674 | 35.4477 | 31.1923 | 22.4573
MK | 30053856 | 346 | RITCHIES RD | 346_Ritchies Rd 33 kV | Limiting Line Name | TR_LINE 11327_1 | TR_LINE 11327_1 | TR_LINE 11327_1 | TR_LINE 11327_1 | TR_LINE 11327_1 | TR_LINE 11327_1 | TR_LINE 11327_1 | TR_LINE 11327_1 | TR_LINE 11327_1 | TR_LINE 11327_1 | TR_LINE 11327_1 | TR_LINE 11327_1 | TR_LINE 11327_1 | TR_LINE 11327_1 | TR_LINE 11327_1
MK | 30053856 | 346 | RITCHIES RD | 346_Ritchies Rd 33 kV | Loading (A) | 78.0162 | 94.8224 | 68.0489 | 76.559 | 93.1061 | 66.856 | 76.5303 | 93.0777 | 66.844 | 77.3631 | 93.9444 | 67.4697 | 77.9846 | 94.8243 | 68.0451
MK | 30053856 | 346 | RITCHIES RD | 346_Ritchies Rd 33 kV | Loading (MVA) | 4.4993 | 5.4231 | 3.9579 | 4.4217 | 5.3334 | 3.8924 | 4.4216 | 5.3334 | 3.8924 | 4.4677 | 5.3795 | 3.9271 | 4.4992 | 5.4231 | 3.9579
MK | 30053856 | 346 | RITCHIES RD | 346_Ritchies Rd 33 kV | Loading (MW) | 4.4435 | 5.3513 | 3.9168 | 4.368 | 5.2641 | 3.8527 | 4.3679 | 5.264 | 3.8527 | 4.4125 | 5.3086 | 3.8865 | 4.4435 | 5.3513 | 3.9168
MK | 30053856 | 346 | RITCHIES RD | 346_Ritchies Rd 33 kV | Power Factor | 0.9876 | 0.98675 | 0.98961 | 0.98784 | 0.98699 | 0.98979 | 0.98785 | 0.987 | 0.9898 | 0.98765 | 0.98682 | 0.98966 | 0.9876 | 0.98675 | 0.98961
MK | 30053856 | 346 | RITCHIES RD | 346_Ritchies Rd 33 kV | Rating (A) | 220 | 304 | 303 | 220 | 304 | 303 | 220 | 304 | 303 | 220 | 304 | 303 | 220 | 304 | 303
MK | 30053856 | 346 | RITCHIES RD | 346_Ritchies Rd 33 kV | Time | 16:00 | 18:30 | 22:00 | 16:00 | 18:30 | 22:00 | 16:00 | 18:30 | 22:00 | 16:00 | 18:30 | 22:00 | 16:00 | 18:30 | 22:00
MK | 30053856 | 346 | RITCHIES RD | 346_Ritchies Rd 33 kV | Voltage at Constrained Conductor | 33.2967 | 33.0202 | 33.5805 | 33.3452 | 33.0727 | 33.6138 | 33.3572 | 33.0824 | 33.6196 | 33.342 | 33.0604 | 33.6053 | 33.3096 | 33.0196 | 33.5823
MK | 30053857 | 347 | MT BASSETT | 347_Mt Bassett 33 kV | % of Rated A | 54.963 | 58.3813 | 46.7725 | 54.5486 | 57.9137 | 46.5669 | 54.5637 | 57.9234 | 46.5792 | 54.5806 | 57.9518 | 46.5928 | 55.0162 | 58.4456 | 46.8161
MK | 30053857 | 347 | MT BASSETT | 347_Mt Bassett 33 kV | Limiting Line Name | TR_CABLE 4883_1 | TR_CABLE 4883_1 | TR_CABLE 4883_1 | TR_CABLE 4883_1 | TR_CABLE 4883_1 | TR_CABLE 4883_1 | TR_CABLE 4883_1 | TR_CABLE 4883_1 | TR_CABLE 4883_1 | TR_CABLE 4883_1 | TR_CABLE 4883_1 | TR_CABLE 4883_1 | TR_CABLE 4883_1 | TR_CABLE 4883_1 | TR_CABLE 4883_1
MK | 30053857 | 347 | MT BASSETT | 347_Mt Bassett 33 kV | Loading (A) | 140.1556 | 148.8722 | 119.2699 | 139.099 | 147.6799 | 118.7456 | 139.1373 | 147.7046 | 118.7769 | 139.1804 | 147.7772 | 118.8116 | 140.2914 | 149.0364 | 119.3811
MK | 30053857 | 347 | MT BASSETT | 347_Mt Bassett 33 kV | Loading (MVA) | 8.2568 | 8.7704 | 7.0795 | 8.1994 | 8.7083 | 7.0382 | 8.2042 | 8.7123 | 7.042 | 8.2061 | 8.714 | 7.0436 | 8.2682 | 8.7803 | 7.0866
MK | 30053857 | 347 | MT BASSETT | 347_Mt Bassett 33 kV | Loading (MW) | 8.097 | 8.587 | 6.9433 | 8.0416 | 8.5268 | 6.91 | 8.0459 | 8.5304 | 6.9134 | 8.0476 | 8.5319 | 6.9149 | 8.1072 | 8.5959 | 6.9498
MK | 30053857 | 347 | MT BASSETT | 347_Mt Bassett 33 kV | Power Factor | 0.98064 | 0.97909 | 0.98077 | 0.98076 | 0.97916 | 0.98178 | 0.98071 | 0.97913 | 0.98174 | 0.98069 | 0.9791 | 0.98172 | 0.98053 | 0.97899 | 0.98069
MK | 30053857 | 347 | MT BASSETT | 347_Mt Bassett 33 kV | Rating (A) | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255
MK | 30053857 | 347 | MT BASSETT | 347_Mt Bassett 33 kV | Time | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 7:30 | 16:30 | 18:30 | 7:30 | 16:30 | 18:30 | 7:30 | 16:30 | 18:30 | 22:00
MK | 30053857 | 347 | MT BASSETT | 347_Mt Bassett 33 kV | Voltage at Constrained Conductor | 34.0127 | 34.0131 | 34.2696 | 34.033 | 34.0447 | 34.2201 | 34.0431 | 34.0547 | 34.2297 | 34.0407 | 34.0448 | 34.2275 | 34.0268 | 34.014 | 34.2724
MK | 30053858 | 348 | Farleigh | 348_Farleigh 33 kV | % of Rated A | 43.2706 | 32.4781 | 25.7792 | 42.2412 | 31.7003 | 25.1865 | 42.2248 | 31.6902 | 25.1822 | 43.2063 | 32.4348 | 25.761 | 43.2523 | 32.4788 | 25.7782
MK | 30053858 | 348 | Farleigh | 348_Farleigh 33 kV | Limiting Line Name | TR_LINE 11976_1 | TR_LINE 11976_1 | TR_LINE 11976_1 | TR_LINE 11976_1 | TR_LINE 11976_1 | TR_LINE 11976_1 | TR_LINE 11976_1 | TR_LINE 11976_1 | TR_LINE 11976_1 | TR_LINE 11976_1 | TR_LINE 11976_1 | TR_LINE 11976_1 | TR_LINE 11976_1 | TR_LINE 11976_1 | TR_LINE 11976_1
MK | 30053858 | 348 | Farleigh | 348_Farleigh 33 kV | Loading (A) | 83.9374 | 84.4355 | 66.5039 | 81.9405 | 82.4133 | 64.9748 | 81.9085 | 82.387 | 64.9638 | 83.8126 | 84.3229 | 66.4568 | 83.9019 | 84.4373 | 66.5013
MK | 30053858 | 348 | Farleigh | 348_Farleigh 33 kV | Loading (MVA) | 4.7862 | 4.7735 | 3.8549 | 4.6806 | 4.6681 | 3.7706 | 4.6805 | 4.668 | 3.7706 | 4.7857 | 4.7731 | 3.8548 | 4.786 | 4.7735 | 3.8549
MK | 30053858 | 348 | Farleigh | 348_Farleigh 33 kV | Loading (MW) | 4.7316 | 4.7179 | 3.8245 | 4.6292 | 4.6158 | 3.7421 | 4.6292 | 4.6157 | 3.7421 | 4.7314 | 4.7177 | 3.8244 | 4.7315 | 4.7179 | 3.8245
MK | 30053858 | 348 | Farleigh | 348_Farleigh 33 kV | Power Factor | 0.9886 | 0.98835 | 0.9921 | 0.98903 | 0.9888 | 0.99245 | 0.98904 | 0.98881 | 0.99245 | 0.98865 | 0.9884 | 0.99212 | 0.98861 | 0.98835 | 0.9921
MK | 30053858 | 348 | Farleigh | 348_Farleigh 33 kV | Rating (A) | 194 | 260 | 258 | 194 | 260 | 258 | 194 | 260 | 258 | 194 | 260 | 258 | 194 | 260 | 258
MK | 30053858 | 348 | Farleigh | 348_Farleigh 33 kV | Time | 16:00 | 18:30 | 22:30 | 16:00 | 18:30 | 22:30 | 16:00 | 18:30 | 22:30 | 16:00 | 18:30 | 22:30 | 16:00 | 18:30 | 22:30
MK | 30053858 | 348 | Farleigh | 348_Farleigh 33 kV | Voltage at Constrained Conductor | 32.9208 | 32.6401 | 33.4663 | 32.9791 | 32.7026 | 33.5046 | 32.9912 | 32.7124 | 33.51 | 32.9668 | 32.681 | 33.4889 | 32.9339 | 32.6395 | 33.4675
MK | 30053859 | 349 | Pioneer Valley-Pinnacle(Marian) | 349_Pioneer Valley - Pinnacle 66 kV | % of Rated A | 40.0083 | 36.4003 | 28.042 | 40.2283 | 36.0993 | 27.8297 | 40.228 | 36.0943 | 27.8274 | 39.9976 | 36.3921 | 28.0385 | 40.3473 | 36.7186 | 28.2854
MK | 30053859 | 349 | Pioneer Valley-Pinnacle(Marian) | 349_Pioneer Valley - Pinnacle 66 kV | Limiting Line Name | TR_LINE 10055_2 | TR_LINE 10055_2 | TR_LINE 10055_2 | TR_LINE 10055_2 | TR_LINE 10055_2 | TR_LINE 10055_2 | TR_LINE 10055_2 | TR_LINE 10055_2 | TR_LINE 10055_2 | TR_LINE 10055_2 | TR_LINE 10055_2 | TR_LINE 10055_2 | TR_LINE 10055_2 | TR_LINE 10055_2 | TR_LINE 10055_2
MK | 30053859 | 349 | Pioneer Valley-Pinnacle(Marian) | 349_Pioneer Valley - Pinnacle 66 kV | Loading (A) | 88.0173 | 110.6556 | 84.9663 | 88.5013 | 109.7408 | 84.3231 | 88.5006 | 109.7255 | 84.3162 | 87.9937 | 110.6307 | 84.9556 | 88.7631 | 111.6234 | 85.7039
MK | 30053859 | 349 | Pioneer Valley-Pinnacle(Marian) | 349_Pioneer Valley - Pinnacle 66 kV | Loading (MVA) | 10.4953 | 13.278 | 10.1098 | 10.4208 | 13.1764 | 10.0371 | 10.4208 | 13.1762 | 10.0371 | 10.4951 | 13.2777 | 10.1097 | 10.5807 | 13.3822 | 10.1933
MK | 30053859 | 349 | Pioneer Valley-Pinnacle(Marian) | 349_Pioneer Valley - Pinnacle 66 kV | Loading (MW) | 10.3661 | 13.0394 | 9.9873 | 10.288 | 12.941 | 9.9172 | 10.288 | 12.941 | 9.9172 | 10.3661 | 13.0393 | 9.9873 | 10.4486 | 13.1385 | 10.0676
MK | 30053859 | 349 | Pioneer Valley-Pinnacle(Marian) | 349_Pioneer Valley - Pinnacle 66 kV | Power Factor | 0.98769 | 0.98203 | 0.98788 | 0.98726 | 0.98214 | 0.98805 | 0.98726 | 0.98215 | 0.98806 | 0.98771 | 0.98205 | 0.98789 | 0.98752 | 0.98179 | 0.98767
MK | 30053859 | 349 | Pioneer Valley-Pinnacle(Marian) | 349_Pioneer Valley - Pinnacle 66 kV | Rating (A) | 220 | 304 | 303 | 220 | 304 | 303 | 220 | 304 | 303 | 220 | 304 | 303 | 220 | 304 | 303
MK | 30053859 | 349 | Pioneer Valley-Pinnacle(Marian) | 349_Pioneer Valley - Pinnacle 66 kV | Time | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00
MK | 30053859 | 349 | Pioneer Valley-Pinnacle(Marian) | 349_Pioneer Valley - Pinnacle 66 kV | Voltage at Constrained Conductor | 68.8438 | 69.2783 | 68.6967 | 67.9813 | 69.3213 | 68.7231 | 67.9818 | 69.3302 | 68.7283 | 68.861 | 69.2927 | 68.7048 | 68.8211 | 69.2168 | 68.6678
MK | 30053869 | 360 | Pinnacle-Crediton/Eungella Dam | 360_Pinnacle-Crediton/Eungella Dam 66 kV | % of Rated A | 11.915 | 10.8938 | 9.3517 | 12.0911 | 10.8867 | 9.3482 | 12.091 | 10.8853 | 9.3474 | 11.9115 | 10.8917 | 9.3504 | 11.9207 | 10.7357 | 9.3573
MK | 30053869 | 360 | Pinnacle-Crediton/Eungella Dam | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Limiting Line Name | TR_LINE 9915_1 | TR_LINE 9915_1 | TR_LINE 9915_1 | TR_LINE 9915_1 | TR_LINE 9915_1 | TR_LINE 9915_1 | TR_LINE 9915_1 | TR_LINE 9915_1 | TR_LINE 9915_1 | TR_LINE 9915_1 | TR_LINE 9915_1 | TR_LINE 9915_1 | TR_LINE 9915_1 | TR_LINE 9915_1 | TR_LINE 9915_1
MK | 30053869 | 360 | Pinnacle-Crediton/Eungella Dam | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Loading (A) | 10.9618 | 12.9636 | 10.5675 | 11.1238 | 12.9552 | 10.5634 | 11.1237 | 12.9535 | 10.5626 | 10.9586 | 12.9612 | 10.566 | 10.9671 | 12.7754 | 10.5737
MK | 30053869 | 360 | Pinnacle-Crediton/Eungella Dam | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Loading (MVA) | 1.2888 | 1.4955 | 1.2459 | 1.2909 | 1.4954 | 1.2459 | 1.2909 | 1.4954 | 1.2459 | 1.2888 | 1.4955 | 1.2459 | 1.2889 | 1.4935 | 1.246
MK | 30053869 | 360 | Pinnacle-Crediton/Eungella Dam | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Loading (MW) | 1.2496 | 1.4556 | 1.2064 | 1.2498 | 1.4556 | 1.2064 | 1.2498 | 1.4556 | 1.2064 | 1.2496 | 1.4556 | 1.2064 | 1.2496 | 1.4554 | 1.2064
MK | 30053869 | 360 | Pinnacle-Crediton/Eungella Dam | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Power Factor | 0.96956 | 0.97329 | 0.96825 | 0.96815 | 0.97334 | 0.96829 | 0.96815 | 0.97335 | 0.9683 | 0.96958 | 0.9733 | 0.96827 | 0.96951 | 0.97447 | 0.96819
MK | 30053869 | 360 | Pinnacle-Crediton/Eungella Dam | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Rating (A) | 92 | 119 | 113 | 92 | 119 | 113 | 92 | 119 | 113 | 92 | 119 | 113 | 92 | 119 | 113
MK | 30053869 | 360 | Pinnacle-Crediton/Eungella Dam | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Time | 16:30 | 19:30 | 22:30 | 16:30 | 19:30 | 22:30 | 16:30 | 19:30 | 22:30 | 16:30 | 19:30 | 22:30 | 16:30 | 19:30 | 22:30
MK | 30053869 | 360 | Pinnacle-Crediton/Eungella Dam | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Voltage at Constrained Conductor | 67.8822 | 66.6044 | 68.0704 | 66.9995 | 66.6439 | 68.0937 | 67 | 66.6519 | 68.0986 | 67.8999 | 66.616 | 68.079 | 67.8529 | 67.494 | 68.0348
MK | 30053873 | 364 | WEST MACKAY 1 | 364_West Mackay No 1 33 kV | % of Rated A | 61.9545 | 39.5474 | 32.3573 | 61.2941 | 39.1284 | 32.0232 | 60.9698 | 38.9247 | 31.8581 | 60.9757 | 38.9328 | 31.8596 | 61.6148 | 39.3445 | 32.1864
MK | 30053873 | 364 | WEST MACKAY 1 | 364_West Mackay No 1 33 kV | Limiting Line Name | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1
MK | 30053873 | 364 | WEST MACKAY 1 | 364_West Mackay No 1 33 kV | Loading (A) | 179.6676 | 162.5395 | 132.6645 | 177.7525 | 160.8175 | 131.2949 | 176.8122 | 159.9802 | 130.6177 | 176.8292 | 160.0136 | 130.6239 | 178.6827 | 161.7055 | 131.9639
MK | 30053873 | 364 | WEST MACKAY 1 | 364_West Mackay No 1 33 kV | Loading (MVA) | 10.671 | 9.6196 | 7.9819 | 10.5671 | 9.5262 | 7.9048 | 10.5152 | 9.4796 | 7.8662 | 10.5152 | 9.4796 | 7.8662 | 10.6189 | 9.573 | 7.9433
MK | 30053873 | 364 | WEST MACKAY 1 | 364_West Mackay No 1 33 kV | Loading (MW) | 10.4105 | 9.3976 | 7.8154 | 10.3109 | 9.3078 | 7.7408 | 10.2612 | 9.2628 | 7.7034 | 10.2612 | 9.2629 | 7.7034 | 10.3607 | 9.3527 | 7.7781
MK | 30053873 | 364 | WEST MACKAY 1 | 364_West Mackay No 1 33 kV | Power Factor | 0.97559 | 0.97692 | 0.97914 | 0.97576 | 0.97707 | 0.97925 | 0.97584 | 0.97714 | 0.97931 | 0.97584 | 0.97713 | 0.97931 | 0.97568 | 0.97699 | 0.9792
MK | 30053873 | 364 | WEST MACKAY 1 | 364_West Mackay No 1 33 kV | Rating (A) | 290 | 411 | 410 | 290 | 411 | 410 | 290 | 411 | 410 | 290 | 411 | 410 | 290 | 411 | 410
MK | 30053873 | 364 | WEST MACKAY 1 | 364_West Mackay No 1 33 kV | Time | 14:00 | 17:00 | 8:30 | 14:00 | 17:00 | 8:30 | 14:00 | 17:00 | 8:30 | 14:00 | 17:00 | 8:30 | 14:00 | 17:00 | 8:30
MK | 30053873 | 364 | WEST MACKAY 1 | 364_West Mackay No 1 33 kV | Voltage at Constrained Conductor | 34.2904 | 34.1695 | 34.7369 | 34.3224 | 34.2001 | 34.7601 | 34.3355 | 34.2107 | 34.7699 | 34.3323 | 34.2038 | 34.7683 | 34.3114 | 34.1792 | 34.7525
MK | 30053874 | 365 | MACKAY CITY 1 | 365_Tennyson St No 1 33 kV | % of Rated A | 8.6492 | 8.1674 | 7.1581 | 8.5271 | 8.0552 | 7.0606 | 8.4672 | 8.0033 | 7.0133 | 8.4447 | 7.9857 | 6.9954 | 8.5072 | 8.047 | 7.046
MK | 30053874 | 365 | MACKAY CITY 1 | 365_Tennyson St No 1 33 kV | Limiting Line Name | TR_CABLE 30_1 | TR_CABLE 30_1 | TR_CABLE 30_1 | TR_CABLE 30_1 | TR_CABLE 30_1 | TR_CABLE 30_1 | TR_CABLE 30_1 | TR_CABLE 30_1 | TR_CABLE 30_1 | TR_CABLE 30_1 | TR_CABLE 30_1 | TR_CABLE 30_1 | TR_CABLE 30_1 | TR_CABLE 30_1 | TR_CABLE 30_1
MK | 30053874 | 365 | MACKAY CITY 1 | 365_Tennyson St No 1 33 kV | Loading (A) | 57.517 | 54.313 | 47.6015 | 56.705 | 53.5669 | 46.9529 | 56.3067 | 53.2222 | 46.6387 | 56.1574 | 53.105 | 46.5195 | 56.5726 | 53.5126 | 46.856
MK | 30053874 | 365 | MACKAY CITY 1 | 365_Tennyson St No 1 33 kV | Loading (MVA) | 3.4068 | 3.2062 | 2.8578 | 3.362 | 3.1651 | 2.8208 | 3.3398 | 3.1458 | 2.8028 | 3.3306 | 3.1383 | 2.7955 | 3.3531 | 3.16 | 2.8144
MK | 30053874 | 365 | MACKAY CITY 1 | 365_Tennyson St No 1 33 kV | Loading (MW) | 2.7961 | 2.6584 | 2.4139 | 2.7655 | 2.63 | 2.3878 | 2.7504 | 2.6167 | 2.3752 | 2.7441 | 2.6113 | 2.37 | 2.7596 | 2.6263 | 2.3835
MK | 30053874 | 365 | MACKAY CITY 1 | 365_Tennyson St No 1 33 kV | Power Factor | 0.82074 | 0.82915 | 0.84469 | 0.82258 | 0.83094 | 0.84651 | 0.82355 | 0.83182 | 0.84745 | 0.8239 | 0.83209 | 0.84781 | 0.82301 | 0.83112 | 0.8469
MK | 30053874 | 365 | MACKAY CITY 1 | 365_Tennyson St No 1 33 kV | Rating (A) | 665 | 665 | 665 | 665 | 665 | 665 | 665 | 665 | 665 | 665 | 665 | 665 | 665 | 665 | 665
MK | 30053874 | 365 | MACKAY CITY 1 | 365_Tennyson St No 1 33 kV | Time | 14:00 | 17:00 | 8:30 | 14:00 | 17:00 | 8:30 | 14:00 | 17:00 | 8:30 | 14:00 | 17:00 | 8:30 | 14:00 | 17:00 | 8:30
MK | 30053874 | 365 | MACKAY CITY 1 | 365_Tennyson St No 1 33 kV | Voltage at Constrained Conductor | 34.1972 | 34.0819 | 34.6612 | 34.2308 | 34.114 | 34.6857 | 34.2447 | 34.1253 | 34.6962 | 34.2419 | 34.1187 | 34.6948 | 34.2202 | 34.0933 | 34.6784
MK | 30053876 | 367 | Pioneer Valley-Greenmount | 367_Pioneer Valley - Greenmount 66 kV | % of Rated A | 0.065017 | 0.047078 | 0.047258 | 0.064993 | 0.047103 | 0.047244 | 0.065001 | 0.047109 | 0.047247 | 0.064995 | 0.047087 | 0.047259 | 0.065 | 0.047042 | 0.047252
MK | 30053876 | 367 | Pioneer Valley-Greenmount | 367_Pioneer Valley - Greenmount 66 kV | Limiting Line Name | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1
MK | 30053876 | 367 | Pioneer Valley-Greenmount | 367_Pioneer Valley - Greenmount 66 kV | Loading (A) | 0.16384 | 0.1643 | 0.16446 | 0.16378 | 0.16439 | 0.16441 | 0.1638 | 0.16441 | 0.16442 | 0.16379 | 0.16434 | 0.16446 | 0.1638 | 0.16418 | 0.16444
MK | 30053876 | 367 | Pioneer Valley-Greenmount | 367_Pioneer Valley - Greenmount 66 kV | Loading (MVA) | 0.019798 | 0.01991 | 0.019947 | 0.019784 | 0.019931 | 0.019936 | 0.019788 | 0.019935 | 0.019938 | 0.019785 | 0.019917 | 0.019948 | 0.019788 | 0.019879 | 0.019942
MK | 30053876 | 367 | Pioneer Valley-Greenmount | 367_Pioneer Valley - Greenmount 66 kV | Loading (MW) | 8.0558e-08 | 8.0961e-08 | 8.1251e-08 | 8.0559e-08 | 8.1179e-08 | 8.1207e-08 | 8.0554e-08 | 8.1185e-08 | 8.1196e-08 | 8.0514e-08 | 8.1049e-08 | 8.1207e-08 | 8.0517e-08 | 8.0968e-08 | 8.125e-08
MK | 30053876 | 367 | Pioneer Valley-Greenmount | 367_Pioneer Valley - Greenmount 66 kV | Power Factor | 4.069e-06 | 4.0664e-06 | 4.0733e-06 | 4.072e-06 | 4.0731e-06 | 4.0734e-06 | 4.0708e-06 | 4.0724e-06 | 4.0724e-06 | 4.0694e-06 | 4.0693e-06 | 4.0709e-06 | 4.069e-06 | 4.0731e-06 | 4.0743e-06
MK | 30053876 | 367 | Pioneer Valley-Greenmount | 367_Pioneer Valley - Greenmount 66 kV | Rating (A) | 252 | 349 | 348 | 252 | 349 | 348 | 252 | 349 | 348 | 252 | 349 | 348 | 252 | 349 | 348
MK | 30053876 | 367 | Pioneer Valley-Greenmount | 367_Pioneer Valley - Greenmount 66 kV | Time | 9:00 | 19:00 | 5:30 | 9:30 | 19:00 | 0:00 | 9:30 | 19:00 | 0:00 | 9:30 | 19:00 | 0:30 | 9:00 | 19:00 | 5:30
MK | 30053876 | 367 | Pioneer Valley-Greenmount | 367_Pioneer Valley - Greenmount 66 kV | Voltage at Constrained Conductor | 69.7651 | 69.9612 | 70.027 | 69.7396 | 69.9981 | 70.0071 | 69.748 | 70.0066 | 70.0113 | 69.7422 | 69.9749 | 70.0293 | 69.747 | 69.907 | 70.0183
MK | 30053881 | 372 | Pioneer Valley-MCKINLEY CREEK | 372_Pioneer Valley-McKinley Creek 33 kV | % of Rated A | 13.7413 | 11.4063 | 9.4916 | 13.915 | 11.4001 | 9.489 | 13.9149 | 11.3986 | 9.4883 | 13.7378 | 11.404 | 9.4905 | 13.7449 | 11.4155 | 9.4951
MK | 30053881 | 372 | Pioneer Valley-MCKINLEY CREEK | 372_Pioneer Valley-McKinley Creek 33 kV | Limiting Line Name | TR_LINE 12781_1 | TR_LINE 12781_1 | TR_LINE 12781_1 | TR_LINE 12781_1 | TR_LINE 12781_1 | TR_LINE 12781_1 | TR_LINE 12781_1 | TR_LINE 12781_1 | TR_LINE 12781_1 | TR_LINE 12781_1 | TR_LINE 12781_1 | TR_LINE 12781_1 | TR_LINE 12781_1 | TR_LINE 12781_1 | TR_LINE 12781_1
MK | 30053881 | 372 | Pioneer Valley-MCKINLEY CREEK | 372_Pioneer Valley-McKinley Creek 33 kV | Loading (A) | 26.7955 | 31.7096 | 25.6274 | 27.1342 | 31.6923 | 25.6203 | 27.134 | 31.6882 | 25.6185 | 26.7888 | 31.703 | 25.6243 | 26.8026 | 31.7352 | 25.6367
MK | 30053881 | 372 | Pioneer Valley-MCKINLEY CREEK | 372_Pioneer Valley-McKinley Creek 33 kV | Loading (MVA) | 3.2053 | 3.8222 | 3.0717 | 3.2053 | 3.8221 | 3.0717 | 3.2053 | 3.8221 | 3.0717 | 3.2053 | 3.8222 | 3.0717 | 3.2053 | 3.8222 | 3.0717
MK | 30053881 | 372 | Pioneer Valley-MCKINLEY CREEK | 372_Pioneer Valley-McKinley Creek 33 kV | Loading (MW) | 3.1584 | 3.763 | 3.027 | 3.1584 | 3.763 | 3.027 | 3.1584 | 3.763 | 3.027 | 3.1584 | 3.763 | 3.027 | 3.1584 | 3.763 | 3.027
MK | 30053881 | 372 | Pioneer Valley-MCKINLEY CREEK | 372_Pioneer Valley-McKinley Creek 33 kV | Power Factor | 0.98535 | 0.98453 | 0.98544 | 0.98535 | 0.98453 | 0.98544 | 0.98535 | 0.98454 | 0.98544 | 0.98535 | 0.98453 | 0.98544 | 0.98535 | 0.98452 | 0.98543
MK | 30053881 | 372 | Pioneer Valley-MCKINLEY CREEK | 372_Pioneer Valley-McKinley Creek 33 kV | Rating (A) | 195 | 278 | 270 | 195 | 278 | 270 | 195 | 278 | 270 | 195 | 278 | 270 | 195 | 278 | 270
MK | 30053881 | 372 | Pioneer Valley-MCKINLEY CREEK | 372_Pioneer Valley-McKinley Creek 33 kV | Time | 16:30 | 18:30 | 22:30 | 16:30 | 18:30 | 22:30 | 16:30 | 18:30 | 22:30 | 16:30 | 18:30 | 22:30 | 16:30 | 18:30 | 22:30
MK | 30053881 | 372 | Pioneer Valley-MCKINLEY CREEK | 372_Pioneer Valley-McKinley Creek 33 kV | Voltage at Constrained Conductor | 69.064 | 69.5917 | 69.202 | 68.2019 | 69.6293 | 69.2212 | 68.2024 | 69.6382 | 69.2259 | 69.0811 | 69.606 | 69.2104 | 69.0459 | 69.5363 | 69.1772
MK | 82846747 | 351 | ALLIGATOR CREEK 33kV FDR | 351_Alligator Creek 33 kV | % of Rated A | 16.9105 | 20.0795 | 17.924 | 16.8911 | 20.0574 | 17.913 | 16.8829 | 20.0499 | 17.9091 | 17.1966 | 20.4279 | 18.2433 | 17.2072 | 20.4475 | 18.252
MK | 82846747 | 351 | ALLIGATOR CREEK 33kV FDR | 351_Alligator Creek 33 kV | Limiting Line Name | TR_CABLE 7120_1 | TR_CABLE 7120_1 | TR_CABLE 7120_1 | TR_CABLE 7120_1 | TR_CABLE 7120_1 | TR_CABLE 7120_1 | TR_CABLE 7120_1 | TR_CABLE 7120_1 | TR_CABLE 7120_1 | TR_CABLE 7120_1 | TR_CABLE 7120_1 | TR_CABLE 7120_1 | TR_CABLE 7120_1 | TR_CABLE 7120_1 | TR_CABLE 7120_1
MK | 82846747 | 351 | ALLIGATOR CREEK 33kV FDR | 351_Alligator Creek 33 kV | Loading (A) | 39.5706 | 46.986 | 41.9421 | 39.5253 | 46.9344 | 41.9164 | 39.506 | 46.9167 | 41.9072 | 40.24 | 47.8013 | 42.6892 | 40.2649 | 47.8471 | 42.7097
MK | 82846747 | 351 | ALLIGATOR CREEK 33kV FDR | 351_Alligator Creek 33 kV | Loading (MVA) | 2.3586 | 2.7804 | 2.5148 | 2.3585 | 2.7803 | 2.5148 | 2.3585 | 2.7803 | 2.5148 | 2.4018 | 2.8315 | 2.561 | 2.4019 | 2.8315 | 2.561
MK | 82846747 | 351 | ALLIGATOR CREEK 33kV FDR | 351_Alligator Creek 33 kV | Loading (MW) | 2.2678 | 2.6696 | 2.4169 | 2.2678 | 2.6696 | 2.4169 | 2.2678 | 2.6696 | 2.4169 | 2.3091 | 2.7182 | 2.4609 | 2.3091 | 2.7183 | 2.4609
MK | 82846747 | 351 | ALLIGATOR CREEK 33kV FDR | 351_Alligator Creek 33 kV | Power Factor | 0.9615 | 0.96017 | 0.96107 | 0.96152 | 0.96019 | 0.96109 | 0.96153 | 0.9602 | 0.96109 | 0.96138 | 0.96002 | 0.96093 | 0.96137 | 0.96 | 0.96092
MK | 82846747 | 351 | ALLIGATOR CREEK 33kV FDR | 351_Alligator Creek 33 kV | Rating (A) | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234
MK | 82846747 | 351 | ALLIGATOR CREEK 33kV FDR | 351_Alligator Creek 33 kV | Time | 13:00 | 18:30 | 22:30 | 13:00 | 18:30 | 22:30 | 13:00 | 18:30 | 22:30 | 13:00 | 18:30 | 22:30 | 13:00 | 18:30 | 22:30
MK | 82846747 | 351 | ALLIGATOR CREEK 33kV FDR | 351_Alligator Creek 33 kV | Voltage at Constrained Conductor | 34.4127 | 34.1642 | 34.6173 | 34.4514 | 34.201 | 34.6381 | 34.4679 | 34.2136 | 34.6455 | 34.4608 | 34.1986 | 34.636 | 34.4399 | 34.1666 | 34.6197
MK | 82913608 | PV 6/5 | PV 6/5 GLENELLA NO 1 | PV 6/5_Glenella No 1 66 kV | % of Rated A | 30.7023 | 31.5578 | 25.1961 | 30.9989 | 31.438 | 25.1102 | 31.0111 | 31.4332 | 25.108 | 30.8316 | 31.7136 | 25.3125 | 31.3022 | 32.2735 | 25.7047
MK | 82913608 | PV 6/5 | PV 6/5 GLENELLA NO 1 | PV 6/5_Glenella No 1 66 kV | Limiting Line Name | TR_LINE 105119_4 | TR_LINE 105119_4 | TR_LINE 105119_4 | TR_LINE 105119_4 | TR_LINE 105119_4 | TR_LINE 105119_4 | TR_LINE 105119_4 | TR_LINE 105119_4 | TR_LINE 105119_4 | TR_LINE 105119_4 | TR_LINE 105119_4 | TR_LINE 105119_4 | TR_LINE 105119_4 | TR_LINE 105119_4 | TR_LINE 105119_4
MK | 82913608 | PV 6/5 | PV 6/5 GLENELLA NO 1 | PV 6/5_Glenella No 1 66 kV | Loading (A) | 248.3765 | 286.5388 | 224.4931 | 250.7761 | 285.451 | 223.7273 | 250.8748 | 285.4083 | 223.708 | 249.423 | 287.9534 | 225.5301 | 253.2301 | 293.0372 | 229.024
MK | 82913608 | PV 6/5 | PV 6/5 GLENELLA NO 1 | PV 6/5_Glenella No 1 66 kV | Loading (MVA) | 29.3673 | 34.0561 | 26.5298 | 29.2754 | 33.9492 | 26.4498 | 29.2842 | 33.9487 | 26.4496 | 29.4952 | 34.2258 | 26.6526 | 29.9214 | 34.7758 | 27.0458
MK | 82913608 | PV 6/5 | PV 6/5 GLENELLA NO 1 | PV 6/5_Glenella No 1 66 kV | Loading (MW) | 29.1661 | 33.7482 | 26.3766 | 29.0816 | 33.6463 | 26.2989 | 29.0821 | 33.6461 | 26.2989 | 29.2897 | 33.9094 | 26.4951 | 29.7094 | 34.4329 | 26.8833
MK | 82913608 | PV 6/5 | PV 6/5 GLENELLA NO 1 | PV 6/5_Glenella No 1 66 kV | Power Factor | 0.99315 | 0.99096 | 0.99423 | 0.99338 | 0.99108 | 0.9943 | 0.9931 | 0.99109 | 0.9943 | 0.99303 | 0.99075 | 0.99409 | 0.99292 | 0.99014 | 0.99399
MK | 82913608 | PV 6/5 | PV 6/5 GLENELLA NO 1 | PV 6/5_Glenella No 1 66 kV | Rating (A) | 809 | 908 | 891 | 809 | 908 | 891 | 809 | 908 | 891 | 809 | 908 | 891 | 809 | 908 | 891
MK | 82913608 | PV 6/5 | PV 6/5 GLENELLA NO 1 | PV 6/5_Glenella No 1 66 kV | Time | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00
MK | 82913608 | PV 6/5 | PV 6/5 GLENELLA NO 1 | PV 6/5_Glenella No 1 66 kV | Voltage at Constrained Conductor | 68.2642 | 68.6201 | 68.2292 | 67.3994 | 68.6653 | 68.2564 | 67.3931 | 68.6746 | 68.2618 | 68.2739 | 68.6232 | 68.2298 | 68.219 | 68.5162 | 68.1801
MK | 82913611 | PV 6/4 | PV 6/4 GLENELLA NO 2 | PV 6/4_Glenella No 2 66 kV | % of Rated A | 30.112 | 31.2372 | 24.6149 | 30.4006 | 31.1165 | 24.5284 | 30.4112 | 31.1119 | 24.5263 | 30.2428 | 31.3947 | 24.7323 | 30.7191 | 31.9598 | 25.1291
MK | 82913611 | PV 6/4 | PV 6/4 GLENELLA NO 2 | PV 6/4_Glenella No 2 66 kV | Limiting Line Name | TR_LINE 105543_1 | TR_LINE 105543_1 | TR_LINE 105543_1 | TR_LINE 105543_1 | TR_LINE 105543_1 | TR_LINE 105543_1 | TR_LINE 105543_1 | TR_LINE 105543_1 | TR_LINE 105543_1 | TR_LINE 105543_1 | TR_LINE 105543_1 | TR_LINE 105543_1 | TR_LINE 105543_1 | TR_LINE 105543_1 | TR_LINE 105543_1
MK | 82913611 | PV 6/4 | PV 6/4 GLENELLA NO 2 | PV 6/4_Glenella No 2 66 kV | Loading (A) | 243.6052 | 283.6329 | 219.3181 | 245.9405 | 282.5372 | 218.5477 | 246.026 | 282.4952 | 218.5291 | 244.6633 | 285.0632 | 220.3638 | 248.5166 | 290.1944 | 223.8996
MK | 82913611 | PV 6/4 | PV 6/4 GLENELLA NO 2 | PV 6/4_Glenella No 2 66 kV | Loading (MVA) | 28.7821 | 33.6616 | 25.9069 | 28.69 | 33.5542 | 25.8264 | 28.6968 | 33.5537 | 25.8262 | 28.9108 | 33.832 | 26.0302 | 29.3413 | 34.3846 | 26.4276
MK | 82913611 | PV 6/4 | PV 6/4 GLENELLA NO 2 | PV 6/4_Glenella No 2 66 kV | Loading (MW) | 28.6658 | 33.4457 | 25.8286 | 28.58 | 33.3425 | 25.7499 | 28.5804 | 33.3424 | 25.7498 | 28.791 | 33.6089 | 25.9487 | 29.2164 | 34.1389 | 26.3423
MK | 82913611 | PV 6/4 | PV 6/4 GLENELLA NO 2 | PV 6/4_Glenella No 2 66 kV | Power Factor | 0.99596 | 0.99359 | 0.99698 | 0.99617 | 0.99369 | 0.99704 | 0.99594 | 0.9937 | 0.99704 | 0.99586 | 0.9934 | 0.99687 | 0.99575 | 0.99286 | 0.99677
MK | 82913611 | PV 6/4 | PV 6/4 GLENELLA NO 2 | PV 6/4_Glenella No 2 66 kV | Rating (A) | 809 | 908 | 891 | 809 | 908 | 891 | 809 | 908 | 891 | 809 | 908 | 891 | 809 | 908 | 891
MK | 82913611 | PV 6/4 | PV 6/4 GLENELLA NO 2 | PV 6/4_Glenella No 2 66 kV | Time | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00
MK | 82913611 | PV 6/4 | PV 6/4 GLENELLA NO 2 | PV 6/4_Glenella No 2 66 kV | Voltage at Constrained Conductor | 68.2142 | 68.52 | 68.1993 | 67.3503 | 68.5663 | 68.2271 | 67.343 | 68.5756 | 68.2325 | 68.2229 | 68.5214 | 68.1987 | 68.1653 | 68.4091 | 68.1466
MK | 83058752 | 395 | MACT-ALST | 395_Tennyson Street-Alfred Street 33 kV | % of Rated A | 27.8471 | 23.1137 | 22.1233 | 27.4709 | 22.8216 | 22.0991 | 27.2305 | 22.6365 | 21.93 | 27.0923 | 22.5243 | 21.8295 | 27.2285 | 22.6334 | 21.6918
MK | 83058752 | 395 | MACT-ALST | 395_Tennyson Street-Alfred Street 33 kV | Limiting Line Name | TR_CABLE 2960_1 | TR_CABLE 2960_1 | TR_CABLE 2960_1 | TR_CABLE 2960_1 | TR_CABLE 2960_1 | TR_CABLE 2960_1 | TR_CABLE 2960_1 | TR_CABLE 2960_1 | TR_CABLE 2960_1 | TR_CABLE 2960_1 | TR_CABLE 2960_1 | TR_CABLE 2960_1 | TR_CABLE 2960_1 | TR_CABLE 2960_1 | TR_CABLE 2960_1
MK | 83058752 | 395 | MACT-ALST | 395_Tennyson Street-Alfred Street 33 kV | Loading (A) | 187.1326 | 155.3242 | 148.6684 | 184.6047 | 153.3612 | 148.5058 | 182.989 | 152.1175 | 147.3696 | 182.0605 | 151.3631 | 146.6945 | 182.9754 | 152.0964 | 145.7687
MK | 83058752 | 395 | MACT-ALST | 395_Tennyson Street-Alfred Street 33 kV | Loading (MVA) | 11.0841 | 9.169 | 8.9329 | 10.9451 | 9.0617 | 8.8113 | 10.8537 | 8.9912 | 8.7464 | 10.7978 | 8.9448 | 8.7057 | 10.8452 | 8.9815 | 8.7623
MK | 83058752 | 395 | MACT-ALST | 395_Tennyson Street-Alfred Street 33 kV | Loading (MW) | 10.2908 | 8.4992 | 8.176 | 10.1549 | 8.3916 | 8.0786 | 10.0672 | 8.3231 | 8.0153 | 10.0143 | 8.2791 | 7.9764 | 10.0627 | 8.3181 | 8.0105
MK | 83058752 | 395 | MACT-ALST | 395_Tennyson Street-Alfred Street 33 kV | Power Factor | 0.92843 | 0.92695 | 0.91526 | 0.9278 | 0.92606 | 0.91685 | 0.92754 | 0.92569 | 0.91642 | 0.92744 | 0.92557 | 0.91622 | 0.92785 | 0.92614 | 0.9142
MK | 83058752 | 395 | MACT-ALST | 395_Tennyson Street-Alfred Street 33 kV | Rating (A) | 672 | 672 | 672 | 672 | 672 | 672 | 672 | 672 | 672 | 672 | 672 | 672 | 672 | 672 | 672
MK | 83058752 | 395 | MACT-ALST | 395_Tennyson Street-Alfred Street 33 kV | Time | 14:00 | 17:00 | 7:30 | 14:00 | 17:00 | 7:30 | 14:00 | 17:00 | 7:30 | 14:00 | 17:00 | 7:30 | 14:00 | 17:00 | 7:30
MK | 83058752 | 395 | MACT-ALST | 395_Tennyson Street-Alfred Street 33 kV | Voltage at Constrained Conductor | 34.1972 | 34.0819 | 34.6907 | 34.2308 | 34.114 | 34.256 | 34.2447 | 34.1253 | 34.2656 | 34.2419 | 34.1187 | 34.2635 | 34.2202 | 34.0933 | 34.7051
MK | 84186116 | 423 | NORTH MACKAY NO 2 | 423_North Mackay No 2 33 kV | % of Rated A | 30.4661 | 35.3382 | 28.0818 | 29.9602 | 35.0582 | 27.8819 | 30.2557 | 35.0542 | 27.8803 | 30.3557 | 35.2076 | 27.986 | 30.4009 | 35.6476 | 28.0348
MK | 84186116 | 423 | NORTH MACKAY NO 2 | 423_North Mackay No 2 33 kV | Limiting Line Name | TR_CABLE 6563_1 | TR_CABLE 6563_1 | TR_CABLE 6563_1 | TR_CABLE 6563_1 | TR_CABLE 6563_1 | TR_CABLE 6563_1 | TR_CABLE 6563_1 | TR_CABLE 6563_1 | TR_CABLE 6563_1 | TR_CABLE 6563_1 | TR_CABLE 6563_1 | TR_CABLE 6563_1 | TR_CABLE 6563_1 | TR_CABLE 6563_1 | TR_CABLE 6563_1
MK | 84186116 | 423 | NORTH MACKAY NO 2 | 423_North Mackay No 2 33 kV | Loading (A) | 186.4522 | 216.2695 | 171.8607 | 183.3561 | 214.5564 | 170.6372 | 185.1648 | 214.5319 | 170.6275 | 185.7771 | 215.4702 | 171.2744 | 186.0535 | 218.1635 | 171.573
MK | 84186116 | 423 | NORTH MACKAY NO 2 | 423_North Mackay No 2 33 kV | Loading (MVA) | 11.0857 | 12.899 | 10.2224 | 11.0443 | 12.8065 | 10.1544 | 11.0077 | 12.8069 | 10.1546 | 11.0473 | 12.852 | 10.1877 | 11.1963 | 12.9895 | 10.3286
MK | 84186116 | 423 | NORTH MACKAY NO 2 | 423_North Mackay No 2 33 kV | Loading (MW) | 10.6314 | 12.5808 | 9.6787 | 10.5459 | 12.4802 | 9.6014 | 10.5465 | 12.4802 | 9.6014 | 10.5889 | 12.5305 | 9.6401 | 10.7157 | 12.6814 | 9.7555
MK | 84186116 | 423 | NORTH MACKAY NO 2 | 423_North Mackay No 2 33 kV | Power Factor | 0.95902 | 0.97533 | 0.94681 | 0.95487 | 0.97452 | 0.94555 | 0.9581 | 0.97449 | 0.94553 | 0.95851 | 0.97498 | 0.94625 | 0.95708 | 0.97629 | 0.94452
MK | 84186116 | 423 | NORTH MACKAY NO 2 | 423_North Mackay No 2 33 kV | Rating (A) | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612
MK | 84186116 | 423 | NORTH MACKAY NO 2 | 423_North Mackay No 2 33 kV | Time | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00
MK | 84186116 | 423 | NORTH MACKAY NO 2 | 423_North Mackay No 2 33 kV | Voltage at Constrained Conductor | 34.3269 | 34.4349 | 34.3413 | 34.7761 | 34.4612 | 34.3572 | 34.3225 | 34.4659 | 34.36 | 34.3323 | 34.4369 | 34.3419 | 34.7436 | 34.3754 | 34.756
MK | 84186121 | 422 | NORTH MACKAY NO 1 | 422_North Mackay No 1 33 kV | % of Rated A | 70.814 | 82.8304 | 67.7084 | 70.8113 | 82.7554 | 67.6727 | 70.82 | 82.7421 | 67.6666 | 71.9645 | 84.2196 | 68.8229 | 73.9884 | 86.7403 | 70.7573
MK | 84186121 | 422 | NORTH MACKAY NO 1 | 422_North Mackay No 1 33 kV | Limiting Line Name | TR_LINE 11650_2 | TR_LINE 11650_2 | TR_LINE 11650_2 | TR_LINE 11650_2 | TR_LINE 11650_2 | TR_LINE 11650_2 | TR_LINE 11650_2 | TR_LINE 11650_2 | TR_LINE 11650_2 | TR_LINE 11650_2 | TR_LINE 11650_2 | TR_LINE 11650_2 | TR_LINE 11650_2 | TR_LINE 11650_2 | TR_LINE 11650_2
MK | 84186121 | 422 | NORTH MACKAY NO 1 | 422_North Mackay No 1 33 kV | Loading (A) | 259.887 | 339.6045 | 270.8335 | 259.8772 | 339.2969 | 270.6907 | 259.9092 | 339.2421 | 270.6663 | 264.1096 | 345.3001 | 275.2912 | 271.5373 | 355.6351 | 283.0288
MK | 84186121 | 422 | NORTH MACKAY NO 1 | 422_North Mackay No 1 33 kV | Loading (MVA) | 15.0829 | 19.4963 | 15.6975 | 15.0829 | 19.4959 | 15.6974 | 15.0829 | 19.4958 | 15.6974 | 15.3196 | 19.8038 | 15.9441 | 15.7148 | 20.3178 | 16.3557
MK | 84186121 | 422 | NORTH MACKAY NO 1 | 422_North Mackay No 1 33 kV | Loading (MW) | 14.9824 | 19.3304 | 15.5889 | 14.9824 | 19.3303 | 15.5888 | 14.9824 | 19.3302 | 15.5888 | 15.216 | 19.6321 | 15.832 | 15.6056 | 20.1355 | 16.2373
MK | 84186121 | 422 | NORTH MACKAY NO 1 | 422_North Mackay No 1 33 kV | Power Factor | 0.99334 | 0.99149 | 0.99308 | 0.99334 | 0.99151 | 0.99308 | 0.99334 | 0.99151 | 0.99309 | 0.99324 | 0.99133 | 0.99297 | 0.99305 | 0.99102 | 0.99277
MK | 84186121 | 422 | NORTH MACKAY NO 1 | 422_North Mackay No 1 33 kV | Rating (A) | 367 | 410 | 400 | 367 | 410 | 400 | 367 | 410 | 400 | 367 | 410 | 400 | 367 | 410 | 400
MK | 84186121 | 422 | NORTH MACKAY NO 1 | 422_North Mackay No 1 33 kV | Time | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00
MK | 84186121 | 422 | NORTH MACKAY NO 1 | 422_North Mackay No 1 33 kV | Voltage at Constrained Conductor | 33.5072 | 33.145 | 33.4633 | 33.5085 | 33.1743 | 33.4806 | 33.5044 | 33.1796 | 33.4836 | 33.489 | 33.1124 | 33.4386 | 33.4132 | 32.9847 | 33.3639
MK | 84216180 | 387 | ALFRED ST 1 | 387_Mackay-Alfred Street 1 33 kV | % of Rated A | 65.128 | 62.8287 | 54.2307 | 64.2766 | 61.994 | 53.5372 | 63.919 | 61.6515 | 53.2411 | 63.8313 | 61.5772 | 53.1631 | 64.3327 | 62.0756 | 53.5617
MK | 84216180 | 387 | ALFRED ST 1 | 387_Mackay-Alfred Street 1 33 kV | Limiting Line Name | TR_CABLE 2967_1 | TR_CABLE 2967_1 | TR_CABLE 2967_1 | TR_CABLE 2967_1 | TR_CABLE 2967_1 | TR_CABLE 2967_1 | TR_CABLE 2967_1 | TR_CABLE 2967_1 | TR_CABLE 2967_1 | TR_CABLE 2967_1 | TR_CABLE 2967_1 | TR_CABLE 2967_1 | TR_CABLE 2967_1 | TR_CABLE 2967_1 | TR_CABLE 2967_1
MK | 84216180 | 387 | ALFRED ST 1 | 387_Mackay-Alfred Street 1 33 kV | Loading (A) | 280.7018 | 270.7919 | 233.7343 | 277.032 | 267.1943 | 230.7455 | 275.4908 | 265.7181 | 229.4689 | 275.1131 | 265.3979 | 229.133 | 277.2737 | 267.5459 | 230.8511
MK | 84216180 | 387 | ALFRED ST 1 | 387_Mackay-Alfred Street 1 33 kV | Loading (MVA) | 16.6104 | 16.0339 | 14.0681 | 16.4021 | 15.8349 | 13.8974 | 16.3154 | 15.7523 | 13.8244 | 16.2917 | 15.7301 | 13.8035 | 16.4134 | 15.8461 | 13.9008
MK | 84216180 | 387 | ALFRED ST 1 | 387_Mackay-Alfred Street 1 33 kV | Loading (MW) | 16.6029 | 16.0233 | 13.9974 | 16.3957 | 15.8211 | 13.8191 | 16.3078 | 15.737 | 13.7426 | 16.2839 | 15.7146 | 13.7209 | 16.4034 | 15.8328 | 13.8227
MK | 84216180 | 387 | ALFRED ST 1 | 387_Mackay-Alfred Street 1 33 kV | Power Factor | 0.99955 | 0.99934 | 0.99497 | 0.9996 | 0.99913 | 0.99436 | 0.99954 | 0.99903 | 0.99408 | 0.99952 | 0.99902 | 0.99401 | 0.99939 | 0.99916 | 0.99438
MK | 84216180 | 387 | ALFRED ST 1 | 387_Mackay-Alfred Street 1 33 kV | Rating (A) | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431
MK | 84216180 | 387 | ALFRED ST 1 | 387_Mackay-Alfred Street 1 33 kV | Time | 16:30 | 17:00 | 8:30 | 16:30 | 17:00 | 8:30 | 16:30 | 17:00 | 8:30 | 16:30 | 17:00 | 8:30 | 16:30 | 17:00 | 8:30
MK | 84216180 | 387 | ALFRED ST 1 | 387_Mackay-Alfred Street 1 33 kV | Voltage at Constrained Conductor | 34.1645 | 34.1855 | 34.7498 | 34.183 | 34.2158 | 34.7728 | 34.1923 | 34.2264 | 34.7826 | 34.1896 | 34.2195 | 34.781 | 34.1767 | 34.195 | 34.7653
MK | 84293483 | 6328 | BROADLEA-MOORVALE | 6328_Broadlea - Moorvale 66 kV | % of Rated A | 13.3641 | 13.2419 | 12.3438 | 13.1405 | 13.0198 | 12.1383 | 13.1405 | 13.0197 | 12.1383 | 13.1405 | 13.02 | 12.1383 | 13.3641 | 13.2424 | 12.3438
MK | 84293483 | 6328 | BROADLEA-MOORVALE | 6328_Broadlea - Moorvale 66 kV | Limiting Line Name | TR_LINE 36093_1 | TR_LINE 36093_1 | TR_LINE 36093_1 | TR_LINE 36093_1 | TR_LINE 36093_1 | TR_LINE 36093_1 | TR_LINE 36093_1 | TR_LINE 36093_1 | TR_LINE 36093_1 | TR_LINE 36093_1 | TR_LINE 36093_1 | TR_LINE 36093_1 | TR_LINE 36093_1 | TR_LINE 36093_1 | TR_LINE 36093_1
MK | 84293483 | 6328 | BROADLEA-MOORVALE | 6328_Broadlea - Moorvale 66 kV | Loading (A) | 51.5855 | 51.5111 | 41.7221 | 50.7222 | 50.647 | 41.0273 | 50.7222 | 50.6468 | 41.0273 | 50.7222 | 50.6476 | 41.0273 | 51.5855 | 51.5129 | 41.7221
MK | 84293483 | 6328 | BROADLEA-MOORVALE | 6328_Broadlea - Moorvale 66 kV | Loading (MVA) | 6.1197 | 6.1786 | 4.9627 | 6.0181 | 6.0761 | 4.8805 | 6.0181 | 6.0761 | 4.8805 | 6.0181 | 6.0761 | 4.8805 | 6.1197 | 6.1786 | 4.9627
MK | 84293483 | 6328 | BROADLEA-MOORVALE | 6328_Broadlea - Moorvale 66 kV | Loading (MW) | 5.9865 | 6.0449 | 4.864 | 5.8881 | 5.9455 | 4.7841 | 5.8881 | 5.9455 | 4.7841 | 5.8881 | 5.9455 | 4.7841 | 5.9865 | 6.0449 | 4.864
MK | 84293483 | 6328 | BROADLEA-MOORVALE | 6328_Broadlea - Moorvale 66 kV | Power Factor | 0.97823 | 0.97835 | 0.98011 | 0.9784 | 0.97852 | 0.98024 | 0.9784 | 0.97852 | 0.98024 | 0.9784 | 0.97852 | 0.98024 | 0.97823 | 0.97835 | 0.98011
MK | 84293483 | 6328 | BROADLEA-MOORVALE | 6328_Broadlea - Moorvale 66 kV | Rating (A) | 386 | 389 | 338 | 386 | 389 | 338 | 386 | 389 | 338 | 386 | 389 | 338 | 386 | 389 | 338
MK | 84293483 | 6328 | BROADLEA-MOORVALE | 6328_Broadlea - Moorvale 66 kV | Time | 15:30 | 19:00 | 23:00 | 15:30 | 19:00 | 23:00 | 15:30 | 19:00 | 23:00 | 15:30 | 19:00 | 23:00 | 15:30 | 19:00 | 23:00
MK | 84293483 | 6328 | BROADLEA-MOORVALE | 6328_Broadlea - Moorvale 66 kV | Voltage at Constrained Conductor | 68.492 | 69.2518 | 68.6734 | 68.5012 | 69.264 | 68.6804 | 68.5012 | 69.2642 | 68.6804 | 68.5012 | 69.2631 | 68.6804 | 68.492 | 69.2495 | 68.6734
MK | 84293489 | 6330 | BROADLEA-MILLENNIUM | 6330 Broadlea - Millennium 66 kV | % of Rated A | 35.2755 | 36.263 | 40.9992 | 35.2734 | 36.261 | 40.9973 | 35.2734 | 36.261 | 40.9973 | 35.2734 | 36.261 | 40.9973 | 35.2755 | 36.263 | 40.9992
MK | 84293489 | 6330 | BROADLEA-MILLENNIUM | 6330 Broadlea - Millennium 66 kV | Limiting Line Name | TR_LINE 63688_1 | TR_LINE 63688_1 | TR_LINE 63688_1 | TR_LINE 63688_1 | TR_LINE 63688_1 | TR_LINE 63688_1 | TR_LINE 63688_1 | TR_LINE 63688_1 | TR_LINE 63688_1 | TR_LINE 63688_1 | TR_LINE 63688_1 | TR_LINE 63688_1 | TR_LINE 63688_1 | TR_LINE 63688_1 | TR_LINE 63688_1
MK | 84293489 | 6330 | BROADLEA-MILLENNIUM | 6330 Broadlea - Millennium 66 kV | Loading (A) | 248.6248 | 266.4654 | 267.2482 | 248.6101 | 266.451 | 267.2359 | 248.6101 | 266.451 | 267.2359 | 248.6101 | 266.451 | 267.2359 | 248.6248 | 266.4654 | 267.2482
MK | 84293489 | 6330 | BROADLEA-MILLENNIUM | 6330 Broadlea - Millennium 66 kV | Loading (MVA) | 29.9365 | 32.0576 | 32.146 | 29.9365 | 32.0576 | 32.146 | 29.9365 | 32.0576 | 32.146 | 29.9365 | 32.0576 | 32.146 | 29.9365 | 32.0576 | 32.146
MK | 84293489 | 6330 | BROADLEA-MILLENNIUM | 6330 Broadlea - Millennium 66 kV | Loading (MW) | 27.7056 | 29.6453 | 29.7921 | 27.7056 | 29.6453 | 29.7921 | 27.7056 | 29.6453 | 29.7921 | 27.7056 | 29.6453 | 29.7921 | 27.7056 | 29.6453 | 29.7921
MK | 84293489 | 6330 | BROADLEA-MILLENNIUM | 6330 Broadlea - Millennium 66 kV | Power Factor | 0.92548 | 0.92475 | 0.92677 | 0.92548 | 0.92475 | 0.92677 | 0.92548 | 0.92475 | 0.92677 | 0.92548 | 0.92475 | 0.92677 | 0.92548 | 0.92475 | 0.92677
MK | 84293489 | 6330 | BROADLEA-MILLENNIUM | 6330 Broadlea - Millennium 66 kV | Rating (A) | 705 | 735 | 652 | 705 | 735 | 652 | 705 | 735 | 652 | 705 | 735 | 652 | 705 | 735 | 652
MK | 84293489 | 6330 | BROADLEA-MILLENNIUM | 6330 Broadlea - Millennium 66 kV | Time | 13:00 | 21:30 | 1:30 | 13:00 | 21:30 | 1:30 | 13:00 | 21:30 | 1:30 | 13:00 | 21:30 | 1:30 | 13:00 | 21:30 | 1:30
MK | 84293489 | 6330 | BROADLEA-MILLENNIUM | 6330 Broadlea - Millennium 66 kV | Voltage at Constrained Conductor | 69.5178 | 69.4591 | 69.4466 | 69.5219 | 69.4628 | 69.4498 | 69.5219 | 69.4628 | 69.4498 | 69.5219 | 69.4628 | 69.4498 | 69.5178 | 69.4591 | 69.4466
MK | 84544397 | 7366 | 132KV MORA - BROD000007680919S-FDTR132 | 7366_Moranbah - Broadlea 132 kV | % of Rated A | 40.2382 | 38.8326 | 44.8025 | 40.1769 | 38.7685 | 44.7495 | 40.1769 | 38.7684 | 44.7495 | 40.1769 | 38.769 | 44.7495 | 40.2382 | 38.834 | 44.8025
MK | 84544397 | 7366 | 132KV MORA - BROD000007680919S-FDTR132 | 7366_Moranbah - Broadlea 132 kV | Limiting Line Name | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1
MK | 84544397 | 7366 | 132KV MORA - BROD000007680919S-FDTR132 | 7366_Moranbah - Broadlea 132 kV | Loading (A) | 283.6733 | 285.4135 | 292.1063 | 283.2408 | 284.9423 | 291.7608 | 283.2408 | 284.9414 | 291.7608 | 283.2408 | 284.946 | 291.7608 | 283.6733 | 285.4233 | 292.1063
MK | 84544397 | 7366 | 132KV MORA - BROD000007680919S-FDTR132 | 7366_Moranbah - Broadlea 132 kV | Loading (MVA) | 67.3865 | 67.773 | 69.3442 | 67.2862 | 67.6665 | 69.2642 | 67.2862 | 67.6665 | 69.2642 | 67.2862 | 67.6666 | 69.2642 | 67.3865 | 67.7731 | 69.3442
MK | 84544397 | 7366 | 132KV MORA - BROD000007680919S-FDTR132 | 7366_Moranbah - Broadlea 132 kV | Loading (MW) | 65.0519 | 65.4027 | 66.9329 | 64.9574 | 65.3026 | 66.857 | 64.9574 | 65.3026 | 66.857 | 64.9574 | 65.3026 | 66.857 | 65.0519 | 65.4027 | 66.9329
MK | 84544397 | 7366 | 132KV MORA - BROD000007680919S-FDTR132 | 7366_Moranbah - Broadlea 132 kV | Power Factor | 0.96536 | 0.96503 | 0.96523 | 0.96539 | 0.96506 | 0.96525 | 0.96539 | 0.96506 | 0.96525 | 0.96539 | 0.96506 | 0.96525 | 0.96536 | 0.96503 | 0.96523
MK | 84544397 | 7366 | 132KV MORA - BROD000007680919S-FDTR132 | 7366_Moranbah - Broadlea 132 kV | Rating (A) | 705 | 735 | 652 | 705 | 735 | 652 | 705 | 735 | 652 | 705 | 735 | 652 | 705 | 735 | 652
MK | 84544397 | 7366 | 132KV MORA - BROD000007680919S-FDTR132 | 7366_Moranbah - Broadlea 132 kV | Time | 13:00 | 19:00 | 1:30 | 13:00 | 19:00 | 1:30 | 13:00 | 19:00 | 1:30 | 13:00 | 19:00 | 1:30 | 13:00 | 19:00 | 1:30
MK | 84544397 | 7366 | 132KV MORA - BROD000007680919S-FDTR132 | 7366_Moranbah - Broadlea 132 kV | Voltage at Constrained Conductor | 137.1493 | 137.0949 | 137.0594 | 137.1544 | 137.106 | 137.0633 | 137.1544 | 137.1064 | 137.0633 | 137.1544 | 137.1043 | 137.0633 | 137.1493 | 137.0904 | 137.0594
MK | 84750025 | 430 | ALFRED ST 2 | 430_Mackay-Alfred Street 2 33 kV | % of Rated A | 47.1169 | 45.4538 | 39.2366 | 46.5009 | 44.8502 | 38.7352 | 46.2423 | 44.6025 | 38.521 | 46.1789 | 44.5488 | 38.4646 | 46.5417 | 44.9092 | 38.7529
MK | 84750025 | 430 | ALFRED ST 2 | 430_Mackay-Alfred Street 2 33 kV | Limiting Line Name | TR_CABLE 8887_1 | TR_CABLE 8887_1 | TR_CABLE 8887_1 | TR_CABLE 8887_1 | TR_CABLE 8887_1 | TR_CABLE 8887_1 | TR_CABLE 8887_1 | TR_CABLE 8887_1 | TR_CABLE 8887_1 | TR_CABLE 8887_1 | TR_CABLE 8887_1 | TR_CABLE 8887_1 | TR_CABLE 8887_1 | TR_CABLE 8887_1 | TR_CABLE 8887_1
MK | 84750025 | 430 | ALFRED ST 2 | 430_Mackay-Alfred Street 2 33 kV | Loading (A) | 272.8069 | 263.1776 | 227.1798 | 269.24 | 259.6827 | 224.2767 | 267.7427 | 258.2486 | 223.0367 | 267.3758 | 257.9375 | 222.7103 | 269.4766 | 260.0243 | 224.3792
MK | 84750025 | 430 | ALFRED ST 2 | 430_Mackay-Alfred Street 2 33 kV | Loading (MVA) | 16.1432 | 15.583 | 13.6736 | 15.9408 | 15.3897 | 13.5078 | 15.8565 | 15.3095 | 13.4369 | 15.8335 | 15.2879 | 13.4166 | 15.9519 | 15.4006 | 13.5111
MK | 84750025 | 430 | ALFRED ST 2 | 430_Mackay-Alfred Street 2 33 kV | Loading (MW) | 16.1355 | 15.5723 | 13.6034 | 15.9341 | 15.3758 | 13.4301 | 15.8488 | 15.294 | 13.3558 | 15.8255 | 15.2723 | 13.3347 | 15.9416 | 15.3871 | 13.4336
MK | 84750025 | 430 | ALFRED ST 2 | 430_Mackay-Alfred Street 2 33 kV | Power Factor | 0.99952 | 0.99931 | 0.99486 | 0.99958 | 0.99909 | 0.99425 | 0.99951 | 0.99899 | 0.99396 | 0.9995 | 0.99898 | 0.99389 | 0.99936 | 0.99912 | 0.99427
MK | 84750025 | 430 | ALFRED ST 2 | 430_Mackay-Alfred Street 2 33 kV | Rating (A) | 579 | 579 | 579 | 579 | 579 | 579 | 579 | 579 | 579 | 579 | 579 | 579 | 579 | 579 | 579
MK | 84750025 | 430 | ALFRED ST 2 | 430_Mackay-Alfred Street 2 33 kV | Time | 16:30 | 17:00 | 8:30 | 16:30 | 17:00 | 8:30 | 16:30 | 17:00 | 8:30 | 16:30 | 17:00 | 8:30 | 16:30 | 17:00 | 8:30
MK | 84750025 | 430 | ALFRED ST 2 | 430_Mackay-Alfred Street 2 33 kV | Voltage at Constrained Conductor | 34.1645 | 34.1855 | 34.7498 | 34.183 | 34.2158 | 34.7728 | 34.1923 | 34.2264 | 34.7826 | 34.1896 | 34.2195 | 34.781 | 34.1767 | 34.195 | 34.7653
NQ | 10132026 | 7182 | ROSS - MILLCHESTER | 7182 Ross - Milchester | % of Rated A | 42.7749 | 39.2315 | 36.287 | 42.3292 | 38.7979 | 35.9477 | 44.5101 | 41.1347 | 38.2666 | 44.5645 | 41.1973 | 38.3106 | 44.9236 | 41.5294 | 38.0196
NQ | 10132026 | 7182 | ROSS - MILLCHESTER | 7182 Ross - Milchester | Limiting Line Name | TR_LINE 76326_1 | TR_LINE 76326_1 | TR_LINE 76326_1 | TR_LINE 76326_1 | TR_LINE 76326_1 | TR_LINE 76326_1 | TR_LINE 76326_1 | TR_LINE 76326_1 | TR_LINE 76326_1 | TR_LINE 76326_1 | TR_LINE 76326_1 | TR_LINE 76326_1 | TR_LINE 76326_1 | TR_LINE 76326_1 | TR_LINE 76326_1
NQ | 10132026 | 7182 | ROSS - MILLCHESTER | 7182 Ross - Milchester | Loading (A) | 133.4576 | 140.4488 | 119.3843 | 132.067 | 138.8964 | 118.2678 | 138.8715 | 147.2623 | 125.8972 | 139.0413 | 147.4864 | 126.0418 | 140.1617 | 148.6752 | 125.0845
NQ | 10132026 | 7182 | ROSS - MILLCHESTER | 7182 Ross - Milchester | Loading (MVA) | 31.5438 | 33.1519 | 28.3975 | 31.2272 | 32.797 | 28.1407 | 32.7957 | 34.7262 | 29.8135 | 32.8329 | 34.7752 | 29.8456 | 33.0869 | 35.0432 | 29.7076
NQ | 10132026 | 7182 | ROSS - MILLCHESTER | 7182 Ross - Milchester | Loading (MW) | 31.2091 | 32.8114 | 27.6642 | 30.8817 | 32.4514 | 27.3912 | 32.4316 | 34.3449 | 29.4238 | 32.4734 | 34.3991 | 29.4598 | 32.736 | 34.6766 | 29.024
NQ | 10132026 | 7182 | ROSS - MILLCHESTER | 7182 Ross - Milchester | Power Factor | 0.98939 | 0.98973 | 0.97418 | 0.98894 | 0.98946 | 0.97337 | 0.9889 | 0.98902 | 0.98693 | 0.98905 | 0.98918 | 0.98708 | 0.9894 | 0.98954 | 0.97699
NQ | 10132026 | 7182 | ROSS - MILLCHESTER | 7182 Ross - Milchester | Rating (A) | 312 | 358 | 329 | 312 | 358 | 329 | 312 | 358 | 329 | 312 | 358 | 329 | 312 | 358 | 329
NQ | 10132026 | 7182 | ROSS - MILLCHESTER | 7182 Ross - Milchester | Time | 15:30 | 19:00 | 22:00 | 15:30 | 19:00 | 22:00 | 15:30 | 19:00 | 22:00 | 15:30 | 19:00 | 22:00 | 15:30 | 19:00 | 22:00
NQ | 10132026 | 7182 | ROSS - MILLCHESTER | 7182 Ross - Milchester | Voltage at Constrained Conductor | 136.4616 | 136.2792 | 137.3322 | 136.5141 | 136.327 | 137.3748 | 136.3464 | 136.146 | 136.7214 | 136.3342 | 136.131 | 136.7115 | 136.2906 | 136.0831 | 137.1207
NQ | 20001222 | AV-CB-1 | Aitkenvale-Cranbrook | AV-CB-1_Aitkenvale-Cranbrook 66 kV | % of Rated A | 14.6301 | 6.9779 | 12.6755 | 14.5071 | 6.9279 | 12.5608 | 16.0637 | 10.8139 | 14.063 | 15.9797 | 10.7408 | 13.9842 | 16.1775 | 10.8315 | 14.1563
NQ | 20001222 | AV-CB-1 | Aitkenvale-Cranbrook | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Limiting Line Name | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1
NQ | 20001222 | AV-CB-1 | Aitkenvale-Cranbrook | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Loading (A) | 48.7181 | 27.214 | 46.0119 | 48.3085 | 27.0186 | 45.5956 | 53.4923 | 42.1742 | 51.0486 | 53.2124 | 41.889 | 50.7626 | 53.8712 | 42.243 | 51.3873
NQ | 20001222 | AV-CB-1 | Aitkenvale-Cranbrook | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Loading (MVA) | 5.8066 | 3.2097 | 5.4796 | 5.7588 | 3.1874 | 5.431 | 6.3232 | 5.0205 | 6.0293 | 6.2898 | 4.9855 | 5.995 | 6.3656 | 5.0252 | 6.0667
NQ | 20001222 | AV-CB-1 | Aitkenvale-Cranbrook | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Loading (MW) | 5.6149 | 2.864 | 5.2893 | 5.5545 | 2.8224 | 5.2278 | 5.6314 | 3.4081 | 5.307 | 5.599 | 3.3665 | 5.2732 | 5.674 | 3.4107 | 5.3442
NQ | 20001222 | AV-CB-1 | Aitkenvale-Cranbrook | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Power Factor | 0.96699 | 0.89228 | 0.96527 | 0.96453 | 0.88548 | 0.96258 | 0.8906 | 0.67885 | 0.88019 | 0.89017 | 0.67526 | 0.87959 | 0.89135 | 0.67872 | 0.88091
NQ | 20001222 | AV-CB-1 | Aitkenvale-Cranbrook | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Rating (A) | 333 | 390 | 363 | 333 | 390 | 363 | 333 | 390 | 363 | 333 | 390 | 363 | 333 | 390 | 363
NQ | 20001222 | AV-CB-1 | Aitkenvale-Cranbrook | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Time | 9:30 | 17:00 | 8:30 | 9:30 | 17:00 | 8:30 | 9:30 | 17:00 | 8:30 | 9:30 | 17:00 | 8:30 | 9:30 | 17:00 | 8:30
NQ | 20001222 | AV-CB-1 | Aitkenvale-Cranbrook | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Voltage at Constrained Conductor | 68.8129 | 68.0951 | 68.7576 | 68.8251 | 68.1106 | 68.7698 | 68.2471 | 68.7285 | 68.1903 | 68.244 | 68.7147 | 68.1844 | 68.2221 | 68.6807 | 68.1613
NQ | 20001857 | AY-HH-1 | AYR-HOMEHILL/JARVISFIELD | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | % of Rated A | 40.881 | 35.9203 | 38.551 | 41.1506 | 36.2031 | 38.864 | 41.0083 | 36.0339 | 39.184 | 41.207 | 36.2415 | 39.3663 | 41.4425 | 36.5533 | 39.1327
NQ | 20001857 | AY-HH-1 | AYR-HOMEHILL/JARVISFIELD | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Limiting Line Name | TR_LINE 31671_1 | TR_LINE 31671_1 | TR_LINE 31671_1 | TR_LINE 31671_1 | TR_LINE 31671_1 | TR_LINE 31671_1 | TR_LINE 31671_1 | TR_LINE 31671_1 | TR_LINE 31671_1 | TR_LINE 31671_1 | TR_LINE 31671_1 | TR_LINE 31671_1 | TR_LINE 31671_1 | TR_LINE 31671_1 | TR_LINE 31671_1
NQ | 20001857 | AY-HH-1 | AYR-HOMEHILL/JARVISFIELD | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Loading (A) | 105.4718 | 105.9642 | 104.8575 | 106.1674 | 106.7985 | 105.7087 | 105.8001 | 106.2995 | 106.5791 | 106.3128 | 106.9119 | 107.0749 | 106.9205 | 107.8317 | 106.4398
NQ | 20001857 | AY-HH-1 | AYR-HOMEHILL/JARVISFIELD | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Loading (MVA) | 12.0544 | 12.0693 | 11.9926 | 12.003 | 12.179 | 11.9449 | 11.9664 | 12.1269 | 12.0425 | 12.023 | 12.1949 | 12.0971 | 12.087 | 12.293 | 12.0266
NQ | 20001857 | AY-HH-1 | AYR-HOMEHILL/JARVISFIELD | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Loading (MW) | 11.8616 | 12.0279 | 11.7661 | 11.8131 | 12.1324 | 11.738 | 11.7783 | 12.0818 | 11.8074 | 11.8331 | 12.1485 | 11.8602 | 11.8956 | 12.2446 | 11.8183
NQ | 20001857 | AY-HH-1 | AYR-HOMEHILL/JARVISFIELD | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Power Factor | 0.98401 | 0.99657 | 0.98111 | 0.98417 | 0.99618 | 0.98267 | 0.98428 | 0.99628 | 0.98048 | 0.98421 | 0.9962 | 0.98042 | 0.98416 | 0.99606 | 0.98268
NQ | 20001857 | AY-HH-1 | AYR-HOMEHILL/JARVISFIELD | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Rating (A) | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272
NQ | 20001857 | AY-HH-1 | AYR-HOMEHILL/JARVISFIELD | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Time | 11:00 | 18:30 | 8:00 | 10:00 | 18:30 | 8:30 | 10:00 | 18:30 | 8:00 | 10:00 | 18:30 | 8:00 | 10:00 | 18:30 | 8:30
NQ | 20001857 | AY-HH-1 | AYR-HOMEHILL/JARVISFIELD | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Voltage at Constrained Conductor | 65.9854 | 65.7601 | 66.032 | 65.2738 | 65.8392 | 65.2398 | 65.3007 | 65.8655 | 65.2353 | 65.2928 | 65.8556 | 65.2278 | 65.2678 | 65.8191 | 65.2346
NQ | 20003134 | BO-DG-1 | Bohle-Dan Gleeson | BO-DG-1_Bohle-Dan Gleeson 66 kV | % of Rated A | 46.0402 | 55.8769 | 39.6286 | 46.2542 | 56.1884 | 39.8428 | 47.7477 | 56.795 | 40.8964 | 48.4908 | 57.7793 | 41.5964 | 49.4468 | 58.9538 | 42.4453
NQ | 20003134 | BO-DG-1 | Bohle-Dan Gleeson | BO-DG-1_Bohle-Dan Gleeson 66 kV | Limiting Line Name | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1
NQ | 20003134 | BO-DG-1 | Bohle-Dan Gleeson | BO-DG-1_Bohle-Dan Gleeson 66 kV | Loading (A) | 205.7997 | 249.7699 | 177.1398 | 206.7564 | 251.162 | 178.0973 | 213.4323 | 253.8737 | 182.8068 | 216.7539 | 258.2735 | 185.9361 | 221.0272 | 263.5234 | 189.7303
NQ | 20003134 | BO-DG-1 | Bohle-Dan Gleeson | BO-DG-1_Bohle-Dan Gleeson 66 kV | Loading (MVA) | 24.2797 | 29.5555 | 21.0291 | 24.3936 | 29.7233 | 21.1443 | 25.4781 | 30.2172 | 21.567 | 25.8684 | 30.7306 | 21.9315 | 26.3651 | 31.3356 | 22.3694
NQ | 20003134 | BO-DG-1 | Bohle-Dan Gleeson | BO-DG-1_Bohle-Dan Gleeson 66 kV | Loading (MW) | 24.2794 | 29.2395 | 21.0075 | 24.3933 | 29.4049 | 21.1232 | 25.0261 | 29.5598 | 21.3557 | 25.4053 | 30.05 | 21.7107 | 25.8833 | 30.6253 | 22.1365
NQ | 20003134 | BO-DG-1 | Bohle-Dan Gleeson | BO-DG-1_Bohle-Dan Gleeson 66 kV | Power Factor | 0.99999 | 0.98931 | 0.99897 | 0.99999 | 0.98929 | 0.999 | 0.98226 | 0.97824 | 0.9902 | 0.9821 | 0.97785 | 0.98994 | 0.98172 | 0.97733 | 0.98959
NQ | 20003134 | BO-DG-1 | Bohle-Dan Gleeson | BO-DG-1_Bohle-Dan Gleeson 66 kV | Rating (A) | 447 | 447 | 447 | 447 | 447 | 447 | 447 | 447 | 447 | 447 | 447 | 447 | 447 | 447 | 447
NQ | 20003134 | BO-DG-1 | Bohle-Dan Gleeson | BO-DG-1_Bohle-Dan Gleeson 66 kV | Time | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00
NQ | 20003134 | BO-DG-1 | Bohle-Dan Gleeson | BO-DG-1_Bohle-Dan Gleeson 66 kV | Voltage at Constrained Conductor | 68.1142 | 68.3185 | 68.5399 | 68.1172 | 68.3255 | 68.5451 | 68.9202 | 68.7189 | 68.1141 | 68.9037 | 68.6959 | 68.0994 | 68.8689 | 68.6527 | 68.0702
NQ | 20003135 | 6127 | BOHLE-BLACK RIVER 1 | 6127_Bohle-Black River 1 66 kV | % of Rated A | 16.2254 | 20.4085 | 16.0302 | 16.3573 | 20.578 | 16.1602 | 16.3338 | 20.647 | 16.4281 | 16.647 | 21.056 | 16.7456 | 16.9658 | 21.4737 | 17.0647
NQ | 20003135 | 6127 | BOHLE-BLACK RIVER 1 | 6127_Bohle-Black River 1 66 kV | Limiting Line Name | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1
NQ | 20003135 | 6127 | BOHLE-BLACK RIVER 1 | 6127_Bohle-Black River 1 66 kV | Loading (A) | 118.283 | 159.7986 | 113.814 | 119.245 | 161.1254 | 114.7374 | 119.073 | 161.6657 | 116.6392 | 121.3562 | 164.8681 | 118.8937 | 123.6809 | 168.1392 | 121.1595
NQ | 20003135 | 6127 | BOHLE-BLACK RIVER 1 | 6127_Bohle-Black River 1 66 kV | Loading (MVA) | 13.8419 | 18.6722 | 13.4222 | 13.9544 | 18.8274 | 13.5314 | 14.0652 | 18.9798 | 13.6386 | 14.3286 | 19.3433 | 13.8965 | 14.5919 | 19.7076 | 14.152
NQ | 20003135 | 6127 | BOHLE-BLACK RIVER 1 | 6127_Bohle-Black River 1 66 kV | Loading (MW) | 13.74 | 18.4539 | 13.33 | 13.8504 | 18.6043 | 13.4372 | 13.9591 | 18.7533 | 13.5419 | 14.218 | 19.1052 | 13.795 | 14.4757 | 19.4567 | 14.0454
NQ | 20003135 | 6127 | BOHLE-BLACK RIVER 1 | 6127_Bohle-Black River 1 66 kV | Power Factor | 0.99264 | 0.98831 | 0.99313 | 0.99254 | 0.98815 | 0.99304 | 0.99246 | 0.98807 | 0.99291 | 0.99228 | 0.98769 | 0.9927 | 0.99203 | 0.98727 | 0.99246
NQ | 20003135 | 6127 | BOHLE-BLACK RIVER 1 | 6127_Bohle-Black River 1 66 kV | Rating (A) | 729 | 783 | 710 | 729 | 783 | 710 | 729 | 783 | 710 | 729 | 783 | 710 | 729 | 783 | 710
NQ | 20003135 | 6127 | BOHLE-BLACK RIVER 1 | 6127_Bohle-Black River 1 66 kV | Time | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00
NQ | 20003135 | 6127 | BOHLE-BLACK RIVER 1 | 6127_Bohle-Black River 1 66 kV | Voltage at Constrained Conductor | 67.5638 | 67.4625 | 68.0875 | 67.5633 | 67.463 | 68.0888 | 68.1979 | 67.7819 | 67.5097 | 68.168 | 67.7382 | 67.4818 | 68.1159 | 67.6711 | 67.4373
NQ | 20003732 | CHTO | CLARESOUTH-CHARTERSTOWERS | CHTO_Clare South - Charters Towers 66 kV | % of Rated A | 66.5499 | 58.498 | 62.6076 | 66.5282 | 58.826 | 63.1828 | 66.5467 | 58.8352 | 63.0341 | 66.5531 | 58.8415 | 63.0387 | 66.5754 | 58.8627 | 63.0589
NQ | 20003732 | CHTO | CLARESOUTH-CHARTERSTOWERS | CHTO_Clare South - Charters Towers 66 kV | Limiting Line Name | TR_LINE 33612_1 | TR_LINE 33612_1 | TR_LINE 33612_1 | TR_LINE 33612_1 | TR_LINE 33612_1 | TR_LINE 33612_1 | TR_LINE 33612_1 | TR_LINE 33612_1 | TR_LINE 33612_1 | TR_LINE 33612_1 | TR_LINE 33612_1 | TR_LINE 33612_1 | TR_LINE 33612_1 | TR_LINE 33612_1 | TR_LINE 33612_1
NQ | 20003732 | CHTO | CLARESOUTH-CHARTERSTOWERS | CHTO_Clare South - Charters Towers 66 kV | Loading (A) | 132.4258 | 130.4418 | 127.7108 | 132.3825 | 131.1734 | 128.8843 | 132.4194 | 131.1938 | 128.581 | 132.4321 | 131.208 | 128.5902 | 132.4765 | 131.2551 | 128.6314
NQ | 20003732 | CHTO | CLARESOUTH-CHARTERSTOWERS | CHTO_Clare South - Charters Towers 66 kV | Loading (MVA) | 14.7071 | 14.4882 | 14.3263 | 14.7069 | 14.5717 | 14.3235 | 14.7071 | 14.5718 | 14.3217 | 14.7071 | 14.5719 | 14.3218 | 14.7074 | 14.5721 | 14.322
NQ | 20003732 | CHTO | CLARESOUTH-CHARTERSTOWERS | CHTO_Clare South - Charters Towers 66 kV | Loading (MW) | 12.6699 | 12.4776 | 12.3308 | 12.6698 | 12.5484 | 12.3306 | 12.6699 | 12.5484 | 12.3303 | 12.6699 | 12.5484 | 12.3304 | 12.6699 | 12.5484 | 12.3304
NQ | 20003732 | CHTO | CLARESOUTH-CHARTERSTOWERS | CHTO_Clare South - Charters Towers 66 kV | Power Factor | 0.86148 | 0.86123 | 0.86071 | 0.86149 | 0.86115 | 0.86086 | 0.86148 | 0.86114 | 0.86095 | 0.86148 | 0.86114 | 0.86095 | 0.86146 | 0.86112 | 0.86094
NQ | 20003732 | CHTO | CLARESOUTH-CHARTERSTOWERS | CHTO_Clare South - Charters Towers 66 kV | Rating (A) | 199 | 223 | 204 | 199 | 223 | 204 | 199 | 223 | 204 | 199 | 223 | 204 | 199 | 223 | 204
NQ | 20003732 | CHTO | CLARESOUTH-CHARTERSTOWERS | CHTO_Clare South - Charters Towers 66 kV | Time | 15:30 | 17:00 | 8:30 | 15:30 | 17:30 | 8:30 | 15:30 | 17:30 | 8:30 | 15:30 | 17:30 | 8:30 | 15:30 | 17:30 | 8:30
NQ | 20003732 | CHTO | CLARESOUTH-CHARTERSTOWERS | CHTO_Clare South - Charters Towers 66 kV | Voltage at Constrained Conductor | 64.1201 | 64.1263 | 64.766 | 64.14 | 64.1362 | 64.1636 | 64.123 | 64.1267 | 64.3071 | 64.1172 | 64.1201 | 64.3027 | 64.0968 | 64.0983 | 64.2832
NQ | 20003733 | EAAY | CLARESOUTH-EASTAYR | EAAY_Clare South - East Ayr 66 kV | % of Rated A | 56.1671 | 40.3433 | 37.267 | 56.0479 | 39.7054 | 36.7799 | 55.8385 | 39.5355 | 37.1289 | 56.052 | 39.6897 | 37.2745 | 56.5055 | 40.024 | 37.07
NQ | 20003733 | EAAY | CLARESOUTH-EASTAYR | EAAY_Clare South - East Ayr 66 kV | Limiting Line Name | TR_LINE 40742_1 | TR_LINE 40742_1 | TR_LINE 40742_1 | TR_LINE 40742_1 | TR_LINE 40742_1 | TR_LINE 40742_1 | TR_LINE 40742_1 | TR_LINE 40742_1 | TR_LINE 40742_1 | TR_LINE 40742_1 | TR_LINE 40742_1 | TR_LINE 40742_1 | TR_LINE 40742_1 | TR_LINE 40742_1 | TR_LINE 40742_1
NQ | 20003733 | EAAY | CLARESOUTH-EASTAYR | EAAY_Clare South - East Ayr 66 kV | Loading (A) | 117.9474 | 127.0776 | 115.5238 | 117.6972 | 125.0681 | 114.0139 | 117.2574 | 124.533 | 115.0959 | 117.7057 | 125.0187 | 115.547 | 118.6581 | 126.0717 | 114.9132
NQ | 20003733 | EAAY | CLARESOUTH-EASTAYR | EAAY_Clare South - East Ayr 66 kV | Loading (MVA) | 13.5604 | 14.545 | 13.2766 | 13.3655 | 14.3293 | 13.1128 | 13.3193 | 14.2732 | 13.0686 | 13.3685 | 14.3267 | 13.118 | 13.4703 | 14.4399 | 13.2116
NQ | 20003733 | EAAY | CLARESOUTH-EASTAYR | EAAY_Clare South - East Ayr 66 kV | Loading (MW) | 13.2879 | 14.1815 | 12.9604 | 13.1021 | 13.9827 | 12.809 | 13.0589 | 13.9311 | 12.763 | 13.1065 | 13.982 | 12.8098 | 13.2021 | 14.0875 | 12.9024
NQ | 20003733 | EAAY | CLARESOUTH-EASTAYR | EAAY_Clare South - East Ayr 66 kV | Power Factor | 0.97991 | 0.97501 | 0.97618 | 0.98029 | 0.97582 | 0.97683 | 0.98046 | 0.97603 | 0.97661 | 0.9804 | 0.97594 | 0.97651 | 0.98009 | 0.97559 | 0.9766
NQ | 20003733 | EAAY | CLARESOUTH-EASTAYR | EAAY_Clare South - East Ayr 66 kV | Rating (A) | 210 | 315 | 310 | 210 | 315 | 310 | 210 | 315 | 310 | 210 | 315 | 310 | 210 | 315 | 310
NQ | 20003733 | EAAY | CLARESOUTH-EASTAYR | EAAY_Clare South - East Ayr 66 kV | Time | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00
NQ | 20003733 | EAAY | CLARESOUTH-EASTAYR | EAAY_Clare South - East Ayr 66 kV | Voltage at Constrained Conductor | 66.378 | 66.0822 | 66.3522 | 65.563 | 66.148 | 66.4013 | 65.5812 | 66.1725 | 65.5556 | 65.5728 | 66.1624 | 65.5462 | 65.5421 | 66.1283 | 66.378
NQ | 20003734 | CLSO-HOHI-1 | CLARESOUTH-HOMEHILL NO.01 | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | % of Rated A | 33.5733 | 31.3787 | 30.55 | 33.209 | 30.6152 | 29.9662 | 33.0727 | 30.4763 | 30.2544 | 33.1664 | 30.5652 | 30.3445 | 33.4356 | 30.8228 | 30.1752
NQ | 20003734 | CLSO-HOHI-1 | CLARESOUTH-HOMEHILL NO.01 | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Limiting Line Name | TR_LINE 35632_1 | TR_LINE 35632_1 | TR_LINE 35632_1 | TR_LINE 35632_1 | TR_LINE 35632_1 | TR_LINE 35632_1 | TR_LINE 35632_1 | TR_LINE 35632_1 | TR_LINE 35632_1 | TR_LINE 35632_1 | TR_LINE 35632_1 | TR_LINE 35632_1 | TR_LINE 35632_1 | TR_LINE 35632_1 | TR_LINE 35632_1
NQ | 20003734 | CLSO-HOHI-1 | CLARESOUTH-HOMEHILL NO.01 | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Loading (A) | 104.7249 | 113.8786 | 102.9283 | 103.589 | 111.1075 | 100.9614 | 103.1636 | 110.6036 | 101.9329 | 103.456 | 110.926 | 102.2362 | 104.2959 | 111.8611 | 101.6655
NQ | 20003734 | CLSO-HOHI-1 | CLARESOUTH-HOMEHILL NO.01 | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Loading (MVA) | 12.0721 | 13.0709 | 11.8619 | 11.7983 | 12.7688 | 11.6456 | 11.753 | 12.7154 | 11.6085 | 11.7854 | 12.7512 | 11.642 | 11.876 | 12.8527 | 11.7234
NQ | 20003734 | CLSO-HOHI-1 | CLARESOUTH-HOMEHILL NO.01 | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Loading (MW) | 11.7979 | 12.7108 | 11.5613 | 11.5393 | 12.4334 | 11.3615 | 11.4967 | 12.3838 | 11.321 | 11.5282 | 12.418 | 11.3529 | 11.6132 | 12.5125 | 11.4349
NQ | 20003734 | CLSO-HOHI-1 | CLARESOUTH-HOMEHILL NO.01 | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Power Factor | 0.97729 | 0.97245 | 0.97466 | 0.97804 | 0.97373 | 0.9756 | 0.97819 | 0.97392 | 0.97523 | 0.97818 | 0.97387 | 0.97517 | 0.97787 | 0.97353 | 0.97539
NQ | 20003734 | CLSO-HOHI-1 | CLARESOUTH-HOMEHILL NO.01 | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Rating (A) | 312 | 363 | 337 | 312 | 363 | 337 | 312 | 363 | 337 | 312 | 363 | 337 | 312 | 363 | 337
NQ | 20003734 | CLSO-HOHI-1 | CLARESOUTH-HOMEHILL NO.01 | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Time | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00
NQ | 20003734 | CLSO-HOHI-1 | CLARESOUTH-HOMEHILL NO.01 | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Voltage at Constrained Conductor | 66.5535 | 66.2678 | 66.5364 | 65.7577 | 66.351 | 66.5956 | 65.7752 | 66.3743 | 65.7511 | 65.7701 | 66.3677 | 65.7449 | 65.742 | 66.3366 | 66.5764
NQ | 20003735 | CLSO-HOHI-2 | CLARESOUTH-HOMEHILL NO.02 | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | % of Rated A | 59.4138 | 45.6876 | 42.3484 | 58.7712 | 44.5746 | 41.5382 | 58.5295 | 44.3722 | 41.9401 | 58.6959 | 44.5018 | 42.0651 | 59.173 | 44.8775 | 41.8285
NQ | 20003735 | CLSO-HOHI-2 | CLARESOUTH-HOMEHILL NO.02 | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Limiting Line Name | TR_LINE 147761_1 | TR_LINE 147761_1 | TR_LINE 147761_1 | TR_LINE 147761_1 | TR_LINE 147761_1 | TR_LINE 147761_1 | TR_LINE 147761_1 | TR_LINE 147761_1 | TR_LINE 147761_1 | TR_LINE 147761_1 | TR_LINE 147761_1 | TR_LINE 147761_1 | TR_LINE 147761_1 | TR_LINE 147761_1 | TR_LINE 147761_1
NQ | 20003735 | CLSO-HOHI-2 | CLARESOUTH-HOMEHILL NO.02 | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Loading (A) | 100.3098 | 109.0796 | 98.5651 | 99.2273 | 106.4232 | 96.6801 | 98.8194 | 105.9399 | 97.6164 | 99.1004 | 106.2495 | 97.9077 | 99.9058 | 107.1465 | 97.3558
NQ | 20003735 | CLSO-HOHI-2 | CLARESOUTH-HOMEHILL NO.02 | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Loading (MVA) | 11.6814 | 12.6639 | 11.475 | 11.4168 | 12.3665 | 11.2627 | 11.3723 | 12.3138 | 11.2303 | 11.4041 | 12.349 | 11.2632 | 11.4931 | 12.4489 | 11.3391
NQ | 20003735 | CLSO-HOHI-2 | CLARESOUTH-HOMEHILL NO.02 | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Loading (MW) | 11.5393 | 12.4591 | 11.3141 | 11.2842 | 12.18 | 11.1136 | 11.2416 | 12.1302 | 11.0775 | 11.2727 | 12.1643 | 11.1092 | 11.3577 | 12.259 | 11.1868
NQ | 20003735 | CLSO-HOHI-2 | CLARESOUTH-HOMEHILL NO.02 | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Power Factor | 0.98784 | 0.98383 | 0.98598 | 0.98838 | 0.98492 | 0.98676 | 0.98851 | 0.98508 | 0.98639 | 0.98848 | 0.98504 | 0.98633 | 0.98822 | 0.98474 | 0.98658
NQ | 20003735 | CLSO-HOHI-2 | CLARESOUTH-HOMEHILL NO.02 | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Rating (A) | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233
NQ | 20003735 | CLSO-HOHI-2 | CLARESOUTH-HOMEHILL NO.02 | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Time | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00
NQ | 20003735 | CLSO-HOHI-2 | CLARESOUTH-HOMEHILL NO.02 | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Voltage at Constrained Conductor | 67.2344 | 67.0293 | 67.2154 | 66.4283 | 67.0887 | 67.258 | 66.4423 | 67.1078 | 66.4215 | 66.4392 | 67.1036 | 66.4176 | 66.4179 | 67.0801 | 67.2443
NQ | 20003736 | CS-ML-1 | CLARESOUTH-MILLAROO | CS-ML-1_Clare South - Millaroo 66 kV | % of Rated A | 44.8425 | 40.6023 | 43.7954 | 44.2977 | 39.9269 | 42.9186 | 43.8022 | 39.483 | 42.9986 | 43.3135 | 39.0433 | 42.5143 | 43.822 | 39.5015 | 42.4586
NQ | 20003736 | CS-ML-1 | CLARESOUTH-MILLAROO | CS-ML-1_Clare South - Millaroo 66 kV | Limiting Line Name | TR_LINE 128012_1 | TR_LINE 128012_1 | TR_LINE 128012_1 | TR_LINE 128012_1 | TR_LINE 128012_1 | TR_LINE 128012_1 | TR_LINE 128012_1 | TR_LINE 128012_1 | TR_LINE 128012_1 | TR_LINE 128012_1 | TR_LINE 128012_1 | TR_LINE 128012_1 | TR_LINE 128012_1 | TR_LINE 128012_1 | TR_LINE 128012_1
NQ | 20003736 | CS-ML-1 | CLARESOUTH-MILLAROO | CS-ML-1_Clare South - Millaroo 66 kV | Loading (A) | 87.4381 | 88.5083 | 87.148 | 86.3759 | 87.0359 | 85.4032 | 85.4096 | 86.0683 | 85.5625 | 84.4566 | 85.1097 | 84.5987 | 85.4482 | 86.1086 | 84.4879
NQ | 20003736 | CS-ML-1 | CLARESOUTH-MILLAROO | CS-ML-1_Clare South - Millaroo 66 kV | Loading (MVA) | 10.087 | 10.2031 | 10.1709 | 9.9629 | 10.0377 | 9.9724 | 9.8544 | 9.9293 | 9.8688 | 9.7461 | 9.8204 | 9.7594 | 9.8573 | 9.9323 | 9.8663
NQ | 20003736 | CS-ML-1 | CLARESOUTH-MILLAROO | CS-ML-1_Clare South - Millaroo 66 kV | Loading (MW) | 8.4603 | 8.5514 | 8.5285 | 8.3542 | 8.4154 | 8.3592 | 8.2697 | 8.3306 | 8.2748 | 8.1853 | 8.2457 | 8.1896 | 8.2501 | 8.3107 | 8.2551
NQ | 20003736 | CS-ML-1 | CLARESOUTH-MILLAROO | CS-ML-1_Clare South - Millaroo 66 kV | Power Factor | 0.83873 | 0.83811 | 0.83852 | 0.83853 | 0.83838 | 0.83824 | 0.8392 | 0.83899 | 0.83848 | 0.83986 | 0.83965 | 0.83915 | 0.83696 | 0.83673 | 0.83669
NQ | 20003736 | CS-ML-1 | CLARESOUTH-MILLAROO | CS-ML-1_Clare South - Millaroo 66 kV | Rating (A) | 195 | 218 | 199 | 195 | 218 | 199 | 195 | 218 | 199 | 195 | 218 | 199 | 195 | 218 | 199
NQ | 20003736 | CS-ML-1 | CLARESOUTH-MILLAROO | CS-ML-1_Clare South - Millaroo 66 kV | Time | 16:00 | 17:00 | 22:00 | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00
NQ | 20003736 | CS-ML-1 | CLARESOUTH-MILLAROO | CS-ML-1_Clare South - Millaroo 66 kV | Voltage at Constrained Conductor | 66.6039 | 66.5562 | 67.3818 | 66.5938 | 66.5847 | 67.4161 | 66.6133 | 66.6064 | 66.5921 | 66.625 | 66.6179 | 66.6035 | 66.603 | 66.5953 | 67.4219
NQ | 20003737 | MOPA | CLARESOUTH-MONAPARK | MOPA_Clare South - Mona Park 66 kV | % of Rated A | 76.3523 | 54.8393 | 51.5677 | 76.5833 | 54.2327 | 51.1071 | 76.38 | 54.0662 | 51.6689 | 76.5666 | 54.2047 | 51.8032 | 77.335 | 54.7594 | 51.5979
NQ | 20003737 | MOPA | CLARESOUTH-MONAPARK | MOPA_Clare South - Mona Park 66 kV | Limiting Line Name | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1
NQ | 20003737 | MOPA | CLARESOUTH-MONAPARK | MOPA_Clare South - Mona Park 66 kV | Loading (A) | 160.3377 | 172.7415 | 159.8577 | 160.8228 | 170.831 | 158.4299 | 160.3959 | 170.3063 | 160.1714 | 160.7878 | 170.7426 | 160.5877 | 162.4015 | 172.49 | 159.9512
NQ | 20003737 | MOPA | CLARESOUTH-MONAPARK | MOPA_Clare South - Mona Park 66 kV | Loading (MVA) | 18.9987 | 20.4481 | 18.9346 | 18.8269 | 20.2275 | 18.7694 | 18.7792 | 20.1689 | 18.7476 | 18.8252 | 20.2206 | 18.7963 | 19.0115 | 20.4244 | 18.9484
NQ | 20003737 | MOPA | CLARESOUTH-MONAPARK | MOPA_Clare South - Mona Park 66 kV | Loading (MW) | 18.0427 | 19.3031 | 17.909 | 17.8727 | 19.1079 | 17.7614 | 17.8232 | 19.0476 | 17.7181 | 17.8663 | 19.0949 | 17.7625 | 18.031 | 19.2738 | 17.9131
NQ | 20003737 | MOPA | CLARESOUTH-MONAPARK | MOPA_Clare South - Mona Park 66 kV | Power Factor | 0.94968 | 0.944 | 0.94583 | 0.94931 | 0.94465 | 0.94629 | 0.94909 | 0.9444 | 0.94509 | 0.94906 | 0.94433 | 0.945 | 0.94843 | 0.94366 | 0.94536
NQ | 20003737 | MOPA | CLARESOUTH-MONAPARK | MOPA_Clare South - Mona Park 66 kV | Rating (A) | 210 | 315 | 310 | 210 | 315 | 310 | 210 | 315 | 310 | 210 | 315 | 310 | 210 | 315 | 310
NQ | 20003737 | MOPA | CLARESOUTH-MONAPARK | MOPA_Clare South - Mona Park 66 kV | Time | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00
NQ | 20003737 | MOPA | CLARESOUTH-MONAPARK | MOPA_Clare South - Mona Park 66 kV | Voltage at Constrained Conductor | 68.4114 | 68.3433 | 68.3852 | 67.5883 | 68.362 | 68.3994 | 67.5965 | 68.3741 | 67.5772 | 67.5969 | 68.374 | 67.5772 | 67.5873 | 68.3637 | 68.3952
NQ | 20004005 | CR-HU-1 | CAPERIVER-HUGHENDEN NO.01 | CR-HU-1_Cape River-Hughenden No 1 66 kV | % of Rated A | 29.226 | 19.9984 | 18.0435 | 28.8742 | 19.7916 | 18.063 | 31.7992 | 22.192 | 18.9997 | 31.7941 | 22.1899 | 19.0038 | 31.87 | 22.227 | 19.1372
NQ | 20004005 | CR-HU-1 | CAPERIVER-HUGHENDEN NO.01 | CR-HU-1_Cape River-Hughenden No 1 66 kV | Limiting Line Name | TR_LINE 53284_2 | TR_LINE 53284_2 | TR_LINE 53284_2 | TR_LINE 53284_2 | TR_LINE 53284_2 | TR_LINE 53284_2 | TR_LINE 53284_2 | TR_LINE 53284_2 | TR_LINE 53284_2 | TR_LINE 53284_2 | TR_LINE 53284_2 | TR_LINE 53284_2 | TR_LINE 53284_2 | TR_LINE 53284_2 | TR_LINE 53284_2
NQ | 20004005 | CR-HU-1 | CAPERIVER-HUGHENDEN NO.01 | CR-HU-1_Cape River-Hughenden No 1 66 kV | Loading (A) | 41.7932 | 42.3966 | 37.7109 | 41.2901 | 41.9582 | 37.7516 | 45.4728 | 47.047 | 39.7094 | 45.4656 | 47.0425 | 39.7179 | 45.5741 | 47.1212 | 39.9967
NQ | 20004005 | CR-HU-1 | CAPERIVER-HUGHENDEN NO.01 | CR-HU-1_Cape River-Hughenden No 1 66 kV | Loading (MVA) | 4.7555 | 4.821 | 4.3102 | 4.7017 | 4.7724 | 4.3107 | 5.1646 | 5.3384 | 4.5353 | 5.1636 | 5.3377 | 4.536 | 5.1746 | 5.3452 | 4.565
NQ | 20004005 | CR-HU-1 | CAPERIVER-HUGHENDEN NO.01 | CR-HU-1_Cape River-Hughenden No 1 66 kV | Loading (MW) | 3.0478 | 3.1354 | 2.5047 | 2.9908 | 3.0664 | 2.4604 | 3.6435 | 3.9116 | 2.8473 | 3.6422 | 3.9103 | 2.8461 | 3.6804 | 3.9483 | 2.8861
NQ | 20004005 | CR-HU-1 | CAPERIVER-HUGHENDEN NO.01 | CR-HU-1_Cape River-Hughenden No 1 66 kV | Power Factor | 0.64089 | 0.65036 | 0.58109 | 0.63611 | 0.64253 | 0.57076 | 0.70549 | 0.73273 | 0.62779 | 0.70537 | 0.73259 | 0.62746 | 0.71123 | 0.73865 | 0.63222
NQ | 20004005 | CR-HU-1 | CAPERIVER-HUGHENDEN NO.01 | CR-HU-1_Cape River-Hughenden No 1 66 kV | Rating (A) | 143 | 212 | 209 | 143 | 212 | 209 | 143 | 212 | 209 | 143 | 212 | 209 | 143 | 212 | 209
NQ | 20004005 | CR-HU-1 | CAPERIVER-HUGHENDEN NO.01 | CR-HU-1_Cape River-Hughenden No 1 66 kV | Time | 15:30 | 18:30 | 8:30 | 15:30 | 18:30 | 8:30 | 15:30 | 18:30 | 8:30 | 15:30 | 18:30 | 8:30 | 15:30 | 18:30 | 8:30
NQ | 20004005 | CR-HU-1 | CAPERIVER-HUGHENDEN NO.01 | CR-HU-1_Cape River-Hughenden No 1 66 kV | Voltage at Constrained Conductor | 65.6952 | 65.6514 | 65.9894 | 65.7431 | 65.6686 | 65.9256 | 65.5726 | 65.5122 | 65.9411 | 65.5702 | 65.5095 | 65.936 | 65.5544 | 65.4923 | 65.8951
NQ | 20004647 | CT-CR-1 | CHARTERSTOWERS-CAPERIVER | CT-CR-1_Charters Towers-CARI No 1 66 kV | % of Rated A | 27.7887 | 26.611 | 23.8878 | 27.2746 | 26.0358 | 23.8972 | 32.7538 | 32.4438 | 26.0926 | 32.7742 | 32.4692 | 26.1003 | 33.1707 | 32.8536 | 26.4672
NQ | 20004647 | CT-CR-1 | CHARTERSTOWERS-CAPERIVER | CT-CR-1_Charters Towers-CARI No 1 66 kV | Limiting Line Name | TR_LINE 31871_1 | TR_LINE 31871_1 | TR_LINE 31871_1 | TR_LINE 31871_1 | TR_LINE 31871_1 | TR_LINE 31871_1 | TR_LINE 31871_1 | TR_LINE 31871_1 | TR_LINE 31871_1 | TR_LINE 31871_1 | TR_LINE 31871_1 | TR_LINE 31871_1 | TR_LINE 31871_1 | TR_LINE 31871_1 | TR_LINE 31871_1
NQ | 20004647 | CT-CR-1 | CHARTERSTOWERS-CAPERIVER | CT-CR-1_Charters Towers-CARI No 1 66 kV | Loading (A) | 51.1312 | 53.2221 | 42.9981 | 50.1853 | 52.0715 | 43.0149 | 60.267 | 64.8876 | 46.9667 | 60.3046 | 64.9385 | 46.9805 | 61.0342 | 65.7073 | 47.6409
NQ | 20004647 | CT-CR-1 | CHARTERSTOWERS-CAPERIVER | CT-CR-1_Charters Towers-CARI No 1 66 kV | Loading (MVA) | 5.9556 | 6.1936 | 5.0164 | 5.8486 | 6.0622 | 5.006 | 7.0199 | 7.5535 | 5.492 | 7.023 | 7.5577 | 5.4928 | 7.1047 | 7.6432 | 5.5673
NQ | 20004647 | CT-CR-1 | CHARTERSTOWERS-CAPERIVER | CT-CR-1_Charters Towers-CARI No 1 66 kV | Loading (MW) | 4.9795 | 5.1548 | 4.1702 | 4.8929 | 5.0616 | 4.1015 | 5.857 | 6.2798 | 4.6417 | 5.8532 | 6.2757 | 4.6393 | 5.9068 | 6.3314 | 4.6998
NQ | 20004647 | CT-CR-1 | CHARTERSTOWERS-CAPERIVER | CT-CR-1_Charters Towers-CARI No 1 66 kV | Power Factor | 0.83611 | 0.83228 | 0.8313 | 0.83658 | 0.83495 | 0.81932 | 0.83434 | 0.83137 | 0.84517 | 0.83344 | 0.83038 | 0.84462 | 0.83139 | 0.82836 | 0.84419
NQ | 20004647 | CT-CR-1 | CHARTERSTOWERS-CAPERIVER | CT-CR-1_Charters Towers-CARI No 1 66 kV | Rating (A) | 184 | 200 | 180 | 184 | 200 | 180 | 184 | 200 | 180 | 184 | 200 | 180 | 184 | 200 | 180
NQ | 20004647 | CT-CR-1 | CHARTERSTOWERS-CAPERIVER | CT-CR-1_Charters Towers-CARI No 1 66 kV | Time | 15:30 | 19:00 | 8:30 | 15:30 | 19:00 | 8:30 | 15:30 | 19:00 | 8:30 | 15:30 | 19:00 | 8:30 | 15:30 | 19:00 | 8:30
NQ | 20004647 | CT-CR-1 | CHARTERSTOWERS-CAPERIVER | CT-CR-1_Charters Towers-CARI No 1 66 kV | Voltage at Constrained Conductor | 67.2478 | 67.188 | 67.3575 | 67.2848 | 67.215 | 67.1905 | 67.2501 | 67.2084 | 67.5116 | 67.2372 | 67.1931 | 67.5013 | 67.2064 | 67.1586 | 67.4686
NQ | 20004649 | CT-MR-1 | MILLCHESTER-CHARTERSTOWERS | CT-MR-1_Millchester-CHTO No 1 66 kV | % of Rated A | 38.2341 | 35.4548 | 30.2705 | 38.7048 | 35.8694 | 30.1378 | 38.2456 | 35.49 | 34.5085 | 38.4122 | 35.6386 | 34.6414 | 38.5699 | 35.811 | 31.4857
NQ | 20004649 | CT-MR-1 | MILLCHESTER-CHARTERSTOWERS | CT-MR-1_Millchester-CHTO No 1 66 kV | Limiting Line Name | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1
NQ | 20004649 | CT-MR-1 | MILLCHESTER-CHARTERSTOWERS | CT-MR-1_Millchester-CHTO No 1 66 kV | Loading (A) | 106.285 | 110.2586 | 85.963 | 107.5936 | 111.5482 | 85.5862 | 106.3168 | 110.3682 | 97.9982 | 106.78 | 110.8304 | 98.3756 | 107.2187 | 111.3664 | 89.4138
NQ | 20004649 | CT-MR-1 | MILLCHESTER-CHARTERSTOWERS | CT-MR-1_Millchester-CHTO No 1 66 kV | Loading (MVA) | 12.3832 | 12.8466 | 10.0247 | 12.5362 | 12.9933 | 9.9852 | 12.3789 | 12.8528 | 11.4498 | 12.4307 | 12.9038 | 11.4921 | 12.476 | 12.9601 | 10.4497
NQ | 20004649 | CT-MR-1 | MILLCHESTER-CHARTERSTOWERS | CT-MR-1_Millchester-CHTO No 1 66 kV | Loading (MW) | 10.2252 | 10.6662 | 8.6098 | 10.3587 | 10.8117 | 8.5551 | 10.2069 | 10.6825 | 9.3137 | 10.2658 | 10.7428 | 9.3639 | 10.3179 | 10.806 | 8.738
NQ | 20004649 | CT-MR-1 | MILLCHESTER-CHARTERSTOWERS | CT-MR-1_Millchester-CHTO No 1 66 kV | Power Factor | 0.82574 | 0.83028 | 0.85886 | 0.8263 | 0.8321 | 0.85678 | 0.82453 | 0.83114 | 0.81344 | 0.82584 | 0.83253 | 0.81481 | 0.82702 | 0.83379 | 0.8362
NQ | 20004649 | CT-MR-1 | MILLCHESTER-CHARTERSTOWERS | CT-MR-1_Millchester-CHTO No 1 66 kV | Rating (A) | 278 | 311 | 284 | 278 | 311 | 284 | 278 | 311 | 284 | 278 | 311 | 284 | 278 | 311 | 284
NQ | 20004649 | CT-MR-1 | MILLCHESTER-CHARTERSTOWERS | CT-MR-1_Millchester-CHTO No 1 66 kV | Time | 16:00 | 17:00 | 22:00 | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 8:30
NQ | 20004649 | CT-MR-1 | MILLCHESTER-CHARTERSTOWERS | CT-MR-1_Millchester-CHTO No 1 66 kV | Voltage at Constrained Conductor | 67.2665 | 67.2688 | 67.3286 | 67.2696 | 67.2507 | 67.3587 | 67.2234 | 67.2345 | 67.456 | 67.2117 | 67.2201 | 67.4453 | 67.1806 | 67.1881 | 67.4746
NQ | 20006056 | GA-BO-1 | GARBUTT-BOHLE | GA-BO-1_Garbutt-Bohle No 1 66 kV | % of Rated A | 38.1766 | 46.8173 | 39.0167 | 38.3584 | 47.0307 | 39.1883 | 36.8705 | 46.8084 | 38.9295 | 37.5116 | 47.6128 | 39.5731 | 38.148 | 48.4579 | 40.2276
NQ | 20006056 | GA-BO-1 | GARBUTT-BOHLE | GA-BO-1_Garbutt-Bohle No 1 66 kV | Limiting Line Name | TR_LINE 32140_1 | TR_LINE 32140_1 | TR_LINE 32140_1 | TR_LINE 32140_1 | TR_LINE 32140_1 | TR_LINE 32140_1 | TR_LINE 128084_1 | TR_LINE 32140_1 | TR_LINE 32140_1 | TR_LINE 51442_1 | TR_LINE 32140_1 | TR_LINE 32140_1 | TR_LINE 60082_1 | TR_LINE 32140_1 | TR_LINE 32140_1
NQ | 20006056 | GA-BO-1 | GARBUTT-BOHLE | GA-BO-1_Garbutt-Bohle No 1 66 kV | Loading (A) | 210.3524 | 272.4763 | 204.4466 | 211.3541 | 273.7185 | 205.3461 | 203.1563 | 272.4247 | 203.9905 | 206.6888 | 277.1061 | 207.3632 | 210.1955 | 282.025 | 210.7923
NQ | 20006056 | GA-BO-1 | GARBUTT-BOHLE | GA-BO-1_Garbutt-Bohle No 1 66 kV | Loading (MVA) | 24.6893 | 31.9773 | 24.178 | 24.8074 | 32.1248 | 24.2856 | 24.2151 | 32.1239 | 23.9218 | 24.6036 | 32.6587 | 24.309 | 24.9631 | 33.2097 | 24.6966
NQ | 20006056 | GA-BO-1 | GARBUTT-BOHLE | GA-BO-1_Garbutt-Bohle No 1 66 kV | Loading (MW) | 24.3685 | 31.7949 | 23.837 | 24.4786 | 31.936 | 23.9389 | 24.2151 | 32.085 | 23.9177 | 24.6036 | 32.6123 | 24.3032 | 24.963 | 33.1548 | 24.6887
NQ | 20006056 | GA-BO-1 | GARBUTT-BOHLE | GA-BO-1_Garbutt-Bohle No 1 66 kV | Power Factor | 0.98701 | 0.9943 | 0.9859 | 0.98675 | 0.99412 | 0.98572 | 1 | 0.99879 | 0.99983 | 1 | 0.99858 | 0.99976 | 1 | 0.99835 | 0.99968
NQ | 20006056 | GA-BO-1 | GARBUTT-BOHLE | GA-BO-1_Garbutt-Bohle No 1 66 kV | Rating (A) | 551 | 582 | 524 | 551 | 582 | 524 | 551 | 582 | 524 | 551 | 582 | 524 | 551 | 582 | 524
NQ | 20006056 | GA-BO-1 | GARBUTT-BOHLE | GA-BO-1_Garbutt-Bohle No 1 66 kV | Time | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00
NQ | 20006056 | GA-BO-1 | GARBUTT-BOHLE | GA-BO-1_Garbutt-Bohle No 1 66 kV | Voltage at Constrained Conductor | 67.7641 | 67.7567 | 68.278 | 67.7657 | 67.7604 | 68.2813 | 68.8169 | 68.0803 | 67.7053 | 68.7261 | 68.0443 | 67.6823 | 68.5668 | 67.9855 | 67.6427
NQ | 20006058 | GA-HP-1 | GARBUTT-HERMITPARK | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | % of Rated A | 33.8941 | 33.2268 | 31.6659 | 33.8611 | 33.2423 | 31.6924 | 32.381 | 31.6213 | 18.2673 | 32.5446 | 31.7751 | 18.4006 | 32.7768 | 32.0391 | 18.5657
NQ | 20006058 | GA-HP-1 | GARBUTT-HERMITPARK | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Limiting Line Name | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1
NQ | 20006058 | GA-HP-1 | GARBUTT-HERMITPARK | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Loading (A) | 116.899 | 119.2494 | 101.2929 | 116.7852 | 119.3049 | 101.3777 | 111.6777 | 113.4841 | 58.4554 | 112.2422 | 114.0364 | 58.882 | 113.0432 | 114.984 | 59.4103
NQ | 20006058 | GA-HP-1 | GARBUTT-HERMITPARK | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Loading (MVA) | 13.832 | 14.1022 | 12.0795 | 13.8199 | 14.111 | 12.0913 | 13.2951 | 13.5033 | 6.8981 | 13.3598 | 13.5661 | 6.9477 | 13.4482 | 13.672 | 7.0075
NQ | 20006058 | GA-HP-1 | GARBUTT-HERMITPARK | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Loading (MW) | 6.0638 | 6.5574 | 3.7236 | 6.0572 | 6.5319 | 3.7335 | 4.9935 | 5.3948 | 1.4339 | 5.0816 | 5.4794 | 1.5235 | 5.207 | 5.613 | 1.6292
NQ | 20006058 | GA-HP-1 | GARBUTT-HERMITPARK | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Power Factor | 0.43839 | 0.46499 | 0.30826 | 0.4383 | 0.4629 | 0.30878 | 0.37559 | 0.39952 | 0.20787 | 0.38037 | 0.4039 | 0.21928 | 0.38719 | 0.41055 | 0.23249
NQ | 20006058 | GA-HP-1 | GARBUTT-HERMITPARK | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Rating (A) | 345 | 359 | 320 | 345 | 359 | 320 | 345 | 359 | 320 | 345 | 359 | 320 | 345 | 359 | 320
NQ | 20006058 | GA-HP-1 | GARBUTT-HERMITPARK | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Time | 16:30 | 17:00 | 8:30 | 16:30 | 17:00 | 8:30 | 16:30 | 17:00 | 8:30 | 16:30 | 17:00 | 8:30 | 16:30 | 17:00 | 8:30
NQ | 20006058 | GA-HP-1 | GARBUTT-HERMITPARK | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Voltage at Constrained Conductor | 68.3145 | 68.2763 | 68.8508 | 68.3211 | 68.287 | 68.8603 | 68.733 | 68.6979 | 68.1305 | 68.7199 | 68.6831 | 68.1236 | 68.6845 | 68.6488 | 68.0992
NQ | 20006059 | GA-NS-1 | GARBUTT-NEILSMITH | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | % of Rated A | 38.9681 | 21.2551 | 24.3669 | 38.46 | 20.9803 | 24.0513 | 38.8859 | 20.856 | 24.3166 | 39.143 | 20.9953 | 24.4767 | 39.6635 | 21.2756 | 24.8014
NQ | 20006059 | GA-NS-1 | GARBUTT-NEILSMITH | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Limiting Line Name | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1
NQ | 20006059 | GA-NS-1 | GARBUTT-NEILSMITH | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Loading (A) | 65.8558 | 50.7997 | 56.7747 | 64.9972 | 50.1428 | 56.0393 | 65.7169 | 49.8459 | 56.6574 | 66.1513 | 50.1787 | 57.0306 | 67.031 | 50.8485 | 57.787
NQ | 20006059 | GA-NS-1 | GARBUTT-NEILSMITH | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Loading (MVA) | 7.8529 | 6.0135 | 6.7754 | 7.7518 | 5.9367 | 6.6886 | 7.7528 | 5.9366 | 6.689 | 7.8033 | 5.9749 | 6.7324 | 7.9044 | 6.0517 | 6.8193
NQ | 20006059 | GA-NS-1 | GARBUTT-NEILSMITH | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Loading (MW) | 7.8425 | 6.0131 | 6.7726 | 7.7423 | 5.9365 | 6.6863 | 7.7424 | 5.9364 | 6.6862 | 7.7924 | 5.9747 | 6.7294 | 7.8926 | 6.0514 | 6.8158
NQ | 20006059 | GA-NS-1 | GARBUTT-NEILSMITH | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Power Factor | 0.99868 | 0.99994 | 0.9996 | 0.99878 | 0.99996 | 0.99965 | 0.99866 | 0.99998 | 0.99958 | 0.9986 | 0.99997 | 0.99955 | 0.9985 | 0.99994 | 0.99948
NQ | 20006059 | GA-NS-1 | GARBUTT-NEILSMITH | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Rating (A) | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233
NQ | 20006059 | GA-NS-1 | GARBUTT-NEILSMITH | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Time | 13:00 | 17:00 | 8:30 | 13:00 | 17:00 | 8:30 | 13:00 | 17:00 | 8:30 | 13:00 | 17:00 | 8:30 | 13:00 | 17:00 | 8:30
NQ | 20006059 | GA-NS-1 | GARBUTT-NEILSMITH | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Voltage at Constrained Conductor | 68.8451 | 68.3448 | 68.8997 | 68.8572 | 68.3559 | 68.9097 | 68.1114 | 68.7617 | 68.1623 | 68.1051 | 68.7471 | 68.1558 | 68.0823 | 68.7133 | 68.1319
NQ | 20006060 | GA-TP-1 | GARBUTT-TOWNSVILLEPORT | GA-TP-1_Garbutt-Townsville Port 1 66 kV | % of Rated A | 82.3329 | 77.1914 | 69.8666 | 80.2664 | 75.6692 | 68.5722 | 79.2724 | 74.8456 | 66.3872 | 79.6179 | 75.2621 | 66.7516 | 79.9956 | 75.7404 | 67.1046
NQ | 20006060 | GA-TP-1 | GARBUTT-TOWNSVILLEPORT | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Limiting Line Name | TR_LINE 161962_1 | TR_LINE 161962_1 | TR_LINE 161962_1 | TR_LINE 161962_1 | TR_LINE 161962_1 | TR_LINE 161962_1 | TR_LINE 161962_1 | TR_LINE 161962_1 | TR_LINE 161962_1 | TR_LINE 161962_1 | TR_LINE 161962_1 | TR_LINE 161962_1 | TR_LINE 161962_1 | TR_LINE 161962_1 | TR_LINE 161962_1
NQ | 20006060 | GA-TP-1 | GARBUTT-TOWNSVILLEPORT | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Loading (A) | 212.4188 | 227.7147 | 190.0372 | 207.0873 | 223.2242 | 186.5164 | 204.5228 | 220.7944 | 180.5731 | 205.4141 | 222.0232 | 181.5644 | 206.3887 | 223.434 | 182.5246
NQ | 20006060 | GA-TP-1 | GARBUTT-TOWNSVILLEPORT | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Loading (MVA) | 25.2709 | 27.1404 | 22.7378 | 24.6316 | 26.6021 | 22.3143 | 24.4457 | 26.3865 | 21.4451 | 24.5491 | 26.5286 | 21.5604 | 24.6552 | 26.6849 | 21.6671
NQ | 20006060 | GA-TP-1 | GARBUTT-TOWNSVILLEPORT | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Loading (MW) | 23.9223 | 25.7054 | 20.8236 | 23.2092 | 25.1013 | 20.3276 | 22.4428 | 24.6554 | 21.2379 | 22.5647 | 24.8239 | 21.357 | 22.7072 | 25.0227 | 21.4697
NQ | 20006060 | GA-TP-1 | GARBUTT-TOWNSVILLEPORT | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Power Factor | 0.94663 | 0.94712 | 0.91582 | 0.94225 | 0.94358 | 0.91097 | 0.91807 | 0.93439 | 0.99034 | 0.91917 | 0.93574 | 0.99057 | 0.92099 | 0.93771 | 0.99089
NQ | 20006060 | GA-TP-1 | GARBUTT-TOWNSVILLEPORT | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Rating (A) | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272
NQ | 20006060 | GA-TP-1 | GARBUTT-TOWNSVILLEPORT | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Time | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00
NQ | 20006060 | GA-TP-1 | GARBUTT-TOWNSVILLEPORT | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Voltage at Constrained Conductor | 68.6859 | 68.8122 | 69.0794 | 68.6719 | 68.8041 | 69.0724 | 69.0082 | 68.9975 | 68.5668 | 68.9993 | 68.9852 | 68.5591 | 68.9704 | 68.9534 | 68.536
NQ | 20007825 | HU-WI-1 | HUGHENDEN-WINTON | HU-WI-1 Hughenden-Winton No 1 66 kV | % of Rated A | 13.8427 | 12.9244 | 11.7015 | 13.6006 | 12.6817 | 11.5653 | 13.6329 | 12.7244 | 11.5509 | 13.6158 | 12.7094 | 11.5389 | 13.6184 | 12.7132 | 11.5352
NQ | 20007825 | HU-WI-1 | HUGHENDEN-WINTON | HU-WI-1 Hughenden-Winton No 1 66 kV | Limiting Line Name | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2
NQ | 20007825 | HU-WI-1 | HUGHENDEN-WINTON | HU-WI-1 Hughenden-Winton No 1 66 kV | Loading (A) | 36.2678 | 37.6099 | 30.8921 | 35.6335 | 36.9037 | 30.5324 | 35.7183 | 37.0281 | 30.4944 | 35.6735 | 36.9844 | 30.4627 | 35.6802 | 36.9954 | 30.453
NQ | 20007825 | HU-WI-1 | HUGHENDEN-WINTON | HU-WI-1 Hughenden-Winton No 1 66 kV | Loading (MVA) | 4.2045 | 4.3432 | 3.5958 | 4.1321 | 4.2633 | 3.556 | 4.1041 | 4.2362 | 3.5294 | 4.0988 | 4.231 | 3.5256 | 4.0965 | 4.2285 | 3.519
NQ | 20007825 | HU-WI-1 | HUGHENDEN-WINTON | HU-WI-1 Hughenden-Winton No 1 66 kV | Loading (MW) | 3.6628 | 3.8714 | 2.6601 | 3.5618 | 3.7642 | 2.5865 | 3.5632 | 3.766 | 2.5866 | 3.5606 | 3.7633 | 2.585 | 3.5607 | 3.7635 | 2.5851
NQ | 20007825 | HU-WI-1 | HUGHENDEN-WINTON | HU-WI-1 Hughenden-Winton No 1 66 kV | Power Factor | 0.87117 | 0.89136 | 0.73976 | 0.862 | 0.88295 | 0.72734 | 0.86821 | 0.889 | 0.73287 | 0.86869 | 0.88946 | 0.73321 | 0.86922 | 0.89003 | 0.73461
NQ | 20007825 | HU-WI-1 | HUGHENDEN-WINTON | HU-WI-1 Hughenden-Winton No 1 66 kV | Rating (A) | 262 | 291 | 264 | 262 | 291 | 264 | 262 | 291 | 264 | 262 | 291 | 264 | 262 | 291 | 264
NQ | 20007825 | HU-WI-1 | HUGHENDEN-WINTON | HU-WI-1 Hughenden-Winton No 1 66 kV | Time | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00
NQ | 20007825 | HU-WI-1 | HUGHENDEN-WINTON | HU-WI-1 Hughenden-Winton No 1 66 kV | Voltage at Constrained Conductor | 66.9312 | 66.6726 | 67.2037 | 66.9499 | 66.6978 | 67.2426 | 66.3382 | 66.0511 | 66.8228 | 66.3367 | 66.0494 | 66.8203 | 66.2858 | 65.9901 | 66.7158
NQ | 20007826 | HU-RI-1 | HUGHENDEN-RICHMOND | HU-RI-1_Hughenden-Richmond No 1 66 kV | % of Rated A | 15.661 | 13.6831 | 11.8669 | 15.4539 | 13.4705 | 11.7642 | 21.3627 | 19.2475 | 15.1666 | 21.3631 | 19.248 | 15.1669 | 21.4986 | 19.4228 | 15.2246
NQ | 20007826 | HU-RI-1 | HUGHENDEN-RICHMOND | HU-RI-1_Hughenden-Richmond No 1 66 kV | Limiting Line Name | TR_LINE 163222_1 | TR_LINE 163213_1 | TR_LINE 163213_1 | TR_LINE 163222_1 | TR_LINE 163213_1 | TR_LINE 163213_1 | TR_LINE 163222_1 | TR_LINE 163213_1 | TR_LINE 163213_1 | TR_LINE 163222_1 | TR_LINE 163213_1 | TR_LINE 163213_1 | TR_LINE 163222_1 | TR_LINE 163213_1 | TR_LINE 163213_1
NQ | 20007826 | HU-RI-1 | HUGHENDEN-RICHMOND | HU-RI-1_Hughenden-Richmond No 1 66 kV | Loading (A) | 44.6339 | 49.6696 | 39.398 | 44.0437 | 48.8981 | 39.0572 | 60.8836 | 69.8685 | 50.3531 | 60.8849 | 69.8703 | 50.3542 | 61.271 | 70.5046 | 50.5458
NQ | 20007826 | HU-RI-1 | HUGHENDEN-RICHMOND | HU-RI-1_Hughenden-Richmond No 1 66 kV | Loading (MVA) | 5.1738 | 5.7124 | 4.5859 | 5.1071 | 5.6279 | 4.5489 | 6.9863 | 7.9634 | 5.8279 | 6.9863 | 7.9634 | 5.8278 | 7.0243 | 8.0274 | 5.8408
NQ | 20007826 | HU-RI-1 | HUGHENDEN-RICHMOND | HU-RI-1_Hughenden-Richmond No 1 66 kV | Loading (MW) | 4.7385 | 5.4257 | 3.7973 | 4.6454 | 5.3157 | 3.7308 | 6.9067 | 7.9493 | 5.5212 | 6.9068 | 7.9493 | 5.5212 | 6.97 | 8.0234 | 5.5801
NQ | 20007826 | HU-RI-1 | HUGHENDEN-RICHMOND | HU-RI-1_Hughenden-Richmond No 1 66 kV | Power Factor | 0.91587 | 0.94981 | 0.82804 | 0.9096 | 0.94453 | 0.82015 | 0.98861 | 0.99823 | 0.94737 | 0.98862 | 0.99823 | 0.94739 | 0.99226 | 0.9995 | 0.95535
NQ | 20007826 | HU-RI-1 | HUGHENDEN-RICHMOND | HU-RI-1_Hughenden-Richmond No 1 66 kV | Rating (A) | 285 | 363 | 332 | 285 | 363 | 332 | 285 | 363 | 332 | 285 | 363 | 332 | 285 | 363 | 332
NQ | 20007826 | HU-RI-1 | HUGHENDEN-RICHMOND | HU-RI-1_Hughenden-Richmond No 1 66 kV | Time | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00
NQ | 20007826 | HU-RI-1 | HUGHENDEN-RICHMOND | HU-RI-1_Hughenden-Richmond No 1 66 kV | Voltage at Constrained Conductor | 66.9245 | 66.3995 | 67.2037 | 66.9466 | 66.4495 | 67.2426 | 66.2502 | 65.8045 | 66.8228 | 66.2487 | 65.803 | 66.8203 | 66.1895 | 65.7354 | 66.7158
NQ | 20008181 | IN-LA-1 | INGHAM-LANNERCOST | IN-LA-1_Ingham-Lannercost No 1 66 kV | % of Rated A | 5.7558 | 9.6956 | 6.2056 | 5.7549 | 9.6939 | 6.2049 | 5.7636 | 9.707 | 6.2091 | 5.7637 | 9.7072 | 6.2091 | 5.7645 | 9.8363 | 6.2106
NQ | 20008181 | IN-LA-1 | INGHAM-LANNERCOST | IN-LA-1_Ingham-Lannercost No 1 66 kV | Limiting Line Name | TR_LINE 32824_1 | TR_LINE 32824_1 | TR_LINE 32824_1 | TR_LINE 32824_1 | TR_LINE 32824_1 | TR_LINE 32824_1 | TR_LINE 32824_1 | TR_LINE 32824_1 | TR_LINE 32824_1 | TR_LINE 32824_1 | TR_LINE 32824_1 | TR_LINE 32824_1 | TR_LINE 32824_1 | TR_LINE 32824_1 | TR_LINE 32824_1
NQ | 20008181 | IN-LA-1 | INGHAM-LANNERCOST | IN-LA-1_Ingham-Lannercost No 1 66 kV | Loading (A) | 7.7127 | 17.5491 | 10.8597 | 7.7115 | 17.546 | 10.8585 | 7.7233 | 17.5696 | 10.8659 | 7.7234 | 17.57 | 10.866 | 7.7245 | 17.8037 | 10.8686
NQ | 20008181 | IN-LA-1 | INGHAM-LANNERCOST | IN-LA-1_Ingham-Lannercost No 1 66 kV | Loading (MVA) | 0.92566 | 2.0988 | 1.3036 | 0.92567 | 2.0988 | 1.3036 | 0.92566 | 2.0988 | 1.3036 | 0.92566 | 2.0988 | 1.3036 | 0.92566 | 2.0993 | 1.3036
NQ | 20008181 | IN-LA-1 | INGHAM-LANNERCOST | IN-LA-1_Ingham-Lannercost No 1 66 kV | Loading (MW) | 0.92533 | 2.0913 | 1.3028 | 0.92533 | 2.0913 | 1.3028 | 0.92533 | 2.0913 | 1.3028 | 0.92533 | 2.0913 | 1.3028 | 0.92533 | 2.0914 | 1.3028
NQ | 20008181 | IN-LA-1 | INGHAM-LANNERCOST | IN-LA-1_Ingham-Lannercost No 1 66 kV | Power Factor | 0.99963 | 0.99643 | 0.99944 | 0.99963 | 0.99643 | 0.99945 | 0.99965 | 0.99641 | 0.99944 | 0.99965 | 0.99641 | 0.99944 | 0.99965 | 0.99626 | 0.99944
NQ | 20008181 | IN-LA-1 | INGHAM-LANNERCOST | IN-LA-1_Ingham-Lannercost No 1 66 kV | Rating (A) | 134 | 181 | 175 | 134 | 181 | 175 | 134 | 181 | 175 | 134 | 181 | 175 | 134 | 181 | 175
NQ | 20008181 | IN-LA-1 | INGHAM-LANNERCOST | IN-LA-1_Ingham-Lannercost No 1 66 kV | Time | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00
NQ | 20008181 | IN-LA-1 | INGHAM-LANNERCOST | IN-LA-1_Ingham-Lannercost No 1 66 kV | Voltage at Constrained Conductor | 69.2923 | 69.0477 | 69.3031 | 69.3034 | 69.0597 | 69.3107 | 69.1971 | 68.9688 | 69.2643 | 69.1964 | 68.9676 | 69.2638 | 69.1865 | 68.0766 | 69.2476
NQ | 20008182 | IN-VC-1 | INGHAM-VICTORIA | IN-VC-1_Ingham-Victoria No 1 66 kV | % of Rated A | 43.9637 | 28.4614 | 29.613 | 43.957 | 28.4558 | 29.6113 | 43.2212 | 28.2855 | 29.2535 | 43.2213 | 28.286 | 29.2535 | 43.5292 | 28.5088 | 29.5897
NQ | 20008182 | IN-VC-1 | INGHAM-VICTORIA | IN-VC-1_Ingham-Victoria No 1 66 kV | Limiting Line Name | TR_LINE 135530_1 | TR_LINE 135530_1 | TR_LINE 135530_1 | TR_LINE 135530_1 | TR_LINE 135530_1 | TR_LINE 135530_1 | TR_LINE 135530_1 | TR_LINE 135530_1 | TR_LINE 135530_1 | TR_LINE 135530_1 | TR_LINE 135530_1 | TR_LINE 135530_1 | TR_LINE 135530_1 | TR_LINE 135530_1 | TR_LINE 135530_1
NQ | 20008182 | IN-VC-1 | INGHAM-VICTORIA | IN-VC-1_Ingham-Victoria No 1 66 kV | Loading (A) | 87.4839 | 63.4656 | 60.4105 | 87.4705 | 63.4531 | 60.407 | 86.0062 | 63.0734 | 59.677 | 86.0065 | 63.0744 | 59.6771 | 86.6191 | 63.5712 | 60.363
NQ | 20008182 | IN-VC-1 | INGHAM-VICTORIA | IN-VC-1_Ingham-Victoria No 1 66 kV | Loading (MVA) | 10.3393 | 7.4475 | 7.1408 | 10.3392 | 7.4474 | 7.1407 | 10.2644 | 7.3922 | 7.1331 | 10.2644 | 7.3922 | 7.1331 | 10.3346 | 7.4484 | 7.2133
NQ | 20008182 | IN-VC-1 | INGHAM-VICTORIA | IN-VC-1_Ingham-Victoria No 1 66 kV | Loading (MW) | 8.71 | 6.5589 | 6.1667 | 8.71 | 6.5589 | 6.1667 | 8.6518 | 6.5125 | 6.134 | 8.6518 | 6.5125 | 6.134 | 8.7094 | 6.5591 | 6.1996
NQ | 20008182 | IN-VC-1 | INGHAM-VICTORIA | IN-VC-1_Ingham-Victoria No 1 66 kV | Power Factor | 0.84242 | 0.88069 | 0.86359 | 0.84242 | 0.8807 | 0.86359 | 0.84289 | 0.88099 | 0.85993 | 0.84289 | 0.88099 | 0.85993 | 0.84274 | 0.8806 | 0.85947
NQ | 20008182 | IN-VC-1 | INGHAM-VICTORIA | IN-VC-1_Ingham-Victoria No 1 66 kV | Rating (A) | 199 | 223 | 204 | 199 | 223 | 204 | 199 | 223 | 204 | 199 | 223 | 204 | 199 | 223 | 204
NQ | 20008182 | IN-VC-1 | INGHAM-VICTORIA | IN-VC-1_Ingham-Victoria No 1 66 kV | Time | 14:30 | 17:30 | 2:30 | 14:30 | 17:30 | 2:30 | 14:30 | 17:30 | 0:30 | 14:30 | 17:30 | 0:30 | 14:30 | 17:30 | 0:30
NQ | 20008182 | IN-VC-1 | INGHAM-VICTORIA | IN-VC-1_Ingham-Victoria No 1 66 kV | Voltage at Constrained Conductor | 68.2344 | 67.7504 | 68.2452 | 68.2442 | 67.7628 | 68.2488 | 68.9038 | 67.6656 | 69.0101 | 68.9035 | 67.6646 | 69.01 | 68.8844 | 67.6457 | 68.9927
NQ | 20008540 | JA-EA-1 | JARVISFIELD-EASTAYR | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | % of Rated A | 18.6502 | 13.4454 | 12.4338 | 18.4778 | 13.2332 | 12.2719 | 18.4728 | 13.2303 | 12.4398 | 18.5304 | 13.2465 | 12.4551 | 18.5979 | 13.2758 | 12.3133
NQ | 20008540 | JA-EA-1 | JARVISFIELD-EASTAYR | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Limiting Line Name | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1
NQ | 20008540 | JA-EA-1 | JARVISFIELD-EASTAYR | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Loading (A) | 31.5189 | 32.2691 | 29.095 | 31.2275 | 31.7597 | 28.7162 | 31.219 | 31.7527 | 29.1091 | 31.3164 | 31.7915 | 29.1449 | 31.4304 | 31.8619 | 28.8131
NQ | 20008540 | JA-EA-1 | JARVISFIELD-EASTAYR | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Loading (MVA) | 3.566 | 3.6779 | 3.3265 | 3.5366 | 3.6238 | 3.2859 | 3.5367 | 3.6245 | 3.2881 | 3.5471 | 3.6283 | 3.2916 | 3.5583 | 3.6342 | 3.2957
NQ | 20008540 | JA-EA-1 | JARVISFIELD-EASTAYR | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Loading (MW) | 1.0977 | 0.44799 | 0.46066 | 1.1878 | 0.5502 | 0.5336 | 1.1882 | 0.54883 | 0.53106 | 1.2212 | 0.58074 | 0.55904 | 1.2479 | 0.60561 | 0.58016
NQ | 20008540 | JA-EA-1 | JARVISFIELD-EASTAYR | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Power Factor | 0.30782 | 0.12181 | 0.13848 | 0.33587 | 0.15183 | 0.16239 | 0.33597 | 0.15142 | 0.16151 | 0.34428 | 0.16006 | 0.16984 | 0.3507 | 0.16664 | 0.17603
NQ | 20008540 | JA-EA-1 | JARVISFIELD-EASTAYR | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Rating (A) | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234
NQ | 20008540 | JA-EA-1 | JARVISFIELD-EASTAYR | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Time | 16:00 | 19:00 | 22:00 | 16:00 | 19:00 | 22:00 | 16:00 | 19:00 | 22:00 | 16:00 | 19:00 | 22:00 | 16:00 | 19:00 | 22:00
NQ | 20008540 | JA-EA-1 | JARVISFIELD-EASTAYR | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Voltage at Constrained Conductor | 65.32 | 65.8043 | 66.0101 | 65.3861 | 65.8767 | 66.065 | 65.4053 | 65.9028 | 65.2157 | 65.3947 | 65.8909 | 65.2048 | 65.3624 | 65.8529 | 66.0387
NQ | 20010916 | MP-AY-1 | MONAPARK-AYR | MP-AY-1 Mona Park - Ayr No 1 66 kV | % of Rated A | 41.8376 | 30.2628 | 28.2895 | 41.1668 | 29.6503 | 27.8897 | 40.926 | 29.4446 | 28.0609 | 41.1127 | 29.5884 | 28.1807 | 41.3615 | 29.8622 | 28.0179
NQ | 20010916 | MP-AY-1 | MONAPARK-AYR | MP-AY-1 Mona Park - Ayr No 1 66 kV | Limiting Line Name | TR_LINE 32495_1 | TR_LINE 32495_1 | TR_LINE 32495_1 | TR_LINE 32495_1 | TR_LINE 32495_1 | TR_LINE 32495_1 | TR_LINE 32495_1 | TR_LINE 32495_1 | TR_LINE 32495_1 | TR_LINE 32495_1 | TR_LINE 32495_1 | TR_LINE 32495_1 | TR_LINE 32495_1 | TR_LINE 32495_1 | TR_LINE 32495_1
NQ | 20010916 | MP-AY-1 | MONAPARK-AYR | MP-AY-1 Mona Park - Ayr No 1 66 kV | Loading (A) | 83.2563 | 88.9722 | 81.7562 | 81.9214 | 87.1715 | 80.6007 | 81.4422 | 86.5669 | 81.0954 | 81.8137 | 86.9896 | 81.4417 | 82.3089 | 87.7944 | 80.9712
NQ | 20010916 | MP-AY-1 | MONAPARK-AYR | MP-AY-1 Mona Park - Ayr No 1 66 kV | Loading (MVA) | 9.4634 | 10.0898 | 9.297 | 9.3193 | 9.8968 | 9.0558 | 9.2689 | 9.8325 | 9.1088 | 9.3098 | 9.8787 | 9.1464 | 9.3623 | 9.964 | 9.0964
NQ | 20010916 | MP-AY-1 | MONAPARK-AYR | MP-AY-1 Mona Park - Ayr No 1 66 kV | Loading (MW) | 9.2269 | 9.9651 | 9.0463 | 9.0929 | 9.7829 | 8.8364 | 9.0494 | 9.7254 | 8.8701 | 9.0877 | 9.7698 | 8.9057 | 9.1382 | 9.8513 | 8.8793
NQ | 20010916 | MP-AY-1 | MONAPARK-AYR | MP-AY-1 Mona Park - Ayr No 1 66 kV | Power Factor | 0.97501 | 0.98763 | 0.97304 | 0.97571 | 0.9885 | 0.97577 | 0.97632 | 0.98911 | 0.97379 | 0.97615 | 0.98897 | 0.97368 | 0.97606 | 0.98869 | 0.97613
NQ | 20010916 | MP-AY-1 | MONAPARK-AYR | MP-AY-1 Mona Park - Ayr No 1 66 kV | Rating (A) | 199 | 294 | 289 | 199 | 294 | 289 | 199 | 294 | 289 | 199 | 294 | 289 | 199 | 294 | 289
NQ | 20010916 | MP-AY-1 | MONAPARK-AYR | MP-AY-1 Mona Park - Ayr No 1 66 kV | Time | 11:00 | 18:30 | 8:00 | 11:00 | 18:30 | 8:30 | 11:00 | 18:30 | 8:00 | 11:00 | 18:30 | 8:00 | 11:00 | 18:30 | 8:30
NQ | 20010916 | MP-AY-1 | MONAPARK-AYR | MP-AY-1 Mona Park - Ayr No 1 66 kV | Voltage at Constrained Conductor | 65.6249 | 65.474 | 65.6537 | 65.6786 | 65.548 | 64.8679 | 65.7081 | 65.577 | 64.8495 | 65.6984 | 65.5651 | 64.8402 | 65.6711 | 65.5247 | 64.8605
NQ | 20010918 | MR-LE-1 | MILLCHESTER-MOUNTLEYSHON | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | % of Rated A | 40.055 | 34.9922 | 41.1213 | 39.4954 | 34.5032 | 40.5493 | 39.5221 | 34.5568 | 40.5992 | 39.5433 | 34.5764 | 40.6213 | 40.0995 | 35.0034 | 41.1992
NQ | 20010918 | MR-LE-1 | MILLCHESTER-MOUNTLEYSHON | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Limiting Line Name | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 49923_1
NQ | 20010918 | MR-LE-1 | MILLCHESTER-MOUNTLEYSHON | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Loading (A) | 73.6241 | 70.0558 | 74.3928 | 72.5617 | 69.0429 | 73.3243 | 72.6253 | 69.1672 | 73.4305 | 72.653 | 69.195 | 73.4594 | 73.7091 | 70.0848 | 74.5389
NQ | 20010918 | MR-LE-1 | MILLCHESTER-MOUNTLEYSHON | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Loading (MVA) | 8.4405 | 8.0587 | 8.5299 | 8.3251 | 7.9485 | 8.4133 | 8.3254 | 7.9502 | 8.4145 | 8.3269 | 7.9516 | 8.4161 | 8.4422 | 8.0524 | 8.5329
NQ | 20010918 | MR-LE-1 | MILLCHESTER-MOUNTLEYSHON | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Loading (MW) | 7.3987 | 7.08 | 7.4726 | 7.2873 | 6.9736 | 7.3601 | 7.3035 | 6.9896 | 7.3768 | 7.2879 | 6.9746 | 7.361 | 7.3993 | 7.0794 | 7.4736
NQ | 20010918 | MR-LE-1 | MILLCHESTER-MOUNTLEYSHON | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Power Factor | 0.87657 | 0.87856 | 0.87604 | 0.87534 | 0.87734 | 0.87481 | 0.87726 | 0.87917 | 0.87668 | 0.87522 | 0.87714 | 0.87464 | 0.87646 | 0.87917 | 0.87586
NQ | 20010918 | MR-LE-1 | MILLCHESTER-MOUNTLEYSHON | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Rating (A) | 188 | 205 | 185 | 188 | 205 | 185 | 188 | 205 | 185 | 188 | 205 | 185 | 188 | 205 | 185
NQ | 20010918 | MR-LE-1 | MILLCHESTER-MOUNTLEYSHON | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Time | 12:30 | 20:30 | 23:00 | 12:30 | 20:30 | 23:00 | 12:30 | 20:30 | 23:00 | 12:30 | 20:30 | 23:00 | 12:30 | 20:30 | 23:00
NQ | 20010918 | MR-LE-1 | MILLCHESTER-MOUNTLEYSHON | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Voltage at Constrained Conductor | 66.1893 | 66.4138 | 66.1995 | 66.2399 | 66.4673 | 66.2461 | 66.1843 | 66.3616 | 66.1592 | 66.1712 | 66.3463 | 66.1458 | 66.1265 | 66.3349 | 66.0929
NQ | 20012877 | ST-GI-1 | Stuart-Giru | ST-GI-1_Stuart-Giru 66 kV | % of Rated A | 12.8858 | 14.4664 | 14.938 | 12.8866 | 14.4659 | 14.9378 | 12.796 | 14.3604 | 14.9807 | 12.7981 | 14.3631 | 14.9829 | 12.803 | 14.3692 | 14.9885
NQ | 20012877 | ST-GI-1 | Stuart-Giru | ST-GI-1_Stuart-Giru 66 kV | Limiting Line Name | TR_LINE 31680_2 | TR_LINE 31680_2 | TR_LINE 31680_2 | TR_LINE 31680_2 | TR_LINE 31680_2 | TR_LINE 31680_2 | TR_LINE 31680_2 | TR_LINE 31680_2 | TR_LINE 31680_2 | TR_LINE 31680_2 | TR_LINE 31680_2 | TR_LINE 31680_2 | TR_LINE 31680_2 | TR_LINE 31680_2 | TR_LINE 31680_2
NQ | 20012877 | ST-GI-1 | Stuart-Giru | ST-GI-1_Stuart-Giru 66 kV | Loading (A) | 12.6281 | 15.479 | 14.3405 | 12.6289 | 15.4785 | 14.3403 | 12.5401 | 15.3656 | 14.3815 | 12.5421 | 15.3686 | 14.3835 | 12.547 | 15.3751 | 14.3889
NQ | 20012877 | ST-GI-1 | Stuart-Giru | ST-GI-1_Stuart-Giru 66 kV | Loading (MVA) | 1.4822 | 1.8102 | 1.687 | 1.4822 | 1.8102 | 1.687 | 1.4821 | 1.8101 | 1.6871 | 1.4821 | 1.8101 | 1.6871 | 1.4821 | 1.8101 | 1.6871
NQ | 20012877 | ST-GI-1 | Stuart-Giru | ST-GI-1_Stuart-Giru 66 kV | Loading (MW) | 1.4743 | 1.7995 | 1.6775 | 1.4743 | 1.7995 | 1.6775 | 1.4743 | 1.7994 | 1.6775 | 1.4743 | 1.7994 | 1.6775 | 1.4743 | 1.7994 | 1.6775
NQ | 20012877 | ST-GI-1 | Stuart-Giru | ST-GI-1_Stuart-Giru 66 kV | Power Factor | 0.9947 | 0.99408 | 0.99435 | 0.9947 | 0.99408 | 0.99435 | 0.99474 | 0.99413 | 0.99433 | 0.99474 | 0.99413 | 0.99433 | 0.99473 | 0.99413 | 0.99433
NQ | 20012877 | ST-GI-1 | Stuart-Giru | ST-GI-1_Stuart-Giru 66 kV | Rating (A) | 98 | 107 | 96 | 98 | 107 | 96 | 98 | 107 | 96 | 98 | 107 | 96 | 98 | 107 | 96
NQ | 20012877 | ST-GI-1 | Stuart-Giru | ST-GI-1_Stuart-Giru 66 kV | Time | 16:30 | 19:30 | 22:00 | 16:30 | 19:30 | 22:00 | 16:30 | 19:30 | 22:00 | 16:30 | 19:30 | 22:00 | 16:30 | 19:30 | 22:00
NQ | 20012877 | ST-GI-1 | Stuart-Giru | ST-GI-1_Stuart-Giru 66 kV | Voltage at Constrained Conductor | 67.7631 | 67.5194 | 67.9203 | 67.7591 | 67.5214 | 67.921 | 68.2344 | 68.0115 | 67.7287 | 68.2235 | 67.9987 | 67.7192 | 68.1973 | 67.9702 | 67.6942
NQ | 20012878 | HP-OO | HERMIT PARK - OONOONBA | HP-OO_Hermit park - Oonoonba 66 kV | % of Rated A | 38.4248 | 36.3963 | 39.1885 | 38.1171 | 36.1027 | 38.8816 | 39.8425 | 37.924 | 39.7724 | 39.8764 | 37.9613 | 39.7568 | 40.0303 | 38.1041 | 39.9107
NQ | 20012878 | HP-OO | HERMIT PARK - OONOONBA | HP-OO_Hermit park - Oonoonba 66 kV | Limiting Line Name | TR_LINE 106404_1 | TR_LINE 106404_1 | TR_LINE 106404_1 | TR_LINE 106404_1 | TR_LINE 106404_1 | TR_LINE 106404_1 | TR_LINE 106404_1 | TR_LINE 106404_1 | TR_LINE 106404_1 | TR_LINE 106404_1 | TR_LINE 106404_1 | TR_LINE 106404_1 | TR_LINE 106404_1 | TR_LINE 106404_1 | TR_LINE 106404_1
NQ | 20012878 | HP-OO | HERMIT PARK - OONOONBA | HP-OO_Hermit park - Oonoonba 66 kV | Loading (A) | 132.5655 | 128.8427 | 122.2682 | 131.504 | 127.8037 | 121.3105 | 137.4567 | 134.2511 | 124.0899 | 137.5735 | 134.3831 | 124.0412 | 138.1046 | 134.8886 | 124.5213
NQ | 20012878 | HP-OO | HERMIT PARK - OONOONBA | HP-OO_Hermit park - Oonoonba 66 kV | Loading (MVA) | 15.6777 | 15.2025 | 14.5498 | 15.5539 | 15.0811 | 14.4367 | 16.3377 | 15.9449 | 14.6703 | 16.3483 | 15.9571 | 14.6629 | 16.4032 | 16.0091 | 14.7145
NQ | 20012878 | HP-OO | HERMIT PARK - OONOONBA | HP-OO_Hermit park - Oonoonba 66 kV | Loading (MW) | 13.7638 | 13.1235 | 12.2902 | 13.5869 | 12.9518 | 12.1187 | 14.4872 | 13.9951 | 14.3328 | 14.4987 | 14.0097 | 14.3235 | 14.5726 | 14.0745 | 14.379
NQ | 20012878 | HP-OO | HERMIT PARK - OONOONBA | HP-OO_Hermit park - Oonoonba 66 kV | Power Factor | 0.87792 | 0.86324 | 0.8447 | 0.87354 | 0.85881 | 0.83943 | 0.88673 | 0.87772 | 0.97699 | 0.88686 | 0.87796 | 0.97686 | 0.8884 | 0.87916 | 0.9772
NQ | 20012878 | HP-OO | HERMIT PARK - OONOONBA | HP-OO_Hermit park - Oonoonba 66 kV | Rating (A) | 345 | 354 | 312 | 345 | 354 | 312 | 345 | 354 | 312 | 345 | 354 | 312 | 345 | 354 | 312
NQ | 20012878 | HP-OO | HERMIT PARK - OONOONBA | HP-OO_Hermit park - Oonoonba 66 kV | Time | 16:00 | 17:00 | 8:30 | 16:00 | 17:00 | 8:30 | 16:30 | 17:00 | 8:30 | 16:30 | 17:00 | 8:30 | 16:30 | 17:00 | 8:30
NQ | 20012878 | HP-OO | HERMIT PARK - OONOONBA | HP-OO_Hermit park - Oonoonba 66 kV | Voltage at Constrained Conductor | 68.2797 | 68.1232 | 68.7043 | 68.2872 | 68.1286 | 68.7083 | 68.6222 | 68.5716 | 68.2563 | 68.6085 | 68.5563 | 68.2483 | 68.5742 | 68.5223 | 68.2248
NQ | 20012879 | ST-RM-1 | Stuart-Rasmussen | ST-RM-1_Stuart-Rasmussen 66 kV | % of Rated A | 19.8371 | 21.0502 | 19.0162 | 19.7447 | 20.9839 | 18.958 | 20.7448 | 22.0323 | 20.0319 | 20.8323 | 22.1463 | 20.1297 | 20.9649 | 22.3142 | 20.2598
NQ | 20012879 | ST-RM-1 | Stuart-Rasmussen | ST-RM-1_Stuart-Rasmussen 66 kV | Limiting Line Name | TR_LINE 32428_1 | TR_LINE 32428_1 | TR_LINE 32428_1 | TR_LINE 32428_1 | TR_LINE 32428_1 | TR_LINE 32428_1 | TR_LINE 32428_1 | TR_LINE 32428_1 | TR_LINE 32428_1 | TR_LINE 32428_1 | TR_LINE 32428_1 | TR_LINE 32428_1 | TR_LINE 32428_1 | TR_LINE 32428_1 | TR_LINE 32428_1
NQ | 20012879 | ST-RM-1 | Stuart-Rasmussen | ST-RM-1_Stuart-Rasmussen 66 kV | Loading (A) | 109.3027 | 122.5123 | 99.6446 | 108.7931 | 122.1263 | 99.3397 | 114.3038 | 128.2279 | 104.9673 | 114.786 | 128.8914 | 105.4796 | 115.5164 | 129.8684 | 106.1614
NQ | 20012879 | ST-RM-1 | Stuart-Rasmussen | ST-RM-1_Stuart-Rasmussen 66 kV | Loading (MVA) | 12.9839 | 14.5711 | 11.8844 | 12.9226 | 14.5255 | 11.8482 | 13.6699 | 15.3209 | 12.485 | 13.7255 | 15.3971 | 12.5442 | 13.8076 | 15.5071 | 12.6208
NQ | 20012879 | ST-RM-1 | Stuart-Rasmussen | ST-RM-1_Stuart-Rasmussen 66 kV | Loading (MW) | 12.9187 | 14.3865 | 11.7658 | 12.8552 | 14.3368 | 11.7271 | 13.1851 | 14.9977 | 12.4496 | 13.2471 | 15.0813 | 12.5101 | 13.3404 | 15.2035 | 12.5877
NQ | 20012879 | ST-RM-1 | Stuart-Rasmussen | ST-RM-1_Stuart-Rasmussen 66 kV | Power Factor | 0.99498 | 0.98733 | 0.99002 | 0.99479 | 0.98701 | 0.98978 | 0.96453 | 0.9789 | 0.99717 | 0.96515 | 0.97949 | 0.99728 | 0.96616 | 0.98042 | 0.99738
NQ | 20012879 | ST-RM-1 | Stuart-Rasmussen | ST-RM-1_Stuart-Rasmussen 66 kV | Rating (A) | 551 | 582 | 524 | 551 | 582 | 524 | 551 | 582 | 524 | 551 | 582 | 524 | 551 | 582 | 524
NQ | 20012879 | ST-RM-1 | Stuart-Rasmussen | ST-RM-1_Stuart-Rasmussen 66 kV | Time | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00
NQ | 20012879 | ST-RM-1 | Stuart-Rasmussen | ST-RM-1_Stuart-Rasmussen 66 kV | Voltage at Constrained Conductor | 68.5824 | 68.6677 | 68.8594 | 68.5784 | 68.6691 | 68.8602 | 69.047 | 68.9827 | 68.6709 | 69.0362 | 68.9689 | 68.6616 | 69.0104 | 68.9393 | 68.637
NQ | 20012880 | ST-RP-1 | Stuart-RossPlains | ST-RP-1_Stuart-Ross Plains 66 kV | % of Rated A | 38.8876 | 37.6807 | 33.1237 | 38.5833 | 37.3896 | 32.9126 | 39.3065 | 38.0852 | 34.5393 | 39.3911 | 38.1765 | 34.6232 | 39.6602 | 38.4497 | 34.8353
NQ | 20012880 | ST-RP-1 | Stuart-RossPlains | ST-RP-1_Stuart-Ross Plains 66 kV | Limiting Line Name | TR_LINE 32390_2 | TR_LINE 32392_1 | TR_LINE 32425_1 | TR_LINE 32834_1 | TR_LINE 32392_1 | TR_LINE 32425_1 | TR_LINE 32425_1 | TR_LINE 32425_1 | TR_LINE 32425_1 | TR_LINE 32425_1 | TR_LINE 32425_1 | TR_LINE 32425_1 | TR_LINE 32425_1 | TR_LINE 32425_1 | TR_LINE 32425_1
NQ | 20012880 | ST-RP-1 | Stuart-RossPlains | ST-RP-1_Stuart-Ross Plains 66 kV | Loading (A) | 264.0468 | 275.069 | 219.61 | 261.9809 | 272.944 | 218.2109 | 266.8913 | 278.0223 | 228.9958 | 267.4653 | 278.6884 | 229.5516 | 269.2927 | 280.6829 | 230.9579
NQ | 20012880 | ST-RP-1 | Stuart-RossPlains | ST-RP-1_Stuart-Ross Plains 66 kV | Loading (MVA) | 31.2173 | 32.421 | 26.1924 | 30.9879 | 32.1739 | 26.0259 | 31.9183 | 33.2209 | 27.2371 | 31.982 | 33.2944 | 27.2995 | 32.1884 | 33.5193 | 27.4569
NQ | 20012880 | ST-RP-1 | Stuart-RossPlains | ST-RP-1_Stuart-Ross Plains 66 kV | Loading (MW) | 31.2173 | 32.4207 | 26.156 | 30.9879 | 32.1738 | 25.986 | 31.6936 | 33.0479 | 27.237 | 31.7611 | 33.1254 | 27.2995 | 31.9797 | 33.3613 | 27.4569
NQ | 20012880 | ST-RP-1 | Stuart-RossPlains | ST-RP-1_Stuart-Ross Plains 66 kV | Power Factor | 1 | 0.99999 | 0.99861 | 1 | 1 | 0.99847 | 0.99296 | 0.99479 | 1 | 0.99309 | 0.99492 | 1 | 0.99351 | 0.99529 | 1
NQ | 20012880 | ST-RP-1 | Stuart-RossPlains | ST-RP-1_Stuart-Ross Plains 66 kV | Rating (A) | 679 | 730 | 663 | 679 | 730 | 663 | 679 | 730 | 663 | 679 | 730 | 663 | 679 | 730 | 663
NQ | 20012880 | ST-RP-1 | Stuart-RossPlains | ST-RP-1_Stuart-Ross Plains 66 kV | Time | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00
NQ | 20012880 | ST-RP-1 | Stuart-RossPlains | ST-RP-1_Stuart-Ross Plains 66 kV | Voltage at Constrained Conductor | 68.258 | 68.0493 | 68.8594 | 68.2909 | 68.0564 | 68.8602 | 69.047 | 68.9877 | 68.6709 | 69.0362 | 68.975 | 68.6616 | 69.0104 | 68.9475 | 68.637
NQ | 20012881 | ST-TOPO-1 | Stuart-TOPO | ST-TOPO-1_Stuart-Townsville Port 66 kV | % of Rated A | 17.0359 | 12.1635 | 14.9912 | 17.7207 | 12.5957 | 15.4908 | 21.0693 | 14.289 | 18.23 | 20.9741 | 14.223 | 18.1489 | 21.1452 | 14.3088 | 18.2861
NQ | 20012881 | ST-TOPO-1 | Stuart-TOPO | ST-TOPO-1_Stuart-Townsville Port 66 kV | Limiting Line Name | TR_LINE 31745_2 | TR_LINE 31664_1 | TR_LINE 31664_1 | TR_LINE 31745_2 | TR_LINE 31664_1 | TR_LINE 31664_1 | TR_LINE 31745_2 | TR_LINE 31664_1 | TR_LINE 31664_1 | TR_LINE 31745_2 | TR_LINE 31664_1 | TR_LINE 31664_1 | TR_LINE 31745_2 | TR_LINE 31664_1 | TR_LINE 31664_1
NQ | 20012881 | ST-TOPO-1 | Stuart-TOPO | ST-TOPO-1_Stuart-Townsville Port 66 kV | Loading (A) | 42.7601 | 38.1934 | 42.2752 | 44.4789 | 39.5505 | 43.684 | 52.8838 | 44.8673 | 51.4086 | 52.6449 | 44.6603 | 51.1799 | 53.0745 | 44.9296 | 51.5669
NQ | 20012881 | ST-TOPO-1 | Stuart-TOPO | ST-TOPO-1_Stuart-Townsville Port 66 kV | Loading (MVA) | 5.111 | 4.5345 | 5.0468 | 5.3155 | 4.6956 | 5.2148 | 6.2822 | 5.3626 | 6.118 | 6.2535 | 5.3369 | 6.0902 | 6.3027 | 5.3671 | 6.1346
NQ | 20012881 | ST-TOPO-1 | Stuart-TOPO | ST-TOPO-1_Stuart-Townsville Port 66 kV | Loading (MW) | 4.0731 | 2.9322 | 3.816 | 4.3426 | 3.1993 | 4.0477 | 6.1264 | 4.737 | 5.9115 | 6.0951 | 4.7021 | 5.8803 | 6.1457 | 4.7322 | 5.9264
NQ | 20012881 | ST-TOPO-1 | Stuart-TOPO | ST-TOPO-1_Stuart-Townsville Port 66 kV | Power Factor | 0.79693 | 0.64665 | 0.75613 | 0.81698 | 0.68133 | 0.7762 | 0.97519 | 0.88334 | 0.96625 | 0.97467 | 0.88104 | 0.96554 | 0.97509 | 0.88171 | 0.96606
NQ | 20012881 | ST-TOPO-1 | Stuart-TOPO | ST-TOPO-1_Stuart-Townsville Port 66 kV | Rating (A) | 251 | 314 | 282 | 251 | 314 | 282 | 251 | 314 | 282 | 251 | 314 | 282 | 251 | 314 | 282
NQ | 20012881 | ST-TOPO-1 | Stuart-TOPO | ST-TOPO-1_Stuart-Townsville Port 66 kV | Time | 11:30 | 17:00 | 8:30 | 11:30 | 17:00 | 8:30 | 11:30 | 17:00 | 8:30 | 11:30 | 17:00 | 8:30 | 11:30 | 17:00 | 8:30
NQ | 20012881 | ST-TOPO-1 | Stuart-TOPO | ST-TOPO-1_Stuart-Townsville Port 66 kV | Voltage at Constrained Conductor | 69.0097 | 68.5456 | 68.9237 | 68.9966 | 68.5456 | 68.921 | 68.5851 | 69.0055 | 68.709 | 68.5809 | 68.9938 | 68.7024 | 68.5619 | 68.9679 | 68.684
NQ | 20012883 | ST-WO-1 | STUA-WOSO | ST-WO-1_Stuart-Woodstock South 1 66 kV | % of Rated A | 51.1265 | 41.7762 | 39.7251 | 50.5793 | 41.2919 | 39.3446 | 54.8829 | 45.7455 | 42.4823 | 54.8485 | 45.7044 | 42.4371 | 55.2139 | 46.0666 | 42.2528
NQ | 20012883 | ST-WO-1 | STUA-WOSO | ST-WO-1_Stuart-Woodstock South 1 66 kV | Limiting Line Name | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1
NQ | 20012883 | ST-WO-1 | STUA-WOSO | ST-WO-1_Stuart-Woodstock South 1 66 kV | Loading (A) | 67.4869 | 69.7662 | 63.1628 | 66.7646 | 68.9574 | 62.5579 | 72.4454 | 76.395 | 67.5468 | 72.4 | 76.3263 | 67.475 | 72.8824 | 76.9312 | 67.182
NQ | 20012883 | ST-WO-1 | STUA-WOSO | ST-WO-1_Stuart-Woodstock South 1 66 kV | Loading (MVA) | 7.9722 | 8.2252 | 7.476 | 7.8884 | 8.1311 | 7.4054 | 8.5663 | 9.0441 | 7.9795 | 8.5597 | 9.0343 | 7.9699 | 8.6121 | 9.0996 | 7.9252
NQ | 20012883 | ST-WO-1 | STUA-WOSO | ST-WO-1_Stuart-Woodstock South 1 66 kV | Loading (MW) | 6.5862 | 6.9295 | 6.2751 | 6.5083 | 6.8483 | 6.2098 | 7.0759 | 7.6577 | 6.502 | 7.0729 | 7.6512 | 6.4955 | 7.1366 | 7.7339 | 6.5877
NQ | 20012883 | ST-WO-1 | STUA-WOSO | ST-WO-1_Stuart-Woodstock South 1 66 kV | Power Factor | 0.82614 | 0.84248 | 0.83937 | 0.82505 | 0.84223 | 0.83856 | 0.82602 | 0.84671 | 0.81484 | 0.8263 | 0.84691 | 0.81501 | 0.82868 | 0.84992 | 0.83123
NQ | 20012883 | ST-WO-1 | STUA-WOSO | ST-WO-1_Stuart-Woodstock South 1 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
NQ | 20012883 | ST-WO-1 | STUA-WOSO | ST-WO-1_Stuart-Woodstock South 1 66 kV | Time | 15:30 | 19:00 | 22:00 | 15:30 | 19:00 | 22:00 | 15:30 | 18:30 | 22:00 | 15:30 | 18:30 | 22:00 | 15:30 | 18:30 | 22:00
NQ | 20012883 | ST-WO-1 | STUA-WOSO | ST-WO-1_Stuart-Woodstock South 1 66 kV | Voltage at Constrained Conductor | 68.2021 | 68.0677 | 68.3353 | 68.2152 | 68.0779 | 68.3449 | 68.2689 | 68.3506 | 68.2038 | 68.2592 | 68.3373 | 68.1943 | 68.2219 | 68.2899 | 68.1078
NQ | 20012969 | TP-NS-1 | TP-NeilSmith | TP-NS-1_Townsville Port-NESM No 1 66 kV | % of Rated A | 25.4487 | 17.1242 | 20.823 | 25.1265 | 16.9093 | 20.5609 | 25.286 | 16.832 | 20.6909 | 25.4522 | 16.9429 | 20.8264 | 25.7884 | 17.1661 | 21.1009
NQ | 20012969 | TP-NS-1 | TP-NeilSmith | TP-NS-1_Townsville Port-NESM No 1 66 kV | Limiting Line Name | TR_LINE 31649_1 | TR_LINE 31649_1 | TR_LINE 31649_1 | TR_LINE 31649_1 | TR_LINE 31649_1 | TR_LINE 31649_1 | TR_LINE 31649_1 | TR_LINE 31649_1 | TR_LINE 31649_1 | TR_LINE 31649_1 | TR_LINE 31649_1 | TR_LINE 31649_1 | TR_LINE 31649_1 | TR_LINE 31649_1 | TR_LINE 31649_1
NQ | 20012969 | TP-NS-1 | TP-NeilSmith | TP-NS-1_Townsville Port-NESM No 1 66 kV | Loading (A) | 65.6574 | 50.5163 | 56.6384 | 64.8262 | 49.8824 | 55.9256 | 65.2377 | 49.6543 | 56.2791 | 65.6665 | 49.9814 | 56.6476 | 66.5339 | 50.64 | 57.3944
NQ | 20012969 | TP-NS-1 | TP-NeilSmith | TP-NS-1_Townsville Port-NESM No 1 66 kV | Loading (MVA) | 7.8407 | 6.0075 | 6.7672 | 7.7402 | 5.931 | 6.6807 | 7.7409 | 5.9313 | 6.681 | 7.7912 | 5.9695 | 6.7243 | 7.8919 | 6.0458 | 6.8109
NQ | 20012969 | TP-NS-1 | TP-NeilSmith | TP-NS-1_Townsville Port-NESM No 1 66 kV | Loading (MW) | 7.832 | 6.0074 | 6.7652 | 7.7322 | 5.931 | 6.679 | 7.7322 | 5.9312 | 6.679 | 7.7821 | 5.9695 | 6.7221 | 7.8819 | 6.0457 | 6.8083
NQ | 20012969 | TP-NS-1 | TP-NeilSmith | TP-NS-1_Townsville Port-NESM No 1 66 kV | Power Factor | 0.99888 | 0.99998 | 0.9997 | 0.99897 | 0.99999 | 0.99975 | 0.99888 | 0.99999 | 0.9997 | 0.99884 | 0.99999 | 0.99967 | 0.99874 | 0.99998 | 0.99962
NQ | 20012969 | TP-NS-1 | TP-NeilSmith | TP-NS-1_Townsville Port-NESM No 1 66 kV | Rating (A) | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272
NQ | 20012969 | TP-NS-1 | TP-NeilSmith | TP-NS-1_Townsville Port-NESM No 1 66 kV | Time | 13:00 | 17:00 | 8:30 | 13:00 | 17:00 | 8:30 | 13:00 | 17:00 | 8:30 | 13:00 | 17:00 | 8:30 | 13:00 | 17:00 | 8:30
NQ | 20012969 | TP-NS-1 | TP-NeilSmith | TP-NS-1_Townsville Port-NESM No 1 66 kV | Voltage at Constrained Conductor | 68.9467 | 68.6601 | 68.9824 | 68.9348 | 68.6468 | 68.9687 | 68.5062 | 68.9651 | 68.5385 | 68.5013 | 68.9557 | 68.5337 | 68.4822 | 68.9286 | 68.5128
NQ | 20013599 | DG-CB-1 | DANGLEESON-CRANBROOK | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | % of Rated A | 33.2865 | 30.3416 | 31.3654 | 32.8841 | 29.9686 | 31.0322 | 32.5222 | 29.645 | 29.6855 | 32.4505 | 29.5771 | 29.622 | 32.7491 | 29.8425 | 29.9063
NQ | 20013599 | DG-CB-1 | DANGLEESON-CRANBROOK | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Limiting Line Name | TR_LINE 126322_1 | TR_LINE 126322_1 | TR_LINE 126322_1 | TR_LINE 126322_1 | TR_LINE 126322_1 | TR_LINE 126322_1 | TR_LINE 126334_1 | TR_LINE 126334_1 | TR_LINE 126322_1 | TR_LINE 126334_1 | TR_LINE 126334_1 | TR_LINE 126322_1 | TR_LINE 126334_1 | TR_LINE 126334_1 | TR_LINE 126322_1
NQ | 20013599 | DG-CB-1 | DANGLEESON-CRANBROOK | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Loading (A) | 150.4551 | 144.4262 | 133.9303 | 148.6362 | 142.6506 | 132.5077 | 146.9987 | 141.1087 | 126.7571 | 146.6746 | 140.7854 | 126.4858 | 148.0243 | 142.0485 | 127.6999
NQ | 20013599 | DG-CB-1 | DANGLEESON-CRANBROOK | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Loading (MVA) | 17.7956 | 17.0398 | 15.9549 | 17.5842 | 16.8336 | 15.7877 | 17.5408 | 16.8241 | 14.9973 | 17.499 | 16.7821 | 14.9638 | 17.6514 | 16.9245 | 15.1026
NQ | 20013599 | DG-CB-1 | DANGLEESON-CRANBROOK | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Loading (MW) | 17.3504 | 16.5439 | 15.1755 | 17.1123 | 16.3105 | 14.9754 | 17.5065 | 16.7944 | 14.9853 | 17.4651 | 16.7528 | 14.9514 | 17.6146 | 16.8928 | 15.0919
NQ | 20013599 | DG-CB-1 | DANGLEESON-CRANBROOK | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Power Factor | 0.97498 | 0.9709 | 0.95115 | 0.97316 | 0.96892 | 0.94855 | 0.99805 | 0.99824 | 0.9992 | 0.99807 | 0.99825 | 0.99918 | 0.99791 | 0.99813 | 0.99929
NQ | 20013599 | DG-CB-1 | DANGLEESON-CRANBROOK | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Rating (A) | 452 | 476 | 427 | 452 | 476 | 427 | 452 | 476 | 427 | 452 | 476 | 427 | 452 | 476 | 427
NQ | 20013599 | DG-CB-1 | DANGLEESON-CRANBROOK | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Time | 16:00 | 17:00 | 8:30 | 16:00 | 17:00 | 8:30 | 16:30 | 17:00 | 8:30 | 16:30 | 17:00 | 8:30 | 16:30 | 17:00 | 8:30
NQ | 20013599 | DG-CB-1 | DANGLEESON-CRANBROOK | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Voltage at Constrained Conductor | 68.2882 | 68.1175 | 68.7788 | 68.3026 | 68.1308 | 68.7888 | 68.8931 | 68.8364 | 68.3091 | 68.8807 | 68.8222 | 68.3028 | 68.8472 | 68.7891 | 68.2812
NQ | 20013608 | GI-AY-1 | GIRU-AYR | GI-AY-1_Giru - Ayr 1 66 kV | % of Rated A | 19.4197 | 20.6192 | 21.1479 | 19.6966 | 20.5955 | 21.1277 | 19.2939 | 20.1359 | 20.9918 | 19.2971 | 20.1404 | 20.996 | 19.7049 | 20.6039 | 21.1375
NQ | 20013608 | GI-AY-1 | GIRU-AYR | GI-AY-1_Giru - Ayr 1 66 kV | Limiting Line Name | TR_LINE 33583_2 | TR_LINE 33583_2 | TR_LINE 33583_2 | TR_LINE 33583_2 | TR_LINE 33583_2 | TR_LINE 33583_2 | TR_LINE 33583_2 | TR_LINE 33583_2 | TR_LINE 33583_2 | TR_LINE 33583_2 | TR_LINE 33583_2 | TR_LINE 33583_2 | TR_LINE 33583_2 | TR_LINE 33583_2 | TR_LINE 33583_2
NQ | 20013608 | GI-AY-1 | GIRU-AYR | GI-AY-1_Giru - Ayr 1 66 kV | Loading (A) | 36.7033 | 42.4756 | 39.3351 | 37.2265 | 42.4266 | 39.2975 | 36.4654 | 41.48 | 39.0447 | 36.4716 | 41.4892 | 39.0526 | 37.2422 | 42.4441 | 39.3157
NQ | 20013608 | GI-AY-1 | GIRU-AYR | GI-AY-1_Giru - Ayr 1 66 kV | Loading (MVA) | 4.1428 | 4.7636 | 4.4305 | 4.1485 | 4.763 | 4.4301 | 4.066 | 4.6602 | 4.3443 | 4.0661 | 4.6603 | 4.3444 | 4.1487 | 4.7632 | 4.4303
NQ | 20013608 | GI-AY-1 | GIRU-AYR | GI-AY-1_Giru - Ayr 1 66 kV | Loading (MW) | 3.8038 | 4.353 | 4.0593 | 3.8043 | 4.3529 | 4.0592 | 3.7299 | 4.2605 | 3.9768 | 3.7299 | 4.2605 | 3.9768 | 3.8043 | 4.3529 | 4.0592
NQ | 20013608 | GI-AY-1 | GIRU-AYR | GI-AY-1_Giru - Ayr 1 66 kV | Power Factor | 0.91818 | 0.9138 | 0.9162 | 0.91702 | 0.91389 | 0.91628 | 0.91733 | 0.91424 | 0.91541 | 0.91732 | 0.91422 | 0.91539 | 0.91698 | 0.91386 | 0.91624
NQ | 20013608 | GI-AY-1 | GIRU-AYR | GI-AY-1_Giru - Ayr 1 66 kV | Rating (A) | 189 | 206 | 186 | 189 | 206 | 186 | 189 | 206 | 186 | 189 | 206 | 186 | 189 | 206 | 186
NQ | 20013608 | GI-AY-1 | GIRU-AYR | GI-AY-1_Giru - Ayr 1 66 kV | Time | 16:30 | 19:30 | 22:00 | 16:30 | 19:30 | 22:00 | 16:30 | 19:30 | 22:00 | 16:30 | 19:30 | 22:00 | 16:30 | 19:30 | 22:00
NQ | 20013608 | GI-AY-1 | GIRU-AYR | GI-AY-1_Giru - Ayr 1 66 kV | Voltage at Constrained Conductor | 65.1675 | 64.749 | 65.0299 | 64.3401 | 64.8162 | 65.0859 | 64.3765 | 64.8639 | 64.239 | 64.3668 | 64.8509 | 64.2274 | 64.3158 | 64.7922 | 65.0588
NQ | 20013609 | IN-GR | INGHAM-BLACKRIVER/GREENVALE | IN-GR_Ingham-Black River/Greenvale 66 kV | % of Rated A | 22.9751 | 18.2119 | 19.1583 | 22.9783 | 18.2148 | 19.1602 | 22.9487 | 18.1935 | 19.1556 | 22.9485 | 18.1932 | 19.1555 | 22.9461 | 18.1617 | 19.1562
NQ | 20013609 | IN-GR | INGHAM-BLACKRIVER/GREENVALE | IN-GR_Ingham-Black River/Greenvale 66 kV | Limiting Line Name | TR_LINE 217286_1 | TR_LINE 217286_1 | TR_LINE 217286_1 | TR_LINE 217286_1 | TR_LINE 217286_1 | TR_LINE 217286_1 | TR_LINE 217286_1 | TR_LINE 217286_1 | TR_LINE 217286_1 | TR_LINE 217286_1 | TR_LINE 217286_1 | TR_LINE 217286_1 | TR_LINE 217286_1 | TR_LINE 217286_1 | TR_LINE 217286_1
NQ | 20013609 | IN-GR | INGHAM-BLACKRIVER/GREENVALE | IN-GR_Ingham-Black River/Greenvale 66 kV | Loading (A) | 15.8528 | 15.8444 | 15.7098 | 15.855 | 15.8469 | 15.7114 | 15.8346 | 15.8283 | 15.7076 | 15.8345 | 15.8281 | 15.7075 | 15.8328 | 15.8007 | 15.7081
NQ | 20013609 | IN-GR | INGHAM-BLACKRIVER/GREENVALE | IN-GR_Ingham-Black River/Greenvale 66 kV | Loading (MVA) | 1.9138 | 1.9009 | 1.8955 | 1.9143 | 1.9016 | 1.8959 | 1.9092 | 1.8973 | 1.8969 | 1.9091 | 1.8973 | 1.8969 | 1.9087 | 1.8959 | 1.8971
NQ | 20013609 | IN-GR | INGHAM-BLACKRIVER/GREENVALE | IN-GR_Ingham-Black River/Greenvale 66 kV | Loading (MW) | 0.63863 | 0.70488 | 0.45397 | 0.63863 | 0.70489 | 0.45398 | 0.63862 | 0.70208 | 0.39758 | 0.63862 | 0.70208 | 0.39758 | 0.63861 | 0.66972 | 0.39564
NQ | 20013609 | IN-GR | INGHAM-BLACKRIVER/GREENVALE | IN-GR_Ingham-Black River/Greenvale 66 kV | Power Factor | 0.3337 | 0.37081 | 0.2395 | 0.33361 | 0.37069 | 0.23945 | 0.3345 | 0.37003 | 0.20959 | 0.3345 | 0.37005 | 0.20959 | 0.33458 | 0.35325 | 0.20854
NQ | 20013609 | IN-GR | INGHAM-BLACKRIVER/GREENVALE | IN-GR_Ingham-Black River/Greenvale 66 kV | Rating (A) | 69 | 87 | 82 | 69 | 87 | 82 | 69 | 87 | 82 | 69 | 87 | 82 | 69 | 87 | 82
NQ | 20013609 | IN-GR | INGHAM-BLACKRIVER/GREENVALE | IN-GR_Ingham-Black River/Greenvale 66 kV | Time | 15:30 | 17:00 | 22:30 | 15:30 | 17:00 | 22:30 | 15:30 | 19:00 | 2:00 | 15:30 | 19:00 | 2:00 | 15:30 | 18:30 | 6:00
NQ | 20013609 | IN-GR | INGHAM-BLACKRIVER/GREENVALE | IN-GR_Ingham-Black River/Greenvale 66 kV | Voltage at Constrained Conductor | 69.6984 | 69.2678 | 69.661 | 69.709 | 69.2803 | 69.6682 | 69.6108 | 69.2067 | 69.7246 | 69.6104 | 69.2055 | 69.7246 | 69.6021 | 69.2739 | 69.7287
NQ | 20013610 | MR-CR-1 | MILLCHESTER-CAPERIVER | MR-CR-1_Millchester-Cape River 1 66 kV | % of Rated A | 48.0821 | 33.8478 | 27.7695 | 47.2413 | 33.169 | 27.7466 | 55.9453 | 40.6533 | 30.3082 | 55.9881 | 40.6905 | 30.3225 | 56.617 | 41.1405 | 30.7199
NQ | 20013610 | MR-CR-1 | MILLCHESTER-CAPERIVER | MR-CR-1_Millchester-Cape River 1 66 kV | Limiting Line Name | TR_LINE 165123_1 | TR_LINE 165123_1 | TR_LINE 165123_1 | TR_LINE 165123_1 | TR_LINE 165123_1 | TR_LINE 165123_1 | TR_LINE 165123_1 | TR_LINE 165123_1 | TR_LINE 165123_1 | TR_LINE 165123_1 | TR_LINE 165123_1 | TR_LINE 165123_1 | TR_LINE 165123_1 | TR_LINE 165123_1 | TR_LINE 165123_1
NQ | 20013610 | MR-CR-1 | MILLCHESTER-CAPERIVER | MR-CR-1_Millchester-Cape River 1 66 kV | Loading (A) | 74.5273 | 77.5114 | 62.759 | 73.224 | 75.9571 | 62.7074 | 86.7153 | 93.0962 | 68.4964 | 86.7815 | 93.1812 | 68.5289 | 87.7564 | 94.2118 | 69.4269
NQ | 20013610 | MR-CR-1 | MILLCHESTER-CAPERIVER | MR-CR-1_Millchester-Cape River 1 66 kV | Loading (MVA) | 8.7468 | 9.0892 | 7.3605 | 8.5984 | 8.9103 | 7.3392 | 10.1776 | 10.9303 | 8.0608 | 10.1836 | 10.9381 | 8.0635 | 10.2935 | 11.0428 | 8.1654
NQ | 20013610 | MR-CR-1 | MILLCHESTER-CAPERIVER | MR-CR-1_Millchester-Cape River 1 66 kV | Loading (MW) | 8.5554 | 8.8632 | 7.1803 | 8.4155 | 8.7019 | 7.1353 | 9.9079 | 10.619 | 7.908 | 9.9103 | 10.6225 | 7.9092 | 10.0063 | 10.6948 | 8.0054
NQ | 20013610 | MR-CR-1 | MILLCHESTER-CAPERIVER | MR-CR-1_Millchester-Cape River 1 66 kV | Power Factor | 0.97812 | 0.97513 | 0.97552 | 0.97874 | 0.97662 | 0.97222 | 0.97351 | 0.97152 | 0.98104 | 0.97317 | 0.97114 | 0.98086 | 0.9721 | 0.96848 | 0.98041
NQ | 20013610 | MR-CR-1 | MILLCHESTER-CAPERIVER | MR-CR-1_Millchester-Cape River 1 66 kV | Rating (A) | 155 | 229 | 226 | 155 | 229 | 226 | 155 | 229 | 226 | 155 | 229 | 226 | 155 | 229 | 226
NQ | 20013610 | MR-CR-1 | MILLCHESTER-CAPERIVER | MR-CR-1_Millchester-Cape River 1 66 kV | Time | 15:30 | 19:00 | 8:30 | 15:30 | 19:00 | 8:30 | 15:30 | 18:30 | 8:30 | 15:30 | 18:30 | 8:30 | 15:30 | 19:00 | 8:30
NQ | 20013610 | MR-CR-1 | MILLCHESTER-CAPERIVER | MR-CR-1_Millchester-Cape River 1 66 kV | Voltage at Constrained Conductor | 67.7597 | 67.702 | 67.7126 | 67.7955 | 67.7272 | 67.5727 | 67.7622 | 67.7857 | 67.9441 | 67.7505 | 67.7725 | 67.9345 | 67.7212 | 67.6728 | 67.9026
NQ | 20013612 | WO-CT-1 | Woodstock-Charters Towers | WO-CT-1_Woodstock-CHTO No 1 66 kV | % of Rated A | 32.8851 | 29.9614 | 30.8427 | 32.5091 | 29.5734 | 30.5013 | 35.5062 | 33.234 | 33.4803 | 35.4807 | 33.1967 | 33.4373 | 35.534 | 33.2 | 32.9942
NQ | 20013612 | WO-CT-1 | Woodstock-Charters Towers | WO-CT-1_Woodstock-CHTO No 1 66 kV | Limiting Line Name | TR_LINE 32389_1 | TR_LINE 32389_1 | TR_LINE 46566_1 | TR_LINE 32389_1 | TR_LINE 32389_1 | TR_LINE 32389_1 | TR_LINE 32389_1 | TR_LINE 46566_1 | TR_LINE 46566_1 | TR_LINE 32389_1 | TR_LINE 46566_1 | TR_LINE 46566_1 | TR_LINE 32389_1 | TR_LINE 46566_1 | TR_LINE 46566_1
NQ | 20013612 | WO-CT-1 | Woodstock-Charters Towers | WO-CT-1_Woodstock-CHTO No 1 66 kV | Loading (A) | 62.1529 | 61.7206 | 51.8157 | 61.4422 | 60.9211 | 56.7323 | 67.1068 | 62.8122 | 56.2469 | 67.0585 | 62.7418 | 56.1747 | 67.1592 | 62.7481 | 55.4302
NQ | 20013612 | WO-CT-1 | Woodstock-Charters Towers | WO-CT-1_Woodstock-CHTO No 1 66 kV | Loading (MVA) | 7.33 | 7.263 | 6.0575 | 7.2478 | 7.1702 | 6.7046 | 7.921 | 7.3368 | 6.5824 | 7.9141 | 7.327 | 6.5729 | 7.9214 | 7.3237 | 6.4652
NQ | 20013612 | WO-CT-1 | Woodstock-Charters Towers | WO-CT-1_Woodstock-CHTO No 1 66 kV | Loading (MW) | 5.7111 | 5.5975 | 4.763 | 5.6343 | 5.5174 | 5.2701 | 6.1937 | 5.622 | 4.93 | 6.1908 | 5.6165 | 4.9245 | 6.19 | 5.6009 | 4.9576
NQ | 20013612 | WO-CT-1 | Woodstock-Charters Towers | WO-CT-1_Woodstock-CHTO No 1 66 kV | Power Factor | 0.77915 | 0.77069 | 0.78631 | 0.77738 | 0.76949 | 0.78604 | 0.78193 | 0.76627 | 0.74896 | 0.78224 | 0.76655 | 0.74921 | 0.78143 | 0.76476 | 0.76681
NQ | 20013612 | WO-CT-1 | Woodstock-Charters Towers | WO-CT-1_Woodstock-CHTO No 1 66 kV | Rating (A) | 189 | 206 | 168 | 189 | 206 | 186 | 189 | 189 | 168 | 189 | 189 | 168 | 189 | 189 | 168
NQ | 20013612 | WO-CT-1 | Woodstock-Charters Towers | WO-CT-1_Woodstock-CHTO No 1 66 kV | Time | 15:30 | 19:00 | 22:00 | 15:30 | 19:00 | 22:00 | 15:30 | 18:30 | 22:00 | 15:30 | 18:30 | 22:00 | 15:30 | 18:30 | 22:00
NQ | 20013612 | WO-CT-1 | Woodstock-Charters Towers | WO-CT-1_Woodstock-CHTO No 1 66 kV | Voltage at Constrained Conductor | 68.0896 | 67.9401 | 67.4948 | 68.1051 | 67.9522 | 68.2305 | 68.1479 | 67.4379 | 67.5653 | 68.138 | 67.4234 | 67.555 | 68.0982 | 67.3862 | 67.3407
NQ | 20013621 | MF-TP-2 | Max Fulton-TPSS No.02 | MF-TP-2_Max Fulton-TOPO No 2 66 kV | % of Rated A | 24.677 | 20.9988 | 22.2058 | 26.5368 | 22.5488 | 23.7964 | 26.6299 | 22.3826 | 23.8929 | 26.6307 | 22.3842 | 23.8937 | 27.0418 | 22.7245 | 24.2456
NQ | 20013621 | MF-TP-2 | Max Fulton-TPSS No.02 | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Limiting Line Name | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1
NQ | 20013621 | MF-TP-2 | Max Fulton-TPSS No.02 | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Loading (A) | 63.6667 | 61.9465 | 60.3997 | 68.4651 | 66.5188 | 64.7263 | 68.7051 | 66.0287 | 64.9887 | 68.7073 | 66.0333 | 64.9908 | 69.7678 | 67.0372 | 65.9482
NQ | 20013621 | MF-TP-2 | Max Fulton-TPSS No.02 | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Loading (MVA) | 7.6102 | 7.3696 | 7.2198 | 8.1818 | 7.9118 | 7.7352 | 8.1589 | 7.8899 | 7.7182 | 8.1587 | 7.8894 | 7.7179 | 8.2822 | 8.0062 | 7.8292
NQ | 20013621 | MF-TP-2 | Max Fulton-TPSS No.02 | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Loading (MW) | 6.8934 | 6.6184 | 6.4034 | 7.5877 | 7.2849 | 7.0482 | 7.538 | 7.2373 | 7.002 | 7.538 | 7.2373 | 7.002 | 7.6868 | 7.3802 | 7.1402
NQ | 20013621 | MF-TP-2 | Max Fulton-TPSS No.02 | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Power Factor | 0.90581 | 0.89806 | 0.88692 | 0.92739 | 0.92077 | 0.91119 | 0.9239 | 0.91729 | 0.90722 | 0.92392 | 0.91735 | 0.90725 | 0.92812 | 0.92181 | 0.912
NQ | 20013621 | MF-TP-2 | Max Fulton-TPSS No.02 | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Rating (A) | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272
NQ | 20013621 | MF-TP-2 | Max Fulton-TPSS No.02 | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Time | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30
NQ | 20013621 | MF-TP-2 | Max Fulton-TPSS No.02 | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Voltage at Constrained Conductor | 69.0121 | 68.686 | 69.0127 | 68.9955 | 68.6704 | 68.9966 | 68.5619 | 68.9889 | 68.5671 | 68.5578 | 68.9797 | 68.5625 | 68.5374 | 68.9525 | 68.5416
NQ | 20013622 | ST-TS-1 | TownsvilleSouth-Stuart No.1 (607) | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | % of Rated A | 48.134 | 45.9436 | 41.3777 | 48.1341 | 45.9083 | 41.354 | 44.8071 | 42.8742 | 39.1912 | 45.0423 | 43.1301 | 39.4168 | 45.6027 | 43.6954 | 39.9029
NQ | 20013622 | ST-TS-1 | TownsvilleSouth-Stuart No.1 (607) | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Limiting Line Name | TR_LINE 157896_1 | TR_LINE 157896_1 | TR_LINE 157896_1 | TR_LINE 157896_1 | TR_LINE 157896_1 | TR_LINE 157896_1 | TR_LINE 157896_1 | TR_LINE 157896_1 | TR_LINE 157896_1 | TR_LINE 157896_1 | TR_LINE 157896_1 | TR_LINE 157896_1 | TR_LINE 157896_1 | TR_LINE 157896_1 | TR_LINE 157896_1
NQ | 20013622 | ST-TS-1 | TownsvilleSouth-Stuart No.1 (607) | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Loading (A) | 443.3142 | 461.2733 | 379.8476 | 443.3154 | 460.9195 | 379.6295 | 412.6735 | 430.4568 | 359.775 | 414.8393 | 433.0257 | 361.8459 | 420.0005 | 438.7015 | 366.3084
NQ | 20013622 | ST-TS-1 | TownsvilleSouth-Stuart No.1 (607) | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Loading (MVA) | 52.6842 | 54.883 | 45.3125 | 52.6814 | 54.8418 | 45.2869 | 49.353 | 51.4353 | 42.8063 | 49.6048 | 51.7327 | 43.0472 | 50.2044 | 52.3897 | 43.5636
NQ | 20013622 | ST-TS-1 | TownsvilleSouth-Stuart No.1 (607) | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Loading (MW) | 52.571 | 54.685 | 44.9952 | 52.5695 | 54.6415 | 44.9671 | 48.6319 | 50.8247 | 42.681 | 48.9022 | 51.1427 | 42.9283 | 49.5433 | 51.8416 | 43.4613
NQ | 20013622 | ST-TS-1 | TownsvilleSouth-Stuart No.1 (607) | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Power Factor | 0.99785 | 0.99639 | 0.993 | 0.99788 | 0.99635 | 0.99294 | 0.98539 | 0.98813 | 0.99707 | 0.98584 | 0.98859 | 0.99724 | 0.98683 | 0.98954 | 0.99765
NQ | 20013622 | ST-TS-1 | TownsvilleSouth-Stuart No.1 (607) | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Rating (A) | 921 | 1003.9999 | 918 | 921 | 1003.9999 | 918 | 921 | 1003.9999 | 918 | 921 | 1003.9999 | 918 | 921 | 1003.9999 | 918
NQ | 20013622 | ST-TS-1 | TownsvilleSouth-Stuart No.1 (607) | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Time | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00
NQ | 20013622 | ST-TS-1 | TownsvilleSouth-Stuart No.1 (607) | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Voltage at Constrained Conductor | 68.6132 | 68.694 | 68.8728 | 68.6094 | 68.6951 | 68.8734 | 69.0473 | 68.9877 | 68.6935 | 69.0372 | 68.9748 | 68.6848 | 69.0131 | 68.9471 | 68.6619
NQ | 20013640 | AY-EA-1 | AYR-EASTAYR | AY-EA-1_Ayr - East Ayr No 1 66 kV | % of Rated A | 19.2667 | 16.5971 | 20.0351 | 19.3408 | 16.5578 | 20.0146 | 19.2285 | 16.3858 | 20.1903 | 19.2492 | 16.4338 | 20.2132 | 19.3418 | 16.5919 | 20.0233
NQ | 20013640 | AY-EA-1 | AYR-EASTAYR | AY-EA-1_Ayr - East Ayr No 1 66 kV | Limiting Line Name | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1
NQ | 20013640 | AY-EA-1 | AYR-EASTAYR | AY-EA-1_Ayr - East Ayr No 1 66 kV | Loading (A) | 49.9007 | 49.1273 | 54.8962 | 50.0926 | 49.0112 | 54.8401 | 49.8019 | 48.502 | 55.3215 | 49.8556 | 48.6439 | 55.3841 | 50.0952 | 49.112 | 54.8637
NQ | 20013640 | AY-EA-1 | AYR-EASTAYR | AY-EA-1_Ayr - East Ayr No 1 66 kV | Loading (MVA) | 5.6719 | 5.5712 | 6.2425 | 5.6314 | 5.5632 | 6.2411 | 5.6001 | 5.5076 | 6.2138 | 5.6053 | 5.5226 | 6.2199 | 5.6298 | 5.5725 | 6.2418
NQ | 20013640 | AY-EA-1 | AYR-EASTAYR | AY-EA-1_Ayr - East Ayr No 1 66 kV | Loading (MW) | 2.8717 | 3.221 | 3.6227 | 2.899 | 3.2188 | 3.626 | 2.8627 | 3.1599 | 3.5871 | 2.8572 | 3.1632 | 3.5845 | 2.8746 | 3.2052 | 3.6082
NQ | 20013640 | AY-EA-1 | AYR-EASTAYR | AY-EA-1_Ayr - East Ayr No 1 66 kV | Power Factor | 0.5063 | 0.57815 | 0.58033 | 0.51479 | 0.57859 | 0.58099 | 0.51119 | 0.57374 | 0.57728 | 0.50973 | 0.57278 | 0.5763 | 0.51061 | 0.57518 | 0.57806
NQ | 20013640 | AY-EA-1 | AYR-EASTAYR | AY-EA-1_Ayr - East Ayr No 1 66 kV | Rating (A) | 259 | 296 | 274 | 259 | 296 | 274 | 259 | 296 | 274 | 259 | 296 | 274 | 259 | 296 | 274
NQ | 20013640 | AY-EA-1 | AYR-EASTAYR | AY-EA-1_Ayr - East Ayr No 1 66 kV | Time | 11:00 | 21:00 | 8:00 | 10:30 | 21:00 | 8:00 | 10:30 | 21:00 | 8:00 | 10:30 | 21:00 | 8:00 | 10:30 | 21:00 | 8:00
NQ | 20013640 | AY-EA-1 | AYR-EASTAYR | AY-EA-1_Ayr - East Ayr No 1 66 kV | Voltage at Constrained Conductor | 65.6239 | 65.474 | 65.6528 | 64.9059 | 65.5346 | 65.7053 | 64.9215 | 65.5606 | 64.8485 | 64.9118 | 65.5468 | 64.8393 | 64.8844 | 65.5088 | 65.6848
NQ | 20013651 | AV-GA-1 | GARBUTT-AITKENVALE | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | % of Rated A | 39.8482 | 37.2472 | 29.3754 | 39.2029 | 36.6541 | 28.9237 | 37.9907 | 35.4536 | 29.4218 | 37.8942 | 35.3741 | 29.3603 | 37.9953 | 35.4899 | 29.4354
NQ | 20013651 | AV-GA-1 | GARBUTT-AITKENVALE | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Limiting Line Name | TR_LINE 58723_1 | TR_LINE 58723_1 | TR_LINE 58723_1 | TR_LINE 58723_1 | TR_LINE 58723_1 | TR_LINE 58723_1 | TR_LINE 34618_1 | TR_LINE 34618_1 | TR_LINE 34618_1 | TR_LINE 34618_1 | TR_LINE 34618_1 | TR_LINE 34618_1 | TR_LINE 34618_1 | TR_LINE 34618_1 | TR_LINE 34618_1
NQ | 20013651 | AV-GA-1 | GARBUTT-AITKENVALE | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Loading (A) | 183.3005 | 192.194 | 139.2383 | 180.3319 | 189.1335 | 137.0973 | 174.7573 | 182.9403 | 139.4591 | 174.3134 | 182.5306 | 139.168 | 174.7783 | 183.1279 | 139.5239
NQ | 20013651 | AV-GA-1 | GARBUTT-AITKENVALE | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Loading (MVA) | 21.6402 | 22.6675 | 16.5761 | 21.2927 | 22.3113 | 16.3236 | 20.8301 | 21.7898 | 16.4646 | 20.7734 | 21.736 | 16.4275 | 20.8183 | 21.7959 | 16.4629
NQ | 20013651 | AV-GA-1 | GARBUTT-AITKENVALE | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Loading (MW) | 21.6104 | 22.6292 | 16.568 | 21.2609 | 22.275 | 16.3161 | 20.4434 | 21.4562 | 16.0273 | 20.3839 | 21.4001 | 15.988 | 20.4303 | 21.4636 | 16.0262
NQ | 20013651 | AV-GA-1 | GARBUTT-AITKENVALE | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Power Factor | 0.99862 | 0.99831 | 0.99951 | 0.99851 | 0.99837 | 0.99954 | 0.98143 | 0.98469 | 0.97344 | 0.98125 | 0.98455 | 0.97324 | 0.98136 | 0.98476 | 0.97347
NQ | 20013651 | AV-GA-1 | GARBUTT-AITKENVALE | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Rating (A) | 460 | 516 | 474 | 460 | 516 | 474 | 460 | 516 | 474 | 460 | 516 | 474 | 460 | 516 | 474
NQ | 20013651 | AV-GA-1 | GARBUTT-AITKENVALE | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Time | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00
NQ | 20013651 | AV-GA-1 | GARBUTT-AITKENVALE | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Voltage at Constrained Conductor | 68.1613 | 68.0932 | 68.7324 | 68.1706 | 68.1077 | 68.7428 | 68.8169 | 68.7674 | 68.1621 | 68.8043 | 68.7517 | 68.1509 | 68.7697 | 68.7161 | 68.1236
NQ | 20013655 | DG-RM-1 | DANGLEESON-RASMUSSEN | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | % of Rated A | 13.2952 | 14.9681 | 9.4384 | 13.5117 | 15.0796 | 9.5266 | 16.2525 | 14.649 | 7.686 | 16.5501 | 14.8967 | 7.9043 | 16.9936 | 15.2779 | 8.2652
NQ | 20013655 | DG-RM-1 | DANGLEESON-RASMUSSEN | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Limiting Line Name | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1
NQ | 20013655 | DG-RM-1 | DANGLEESON-RASMUSSEN | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Loading (A) | 33.3709 | 57.6272 | 35.8658 | 33.9144 | 58.0565 | 36.2011 | 40.7938 | 56.3988 | 29.2069 | 41.5408 | 57.3522 | 30.0364 | 42.654 | 58.8201 | 31.4079
NQ | 20013655 | DG-RM-1 | DANGLEESON-RASMUSSEN | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Loading (MVA) | 3.944 | 6.8398 | 4.2634 | 4.0085 | 6.8916 | 4.3036 | 4.8831 | 6.7449 | 3.4533 | 4.9716 | 6.8572 | 3.5508 | 5.1026 | 7.0294 | 3.7115
NQ | 20013655 | DG-RM-1 | DANGLEESON-RASMUSSEN | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Loading (MW) | 3.7832 | 6.1398 | 4.0818 | 3.8457 | 6.1886 | 4.12 | 3.5292 | 5.5574 | 3.4081 | 3.6312 | 5.6762 | 3.5035 | 3.7842 | 5.8583 | 3.6596
NQ | 20013655 | DG-RM-1 | DANGLEESON-RASMUSSEN | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Power Factor | 0.95921 | 0.89766 | 0.95741 | 0.95938 | 0.898 | 0.95733 | 0.72272 | 0.82394 | 0.98691 | 0.73039 | 0.82777 | 0.98668 | 0.74162 | 0.83339 | 0.986
NQ | 20013655 | DG-RM-1 | DANGLEESON-RASMUSSEN | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Rating (A) | 251 | 385 | 380 | 251 | 385 | 380 | 251 | 385 | 380 | 251 | 385 | 380 | 251 | 385 | 380
NQ | 20013655 | DG-RM-1 | DANGLEESON-RASMUSSEN | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Time | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00
NQ | 20013655 | DG-RM-1 | DANGLEESON-RASMUSSEN | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Voltage at Constrained Conductor | 68.2359 | 68.5257 | 68.6296 | 68.2393 | 68.5339 | 68.6354 | 69.1103 | 69.0467 | 68.2635 | 69.0972 | 69.0299 | 68.252 | 69.0669 | 68.9974 | 68.2267
NQ | 20013660 | MF-TP-1 | Max Fulton-TPSS No.01 | MF-TP-1_Max Fulton-TOPO No 1 66 kV | % of Rated A | 22.6072 | 19.0661 | 19.9022 | 24.9189 | 21.0149 | 21.9359 | 24.9147 | 20.7772 | 21.9307 | 24.9162 | 20.7801 | 21.9322 | 25.4168 | 21.2038 | 22.3773
NQ | 20013660 | MF-TP-1 | Max Fulton-TPSS No.01 | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Limiting Line Name | TR_LINE 31651_1 | TR_LINE 31651_1 | TR_LINE 31651_1 | TR_LINE 31651_1 | TR_LINE 31651_1 | TR_LINE 31651_1 | TR_LINE 31651_1 | TR_LINE 31651_1 | TR_LINE 31651_1 | TR_LINE 31651_1 | TR_LINE 31651_1 | TR_LINE 31651_1 | TR_LINE 31651_1 | TR_LINE 31651_1 | TR_LINE 31651_1
NQ | 20013660 | MF-TP-1 | Max Fulton-TPSS No.01 | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Loading (A) | 58.3251 | 56.2436 | 54.1326 | 64.2892 | 61.9925 | 59.6641 | 64.2783 | 61.2913 | 59.6501 | 64.2822 | 61.2997 | 59.6542 | 65.5738 | 62.5495 | 60.8647
NQ | 20013660 | MF-TP-1 | Max Fulton-TPSS No.01 | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Loading (MVA) | 6.9679 | 6.6876 | 6.4672 | 7.6784 | 7.3693 | 7.1263 | 7.6288 | 7.3197 | 7.0802 | 7.6288 | 7.3198 | 7.0802 | 7.7797 | 7.466 | 7.2216
NQ | 20013660 | MF-TP-1 | Max Fulton-TPSS No.01 | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Loading (MW) | 6.8877 | 6.6127 | 6.3976 | 7.582 | 7.2793 | 7.0425 | 7.5325 | 7.2316 | 6.9965 | 7.5325 | 7.2316 | 6.9965 | 7.681 | 7.3745 | 7.1347
NQ | 20013660 | MF-TP-1 | Max Fulton-TPSS No.01 | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Power Factor | 0.98848 | 0.9888 | 0.98924 | 0.98745 | 0.98779 | 0.98824 | 0.98738 | 0.98796 | 0.98818 | 0.98738 | 0.98796 | 0.98818 | 0.98732 | 0.98774 | 0.98796
NQ | 20013660 | MF-TP-1 | Max Fulton-TPSS No.01 | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Rating (A) | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272
NQ | 20013660 | MF-TP-1 | Max Fulton-TPSS No.01 | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Time | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30
NQ | 20013660 | MF-TP-1 | Max Fulton-TPSS No.01 | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Voltage at Constrained Conductor | 68.9745 | 68.6491 | 68.9763 | 68.956 | 68.6317 | 68.9586 | 68.522 | 68.9504 | 68.5286 | 68.518 | 68.9411 | 68.524 | 68.4972 | 68.9136 | 68.5028
NQ | 20013662 | ST-TS-2 | TownsvilleSouth-Stuart No.2 (608) | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | % of Rated A | 48.911 | 46.6852 | 42.0457 | 48.9111 | 46.6494 | 42.0215 | 45.5304 | 43.5663 | 39.8238 | 45.7694 | 43.8263 | 40.0531 | 46.3388 | 44.4007 | 40.547
NQ | 20013662 | ST-TS-2 | TownsvilleSouth-Stuart No.2 (608) | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Limiting Line Name | TR_LINE 157898_1 | TR_LINE 157898_1 | TR_LINE 157898_1 | TR_LINE 157898_1 | TR_LINE 157898_1 | TR_LINE 157898_1 | TR_LINE 157898_1 | TR_LINE 157898_1 | TR_LINE 157898_1 | TR_LINE 157898_1 | TR_LINE 157898_1 | TR_LINE 157898_1 | TR_LINE 157898_1 | TR_LINE 157898_1 | TR_LINE 157898_1
NQ | 20013662 | ST-TS-2 | TownsvilleSouth-Stuart No.2 (608) | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Loading (A) | 450.4704 | 468.7194 | 385.9793 | 450.4715 | 468.3598 | 385.7576 | 419.3351 | 437.4054 | 365.5827 | 421.5358 | 440.0158 | 367.687 | 426.7804 | 445.7831 | 372.2215
NQ | 20013662 | ST-TS-2 | TownsvilleSouth-Stuart No.2 (608) | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Loading (MVA) | 53.5369 | 55.7713 | 46.0455 | 53.5341 | 55.7295 | 46.0195 | 50.1514 | 52.2675 | 43.4988 | 50.4072 | 52.5697 | 43.7436 | 51.0166 | 53.2373 | 44.2683
NQ | 20013662 | ST-TS-2 | TownsvilleSouth-Stuart No.2 (608) | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Loading (MW) | 53.4495 | 55.6081 | 45.7672 | 53.4479 | 55.564 | 45.7388 | 49.4888 | 51.7128 | 43.3979 | 49.7626 | 52.035 | 43.6485 | 50.4125 | 52.7432 | 44.1884
NQ | 20013662 | ST-TS-2 | TownsvilleSouth-Stuart No.2 (608) | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Power Factor | 0.99837 | 0.99707 | 0.99396 | 0.99839 | 0.99703 | 0.9939 | 0.98679 | 0.98939 | 0.99768 | 0.98721 | 0.98983 | 0.99783 | 0.98816 | 0.99072 | 0.99819
NQ | 20013662 | ST-TS-2 | TownsvilleSouth-Stuart No.2 (608) | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Rating (A) | 921 | 1003.9999 | 918 | 921 | 1003.9999 | 918 | 921 | 1003.9999 | 918 | 921 | 1003.9999 | 918 | 921 | 1003.9999 | 918
NQ | 20013662 | ST-TS-2 | TownsvilleSouth-Stuart No.2 (608) | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Time | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00
NQ | 20013662 | ST-TS-2 | TownsvilleSouth-Stuart No.2 (608) | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Voltage at Constrained Conductor | 68.6162 | 68.697 | 68.8751 | 68.6123 | 68.6981 | 68.8758 | 69.0496 | 68.9901 | 68.6959 | 69.0395 | 68.9773 | 68.6872 | 69.0155 | 68.9497 | 68.6643
NQ | 25267806 | DG-PA-1 | DANGLEESON-PETERARLETT | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | % of Rated A | 16.0502 | 16.631 | 14.7872 | 15.9855 | 14.2894 | 14.758 | 19.1714 | 17.6847 | 11.9702 | 19.2321 | 17.7281 | 12.0633 | 19.4614 | 17.9331 | 12.3432
NQ | 25267806 | DG-PA-1 | DANGLEESON-PETERARLETT | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Limiting Line Name | TR_LINE 32461_1 | TR_LINE 32461_1 | TR_LINE 32461_1 | TR_LINE 32461_1 | TR_LINE 32461_1 | TR_LINE 32461_1 | TR_LINE 32461_1 | TR_LINE 32461_1 | TR_LINE 32461_1 | TR_LINE 32461_1 | TR_LINE 32461_1 | TR_LINE 32461_1 | TR_LINE 32461_1 | TR_LINE 32461_1 | TR_LINE 32461_1
NQ | 25267806 | DG-PA-1 | DANGLEESON-PETERARLETT | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Loading (A) | 88.4366 | 96.7924 | 77.4847 | 88.0803 | 83.1641 | 77.3319 | 105.6254 | 102.9157 | 62.724 | 105.9596 | 103.1681 | 63.2116 | 107.223 | 104.3613 | 64.6784
NQ | 25267806 | DG-PA-1 | DANGLEESON-PETERARLETT | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Loading (MVA) | 10.4609 | 11.4309 | 9.1966 | 10.4203 | 9.8245 | 9.1793 | 12.5679 | 12.2263 | 7.4112 | 12.6051 | 12.2532 | 7.4679 | 12.749 | 12.3883 | 7.6387
NQ | 25267806 | DG-PA-1 | DANGLEESON-PETERARLETT | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Loading (MW) | 8.3686 | 7.2032 | 7.1652 | 8.3213 | 5.516 | 7.138 | 6.9493 | 6.4381 | 5.8809 | 6.9819 | 6.4618 | 5.9315 | 7.1556 | 6.6283 | 6.1063
NQ | 25267806 | DG-PA-1 | DANGLEESON-PETERARLETT | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Power Factor | 0.79999 | 0.63015 | 0.77912 | 0.79857 | 0.56145 | 0.77761 | 0.55294 | 0.52658 | 0.79351 | 0.5539 | 0.52735 | 0.79427 | 0.56127 | 0.53504 | 0.7994
NQ | 25267806 | DG-PA-1 | DANGLEESON-PETERARLETT | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Rating (A) | 551 | 582 | 524 | 551 | 582 | 524 | 551 | 582 | 524 | 551 | 582 | 524 | 551 | 582 | 524
NQ | 25267806 | DG-PA-1 | DANGLEESON-PETERARLETT | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Time | 14:30 | 18:00 | 8:30 | 14:30 | 19:00 | 8:30 | 16:30 | 17:30 | 8:30 | 16:30 | 17:30 | 8:30 | 16:30 | 17:30 | 8:30
NQ | 25267806 | DG-PA-1 | DANGLEESON-PETERARLETT | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Voltage at Constrained Conductor | 68.293 | 68.1834 | 68.5251 | 68.3031 | 68.2049 | 68.5316 | 68.6966 | 68.5887 | 68.2177 | 68.6823 | 68.5718 | 68.2093 | 68.6482 | 68.5351 | 68.1864
NQ | 25267807 | PA-RP-1 | PETERARLETT-ROSSPLAINS | PA-RP-1_Peter Arlett-Ross Plains 66 kV | % of Rated A | 52.4899 | 49.1336 | 46.2973 | 52.3191 | 49.0274 | 46.204 | 55.0579 | 51.4652 | 50.6107 | 55.2653 | 51.6896 | 50.8144 | 55.3461 | 51.81 | 50.8867
NQ | 25267807 | PA-RP-1 | PETERARLETT-ROSSPLAINS | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Limiting Line Name | TR_LINE 32958_1 | TR_LINE 32958_1 | TR_LINE 45760_1 | TR_LINE 32958_1 | TR_LINE 32958_1 | TR_LINE 45760_1 | TR_LINE 45760_1 | TR_LINE 45760_1 | TR_LINE 32958_1 | TR_LINE 45760_1 | TR_LINE 45760_1 | TR_LINE 32958_1 | TR_LINE 45760_1 | TR_LINE 45760_1 | TR_LINE 32958_1
NQ | 25267807 | PA-RP-1 | PETERARLETT-ROSSPLAINS | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Loading (A) | 135.4222 | 144.942 | 125.9286 | 134.9816 | 144.6289 | 125.6749 | 142.0494 | 151.8222 | 137.6578 | 142.5844 | 152.4844 | 138.2118 | 142.793 | 152.8394 | 138.4086
NQ | 25267807 | PA-RP-1 | PETERARLETT-ROSSPLAINS | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Loading (MVA) | 15.9608 | 17.0681 | 14.959 | 15.9094 | 17.0336 | 14.9302 | 16.9325 | 18.0741 | 16.2623 | 16.993 | 18.149 | 16.325 | 17.0097 | 18.1814 | 16.3413
NQ | 25267807 | PA-RP-1 | PETERARLETT-ROSSPLAINS | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Loading (MW) | 15.9467 | 17.0454 | 14.959 | 15.8953 | 17.0128 | 14.9301 | 16.5857 | 17.8049 | 16.2137 | 16.6522 | 17.8853 | 16.2752 | 16.6764 | 17.9267 | 16.2914
NQ | 25267807 | PA-RP-1 | PETERARLETT-ROSSPLAINS | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Power Factor | 0.99912 | 0.99867 | 1 | 0.99911 | 0.99878 | 1 | 0.97952 | 0.98511 | 0.99701 | 0.97994 | 0.98547 | 0.99695 | 0.9804 | 0.98599 | 0.99695
NQ | 25267807 | PA-RP-1 | PETERARLETT-ROSSPLAINS | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Rating (A) | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272
NQ | 25267807 | PA-RP-1 | PETERARLETT-ROSSPLAINS | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Time | 16:30 | 19:30 | 22:00 | 16:30 | 19:30 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00
NQ | 25267807 | PA-RP-1 | PETERARLETT-ROSSPLAINS | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Voltage at Constrained Conductor | 68.0463 | 67.9877 | 68.5833 | 68.0485 | 67.9973 | 68.5891 | 68.8209 | 68.7323 | 68.2057 | 68.8079 | 68.7175 | 68.194 | 68.7748 | 68.6801 | 68.1652
NQ | 25273587 | RI-JC-1 | Richmond-Julia Creek No.1 66kV feeder | RI-JC-1_Richmond-Julia Creek No 1 66 kV | % of Rated A | 7.0069 | 7.1085 | 4.9281 | 6.8388 | 6.91 | 4.8547 | 9.2793 | 10.0189 | 5.9398 | 9.2795 | 10.0192 | 5.9399 | 9.3427 | 10.1077 | 5.8244
NQ | 25273587 | RI-JC-1 | Richmond-Julia Creek No.1 66kV feeder | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Limiting Line Name | TR_LINE 32331_1 | TR_LINE 32331_1 | TR_LINE 32331_1 | TR_LINE 32331_1 | TR_LINE 32331_1 | TR_LINE 32331_1 | TR_LINE 162594_1 | TR_LINE 162594_1 | TR_LINE 32331_1 | TR_LINE 162594_1 | TR_LINE 162594_1 | TR_LINE 32331_1 | TR_LINE 162594_1 | TR_LINE 162594_1 | TR_LINE 32331_1
NQ | 25273587 | RI-JC-1 | Richmond-Julia Creek No.1 66kV feeder | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Loading (A) | 24.8746 | 27.5809 | 20.698 | 24.2776 | 26.811 | 20.3897 | 32.9414 | 38.8732 | 24.947 | 32.9424 | 38.8744 | 24.9474 | 33.1666 | 39.2178 | 24.4623
NQ | 25273587 | RI-JC-1 | Richmond-Julia Creek No.1 66kV feeder | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Loading (MVA) | 2.8557 | 3.1252 | 2.4109 | 2.7922 | 3.0438 | 2.3778 | 3.5459 | 4.0522 | 2.8462 | 3.5459 | 4.0522 | 2.8461 | 3.5513 | 4.0602 | 2.7814
NQ | 25273587 | RI-JC-1 | Richmond-Julia Creek No.1 66kV feeder | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Loading (MW) | 2.5638 | 2.9352 | 1.8486 | 2.4732 | 2.8308 | 1.784 | 3.4498 | 3.9352 | 2.5662 | 3.4498 | 3.9352 | 2.5662 | 3.4218 | 3.9034 | 2.5448
NQ | 25273587 | RI-JC-1 | Richmond-Julia Creek No.1 66kV feeder | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Power Factor | 0.89776 | 0.93921 | 0.76675 | 0.88575 | 0.93002 | 0.75028 | 0.9729 | 0.97112 | 0.90163 | 0.9729 | 0.97112 | 0.90165 | 0.96354 | 0.96139 | 0.91494
NQ | 25273587 | RI-JC-1 | Richmond-Julia Creek No.1 66kV feeder | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Rating (A) | 355 | 388 | 420 | 355 | 388 | 420 | 355 | 388 | 420 | 355 | 388 | 420 | 355 | 388 | 420
NQ | 25273587 | RI-JC-1 | Richmond-Julia Creek No.1 66kV feeder | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Time | 16:00 | 18:30 | 22:00 | 16:00 | 18:30 | 22:00 | 16:00 | 18:30 | 22:00 | 16:00 | 18:30 | 22:00 | 16:00 | 18:30 | 22:00
NQ | 25273587 | RI-JC-1 | Richmond-Julia Creek No.1 66kV feeder | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Voltage at Constrained Conductor | 66.2832 | 65.4198 | 67.2505 | 66.4016 | 65.5456 | 67.3305 | 62.1472 | 60.184 | 65.8692 | 62.1454 | 60.182 | 65.8665 | 61.8195 | 59.7724 | 65.646
NQ | 25275522 | 6266 | BOHLE-BLACK RIVER 2 | 6266_Bohle-Black River No 2 66 kV | % of Rated A | 16.4052 | 20.6348 | 16.2078 | 16.5386 | 20.8061 | 16.3393 | 16.5148 | 20.8759 | 16.6101 | 16.8314 | 21.2894 | 16.9312 | 17.1539 | 21.7118 | 17.2539
NQ | 25275522 | 6266 | BOHLE-BLACK RIVER 2 | 6266_Bohle-Black River No 2 66 kV | Limiting Line Name | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1
NQ | 25275522 | 6266 | BOHLE-BLACK RIVER 2 | 6266_Bohle-Black River No 2 66 kV | Loading (A) | 119.5923 | 161.5681 | 115.0738 | 120.5649 | 162.9096 | 116.0073 | 120.3911 | 163.4559 | 117.9303 | 122.6995 | 166.6937 | 120.2098 | 125.05 | 170.0011 | 122.5007
NQ | 25275522 | 6266 | BOHLE-BLACK RIVER 2 | 6266_Bohle-Black River No 2 66 kV | Loading (MVA) | 13.9954 | 18.8795 | 13.571 | 14.1091 | 19.0364 | 13.6814 | 14.2211 | 19.1905 | 13.7899 | 14.4875 | 19.558 | 14.0506 | 14.7537 | 19.9264 | 14.309
NQ | 25275522 | 6266 | BOHLE-BLACK RIVER 2 | 6266_Bohle-Black River No 2 66 kV | Loading (MW) | 13.9008 | 18.6731 | 13.4857 | 14.0125 | 18.8254 | 13.5942 | 14.1226 | 18.9763 | 13.7003 | 14.3846 | 19.3326 | 13.9564 | 14.6455 | 19.6885 | 14.2098
NQ | 25275522 | 6266 | BOHLE-BLACK RIVER 2 | 6266_Bohle-Black River No 2 66 kV | Power Factor | 0.99324 | 0.98907 | 0.99371 | 0.99315 | 0.98892 | 0.99363 | 0.99307 | 0.98884 | 0.9935 | 0.9929 | 0.98848 | 0.9933 | 0.99266 | 0.98806 | 0.99307
NQ | 25275522 | 6266 | BOHLE-BLACK RIVER 2 | 6266_Bohle-Black River No 2 66 kV | Rating (A) | 729 | 783 | 710 | 729 | 783 | 710 | 729 | 783 | 710 | 729 | 783 | 710 | 729 | 783 | 710
NQ | 25275522 | 6266 | BOHLE-BLACK RIVER 2 | 6266_Bohle-Black River No 2 66 kV | Time | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00
NQ | 25275522 | 6266 | BOHLE-BLACK RIVER 2 | 6266_Bohle-Black River No 2 66 kV | Voltage at Constrained Conductor | 67.5651 | 67.4643 | 68.0887 | 67.5646 | 67.4648 | 68.09 | 68.1992 | 67.7837 | 67.5109 | 68.1693 | 67.74 | 67.483 | 68.1172 | 67.673 | 67.4386
NQ | 25275871 | KA-AY-01 | AYR-KALAMIA | KA-AY-01_Ayr - Kalamia No 1 66 kV | % of Rated A | 13.972 | 17.8978 | 15.0828 | 13.96 | 17.8802 | 15.0695 | 13.6352 | 17.4534 | 14.9138 | 13.9619 | 17.8766 | 15.2723 | 13.9617 | 17.8877 | 15.0759
NQ | 25275871 | KA-AY-01 | AYR-KALAMIA | KA-AY-01_Ayr - Kalamia No 1 66 kV | Limiting Line Name | TR_LINE 32782_1 | TR_LINE 32782_1 | TR_LINE 32782_1 | TR_LINE 32782_1 | TR_LINE 32782_1 | TR_LINE 32782_1 | TR_LINE 32782_1 | TR_LINE 32782_1 | TR_LINE 32782_1 | TR_LINE 32782_1 | TR_LINE 32782_1 | TR_LINE 32782_1 | TR_LINE 32782_1 | TR_LINE 32782_1 | TR_LINE 32782_1
NQ | 25275871 | KA-AY-01 | AYR-KALAMIA | KA-AY-01_Ayr - Kalamia No 1 66 kV | Loading (A) | 27.8043 | 39.9121 | 30.7688 | 27.7805 | 39.8728 | 30.7417 | 27.134 | 38.921 | 30.4241 | 27.7841 | 39.8649 | 31.1554 | 27.7838 | 39.8895 | 30.7548
NQ | 25275871 | KA-AY-01 | AYR-KALAMIA | KA-AY-01_Ayr - Kalamia No 1 66 kV | Loading (MVA) | 3.1425 | 4.4891 | 3.4824 | 3.1424 | 4.4889 | 3.4823 | 3.0711 | 4.3844 | 3.4017 | 3.1438 | 4.4889 | 3.4823 | 3.1424 | 4.489 | 3.4823
NQ | 25275871 | KA-AY-01 | AYR-KALAMIA | KA-AY-01_Ayr - Kalamia No 1 66 kV | Loading (MW) | 2.7527 | 3.907 | 3.0456 | 2.7527 | 3.907 | 3.0456 | 2.6901 | 3.8179 | 2.9763 | 2.7528 | 3.907 | 3.0456 | 2.7527 | 3.907 | 3.0456
NQ | 25275871 | KA-AY-01 | AYR-KALAMIA | KA-AY-01_Ayr - Kalamia No 1 66 kV | Power Factor | 0.87595 | 0.87032 | 0.87458 | 0.87597 | 0.87036 | 0.87461 | 0.87595 | 0.87079 | 0.87494 | 0.87563 | 0.87036 | 0.8746 | 0.87597 | 0.87034 | 0.87459
NQ | 25275871 | KA-AY-01 | AYR-KALAMIA | KA-AY-01_Ayr - Kalamia No 1 66 kV | Rating (A) | 199 | 223 | 204 | 199 | 223 | 204 | 199 | 223 | 204 | 199 | 223 | 204 | 199 | 223 | 204
NQ | 25275871 | KA-AY-01 | AYR-KALAMIA | KA-AY-01_Ayr - Kalamia No 1 66 kV | Time | 11:00 | 21:00 | 22:00 | 11:00 | 21:00 | 22:00 | 11:00 | 21:00 | 22:00 | 11:00 | 21:00 | 22:00 | 11:00 | 21:00 | 22:00
NQ | 25275871 | KA-AY-01 | AYR-KALAMIA | KA-AY-01_Ayr - Kalamia No 1 66 kV | Voltage at Constrained Conductor | 65.2537 | 64.9377 | 65.3438 | 65.3077 | 64.9989 | 65.3994 | 65.346 | 65.038 | 64.553 | 65.3274 | 65.0112 | 64.5317 | 65.3002 | 64.9729 | 65.3725
NQ | 25279916 | BC-IN-1 | Black River - Ingham | BC-IN-1_Black River - Ingham No 1 66 kV | % of Rated A | 27.8507 | 32.8549 | 27.0645 | 27.8509 | 32.8546 | 27.064 | 27.2325 | 32.2602 | 26.9419 | 27.5952 | 32.7149 | 27.3156 | 27.6174 | 32.7493 | 27.3345
NQ | 25279916 | BC-IN-1 | Black River - Ingham | BC-IN-1_Black River - Ingham No 1 66 kV | Limiting Line Name | TR_LINE 128321_1 | TR_LINE 128321_1 | TR_LINE 128321_1 | TR_LINE 128321_1 | TR_LINE 128321_1 | TR_LINE 128321_1 | TR_LINE 128321_1 | TR_LINE 128321_1 | TR_LINE 128321_1 | TR_LINE 128321_1 | TR_LINE 128321_1 | TR_LINE 128321_1 | TR_LINE 128321_1 | TR_LINE 128321_1 | TR_LINE 128321_1
NQ | 25279916 | BC-IN-1 | Black River - Ingham | BC-IN-1_Black River - Ingham No 1 66 kV | Loading (A) | 52.6349 | 67.6776 | 50.3373 | 52.6353 | 67.677 | 50.3362 | 51.4666 | 66.4525 | 50.1092 | 52.152 | 67.3892 | 50.8043 | 52.1939 | 67.4601 | 50.8395
NQ | 25279916 | BC-IN-1 | Black River - Ingham | BC-IN-1_Black River - Ingham No 1 66 kV | Loading (MVA) | 6.1336 | 7.8643 | 5.9127 | 6.1336 | 7.8643 | 5.9127 | 6.0545 | 7.7595 | 5.8359 | 6.1321 | 7.8631 | 5.914 | 6.1323 | 7.8635 | 5.9142
NQ | 25279916 | BC-IN-1 | Black River - Ingham | BC-IN-1_Black River - Ingham No 1 66 kV | Loading (MW) | 6.0827 | 7.7743 | 5.8704 | 6.0827 | 7.7743 | 5.8704 | 6.0059 | 7.6725 | 5.7938 | 6.0823 | 7.7739 | 5.8708 | 6.0824 | 7.774 | 5.8709
NQ | 25279916 | BC-IN-1 | Black River - Ingham | BC-IN-1_Black River - Ingham No 1 66 kV | Power Factor | 0.99171 | 0.98856 | 0.99284 | 0.99171 | 0.98856 | 0.99284 | 0.99197 | 0.98879 | 0.9928 | 0.99188 | 0.98865 | 0.99269 | 0.99185 | 0.98862 | 0.99267
NQ | 25279916 | BC-IN-1 | Black River - Ingham | BC-IN-1_Black River - Ingham No 1 66 kV | Rating (A) | 189 | 206 | 186 | 189 | 206 | 186 | 189 | 206 | 186 | 189 | 206 | 186 | 189 | 206 | 186
NQ | 25279916 | BC-IN-1 | Black River - Ingham | BC-IN-1_Black River - Ingham No 1 66 kV | Time | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00
NQ | 25279916 | BC-IN-1 | Black River - Ingham | BC-IN-1_Black River - Ingham No 1 66 kV | Voltage at Constrained Conductor | 67.2789 | 67.0893 | 67.8169 | 67.2784 | 67.0898 | 67.8182 | 67.9197 | 67.4157 | 67.2402 | 67.8859 | 67.3666 | 67.2083 | 67.8335 | 67.299 | 67.1636
NQ | 82903972 | 7307 | King Creek - Blue Valley 132 kV | 7307_King Creek - Blue Valley 132 kV | % of Rated A | 2.9104 | 2.7899 | 3.0854 | 2.91 | 2.7896 | 3.0852 | 2.91 | 2.7895 | 3.0852 | 2.9101 | 2.7897 | 3.0852 | 2.9103 | 2.79 | 3.0854
NQ | 82903972 | 7307 | King Creek - Blue Valley 132 kV | 7307_King Creek - Blue Valley 132 kV | Limiting Line Name | TR_LINE 62480_1 | TR_LINE 62480_1 | TR_LINE 62480_1 | TR_LINE 62480_1 | TR_LINE 62480_1 | TR_LINE 62480_1 | TR_LINE 62480_1 | TR_LINE 62480_1 | TR_LINE 62480_1 | TR_LINE 62480_1 | TR_LINE 62480_1 | TR_LINE 62480_1 | TR_LINE 62480_1 | TR_LINE 62480_1 | TR_LINE 62480_1
NQ | 82903972 | 7307 | King Creek - Blue Valley 132 kV | 7307_King Creek - Blue Valley 132 kV | Loading (A) | 13.1549 | 13.2801 | 13.1745 | 13.1533 | 13.2785 | 13.1738 | 13.1531 | 13.2782 | 13.1737 | 13.1536 | 13.2789 | 13.174 | 13.1547 | 13.2802 | 13.1748
NQ | 82903972 | 7307 | King Creek - Blue Valley 132 kV | 7307_King Creek - Blue Valley 132 kV | Loading (MVA) | 3.1942 | 3.2221 | 3.2016 | 3.1942 | 3.2221 | 3.2016 | 3.1942 | 3.2221 | 3.2016 | 3.1942 | 3.2221 | 3.2016 | 3.1942 | 3.2221 | 3.2016
NQ | 82903972 | 7307 | King Creek - Blue Valley 132 kV | 7307_King Creek - Blue Valley 132 kV | Loading (MW) | 2.9691 | 2.9948 | 2.9759 | 2.9691 | 2.9948 | 2.9759 | 2.9691 | 2.9948 | 2.9759 | 2.9691 | 2.9948 | 2.9759 | 2.9691 | 2.9948 | 2.9759
NQ | 82903972 | 7307 | King Creek - Blue Valley 132 kV | 7307_King Creek - Blue Valley 132 kV | Power Factor | 0.92952 | 0.92946 | 0.92952 | 0.92952 | 0.92946 | 0.92952 | 0.92952 | 0.92946 | 0.92952 | 0.92952 | 0.92946 | 0.92952 | 0.92952 | 0.92946 | 0.92951
NQ | 82903972 | 7307 | King Creek - Blue Valley 132 kV | 7307_King Creek - Blue Valley 132 kV | Rating (A) | 452 | 476 | 427 | 452 | 476 | 427 | 452 | 476 | 427 | 452 | 476 | 427 | 452 | 476 | 427
NQ | 82903972 | 7307 | King Creek - Blue Valley 132 kV | 7307_King Creek - Blue Valley 132 kV | Time | 15:00 | 18:00 | 23:00 | 15:00 | 18:00 | 23:00 | 15:00 | 18:00 | 23:00 | 15:00 | 18:00 | 23:00 | 15:00 | 18:00 | 23:00
NQ | 82903972 | 7307 | King Creek - Blue Valley 132 kV | 7307_King Creek - Blue Valley 132 kV | Voltage at Constrained Conductor | 140.1877 | 140.0813 | 140.3046 | 140.2045 | 140.0973 | 140.3118 | 140.2068 | 140.101 | 140.313 | 140.202 | 140.0939 | 140.3101 | 140.19 | 140.0804 | 140.3014
NQ | 82908830 | 7308 | Stony Creek - Havilah 132 kV | 7308_Stony Creek - Havilah 132 kV | % of Rated A | 1.6864 | 0.90799 | 1.902 | 1.6862 | 0.90811 | 1.9018 | 1.6862 | 0.90809 | 1.9019 | 1.6863 | 0.90805 | 1.9019 | 1.6864 | 0.90796 | 1.902
NQ | 82908830 | 7308 | Stony Creek - Havilah 132 kV | 7308_Stony Creek - Havilah 132 kV | Limiting Line Name | TR_LINE 67638_1 | TR_LINE 67629_1 | TR_LINE 67638_1 | TR_LINE 67638_1 | TR_LINE 67629_1 | TR_LINE 67638_1 | TR_LINE 67638_1 | TR_LINE 67629_1 | TR_LINE 67638_1 | TR_LINE 67638_1 | TR_LINE 67629_1 | TR_LINE 67638_1 | TR_LINE 67638_1 | TR_LINE 67629_1 | TR_LINE 67638_1
NQ | 82908830 | 7308 | Stony Creek - Havilah 132 kV | 7308_Stony Creek - Havilah 132 kV | Loading (A) | 7.3696 | 4.0496 | 7.4369 | 7.3688 | 4.0502 | 7.4362 | 7.3689 | 4.0501 | 7.4364 | 7.3691 | 4.0499 | 7.4366 | 7.3696 | 4.0495 | 7.4368
NQ | 82908830 | 7308 | Stony Creek - Havilah 132 kV | 7308_Stony Creek - Havilah 132 kV | Loading (MVA) | 1.7886 | 0.98285 | 1.8049 | 1.7886 | 0.9831 | 1.8049 | 1.7886 | 0.98307 | 1.8049 | 1.7886 | 0.98298 | 1.8049 | 1.7886 | 0.98279 | 1.8049
NQ | 82908830 | 7308 | Stony Creek - Havilah 132 kV | 7308_Stony Creek - Havilah 132 kV | Loading (MW) | 1.6705 | 5.6282e-05 | 1.6857 | 1.6705 | 5.6296e-05 | 1.6857 | 1.6705 | 5.6294e-05 | 1.6857 | 1.6705 | 5.6289e-05 | 1.6857 | 1.6705 | 5.6278e-05 | 1.6857
NQ | 82908830 | 7308 | Stony Creek - Havilah 132 kV | 7308_Stony Creek - Havilah 132 kV | Power Factor | 0.93397 | 5.7264e-05 | 0.93393 | 0.93397 | 5.7264e-05 | 0.93394 | 0.93397 | 5.7264e-05 | 0.93393 | 0.93397 | 5.7264e-05 | 0.93393 | 0.93397 | 5.7264e-05 | 0.93393
NQ | 82908830 | 7308 | Stony Creek - Havilah 132 kV | 7308_Stony Creek - Havilah 132 kV | Rating (A) | 437 | 446 | 391 | 437 | 446 | 391 | 437 | 446 | 391 | 437 | 446 | 391 | 437 | 446 | 391
NQ | 82908830 | 7308 | Stony Creek - Havilah 132 kV | 7308_Stony Creek - Havilah 132 kV | Time | 11:00 | 21:00 | 2:30 | 11:00 | 21:00 | 2:30 | 11:00 | 21:00 | 2:30 | 11:00 | 21:00 | 2:30 | 11:00 | 21:00 | 2:30
NQ | 82908830 | 7308 | Stony Creek - Havilah 132 kV | 7308_Stony Creek - Havilah 132 kV | Voltage at Constrained Conductor | 140.1247 | 140.1232 | 140.1224 | 140.1397 | 140.1409 | 140.1362 | 140.1372 | 140.1389 | 140.1325 | 140.1343 | 140.1325 | 140.1292 | 140.1233 | 140.1188 | 140.1251
NQ | 82908833 | 7309 | Stony Creek - Fig Tree 132 kV | 7309_Stony Creek - Fig Tree 132 kV | % of Rated A | 1.1787 | 1.1199 | 1.2536 | 1.1787 | 1.1199 | 1.2536 | 1.1787 | 1.1199 | 1.2536 | 1.1787 | 1.1199 | 1.2536 | 1.1787 | 1.1199 | 1.2536
NQ | 82908833 | 7309 | Stony Creek - Fig Tree 132 kV | 7309_Stony Creek - Fig Tree 132 kV | Limiting Line Name | TR_LINE 67630_1 | TR_LINE 67630_1 | TR_LINE 67630_1 | TR_LINE 67630_1 | TR_LINE 67630_1 | TR_LINE 67630_1 | TR_LINE 67630_1 | TR_LINE 67630_1 | TR_LINE 67630_1 | TR_LINE 67630_1 | TR_LINE 67630_1 | TR_LINE 67630_1 | TR_LINE 67630_1 | TR_LINE 67630_1 | TR_LINE 67630_1
NQ | 82908833 | 7309 | Stony Creek - Fig Tree 132 kV | 7309_Stony Creek - Fig Tree 132 kV | Loading (A) | 5.3276 | 5.3307 | 5.3528 | 5.3276 | 5.3307 | 5.3528 | 5.3276 | 5.3307 | 5.3528 | 5.3276 | 5.3307 | 5.3527 | 5.3276 | 5.3307 | 5.3528
NQ | 82908833 | 7309 | Stony Creek - Fig Tree 132 kV | 7309_Stony Creek - Fig Tree 132 kV | Loading (MVA) | 1.2925 | 1.293 | 1.2993 | 1.2927 | 1.2931 | 1.2992 | 1.2926 | 1.2931 | 1.2992 | 1.2926 | 1.2931 | 1.2991 | 1.2924 | 1.2929 | 1.2992
NQ | 82908833 | 7309 | Stony Creek - Fig Tree 132 kV | 7309_Stony Creek - Fig Tree 132 kV | Loading (MW) | 0.97909 | 0.98028 | 0.98848 | 0.97909 | 0.98028 | 0.98848 | 0.97909 | 0.98028 | 0.98848 | 0.97909 | 0.98028 | 0.98848 | 0.97909 | 0.98028 | 0.98848
NQ | 82908833 | 7309 | Stony Creek - Fig Tree 132 kV | 7309_Stony Creek - Fig Tree 132 kV | Power Factor | 0.75752 | 0.75816 | 0.7608 | 0.75742 | 0.75806 | 0.76085 | 0.75744 | 0.75807 | 0.76086 | 0.75747 | 0.75811 | 0.76088 | 0.75756 | 0.75817 | 0.76084
NQ | 82908833 | 7309 | Stony Creek - Fig Tree 132 kV | 7309_Stony Creek - Fig Tree 132 kV | Rating (A) | 452 | 476 | 427 | 452 | 476 | 427 | 452 | 476 | 427 | 452 | 476 | 427 | 452 | 476 | 427
NQ | 82908833 | 7309 | Stony Creek - Fig Tree 132 kV | 7309_Stony Creek - Fig Tree 132 kV | Time | 16:30 | 20:00 | 22:30 | 16:30 | 20:00 | 22:30 | 16:30 | 20:00 | 22:30 | 16:30 | 20:00 | 22:30 | 16:30 | 20:00 | 22:30
NQ | 82908833 | 7309 | Stony Creek - Fig Tree 132 kV | 7309_Stony Creek - Fig Tree 132 kV | Voltage at Constrained Conductor | 140.0676 | 140.0365 | 140.1402 | 140.0856 | 140.0548 | 140.1316 | 140.0831 | 140.0528 | 140.1294 | 140.0767 | 140.0457 | 140.126 | 140.0617 | 140.0344 | 140.1328
NQ | 82912295 | BEGA 2 | GARBUTT-BELGIANGARDENS NO.02 | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | % of Rated A | 7.8516 | 8.5451 | 6.8014 | 7.851 | 8.544 | 6.8009 | 7.8138 | 8.5052 | 6.855 | 7.9494 | 8.6566 | 6.969 | 8.1326 | 8.8611 | 7.1239
NQ | 82912295 | BEGA 2 | GARBUTT-BELGIANGARDENS NO.02 | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | Limiting Line Name | TR_CABLE 16086_1 | TR_CABLE 16086_1 | TR_CABLE 16086_1 | TR_CABLE 16086_1 | TR_CABLE 16086_1 | TR_CABLE 16086_1 | TR_CABLE 16086_1 | TR_CABLE 16086_1 | TR_CABLE 16086_1 | TR_CABLE 16086_1 | TR_CABLE 16086_1 | TR_CABLE 16086_1 | TR_CABLE 16086_1 | TR_CABLE 16086_1 | TR_CABLE 16086_1
NQ | 82912295 | BEGA 2 | GARBUTT-BELGIANGARDENS NO.02 | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | Loading (A) | 62.3418 | 67.8481 | 54.0033 | 62.337 | 67.8391 | 53.9995 | 62.0418 | 67.5309 | 54.4283 | 63.1183 | 68.7335 | 55.3338 | 64.5727 | 70.3568 | 56.564
NQ | 82912295 | BEGA 2 | GARBUTT-BELGIANGARDENS NO.02 | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | Loading (MVA) | 7.3862 | 8.0389 | 6.4544 | 7.3863 | 8.0391 | 6.4545 | 7.395 | 8.0408 | 6.4347 | 7.522 | 8.1818 | 6.5408 | 7.6914 | 8.3702 | 6.6742
NQ | 82912295 | BEGA 2 | GARBUTT-BELGIANGARDENS NO.02 | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | Loading (MW) | 7.1898 | 7.8858 | 6.1608 | 7.1898 | 7.8858 | 6.1608 | 7.1903 | 7.8815 | 6.1598 | 7.3269 | 8.0313 | 6.2767 | 7.509 | 8.2311 | 6.4239
NQ | 82912295 | BEGA 2 | GARBUTT-BELGIANGARDENS NO.02 | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | Power Factor | 0.97342 | 0.98096 | 0.95451 | 0.9734 | 0.98094 | 0.95448 | 0.97231 | 0.98019 | 0.95727 | 0.97406 | 0.98161 | 0.95961 | 0.97628 | 0.98338 | 0.96251
NQ | 82912295 | BEGA 2 | GARBUTT-BELGIANGARDENS NO.02 | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | Rating (A) | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794
NQ | 82912295 | BEGA 2 | GARBUTT-BELGIANGARDENS NO.02 | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | Time | 16:30 | 19:30 | 22:30 | 16:30 | 19:30 | 22:30 | 16:30 | 19:00 | 22:30 | 16:30 | 19:00 | 22:30 | 16:30 | 19:00 | 22:00
NQ | 82912295 | BEGA 2 | GARBUTT-BELGIANGARDENS NO.02 | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | Voltage at Constrained Conductor | 68.4035 | 68.4065 | 69.0036 | 68.41 | 68.4172 | 69.0104 | 68.8169 | 68.7438 | 68.2566 | 68.8043 | 68.726 | 68.2464 | 68.7697 | 68.6863 | 68.1236
NQ | 82912298 | BEGA 1 | GARBUTT-BELGIANGARDENS NO.01 | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | % of Rated A | 7.8582 | 8.5514 | 6.8088 | 7.8576 | 8.5503 | 6.8083 | 7.8205 | 8.5116 | 6.8621 | 7.956 | 8.663 | 6.9761 | 8.1391 | 8.8673 | 7.1309
NQ | 82912298 | BEGA 1 | GARBUTT-BELGIANGARDENS NO.01 | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | Limiting Line Name | TR_CABLE 4808_1 | TR_CABLE 4808_1 | TR_CABLE 4808_1 | TR_CABLE 4808_1 | TR_CABLE 4808_1 | TR_CABLE 4808_1 | TR_CABLE 4808_1 | TR_CABLE 4808_1 | TR_CABLE 4808_1 | TR_CABLE 4808_1 | TR_CABLE 4808_1 | TR_CABLE 4808_1 | TR_CABLE 4808_1 | TR_CABLE 4808_1 | TR_CABLE 4808_1
NQ | 82912298 | BEGA 1 | GARBUTT-BELGIANGARDENS NO.01 | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | Loading (A) | 62.3943 | 67.8985 | 54.0616 | 62.3896 | 67.8896 | 54.0578 | 62.095 | 67.5818 | 54.4852 | 63.171 | 68.784 | 55.3901 | 64.6248 | 70.4067 | 56.6194
NQ | 82912298 | BEGA 1 | GARBUTT-BELGIANGARDENS NO.01 | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | Loading (MVA) | 7.3924 | 8.0449 | 6.4613 | 7.3925 | 8.0451 | 6.4615 | 7.4014 | 8.0468 | 6.4415 | 7.5282 | 8.1878 | 6.5475 | 7.6976 | 8.3762 | 6.6807
NQ | 82912298 | BEGA 1 | GARBUTT-BELGIANGARDENS NO.01 | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | Loading (MW) | 7.193 | 7.8893 | 6.1635 | 7.193 | 7.8893 | 6.1635 | 7.1935 | 7.8849 | 6.1626 | 7.3301 | 8.0349 | 6.2795 | 7.5123 | 8.2347 | 6.4268
NQ | 82912298 | BEGA 1 | GARBUTT-BELGIANGARDENS NO.01 | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | Power Factor | 0.97303 | 0.98066 | 0.95391 | 0.97301 | 0.98064 | 0.95389 | 0.97191 | 0.97988 | 0.9567 | 0.97368 | 0.98132 | 0.95907 | 0.97593 | 0.98312 | 0.962
NQ | 82912298 | BEGA 1 | GARBUTT-BELGIANGARDENS NO.01 | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | Rating (A) | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794
NQ | 82912298 | BEGA 1 | GARBUTT-BELGIANGARDENS NO.01 | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | Time | 16:30 | 19:30 | 22:30 | 16:30 | 19:30 | 22:30 | 16:30 | 19:00 | 22:30 | 16:30 | 19:00 | 22:30 | 16:30 | 19:00 | 22:00
NQ | 82912298 | BEGA 1 | GARBUTT-BELGIANGARDENS NO.01 | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | Voltage at Constrained Conductor | 68.4035 | 68.4065 | 69.0036 | 68.41 | 68.4172 | 69.0104 | 68.8169 | 68.7438 | 68.2566 | 68.8043 | 68.726 | 68.2464 | 68.7697 | 68.6863 | 68.1236
NQ | 83878913 | 6299 | TOPO FDR | 6299_Townsville Port 66 kV | % of Rated A | 38.9724 | 35.7438 | 32.4441 | 39.1548 | 35.8979 | 32.5585 | 37.4069 | 34.3126 | 31.5927 | 37.5556 | 34.4732 | 31.7224 | 37.9848 | 34.8798 | 32.0755
NQ | 83878913 | 6299 | TOPO FDR | 6299_Townsville Port 66 kV | Limiting Line Name | TR_LINE 96490_1 | TR_LINE 96490_1 | TR_LINE 96490_1 | TR_LINE 96490_1 | TR_LINE 96490_1 | TR_LINE 96490_1 | TR_LINE 96490_1 | TR_LINE 96490_1 | TR_LINE 96490_1 | TR_LINE 96490_1 | TR_LINE 96490_1 | TR_LINE 96490_1 | TR_LINE 96490_1 | TR_LINE 96490_1 | TR_LINE 96490_1
NQ | 83878913 | 6299 | TOPO FDR | 6299_Townsville Port 66 kV | Loading (A) | 425.5787 | 430.7123 | 359.1558 | 427.5701 | 432.57 | 360.4223 | 408.4837 | 413.4668 | 349.7311 | 410.1068 | 415.4025 | 351.1668 | 414.7942 | 420.3013 | 355.0763
NQ | 83878913 | 6299 | TOPO FDR | 6299_Townsville Port 66 kV | Loading (MVA) | 50.6361 | 51.2391 | 42.9606 | 50.8599 | 51.4499 | 43.1061 | 48.8117 | 49.4078 | 41.5356 | 48.9999 | 49.6312 | 41.7346 | 49.5403 | 50.1949 | 42.1856
NQ | 83878913 | 6299 | TOPO FDR | 6299_Townsville Port 66 kV | Loading (MW) | 50.4382 | 51.031 | 42.3903 | 50.6766 | 51.2533 | 42.5526 | 48.3436 | 48.911 | 41.5057 | 48.5394 | 49.1456 | 41.6708 | 49.1091 | 49.7415 | 42.1304
NQ | 83878913 | 6299 | TOPO FDR | 6299_Townsville Port 66 kV | Power Factor | 0.99609 | 0.99594 | 0.98672 | 0.9964 | 0.99618 | 0.98716 | 0.99041 | 0.98994 | 0.99928 | 0.9906 | 0.99022 | 0.99847 | 0.9913 | 0.99097 | 0.99869
NQ | 83878913 | 6299 | TOPO FDR | 6299_Townsville Port 66 kV | Rating (A) | 1092 | 1205 | 1107 | 1092 | 1205 | 1107 | 1092 | 1205 | 1107 | 1092 | 1205 | 1107 | 1092 | 1205 | 1107
NQ | 83878913 | 6299 | TOPO FDR | 6299_Townsville Port 66 kV | Time | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00 | 16:30 | 19:00 | 8:30 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00
NQ | 83878913 | 6299 | TOPO FDR | 6299_Townsville Port 66 kV | Voltage at Constrained Conductor | 68.6942 | 68.6837 | 69.06 | 68.6764 | 68.6701 | 69.0504 | 68.9903 | 68.9913 | 68.5686 | 68.9822 | 68.9803 | 68.6154 | 68.9549 | 68.9506 | 68.5934
NQ | 83969140 | 6312 | MERINDA-HOMEHILL | 6312_Merinda - Home Hill 66 kV | % of Rated A | 7.9763 | 7.4892 | 7.0132 | 7.0158 | 6.3139 | 6.2655 | 7.0139 | 6.2067 | 6.2243 | 7.0142 | 6.2069 | 6.2253 | 7.0158 | 6.2081 | 6.2144
NQ | 83969140 | 6312 | MERINDA-HOMEHILL | 6312_Merinda - Home Hill 66 kV | Limiting Line Name | TR_LINE 77683_1 | TR_LINE 77683_1 | TR_LINE 77683_1 | TR_LINE 180012_1 | TR_LINE 77683_1 | TR_LINE 32515_1 | TR_LINE 180012_1 | TR_LINE 77683_1 | TR_LINE 32515_1 | TR_LINE 180012_1 | TR_LINE 77683_1 | TR_LINE 32515_1 | TR_LINE 180012_1 | TR_LINE 77683_1 | TR_LINE 32515_1
NQ | 83969140 | 6312 | MERINDA-HOMEHILL | 6312_Merinda - Home Hill 66 kV | Loading (A) | 19.6217 | 20.4456 | 17.4628 | 12.2776 | 17.237 | 16.4157 | 12.2743 | 16.9442 | 16.3077 | 12.2748 | 16.9448 | 16.3104 | 12.2777 | 16.9482 | 16.2817
NQ | 83969140 | 6312 | MERINDA-HOMEHILL | 6312_Merinda - Home Hill 66 kV | Loading (MVA) | 2.2582 | 2.322 | 2.012 | 1.3941 | 1.9612 | 1.8919 | 1.3944 | 1.9286 | 1.8556 | 1.3944 | 1.9285 | 1.8557 | 1.3941 | 1.928 | 1.8759
NQ | 83969140 | 6312 | MERINDA-HOMEHILL | 6312_Merinda - Home Hill 66 kV | Loading (MW) | 2.1591 | 2.2375 | 1.8548 | 1.2511 | 1.7692 | 1.5344 | 1.2511 | 1.7229 | 1.5064 | 1.2511 | 1.7229 | 1.5064 | 1.2511 | 1.7229 | 1.5063
NQ | 83969140 | 6312 | MERINDA-HOMEHILL | 6312_Merinda - Home Hill 66 kV | Power Factor | 0.95612 | 0.96361 | 0.92188 | 0.89746 | 0.90208 | 0.81107 | 0.89724 | 0.89334 | 0.81185 | 0.89727 | 0.89339 | 0.81178 | 0.89746 | 0.89361 | 0.80297
NQ | 83969140 | 6312 | MERINDA-HOMEHILL | 6312_Merinda - Home Hill 66 kV | Rating (A) | 246 | 273 | 249 | 175 | 273 | 262 | 175 | 273 | 262 | 175 | 273 | 262 | 175 | 273 | 262
NQ | 83969140 | 6312 | MERINDA-HOMEHILL | 6312_Merinda - Home Hill 66 kV | Time | 16:30 | 17:00 | 8:30 | 16:30 | 17:00 | 22:00 | 16:30 | 17:00 | 22:00 | 16:30 | 17:00 | 22:00 | 16:30 | 17:00 | 22:00
NQ | 83969140 | 6312 | MERINDA-HOMEHILL | 6312_Merinda - Home Hill 66 kV | Voltage at Constrained Conductor | 66.4441 | 65.5681 | 66.5199 | 65.5562 | 65.6915 | 66.5386 | 65.5896 | 65.7141 | 65.6934 | 65.5842 | 65.7085 | 65.6871 | 65.5553 | 65.6792 | 66.5189
NQ | 84212381 | 6321 | 66kV LUCINDA FDR | 6321_Lucinda 66 kV | % of Rated A | 21.0399 | 22.344 | 21.0043 | 21.0368 | 22.0415 | 21.0017 | 20.4581 | 21.9905 | 20.6425 | 20.4654 | 21.9909 | 20.6426 | 20.8419 | 22.382 | 21.0228
NQ | 84212381 | 6321 | 66kV LUCINDA FDR | 6321_Lucinda 66 kV | Limiting Line Name | TR_LINE 90734_2 | TR_LINE 90734_2 | TR_LINE 90734_2 | TR_LINE 90734_2 | TR_LINE 90734_2 | TR_LINE 90734_2 | TR_LINE 90734_2 | TR_LINE 90734_2 | TR_LINE 90734_2 | TR_LINE 90734_2 | TR_LINE 90734_2 | TR_LINE 90734_2 | TR_LINE 90734_2 | TR_LINE 90734_2 | TR_LINE 90734_2
NQ | 84212381 | 6321 | 66kV LUCINDA FDR | 6321_Lucinda 66 kV | Loading (A) | 41.8694 | 49.827 | 42.8487 | 41.8632 | 49.1525 | 42.8435 | 40.7116 | 49.0388 | 42.1106 | 40.7262 | 49.0396 | 42.111 | 41.4754 | 49.9119 | 42.8866
NQ | 84212381 | 6321 | 66kV LUCINDA FDR | 6321_Lucinda 66 kV | Loading (MVA) | 4.9231 | 5.806 | 5.0823 | 4.923 | 5.8036 | 5.0823 | 4.8354 | 5.7085 | 4.993 | 4.8355 | 5.7085 | 4.993 | 4.9222 | 5.8067 | 5.0826
NQ | 84212381 | 6321 | 66kV LUCINDA FDR | 6321_Lucinda 66 kV | Loading (MW) | 4.4832 | 5.2742 | 4.6245 | 4.4832 | 5.2739 | 4.6245 | 4.4113 | 5.1935 | 4.5504 | 4.4114 | 5.1935 | 4.5504 | 4.4832 | 5.2743 | 4.6245
NQ | 84212381 | 6321 | 66kV LUCINDA FDR | 6321_Lucinda 66 kV | Power Factor | 0.91065 | 0.9084 | 0.90992 | 0.91066 | 0.90873 | 0.90992 | 0.91231 | 0.90978 | 0.91136 | 0.91229 | 0.90978 | 0.91136 | 0.91081 | 0.90831 | 0.90987
NQ | 84212381 | 6321 | 66kV LUCINDA FDR | 6321_Lucinda 66 kV | Rating (A) | 199 | 223 | 204 | 199 | 223 | 204 | 199 | 223 | 204 | 199 | 223 | 204 | 199 | 223 | 204
NQ | 84212381 | 6321 | 66kV LUCINDA FDR | 6321_Lucinda 66 kV | Time | 13:30 | 19:30 | 22:00 | 13:30 | 19:30 | 22:00 | 13:30 | 19:30 | 22:00 | 13:30 | 19:30 | 22:00 | 13:30 | 19:30 | 22:00
NQ | 84212381 | 6321 | 66kV LUCINDA FDR | 6321_Lucinda 66 kV | Voltage at Constrained Conductor | 67.8858 | 67.2752 | 68.4799 | 67.8952 | 68.1702 | 68.4875 | 68.5726 | 67.2077 | 68.4556 | 68.5497 | 67.2067 | 68.4552 | 68.5183 | 67.1687 | 68.4236
NQ | 84253050 | 6325 | OONOONBA-STUART | 6325_Oonoonba-Stuart 66 kV | % of Rated A | 68.462 | 68.9915 | 61.7628 | 68.2046 | 68.8574 | 61.6391 | 70.3768 | 71.5505 | 65.7491 | 70.6187 | 71.8656 | 65.9964 | 71.2244 | 72.5225 | 66.4962
NQ | 84253050 | 6325 | OONOONBA-STUART | 6325_Oonoonba-Stuart 66 kV | Limiting Line Name | TR_LINE 31738_1 | TR_LINE 31738_1 | TR_LINE 31738_1 | TR_LINE 31738_1 | TR_LINE 31738_1 | TR_LINE 31738_1 | TR_LINE 31738_1 | TR_LINE 31738_1 | TR_LINE 31738_1 | TR_LINE 31738_1 | TR_LINE 31738_1 | TR_LINE 31738_1 | TR_LINE 31738_1 | TR_LINE 31738_1 | TR_LINE 31738_1
NQ | 84253050 | 6325 | OONOONBA-STUART | 6325_Oonoonba-Stuart 66 kV | Loading (A) | 222.5016 | 229.0518 | 180.9649 | 221.665 | 228.6066 | 180.6026 | 228.7247 | 237.5478 | 192.6448 | 229.5107 | 238.5936 | 193.3693 | 231.4793 | 240.7747 | 194.8339
NQ | 84253050 | 6325 | OONOONBA-STUART | 6325_Oonoonba-Stuart 66 kV | Loading (MVA) | 26.4305 | 27.2425 | 21.5833 | 26.3297 | 27.1901 | 21.5404 | 27.3539 | 28.3826 | 22.9135 | 27.4436 | 28.5018 | 22.9965 | 27.6686 | 28.75 | 23.1624
NQ | 84253050 | 6325 | OONOONBA-STUART | 6325_Oonoonba-Stuart 66 kV | Loading (MW) | 25.8054 | 26.6701 | 20.5232 | 25.6918 | 26.6079 | 20.4678 | 26.7595 | 27.8784 | 22.8324 | 26.8546 | 28.0055 | 22.9167 | 27.0967 | 28.2717 | 23.0842
NQ | 84253050 | 6325 | OONOONBA-STUART | 6325_Oonoonba-Stuart 66 kV | Power Factor | 0.97635 | 0.97899 | 0.95088 | 0.97578 | 0.97859 | 0.95021 | 0.97827 | 0.98224 | 0.99646 | 0.97854 | 0.98259 | 0.99653 | 0.97933 | 0.98336 | 0.99662
NQ | 84253050 | 6325 | OONOONBA-STUART | 6325_Oonoonba-Stuart 66 kV | Rating (A) | 325 | 332 | 293 | 325 | 332 | 293 | 325 | 332 | 293 | 325 | 332 | 293 | 325 | 332 | 293
NQ | 84253050 | 6325 | OONOONBA-STUART | 6325_Oonoonba-Stuart 66 kV | Time | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00
NQ | 84253050 | 6325 | OONOONBA-STUART | 6325_Oonoonba-Stuart 66 kV | Voltage at Constrained Conductor | 68.5824 | 68.6677 | 68.8594 | 68.5784 | 68.6691 | 68.8602 | 69.047 | 68.9827 | 68.6709 | 69.0362 | 68.9689 | 68.6616 | 69.0104 | 68.9393 | 68.637
NQ | 111543431 | 6382 | JACR - HUGH FDR 6382 | 6382 JACR-HUGH 132kV | % of Rated A | 47.9849 | 49.1729 | 41.2323 | 47.1961 | 48.259 | 40.8365 | 56.1201 | 60.175 | 45.1231 | 56.1158 | 60.1748 | 45.1153 | 56.7521 | 60.9004 | 45.5933
NQ | 111543431 | 6382 | JACR - HUGH FDR 6382 | 6382 JACR-HUGH 132kV | Limiting Line Name | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line
NQ | 111543431 | 6382 | JACR - HUGH FDR 6382 | 6382 JACR-HUGH 132kV | Loading (A) | 68.1386 | 69.8255 | 58.5499 | 67.0184 | 68.5277 | 57.9878 | 79.5292 | 85.1319 | 64.0748 | 79.5211 | 85.1301 | 64.0638 | 80.3724 | 86.1046 | 64.7425
NQ | 111543431 | 6382 | JACR - HUGH FDR 6382 | 6382 JACR-HUGH 132kV | Loading (MVA) | 7.9322 | 8.1249 | 6.8342 | 7.8046 | 7.9759 | 6.7675 | 9.2376 | 9.8765 | 7.471 | 9.2366 | 9.8761 | 7.4695 | 9.3324 | 9.9854 | 7.5458
NQ | 111543431 | 6382 | JACR - HUGH FDR 6382 | 6382 JACR-HUGH 132kV | Loading (MW) | 7.9117 | 8.116 | 6.6649 | 7.7745 | 7.9605 | 6.5968 | 9.2256 | 9.8177 | 7.3985 | 9.2242 | 9.8168 | 7.398 | 9.309 | 9.9007 | 7.4938
NQ | 111543431 | 6382 | JACR - HUGH FDR 6382 | 6382 JACR-HUGH 132kV | Power Factor | 0.99742 | 0.9989 | 0.97522 | 0.99614 | 0.99806 | 0.97477 | 0.9987 | 0.99405 | 0.99031 | 0.99866 | 0.99399 | 0.99042 | 0.99749 | 0.99152 | 0.99311
NQ | 111543431 | 6382 | JACR - HUGH FDR 6382 | 6382 JACR-HUGH 132kV | Rating (A) | 142 | 142 | 142 | 142 | 142 | 142 | 142 | 142 | 142 | 142 | 142 | 142 | 142 | 142 | 142
NQ | 111543431 | 6382 | JACR - HUGH FDR 6382 | 6382 JACR-HUGH 132kV | Time | 15:30 | 18:30 | 8:30 | 15:30 | 18:30 | 8:30 | 15:30 | 18:30 | 8:30 | 15:30 | 18:30 | 8:30 | 15:30 | 18:30 | 8:30
NQ | 111543431 | 6382 | JACR - HUGH FDR 6382 | 6382 JACR-HUGH 132kV | Voltage at Constrained Conductor | 67.2111 | 67.1809 | 67.3911 | 67.2352 | 67.1978 | 67.3802 | 67.0614 | 66.9805 | 67.3175 | 67.0606 | 66.9797 | 67.3159 | 67.0387 | 66.9543 | 67.2912
NQ | 111675890 | 7460 | CPRE-JACR FDR | 6383 CARI-CPRE 66kV | % of Rated A | 22.949 | 20.5951 | 18.2378 | 22.5124 | 20.1495 | 18.056 | 27.3193 | 25.754 | 20.2293 | 27.3333 | 25.7751 | 20.2288 | 27.6955 | 26.1249 | 20.5011
NQ | 111675890 | 7460 | CPRE-JACR FDR | 6383 CARI-CPRE 66kV | Limiting Line Name | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1
NQ | 111675890 | 7460 | CPRE-JACR FDR | 6383 CARI-CPRE 66kV | Loading (A) | 71.6008 | 73.7305 | 60.0017 | 70.2387 | 72.1353 | 59.4038 | 85.2364 | 92.1992 | 66.554 | 85.2799 | 92.275 | 66.5525 | 86.4099 | 93.527 | 67.4486
NQ | 111675890 | 7460 | CPRE-JACR FDR | 6383 CARI-CPRE 66kV | Loading (MVA) | 8.1473 | 8.384 | 6.858 | 7.9981 | 8.2048 | 6.7831 | 9.6807 | 10.4619 | 7.6014 | 9.6853 | 10.4701 | 7.6006 | 9.8113 | 10.6093 | 7.6982
NQ | 111675890 | 7460 | CPRE-JACR FDR | 6383 CARI-CPRE 66kV | Loading (MW) | 8.1341 | 8.3449 | 6.8461 | 7.9913 | 8.1851 | 6.7786 | 9.4879 | 10.1 | 7.5985 | 9.4866 | 10.099 | 7.5981 | 9.5739 | 10.1858 | 7.6976
NQ | 111675890 | 7460 | CPRE-JACR FDR | 6383 CARI-CPRE 66kV | Power Factor | 0.99838 | 0.99534 | 0.99826 | 0.99915 | 0.9976 | 0.99933 | 0.98009 | 0.96541 | 0.99962 | 0.97948 | 0.96456 | 0.99967 | 0.97581 | 0.96008 | 0.99992
NQ | 111675890 | 7460 | CPRE-JACR FDR | 6383 CARI-CPRE 66kV | Rating (A) | 312 | 358 | 329 | 312 | 358 | 329 | 312 | 358 | 329 | 312 | 358 | 329 | 312 | 358 | 329
NQ | 111675890 | 7460 | CPRE-JACR FDR | 6383 CARI-CPRE 66kV | Time | 15:30 | 18:30 | 8:30 | 15:30 | 18:30 | 8:30 | 15:30 | 18:30 | 8:30 | 15:30 | 18:30 | 8:30 | 15:30 | 18:30 | 8:30
NQ | 111675890 | 7460 | CPRE-JACR FDR | 6383 CARI-CPRE 66kV | Voltage at Constrained Conductor | 65.6952 | 65.6514 | 65.9894 | 65.7431 | 65.6686 | 65.9256 | 65.5726 | 65.5122 | 65.9411 | 65.5702 | 65.5095 | 65.936 | 65.5544 | 65.4923 | 65.8951
NQ | 111675890 | 7460 | CPRE-JACR FDR | 7460 CPRE-JACR 132kV | % of Rated A | 29.6526 | 18.7954 | 16.0578 | 29.1539 | 18.5803 | 16.1684 | 32.6066 | 21.1082 | 17.097 | 32.6069 | 21.1096 | 17.1105 | 32.7788 | 21.2133 | 17.3354
NQ | 111675890 | 7460 | CPRE-JACR FDR | 7460 CPRE-JACR 132kV | Limiting Line Name | TR_LINE 51339257_1 | TR_LINE 51339257_1 | TR_LINE 51339257_1 | TR_LINE 51339257_1 | TR_LINE 51339257_1 | TR_LINE 51339257_1 | TR_LINE 51339257_1 | TR_LINE 51339257_1 | TR_LINE 51339257_1 | TR_LINE 51339257_1 | TR_LINE 51339257_1 | TR_LINE 51339257_1 | TR_LINE 51339257_1 | TR_LINE 51339257_1 | TR_LINE 51339257_1
NQ | 111675890 | 7460 | CPRE-JACR FDR | 7460 CPRE-JACR 132kV | Loading (A) | 51.299 | 52.2511 | 44.6407 | 50.4362 | 51.6531 | 44.9481 | 56.4094 | 58.6809 | 47.5296 | 56.41 | 58.6846 | 47.5671 | 56.7073 | 58.973 | 48.1923
NQ | 111675890 | 7460 | CPRE-JACR FDR | 7460 CPRE-JACR 132kV | Loading (MVA) | 11.7361 | 11.9492 | 10.2477 | 11.5452 | 11.8136 | 10.3104 | 12.8949 | 13.4092 | 10.9054 | 12.8948 | 13.4099 | 10.9133 | 12.9613 | 13.474 | 11.0513
NQ | 111675890 | 7460 | CPRE-JACR FDR | 7460 CPRE-JACR 132kV | Loading (MW) | 8.0875 | 8.2985 | 6.8002 | 7.9448 | 8.1385 | 6.7328 | 9.4412 | 10.0529 | 7.5522 | 9.4399 | 10.052 | 7.5517 | 9.5273 | 10.1387 | 7.6512
NQ | 111675890 | 7460 | CPRE-JACR FDR | 7460 CPRE-JACR 132kV | Power Factor | 0.68911 | 0.69448 | 0.66358 | 0.68815 | 0.68891 | 0.65301 | 0.73217 | 0.7497 | 0.69252 | 0.73207 | 0.7496 | 0.69198 | 0.73506 | 0.75247 | 0.69234
NQ | 111675890 | 7460 | CPRE-JACR FDR | 7460 CPRE-JACR 132kV | Rating (A) | 173 | 278 | 278 | 173 | 278 | 278 | 173 | 278 | 278 | 173 | 278 | 278 | 173 | 278 | 278
NQ | 111675890 | 7460 | CPRE-JACR FDR | 7460 CPRE-JACR 132kV | Time | 15:30 | 18:30 | 8:30 | 15:30 | 18:30 | 8:30 | 15:30 | 18:30 | 8:30 | 15:30 | 18:30 | 8:30 | 15:30 | 18:30 | 8:30
NQ | 111675890 | 7460 | CPRE-JACR FDR | 7460 CPRE-JACR 132kV | Voltage at Constrained Conductor | 132.0853 | 132.0335 | 132.5369 | 132.1597 | 132.0456 | 132.4348 | 131.9793 | 131.9311 | 132.4694 | 131.9772 | 131.9288 | 132.4611 | 131.9618 | 131.9112 | 132.3954
NQMK | 20010276 | ME-PR-1 | Merinda-Proserpine No.1 | ME-PR-1_Merinda - Proserpine No 1 66 kV | % of Rated A | 12.7502 | 6.1195 | 8.4075 | 12.5711 | 6.0018 | 8.3041 | 12.5592 | 6.5532 | 8.2949 | 12.5791 | 6.0422 | 8.2911 | 12.6896 | 6.1439 | 12.4901
NQMK | 20010276 | ME-PR-1 | Merinda-Proserpine No.1 | ME-PR-1_Merinda - Proserpine No 1 66 kV | Limiting Line Name | TR_LINE 175214_1 | TR_LINE 175214_1 | TR_LINE 175214_1 | TR_LINE 175214_1 | TR_LINE 175214_1 | TR_LINE 175214_1 | TR_LINE 175214_1 | TR_LINE 175214_1 | TR_LINE 175214_1 | TR_LINE 175214_1 | TR_LINE 175214_1 | TR_LINE 175214_1 | TR_LINE 175214_1 | TR_LINE 175214_1 | TR_LINE 112170_1
NQMK | 20010276 | ME-PR-1 | Merinda-Proserpine No.1 | ME-PR-1_Merinda - Proserpine No 1 66 kV | Loading (A) | 24.6079 | 16.7674 | 22.448 | 24.2621 | 16.445 | 22.1719 | 24.2393 | 17.9557 | 22.1474 | 24.2777 | 16.5558 | 22.1374 | 24.4909 | 16.8344 | 27.2284
NQMK | 20010276 | ME-PR-1 | Merinda-Proserpine No.1 | ME-PR-1_Merinda - Proserpine No 1 66 kV | Loading (MVA) | 2.8332 | 1.9355 | 2.5859 | 2.7964 | 1.9 | 2.5563 | 2.7939 | 2.0724 | 2.5536 | 2.7978 | 1.9121 | 2.5523 | 2.82 | 1.9424 | 3.199
NQMK | 20010276 | ME-PR-1 | Merinda-Proserpine No.1 | ME-PR-1_Merinda - Proserpine No 1 66 kV | Loading (MW) | 1.9217 | 1.5922 | 1.201 | 1.9065 | 1.5674 | 1.1878 | 1.9052 | 1.4323 | 1.1864 | 1.9074 | 1.5767 | 1.1916 | 1.9222 | 1.5974 | 1.665
NQMK | 20010276 | ME-PR-1 | Merinda-Proserpine No.1 | ME-PR-1_Merinda - Proserpine No 1 66 kV | Power Factor | 0.67829 | 0.82263 | 0.46445 | 0.68178 | 0.82492 | 0.46464 | 0.68194 | 0.69112 | 0.46461 | 0.68174 | 0.8246 | 0.46687 | 0.68162 | 0.82235 | 0.52049
NQMK | 20010276 | ME-PR-1 | Merinda-Proserpine No.1 | ME-PR-1_Merinda - Proserpine No 1 66 kV | Rating (A) | 193 | 274 | 267 | 193 | 274 | 267 | 193 | 274 | 267 | 193 | 274 | 267 | 193 | 274 | 218
NQMK | 20010276 | ME-PR-1 | Merinda-Proserpine No.1 | ME-PR-1_Merinda - Proserpine No 1 66 kV | Time | 11:00 | 17:00 | 8:00 | 11:00 | 17:00 | 8:00 | 11:00 | 17:30 | 8:00 | 11:00 | 17:00 | 8:00 | 11:00 | 17:00 | 22:00
NQMK | 20010276 | ME-PR-1 | Merinda-Proserpine No.1 | ME-PR-1_Merinda - Proserpine No 1 66 kV | Voltage at Constrained Conductor | 66.4724 | 66.6433 | 66.5075 | 66.5429 | 66.7065 | 66.5662 | 66.5466 | 66.6368 | 66.5695 | 66.5345 | 66.6802 | 66.566 | 66.4789 | 66.6177 | 67.8307
NQMK | 20013617 | PR-BN-1 | Proserpine-Bowen No.1 | PR-BN-1_Proserpine - Bowen No 1 66 kV | % of Rated A | 2.6884 | 2.3335 | 2.5503 | 2.6836 | 2.3357 | 2.5396 | 2.6837 | 2.3359 | 2.5397 | 2.6841 | 2.3349 | 2.539 | 2.6871 | 2.3325 | 2.5491
NQMK | 20013617 | PR-BN-1 | Proserpine-Bowen No.1 | PR-BN-1_Proserpine - Bowen No 1 66 kV | Limiting Line Name | TR_LINE 175048_1 | TR_LINE 175048_1 | TR_LINE 175048_1 | TR_LINE 175048_1 | TR_LINE 175048_1 | TR_LINE 175048_1 | TR_LINE 175048_1 | TR_LINE 175048_1 | TR_LINE 175048_1 | TR_LINE 175048_1 | TR_LINE 175048_1 | TR_LINE 175048_1 | TR_LINE 175048_1 | TR_LINE 175048_1 | TR_LINE 175048_1
NQMK | 20013617 | PR-BN-1 | Proserpine-Bowen No.1 | PR-BN-1_Proserpine - Bowen No 1 66 kV | Loading (A) | 7.9577 | 7.9106 | 7.9825 | 7.9433 | 7.918 | 7.949 | 7.9436 | 7.9186 | 7.9493 | 7.9449 | 7.9153 | 7.9472 | 7.9539 | 7.9073 | 7.9786
NQMK | 20013617 | PR-BN-1 | Proserpine-Bowen No.1 | PR-BN-1_Proserpine - Bowen No 1 66 kV | Loading (MVA) | 0.93144 | 0.92046 | 0.93726 | 0.92808 | 0.92218 | 0.92941 | 0.92815 | 0.92232 | 0.92947 | 0.92844 | 0.92154 | 0.92899 | 0.93055 | 0.91968 | 0.93635
NQMK | 20013617 | PR-BN-1 | Proserpine-Bowen No.1 | PR-BN-1_Proserpine - Bowen No 1 66 kV | Loading (MW) | 0.0010995 | 0.0010865 | 0.0011064 | 0.0010955 | 0.0010886 | 0.0010971 | 0.0010956 | 0.0010887 | 0.0010972 | 0.001096 | 0.0010878 | 0.0010966 | 0.0010985 | 0.0010856 | 0.0011053
NQMK | 20013617 | PR-BN-1 | Proserpine-Bowen No.1 | PR-BN-1_Proserpine - Bowen No 1 66 kV | Power Factor | 0.0011804 | 0.0011804 | 0.0011804 | 0.0011804 | 0.0011804 | 0.0011804 | 0.0011804 | 0.0011804 | 0.0011804 | 0.0011804 | 0.0011804 | 0.0011804 | 0.0011804 | 0.0011804 | 0.0011804
NQMK | 20013617 | PR-BN-1 | Proserpine-Bowen No.1 | PR-BN-1_Proserpine - Bowen No 1 66 kV | Rating (A) | 296 | 339 | 313 | 296 | 339 | 313 | 296 | 339 | 313 | 296 | 339 | 313 | 296 | 339 | 313
NQMK | 20013617 | PR-BN-1 | Proserpine-Bowen No.1 | PR-BN-1_Proserpine - Bowen No 1 66 kV | Time | 10:30 | 21:30 | 7:00 | 11:00 | 21:30 | 5:00 | 11:00 | 21:30 | 5:00 | 13:00 | 21:30 | 5:00 | 10:30 | 21:30 | 7:00
NQMK | 20013617 | PR-BN-1 | Proserpine-Bowen No.1 | PR-BN-1_Proserpine - Bowen No 1 66 kV | Voltage at Constrained Conductor | 67.5785 | 67.1789 | 67.7891 | 67.4565 | 67.2418 | 67.5046 | 67.4589 | 67.2468 | 67.5069 | 67.4696 | 67.2184 | 67.4894 | 67.5461 | 67.1505 | 67.7561
NQMK | 20013643 | ME-BN-1 | Merinda-Bowen | ME-BN-1_Merinda - Bowen No 1 66 kV | % of Rated A | 58.9124 | 57.9616 | 50.3559 | 58.8805 | 57.9326 | 50.338 | 58.8787 | 57.9297 | 50.3369 | 59.2311 | 58.2981 | 50.6022 | 59.9447 | 59.0486 | 50.697
NQMK | 20013643 | ME-BN-1 | Merinda-Bowen | ME-BN-1_Merinda - Bowen No 1 66 kV | Limiting Line Name | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1
NQMK | 20013643 | ME-BN-1 | Merinda-Bowen | ME-BN-1_Merinda - Bowen No 1 66 kV | Loading (A) | 114.8792 | 126.3562 | 100.2082 | 114.8171 | 126.2931 | 100.1725 | 114.8135 | 126.2866 | 100.1705 | 115.5007 | 127.0899 | 100.6985 | 116.8921 | 128.7259 | 100.8869
NQMK | 20013643 | ME-BN-1 | Merinda-Bowen | ME-BN-1_Merinda - Bowen No 1 66 kV | Loading (MVA) | 13.3843 | 14.6947 | 11.7183 | 13.3897 | 14.6987 | 11.7246 | 13.39 | 14.6991 | 11.725 | 13.4656 | 14.7861 | 11.7833 | 13.6166 | 14.9598 | 11.8754
NQMK | 20013643 | ME-BN-1 | Merinda-Bowen | ME-BN-1_Merinda - Bowen No 1 66 kV | Loading (MW) | 12.334 | 13.8075 | 10.2769 | 12.3338 | 13.8073 | 10.2768 | 12.3337 | 13.8073 | 10.2768 | 12.4254 | 13.9101 | 10.3528 | 12.6087 | 14.1159 | 10.5029
NQMK | 20013643 | ME-BN-1 | Merinda-Bowen | ME-BN-1_Merinda - Bowen No 1 66 kV | Power Factor | 0.92153 | 0.93962 | 0.87699 | 0.92114 | 0.93936 | 0.87652 | 0.92112 | 0.93933 | 0.87649 | 0.92275 | 0.94075 | 0.87861 | 0.92598 | 0.94359 | 0.88443
NQMK | 20013643 | ME-BN-1 | Merinda-Bowen | ME-BN-1_Merinda - Bowen No 1 66 kV | Rating (A) | 195 | 218 | 199 | 195 | 218 | 199 | 195 | 218 | 199 | 195 | 218 | 199 | 195 | 218 | 199
NQMK | 20013643 | ME-BN-1 | Merinda-Bowen | ME-BN-1_Merinda - Bowen No 1 66 kV | Time | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00
NQMK | 20013643 | ME-BN-1 | Merinda-Bowen | ME-BN-1_Merinda - Bowen No 1 66 kV | Voltage at Constrained Conductor | 67.2656 | 67.1436 | 67.5152 | 67.3291 | 67.1952 | 67.5754 | 67.3327 | 67.2005 | 67.5788 | 67.3099 | 67.1712 | 67.5588 | 67.2545 | 67.0962 | 67.9599
NQMK | 30053760 | 118 | CANNONVALE NO 2 | 118_Cannonvale No 2 66 kV | % of Rated A | 80.9922 | 87.3695 | 71.4749 | 76.3488 | 79.3482 | 62.7112 | 76.3423 | 79.8994 | 62.7067 | 76.5745 | 79.5997 | 62.8872 | 77.8881 | 81.0076 | 64.6145
NQMK | 30053760 | 118 | CANNONVALE NO 2 | 118_Cannonvale No 2 66 kV | Limiting Line Name | TR_CABLE 7280_1 | TR_CABLE 7280_1 | TR_CABLE 7280_1 | TR_CABLE 7280_1 | TR_CABLE 7280_1 | TR_CABLE 7280_1 | TR_CABLE 7280_1 | TR_CABLE 7280_1 | TR_CABLE 7280_1 | TR_CABLE 7280_1 | TR_CABLE 7280_1 | TR_CABLE 7280_1 | TR_CABLE 7280_1 | TR_CABLE 7280_1 | TR_CABLE 7280_1
NQMK | 30053760 | 118 | CANNONVALE NO 2 | 118_Cannonvale No 2 66 kV | Loading (A) | 156.3149 | 168.6231 | 137.9466 | 147.3531 | 153.142 | 121.0325 | 147.3406 | 154.2058 | 121.024 | 147.7888 | 153.6274 | 121.3723 | 150.324 | 156.3446 | 124.706
NQMK | 30053760 | 118 | CANNONVALE NO 2 | 118_Cannonvale No 2 66 kV | Loading (MVA) | 18.0562 | 19.5351 | 16.0427 | 17.0436 | 17.7793 | 14.0931 | 17.0437 | 17.7979 | 14.0934 | 17.0878 | 17.8278 | 14.1282 | 17.3616 | 18.1233 | 14.3374
NQMK | 30053760 | 118 | CANNONVALE NO 2 | 118_Cannonvale No 2 66 kV | Loading (MW) | 16.9801 | 18.635 | 14.4734 | 16.9289 | 17.6878 | 13.7697 | 16.9288 | 17.7044 | 13.7696 | 16.9761 | 17.7393 | 13.8094 | 17.2649 | 18.0487 | 14.0515
NQMK | 30053760 | 118 | CANNONVALE NO 2 | 118_Cannonvale No 2 66 kV | Power Factor | 0.9404 | 0.95393 | 0.90218 | 0.99327 | 0.99486 | 0.97705 | 0.99326 | 0.99474 | 0.97703 | 0.99346 | 0.99504 | 0.97744 | 0.99443 | 0.99588 | 0.98006
NQMK | 30053760 | 118 | CANNONVALE NO 2 | 118_Cannonvale No 2 66 kV | Rating (A) | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193
NQMK | 30053760 | 118 | CANNONVALE NO 2 | 118_Cannonvale No 2 66 kV | Time | 16:30 | 18:30 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 17:30 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00
NQMK | 30053760 | 118 | CANNONVALE NO 2 | 118_Cannonvale No 2 66 kV | Voltage at Constrained Conductor | 66.6909 | 66.8863 | 67.1436 | 66.7792 | 67.0284 | 67.2271 | 66.7852 | 66.6358 | 67.233 | 66.7551 | 66.9992 | 67.2056 | 66.6808 | 66.9257 | 66.3777
NQMK | 30053761 | 119 | CANNONVALE NO 1 | 119_Cannonvale No 1 66 kV | % of Rated A | 84.6369 | 59.221 | 48.0425 | 79.8885 | 59.5149 | 47.859 | 79.8818 | 59.8846 | 47.8626 | 80.1319 | 59.7089 | 47.9836 | 81.4933 | 60.7738 | 49.2052
NQMK | 30053761 | 119 | CANNONVALE NO 1 | 119_Cannonvale No 1 66 kV | Limiting Line Name | TR_LINE 13013_1 | TR_LINE 13013_1 | TR_LINE 13013_1 | TR_LINE 13015_1 | TR_LINE 13015_1 | TR_LINE 13015_1 | TR_LINE 13015_1 | TR_LINE 13015_1 | TR_LINE 13015_1 | TR_LINE 13015_1 | TR_LINE 13015_1 | TR_LINE 13015_1 | TR_LINE 13015_1 | TR_LINE 13015_1 | TR_LINE 13015_1
NQMK | 30053761 | 119 | CANNONVALE NO 1 | 119_Cannonvale No 1 66 kV | Loading (A) | 156.575 | 153.3792 | 121.0649 | 147.7938 | 154.1437 | 120.6046 | 147.7813 | 155.1012 | 120.6137 | 148.2441 | 154.6461 | 120.9187 | 150.7626 | 157.4042 | 123.9972
NQMK | 30053761 | 119 | CANNONVALE NO 1 | 119_Cannonvale No 1 66 kV | Loading (MVA) | 17.9491 | 17.6469 | 13.8302 | 16.9997 | 17.7939 | 13.8368 | 16.9998 | 17.7977 | 13.8364 | 17.0449 | 17.8436 | 13.8702 | 17.3121 | 18.114 | 14.1907
NQMK | 30053761 | 119 | CANNONVALE NO 1 | 119_Cannonvale No 1 66 kV | Loading (MW) | 17.8069 | 17.5232 | 13.785 | 16.7955 | 17.626 | 13.362 | 16.7954 | 17.624 | 13.3621 | 16.8446 | 17.6797 | 13.4003 | 17.1309 | 17.9697 | 13.7556
NQMK | 30053761 | 119 | CANNONVALE NO 1 | 119_Cannonvale No 1 66 kV | Power Factor | 0.99207 | 0.99299 | 0.99673 | 0.98799 | 0.99056 | 0.96569 | 0.98797 | 0.99024 | 0.96572 | 0.98825 | 0.99081 | 0.96612 | 0.98953 | 0.99204 | 0.96934
NQMK | 30053761 | 119 | CANNONVALE NO 1 | 119_Cannonvale No 1 66 kV | Rating (A) | 185 | 259 | 252 | 185 | 259 | 252 | 185 | 259 | 252 | 185 | 259 | 252 | 185 | 259 | 252
NQMK | 30053761 | 119 | CANNONVALE NO 1 | 119_Cannonvale No 1 66 kV | Time | 16:00 | 17:30 | 8:30 | 16:30 | 18:00 | 8:30 | 16:30 | 17:30 | 8:30 | 16:30 | 18:00 | 8:30 | 16:30 | 18:30 | 22:00
NQMK | 30053761 | 119 | CANNONVALE NO 1 | 119_Cannonvale No 1 66 kV | Voltage at Constrained Conductor | 66.1851 | 66.4266 | 65.9553 | 66.4086 | 66.6477 | 66.2384 | 66.4147 | 66.2503 | 66.2319 | 66.3828 | 66.6167 | 66.2259 | 66.2973 | 66.441 | 66.074
NQMK | 30053762 | 120 | Proserpine-Calen | 120_Prosperpine - Calen 66 kV | % of Rated A | 23.5117 | 22.5095 | 17.8183 | 22.9304 | 21.9841 | 17.4609 | 22.9283 | 21.9809 | 17.4594 | 23.8996 | 22.9897 | 18.2438 | 23.9264 | 23.0153 | 18.4681
NQMK | 30053762 | 120 | Proserpine-Calen | 120_Prosperpine - Calen 66 kV | Limiting Line Name | TR_LINE 89457_1 | TR_LINE 10511_1 | TR_LINE 89457_1 | TR_LINE 89457_1 | TR_LINE 10511_1 | TR_LINE 89457_1 | TR_LINE 89457_1 | TR_LINE 10511_1 | TR_LINE 89457_1 | TR_LINE 89457_1 | TR_LINE 10511_1 | TR_LINE 89457_1 | TR_LINE 89457_1 | TR_LINE 10511_1 | TR_LINE 89457_1
NQMK | 30053762 | 120 | Proserpine-Calen | 120_Prosperpine - Calen 66 kV | Loading (A) | 31.0354 | 39.8407 | 30.2911 | 30.2681 | 38.9109 | 29.6835 | 30.2654 | 38.9052 | 29.681 | 31.5475 | 40.6907 | 31.0145 | 31.5829 | 40.736 | 31.3958
NQMK | 30053762 | 120 | Proserpine-Calen | 120_Prosperpine - Calen 66 kV | Loading (MVA) | 3.585 | 4.5595 | 3.5227 | 3.501 | 4.4611 | 3.4564 | 3.501 | 4.461 | 3.4564 | 3.6476 | 4.6597 | 3.6102 | 3.6476 | 4.6599 | 3.6096
NQMK | 30053762 | 120 | Proserpine-Calen | 120_Prosperpine - Calen 66 kV | Loading (MW) | 3.5785 | 4.5507 | 3.5094 | 3.4925 | 4.4538 | 3.4407 | 3.4925 | 4.4538 | 3.4407 | 3.6417 | 4.6503 | 3.5982 | 3.6418 | 4.6504 | 3.5997
NQMK | 30053762 | 120 | Proserpine-Calen | 120_Prosperpine - Calen 66 kV | Power Factor | 0.99819 | 0.99807 | 0.99621 | 0.99758 | 0.99837 | 0.99547 | 0.99758 | 0.99837 | 0.99546 | 0.99837 | 0.99797 | 0.99667 | 0.99841 | 0.99795 | 0.99727
NQMK | 30053762 | 120 | Proserpine-Calen | 120_Prosperpine - Calen 66 kV | Rating (A) | 132 | 177 | 170 | 132 | 177 | 170 | 132 | 177 | 170 | 132 | 177 | 170 | 132 | 177 | 170
NQMK | 30053762 | 120 | Proserpine-Calen | 120_Prosperpine - Calen 66 kV | Time | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00
NQMK | 30053762 | 120 | Proserpine-Calen | 120_Prosperpine - Calen 66 kV | Voltage at Constrained Conductor | 66.6909 | 66.0744 | 67.1436 | 66.7792 | 66.1921 | 67.2271 | 66.7852 | 66.2015 | 67.233 | 66.7551 | 66.1156 | 67.2056 | 66.6808 | 66.0449 | 66.3777
NQMK | 80001012 | PROS-KECR-1 | Proserpine No.1 66kV Feeder | PROS-KECR-1_Proserpine No 1 66 kV | % of Rated A | 15.72 | 15.3129 | 12.6298 | 15.5713 | 15.1758 | 12.5114 | 15.4423 | 15.0492 | 12.4077 | 15.577 | 15.1796 | 12.5154 | 15.7224 | 15.317 | 12.778
NQMK | 80001012 | PROS-KECR-1 | Proserpine No.1 66kV Feeder | PROS-KECR-1_Proserpine No 1 66 kV | Limiting Line Name | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1
NQMK | 80001012 | PROS-KECR-1 | Proserpine No.1 66kV Feeder | PROS-KECR-1_Proserpine No 1 66 kV | Loading (A) | 27.8244 | 36.1384 | 28.5434 | 27.5612 | 35.8149 | 28.2757 | 27.3329 | 35.5161 | 28.0415 | 27.5713 | 35.8238 | 28.2849 | 27.8287 | 36.1482 | 28.8783
NQMK | 80001012 | PROS-KECR-1 | Proserpine No.1 66kV Feeder | PROS-KECR-1_Proserpine No 1 66 kV | Loading (MVA) | 3.2139 | 4.1625 | 3.3193 | 3.1877 | 4.1285 | 3.2923 | 3.1616 | 4.0946 | 3.2653 | 3.1877 | 4.1285 | 3.2923 | 3.2139 | 4.1625 | 3.3199
NQMK | 80001012 | PROS-KECR-1 | Proserpine No.1 66kV Feeder | PROS-KECR-1_Proserpine No 1 66 kV | Loading (MW) | 3.095 | 3.9991 | 3.1961 | 3.07 | 3.9669 | 3.1703 | 3.0451 | 3.9346 | 3.1445 | 3.07 | 3.9669 | 3.1703 | 3.095 | 3.9991 | 3.1961
NQMK | 80001012 | PROS-KECR-1 | Proserpine No.1 66kV Feeder | PROS-KECR-1_Proserpine No 1 66 kV | Power Factor | 0.96301 | 0.96075 | 0.96287 | 0.96309 | 0.96085 | 0.96295 | 0.96315 | 0.96093 | 0.96301 | 0.96308 | 0.96084 | 0.96294 | 0.96301 | 0.96075 | 0.96269
NQMK | 80001012 | PROS-KECR-1 | Proserpine No.1 66kV Feeder | PROS-KECR-1_Proserpine No 1 66 kV | Rating (A) | 177 | 236 | 226 | 177 | 236 | 226 | 177 | 236 | 226 | 177 | 236 | 226 | 177 | 236 | 226
NQMK | 80001012 | PROS-KECR-1 | Proserpine No.1 66kV Feeder | PROS-KECR-1_Proserpine No 1 66 kV | Time | 16:30 | 19:30 | 22:00 | 16:30 | 19:30 | 22:00 | 16:30 | 19:30 | 22:00 | 16:30 | 19:30 | 22:00 | 16:30 | 19:30 | 22:00
NQMK | 80001012 | PROS-KECR-1 | Proserpine No.1 66kV Feeder | PROS-KECR-1_Proserpine No 1 66 kV | Voltage at Constrained Conductor | 66.6875 | 66.5005 | 67.1402 | 66.7758 | 66.5532 | 67.2236 | 66.7819 | 66.5616 | 67.2295 | 66.7517 | 66.537 | 67.2021 | 66.6774 | 66.4827 | 66.3741
NQMK | 80075847 | PROS-KECR-2 | Proserpine No.2 66kV Feeder | PROS-KECR-2_Proserpine No 2 66 kV | % of Rated A | 31.4887 | 30.6877 | 25.2995 | 31.1903 | 30.4124 | 25.0618 | 30.9315 | 30.1582 | 24.8539 | 31.2018 | 30.42 | 25.07 | 31.4935 | 30.6865 | 25.5973
NQMK | 80075847 | PROS-KECR-2 | Proserpine No.2 66kV Feeder | PROS-KECR-2_Proserpine No 2 66 kV | Limiting Line Name | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1
NQMK | 80075847 | PROS-KECR-2 | Proserpine No.2 66kV Feeder | PROS-KECR-2_Proserpine No 2 66 kV | Loading (A) | 55.7334 | 72.4214 | 57.1753 | 55.2052 | 71.7716 | 56.638 | 54.7471 | 71.1717 | 56.1681 | 55.2255 | 71.7896 | 56.6565 | 55.7419 | 72.4185 | 57.8482
NQMK | 80075847 | PROS-KECR-2 | Proserpine No.2 66kV Feeder | PROS-KECR-2_Proserpine No 2 66 kV | Loading (MVA) | 6.4375 | 8.3416 | 6.6489 | 6.3849 | 8.2733 | 6.5946 | 6.3325 | 8.2052 | 6.5404 | 6.385 | 8.2733 | 6.5946 | 6.4375 | 8.339 | 6.6504
NQMK | 80075847 | PROS-KECR-2 | Proserpine No.2 66kV Feeder | PROS-KECR-2_Proserpine No 2 66 kV | Loading (MW) | 6.2 | 8.0151 | 6.4027 | 6.1499 | 7.9503 | 6.3509 | 6.0998 | 7.8855 | 6.2992 | 6.1499 | 7.9503 | 6.3509 | 6.2 | 8.0146 | 6.4029
NQMK | 80075847 | PROS-KECR-2 | Proserpine No.2 66kV Feeder | PROS-KECR-2_Proserpine No 2 66 kV | Power Factor | 0.96311 | 0.96086 | 0.96297 | 0.96319 | 0.96096 | 0.96305 | 0.96325 | 0.96104 | 0.96311 | 0.96318 | 0.96095 | 0.96304 | 0.9631 | 0.9611 | 0.96279
NQMK | 80075847 | PROS-KECR-2 | Proserpine No.2 66kV Feeder | PROS-KECR-2_Proserpine No 2 66 kV | Rating (A) | 177 | 236 | 226 | 177 | 236 | 226 | 177 | 236 | 226 | 177 | 236 | 226 | 177 | 236 | 226
NQMK | 80075847 | PROS-KECR-2 | Proserpine No.2 66kV Feeder | PROS-KECR-2_Proserpine No 2 66 kV | Time | 16:30 | 19:30 | 22:00 | 16:30 | 19:30 | 22:00 | 16:30 | 19:30 | 22:00 | 16:30 | 19:30 | 22:00 | 16:30 | 19:30 | 22:00
NQMK | 80075847 | PROS-KECR-2 | Proserpine No.2 66kV Feeder | PROS-KECR-2_Proserpine No 2 66 kV | Voltage at Constrained Conductor | 66.687 | 66.4998 | 67.1396 | 66.7753 | 66.5525 | 67.2231 | 66.7814 | 66.5609 | 67.229 | 66.7512 | 66.5363 | 67.2016 | 66.6769 | 66.482 | 66.3736
NQMK | 84211409 | 426 | MT ROOPER | 426_Mt Rooper 66 kV | % of Rated A | 48.1268 | 40.0716 | 34.5185 | 46.9989 | 39.2515 | 33.7875 | 46.9945 | 39.5727 | 33.7912 | 47.0217 | 39.2757 | 33.797 | 47.4843 | 39.6656 | 34.1018
NQMK | 84211409 | 426 | MT ROOPER | 426_Mt Rooper 66 kV | Limiting Line Name | TR_LINE 97526_1 | TR_CABLE 11763_1 | TR_CABLE 11763_1 | TR_LINE 97526_1 | TR_CABLE 11763_1 | TR_CABLE 11763_1 | TR_LINE 97526_1 | TR_CABLE 11763_1 | TR_CABLE 11763_1 | TR_LINE 97526_1 | TR_CABLE 11763_1 | TR_CABLE 11763_1 | TR_LINE 97526_1 | TR_CABLE 11763_1 | TR_CABLE 11763_1
NQMK | 84211409 | 426 | MT ROOPER | 426_Mt Rooper 66 kV | Loading (A) | 119.835 | 112.2005 | 96.6517 | 117.0264 | 109.9041 | 94.6051 | 117.0155 | 110.8035 | 94.6155 | 117.0832 | 109.9719 | 94.6316 | 118.2352 | 111.0636 | 95.4851
NQMK | 84211409 | 426 | MT ROOPER | 426_Mt Rooper 66 kV | Loading (MVA) | 13.3261 | 12.4956 | 10.7682 | 13.2179 | 12.4015 | 10.6869 | 13.2178 | 12.4057 | 10.687 | 13.2183 | 12.4018 | 10.687 | 13.3217 | 12.4962 | 10.7677
NQMK | 84211409 | 426 | MT ROOPER | 426_Mt Rooper 66 kV | Loading (MW) | 13.1217 | 12.2445 | 10.5681 | 13.0198 | 12.1527 | 10.4889 | 13.0198 | 12.1546 | 10.4889 | 13.02 | 12.1529 | 10.489 | 13.1201 | 12.2445 | 10.5677
NQMK | 84211409 | 426 | MT ROOPER | 426_Mt Rooper 66 kV | Power Factor | 0.98466 | 0.9799 | 0.98142 | 0.98501 | 0.97994 | 0.98147 | 0.98502 | 0.97975 | 0.98147 | 0.985 | 0.97993 | 0.98147 | 0.98486 | 0.97986 | 0.98143
NQMK | 84211409 | 426 | MT ROOPER | 426_Mt Rooper 66 kV | Rating (A) | 249 | 280 | 280 | 249 | 280 | 280 | 249 | 280 | 280 | 249 | 280 | 280 | 249 | 280 | 280
NQMK | 84211409 | 426 | MT ROOPER | 426_Mt Rooper 66 kV | Time | 16:00 | 17:30 | 8:30 | 16:00 | 17:30 | 8:30 | 16:00 | 17:30 | 8:30 | 16:00 | 17:30 | 8:30 | 16:00 | 17:30 | 8:30
NQMK | 84211409 | 426 | MT ROOPER | 426_Mt Rooper 66 kV | Voltage at Constrained Conductor | 64.2034 | 64.2988 | 64.3237 | 65.2107 | 65.1476 | 65.2194 | 65.2164 | 64.6411 | 65.2126 | 65.1809 | 65.1093 | 65.2019 | 65.0509 | 64.9599 | 65.1066
SW | 60026645 | F008D | CENTRAL DALBY 2 | F008D_Central Dalby 2 33 kV | % of Rated A | 32.0339 | 32.6018 | 21.1662 | 31.6171 | 32.1778 | 20.9196 | 31.3479 | 31.9125 | 20.7669 | 31.7668 | 31.9243 | 20.6495 | 32.0701 | 31.768 | 20.8189
SW | 60026645 | F008D | CENTRAL DALBY 2 | F008D_Central Dalby 2 33 kV | Limiting Line Name | TR_CABLE 4401_1 | TR_CABLE 4401_1 | TR_LINE 92498_1 | TR_CABLE 4401_1 | TR_CABLE 4401_1 | TR_LINE 92498_1 | TR_CABLE 4401_1 | TR_CABLE 4401_1 | TR_LINE 92498_1 | TR_CABLE 4401_1 | TR_CABLE 4401_1 | TR_LINE 92498_1 | TR_CABLE 4401_1 | TR_CABLE 4401_1 | TR_LINE 92498_1
SW | 60026645 | F008D | CENTRAL DALBY 2 | F008D_Central Dalby 2 33 kV | Loading (A) | 160.1694 | 163.0089 | 101.4834 | 158.0855 | 160.8892 | 100.3002 | 156.7394 | 159.5626 | 99.5673 | 158.834 | 159.6215 | 99.0028 | 160.3507 | 158.84 | 99.8169
SW | 60026645 | F008D | CENTRAL DALBY 2 | F008D_Central Dalby 2 33 kV | Loading (MVA) | 9.2027 | 9.2483 | 5.8875 | 9.0906 | 9.1363 | 5.8208 | 9.0187 | 9.0663 | 5.7796 | 9.0262 | 9.0665 | 5.7792 | 9.101 | 9.025 | 5.7942
SW | 60026645 | F008D | CENTRAL DALBY 2 | F008D_Central Dalby 2 33 kV | Loading (MW) | 8.6461 | 8.6849 | 5.6055 | 8.5444 | 8.5836 | 5.5437 | 8.4788 | 8.5199 | 5.5055 | 8.4787 | 8.5199 | 5.5052 | 8.551 | 8.4751 | 5.5186
SW | 60026645 | F008D | CENTRAL DALBY 2 | F008D_Central Dalby 2 33 kV | Power Factor | 0.93951 | 0.93907 | 0.95211 | 0.93991 | 0.93951 | 0.9524 | 0.94013 | 0.93973 | 0.95257 | 0.93934 | 0.93971 | 0.95259 | 0.93957 | 0.93907 | 0.95243
SW | 60026645 | F008D | CENTRAL DALBY 2 | F008D_Central Dalby 2 33 kV | Rating (A) | 500 | 500 | 480 | 500 | 500 | 480 | 500 | 500 | 480 | 500 | 500 | 480 | 500 | 500 | 480
SW | 60026645 | F008D | CENTRAL DALBY 2 | F008D_Central Dalby 2 33 kV | Time | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00 | 16:30 | 17:00 | 22:30
SW | 60026645 | F008D | CENTRAL DALBY 2 | F008D_Central Dalby 2 33 kV | Voltage at Constrained Conductor | 33.1724 | 32.7561 | 33.4944 | 33.2002 | 32.7855 | 33.5058 | 33.2206 | 32.805 | 33.5136 | 32.8097 | 32.7935 | 33.7024 | 32.7685 | 32.8041 | 33.5141
SW | 60026646 | F019D | WEST DALBY NO 1 | F019D_West Dalby No 1 33 kV | % of Rated A | 34.6636 | 31.8086 | 26.0746 | 34.221 | 31.4047 | 25.8679 | 33.906 | 31.1271 | 25.7094 | 34.3594 | 31.1385 | 25.7147 | 34.6255 | 31.0744 | 25.8207
SW | 60026646 | F019D | WEST DALBY NO 1 | F019D_West Dalby No 1 33 kV | Limiting Line Name | TR_LINE 58890_1 | TR_LINE 58890_1 | TR_LINE 58890_1 | TR_LINE 58890_1 | TR_LINE 58890_1 | TR_LINE 58890_1 | TR_LINE 58890_1 | TR_LINE 58890_1 | TR_LINE 58890_1 | TR_LINE 58890_1 | TR_LINE 58890_1 | TR_LINE 58890_1 | TR_LINE 58890_1 | TR_LINE 58890_1 | TR_LINE 58890_1
SW | 60026646 | F019D | WEST DALBY NO 1 | F019D_West Dalby No 1 33 kV | Loading (A) | 129.9593 | 130.0684 | 95.9214 | 128.2997 | 128.4169 | 95.1604 | 127.1184 | 127.2813 | 94.5771 | 128.8187 | 127.3281 | 94.5966 | 129.817 | 127.0657 | 94.9869
SW | 60026646 | F019D | WEST DALBY NO 1 | F019D_West Dalby No 1 33 kV | Loading (MVA) | 7.5357 | 7.4501 | 5.5365 | 7.4446 | 7.361 | 5.4942 | 7.38 | 7.2996 | 5.4616 | 7.3881 | 7.2998 | 5.4617 | 7.4368 | 7.2868 | 5.4815
SW | 60026646 | F019D | WEST DALBY NO 1 | F019D_West Dalby No 1 33 kV | Loading (MW) | 7.1377 | 7.0639 | 5.1504 | 7.0542 | 6.9824 | 5.1104 | 6.9949 | 6.926 | 5.0799 | 6.9967 | 6.926 | 5.0799 | 7.0442 | 6.9079 | 5.0989
SW | 60026646 | F019D | WEST DALBY NO 1 | F019D_West Dalby No 1 33 kV | Power Factor | 0.94718 | 0.94816 | 0.93026 | 0.94755 | 0.94856 | 0.93016 | 0.94782 | 0.94881 | 0.93011 | 0.94702 | 0.94879 | 0.9301 | 0.94721 | 0.948 | 0.9302
SW | 60026646 | F019D | WEST DALBY NO 1 | F019D_West Dalby No 1 33 kV | Rating (A) | 375 | 409 | 368 | 375 | 409 | 368 | 375 | 409 | 368 | 375 | 409 | 368 | 375 | 409 | 368
SW | 60026646 | F019D | WEST DALBY NO 1 | F019D_West Dalby No 1 33 kV | Time | 16:30 | 17:30 | 8:00 | 16:30 | 17:30 | 8:00 | 16:30 | 17:30 | 8:00 | 16:30 | 17:30 | 8:00 | 16:30 | 17:00 | 8:00
SW | 60026646 | F019D | WEST DALBY NO 1 | F019D_West Dalby No 1 33 kV | Voltage at Constrained Conductor | 33.4776 | 33.0698 | 33.3243 | 33.5009 | 33.0946 | 33.3338 | 33.5186 | 33.1113 | 33.3408 | 33.1125 | 33.0999 | 33.3344 | 33.0744 | 33.1093 | 33.3176
SW | 60026664 | F039D | WEST DALBY NO 2 | F039D_West Dalby No 2 33 kV | % of Rated A | 27.8883 | 8.7956 | 30.4236 | 28.0154 | 8.7799 | 30.3088 | 28.0796 | 8.6134 | 30.1383 | 27.7075 | 8.6761 | 30.1447 | 27.7675 | 8.4931 | 30.0446
SW | 60026664 | F039D | WEST DALBY NO 2 | F039D_West Dalby No 2 33 kV | Limiting Line Name | TR_CABLE 139_1 | TR_CABLE 139_1 | TR_CABLE 139_1 | TR_CABLE 139_1 | TR_CABLE 139_1 | TR_CABLE 139_1 | TR_CABLE 139_1 | TR_CABLE 139_1 | TR_CABLE 139_1 | TR_CABLE 139_1 | TR_CABLE 139_1 | TR_CABLE 139_1 | TR_CABLE 139_1 | TR_CABLE 139_1 | TR_CABLE 139_1
SW | 60026664 | F039D | WEST DALBY NO 2 | F039D_West Dalby No 2 33 kV | Loading (A) | 79.2027 | 24.9796 | 86.4031 | 79.5636 | 24.9349 | 86.0771 | 79.746 | 24.4619 | 85.5927 | 78.6892 | 24.6403 | 85.6108 | 78.8597 | 24.1204 | 85.3266
SW | 60026664 | F039D | WEST DALBY NO 2 | F039D_West Dalby No 2 33 kV | Loading (MVA) | 4.5728 | 1.4446 | 4.9484 | 4.5672 | 1.4424 | 4.9314 | 4.5514 | 1.4241 | 4.9049 | 4.5452 | 1.4257 | 4.905 | 4.525 | 1.3946 | 4.8861
SW | 60026664 | F039D | WEST DALBY NO 2 | F039D_West Dalby No 2 33 kV | Loading (MW) | 4.1367 | 1.36 | 4.5315 | 4.13 | 1.3581 | 4.5154 | 4.112 | 1.3413 | 4.4899 | 4.1105 | 1.3415 | 4.4899 | 4.0881 | 1.3117 | 4.4713
SW | 60026664 | F039D | WEST DALBY NO 2 | F039D_West Dalby No 2 33 kV | Power Factor | 0.90463 | 0.94147 | 0.91576 | 0.90427 | 0.94156 | 0.91564 | 0.90346 | 0.94183 | 0.91539 | 0.90435 | 0.94091 | 0.91538 | 0.90345 | 0.94056 | 0.9151
SW | 60026664 | F039D | WEST DALBY NO 2 | F039D_West Dalby No 2 33 kV | Rating (A) | 284 | 284 | 284 | 284 | 284 | 284 | 284 | 284 | 284 | 284 | 284 | 284 | 284 | 284 | 284
SW | 60026664 | F039D | WEST DALBY NO 2 | F039D_West Dalby No 2 33 kV | Time | 11:00 | 21:30 | 8:00 | 11:00 | 21:30 | 8:00 | 11:00 | 21:30 | 8:00 | 11:00 | 21:30 | 8:00 | 11:00 | 21:30 | 8:00
SW | 60026664 | F039D | WEST DALBY NO 2 | F039D_West Dalby No 2 33 kV | Voltage at Constrained Conductor | 33.3332 | 33.3878 | 33.0653 | 33.1417 | 33.3988 | 33.0768 | 32.9512 | 33.6123 | 33.0853 | 33.3487 | 33.4065 | 33.0789 | 33.1287 | 33.3821 | 33.0611
SW | 60026667 | F060T | TARA | F060T_Tara 33 kV | % of Rated A | 15.495 | 12.9984 | 11.1588 | 15.4903 | 12.9946 | 11.1577 | 14.7939 | 12.364 | 10.7536 | 14.7681 | 12.3667 | 10.7859 | 15.4632 | 13.0025 | 11.1745
SW | 60026667 | F060T | TARA | F060T_Tara 33 kV | Limiting Line Name | TR_LINE 23982_1 | TR_LINE 23982_1 | TR_LINE 23982_1 | TR_LINE 23982_1 | TR_LINE 23982_1 | TR_LINE 23982_1 | TR_LINE 23982_1 | TR_LINE 23982_1 | TR_LINE 23982_1 | TR_LINE 23982_1 | TR_LINE 23982_1 | TR_LINE 23982_1 | TR_LINE 23982_1 | TR_LINE 23982_1 | TR_LINE 23982_1
SW | 60026667 | F060T | TARA | F060T_Tara 33 kV | Loading (A) | 14.4104 | 15.8581 | 13.0558 | 14.406 | 15.8534 | 13.0546 | 13.7583 | 15.0841 | 12.5817 | 13.7344 | 15.0873 | 12.6194 | 14.3808 | 15.8631 | 13.0741
SW | 60026667 | F060T | TARA | F060T_Tara 33 kV | Loading (MVA) | 0.82353 | 0.91089 | 0.74946 | 0.82367 | 0.91102 | 0.74958 | 0.78735 | 0.86764 | 0.72286 | 0.78864 | 0.86753 | 0.71835 | 0.8246 | 0.91077 | 0.74791
SW | 60026667 | F060T | TARA | F060T_Tara 33 kV | Loading (MW) | 0.78458 | 0.88027 | 0.68452 | 0.78458 | 0.88026 | 0.68452 | 0.74082 | 0.82985 | 0.64919 | 0.74079 | 0.82986 | 0.64919 | 0.78455 | 0.88028 | 0.68453
SW | 60026667 | F060T | TARA | F060T_Tara 33 kV | Power Factor | 0.95271 | 0.96638 | 0.91335 | 0.95254 | 0.96624 | 0.91321 | 0.94091 | 0.95645 | 0.89809 | 0.93933 | 0.95658 | 0.90373 | 0.95142 | 0.96652 | 0.91525
SW | 60026667 | F060T | TARA | F060T_Tara 33 kV | Rating (A) | 93 | 122 | 117 | 93 | 122 | 117 | 93 | 122 | 117 | 93 | 122 | 117 | 93 | 122 | 117
SW | 60026667 | F060T | TARA | F060T_Tara 33 kV | Time | 16:00 | 18:00 | 22:00 | 16:00 | 18:00 | 22:00 | 16:00 | 18:00 | 22:00 | 16:00 | 18:00 | 22:00 | 16:00 | 18:00 | 22:00
SW | 60026667 | F060T | TARA | F060T_Tara 33 kV | Voltage at Constrained Conductor | 32.9946 | 33.1632 | 33.1424 | 33.0103 | 33.1774 | 33.1507 | 33.04 | 33.2091 | 33.1705 | 33.1518 | 33.1979 | 32.8651 | 33.1056 | 33.148 | 33.0277
SW | 60026669 | F067C | KOGAN | F067C_Kogan 33 kV | % of Rated A | 59.1912 | 31.6168 | 40.5331 | 59.1849 | 31.6106 | 40.5305 | 59.177 | 31.9834 | 40.5266 | 59.1706 | 31.9773 | 40.5239 | 59.1842 | 31.9894 | 40.529
SW | 60026669 | F067C | KOGAN | F067C_Kogan 33 kV | Limiting Line Name | TR_LINE 27340_1 | TR_LINE 27340_1 | TR_LINE 27340_1 | TR_LINE 27340_1 | TR_LINE 27340_1 | TR_LINE 27340_1 | TR_LINE 27340_1 | TR_LINE 27340_1 | TR_LINE 27340_1 | TR_LINE 27340_1 | TR_LINE 27340_1 | TR_LINE 27340_1 | TR_LINE 27340_1 | TR_LINE 27340_1 | TR_LINE 27340_1
SW | 60026669 | F067C | KOGAN | F067C_Kogan 33 kV | Loading (A) | 54.8986 | 38.4294 | 47.2768 | 54.8926 | 38.4219 | 47.2737 | 54.8853 | 38.8753 | 47.2692 | 54.8793 | 38.8678 | 47.266 | 54.892 | 38.8826 | 47.272
SW | 60026669 | F067C | KOGAN | F067C_Kogan 33 kV | Loading (MVA) | 3.0699 | 2.1616 | 2.6354 | 3.0698 | 2.1615 | 2.6354 | 3.0698 | 2.1875 | 2.6354 | 3.0697 | 2.1875 | 2.6354 | 3.0698 | 2.1875 | 2.6354
SW | 60026669 | F067C | KOGAN | F067C_Kogan 33 kV | Loading (MW) | 2.4247 | 1.7566 | 2.0984 | 2.4247 | 1.7566 | 2.0984 | 2.4247 | 1.7687 | 2.0984 | 2.4247 | 1.7687 | 2.0984 | 2.4247 | 1.7687 | 2.0984
SW | 60026669 | F067C | KOGAN | F067C_Kogan 33 kV | Power Factor | 0.78985 | 0.81267 | 0.79623 | 0.78986 | 0.81268 | 0.79623 | 0.78987 | 0.80853 | 0.79624 | 0.78987 | 0.80854 | 0.79624 | 0.78986 | 0.80852 | 0.79623
SW | 60026669 | F067C | KOGAN | F067C_Kogan 33 kV | Rating (A) | 93 | 122 | 117 | 93 | 122 | 117 | 93 | 122 | 117 | 93 | 122 | 117 | 93 | 122 | 117
SW | 60026669 | F067C | KOGAN | F067C_Kogan 33 kV | Time | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30
SW | 60026669 | F067C | KOGAN | F067C_Kogan 33 kV | Voltage at Constrained Conductor | 32.2846 | 32.4748 | 32.1839 | 32.2876 | 32.4806 | 32.1858 | 32.2914 | 32.4871 | 32.1886 | 32.2944 | 32.4929 | 32.1906 | 32.288 | 32.4816 | 32.1869
SW | 60026670 | F069C | BRIGALOW | F069C_Brigalow 33 kV | % of Rated A | 32.2912 | 24.6945 | 19.4343 | 32.2864 | 24.6908 | 19.4329 | 32.2796 | 24.6853 | 19.4298 | 32.2748 | 24.6817 | 19.4283 | 32.2843 | 24.6898 | 19.4315
SW | 60026670 | F069C | BRIGALOW | F069C_Brigalow 33 kV | Limiting Line Name | TR_LINE 28423_1 | TR_LINE 28423_1 | TR_LINE 28423_1 | TR_LINE 28423_1 | TR_LINE 28423_1 | TR_LINE 28423_1 | TR_LINE 28423_1 | TR_LINE 28423_1 | TR_LINE 28423_1 | TR_LINE 28423_1 | TR_LINE 28423_1 | TR_LINE 28423_1 | TR_LINE 28423_1 | TR_LINE 28423_1 | TR_LINE 28423_1
SW | 60026670 | F069C | BRIGALOW | F069C_Brigalow 33 kV | Loading (A) | 19.6975 | 19.0146 | 14.187 | 19.6946 | 19.0118 | 14.186 | 19.6904 | 19.0075 | 14.1837 | 19.6875 | 19.0048 | 14.1826 | 19.6933 | 19.011 | 14.185
SW | 60026670 | F069C | BRIGALOW | F069C_Brigalow 33 kV | Loading (MVA) | 1.1217 | 1.0829 | 0.806 | 1.1217 | 1.0828 | 0.806 | 1.1217 | 1.0828 | 0.806 | 1.1217 | 1.0828 | 0.806 | 1.1217 | 1.0828 | 0.806
SW | 60026670 | F069C | BRIGALOW | F069C_Brigalow 33 kV | Loading (MW) | 1.1195 | 1.081 | 0.80595 | 1.1195 | 1.081 | 0.80595 | 1.1195 | 1.081 | 0.80595 | 1.1195 | 1.081 | 0.80595 | 1.1195 | 1.081 | 0.80595
SW | 60026670 | F069C | BRIGALOW | F069C_Brigalow 33 kV | Power Factor | 0.99801 | 0.99827 | 0.99994 | 0.99801 | 0.99828 | 0.99994 | 0.99801 | 0.99828 | 0.99994 | 0.99802 | 0.99828 | 0.99994 | 0.99801 | 0.99828 | 0.99994
SW | 60026670 | F069C | BRIGALOW | F069C_Brigalow 33 kV | Rating (A) | 61 | 77 | 73 | 61 | 77 | 73 | 61 | 77 | 73 | 61 | 77 | 73 | 61 | 77 | 73
SW | 60026670 | F069C | BRIGALOW | F069C_Brigalow 33 kV | Time | 14:30 | 18:30 | 22:30 | 14:30 | 18:30 | 22:30 | 14:30 | 18:30 | 22:30 | 14:30 | 18:30 | 22:30 | 14:30 | 18:30 | 22:30
SW | 60026670 | F069C | BRIGALOW | F069C_Brigalow 33 kV | Voltage at Constrained Conductor | 32.8784 | 32.8793 | 32.8009 | 32.883 | 32.8838 | 32.8033 | 32.8895 | 32.8908 | 32.8082 | 32.8941 | 32.8952 | 32.8107 | 32.885 | 32.8851 | 32.8054
SW | 60026673 | F073C | FAIRYMEADOW | F073C_Fairymeadow 33 kV | % of Rated A | 4.0916 | 4.5284 | 3.5311 | 4.091 | 4.5278 | 3.5309 | 4.0903 | 4.5271 | 3.5376 | 4.0898 | 4.5266 | 3.5372 | 4.0908 | 4.5278 | 3.5308
SW | 60026673 | F073C | FAIRYMEADOW | F073C_Fairymeadow 33 kV | Limiting Line Name | TR_LINE 174241_1 | TR_CABLE 124_1 | TR_LINE 174241_1 | TR_LINE 174241_1 | TR_CABLE 124_1 | TR_LINE 174241_1 | TR_LINE 174241_1 | TR_CABLE 124_1 | TR_LINE 177654_1 | TR_LINE 174241_1 | TR_CABLE 124_1 | TR_LINE 177654_1 | TR_LINE 174241_1 | TR_CABLE 124_1 | TR_LINE 174241_1
SW | 60026673 | F073C | FAIRYMEADOW | F073C_Fairymeadow 33 kV | Loading (A) | 3.8052 | 4.5284 | 4.0961 | 3.8047 | 4.5278 | 4.0958 | 3.804 | 4.5271 | 4.1036 | 3.8035 | 4.5266 | 4.1032 | 3.8045 | 4.5278 | 4.0958
SW | 60026673 | F073C | FAIRYMEADOW | F073C_Fairymeadow 33 kV | Loading (MVA) | 0.21939 | 0.25784 | 0.23839 | 0.21941 | 0.25784 | 0.23839 | 0.21942 | 0.25784 | 0.23398 | 0.21943 | 0.25784 | 0.23398 | 0.21941 | 0.25784 | 0.23839
SW | 60026673 | F073C | FAIRYMEADOW | F073C_Fairymeadow 33 kV | Loading (MW) | 0.21502 | 0.23949 | 0.23441 | 0.21502 | 0.23949 | 0.23441 | 0.21502 | 0.23949 | 0.23385 | 0.21502 | 0.23949 | 0.23385 | 0.21502 | 0.23949 | 0.23441
SW | 60026673 | F073C | FAIRYMEADOW | F073C_Fairymeadow 33 kV | Power Factor | 0.98005 | 0.92883 | 0.9833 | 0.98001 | 0.92883 | 0.98328 | 0.97996 | 0.92882 | 0.99942 | 0.97992 | 0.92882 | 0.99942 | 0.97999 | 0.92883 | 0.98327
SW | 60026673 | F073C | FAIRYMEADOW | F073C_Fairymeadow 33 kV | Rating (A) | 93 | 100 | 116 | 93 | 100 | 116 | 93 | 100 | 116 | 93 | 100 | 116 | 93 | 100 | 116
SW | 60026673 | F073C | FAIRYMEADOW | F073C_Fairymeadow 33 kV | Time | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00
SW | 60026673 | F073C | FAIRYMEADOW | F073C_Fairymeadow 33 kV | Voltage at Constrained Conductor | 33.2884 | 32.8732 | 33.6009 | 33.2945 | 32.8773 | 33.6038 | 33.302 | 32.8826 | 32.9202 | 33.3081 | 32.8867 | 32.9231 | 33.2969 | 32.8773 | 33.6046
SW | 60026674 | F075S | ST GEORGE TOWN | F075S_St George Town 33 kV | % of Rated A | 56.44 | 57.2715 | 40.5585 | 55.3318 | 56.147 | 39.769 | 55.3257 | 56.1403 | 39.8397 | 55.3243 | 56.139 | 39.8392 | 56.4324 | 57.2633 | 40.6303
SW | 60026674 | F075S | ST GEORGE TOWN | F075S_St George Town 33 kV | Limiting Line Name | TR_CABLE 16563_1 | TR_CABLE 16563_1 | TR_LINE 25567_1 | TR_CABLE 16563_1 | TR_CABLE 16563_1 | TR_LINE 25567_1 | TR_CABLE 16563_1 | TR_CABLE 16563_1 | TR_LINE 25567_1 | TR_CABLE 16563_1 | TR_CABLE 16563_1 | TR_LINE 25567_1 | TR_CABLE 16563_1 | TR_CABLE 16563_1 | TR_LINE 25567_1
SW | 60026674 | F075S | ST GEORGE TOWN | F075S_St George Town 33 kV | Loading (A) | 92.5616 | 93.9252 | 66.4933 | 90.7442 | 92.0811 | 65.1985 | 90.7341 | 92.0701 | 65.3144 | 90.7319 | 92.0679 | 65.3136 | 92.5491 | 93.9117 | 66.6111
SW | 60026674 | F075S | ST GEORGE TOWN | F075S_St George Town 33 kV | Loading (MVA) | 5.3372 | 5.4127 | 3.8097 | 5.2309 | 5.305 | 3.735 | 5.2309 | 5.3049 | 3.7354 | 5.2309 | 5.3049 | 3.7354 | 5.3371 | 5.4126 | 3.8101
SW | 60026674 | F075S | ST GEORGE TOWN | F075S_St George Town 33 kV | Loading (MW) | 5.1265 | 5.198 | 3.6749 | 5.026 | 5.0961 | 3.6037 | 5.026 | 5.0961 | 3.6039 | 5.026 | 5.0961 | 3.6039 | 5.1265 | 5.1979 | 3.6751
SW | 60026674 | F075S | ST GEORGE TOWN | F075S_St George Town 33 kV | Power Factor | 0.96053 | 0.96033 | 0.96463 | 0.96082 | 0.96063 | 0.96485 | 0.96083 | 0.96063 | 0.96481 | 0.96083 | 0.96063 | 0.96481 | 0.96054 | 0.96034 | 0.96459
SW | 60026674 | F075S | ST GEORGE TOWN | F075S_St George Town 33 kV | Rating (A) | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164
SW | 60026674 | F075S | ST GEORGE TOWN | F075S_St George Town 33 kV | Time | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00
SW | 60026674 | F075S | ST GEORGE TOWN | F075S_St George Town 33 kV | Voltage at Constrained Conductor | 33.2903 | 33.2713 | 33.079 | 33.2811 | 33.2622 | 33.0748 | 33.2846 | 33.2659 | 33.0191 | 33.2853 | 33.2666 | 33.0195 | 33.2945 | 33.2757 | 33.0236
SW | 60026675 | F077S | MAIN CAMP | F077S_Main Camp 33 kV | % of Rated A | 80.1883 | 59.1204 | 72.5624 | 80.2073 | 59.1405 | 72.5742 | 80.1948 | 59.1331 | 72.5655 | 80.1931 | 59.1315 | 72.5643 | 80.1739 | 59.1113 | 72.5525
SW | 60026675 | F077S | MAIN CAMP | F077S_Main Camp 33 kV | Limiting Line Name | TR_CABLE 16560_1 | TR_CABLE 16560_1 | TR_CABLE 16560_1 | TR_CABLE 16560_1 | TR_CABLE 16560_1 | TR_CABLE 16560_1 | TR_CABLE 16560_1 | TR_CABLE 16560_1 | TR_CABLE 16560_1 | TR_CABLE 16560_1 | TR_CABLE 16560_1 | TR_CABLE 16560_1 | TR_CABLE 16560_1 | TR_CABLE 16560_1 | TR_CABLE 16560_1
SW | 60026675 | F077S | MAIN CAMP | F077S_Main Camp 33 kV | Loading (A) | 80.1883 | 59.1204 | 72.5624 | 80.2073 | 59.1405 | 72.5742 | 80.1948 | 59.1331 | 72.5655 | 80.1931 | 59.1315 | 72.5643 | 80.1739 | 59.1113 | 72.5525
SW | 60026675 | F077S | MAIN CAMP | F077S_Main Camp 33 kV | Loading (MVA) | 4.6099 | 3.4077 | 4.1595 | 4.6101 | 3.4079 | 4.1597 | 4.61 | 3.4078 | 4.1596 | 4.61 | 3.4078 | 4.1596 | 4.6097 | 3.4076 | 4.1594
SW | 60026675 | F077S | MAIN CAMP | F077S_Main Camp 33 kV | Loading (MW) | 4.0918 | 3.1221 | 3.7297 | 4.0918 | 3.1221 | 3.7297 | 4.0918 | 3.1221 | 3.7297 | 4.0918 | 3.1221 | 3.7297 | 4.0917 | 3.1221 | 3.7296
SW | 60026675 | F077S | MAIN CAMP | F077S_Main Camp 33 kV | Power Factor | 0.8876 | 0.9162 | 0.89665 | 0.88757 | 0.91615 | 0.89663 | 0.88759 | 0.91617 | 0.89665 | 0.88759 | 0.91617 | 0.89665 | 0.88763 | 0.91622 | 0.89668
SW | 60026675 | F077S | MAIN CAMP | F077S_Main Camp 33 kV | Rating (A) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
SW | 60026675 | F077S | MAIN CAMP | F077S_Main Camp 33 kV | Time | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30
SW | 60026675 | F077S | MAIN CAMP | F077S_Main Camp 33 kV | Voltage at Constrained Conductor | 33.191 | 33.2781 | 33.0958 | 33.1848 | 33.2689 | 33.0915 | 33.1889 | 33.2723 | 33.0946 | 33.1894 | 33.273 | 33.0951 | 33.1957 | 33.2822 | 33.0993
SW | 60026676 | F079S | ST GEORGE MEATWORKS | F079S_St George Meatworks 33 kV | % of Rated A | 45.6896 | 46.6402 | 45.2986 | 45.7011 | 46.6516 | 45.3054 | 44.0664 | 45.2142 | 43.933 | 44.0656 | 45.2132 | 43.9325 | 44.0547 | 45.2023 | 43.9262
SW | 60026676 | F079S | ST GEORGE MEATWORKS | F079S_St George Meatworks 33 kV | Limiting Line Name | TR_CABLE 16561_1 | TR_CABLE 16561_1 | TR_CABLE 16561_1 | TR_CABLE 16561_1 | TR_CABLE 16561_1 | TR_CABLE 16561_1 | TR_CABLE 16561_1 | TR_CABLE 16561_1 | TR_CABLE 16561_1 | TR_CABLE 16561_1 | TR_CABLE 16561_1 | TR_CABLE 16561_1 | TR_CABLE 16561_1 | TR_CABLE 16561_1 | TR_CABLE 16561_1
SW | 60026676 | F079S | ST GEORGE MEATWORKS | F079S_St George Meatworks 33 kV | Loading (A) | 45.6896 | 46.6402 | 45.2986 | 45.7011 | 46.6516 | 45.3054 | 44.0664 | 45.2142 | 43.933 | 44.0656 | 45.2132 | 43.9325 | 44.0547 | 45.2023 | 43.9262
SW | 60026676 | F079S | ST GEORGE MEATWORKS | F079S_St George Meatworks 33 kV | Loading (MVA) | 2.6345 | 2.6863 | 2.6011 | 2.6345 | 2.6862 | 2.601 | 2.5405 | 2.6038 | 2.518 | 2.5405 | 2.6038 | 2.518 | 2.5406 | 2.6039 | 2.518
SW | 60026676 | F079S | ST GEORGE MEATWORKS | F079S_St George Meatworks 33 kV | Loading (MW) | 2.6343 | 2.6863 | 2.6007 | 2.6343 | 2.6862 | 2.6007 | 2.5395 | 2.6034 | 2.517 | 2.5395 | 2.6034 | 2.517 | 2.5396 | 2.6035 | 2.517
SW | 60026676 | F079S | ST GEORGE MEATWORKS | F079S_St George Meatworks 33 kV | Power Factor | 0.99993 | 0.99999 | 0.99986 | 0.99993 | 0.99999 | 0.99987 | 0.99962 | 0.99985 | 0.99959 | 0.99962 | 0.99985 | 0.99959 | 0.99961 | 0.99984 | 0.99958
SW | 60026676 | F079S | ST GEORGE MEATWORKS | F079S_St George Meatworks 33 kV | Rating (A) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
SW | 60026676 | F079S | ST GEORGE MEATWORKS | F079S_St George Meatworks 33 kV | Time | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00
SW | 60026676 | F079S | ST GEORGE MEATWORKS | F079S_St George Meatworks 33 kV | Voltage at Constrained Conductor | 33.291 | 33.2531 | 33.1517 | 33.2818 | 33.2443 | 33.1461 | 33.2852 | 33.2484 | 33.0905 | 33.2859 | 33.2492 | 33.0909 | 33.2951 | 33.258 | 33.0964
SW | 60026679 | F083C | CHINCHILLA | F083C_Chinchilla 33 kV | % of Rated A | 66.3357 | 63.7158 | 43.964 | 65.7879 | 63.2089 | 43.6272 | 65.2376 | 62.6988 | 43.2896 | 64.6909 | 62.1927 | 42.9531 | 65.741 | 63.2211 | 43.6574
SW | 60026679 | F083C | CHINCHILLA | F083C_Chinchilla 33 kV | Limiting Line Name | TR_LINE 195206_1 | TR_LINE 195206_1 | TR_LINE 195206_1 | TR_LINE 195206_1 | TR_LINE 195206_1 | TR_LINE 195206_1 | TR_LINE 195206_1 | TR_LINE 195206_1 | TR_LINE 195206_1 | TR_LINE 195206_1 | TR_LINE 195206_1 | TR_LINE 195206_1 | TR_LINE 195206_1 | TR_LINE 195206_1 | TR_LINE 195206_1
SW | 60026679 | F083C | CHINCHILLA | F083C_Chinchilla 33 kV | Loading (A) | 221.5591 | 214.7202 | 128.3728 | 219.7294 | 213.0118 | 127.3894 | 217.8913 | 211.2926 | 126.4036 | 216.0652 | 209.5874 | 125.4211 | 219.5727 | 213.0529 | 127.4776
SW | 60026679 | F083C | CHINCHILLA | F083C_Chinchilla 33 kV | Loading (MVA) | 12.7707 | 12.385 | 7.4713 | 12.6676 | 12.2886 | 7.4147 | 12.5645 | 12.1922 | 7.3582 | 12.4615 | 12.0958 | 7.3017 | 12.6594 | 12.2917 | 7.42
SW | 60026679 | F083C | CHINCHILLA | F083C_Chinchilla 33 kV | Loading (MW) | 12.3565 | 11.9939 | 7.2895 | 12.259 | 11.9026 | 7.2352 | 12.1615 | 11.8112 | 7.1809 | 12.0641 | 11.7198 | 7.1265 | 12.2527 | 11.9066 | 7.2408
SW | 60026679 | F083C | CHINCHILLA | F083C_Chinchilla 33 kV | Power Factor | 0.96757 | 0.96842 | 0.97567 | 0.96775 | 0.96859 | 0.97578 | 0.96793 | 0.96875 | 0.9759 | 0.96811 | 0.96891 | 0.97602 | 0.96787 | 0.96867 | 0.97585
SW | 60026679 | F083C | CHINCHILLA | F083C_Chinchilla 33 kV | Rating (A) | 334 | 337 | 292 | 334 | 337 | 292 | 334 | 337 | 292 | 334 | 337 | 292 | 334 | 337 | 292
SW | 60026679 | F083C | CHINCHILLA | F083C_Chinchilla 33 kV | Time | 16:30 | 17:00 | 22:00 | 16:30 | 17:00 | 22:00 | 16:30 | 17:00 | 22:00 | 16:30 | 17:00 | 22:00 | 16:30 | 17:00 | 22:00
SW | 60026679 | F083C | CHINCHILLA | F083C_Chinchilla 33 kV | Voltage at Constrained Conductor | 33.2785 | 33.3015 | 33.6019 | 33.2847 | 33.3072 | 33.6049 | 33.2923 | 33.3147 | 33.6086 | 33.2984 | 33.3204 | 33.6117 | 33.2871 | 33.3092 | 33.6057
SW | 60026682 | F095D | KAIMKILLENBUN | F095D_Kaimkillenbun 33 kV | % of Rated A | 19.5453 | 22.0866 | 17.7286 | 19.5324 | 21.8097 | 17.7226 | 19.5226 | 22.1507 | 17.7185 | 19.7663 | 22.0715 | 17.6198 | 21.3656 | 23.876 | 18.7665
SW | 60026682 | F095D | KAIMKILLENBUN | F095D_Kaimkillenbun 33 kV | Limiting Line Name | TR_LINE 81370_2 | TR_CABLE 5206_1 | TR_CABLE 5206_1 | TR_LINE 81370_2 | TR_CABLE 5206_1 | TR_CABLE 5206_1 | TR_LINE 81370_2 | TR_CABLE 5206_1 | TR_CABLE 5206_1 | TR_LINE 81370_2 | TR_CABLE 5206_1 | TR_CABLE 5206_1 | TR_LINE 23016_1 | TR_CABLE 5206_1 | TR_CABLE 5206_1
SW | 60026682 | F095D | KAIMKILLENBUN | F095D_Kaimkillenbun 33 kV | Loading (A) | 18.1771 | 22.0866 | 17.7286 | 18.1652 | 21.8097 | 17.7226 | 18.1561 | 22.1507 | 17.7185 | 18.3826 | 22.0715 | 17.6198 | 19.8686 | 23.876 | 18.7665
SW | 60026682 | F095D | KAIMKILLENBUN | F095D_Kaimkillenbun 33 kV | Loading (MVA) | 1.0577 | 1.2732 | 1.0287 | 1.0577 | 1.2725 | 1.0287 | 1.0577 | 1.2732 | 1.0287 | 1.058 | 1.2731 | 1.0287 | 1.1403 | 1.3758 | 1.1015
SW | 60026682 | F095D | KAIMKILLENBUN | F095D_Kaimkillenbun 33 kV | Loading (MW) | 1.0573 | 1.2732 | 1.0263 | 1.0573 | 1.2725 | 1.0263 | 1.0573 | 1.2732 | 1.0263 | 1.0578 | 1.2731 | 1.0261 | 1.1402 | 1.3743 | 1.1004
SW | 60026682 | F095D | KAIMKILLENBUN | F095D_Kaimkillenbun 33 kV | Power Factor | 0.99964 | 1 | 0.99767 | 0.99963 | 0.99999 | 0.99765 | 0.99962 | 1 | 0.99764 | 0.99978 | 1 | 0.99741 | 0.99989 | 0.99893 | 0.99902
SW | 60026682 | F095D | KAIMKILLENBUN | F095D_Kaimkillenbun 33 kV | Rating (A) | 93 | 100 | 100 | 93 | 100 | 100 | 93 | 100 | 100 | 93 | 100 | 100 | 93 | 100 | 100
SW | 60026682 | F095D | KAIMKILLENBUN | F095D_Kaimkillenbun 33 kV | Time | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00
SW | 60026682 | F095D | KAIMKILLENBUN | F095D_Kaimkillenbun 33 kV | Voltage at Constrained Conductor | 33.5953 | 33.2815 | 33.501 | 33.6169 | 33.685 | 33.5123 | 33.6334 | 33.1868 | 33.52 | 33.2292 | 33.3032 | 33.7088 | 33.136 | 33.2682 | 33.887
SW | 60026684 | F106R | ROMA EAST | F106R_Roma East 33 kV | % of Rated A | 74.4787 | 74.6342 | 56.5358 | 73.686 | 73.838 | 55.9556 | 84.6429 | 84.8133 | 64.0972 | 84.6642 | 84.8352 | 64.0797 | 85.4748 | 85.65 | 64.6675
SW | 60026684 | F106R | ROMA EAST | F106R_Roma East 33 kV | Limiting Line Name | TR_LINE 44567_2 | TR_LINE 44567_2 | TR_LINE 44567_2 | TR_LINE 44567_2 | TR_LINE 44567_2 | TR_LINE 44567_2 | TR_LINE 44567_2 | TR_LINE 44567_2 | TR_LINE 44567_2 | TR_LINE 44567_2 | TR_LINE 44567_2 | TR_LINE 44567_2 | TR_LINE 44567_2 | TR_LINE 44567_2 | TR_LINE 44567_2
SW | 60026684 | F106R | ROMA EAST | F106R_Roma East 33 kV | Loading (A) | 190.6625 | 190.3144 | 123.8107 | 188.6332 | 188.284 | 122.54 | 216.6828 | 216.271 | 140.3702 | 216.7373 | 216.3267 | 140.3318 | 218.8126 | 218.4046 | 141.619
SW | 60026684 | F106R | ROMA EAST | F106R_Roma East 33 kV | Loading (MVA) | 10.4459 | 10.4246 | 6.8472 | 10.3411 | 10.3199 | 6.7793 | 11.806 | 11.7819 | 7.7327 | 11.8062 | 11.7821 | 7.7298 | 11.9119 | 11.8876 | 7.798
SW | 60026684 | F106R | ROMA EAST | F106R_Roma East 33 kV | Loading (MW) | 10.02 | 9.9999 | 6.6071 | 9.9214 | 9.9015 | 6.5423 | 11.301 | 11.2785 | 7.4502 | 11.3011 | 11.2785 | 7.4497 | 11.3998 | 11.377 | 7.5146
SW | 60026684 | F106R | ROMA EAST | F106R_Roma East 33 kV | Power Factor | 0.95923 | 0.95926 | 0.96493 | 0.95942 | 0.95946 | 0.96505 | 0.95722 | 0.95727 | 0.96346 | 0.95721 | 0.95726 | 0.96377 | 0.95701 | 0.95705 | 0.96366
SW | 60026684 | F106R | ROMA EAST | F106R_Roma East 33 kV | Rating (A) | 256 | 255 | 219 | 256 | 255 | 219 | 256 | 255 | 219 | 256 | 255 | 219 | 256 | 255 | 219
SW | 60026684 | F106R | ROMA EAST | F106R_Roma East 33 kV | Time | 16:30 | 17:00 | 22:00 | 16:30 | 17:00 | 22:00 | 16:30 | 17:00 | 22:00 | 16:30 | 17:00 | 22:00 | 16:30 | 17:00 | 22:00
SW | 60026684 | F106R | ROMA EAST | F106R_Roma East 33 kV | Voltage at Constrained Conductor | 31.6315 | 31.6246 | 31.9298 | 31.6509 | 31.6447 | 31.9407 | 31.4572 | 31.4527 | 31.8051 | 31.4497 | 31.445 | 31.8016 | 31.4302 | 31.4247 | 31.7908
SW | 60026689 | F127R | ROMA WEST | F127R_Roma West 33 kV | % of Rated A | 73.0897 | 54.7326 | 38.9063 | 73.0588 | 54.7078 | 38.8969 | 71.7074 | 53.668 | 38.154 | 73.3471 | 54.8983 | 39.0112 | 73.381 | 54.923 | 39.0204
SW | 60026689 | F127R | ROMA WEST | F127R_Roma West 33 kV | Limiting Line Name | TR_LINE 27140_1 | TR_LINE 27140_1 | TR_LINE 27140_1 | TR_LINE 27140_1 | TR_LINE 27140_1 | TR_LINE 27140_1 | TR_LINE 27140_1 | TR_LINE 27140_1 | TR_LINE 27140_1 | TR_LINE 27140_1 | TR_LINE 27140_1 | TR_LINE 27140_1 | TR_LINE 27140_1 | TR_LINE 27140_1 | TR_LINE 27140_1
SW | 60026689 | F127R | ROMA WEST | F127R_Roma West 33 kV | Loading (A) | 84.7839 | 87.572 | 60.6937 | 84.748 | 87.5322 | 60.679 | 83.1803 | 85.8686 | 59.5201 | 85.0824 | 87.8371 | 60.8572 | 85.1218 | 87.8766 | 60.8717
SW | 60026689 | F127R | ROMA WEST | F127R_Roma West 33 kV | Loading (MVA) | 4.6346 | 4.7783 | 3.3451 | 4.6345 | 4.7783 | 3.3451 | 4.5347 | 4.6732 | 3.2733 | 4.6352 | 4.7767 | 3.3454 | 4.6352 | 4.7768 | 3.3454
SW | 60026689 | F127R | ROMA WEST | F127R_Roma West 33 kV | Loading (MW) | 4.4818 | 4.6188 | 3.2456 | 4.4818 | 4.6188 | 3.2455 | 4.3861 | 4.5196 | 3.1763 | 4.4819 | 4.6183 | 3.2456 | 4.482 | 4.6184 | 3.2456
SW | 60026689 | F127R | ROMA WEST | F127R_Roma West 33 kV | Power Factor | 0.96703 | 0.96661 | 0.97023 | 0.96704 | 0.96662 | 0.97023 | 0.96722 | 0.96713 | 0.97037 | 0.96694 | 0.96685 | 0.97018 | 0.96693 | 0.96684 | 0.97018
SW | 60026689 | F127R | ROMA WEST | F127R_Roma West 33 kV | Rating (A) | 116 | 160 | 156 | 116 | 160 | 156 | 116 | 160 | 156 | 116 | 160 | 156 | 116 | 160 | 156
SW | 60026689 | F127R | ROMA WEST | F127R_Roma West 33 kV | Time | 16:00 | 18:30 | 22:00 | 16:00 | 18:30 | 22:00 | 16:00 | 18:30 | 22:00 | 16:00 | 18:30 | 22:00 | 16:00 | 18:30 | 22:00
SW | 60026689 | F127R | ROMA WEST | F127R_Roma West 33 kV | Voltage at Constrained Conductor | 31.5601 | 31.503 | 31.8208 | 31.573 | 31.5168 | 31.8283 | 31.4753 | 31.4208 | 31.7513 | 31.4531 | 31.3971 | 31.7373 | 31.4391 | 31.3835 | 31.73
SW | 60026700 | F2060 | SLADEVALE 1 | F2060_Sladevale 1 33kV | % of Rated A | 12.0695 | 14.5114 | 8.8745 | 11.8395 | 14.2085 | 8.743 | 11.8357 | 14.2025 | 8.7438 | 12.1235 | 14.5145 | 8.8681 | 12.1461 | 14.5435 | 8.862
SW | 60026700 | F2060 | SLADEVALE 1 | F2060_Sladevale 1 33kV | Limiting Line Name | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1
SW | 60026700 | F2060 | SLADEVALE 1 | F2060_Sladevale 1 33kV | Loading (A) | 76.6416 | 92.1476 | 56.3533 | 75.1811 | 90.2239 | 55.5179 | 75.1565 | 90.186 | 55.5231 | 76.9845 | 92.1674 | 56.3122 | 77.1276 | 92.3512 | 56.2738
SW | 60026700 | F2060 | SLADEVALE 1 | F2060_Sladevale 1 33kV | Loading (MVA) | 4.519 | 5.3821 | 3.3324 | 4.434 | 5.2717 | 3.2833 | 4.4341 | 5.2715 | 3.283 | 4.5184 | 5.4287 | 3.3344 | 4.5183 | 5.43 | 3.3362
SW | 60026700 | F2060 | SLADEVALE 1 | F2060_Sladevale 1 33kV | Loading (MW) | 4.4628 | 5.3735 | 3.0946 | 4.3711 | 5.2598 | 3.0321 | 4.3709 | 5.2595 | 3.0322 | 4.466 | 5.4191 | 3.0941 | 4.4673 | 5.421 | 3.0938
SW | 60026700 | F2060 | SLADEVALE 1 | F2060_Sladevale 1 33kV | Power Factor | 0.98758 | 0.9984 | 0.92864 | 0.98581 | 0.99775 | 0.92349 | 0.98574 | 0.99773 | 0.92358 | 0.9884 | 0.99824 | 0.92795 | 0.98873 | 0.99834 | 0.92737
SW | 60026700 | F2060 | SLADEVALE 1 | F2060_Sladevale 1 33kV | Rating (A) | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635
SW | 60026700 | F2060 | SLADEVALE 1 | F2060_Sladevale 1 33kV | Time | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00
SW | 60026700 | F2060 | SLADEVALE 1 | F2060_Sladevale 1 33kV | Voltage at Constrained Conductor | 34.042 | 33.7217 | 34.1406 | 34.051 | 33.734 | 34.1444 | 34.0627 | 33.7467 | 34.1383 | 33.8863 | 34.006 | 34.1864 | 33.8222 | 33.9464 | 34.228
SW | 60026708 | F217R | ST GEORGE | F217R_St George 66 kV | % of Rated A | 34.6988 | 33.7165 | 33.1953 | 34.3995 | 33.4239 | 32.9725 | 34.3196 | 33.3444 | 32.0438 | 34.3319 | 33.3568 | 32.0526 | 34.6314 | 33.6498 | 32.2639
SW | 60026708 | F217R | ST GEORGE | F217R_St George 66 kV | Limiting Line Name | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1
SW | 60026708 | F217R | ST GEORGE | F217R_St George 66 kV | Loading (A) | 155.1037 | 153.0731 | 131.4534 | 153.7657 | 151.7444 | 130.5712 | 153.4085 | 151.3836 | 126.8933 | 153.4637 | 151.4397 | 126.9285 | 154.8022 | 152.7701 | 127.7649
SW | 60026708 | F217R | ST GEORGE | F217R_St George 66 kV | Loading (MVA) | 17.3726 | 17.1439 | 14.7007 | 17.2276 | 17 | 14.6042 | 17.1539 | 16.9266 | 14.1974 | 17.1577 | 16.9306 | 14.2 | 17.3025 | 17.0743 | 14.2918
SW | 60026708 | F217R | ST GEORGE | F217R_St George 66 kV | Loading (MW) | 16.0121 | 15.7728 | 13.2143 | 15.8657 | 15.6279 | 13.1173 | 15.7571 | 15.5196 | 12.7038 | 15.7588 | 15.5214 | 12.7048 | 15.9051 | 15.6663 | 12.7969
SW | 60026708 | F217R | ST GEORGE | F217R_St George 66 kV | Power Factor | 0.92168 | 0.92003 | 0.89889 | 0.92095 | 0.91929 | 0.89819 | 0.91857 | 0.91687 | 0.8948 | 0.91847 | 0.91677 | 0.8947 | 0.91924 | 0.91753 | 0.89541
SW | 60026708 | F217R | ST GEORGE | F217R_St George 66 kV | Rating (A) | 447 | 454 | 396 | 447 | 454 | 396 | 447 | 454 | 396 | 447 | 454 | 396 | 447 | 454 | 396
SW | 60026708 | F217R | ST GEORGE | F217R_St George 66 kV | Time | 16:30 | 17:00 | 22:00 | 16:30 | 17:00 | 22:00 | 16:30 | 17:00 | 22:30 | 16:30 | 17:00 | 22:30 | 16:30 | 17:00 | 22:30
SW | 60026708 | F217R | ST GEORGE | F217R_St George 66 kV | Voltage at Constrained Conductor | 64.6671 | 64.662 | 64.5662 | 64.6853 | 64.6807 | 64.5756 | 64.5584 | 64.5552 | 64.5965 | 64.5496 | 64.5462 | 64.5905 | 64.5314 | 64.5274 | 64.5823
SW | 60026714 | F2325 | BROXBURN | F2325_Broxburn 33 kV | % of Rated A | 50.6222 | 54.283 | 42.8749 | 53.5686 | 56.5702 | 45.2629 | 53.5629 | 56.5645 | 45.2629 | 53.1221 | 56.6204 | 44.6299 | 54.6409 | 57.3353 | 45.1513
SW | 60026714 | F2325 | BROXBURN | F2325_Broxburn 33 kV | Limiting Line Name | TR_LINE 174733_1 | TR_LINE 174733_1 | TR_LINE 174733_1 | TR_LINE 174733_1 | TR_LINE 174733_1 | TR_LINE 174733_1 | TR_LINE 174733_1 | TR_LINE 174733_1 | TR_LINE 174733_1 | TR_LINE 174733_1 | TR_LINE 174733_1 | TR_LINE 174733_1 | TR_LINE 174733_1 | TR_LINE 174733_1 | TR_LINE 174733_1
SW | 60026714 | F2325 | BROXBURN | F2325_Broxburn 33 kV | Loading (A) | 169.0771 | 182.9326 | 125.1937 | 178.918 | 190.6405 | 132.1667 | 178.8991 | 190.6212 | 132.1667 | 177.4267 | 190.8097 | 130.3182 | 182.4996 | 193.219 | 131.8407
SW | 60026714 | F2325 | BROXBURN | F2325_Broxburn 33 kV | Loading (MVA) | 9.2021 | 9.7887 | 6.9041 | 9.6927 | 10.3109 | 7.2666 | 9.6926 | 10.3109 | 7.2666 | 9.6946 | 10.3113 | 7.2666 | 9.7891 | 10.4107 | 7.3398
SW | 60026714 | F2325 | BROXBURN | F2325_Broxburn 33 kV | Loading (MW) | 8.6488 | 9.188 | 6.5162 | 9.0992 | 9.6666 | 6.8553 | 9.0992 | 9.6666 | 6.8553 | 9.0993 | 9.6666 | 6.8555 | 9.1892 | 9.7622 | 6.9233
SW | 60026714 | F2325 | BROXBURN | F2325_Broxburn 33 kV | Power Factor | 0.93987 | 0.93863 | 0.94381 | 0.93877 | 0.93751 | 0.9434 | 0.93877 | 0.93751 | 0.9434 | 0.93859 | 0.93747 | 0.94342 | 0.93872 | 0.9377 | 0.94325
SW | 60026714 | F2325 | BROXBURN | F2325_Broxburn 33 kV | Rating (A) | 334 | 337 | 292 | 334 | 337 | 292 | 334 | 337 | 292 | 334 | 337 | 292 | 334 | 337 | 292
SW | 60026714 | F2325 | BROXBURN | F2325_Broxburn 33 kV | Time | 16:30 | 17:30 | 22:30 | 16:30 | 17:30 | 22:30 | 16:30 | 17:30 | 22:30 | 16:30 | 17:30 | 22:30 | 16:30 | 17:30 | 22:30
SW | 60026714 | F2325 | BROXBURN | F2325_Broxburn 33 kV | Voltage at Constrained Conductor | 31.4225 | 30.894 | 31.8395 | 31.2773 | 31.2264 | 31.7432 | 31.2805 | 31.2294 | 31.7431 | 31.5465 | 31.1999 | 32.1932 | 30.9685 | 31.1079 | 32.1423
SW | 60026720 | F2450 | CARRINGTON ROAD | F2450_Carrington Road 33 kV | % of Rated A | 20.7751 | 9.4164 | 17.8606 | 20.7693 | 9.4117 | 17.8565 | 20.7682 | 9.4107 | 17.856 | 20.8289 | 9.3699 | 17.899 | 21.1597 | 9.6628 | 18.1983
SW | 60026720 | F2450 | CARRINGTON ROAD | F2450_Carrington Road 33 kV | Limiting Line Name | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1
SW | 60026720 | F2450 | CARRINGTON ROAD | F2450_Carrington Road 33 kV | Loading (A) | 70.0121 | 31.7332 | 60.1901 | 69.9924 | 31.7174 | 60.1763 | 69.9889 | 31.7139 | 60.1747 | 70.1934 | 31.5766 | 60.3195 | 71.3081 | 32.5636 | 61.3281
SW | 60026720 | F2450 | CARRINGTON ROAD | F2450_Carrington Road 33 kV | Loading (MVA) | 4.077 | 1.8523 | 3.5071 | 4.077 | 1.8523 | 3.507 | 4.077 | 1.8523 | 3.507 | 4.0774 | 1.8523 | 3.5073 | 4.1781 | 1.8988 | 3.5953
SW | 60026720 | F2450 | CARRINGTON ROAD | F2450_Carrington Road 33 kV | Loading (MW) | 3.6427 | 1.6685 | 3.1402 | 3.6427 | 1.6685 | 3.1402 | 3.6427 | 1.6685 | 3.1402 | 3.6427 | 1.6686 | 3.1402 | 3.7338 | 1.7101 | 3.2187
SW | 60026720 | F2450 | CARRINGTON ROAD | F2450_Carrington Road 33 kV | Power Factor | 0.89347 | 0.90077 | 0.89539 | 0.89348 | 0.90077 | 0.8954 | 0.89348 | 0.90078 | 0.8954 | 0.8934 | 0.90082 | 0.89534 | 0.89365 | 0.90061 | 0.89524
SW | 60026720 | F2450 | CARRINGTON ROAD | F2450_Carrington Road 33 kV | Rating (A) | 337 | 337 | 337 | 337 | 337 | 337 | 337 | 337 | 337 | 337 | 337 | 337 | 337 | 337 | 337
SW | 60026720 | F2450 | CARRINGTON ROAD | F2450_Carrington Road 33 kV | Time | 9:30 | 18:30 | 7:30 | 9:30 | 18:30 | 7:30 | 9:30 | 18:30 | 7:30 | 9:30 | 18:30 | 7:30 | 9:30 | 18:30 | 7:30
SW | 60026720 | F2450 | CARRINGTON ROAD | F2450_Carrington Road 33 kV | Voltage at Constrained Conductor | 33.6209 | 33.7011 | 33.6402 | 33.6301 | 33.7177 | 33.6477 | 33.6317 | 33.7215 | 33.6485 | 33.5369 | 33.8671 | 33.5699 | 33.8283 | 33.6663 | 33.8469
SW | 60026721 | F2460 | CECIL PLAINS | F2460_Cecil Plains 33 kV | % of Rated A | 30.5687 | 20.2559 | 20.1685 | 30.5647 | 20.028 | 20.1666 | 30.5653 | 20.0286 | 20.1669 | 30.5602 | 20.3285 | 20.1628 | 30.8831 | 20.3121 | 19.9127
SW | 60026721 | F2460 | CECIL PLAINS | F2460_Cecil Plains 33 kV | Limiting Line Name | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1
SW | 60026721 | F2460 | CECIL PLAINS | F2460_Cecil Plains 33 kV | Loading (A) | 43.7133 | 42.7399 | 41.9505 | 43.7075 | 42.2591 | 41.9466 | 43.7084 | 42.2603 | 41.9471 | 43.701 | 42.8932 | 41.9386 | 44.1629 | 42.8585 | 41.4184
SW | 60026721 | F2460 | CECIL PLAINS | F2460_Cecil Plains 33 kV | Loading (MVA) | 2.5607 | 2.4709 | 2.4286 | 2.5593 | 2.4611 | 2.4279 | 2.5595 | 2.4613 | 2.428 | 2.5577 | 2.4843 | 2.4265 | 2.5545 | 2.4774 | 2.4245
SW | 60026721 | F2460 | CECIL PLAINS | F2460_Cecil Plains 33 kV | Loading (MW) | 1.6163 | 1.4525 | 1.356 | 1.6163 | 1.4659 | 1.356 | 1.6163 | 1.4659 | 1.356 | 1.6163 | 1.4664 | 1.356 | 1.6082 | 1.4664 | 1.3556
SW | 60026721 | F2460 | CECIL PLAINS | F2460_Cecil Plains 33 kV | Power Factor | 0.6312 | 0.58787 | 0.55835 | 0.63156 | 0.59563 | 0.55851 | 0.6315 | 0.59557 | 0.55849 | 0.63195 | 0.59026 | 0.55884 | 0.62957 | 0.59191 | 0.55914
SW | 60026721 | F2460 | CECIL PLAINS | F2460_Cecil Plains 33 kV | Rating (A) | 143 | 211 | 208 | 143 | 211 | 208 | 143 | 211 | 208 | 143 | 211 | 208 | 143 | 211 | 208
SW | 60026721 | F2460 | CECIL PLAINS | F2460_Cecil Plains 33 kV | Time | 15:00 | 18:00 | 8:30 | 15:00 | 17:00 | 8:30 | 15:00 | 17:00 | 8:30 | 15:00 | 17:00 | 8:30 | 16:30 | 17:00 | 8:30
SW | 60026721 | F2460 | CECIL PLAINS | F2460_Cecil Plains 33 kV | Voltage at Constrained Conductor | 33.8208 | 33.3774 | 33.4243 | 33.8063 | 33.6237 | 33.4177 | 33.8085 | 33.6261 | 33.4186 | 33.7901 | 33.4396 | 33.4043 | 33.3953 | 33.3728 | 33.7958
SW | 60026723 | F2520 | CLIFTON | F2520_Clifton 33 kV | % of Rated A | 45.6676 | 62.7175 | 43.5205 | 51.1974 | 70.0653 | 47.9712 | 54.4209 | 74.9703 | 50.8416 | 53.9395 | 75.5478 | 50.8625 | 54.037 | 75.4373 | 50.6615
SW | 60026723 | F2520 | CLIFTON | F2520_Clifton 33 kV | Limiting Line Name | TR_LINE 188412_1 | TR_LINE 188412_1 | TR_LINE 188412_1 | TR_LINE 188412_1 | TR_LINE 188412_1 | TR_LINE 188412_1 | TR_LINE 188412_1 | TR_LINE 188412_1 | TR_LINE 188412_1 | TR_LINE 188412_1 | TR_LINE 188412_1 | TR_LINE 188412_1 | TR_LINE 188412_1 | TR_LINE 188412_1 | TR_LINE 188412_1
SW | 60026723 | F2520 | CLIFTON | F2520_Clifton 33 kV | Loading (A) | 55.7145 | 76.5154 | 53.095 | 62.4609 | 85.4796 | 58.5249 | 66.3935 | 91.4637 | 62.0268 | 65.8062 | 92.1684 | 62.0523 | 65.9251 | 92.0335 | 61.807
SW | 60026723 | F2520 | CLIFTON | F2520_Clifton 33 kV | Loading (MVA) | 3.2242 | 4.2318 | 3.0633 | 3.5476 | 4.7229 | 3.363 | 3.7615 | 5.0298 | 3.555 | 3.7565 | 5.0351 | 3.5637 | 3.7542 | 5.0274 | 3.5511
SW | 60026723 | F2520 | CLIFTON | F2520_Clifton 33 kV | Loading (MW) | 2.9799 | 4.1086 | 2.7957 | 3.3607 | 4.637 | 3.1504 | 3.5898 | 4.9577 | 3.3644 | 3.5883 | 4.9601 | 3.3644 | 3.5886 | 4.9599 | 3.3639
SW | 60026723 | F2520 | CLIFTON | F2520_Clifton 33 kV | Power Factor | 0.92421 | 0.97088 | 0.91265 | 0.94732 | 0.98182 | 0.93678 | 0.95433 | 0.98567 | 0.9464 | 0.95523 | 0.98511 | 0.94409 | 0.95589 | 0.98657 | 0.9473
SW | 60026723 | F2520 | CLIFTON | F2520_Clifton 33 kV | Rating (A) | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122
SW | 60026723 | F2520 | CLIFTON | F2520_Clifton 33 kV | Time | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 18:30 | 22:00
SW | 60026723 | F2520 | CLIFTON | F2520_Clifton 33 kV | Voltage at Constrained Conductor | 33.4116 | 31.9313 | 33.3096 | 32.7921 | 31.8994 | 33.1765 | 32.7099 | 31.7495 | 33.09 | 32.9575 | 31.5402 | 33.1574 | 32.8784 | 31.5381 | 33.1711
SW | 60026737 | F2777 | EAST STANTHORPE | F2777_East Stanthorpe 33 kV | % of Rated A | 1.6186 | 1.184 | 1.2479 | 1.6188 | 1.1841 | 1.248 | 1.6179 | 1.1874 | 1.2475 | 1.6171 | 1.1844 | 1.248 | 1.6175 | 1.1845 | 1.2464
SW | 60026737 | F2777 | EAST STANTHORPE | F2777_East Stanthorpe 33 kV | Limiting Line Name | TR_LINE 140241_1 | TR_LINE 140241_1 | TR_LINE 140241_1 | TR_LINE 140241_1 | TR_LINE 140241_1 | TR_LINE 140241_1 | TR_LINE 140241_1 | TR_LINE 140241_1 | TR_LINE 140241_1 | TR_LINE 140241_1 | TR_LINE 140241_1 | TR_LINE 140241_1 | TR_LINE 140241_1 | TR_LINE 140241_1 | TR_LINE 140241_1
SW | 60026737 | F2777 | EAST STANTHORPE | F2777_East Stanthorpe 33 kV | Loading (A) | 2.4926 | 2.4626 | 2.5082 | 2.493 | 2.4629 | 2.5084 | 2.4916 | 2.4698 | 2.5075 | 2.4903 | 2.4635 | 2.5084 | 2.4909 | 2.4638 | 2.5053
SW | 60026737 | F2777 | EAST STANTHORPE | F2777_East Stanthorpe 33 kV | Loading (MVA) | 0.14889 | 0.14523 | 0.15086 | 0.14894 | 0.14526 | 0.15089 | 0.14888 | 0.14607 | 0.15089 | 0.14872 | 0.14533 | 0.15089 | 0.14879 | 0.14536 | 0.15062
SW | 60026737 | F2777 | EAST STANTHORPE | F2777_East Stanthorpe 33 kV | Loading (MW) | 7.0695e-05 | 6.9056e-05 | 7.153e-05 | 7.0718e-05 | 6.9072e-05 | 7.1544e-05 | 7.0589e-05 | 6.9456e-05 | 7.1441e-05 | 7.0515e-05 | 6.9105e-05 | 7.1543e-05 | 7.055e-05 | 6.9121e-05 | 7.1314e-05
SW | 60026737 | F2777 | EAST STANTHORPE | F2777_East Stanthorpe 33 kV | Power Factor | 0.00047482 | 0.00047551 | 0.00047414 | 0.00047482 | 0.00047551 | 0.00047415 | 0.00047414 | 0.00047551 | 0.00047348 | 0.00047414 | 0.00047551 | 0.00047415 | 0.00047414 | 0.00047551 | 0.00047348
SW | 60026737 | F2777 | EAST STANTHORPE | F2777_East Stanthorpe 33 kV | Rating (A) | 154 | 208 | 201 | 154 | 208 | 201 | 154 | 208 | 201 | 154 | 208 | 201 | 154 | 208 | 201
SW | 60026737 | F2777 | EAST STANTHORPE | F2777_East Stanthorpe 33 kV | Time | 10:00 | 21:30 | 3:30 | 10:00 | 21:30 | 3:30 | 10:00 | 21:30 | 3:00 | 10:00 | 19:30 | 3:00 | 10:30 | 20:30 | 3:00
SW | 60026737 | F2777 | EAST STANTHORPE | F2777_East Stanthorpe 33 kV | Voltage at Constrained Conductor | 34.4862 | 34.0473 | 34.7263 | 34.4918 | 34.0511 | 34.7295 | 34.4971 | 34.1458 | 34.741 | 34.479 | 34.0593 | 34.7293 | 34.4874 | 34.0632 | 34.7099
SW | 60026738 | F2780 | WARWICK EAST 1 | F2780_East Warwick No 1 33 kV | % of Rated A | 28.365 | 29.9195 | 20.6145 | 28.0783 | 29.608 | 20.4349 | 27.9294 | 29.4473 | 20.2597 | 28.0086 | 29.4786 | 20.2411 | 28.3394 | 29.8267 | 20.4043
SW | 60026738 | F2780 | WARWICK EAST 1 | F2780_East Warwick No 1 33 kV | Limiting Line Name | TR_LINE 23896_1 | TR_LINE 23896_1 | TR_LINE 23896_1 | TR_LINE 23896_1 | TR_LINE 23896_1 | TR_LINE 23896_1 | TR_LINE 23896_1 | TR_LINE 23896_1 | TR_LINE 23896_1 | TR_LINE 23896_1 | TR_LINE 23896_1 | TR_LINE 23896_1 | TR_LINE 23896_1 | TR_LINE 23896_1 | TR_LINE 23896_1
SW | 60026738 | F2780 | WARWICK EAST 1 | F2780_East Warwick No 1 33 kV | Loading (A) | 150.3343 | 162.463 | 98.3311 | 148.8148 | 160.7712 | 97.4745 | 148.0258 | 159.8987 | 96.6387 | 148.4458 | 160.069 | 96.5499 | 150.1989 | 161.9591 | 97.3287
SW | 60026738 | F2780 | WARWICK EAST 1 | F2780_East Warwick No 1 33 kV | Loading (MVA) | 8.8681 | 9.5834 | 5.8124 | 8.7803 | 9.4872 | 5.7622 | 8.7367 | 9.4393 | 5.7118 | 8.7169 | 9.4381 | 5.7147 | 8.8032 | 9.5329 | 5.7678
SW | 60026738 | F2780 | WARWICK EAST 1 | F2780_East Warwick No 1 33 kV | Loading (MW) | 8.7073 | 9.4591 | 5.3965 | 8.6143 | 9.358 | 5.339 | 8.5677 | 9.3073 | 5.3103 | 8.5685 | 9.3075 | 5.3102 | 8.6617 | 9.4088 | 5.3677
SW | 60026738 | F2780 | WARWICK EAST 1 | F2780_East Warwick No 1 33 kV | Power Factor | 0.98187 | 0.98704 | 0.92845 | 0.98109 | 0.98638 | 0.92655 | 0.98065 | 0.98602 | 0.9297 | 0.98297 | 0.98616 | 0.92921 | 0.98392 | 0.98698 | 0.93063
SW | 60026738 | F2780 | WARWICK EAST 1 | F2780_East Warwick No 1 33 kV | Rating (A) | 530 | 543 | 477 | 530 | 543 | 477 | 530 | 543 | 477 | 530 | 543 | 477 | 530 | 543 | 477
SW | 60026738 | F2780 | WARWICK EAST 1 | F2780_East Warwick No 1 33 kV | Time | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00
SW | 60026738 | F2780 | WARWICK EAST 1 | F2780_East Warwick No 1 33 kV | Voltage at Constrained Conductor | 34.0574 | 34.0568 | 34.1275 | 34.0645 | 34.0696 | 34.1301 | 34.0761 | 34.0827 | 34.1239 | 33.9026 | 34.042 | 34.1731 | 33.8388 | 33.9828 | 34.2145
SW | 60026739 | F2785 | WARWICK EAST 2 | F2785_East Warwick No 2 33 kV | % of Rated A | 28.2248 | 29.7717 | 20.5127 | 27.9395 | 29.4616 | 20.334 | 27.7914 | 29.3018 | 20.1596 | 27.8702 | 29.3329 | 20.1411 | 28.1994 | 29.6793 | 20.3035
SW | 60026739 | F2785 | WARWICK EAST 2 | F2785_East Warwick No 2 33 kV | Limiting Line Name | TR_LINE 23891_1 | TR_LINE 23891_1 | TR_LINE 23891_1 | TR_LINE 23891_1 | TR_LINE 23891_1 | TR_LINE 23891_1 | TR_LINE 23891_1 | TR_LINE 23891_1 | TR_LINE 23891_1 | TR_LINE 23891_1 | TR_LINE 23891_1 | TR_LINE 23891_1 | TR_LINE 23891_1 | TR_LINE 23891_1 | TR_LINE 23891_1
SW | 60026739 | F2785 | WARWICK EAST 2 | F2785_East Warwick No 2 33 kV | Loading (A) | 149.5913 | 161.6601 | 97.8454 | 148.0794 | 159.9767 | 96.993 | 147.2943 | 159.1085 | 96.1613 | 147.7122 | 159.2779 | 96.0729 | 149.4566 | 161.1587 | 96.8479
SW | 60026739 | F2785 | WARWICK EAST 2 | F2785_East Warwick No 2 33 kV | Loading (MVA) | 8.8243 | 9.536 | 5.7837 | 8.7369 | 9.4403 | 5.7337 | 8.6935 | 9.3926 | 5.6836 | 8.6738 | 9.3914 | 5.6865 | 8.7597 | 9.4858 | 5.7393
SW | 60026739 | F2785 | WARWICK EAST 2 | F2785_East Warwick No 2 33 kV | Loading (MW) | 8.665 | 9.413 | 5.3708 | 8.5724 | 9.3124 | 5.3135 | 8.5261 | 9.262 | 5.2849 | 8.5268 | 9.2621 | 5.2849 | 8.6196 | 9.3629 | 5.3421
SW | 60026739 | F2785 | WARWICK EAST 2 | F2785_East Warwick No 2 33 kV | Power Factor | 0.98195 | 0.9871 | 0.9286 | 0.98117 | 0.98645 | 0.92671 | 0.98074 | 0.98609 | 0.92986 | 0.98305 | 0.98623 | 0.92937 | 0.984 | 0.98705 | 0.93079
SW | 60026739 | F2785 | WARWICK EAST 2 | F2785_East Warwick No 2 33 kV | Rating (A) | 530 | 543 | 477 | 530 | 543 | 477 | 530 | 543 | 477 | 530 | 543 | 477 | 530 | 543 | 477
SW | 60026739 | F2785 | WARWICK EAST 2 | F2785_East Warwick No 2 33 kV | Time | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00
SW | 60026739 | F2785 | WARWICK EAST 2 | F2785_East Warwick No 2 33 kV | Voltage at Constrained Conductor | 34.0574 | 34.0568 | 34.1275 | 34.0645 | 34.0696 | 34.1301 | 34.0761 | 34.0827 | 34.1239 | 33.9026 | 34.042 | 34.1731 | 33.8388 | 33.9828 | 34.2145
SW | 60026753 | F3040 | HAMPTON STREET | F3040 Hampton Street | % of Rated A | 0.30921 | 0.30906 | 0.30918 | 0.30903 | 0.3091 | 0.30919 | 0.30906 | 0.30912 | 0.30919 | 0.30919 | 0.3086 | 0.30911 | 0.30916 | 0.30926 | 0.309
SW | 60026753 | F3040 | HAMPTON STREET | F3040 Hampton Street | Limiting Line Name | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1
SW | 60026753 | F3040 | HAMPTON STREET | F3040 Hampton Street | Loading (A) | 1.546 | 1.5453 | 1.5459 | 1.5452 | 1.5455 | 1.546 | 1.5453 | 1.5456 | 1.546 | 1.5459 | 1.543 | 1.5456 | 1.5458 | 1.5463 | 1.545
SW | 60026753 | F3040 | HAMPTON STREET | F3040 Hampton Street | Loading (MVA) | 0.093632 | 0.093545 | 0.093617 | 0.093527 | 0.093571 | 0.093624 | 0.093544 | 0.093581 | 0.093625 | 0.093622 | 0.093268 | 0.093577 | 0.093607 | 0.093667 | 0.09351
SW | 60026753 | F3040 | HAMPTON STREET | F3040 Hampton Street | Loading (MW) | 0.0013196 | 0.0013183 | 0.0013193 | 0.0013181 | 0.0013187 | 0.0013194 | 0.0013183 | 0.0013188 | 0.0013195 | 0.0013194 | 0.0013144 | 0.0013188 | 0.0013192 | 0.00132 | 0.0013178
SW | 60026753 | F3040 | HAMPTON STREET | F3040 Hampton Street | Power Factor | 0.014093 | 0.014093 | 0.014093 | 0.014093 | 0.014093 | 0.014093 | 0.014093 | 0.014093 | 0.014093 | 0.014093 | 0.014093 | 0.014093 | 0.014093 | 0.014093 | 0.014093
SW | 60026753 | F3040 | HAMPTON STREET | F3040 Hampton Street | Rating (A) | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500
SW | 60026753 | F3040 | HAMPTON STREET | F3040 Hampton Street | Time | 16:30 | 18:30 | 2:30 | 15:00 | 17:00 | 2:30 | 15:00 | 17:00 | 2:30 | 14:30 | 20:00 | 2:30 | 14:00 | 21:00 | 2:30
SW | 60026753 | F3040 | HAMPTON STREET | F3040 Hampton Street | Voltage at Constrained Conductor | 34.9662 | 34.9498 | 34.9633 | 34.9465 | 34.9547 | 34.9645 | 34.9497 | 34.9565 | 34.9648 | 34.9641 | 34.898 | 34.9559 | 34.9614 | 34.9725 | 34.9433
SW | 60026769 | F3255 | JENNINGS STREET | F3255_Jennings Street 33 kV | % of Rated A | 34.5105 | 33.8576 | 27.8818 | 34.6695 | 33.5679 | 27.6471 | 34.3682 | 33.2794 | 27.4138 | 34.2601 | 33.5672 | 27.5404 | 34.4574 | 33.7514 | 27.6713
SW | 60026769 | F3255 | JENNINGS STREET | F3255_Jennings Street 33 kV | Limiting Line Name | TR_CABLE 7923_1 | TR_CABLE 7923_1 | TR_CABLE 7923_1 | TR_CABLE 7923_1 | TR_CABLE 7923_1 | TR_CABLE 7923_1 | TR_CABLE 7923_1 | TR_CABLE 7923_1 | TR_CABLE 7923_1 | TR_CABLE 7923_1 | TR_CABLE 7923_1 | TR_CABLE 7923_1 | TR_CABLE 7923_1 | TR_CABLE 7923_1 | TR_CABLE 7923_1
SW | 60026769 | F3255 | JENNINGS STREET | F3255_Jennings Street 33 kV | Loading (A) | 212.9301 | 208.9016 | 172.0308 | 213.911 | 207.1142 | 170.5826 | 212.0517 | 205.3337 | 169.1429 | 211.385 | 207.1094 | 169.9245 | 212.6019 | 208.246 | 170.7319
SW | 60026769 | F3255 | JENNINGS STREET | F3255_Jennings Street 33 kV | Loading (MVA) | 12.7906 | 12.4683 | 10.2522 | 12.6853 | 12.3639 | 10.167 | 12.578 | 12.2596 | 10.0818 | 12.6256 | 12.3663 | 10.1246 | 12.6803 | 12.4197 | 10.1674
SW | 60026769 | F3255 | JENNINGS STREET | F3255_Jennings Street 33 kV | Loading (MW) | 12.3702 | 12.0706 | 9.9648 | 12.2706 | 11.9723 | 9.8837 | 12.1698 | 11.874 | 9.8026 | 12.2192 | 11.9747 | 9.8432 | 12.2698 | 12.0242 | 9.8838
SW | 60026769 | F3255 | JENNINGS STREET | F3255_Jennings Street 33 kV | Power Factor | 0.96713 | 0.9681 | 0.97196 | 0.96731 | 0.96833 | 0.97214 | 0.96755 | 0.96855 | 0.97231 | 0.96781 | 0.96833 | 0.97221 | 0.96763 | 0.96816 | 0.9721
SW | 60026769 | F3255 | JENNINGS STREET | F3255_Jennings Street 33 kV | Rating (A) | 617 | 617 | 617 | 617 | 617 | 617 | 617 | 617 | 617 | 617 | 617 | 617 | 617 | 617 | 617
SW | 60026769 | F3255 | JENNINGS STREET | F3255_Jennings Street 33 kV | Time | 16:30 | 17:30 | 22:30 | 16:30 | 17:30 | 22:30 | 16:30 | 17:30 | 22:30 | 16:30 | 17:00 | 22:30 | 16:30 | 17:00 | 22:30
SW | 60026769 | F3255 | JENNINGS STREET | F3255_Jennings Street 33 kV | Voltage at Constrained Conductor | 34.6812 | 34.4592 | 34.4073 | 34.2379 | 34.4656 | 34.4109 | 34.2459 | 34.4711 | 34.4131 | 34.4839 | 34.4731 | 34.4001 | 34.4351 | 34.4328 | 34.3823
SW | 60026772 | F3315 | SLADEVALE 2 | F3315_Sladevale 2 33kV | % of Rated A | 7.2168 | 7.6132 | 6.8488 | 7.2175 | 7.6141 | 6.8492 | 7.2188 | 7.6149 | 6.8499 | 7.1998 | 7.6123 | 6.8486 | 7.1929 | 7.6088 | 6.8447
SW | 60026772 | F3315 | SLADEVALE 2 | F3315_Sladevale 2 33kV | Limiting Line Name | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1
SW | 60026772 | F3315 | SLADEVALE 2 | F3315_Sladevale 2 33kV | Loading (A) | 45.8264 | 48.3441 | 43.4896 | 45.8313 | 48.3492 | 43.4925 | 45.8395 | 48.3547 | 43.4968 | 45.7189 | 48.3382 | 43.4883 | 45.6751 | 48.316 | 43.4637
SW | 60026772 | F3315 | SLADEVALE 2 | F3315_Sladevale 2 33kV | Loading (MVA) | 2.7076 | 2.8523 | 2.6071 | 2.7085 | 2.8537 | 2.6075 | 2.7099 | 2.8551 | 2.6081 | 2.689 | 2.8508 | 2.607 | 2.6813 | 2.8444 | 2.6038
SW | 60026772 | F3315 | SLADEVALE 2 | F3315_Sladevale 2 33kV | Loading (MW) | 1.6772 | 2.0246 | 1.0555 | 1.6771 | 2.0246 | 1.0555 | 1.6771 | 2.0245 | 1.0555 | 1.6776 | 2.0247 | 1.0555 | 1.6777 | 2.0249 | 1.0555
SW | 60026772 | F3315 | SLADEVALE 2 | F3315_Sladevale 2 33kV | Power Factor | 0.61942 | 0.70981 | 0.40485 | 0.61922 | 0.70946 | 0.40479 | 0.61889 | 0.70909 | 0.40471 | 0.62388 | 0.71021 | 0.40488 | 0.62572 | 0.71189 | 0.40538
SW | 60026772 | F3315 | SLADEVALE 2 | F3315_Sladevale 2 33kV | Rating (A) | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635
SW | 60026772 | F3315 | SLADEVALE 2 | F3315_Sladevale 2 33kV | Time | 16:30 | 18:00 | 5:30 | 16:30 | 18:00 | 5:30 | 16:30 | 18:00 | 5:30 | 16:30 | 18:00 | 5:30 | 16:30 | 18:00 | 5:30
SW | 60026772 | F3315 | SLADEVALE 2 | F3315_Sladevale 2 33kV | Voltage at Constrained Conductor | 34.1122 | 34.0638 | 34.6113 | 34.1193 | 34.0763 | 34.6139 | 34.131 | 34.0894 | 34.6178 | 33.9568 | 34.0497 | 34.6101 | 33.8928 | 33.989 | 34.5878
SW | 60026789 | F3530 | MILLMERRAN | F3530_Millmerran 33 kV | % of Rated A | 46.7553 | 38.6959 | 26.946 | 45.4757 | 37.9882 | 26.2075 | 45.4706 | 37.9845 | 26.2074 | 45.7104 | 38.1322 | 26.1545 | 46.5748 | 38.7661 | 26.867
SW | 60026789 | F3530 | MILLMERRAN | F3530_Millmerran 33 kV | Limiting Line Name | TR_LINE 23295_1 | TR_LINE 23295_1 | TR_LINE 23295_1 | TR_LINE 23295_1 | TR_LINE 23295_1 | TR_LINE 23295_1 | TR_LINE 23295_1 | TR_LINE 23295_1 | TR_LINE 23295_1 | TR_LINE 23295_1 | TR_LINE 23295_1 | TR_LINE 23295_1 | TR_LINE 23295_1 | TR_LINE 23295_1 | TR_LINE 23295_1
SW | 60026789 | F3530 | MILLMERRAN | F3530_Millmerran 33 kV | Loading (A) | 59.1477 | 69.4038 | 46.9436 | 57.5253 | 68.1347 | 45.6536 | 57.5189 | 68.128 | 45.6535 | 57.825 | 68.394 | 45.5608 | 58.9184 | 69.5319 | 46.8053
SW | 60026789 | F3530 | MILLMERRAN | F3530_Millmerran 33 kV | Loading (MVA) | 3.4545 | 4.0802 | 2.756 | 3.3615 | 3.9724 | 2.6826 | 3.3615 | 3.9723 | 2.6826 | 3.3625 | 3.9739 | 2.6822 | 3.4533 | 4.08 | 2.7555
SW | 60026789 | F3530 | MILLMERRAN | F3530_Millmerran 33 kV | Loading (MW) | 3.4164 | 4.026 | 2.7333 | 3.3257 | 3.9209 | 2.6612 | 3.3257 | 3.9209 | 2.6612 | 3.3266 | 3.922 | 2.661 | 3.4156 | 4.0263 | 2.7329
SW | 60026789 | F3530 | MILLMERRAN | F3530_Millmerran 33 kV | Power Factor | 0.98897 | 0.98671 | 0.99174 | 0.98935 | 0.98705 | 0.99205 | 0.98935 | 0.98705 | 0.99205 | 0.98935 | 0.98694 | 0.99209 | 0.98907 | 0.98683 | 0.9918
SW | 60026789 | F3530 | MILLMERRAN | F3530_Millmerran 33 kV | Rating (A) | 127 | 180 | 175 | 127 | 180 | 175 | 127 | 180 | 175 | 127 | 180 | 175 | 127 | 180 | 175
SW | 60026789 | F3530 | MILLMERRAN | F3530_Millmerran 33 kV | Time | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00
SW | 60026789 | F3530 | MILLMERRAN | F3530_Millmerran 33 kV | Voltage at Constrained Conductor | 33.7201 | 33.9419 | 33.8961 | 33.7379 | 33.6606 | 33.9246 | 33.7414 | 33.6636 | 33.9247 | 33.5722 | 33.5462 | 33.9889 | 33.8396 | 33.8779 | 33.9891
SW | 60026795 | F3820 | BOUNDARY ROAD | F3820_Boundary Road 33 kV | % of Rated A | 46.6771 | 40.3842 | 32.8045 | 46.1105 | 39.8934 | 32.418 | 46.1024 | 39.8868 | 32.4171 | 58.2413 | 50.3182 | 41.0909 | 72.2366 | 62.2346 | 49.9941
SW | 60026795 | F3820 | BOUNDARY ROAD | F3820_Boundary Road 33 kV | Limiting Line Name | TR_CABLE 73_1 | TR_CABLE 73_1 | TR_CABLE 73_1 | TR_CABLE 73_1 | TR_CABLE 73_1 | TR_CABLE 73_1 | TR_CABLE 73_1 | TR_CABLE 73_1 | TR_CABLE 73_1 | TR_CABLE 73_1 | TR_CABLE 73_1 | TR_CABLE 73_1 | TR_CABLE 73_1 | TR_CABLE 73_1 | TR_CABLE 73_1
SW | 60026795 | F3820 | BOUNDARY ROAD | F3820_Boundary Road 33 kV | Loading (A) | 322.0718 | 278.6512 | 226.351 | 318.1626 | 275.2645 | 223.6844 | 318.1064 | 275.2189 | 223.6782 | 401.8646 | 347.1956 | 283.527 | 498.4327 | 429.419 | 344.9591
SW | 60026795 | F3820 | BOUNDARY ROAD | F3820_Boundary Road 33 kV | Loading (MVA) | 18.8304 | 16.3111 | 13.2835 | 18.6102 | 16.1215 | 13.1303 | 18.6099 | 16.1212 | 13.1303 | 23.5865 | 20.4137 | 16.5988 | 29.0421 | 25.0889 | 20.356
SW | 60026795 | F3820 | BOUNDARY ROAD | F3820_Boundary Road 33 kV | Loading (MW) | 17.2327 | 15.0273 | 12.343 | 17.0415 | 14.861 | 12.2069 | 17.0414 | 14.8609 | 12.2068 | 21.2608 | 18.5314 | 15.2122 | 25.8835 | 22.5445 | 18.4885
SW | 60026795 | F3820 | BOUNDARY ROAD | F3820_Boundary Road 33 kV | Power Factor | 0.91515 | 0.92129 | 0.9292 | 0.9157 | 0.92181 | 0.92967 | 0.91572 | 0.92183 | 0.92967 | 0.9014 | 0.90779 | 0.91647 | 0.89124 | 0.89858 | 0.90826
SW | 60026795 | F3820 | BOUNDARY ROAD | F3820_Boundary Road 33 kV | Rating (A) | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690
SW | 60026795 | F3820 | BOUNDARY ROAD | F3820_Boundary Road 33 kV | Time | 16:30 | 17:00 | 8:00 | 16:30 | 17:00 | 8:00 | 16:30 | 17:00 | 8:00 | 16:30 | 17:00 | 8:00 | 16:30 | 17:00 | 8:00
SW | 60026795 | F3820 | BOUNDARY ROAD | F3820_Boundary Road 33 kV | Voltage at Constrained Conductor | 33.7556 | 33.7958 | 33.882 | 33.7709 | 33.8138 | 33.8906 | 33.7762 | 33.8188 | 33.8915 | 33.8862 | 33.9458 | 33.8003 | 33.6404 | 33.7318 | 34.0695
SW | 60026796 | F3830 | NORWIN | F3830_Norwin 33 kV | % of Rated A | 55.2094 | 19.0748 | 43.6032 | 55.3687 | 18.971 | 43.6128 | 55.5104 | 18.9701 | 43.6115 | 54.4492 | 18.88 | 43.6326 | 55.4649 | 19.0427 | 43.0557
SW | 60026796 | F3830 | NORWIN | F3830_Norwin 33 kV | Limiting Line Name | TR_CABLE 175_1 | TR_CABLE 175_1 | TR_CABLE 175_1 | TR_CABLE 175_1 | TR_CABLE 175_1 | TR_CABLE 175_1 | TR_CABLE 175_1 | TR_CABLE 175_1 | TR_CABLE 175_1 | TR_CABLE 175_1 | TR_CABLE 175_1 | TR_CABLE 175_1 | TR_CABLE 175_1 | TR_CABLE 175_1 | TR_CABLE 175_1
SW | 60026796 | F3830 | NORWIN | F3830_Norwin 33 kV | Loading (A) | 64.0429 | 22.1267 | 50.5797 | 64.2276 | 22.0064 | 50.5909 | 64.392 | 22.0053 | 50.5893 | 63.1611 | 21.9007 | 50.6139 | 64.3393 | 22.0896 | 49.9447
SW | 60026796 | F3830 | NORWIN | F3830_Norwin 33 kV | Loading (MVA) | 3.4661 | 1.2377 | 2.7442 | 3.4665 | 1.2353 | 2.7442 | 3.4668 | 1.2353 | 2.7442 | 3.4675 | 1.234 | 2.7442 | 3.4667 | 1.2364 | 2.7443
SW | 60026796 | F3830 | NORWIN | F3830_Norwin 33 kV | Loading (MW) | 2.766 | 0.99872 | 2.1973 | 2.766 | 0.99678 | 2.1973 | 2.7661 | 0.99678 | 2.1973 | 2.7661 | 0.99568 | 2.1974 | 2.7661 | 0.99761 | 2.1974
SW | 60026796 | F3830 | NORWIN | F3830_Norwin 33 kV | Power Factor | 0.79802 | 0.80689 | 0.80073 | 0.79794 | 0.80691 | 0.80072 | 0.79787 | 0.80691 | 0.80072 | 0.79773 | 0.80685 | 0.80071 | 0.79789 | 0.80688 | 0.80071
SW | 60026796 | F3830 | NORWIN | F3830_Norwin 33 kV | Rating (A) | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116
SW | 60026796 | F3830 | NORWIN | F3830_Norwin 33 kV | Time | 11:00 | 18:00 | 8:30 | 11:00 | 19:00 | 8:30 | 11:00 | 19:00 | 8:30 | 11:00 | 19:30 | 8:30 | 11:00 | 18:30 | 8:30
SW | 60026796 | F3830 | NORWIN | F3830_Norwin 33 kV | Voltage at Constrained Conductor | 31.2468 | 32.2959 | 31.324 | 31.1604 | 32.4089 | 31.3173 | 31.084 | 32.4103 | 31.3182 | 31.6963 | 32.5319 | 31.3035 | 31.1085 | 32.3152 | 31.723
SW | 60026800 | F3855 | O'MARAS ROAD | F3855 Omaras Road 33 kV | % of Rated A | 18.3509 | 16.4353 | 18.1937 | 18.3467 | 16.4731 | 18.1891 | 18.3458 | 16.4368 | 18.1887 | 18.3939 | 16.3604 | 18.2367 | 18.2317 | 16.4634 | 18.0897
SW | 60026800 | F3855 | O'MARAS ROAD | F3855 Omaras Road 33 kV | Limiting Line Name | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1
SW | 60026800 | F3855 | O'MARAS ROAD | F3855 Omaras Road 33 kV | Loading (A) | 42.7576 | 38.2942 | 42.3914 | 42.7477 | 38.3823 | 42.3807 | 42.7456 | 38.2977 | 42.3796 | 42.8579 | 38.1197 | 42.4916 | 42.4798 | 38.3596 | 42.149
SW | 60026800 | F3855 | O'MARAS ROAD | F3855 Omaras Road 33 kV | Loading (MVA) | 2.5 | 2.2322 | 2.476 | 2.5 | 2.2337 | 2.476 | 2.5 | 2.2337 | 2.476 | 2.5 | 2.2322 | 2.476 | 2.5 | 2.2322 | 2.476
SW | 60026800 | F3855 | O'MARAS ROAD | F3855 Omaras Road 33 kV | Loading (MW) | 2.215 | 1.9778 | 2.1937 | 2.215 | 1.9791 | 2.1937 | 2.215 | 1.9791 | 2.1937 | 2.215 | 1.9778 | 2.1937 | 2.215 | 1.9778 | 2.1937
SW | 60026800 | F3855 | O'MARAS ROAD | F3855 Omaras Road 33 kV | Power Factor | 0.886 | 0.886 | 0.886 | 0.886 | 0.886 | 0.886 | 0.886 | 0.886 | 0.886 | 0.886 | 0.886 | 0.886 | 0.886 | 0.886 | 0.886
SW | 60026800 | F3855 | O'MARAS ROAD | F3855 Omaras Road 33 kV | Rating (A) | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233
SW | 60026800 | F3855 | O'MARAS ROAD | F3855 Omaras Road 33 kV | Time | 9:00 | 17:00 | 8:00 | 9:00 | 21:30 | 8:00 | 9:00 | 21:30 | 8:00 | 9:00 | 17:00 | 8:00 | 9:00 | 17:00 | 8:00
SW | 60026800 | F3855 | O'MARAS ROAD | F3855 Omaras Road 33 kV | Voltage at Constrained Conductor | 33.7572 | 33.655 | 33.7219 | 33.765 | 33.6003 | 33.7304 | 33.7666 | 33.6745 | 33.7313 | 33.6782 | 33.809 | 33.6424 | 33.978 | 33.5976 | 33.9159
SW | 60026810 | F3970 | POZIERES | F3970_Pozieres 33 kV | % of Rated A | 36.4972 | 24.1782 | 20.6286 | 35.2904 | 23.3781 | 19.9498 | 35.2827 | 23.37 | 19.9474 | 35.3036 | 23.3987 | 19.9542 | 36.6053 | 24.2709 | 20.6798
SW | 60026810 | F3970 | POZIERES | F3970_Pozieres 33 kV | Limiting Line Name | TR_LINE 24233_1 | TR_LINE 23973_2 | TR_LINE 23973_2 | TR_LINE 24233_1 | TR_LINE 23973_2 | TR_LINE 23973_2 | TR_LINE 24233_1 | TR_LINE 23973_2 | TR_LINE 23973_2 | TR_LINE 24233_1 | TR_LINE 23973_2 | TR_LINE 23973_2 | TR_LINE 24233_1 | TR_LINE 23973_2 | TR_LINE 23973_2
SW | 60026810 | F3970 | POZIERES | F3970_Pozieres 33 kV | Loading (A) | 52.1902 | 50.2818 | 41.4547 | 50.4646 | 48.6177 | 40.0903 | 50.4535 | 48.6009 | 40.0854 | 50.4834 | 48.6605 | 40.0991 | 52.3448 | 50.4748 | 41.5575
SW | 60026810 | F3970 | POZIERES | F3970_Pozieres 33 kV | Loading (MVA) | 3.1282 | 3.0131 | 2.5555 | 3.0261 | 2.9134 | 2.4712 | 3.026 | 2.9133 | 2.4711 | 3.0261 | 2.9135 | 2.4712 | 3.1285 | 3.0129 | 2.5558
SW | 60026810 | F3970 | POZIERES | F3970_Pozieres 33 kV | Loading (MW) | 2.7669 | 2.6736 | 2.2758 | 2.6775 | 2.5867 | 2.2019 | 2.6775 | 2.5867 | 2.2019 | 2.6775 | 2.5867 | 2.2019 | 2.7669 | 2.6737 | 2.2759
SW | 60026810 | F3970 | POZIERES | F3970_Pozieres 33 kV | Power Factor | 0.88449 | 0.88732 | 0.89055 | 0.88481 | 0.88786 | 0.89105 | 0.88482 | 0.88787 | 0.89105 | 0.88481 | 0.88783 | 0.89104 | 0.88443 | 0.88743 | 0.89048
SW | 60026810 | F3970 | POZIERES | F3970_Pozieres 33 kV | Rating (A) | 143 | 208 | 201 | 143 | 208 | 201 | 143 | 208 | 201 | 143 | 208 | 201 | 143 | 208 | 201
SW | 60026810 | F3970 | POZIERES | F3970_Pozieres 33 kV | Time | 13:30 | 18:00 | 8:30 | 13:30 | 18:00 | 8:30 | 13:30 | 18:00 | 8:30 | 13:30 | 18:00 | 8:30 | 13:30 | 18:00 | 8:30
SW | 60026810 | F3970 | POZIERES | F3970_Pozieres 33 kV | Voltage at Constrained Conductor | 34.6058 | 34.5977 | 35.5912 | 34.6203 | 34.5973 | 35.5878 | 34.6277 | 34.6087 | 35.592 | 34.6077 | 34.5684 | 35.5803 | 34.5061 | 34.4624 | 35.5072
SW | 60026811 | F3980 | PURRAWUNDA | F3980_Purrawunda 33 kV | % of Rated A | 45.7488 | 53.6503 | 45.3907 | 45.1241 | 52.8519 | 44.7802 | 45.1193 | 52.8472 | 44.7792 | 45.0179 | 52.5345 | 44.789 | 45.8494 | 53.692 | 44.9043
SW | 60026811 | F3980 | PURRAWUNDA | F3980_Purrawunda 33 kV | Limiting Line Name | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1
SW | 60026811 | F3980 | PURRAWUNDA | F3980_Purrawunda 33 kV | Loading (A) | 96.5299 | 113.2022 | 95.7743 | 95.2118 | 111.5175 | 94.4862 | 95.2018 | 111.5075 | 94.4841 | 94.9878 | 110.8478 | 94.5048 | 96.7422 | 113.2901 | 94.748
SW | 60026811 | F3980 | PURRAWUNDA | F3980_Purrawunda 33 kV | Loading (MVA) | 5.6461 | 6.632 | 5.6058 | 5.5715 | 6.5365 | 5.5318 | 5.5718 | 6.5366 | 5.5319 | 5.578 | 6.5258 | 5.5313 | 5.6406 | 6.631 | 5.6031
SW | 60026811 | F3980 | PURRAWUNDA | F3980_Purrawunda 33 kV | Loading (MW) | 5.4034 | 6.4944 | 5.3549 | 5.3155 | 6.3879 | 5.2679 | 5.3155 | 6.3878 | 5.2679 | 5.3147 | 6.3854 | 5.268 | 5.4042 | 6.4948 | 5.3514
SW | 60026811 | F3980 | PURRAWUNDA | F3980_Purrawunda 33 kV | Power Factor | 0.95701 | 0.97925 | 0.95525 | 0.95406 | 0.97726 | 0.9523 | 0.954 | 0.97723 | 0.95228 | 0.95279 | 0.97848 | 0.9524 | 0.95809 | 0.97946 | 0.95508
SW | 60026811 | F3980 | PURRAWUNDA | F3980_Purrawunda 33 kV | Rating (A) | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211
SW | 60026811 | F3980 | PURRAWUNDA | F3980_Purrawunda 33 kV | Time | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00
SW | 60026811 | F3980 | PURRAWUNDA | F3980_Purrawunda 33 kV | Voltage at Constrained Conductor | 33.7695 | 33.8243 | 33.793 | 33.7846 | 33.8409 | 33.8019 | 33.7899 | 33.8446 | 33.803 | 33.9038 | 33.9896 | 33.7918 | 33.6625 | 33.7928 | 34.1425
SW | 60026813 | F4005 | RACECOURSE | F4005_Racecourse 33 kV | % of Rated A | 25.4495 | 23.1545 | 14.1073 | 25.0318 | 22.7731 | 13.8813 | 24.8944 | 22.6465 | 13.8068 | 24.9752 | 22.7376 | 13.8115 | 24.9355 | 23.0041 | 13.7392
SW | 60026813 | F4005 | RACECOURSE | F4005_Racecourse 33 kV | Limiting Line Name | TR_CABLE 65_1 | TR_CABLE 65_1 | TR_CABLE 65_1 | TR_CABLE 65_1 | TR_CABLE 65_1 | TR_CABLE 65_1 | TR_CABLE 65_1 | TR_CABLE 65_1 | TR_CABLE 65_1 | TR_CABLE 65_1 | TR_CABLE 65_1 | TR_CABLE 65_1 | TR_CABLE 65_1 | TR_CABLE 65_1 | TR_CABLE 65_1
SW | 60026813 | F4005 | RACECOURSE | F4005_Racecourse 33 kV | Loading (A) | 179.6737 | 163.4708 | 99.5972 | 176.7247 | 160.778 | 98.002 | 175.7545 | 159.8841 | 97.476 | 176.3247 | 160.5272 | 97.5091 | 176.0446 | 162.4089 | 96.9985
SW | 60026813 | F4005 | RACECOURSE | F4005_Racecourse 33 kV | Loading (MVA) | 10.4263 | 9.5785 | 5.8103 | 10.261 | 9.4268 | 5.719 | 10.2059 | 9.3763 | 5.6886 | 10.2071 | 9.3775 | 5.6887 | 10.2643 | 9.426 | 5.7179
SW | 60026813 | F4005 | RACECOURSE | F4005_Racecourse 33 kV | Loading (MW) | 10.0825 | 9.2736 | 5.6552 | 9.9252 | 9.129 | 5.5672 | 9.8728 | 9.0807 | 5.5378 | 9.873 | 9.081 | 5.5378 | 9.9258 | 9.1288 | 5.567
SW | 60026813 | F4005 | RACECOURSE | F4005_Racecourse 33 kV | Power Factor | 0.96702 | 0.96817 | 0.97332 | 0.96728 | 0.9684 | 0.97344 | 0.96736 | 0.96848 | 0.97349 | 0.96727 | 0.96838 | 0.97348 | 0.96703 | 0.96847 | 0.9736
SW | 60026813 | F4005 | RACECOURSE | F4005_Racecourse 33 kV | Rating (A) | 706 | 706 | 706 | 706 | 706 | 706 | 706 | 706 | 706 | 706 | 706 | 706 | 706 | 706 | 706
SW | 60026813 | F4005 | RACECOURSE | F4005_Racecourse 33 kV | Time | 15:30 | 17:30 | 22:00 | 15:30 | 17:30 | 22:00 | 15:30 | 17:30 | 22:00 | 15:30 | 17:30 | 22:00 | 15:30 | 17:30 | 22:00
SW | 60026813 | F4005 | RACECOURSE | F4005_Racecourse 33 kV | Voltage at Constrained Conductor | 33.5033 | 33.8295 | 33.6813 | 33.5221 | 33.8514 | 33.692 | 33.5262 | 33.8582 | 33.6938 | 33.4217 | 33.7271 | 33.6826 | 33.6623 | 33.5088 | 34.0339
SW | 60026814 | F4015 | RAMSAY STREET | F4015_Ramsay Street 33 kV | % of Rated A | 34.9582 | 34.2904 | 28.2435 | 35.1126 | 33.997 | 28.0057 | 34.8074 | 33.7047 | 27.7694 | 34.698 | 33.9962 | 27.8977 | 34.8977 | 34.1827 | 28.0302
SW | 60026814 | F4015 | RAMSAY STREET | F4015_Ramsay Street 33 kV | Limiting Line Name | TR_CABLE 7922_1 | TR_CABLE 7922_1 | TR_CABLE 7922_1 | TR_CABLE 7922_1 | TR_CABLE 7922_1 | TR_CABLE 7922_1 | TR_CABLE 7922_1 | TR_CABLE 7922_1 | TR_CABLE 7922_1 | TR_CABLE 7922_1 | TR_CABLE 7922_1 | TR_CABLE 7922_1 | TR_CABLE 7922_1 | TR_CABLE 7922_1 | TR_CABLE 7922_1
SW | 60026814 | F4015 | RAMSAY STREET | F4015_Ramsay Street 33 kV | Loading (A) | 209.7491 | 205.7422 | 169.4609 | 210.6757 | 203.9817 | 168.0344 | 208.8446 | 202.2282 | 166.6162 | 208.188 | 203.977 | 167.3861 | 209.3864 | 205.0964 | 168.1814
SW | 60026814 | F4015 | RAMSAY STREET | F4015_Ramsay Street 33 kV | Loading (MVA) | 12.5894 | 12.27 | 10.0925 | 12.4832 | 12.1674 | 10.0087 | 12.3777 | 12.0648 | 9.9249 | 12.4247 | 12.1698 | 9.9669 | 12.4784 | 12.2221 | 10.0091
SW | 60026814 | F4015 | RAMSAY STREET | F4015_Ramsay Street 33 kV | Loading (MW) | 12.1944 | 11.897 | 9.8232 | 12.0941 | 11.8001 | 9.7433 | 11.9948 | 11.7032 | 9.6634 | 12.0435 | 11.8025 | 9.7034 | 12.0933 | 11.8513 | 9.7434
SW | 60026814 | F4015 | RAMSAY STREET | F4015_Ramsay Street 33 kV | Power Factor | 0.96863 | 0.9696 | 0.97332 | 0.96883 | 0.96982 | 0.97349 | 0.96907 | 0.97003 | 0.97365 | 0.96932 | 0.96982 | 0.97356 | 0.96914 | 0.96966 | 0.97345
SW | 60026814 | F4015 | RAMSAY STREET | F4015_Ramsay Street 33 kV | Rating (A) | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600
SW | 60026814 | F4015 | RAMSAY STREET | F4015_Ramsay Street 33 kV | Time | 16:30 | 17:30 | 22:30 | 16:30 | 17:30 | 22:30 | 16:30 | 17:30 | 22:30 | 16:30 | 17:00 | 22:30 | 16:30 | 17:00 | 22:30
SW | 60026814 | F4015 | RAMSAY STREET | F4015_Ramsay Street 33 kV | Voltage at Constrained Conductor | 34.6531 | 34.4319 | 34.385 | 34.2098 | 34.4385 | 34.3888 | 34.2182 | 34.4443 | 34.3912 | 34.4563 | 34.4461 | 34.3781 | 34.4073 | 34.4056 | 34.3602
SW | 60026827 | F4245 | STANTHORPE | F4245_Stanthorpe 33 kV | % of Rated A | 48.0992 | 63.1942 | 44.847 | 49.5616 | 65.431 | 46.1264 | 49.552 | 65.4137 | 46.1282 | 49.3206 | 65.4403 | 46.0865 | 49.7646 | 65.6024 | 46.3832
SW | 60026827 | F4245 | STANTHORPE | F4245_Stanthorpe 33 kV | Limiting Line Name | TR_CABLE 107_1 | TR_CABLE 107_1 | TR_LINE 23344_1 | TR_CABLE 107_1 | TR_CABLE 107_1 | TR_LINE 23344_1 | TR_CABLE 107_1 | TR_CABLE 107_1 | TR_LINE 23344_1 | TR_CABLE 107_1 | TR_CABLE 107_1 | TR_LINE 23344_1 | TR_CABLE 107_1 | TR_CABLE 107_1 | TR_LINE 23344_1
SW | 60026827 | F4245 | STANTHORPE | F4245_Stanthorpe 33 kV | Loading (A) | 140.4496 | 184.5271 | 130.9533 | 144.7199 | 191.0586 | 134.689 | 144.6917 | 191.0079 | 134.6943 | 144.0162 | 191.0857 | 134.5726 | 145.3127 | 191.559 | 135.4389
SW | 60026827 | F4245 | STANTHORPE | F4245_Stanthorpe 33 kV | Loading (MVA) | 8.5499 | 10.987 | 8.1125 | 8.8029 | 11.3591 | 8.3393 | 8.8037 | 11.3578 | 8.339 | 8.8252 | 11.3589 | 8.3446 | 8.8813 | 11.4598 | 8.4051
SW | 60026827 | F4245 | STANTHORPE | F4245_Stanthorpe 33 kV | Loading (MW) | 8.0943 | 10.844 | 7.5338 | 8.3893 | 11.2388 | 7.8093 | 8.3893 | 11.2396 | 7.8093 | 8.389 | 11.2388 | 7.8092 | 8.4629 | 11.3381 | 7.878
SW | 60026827 | F4245 | STANTHORPE | F4245_Stanthorpe 33 kV | Power Factor | 0.94671 | 0.98699 | 0.92867 | 0.95302 | 0.98941 | 0.93645 | 0.95292 | 0.98959 | 0.93648 | 0.95057 | 0.98943 | 0.93584 | 0.95288 | 0.98938 | 0.93728
SW | 60026827 | F4245 | STANTHORPE | F4245_Stanthorpe 33 kV | Rating (A) | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292
SW | 60026827 | F4245 | STANTHORPE | F4245_Stanthorpe 33 kV | Time | 16:30 | 19:30 | 22:00 | 16:30 | 19:30 | 22:00 | 16:30 | 19:30 | 22:00 | 16:30 | 19:30 | 22:00 | 16:30 | 19:30 | 22:00
SW | 60026827 | F4245 | STANTHORPE | F4245_Stanthorpe 33 kV | Voltage at Constrained Conductor | 35.1464 | 34.3762 | 35.7666 | 35.1184 | 34.3256 | 35.7467 | 35.1287 | 34.3307 | 35.7442 | 35.3797 | 34.3201 | 35.8005 | 35.2869 | 34.5394 | 35.8295
SW | 60026834 | F4470 | VACY STREET | F4470 Vacy Street | % of Rated A | 0.45424 | 0.45403 | 0.4542 | 0.45399 | 0.45409 | 0.45422 | 0.45403 | 0.45412 | 0.45422 | 0.45421 | 0.45336 | 0.45411 | 0.45418 | 0.45432 | 0.45394
SW | 60026834 | F4470 | VACY STREET | F4470 Vacy Street | Limiting Line Name | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2
SW | 60026834 | F4470 | VACY STREET | F4470 Vacy Street | Loading (A) | 2.2712 | 2.2701 | 2.271 | 2.2699 | 2.2705 | 2.2711 | 2.2701 | 2.2706 | 2.2711 | 2.2711 | 2.2668 | 2.2705 | 2.2709 | 2.2716 | 2.2697
SW | 60026834 | F4470 | VACY STREET | F4470 Vacy Street | Loading (MVA) | 0.13755 | 0.13742 | 0.13753 | 0.1374 | 0.13746 | 0.13754 | 0.13742 | 0.13748 | 0.13754 | 0.13754 | 0.13702 | 0.13747 | 0.13751 | 0.1376 | 0.13737
SW | 60026834 | F4470 | VACY STREET | F4470 Vacy Street | Loading (MW) | 0.0023911 | 0.0023889 | 0.0023907 | 0.0023884 | 0.0023895 | 0.0023909 | 0.0023888 | 0.0023898 | 0.0023909 | 0.0023908 | 0.0023818 | 0.0023897 | 0.0023904 | 0.002392 | 0.002388
SW | 60026834 | F4470 | VACY STREET | F4470 Vacy Street | Power Factor | 0.017383 | 0.017383 | 0.017383 | 0.017383 | 0.017383 | 0.017383 | 0.017383 | 0.017383 | 0.017383 | 0.017383 | 0.017383 | 0.017383 | 0.017383 | 0.017383 | 0.017383
SW | 60026834 | F4470 | VACY STREET | F4470 Vacy Street | Rating (A) | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500
SW | 60026834 | F4470 | VACY STREET | F4470 Vacy Street | Time | 16:30 | 18:30 | 2:30 | 15:00 | 17:00 | 2:30 | 15:00 | 17:00 | 2:30 | 14:30 | 20:00 | 2:30 | 14:00 | 21:00 | 2:30
SW | 60026834 | F4470 | VACY STREET | F4470 Vacy Street | Voltage at Constrained Conductor | 34.9662 | 34.9498 | 34.9633 | 34.9465 | 34.9547 | 34.9645 | 34.9497 | 34.9565 | 34.9648 | 34.9641 | 34.898 | 34.9559 | 34.9614 | 34.9725 | 34.9433
SW | 60026843 | F4605 | WEST WARWICK | F4605_West Warwick 33 kV | % of Rated A | 42.9025 | 52.2997 | 33.664 | 42.893 | 52.2834 | 33.6614 | 42.4955 | 51.7929 | 33.3709 | 43.1117 | 51.8788 | 33.617 | 43.5836 | 52.4147 | 33.8706
SW | 60026843 | F4605 | WEST WARWICK | F4605_West Warwick 33 kV | Limiting Line Name | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1
SW | 60026843 | F4605 | WEST WARWICK | F4605_West Warwick 33 kV | Loading (A) | 166.8895 | 205.0133 | 114.4565 | 166.8527 | 204.9494 | 114.4476 | 165.3064 | 203.0268 | 113.4599 | 167.7033 | 203.3637 | 114.2968 | 169.5391 | 205.4641 | 115.1588
SW | 60026843 | F4605 | WEST WARWICK | F4605_West Warwick 33 kV | Loading (MVA) | 9.8447 | 11.9873 | 6.7656 | 9.8445 | 11.987 | 6.7656 | 9.7566 | 11.879 | 6.706 | 9.8477 | 11.9857 | 6.7652 | 9.9368 | 12.0887 | 6.8245
SW | 60026843 | F4605 | WEST WARWICK | F4605_West Warwick 33 kV | Loading (MW) | 9.5492 | 11.5756 | 6.603 | 9.5492 | 11.5755 | 6.603 | 9.4658 | 11.474 | 6.5456 | 9.5503 | 11.5739 | 6.6028 | 9.6342 | 11.6747 | 6.6601
SW | 60026843 | F4605 | WEST WARWICK | F4605_West Warwick 33 kV | Power Factor | 0.96999 | 0.96565 | 0.97597 | 0.97 | 0.96567 | 0.97597 | 0.97019 | 0.9659 | 0.97608 | 0.9698 | 0.96564 | 0.976 | 0.96955 | 0.96575 | 0.97592
SW | 60026843 | F4605 | WEST WARWICK | F4605_West Warwick 33 kV | Rating (A) | 389 | 392 | 340 | 389 | 392 | 340 | 389 | 392 | 340 | 389 | 392 | 340 | 389 | 392 | 340
SW | 60026843 | F4605 | WEST WARWICK | F4605_West Warwick 33 kV | Time | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00
SW | 60026843 | F4605 | WEST WARWICK | F4605_West Warwick 33 kV | Voltage at Constrained Conductor | 34.0574 | 33.7582 | 34.1275 | 34.0645 | 33.7679 | 34.1301 | 34.0761 | 33.7805 | 34.1239 | 33.9026 | 34.0274 | 34.1731 | 33.8388 | 33.969 | 34.2145
SW | 60026846 | F4685 | WYALLA STREET | F4685_Wyalla Street 33 kV | % of Rated A | 22.9886 | 20.9159 | 12.7448 | 22.6113 | 20.5714 | 12.5407 | 22.4872 | 20.457 | 12.4735 | 22.5601 | 20.5393 | 12.4777 | 22.5243 | 20.78 | 12.4124
SW | 60026846 | F4685 | WYALLA STREET | F4685_Wyalla Street 33 kV | Limiting Line Name | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1
SW | 60026846 | F4685 | WYALLA STREET | F4685_Wyalla Street 33 kV | Loading (A) | 158.621 | 144.3195 | 87.9392 | 156.018 | 141.9426 | 86.5311 | 155.1617 | 141.1536 | 86.0668 | 155.6649 | 141.7211 | 86.096 | 155.418 | 143.3817 | 85.6456
SW | 60026846 | F4685 | WYALLA STREET | F4685_Wyalla Street 33 kV | Loading (MVA) | 9.2047 | 8.4563 | 5.1302 | 9.0587 | 8.3224 | 5.0496 | 9.0101 | 8.2778 | 5.0228 | 9.0112 | 8.2789 | 5.0228 | 9.0616 | 8.3217 | 5.0487
SW | 60026846 | F4685 | WYALLA STREET | F4685_Wyalla Street 33 kV | Loading (MW) | 8.8913 | 8.1781 | 4.9876 | 8.7526 | 8.0506 | 4.9099 | 8.7064 | 8.0081 | 4.8841 | 8.7066 | 8.0082 | 4.8841 | 8.7531 | 8.0504 | 4.9098
SW | 60026846 | F4685 | WYALLA STREET | F4685_Wyalla Street 33 kV | Power Factor | 0.96595 | 0.9671 | 0.97221 | 0.96621 | 0.96733 | 0.97234 | 0.96629 | 0.96741 | 0.97238 | 0.9662 | 0.9673 | 0.97237 | 0.96595 | 0.9674 | 0.97249
SW | 60026846 | F4685 | WYALLA STREET | F4685_Wyalla Street 33 kV | Rating (A) | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690
SW | 60026846 | F4685 | WYALLA STREET | F4685_Wyalla Street 33 kV | Time | 15:30 | 17:30 | 22:00 | 15:30 | 17:30 | 22:00 | 15:30 | 17:30 | 22:00 | 15:30 | 17:30 | 22:00 | 15:30 | 17:30 | 22:00
SW | 60026846 | F4685 | WYALLA STREET | F4685_Wyalla Street 33 kV | Voltage at Constrained Conductor | 33.5033 | 33.8295 | 33.6813 | 33.5221 | 33.8514 | 33.692 | 33.5262 | 33.8582 | 33.6938 | 33.4217 | 33.7271 | 33.6826 | 33.6623 | 33.5088 | 34.0339
SW | 60026848 | 790 | 790 WARWICK - STANTHORPE | 790_Warwick-Stanthorpe 110 kV | % of Rated A | 43.8609 | 38.5733 | 28.5124 | 44.7052 | 39.5418 | 29.0821 | 44.6935 | 39.5364 | 29.0837 | 44.4125 | 39.548 | 29.0466 | 45.1232 | 39.8069 | 29.3902
SW | 60026848 | 790 | 790 WARWICK - STANTHORPE | 790_Warwick-Stanthorpe 110 kV | Limiting Line Name | TR_LINE 198182_1 | TR_LINE 198182_1 | TR_LINE 198182_1 | TR_LINE 198182_1 | TR_LINE 198182_1 | TR_LINE 198182_1 | TR_LINE 198182_1 | TR_LINE 198182_1 | TR_LINE 198182_1 | TR_LINE 198182_1 | TR_LINE 198182_1 | TR_LINE 198182_1 | TR_LINE 198182_1 | TR_LINE 198182_1 | TR_LINE 198182_1
SW | 60026848 | 790 | 790 WARWICK - STANTHORPE | 790_Warwick-Stanthorpe 110 kV | Loading (A) | 55.7034 | 69.4319 | 49.8967 | 56.7756 | 71.1752 | 50.8936 | 56.7608 | 71.1655 | 50.8965 | 56.4039 | 71.1865 | 50.8315 | 57.3064 | 71.6524 | 51.4329
SW | 60026848 | 790 | 790 WARWICK - STANTHORPE | 790_Warwick-Stanthorpe 110 kV | Loading (MVA) | 10.8829 | 13.3302 | 9.8806 | 11.0877 | 13.6528 | 10.0732 | 11.088 | 13.6534 | 10.073 | 11.0947 | 13.6528 | 10.0759 | 11.2456 | 13.8302 | 10.2042
SW | 60026848 | 790 | 790 WARWICK - STANTHORPE | 790_Warwick-Stanthorpe 110 kV | Loading (MW) | 10.8173 | 13.3284 | 9.7101 | 11.0284 | 13.6522 | 9.9149 | 11.0283 | 13.653 | 9.9149 | 11.0267 | 13.6523 | 9.9147 | 11.1896 | 13.8299 | 10.0546
SW | 60026848 | 790 | 790 WARWICK - STANTHORPE | 790_Warwick-Stanthorpe 110 kV | Power Factor | 0.99397 | 0.99986 | 0.98275 | 0.99465 | 0.99996 | 0.98429 | 0.99462 | 0.99997 | 0.9843 | 0.99387 | 0.99996 | 0.984 | 0.99502 | 0.99998 | 0.98534
SW | 60026848 | 790 | 790 WARWICK - STANTHORPE | 790_Warwick-Stanthorpe 110 kV | Rating (A) | 127 | 180 | 175 | 127 | 180 | 175 | 127 | 180 | 175 | 127 | 180 | 175 | 127 | 180 | 175
SW | 60026848 | 790 | 790 WARWICK - STANTHORPE | 790_Warwick-Stanthorpe 110 kV | Time | 16:30 | 19:30 | 22:00 | 16:30 | 19:30 | 22:00 | 16:30 | 19:30 | 22:00 | 16:30 | 19:30 | 22:00 | 16:30 | 19:30 | 22:00
SW | 60026848 | 790 | 790 WARWICK - STANTHORPE | 790_Warwick-Stanthorpe 110 kV | Voltage at Constrained Conductor | 112.7983 | 110.8452 | 114.3276 | 112.7509 | 110.7472 | 114.2726 | 112.783 | 110.7673 | 114.2649 | 113.5652 | 110.73 | 114.4428 | 113.2971 | 111.4388 | 114.5451
SW | 60026891 | F074C | MILES - CONDAMINE | F074C_Miles-Condamine 33 kV | % of Rated A | 16.609 | 12.7917 | 11.0004 | 16.5893 | 12.1951 | 10.5219 | 16.5893 | 12.1951 | 10.5219 | 16.5893 | 12.1951 | 10.5219 | 16.609 | 12.7917 | 11.0004
SW | 60026891 | F074C | MILES - CONDAMINE | F074C_Miles-Condamine 33 kV | Limiting Line Name | TR_LINE 138809_5 | TR_LINE 42883_1 | TR_LINE 42883_1 | TR_LINE 138809_5 | TR_LINE 195522_1 | TR_LINE 42883_1 | TR_LINE 138809_5 | TR_LINE 195522_1 | TR_LINE 42883_1 | TR_LINE 138809_5 | TR_LINE 195522_1 | TR_LINE 42883_1 | TR_LINE 138809_5 | TR_LINE 42883_1 | TR_LINE 42883_1
SW | 60026891 | F074C | MILES - CONDAMINE | F074C_Miles-Condamine 33 kV | Loading (A) | 23.7509 | 37.7356 | 28.9312 | 23.7227 | 35.9756 | 27.6725 | 23.7227 | 35.9756 | 27.6725 | 23.7228 | 35.9756 | 27.6725 | 23.7509 | 37.7356 | 28.9312
SW | 60026891 | F074C | MILES - CONDAMINE | F074C_Miles-Condamine 33 kV | Loading (MVA) | 1.3389 | 2.1411 | 1.6483 | 1.3389 | 2.0442 | 1.5774 | 1.3389 | 2.0442 | 1.5774 | 1.3389 | 2.0442 | 1.5774 | 1.3389 | 2.1411 | 1.6483
SW | 60026891 | F074C | MILES - CONDAMINE | F074C_Miles-Condamine 33 kV | Loading (MW) | 1.3375 | 2.1409 | 1.6434 | 1.3374 | 2.0436 | 1.5717 | 1.3374 | 2.0436 | 1.5717 | 1.3374 | 2.0436 | 1.5717 | 1.3375 | 2.1409 | 1.6434
SW | 60026891 | F074C | MILES - CONDAMINE | F074C_Miles-Condamine 33 kV | Power Factor | 0.99896 | 0.99993 | 0.99703 | 0.99891 | 0.99971 | 0.99638 | 0.99891 | 0.99971 | 0.99638 | 0.99891 | 0.99971 | 0.99638 | 0.99896 | 0.99993 | 0.99703
SW | 60026891 | F074C | MILES - CONDAMINE | F074C_Miles-Condamine 33 kV | Rating (A) | 143 | 295 | 263 | 143 | 295 | 263 | 143 | 295 | 263 | 143 | 295 | 263 | 143 | 295 | 263
SW | 60026891 | F074C | MILES - CONDAMINE | F074C_Miles-Condamine 33 kV | Time | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00
SW | 60026891 | F074C | MILES - CONDAMINE | F074C_Miles-Condamine 33 kV | Voltage at Constrained Conductor | 32.5466 | 32.7582 | 32.8931 | 32.5852 | 32.8065 | 32.9108 | 32.5852 | 32.8064 | 32.9108 | 32.5851 | 32.8064 | 32.9107 | 32.5466 | 32.7582 | 32.8931
SW | 60026893 | F077C | WANDOAN | F077C_Wandoan 33 kV | % of Rated A | 36.6278 | 23.1986 | 17.1031 | 36.599 | 23.4161 | 17.0926 | 36.5991 | 23.4161 | 17.0926 | 36.5991 | 23.4161 | 17.0926 | 36.6279 | 23.1986 | 17.1031
SW | 60026893 | F077C | WANDOAN | F077C_Wandoan 33 kV | Limiting Line Name | TR_LINE 23394_1 | TR_LINE 23394_1 | TR_LINE 23394_1 | TR_LINE 23394_1 | TR_LINE 23394_1 | TR_LINE 23394_1 | TR_LINE 23394_1 | TR_LINE 23394_1 | TR_LINE 23394_1 | TR_LINE 23394_1 | TR_LINE 23394_1 | TR_LINE 23394_1 | TR_LINE 23394_1 | TR_LINE 23394_1 | TR_LINE 23394_1
SW | 60026893 | F077C | WANDOAN | F077C_Wandoan 33 kV | Loading (A) | 63.3652 | 64.4912 | 47.5458 | 63.3154 | 65.0959 | 47.5167 | 63.3155 | 65.0959 | 47.5167 | 63.3156 | 65.096 | 47.5167 | 63.3653 | 64.4913 | 47.5458
SW | 60026893 | F077C | WANDOAN | F077C_Wandoan 33 kV | Loading (MVA) | 3.5286 | 3.5859 | 2.6873 | 3.5283 | 3.6189 | 2.6871 | 3.5283 | 3.6189 | 2.6871 | 3.5283 | 3.6189 | 2.6871 | 3.5286 | 3.5859 | 2.6873
SW | 60026893 | F077C | WANDOAN | F077C_Wandoan 33 kV | Loading (MW) | 3.461 | 3.5215 | 2.6507 | 3.4609 | 3.555 | 2.6506 | 3.4609 | 3.555 | 2.6506 | 3.4609 | 3.555 | 2.6506 | 3.461 | 3.5215 | 2.6507
SW | 60026893 | F077C | WANDOAN | F077C_Wandoan 33 kV | Power Factor | 0.98086 | 0.98204 | 0.98636 | 0.98089 | 0.98236 | 0.98643 | 0.98089 | 0.98236 | 0.98643 | 0.98089 | 0.98236 | 0.98643 | 0.98086 | 0.98204 | 0.98636
SW | 60026893 | F077C | WANDOAN | F077C_Wandoan 33 kV | Rating (A) | 173 | 278 | 278 | 173 | 278 | 278 | 173 | 278 | 278 | 173 | 278 | 278 | 173 | 278 | 278
SW | 60026893 | F077C | WANDOAN | F077C_Wandoan 33 kV | Time | 16:30 | 17:30 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 17:30 | 22:00
SW | 60026893 | F077C | WANDOAN | F077C_Wandoan 33 kV | Voltage at Constrained Conductor | 32.1503 | 32.1021 | 32.6325 | 32.1732 | 32.0964 | 32.649 | 32.1732 | 32.0964 | 32.649 | 32.1731 | 32.0964 | 32.649 | 32.1503 | 32.102 | 32.6325
SW | 60026994 | F083S | Dirrabandi Town 33 kV | F083S_Dirrabandi Town 33 kV | % of Rated A | 12.7706 | 11.452 | 11.7363 | 12.7745 | 11.454 | 11.7382 | 12.7726 | 11.4537 | 11.7572 | 12.7724 | 11.4536 | 11.757 | 12.7684 | 11.4515 | 11.7552
SW | 60026994 | F083S | Dirrabandi Town 33 kV | F083S_Dirrabandi Town 33 kV | Limiting Line Name | TR_LINE 27419_1 | TR_LINE 44480_1 | TR_LINE 44480_1 | TR_LINE 27419_1 | TR_LINE 44480_1 | TR_LINE 44480_1 | TR_LINE 27419_1 | TR_LINE 44480_1 | TR_LINE 44480_1 | TR_LINE 27419_1 | TR_LINE 44480_1 | TR_LINE 44480_1 | TR_LINE 27419_1 | TR_LINE 44480_1 | TR_LINE 44480_1
SW | 60026994 | F083S | Dirrabandi Town 33 kV | F083S_Dirrabandi Town 33 kV | Loading (A) | 9.3226 | 10.4213 | 10.0932 | 9.3254 | 10.4232 | 10.0948 | 9.324 | 10.4229 | 10.1112 | 9.3238 | 10.4227 | 10.111 | 9.321 | 10.4209 | 10.1094
SW | 60026994 | F083S | Dirrabandi Town 33 kV | F083S_Dirrabandi Town 33 kV | Loading (MVA) | 0.51699 | 0.57951 | 0.56148 | 0.517 | 0.5795 | 0.56146 | 0.517 | 0.5795 | 0.56132 | 0.517 | 0.5795 | 0.56132 | 0.51699 | 0.57951 | 0.56133
SW | 60026994 | F083S | Dirrabandi Town 33 kV | F083S_Dirrabandi Town 33 kV | Loading (MW) | 0.45777 | 0.57647 | 0.55731 | 0.45778 | 0.57647 | 0.55731 | 0.45778 | 0.57647 | 0.55731 | 0.45778 | 0.57647 | 0.55731 | 0.45777 | 0.57647 | 0.55731
SW | 60026994 | F083S | Dirrabandi Town 33 kV | F083S_Dirrabandi Town 33 kV | Power Factor | 0.88545 | 0.99476 | 0.99258 | 0.88545 | 0.99478 | 0.99261 | 0.88545 | 0.99478 | 0.99287 | 0.88545 | 0.99477 | 0.99287 | 0.88546 | 0.99475 | 0.99284
SW | 60026994 | F083S | Dirrabandi Town 33 kV | F083S_Dirrabandi Town 33 kV | Rating (A) | 73 | 91 | 86 | 73 | 91 | 86 | 73 | 91 | 86 | 73 | 91 | 86 | 73 | 91 | 86
SW | 60026994 | F083S | Dirrabandi Town 33 kV | F083S_Dirrabandi Town 33 kV | Time | 12:00 | 21:30 | 22:00 | 12:00 | 21:30 | 22:00 | 12:00 | 21:30 | 22:00 | 12:00 | 21:30 | 22:00 | 12:00 | 21:30 | 22:00
SW | 60026994 | F083S | Dirrabandi Town 33 kV | F083S_Dirrabandi Town 33 kV | Voltage at Constrained Conductor | 32.0175 | 32.1056 | 32.1175 | 32.0084 | 32.099 | 32.1115 | 32.0128 | 32.0999 | 32.0513 | 32.0134 | 32.1005 | 32.0517 | 32.0229 | 32.107 | 32.0576
SW | 60027002 | F097D | JANDOWAE | F097D_Jandowae 33 kV | % of Rated A | 26.7012 | 12.4141 | 18.1267 | 26.6807 | 12.3992 | 18.12 | 26.6658 | 12.3909 | 18.1146 | 26.6715 | 12.5623 | 18.1178 | 26.6982 | 12.5797 | 18.1283
SW | 60027002 | F097D | JANDOWAE | F097D_Jandowae 33 kV | Limiting Line Name | TR_LINE 76815_3 | TR_LINE 76815_3 | TR_LINE 76815_3 | TR_LINE 76815_3 | TR_LINE 76815_3 | TR_LINE 76815_3 | TR_LINE 76815_3 | TR_LINE 76815_3 | TR_LINE 76815_3 | TR_LINE 76815_3 | TR_LINE 76815_3 | TR_LINE 76815_3 | TR_LINE 76815_3 | TR_LINE 76815_3 | TR_LINE 76815_3
SW | 60027002 | F097D | JANDOWAE | F097D_Jandowae 33 kV | Loading (A) | 38.1295 | 26.3179 | 37.8318 | 38.1002 | 26.2862 | 37.8176 | 38.0789 | 26.2688 | 37.8063 | 38.0872 | 26.6322 | 37.8131 | 38.1253 | 26.6691 | 37.835
SW | 60027002 | F097D | JANDOWAE | F097D_Jandowae 33 kV | Loading (MVA) | 2.1667 | 1.5098 | 2.1734 | 2.1665 | 1.5093 | 2.1733 | 2.1664 | 1.5092 | 2.1732 | 2.1664 | 1.511 | 2.1733 | 2.1667 | 1.5112 | 2.1734
SW | 60027002 | F097D | JANDOWAE | F097D_Jandowae 33 kV | Loading (MW) | 1.9715 | 1.4417 | 1.9821 | 1.9715 | 1.4416 | 1.9821 | 1.9715 | 1.4416 | 1.9821 | 1.9715 | 1.4418 | 1.9821 | 1.9715 | 1.4418 | 1.9821
SW | 60027002 | F097D | JANDOWAE | F097D_Jandowae 33 kV | Power Factor | 0.90991 | 0.95491 | 0.912 | 0.90999 | 0.95517 | 0.91203 | 0.91004 | 0.95524 | 0.91206 | 0.91002 | 0.95417 | 0.91205 | 0.90993 | 0.95404 | 0.91199
SW | 60027002 | F097D | JANDOWAE | F097D_Jandowae 33 kV | Rating (A) | 143 | 212 | 209 | 143 | 212 | 209 | 143 | 212 | 209 | 143 | 212 | 209 | 143 | 212 | 209
SW | 60027002 | F097D | JANDOWAE | F097D_Jandowae 33 kV | Time | 14:30 | 17:00 | 7:30 | 14:30 | 17:00 | 7:30 | 14:30 | 17:00 | 7:30 | 14:30 | 17:00 | 7:30 | 14:30 | 17:00 | 7:30
SW | 60027002 | F097D | JANDOWAE | F097D_Jandowae 33 kV | Voltage at Constrained Conductor | 32.8084 | 33.1217 | 33.1681 | 32.8306 | 33.1504 | 33.1791 | 32.8467 | 33.1701 | 33.1878 | 32.8405 | 32.7571 | 33.1825 | 32.8115 | 32.7165 | 33.1656
SW | 60027003 | F099D | WARRA | F099D_Warra 33 kV | % of Rated A | 62.7729 | 22.4205 | 55.1394 | 63.1481 | 22.3982 | 55.1187 | 63.5264 | 22.3831 | 55.1032 | 62.7424 | 22.3919 | 55.1149 | 63.1742 | 22.1134 | 55.147
SW | 60027003 | F099D | WARRA | F099D_Warra 33 kV | Limiting Line Name | TR_CABLE 132_1 | TR_LINE 25305_1 | TR_LINE 25305_1 | TR_CABLE 132_1 | TR_LINE 25305_1 | TR_LINE 25305_1 | TR_CABLE 132_1 | TR_LINE 25305_1 | TR_LINE 25305_1 | TR_CABLE 132_1 | TR_LINE 25305_1 | TR_LINE 25305_1 | TR_CABLE 132_1 | TR_LINE 25305_1 | TR_LINE 25305_1
SW | 60027003 | F099D | WARRA | F099D_Warra 33 kV | Loading (A) | 62.7729 | 39.6793 | 86.5626 | 63.1481 | 39.6398 | 86.5301 | 63.5265 | 39.6131 | 86.5058 | 62.7424 | 39.6285 | 86.5241 | 63.1742 | 39.1357 | 86.5745
SW | 60027003 | F099D | WARRA | F099D_Warra 33 kV | Loading (MVA) | 3.5679 | 2.249 | 4.9524 | 3.568 | 2.2488 | 4.9523 | 3.568 | 2.2486 | 4.9522 | 3.5679 | 2.2487 | 4.9522 | 3.568 | 2.2214 | 4.9525
SW | 60027003 | F099D | WARRA | F099D_Warra 33 kV | Loading (MW) | 3.1222 | 2.1146 | 4.4977 | 3.1222 | 2.1145 | 4.4977 | 3.1222 | 2.1145 | 4.4977 | 3.1222 | 2.1145 | 4.4977 | 3.1222 | 2.0925 | 4.4977
SW | 60027003 | F099D | WARRA | F099D_Warra 33 kV | Power Factor | 0.87507 | 0.94024 | 0.90819 | 0.87506 | 0.94032 | 0.90821 | 0.87505 | 0.94038 | 0.90823 | 0.87507 | 0.94034 | 0.90821 | 0.87506 | 0.94196 | 0.90818
SW | 60027003 | F099D | WARRA | F099D_Warra 33 kV | Rating (A) | 100 | 177 | 157 | 100 | 177 | 157 | 100 | 177 | 157 | 100 | 177 | 157 | 100 | 177 | 157
SW | 60027003 | F099D | WARRA | F099D_Warra 33 kV | Time | 11:00 | 17:30 | 8:00 | 11:00 | 17:30 | 8:00 | 11:00 | 17:30 | 8:00 | 11:00 | 17:30 | 8:00 | 11:00 | 18:00 | 8:00
SW | 60027003 | F099D | WARRA | F099D_Warra 33 kV | Voltage at Constrained Conductor | 32.8158 | 32.7235 | 33.0314 | 32.6212 | 32.7529 | 33.0428 | 32.4273 | 32.7728 | 33.0514 | 32.8318 | 32.7613 | 33.0449 | 32.6077 | 32.7712 | 33.0272
SW | 60300324 | F5530 | 728 MR - South Toowo | 728_Middle Ridge-South Toowoomba 110 kV | % of Rated A | 22.2481 | 21.1518 | 16.9679 | 22.0977 | 21.0457 | 16.9113 | 22.023 | 20.9936 | 16.8897 | 21.8911 | 20.9557 | 16.8895 | 22.0589 | 21.1317 | 16.9811
SW | 60300324 | F5530 | 728 MR - South Toowo | 728_Middle Ridge-South Toowoomba 110 kV | Limiting Line Name | TR_LINE 33947_1 | TR_LINE 33947_1 | TR_LINE 33947_1 | TR_LINE 33947_1 | TR_LINE 33947_1 | TR_LINE 33947_1 | TR_LINE 33947_1 | TR_LINE 33947_1 | TR_LINE 33947_1 | TR_LINE 33947_1 | TR_LINE 33947_1 | TR_LINE 33947_1 | TR_LINE 33947_1 | TR_LINE 33947_1 | TR_LINE 33947_1
SW | 60300324 | F5530 | 728 MR - South Toowo | 728_Middle Ridge-South Toowoomba 110 kV | Loading (A) | 228.9328 | 224.6319 | 161.7042 | 227.3852 | 223.5053 | 161.1651 | 226.6167 | 222.9523 | 160.9591 | 225.2592 | 222.5494 | 160.957 | 226.986 | 224.4186 | 161.8296
SW | 60300324 | F5530 | 728 MR - South Toowo | 728_Middle Ridge-South Toowoomba 110 kV | Loading (MVA) | 45.9848 | 45.1155 | 32.4114 | 45.675 | 44.8945 | 32.3049 | 45.5241 | 44.7862 | 32.2637 | 45.5522 | 44.9737 | 32.3118 | 45.8489 | 45.3097 | 32.5349
SW | 60300324 | F5530 | 728 MR - South Toowo | 728_Middle Ridge-South Toowoomba 110 kV | Loading (MW) | 45.704 | 44.8053 | 30.8609 | 45.4131 | 44.5705 | 30.7376 | 45.2515 | 44.457 | 30.687 | 45.25 | 44.6581 | 30.7179 | 45.5683 | 45.0184 | 30.966
SW | 60300324 | F5530 | 728 MR - South Toowo | 728_Middle Ridge-South Toowoomba 110 kV | Power Factor | 0.9939 | 0.99312 | 0.95216 | 0.99427 | 0.99278 | 0.95148 | 0.99401 | 0.99265 | 0.95113 | 0.99337 | 0.99298 | 0.95067 | 0.99388 | 0.99357 | 0.95178
SW | 60300324 | F5530 | 728 MR - South Toowo | 728_Middle Ridge-South Toowoomba 110 kV | Rating (A) | 1029 | 1062 | 953 | 1029 | 1062 | 953 | 1029 | 1062 | 953 | 1029 | 1062 | 953 | 1029 | 1062 | 953
SW | 60300324 | F5530 | 728 MR - South Toowo | 728_Middle Ridge-South Toowoomba 110 kV | Time | 16:30 | 17:00 | 22:00 | 16:30 | 17:00 | 22:00 | 16:30 | 17:00 | 22:00 | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00
SW | 60300324 | F5530 | 728 MR - South Toowo | 728_Middle Ridge-South Toowoomba 110 kV | Voltage at Constrained Conductor | 115.9699 | 115.9562 | 115.7221 | 115.9727 | 115.9698 | 115.7275 | 115.9816 | 115.9769 | 115.7278 | 116.7526 | 116.6734 | 115.9021 | 116.6191 | 116.566 | 116.0729
SW | 60300325 | F5555 | 734 MR - Yarranlea | F5555_734(Middle Ridge-Yarranlea) 110 kV | % of Rated A | 21.6402 | 23.3103 | 19.6498 | 21.9708 | 23.5878 | 19.8408 | 21.9684 | 23.5853 | 19.8408 | 21.7799 | 23.6096 | 19.8011 | 22.1848 | 23.9808 | 20.036
SW | 60300325 | F5555 | 734 MR - Yarranlea | F5555_734(Middle Ridge-Yarranlea) 110 kV | Limiting Line Name | TR_LINE 25640_1 | TR_LINE 25640_1 | TR_LINE 25640_1 | TR_LINE 25640_1 | TR_LINE 25640_1 | TR_LINE 25640_1 | TR_LINE 25640_1 | TR_LINE 25640_1 | TR_LINE 25640_1 | TR_LINE 25640_1 | TR_LINE 25640_1 | TR_LINE 25640_1 | TR_LINE 25640_1 | TR_LINE 25640_1 | TR_LINE 25640_1
SW | 60300325 | F5555 | 734 MR - Yarranlea | F5555_734(Middle Ridge-Yarranlea) 110 kV | Loading (A) | 62.1074 | 66.6675 | 48.535 | 63.0562 | 67.461 | 49.0068 | 63.0492 | 67.4539 | 49.0067 | 62.5082 | 67.5235 | 48.9086 | 63.6703 | 68.5851 | 49.4889
SW | 60300325 | F5555 | 734 MR - Yarranlea | F5555_734(Middle Ridge-Yarranlea) 110 kV | Loading (MVA) | 12.2018 | 13.1589 | 9.5682 | 12.3836 | 13.3135 | 9.6599 | 12.3832 | 13.3131 | 9.6599 | 12.3635 | 13.3168 | 9.6558 | 12.5718 | 13.5072 | 9.7827
SW | 60300325 | F5555 | 734 MR - Yarranlea | F5555_734(Middle Ridge-Yarranlea) 110 kV | Loading (MW) | 11.329 | 12.1064 | 9.0165 | 11.4866 | 12.2575 | 9.1014 | 11.4865 | 12.2574 | 9.1014 | 11.4803 | 12.2585 | 9.1004 | 11.6386 | 12.4167 | 9.2118
SW | 60300325 | F5555 | 734 MR - Yarranlea | F5555_734(Middle Ridge-Yarranlea) 110 kV | Power Factor | 0.92847 | 0.92001 | 0.94234 | 0.92757 | 0.92069 | 0.94218 | 0.92758 | 0.9207 | 0.94218 | 0.92856 | 0.92053 | 0.94248 | 0.92577 | 0.91926 | 0.94164
SW | 60300325 | F5555 | 734 MR - Yarranlea | F5555_734(Middle Ridge-Yarranlea) 110 kV | Rating (A) | 287 | 286 | 247 | 287 | 286 | 247 | 287 | 286 | 247 | 287 | 286 | 247 | 287 | 286 | 247
SW | 60300325 | F5555 | 734 MR - Yarranlea | F5555_734(Middle Ridge-Yarranlea) 110 kV | Time | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00
SW | 60300325 | F5555 | 734 MR - Yarranlea | F5555_734(Middle Ridge-Yarranlea) 110 kV | Voltage at Constrained Conductor | 113.4277 | 113.9582 | 113.8191 | 113.3854 | 113.9404 | 113.8038 | 113.3947 | 113.9492 | 113.8041 | 114.1944 | 113.8634 | 113.9839 | 113.999 | 113.704 | 114.127
SW | 60300326 | F5560 | 735 MR - Warwick | F5560_735(Middle Ridge-Warwick) 110 kV | % of Rated A | 41.2745 | 37.0218 | 27.5108 | 41.2276 | 36.9969 | 27.5311 | 41.08 | 36.8547 | 27.4165 | 40.9396 | 36.7862 | 27.47 | 41.3313 | 37.1523 | 27.6401
SW | 60300326 | F5560 | 735 MR - Warwick | F5560_735(Middle Ridge-Warwick) 110 kV | Limiting Line Name | TR_LINE 94897_1 | TR_LINE 94897_1 | TR_LINE 25701_1 | TR_LINE 94897_1 | TR_LINE 94897_1 | TR_LINE 25701_1 | TR_LINE 94897_1 | TR_LINE 94897_1 | TR_LINE 25701_1 | TR_LINE 94897_1 | TR_LINE 94897_1 | TR_LINE 25701_1 | TR_LINE 94897_1 | TR_LINE 94897_1 | TR_LINE 25701_1
SW | 60300326 | F5560 | 735 MR - Warwick | F5560_735(Middle Ridge-Warwick) 110 kV | Loading (A) | 106.0756 | 118.4699 | 80.8817 | 105.9549 | 118.3899 | 80.9414 | 105.5755 | 117.9351 | 80.6045 | 105.2148 | 117.7159 | 80.7617 | 106.2214 | 118.8875 | 81.2618
SW | 60300326 | F5560 | 735 MR - Warwick | F5560_735(Middle Ridge-Warwick) 110 kV | Loading (MVA) | 21.3085 | 23.7946 | 16.2112 | 21.2848 | 23.7807 | 16.2239 | 21.2102 | 23.6904 | 16.1564 | 21.2782 | 23.7893 | 16.2122 | 21.4572 | 24.0035 | 16.3365
SW | 60300326 | F5560 | 735 MR - Warwick | F5560_735(Middle Ridge-Warwick) 110 kV | Loading (MW) | 19.7706 | 22.7469 | 13.4278 | 19.7395 | 22.7283 | 13.4445 | 19.6486 | 22.6233 | 13.3991 | 19.7402 | 22.6843 | 13.452 | 19.975 | 22.9459 | 13.604
SW | 60300326 | F5560 | 735 MR - Warwick | F5560_735(Middle Ridge-Warwick) 110 kV | Power Factor | 0.92783 | 0.95597 | 0.82831 | 0.9274 | 0.95575 | 0.82869 | 0.92637 | 0.95495 | 0.82934 | 0.92772 | 0.95355 | 0.82974 | 0.93093 | 0.95594 | 0.83273
SW | 60300326 | F5560 | 735 MR - Warwick | F5560_735(Middle Ridge-Warwick) 110 kV | Rating (A) | 257 | 320 | 294 | 257 | 320 | 294 | 257 | 320 | 294 | 257 | 320 | 294 | 257 | 320 | 294
SW | 60300326 | F5560 | 735 MR - Warwick | F5560_735(Middle Ridge-Warwick) 110 kV | Time | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00
SW | 60300326 | F5560 | 735 MR - Warwick | F5560_735(Middle Ridge-Warwick) 110 kV | Voltage at Constrained Conductor | 115.9783 | 115.9603 | 115.7189 | 115.9811 | 115.9708 | 115.7241 | 115.9902 | 115.9763 | 115.7242 | 116.761 | 116.677 | 115.8983 | 116.6271 | 116.5676 | 116.0678
SW | 60306799 | F3095 | Highfields | F3095_Highfields 33 kV | % of Rated A | 52.4964 | 43.5424 | 33.3412 | 51.8699 | 42.936 | 32.9471 | 52.0438 | 42.5222 | 33.0637 | 52.0715 | 43.5509 | 33.2703 | 22.8078 | 20.4961 | 15.0118
SW | 60306799 | F3095 | Highfields | F3095_Highfields 33 kV | Limiting Line Name | TR_LINE 194642_1 | TR_LINE 194642_1 | TR_LINE 194642_1 | TR_LINE 194642_1 | TR_LINE 194642_1 | TR_LINE 194642_1 | TR_LINE 194642_1 | TR_LINE 194642_1 | TR_LINE 194642_1 | TR_LINE 194642_1 | TR_LINE 194642_1 | TR_LINE 194642_1 | TR_LINE 194642_1 | TR_LINE 194642_1 | TR_LINE 194642_1
SW | 60306799 | F3095 | Highfields | F3095_Highfields 33 kV | Loading (A) | 88.7078 | 104.491 | 78.0072 | 87.6489 | 103.0355 | 77.0848 | 87.9429 | 102.0425 | 77.3577 | 87.9897 | 104.5115 | 77.8412 | 38.5345 | 49.1808 | 35.1166
SW | 60306799 | F3095 | Highfields | F3095_Highfields 33 kV | Loading (MVA) | 5.1619 | 6.027 | 4.5388 | 5.1013 | 5.9453 | 4.486 | 5.1189 | 5.9665 | 4.502 | 5.1578 | 6.0253 | 4.5369 | 2.2759 | 2.8621 | 2.0666
SW | 60306799 | F3095 | Highfields | F3095_Highfields 33 kV | Loading (MW) | 4.9022 | 5.7391 | 4.3025 | 4.8428 | 5.6596 | 4.2504 | 4.8636 | 5.6877 | 4.2696 | 4.9023 | 5.7415 | 4.3038 | 2.1739 | 2.7506 | 1.9664
SW | 60306799 | F3095 | Highfields | F3095_Highfields 33 kV | Power Factor | 0.94968 | 0.95223 | 0.94795 | 0.94932 | 0.95194 | 0.94749 | 0.95012 | 0.95327 | 0.94838 | 0.95045 | 0.95291 | 0.94861 | 0.95521 | 0.96106 | 0.9515
SW | 60306799 | F3095 | Highfields | F3095_Highfields 33 kV | Rating (A) | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234
SW | 60306799 | F3095 | Highfields | F3095_Highfields 33 kV | Time | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00
SW | 60306799 | F3095 | Highfields | F3095_Highfields 33 kV | Voltage at Constrained Conductor | 33.5962 | 33.3012 | 33.5926 | 33.6029 | 33.3141 | 33.5992 | 33.6062 | 33.7583 | 33.5998 | 33.8435 | 33.2851 | 33.6504 | 34.0984 | 33.5993 | 33.9771
SW | 60306800 | F3815 | North Street No 1 | F3815 North Street No 1 33 kV | % of Rated A | 1.3287 | 0.9961 | 1.0352 | 1.3289 | 0.9962 | 1.0353 | 1.329 | 0.99624 | 1.0353 | 1.3289 | 0.99669 | 1.0355 | 1.3288 | 0.99684 | 1.0347
SW | 60306800 | F3815 | North Street No 1 | F3815 North Street No 1 33 kV | Limiting Line Name | TR_LINE 181524_1 | TR_LINE 181524_1 | TR_LINE 181524_1 | TR_LINE 181524_1 | TR_LINE 181524_1 | TR_LINE 181524_1 | TR_LINE 181524_1 | TR_LINE 181524_1 | TR_LINE 181524_1 | TR_LINE 181524_1 | TR_LINE 181524_1 | TR_LINE 181524_1 | TR_LINE 181524_1 | TR_LINE 181524_1 | TR_LINE 181524_1
SW | 60306800 | F3815 | North Street No 1 | F3815 North Street No 1 33 kV | Loading (A) | 2.3518 | 2.3508 | 2.3396 | 2.3521 | 2.351 | 2.3397 | 2.3522 | 2.3511 | 2.3398 | 2.3521 | 2.3522 | 2.3401 | 2.3519 | 2.3525 | 2.3385
SW | 60306800 | F3815 | North Street No 1 | F3815 North Street No 1 33 kV | Loading (MVA) | 0.14001 | 0.1399 | 0.13857 | 0.14005 | 0.13992 | 0.13858 | 0.14007 | 0.13994 | 0.13859 | 0.14005 | 0.14006 | 0.13863 | 0.14003 | 0.1401 | 0.13843
SW | 60306800 | F3815 | North Street No 1 | F3815 North Street No 1 33 kV | Loading (MW) | 0.00044702 | 0.00044664 | 0.00044241 | 0.00044713 | 0.00044673 | 0.00044245 | 0.0004472 | 0.00044677 | 0.00044246 | 0.00044714 | 0.00044717 | 0.0004426 | 0.00044706 | 0.0004473 | 0.00044197
SW | 60306800 | F3815 | North Street No 1 | F3815 North Street No 1 33 kV | Power Factor | 0.0031927 | 0.0031927 | 0.0031927 | 0.0031927 | 0.0031927 | 0.0031927 | 0.0031927 | 0.0031927 | 0.0031927 | 0.0031927 | 0.0031927 | 0.0031927 | 0.0031927 | 0.0031927 | 0.0031927
SW | 60306800 | F3815 | North Street No 1 | F3815 North Street No 1 33 kV | Rating (A) | 177 | 236 | 226 | 177 | 236 | 226 | 177 | 236 | 226 | 177 | 236 | 226 | 177 | 236 | 226
SW | 60306800 | F3815 | North Street No 1 | F3815 North Street No 1 33 kV | Time | 15:00 | 21:00 | 2:00 | 15:00 | 21:00 | 2:00 | 15:00 | 21:00 | 2:00 | 13:30 | 21:30 | 3:00 | 15:00 | 21:00 | 1:00
SW | 60306800 | F3815 | North Street No 1 | F3815 North Street No 1 33 kV | Voltage at Constrained Conductor | 34.3727 | 34.3582 | 34.1948 | 34.3769 | 34.3616 | 34.1964 | 34.3794 | 34.363 | 34.197 | 34.3772 | 34.3785 | 34.2024 | 34.3743 | 34.3836 | 34.1781
SW | 60306801 | F3910 | Perseverence Creek 1 | F3910_Perseverence Creek 1 33 kV | % of Rated A | 49.5896 | 39.2186 | 34.5899 | 49.4687 | 39.0859 | 34.5849 | 49.3484 | 38.8289 | 34.5797 | 50.3317 | 39.1819 | 34.6011 | 70.9705 | 56.0697 | 34.4673
SW | 60306801 | F3910 | Perseverence Creek 1 | F3910_Perseverence Creek 1 33 kV | Limiting Line Name | TR_LINE 187299_1 | TR_LINE 187299_1 | TR_LINE 183865_2 | TR_LINE 187299_1 | TR_LINE 187299_1 | TR_LINE 183865_2 | TR_LINE 187299_1 | TR_LINE 187299_1 | TR_LINE 183865_2 | TR_LINE 187299_1 | TR_LINE 187299_1 | TR_LINE 183865_2 | TR_LINE 187299_1 | TR_LINE 187299_1 | TR_LINE 183865_2
SW | 60306801 | F3910 | Perseverence Creek 1 | F3910_Perseverence Creek 1 33 kV | Loading (A) | 83.8063 | 94.1245 | 80.9121 | 83.602 | 93.8059 | 80.9004 | 83.3987 | 93.1891 | 80.888 | 85.0605 | 94.0365 | 80.9383 | 119.9401 | 134.5672 | 80.625
SW | 60306801 | F3910 | Perseverence Creek 1 | F3910_Perseverence Creek 1 33 kV | Loading (MVA) | 4.7378 | 5.2311 | 4.5739 | 4.7275 | 5.2146 | 4.5739 | 4.7169 | 5.1664 | 4.5738 | 4.738 | 5.2068 | 4.574 | 6.7091 | 7.3857 | 4.5743
SW | 60306801 | F3910 | Perseverence Creek 1 | F3910_Perseverence Creek 1 33 kV | Loading (MW) | 4.498 | 5.0228 | 4.2149 | 4.4873 | 5.006 | 4.2149 | 4.4774 | 4.9672 | 4.2149 | 4.4981 | 5.0073 | 4.2149 | 6.691 | 7.3823 | 4.2148
SW | 60306801 | F3910 | Perseverence Creek 1 | F3910_Perseverence Creek 1 33 kV | Power Factor | 0.94938 | 0.96018 | 0.92151 | 0.9492 | 0.95999 | 0.92151 | 0.94923 | 0.96145 | 0.92152 | 0.94937 | 0.96168 | 0.92149 | 0.99731 | 0.99954 | 0.92141
SW | 60306801 | F3910 | Perseverence Creek 1 | F3910_Perseverence Creek 1 33 kV | Rating (A) | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234
SW | 60306801 | F3910 | Perseverence Creek 1 | F3910_Perseverence Creek 1 33 kV | Time | 14:00 | 21:30 | 6:30 | 14:00 | 21:30 | 6:30 | 14:00 | 20:00 | 6:30 | 14:00 | 20:00 | 6:30 | 16:30 | 18:00 | 6:30
SW | 60306801 | F3910 | Perseverence Creek 1 | F3910_Perseverence Creek 1 33 kV | Voltage at Constrained Conductor | 32.6393 | 32.087 | 32.6371 | 32.6476 | 32.0947 | 32.6416 | 32.6538 | 32.008 | 32.6463 | 32.1595 | 31.9681 | 32.6271 | 32.2952 | 31.6877 | 32.7562
SW | 60306802 | F7233 | 7233 MR - Torrington | 7233_Middle Ridge-Torrington 110 kV | % of Rated A | 23.646 | 21.4486 | 15.0184 | 23.4121 | 21.2369 | 14.8711 | 23.3814 | 21.2047 | 14.8568 | 24.8219 | 22.4427 | 15.7529 | 26.9801 | 24.1993 | 17.3959
SW | 60306802 | F7233 | 7233 MR - Torrington | 7233_Middle Ridge-Torrington 110 kV | Limiting Line Name | TR_LINE 27024_2 | TR_LINE 27024_2 | TR_LINE 27024_2 | TR_LINE 27024_2 | TR_LINE 27024_2 | TR_LINE 27024_2 | TR_LINE 27024_2 | TR_LINE 27024_2 | TR_LINE 27024_2 | TR_LINE 27024_2 | TR_LINE 27024_2 | TR_LINE 27024_2 | TR_LINE 27024_2 | TR_LINE 27024_2 | TR_LINE 27024_2
SW | 60306802 | F7233 | 7233 MR - Torrington | 7233_Middle Ridge-Torrington 110 kV | Loading (A) | 207.1406 | 206.3 | 128.2568 | 205.0895 | 204.2612 | 126.9995 | 204.8208 | 203.9519 | 126.8769 | 217.4348 | 215.8598 | 134.1584 | 236.3331 | 232.7439 | 148.139
SW | 60306802 | F7233 | 7233 MR - Torrington | 7233_Middle Ridge-Torrington 110 kV | Loading (MVA) | 41.4297 | 41.5367 | 25.584 | 41.0228 | 41.1337 | 25.336 | 40.9726 | 41.0749 | 25.3118 | 43.7679 | 43.4257 | 26.8671 | 47.4841 | 46.7493 | 29.6977
SW | 60306802 | F7233 | 7233 MR - Torrington | 7233_Middle Ridge-Torrington 110 kV | Loading (MW) | 39.2872 | 39.481 | 24.8732 | 38.9266 | 39.123 | 24.6413 | 38.8859 | 39.0756 | 24.6199 | 41.2277 | 41.0429 | 26.0385 | 44.0938 | 43.6029 | 28.5009
SW | 60306802 | F7233 | 7233 MR - Torrington | 7233_Middle Ridge-Torrington 110 kV | Power Factor | 0.94829 | 0.95051 | 0.97222 | 0.9489 | 0.95112 | 0.97258 | 0.94907 | 0.95133 | 0.97267 | 0.94196 | 0.94513 | 0.96916 | 0.9286 | 0.9327 | 0.9597
SW | 60306802 | F7233 | 7233 MR - Torrington | 7233_Middle Ridge-Torrington 110 kV | Rating (A) | 878 | 964 | 854 | 878 | 964 | 854 | 878 | 964 | 854 | 878 | 964 | 854 | 878 | 964 | 854
SW | 60306802 | F7233 | 7233 MR - Torrington | 7233_Middle Ridge-Torrington 110 kV | Time | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00
SW | 60306802 | F7233 | 7233 MR - Torrington | 7233_Middle Ridge-Torrington 110 kV | Voltage at Constrained Conductor | 115.4745 | 116.2445 | 115.1666 | 115.4838 | 116.2657 | 115.1794 | 115.4938 | 116.2754 | 115.1806 | 116.216 | 116.1487 | 115.6226 | 116.0013 | 115.9674 | 115.7424
SW | 60306803 | F5535 | 730 MR - South Toowo | 730_Middle Ridge-South Toowoomba 110 kV | % of Rated A | 22.2541 | 21.1576 | 16.9726 | 22.1037 | 21.0514 | 16.9159 | 22.029 | 20.9994 | 16.8943 | 21.8971 | 20.962 | 16.8941 | 22.065 | 21.1382 | 16.9857
SW | 60306803 | F5535 | 730 MR - South Toowo | 730_Middle Ridge-South Toowoomba 110 kV | Limiting Line Name | TR_LINE 33960_1 | TR_LINE 33960_1 | TR_LINE 33960_1 | TR_LINE 33960_1 | TR_LINE 33960_1 | TR_LINE 33960_1 | TR_LINE 33960_1 | TR_LINE 33960_1 | TR_LINE 33960_1 | TR_LINE 33960_1 | TR_LINE 33960_1 | TR_LINE 33960_1 | TR_LINE 33960_1 | TR_LINE 33960_1 | TR_LINE 33960_1
SW | 60306803 | F5535 | 730 MR - South Toowo | 730_Middle Ridge-South Toowoomba 110 kV | Loading (A) | 228.9948 | 224.6933 | 161.7484 | 227.4467 | 223.5662 | 161.2089 | 226.6782 | 223.0132 | 161.0029 | 225.3207 | 222.617 | 161.0009 | 227.0485 | 224.4873 | 161.8741
SW | 60306803 | F5535 | 730 MR - South Toowo | 730_Middle Ridge-South Toowoomba 110 kV | Loading (MVA) | 45.9972 | 45.1278 | 32.4203 | 45.6873 | 44.9068 | 32.3137 | 45.5365 | 44.7984 | 32.2724 | 45.5647 | 44.9874 | 32.3207 | 45.8616 | 45.3236 | 32.5438
SW | 60306803 | F5535 | 730 MR - South Toowo | 730_Middle Ridge-South Toowoomba 110 kV | Loading (MW) | 45.7165 | 44.8176 | 30.87 | 45.4254 | 44.5827 | 30.7466 | 45.2638 | 44.4693 | 30.696 | 45.2624 | 44.6717 | 30.7269 | 45.5809 | 45.0323 | 30.9752
SW | 60306803 | F5535 | 730 MR - South Toowo | 730_Middle Ridge-South Toowoomba 110 kV | Power Factor | 0.9939 | 0.99313 | 0.95218 | 0.99427 | 0.99278 | 0.9515 | 0.99401 | 0.99265 | 0.95115 | 0.99337 | 0.99298 | 0.95069 | 0.99388 | 0.99357 | 0.9518
SW | 60306803 | F5535 | 730 MR - South Toowo | 730_Middle Ridge-South Toowoomba 110 kV | Rating (A) | 1029 | 1062 | 953 | 1029 | 1062 | 953 | 1029 | 1062 | 953 | 1029 | 1062 | 953 | 1029 | 1062 | 953
SW | 60306803 | F5535 | 730 MR - South Toowo | 730_Middle Ridge-South Toowoomba 110 kV | Time | 16:30 | 17:00 | 22:00 | 16:30 | 17:00 | 22:00 | 16:30 | 17:00 | 22:00 | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00
SW | 60306803 | F5535 | 730 MR - South Toowo | 730_Middle Ridge-South Toowoomba 110 kV | Voltage at Constrained Conductor | 115.9699 | 115.9562 | 115.7221 | 115.9727 | 115.9698 | 115.7275 | 115.9816 | 115.9769 | 115.7278 | 116.7526 | 116.6734 | 115.9021 | 116.6191 | 116.566 | 116.0729
SW | 60306804 | F5550 | 733 MR - Yarranlea | F5550_733(Middle Ridge-Yarranlea) 110 kV | % of Rated A | 21.6581 | 23.3295 | 19.6658 | 21.989 | 23.6072 | 19.857 | 21.9865 | 23.6047 | 19.857 | 21.7978 | 23.6291 | 19.8172 | 22.2031 | 24.0006 | 20.0523
SW | 60306804 | F5550 | 733 MR - Yarranlea | F5550_733(Middle Ridge-Yarranlea) 110 kV | Limiting Line Name | TR_LINE 224268_1 | TR_LINE 224268_1 | TR_LINE 224268_1 | TR_LINE 224268_1 | TR_LINE 224268_1 | TR_LINE 224268_1 | TR_LINE 224268_1 | TR_LINE 224268_1 | TR_LINE 224268_1 | TR_LINE 224268_1 | TR_LINE 224268_1 | TR_LINE 224268_1 | TR_LINE 224268_1 | TR_LINE 224268_1 | TR_LINE 224268_1
SW | 60306804 | F5550 | 733 MR - Yarranlea | F5550_733(Middle Ridge-Yarranlea) 110 kV | Loading (A) | 62.1587 | 66.7224 | 48.5745 | 63.1083 | 67.5165 | 49.0468 | 63.1014 | 67.5094 | 49.0467 | 62.5598 | 67.5791 | 48.9486 | 63.723 | 68.6416 | 49.5293
SW | 60306804 | F5550 | 733 MR - Yarranlea | F5550_733(Middle Ridge-Yarranlea) 110 kV | Loading (MVA) | 12.2119 | 13.1698 | 9.576 | 12.3938 | 13.3245 | 9.6678 | 12.3935 | 13.3241 | 9.6678 | 12.3738 | 13.3278 | 9.6637 | 12.5823 | 13.5184 | 9.7907
SW | 60306804 | F5550 | 733 MR - Yarranlea | F5550_733(Middle Ridge-Yarranlea) 110 kV | Loading (MW) | 11.3308 | 12.1074 | 9.0195 | 11.4883 | 12.2585 | 9.1044 | 11.4882 | 12.2584 | 9.1044 | 11.4822 | 12.2596 | 9.1033 | 11.6402 | 12.4175 | 9.2147
SW | 60306804 | F5550 | 733 MR - Yarranlea | F5550_733(Middle Ridge-Yarranlea) 110 kV | Power Factor | 0.92785 | 0.91933 | 0.94188 | 0.92693 | 0.92 | 0.94172 | 0.92695 | 0.92002 | 0.94172 | 0.92794 | 0.91985 | 0.94201 | 0.92513 | 0.91857 | 0.94117
SW | 60306804 | F5550 | 733 MR - Yarranlea | F5550_733(Middle Ridge-Yarranlea) 110 kV | Rating (A) | 287 | 286 | 247 | 287 | 286 | 247 | 287 | 286 | 247 | 287 | 286 | 247 | 287 | 286 | 247
SW | 60306804 | F5550 | 733 MR - Yarranlea | F5550_733(Middle Ridge-Yarranlea) 110 kV | Time | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00
SW | 60306804 | F5550 | 733 MR - Yarranlea | F5550_733(Middle Ridge-Yarranlea) 110 kV | Voltage at Constrained Conductor | 113.428 | 113.9585 | 113.8193 | 113.3857 | 113.9407 | 113.804 | 113.395 | 113.9494 | 113.8042 | 114.1947 | 113.8637 | 113.984 | 113.9993 | 113.7042 | 114.1272
SW | 60306805 | F5565 | 736 MR - Warwick | F5565_736(Middle Ridge-Warwick) 110 kV | % of Rated A | 16.5544 | 18.2924 | 13.9719 | 16.535 | 18.2785 | 13.9825 | 16.4739 | 18.2027 | 13.9228 | 16.4148 | 18.1589 | 13.9501 | 16.5841 | 18.3566 | 14.0387
SW | 60306805 | F5565 | 736 MR - Warwick | F5565_736(Middle Ridge-Warwick) 110 kV | Limiting Line Name | TR_LINE 141691_1 | TR_LINE 141754_1 | TR_LINE 141691_1 | TR_LINE 141691_1 | TR_LINE 141754_1 | TR_LINE 141691_1 | TR_LINE 141691_1 | TR_LINE 141754_1 | TR_LINE 141691_1 | TR_LINE 141691_1 | TR_LINE 141754_1 | TR_LINE 141691_1 | TR_LINE 141754_1 | TR_LINE 141754_1 | TR_LINE 141691_1
SW | 60306805 | F5565 | 736 MR - Warwick | F5565_736(Middle Ridge-Warwick) 110 kV | Loading (A) | 126.3103 | 142.496 | 95.7073 | 126.1618 | 142.3877 | 95.7802 | 125.6962 | 141.797 | 95.371 | 125.245 | 141.4563 | 95.5584 | 126.5359 | 142.9964 | 96.1653
SW | 60306805 | F5565 | 736 MR - Warwick | F5565_736(Middle Ridge-Warwick) 110 kV | Loading (MVA) | 25.3443 | 28.0851 | 19.1866 | 25.3153 | 28.0679 | 19.202 | 25.2243 | 27.9592 | 19.1199 | 25.3006 | 28.0721 | 19.1863 | 25.2334 | 28.3321 | 19.3361
SW | 60306805 | F5565 | 736 MR - Warwick | F5565_736(Middle Ridge-Warwick) 110 kV | Loading (MW) | 25.3294 | 27.9668 | 18.5859 | 25.2994 | 27.9513 | 18.6042 | 25.206 | 27.8482 | 18.5305 | 25.2857 | 27.9689 | 18.5983 | 25.2176 | 28.2123 | 18.7693
SW | 60306805 | F5565 | 736 MR - Warwick | F5565_736(Middle Ridge-Warwick) 110 kV | Power Factor | 0.99941 | 0.99579 | 0.96869 | 0.99937 | 0.99585 | 0.96887 | 0.99927 | 0.99603 | 0.96917 | 0.99941 | 0.99632 | 0.96935 | 0.99937 | 0.99577 | 0.97069
SW | 60306805 | F5565 | 736 MR - Warwick | F5565_736(Middle Ridge-Warwick) 110 kV | Rating (A) | 763 | 779 | 685 | 763 | 779 | 685 | 763 | 779 | 685 | 763 | 779 | 685 | 763 | 779 | 685
SW | 60306805 | F5565 | 736 MR - Warwick | F5565_736(Middle Ridge-Warwick) 110 kV | Time | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00
SW | 60306805 | F5565 | 736 MR - Warwick | F5565_736(Middle Ridge-Warwick) 110 kV | Voltage at Constrained Conductor | 115.846 | 113.7921 | 115.7423 | 115.8497 | 113.8091 | 115.7474 | 115.861 | 113.8407 | 115.747 | 116.63 | 114.5756 | 115.9209 | 115.1336 | 114.3914 | 116.0889
SW | 60306930 | F3867 | PAMPAS | F3867_Pampas 33 kV | % of Rated A | 63.8009 | 72.2407 | 56.525 | 62.6036 | 68.6404 | 55.4769 | 62.5967 | 68.6338 | 55.4767 | 62.0874 | 69.8257 | 55.3652 | 64.4514 | 71.3837 | 56.3602
SW | 60306930 | F3867 | PAMPAS | F3867_Pampas 33 kV | Limiting Line Name | TR_CABLE 106_1 | TR_CABLE 106_1 | TR_LINE 23248_1 | TR_CABLE 106_1 | TR_CABLE 106_1 | TR_LINE 23248_1 | TR_CABLE 106_1 | TR_CABLE 106_1 | TR_LINE 23248_1 | TR_CABLE 106_1 | TR_CABLE 106_1 | TR_LINE 23248_1 | TR_CABLE 106_1 | TR_CABLE 106_1 | TR_LINE 23248_1
SW | 60306930 | F3867 | PAMPAS | F3867_Pampas 33 kV | Loading (A) | 191.4027 | 216.7221 | 166.1833 | 187.8109 | 205.9211 | 163.1017 | 187.7902 | 205.9015 | 163.1012 | 186.2622 | 209.4772 | 162.7734 | 193.3544 | 214.1512 | 165.6988
SW | 60306930 | F3867 | PAMPAS | F3867_Pampas 33 kV | Loading (MVA) | 10.3883 | 11.5249 | 9.1854 | 10.1979 | 11.3121 | 9.0219 | 10.1978 | 11.312 | 9.0219 | 10.2006 | 11.3159 | 9.0207 | 10.3888 | 11.5248 | 9.1835
SW | 60306930 | F3867 | PAMPAS | F3867_Pampas 33 kV | Loading (MW) | 9.4428 | 10.4804 | 8.3326 | 9.2703 | 10.2877 | 8.1846 | 9.2703 | 10.2877 | 8.1845 | 9.2715 | 10.289 | 8.1842 | 9.4422 | 10.4809 | 8.3321
SW | 60306930 | F3867 | PAMPAS | F3867_Pampas 33 kV | Power Factor | 0.90898 | 0.90938 | 0.90715 | 0.90905 | 0.90945 | 0.90718 | 0.90905 | 0.90945 | 0.90718 | 0.90891 | 0.90925 | 0.90727 | 0.90888 | 0.90942 | 0.90728
SW | 60306930 | F3867 | PAMPAS | F3867_Pampas 33 kV | Rating (A) | 300 | 300 | 294 | 300 | 300 | 294 | 300 | 300 | 294 | 300 | 300 | 294 | 300 | 300 | 294
SW | 60306930 | F3867 | PAMPAS | F3867_Pampas 33 kV | Time | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00
SW | 60306930 | F3867 | PAMPAS | F3867_Pampas 33 kV | Voltage at Constrained Conductor | 31.3356 | 30.7024 | 31.9118 | 31.3493 | 31.7163 | 31.936 | 31.3525 | 31.719 | 31.9361 | 31.6184 | 31.1882 | 31.9959 | 31.0208 | 31.0707 | 31.9985
SW | 60320796 | F5540 | 7244 TANGKAM - DALBY | F5540_7244 Tangkam-Dalby 110 kV | % of Rated A | 29.0997 | 28.6414 | 22.3255 | 28.7804 | 28.3292 | 22.1703 | 28.5236 | 28.0843 | 22.0361 | 28.463 | 28.0949 | 22.0408 | 28.8177 | 28.4541 | 22.1927
SW | 60320796 | F5540 | 7244 TANGKAM - DALBY | F5540_7244 Tangkam-Dalby 110 kV | Limiting Line Name | TR_LINE 140812_1 | TR_LINE 140812_1 | TR_LINE 140812_1 | TR_LINE 140812_1 | TR_LINE 140812_1 | TR_LINE 140812_1 | TR_LINE 140812_1 | TR_LINE 140812_1 | TR_LINE 140812_1 | TR_LINE 140812_1 | TR_LINE 140812_1 | TR_LINE 140812_1 | TR_LINE 140812_1 | TR_LINE 140812_1 | TR_LINE 140812_1
SW | 60320796 | F5540 | 7244 TANGKAM - DALBY | F5540_7244 Tangkam-Dalby 110 kV | Loading (A) | 76.8182 | 77.0403 | 52.4649 | 75.9752 | 76.2006 | 52.1001 | 75.2973 | 75.5418 | 51.7849 | 75.1423 | 75.5703 | 51.7958 | 76.0736 | 76.5364 | 52.1528
SW | 60320796 | F5540 | 7244 TANGKAM - DALBY | F5540_7244 Tangkam-Dalby 110 kV | Loading (MVA) | 14.8587 | 14.9448 | 10.2073 | 14.7022 | 14.7892 | 10.1383 | 14.5762 | 14.6664 | 10.0784 | 14.5898 | 14.6671 | 10.0786 | 14.7572 | 14.8424 | 10.1438
SW | 60320796 | F5540 | 7244 TANGKAM - DALBY | F5540_7244 Tangkam-Dalby 110 kV | Loading (MW) | 14.4363 | 14.5204 | 10.0069 | 14.2937 | 14.379 | 9.9416 | 14.1779 | 14.2661 | 9.8848 | 14.182 | 14.2662 | 9.8849 | 14.3402 | 14.4335 | 9.9461
SW | 60320796 | F5540 | 7244 TANGKAM - DALBY | F5540_7244 Tangkam-Dalby 110 kV | Power Factor | 0.97157 | 0.9716 | 0.98037 | 0.97221 | 0.97226 | 0.9806 | 0.97267 | 0.97271 | 0.98079 | 0.97205 | 0.97267 | 0.98077 | 0.97174 | 0.97245 | 0.98051
SW | 60320796 | F5540 | 7244 TANGKAM - DALBY | F5540_7244 Tangkam-Dalby 110 kV | Rating (A) | 264 | 269 | 235 | 264 | 269 | 235 | 264 | 269 | 235 | 264 | 269 | 235 | 264 | 269 | 235
SW | 60320796 | F5540 | 7244 TANGKAM - DALBY | F5540_7244 Tangkam-Dalby 110 kV | Time | 16:30 | 17:30 | 8:00 | 16:30 | 17:30 | 8:00 | 16:30 | 17:30 | 8:00 | 16:30 | 17:30 | 8:00 | 16:30 | 17:30 | 8:00
SW | 60320796 | F5540 | 7244 TANGKAM - DALBY | F5540_7244 Tangkam-Dalby 110 kV | Voltage at Constrained Conductor | 111.6753 | 111.9986 | 112.3259 | 111.7248 | 112.0538 | 112.3479 | 111.7649 | 112.0923 | 112.3641 | 112.0994 | 112.0554 | 112.3433 | 111.9982 | 111.963 | 112.2951
SW | 60320797 | F5545 | 7245 TANGKAM - DALBY | F5545_7245 Tangkam-Dalby 110 kV | % of Rated A | 63.1757 | 44.7029 | 31.3003 | 62.4825 | 44.2157 | 31.0826 | 61.9249 | 43.8334 | 30.8945 | 61.7917 | 43.8499 | 30.901 | 62.5624 | 44.4111 | 31.1139
SW | 60320797 | F5545 | 7245 TANGKAM - DALBY | F5545_7245 Tangkam-Dalby 110 kV | Limiting Line Name | TR_LINE 215532_1 | TR_LINE 215532_1 | TR_LINE 215532_1 | TR_LINE 215532_1 | TR_LINE 215532_1 | TR_LINE 215532_1 | TR_LINE 215532_1 | TR_LINE 215532_1 | TR_LINE 215532_1 | TR_LINE 215532_1 | TR_LINE 215532_1 | TR_LINE 215532_1 | TR_LINE 215532_1 | TR_LINE 215532_1 | TR_LINE 215532_1
SW | 60320797 | F5545 | 7245 TANGKAM - DALBY | F5545_7245 Tangkam-Dalby 110 kV | Loading (A) | 80.2144 | 80.4464 | 54.7755 | 79.3343 | 79.5697 | 54.3945 | 78.6263 | 78.8817 | 54.0653 | 78.4569 | 78.9114 | 54.0767 | 79.4356 | 79.9216 | 54.4494
SW | 60320797 | F5545 | 7245 TANGKAM - DALBY | F5545_7245 Tangkam-Dalby 110 kV | Loading (MVA) | 15.5283 | 15.6183 | 10.6611 | 15.3646 | 15.4555 | 10.589 | 15.2328 | 15.327 | 10.5264 | 15.2465 | 15.3278 | 10.5266 | 15.4219 | 15.5114 | 10.5947
SW | 60320797 | F5545 | 7245 TANGKAM - DALBY | F5545_7245 Tangkam-Dalby 110 kV | Loading (MW) | 15.0389 | 15.1265 | 10.4313 | 14.8911 | 14.98 | 10.3635 | 14.771 | 14.8629 | 10.3045 | 14.7754 | 14.863 | 10.3046 | 14.939 | 15.037 | 10.3681
SW | 60320797 | F5545 | 7245 TANGKAM - DALBY | F5545_7245 Tangkam-Dalby 110 kV | Power Factor | 0.96848 | 0.96851 | 0.97845 | 0.96918 | 0.96923 | 0.9787 | 0.96968 | 0.96972 | 0.97892 | 0.9691 | 0.96968 | 0.9789 | 0.96869 | 0.96942 | 0.97861
SW | 60320797 | F5545 | 7245 TANGKAM - DALBY | F5545_7245 Tangkam-Dalby 110 kV | Rating (A) | 127 | 180 | 175 | 127 | 180 | 175 | 127 | 180 | 175 | 127 | 180 | 175 | 127 | 180 | 175
SW | 60320797 | F5545 | 7245 TANGKAM - DALBY | F5545_7245 Tangkam-Dalby 110 kV | Time | 16:30 | 17:30 | 8:00 | 16:30 | 17:30 | 8:00 | 16:30 | 17:30 | 8:00 | 16:30 | 17:30 | 8:00 | 16:30 | 17:30 | 8:00
SW | 60320797 | F5545 | 7245 TANGKAM - DALBY | F5545_7245 Tangkam-Dalby 110 kV | Voltage at Constrained Conductor | 111.7666 | 112.0901 | 112.371 | 111.8148 | 112.144 | 112.3927 | 111.8538 | 112.1814 | 112.4086 | 112.196 | 112.1446 | 112.3878 | 112.0885 | 112.0535 | 112.34
SW | 60322637 | F3253 | JELLICOE STREET | F3253_Jellicoe Street 33 kV | % of Rated A | 0.9623 | 0.68279 | 0.59261 | 0.96279 | 0.68107 | 0.59276 | 0.96287 | 0.68113 | 0.59277 | 0.95709 | 0.679 | 0.59067 | 0.9561 | 0.67284 | 0.58801
SW | 60322637 | F3253 | JELLICOE STREET | F3253_Jellicoe Street 33 kV | Limiting Line Name | TR_LINE 23977_2 | TR_LINE 23977_2 | TR_LINE 23977_2 | TR_LINE 23977_2 | TR_LINE 23977_2 | TR_LINE 23977_2 | TR_LINE 23977_2 | TR_LINE 23977_2 | TR_LINE 23977_2 | TR_LINE 23977_2 | TR_LINE 23977_2 | TR_LINE 23977_2 | TR_LINE 23977_2 | TR_LINE 23977_2 | TR_LINE 23977_2
SW | 60322637 | F3253 | JELLICOE STREET | F3253_Jellicoe Street 33 kV | Loading (A) | 2.1267 | 2.1303 | 2.1393 | 2.1278 | 2.125 | 2.1399 | 2.1279 | 2.1251 | 2.1399 | 2.1152 | 2.1185 | 2.1323 | 2.113 | 2.0993 | 2.1227
SW | 60322637 | F3253 | JELLICOE STREET | F3253_Jellicoe Street 33 kV | Loading (MVA) | 0.12425 | 0.12467 | 0.12573 | 0.12437 | 0.12405 | 0.12579 | 0.12439 | 0.12407 | 0.1258 | 0.12291 | 0.12329 | 0.12491 | 0.12265 | 0.12107 | 0.12378
SW | 60322637 | F3253 | JELLICOE STREET | F3253_Jellicoe Street 33 kV | Loading (MW) | 0.002201 | 0.0022085 | 0.0022272 | 0.0022032 | 0.0021974 | 0.0022283 | 0.0022036 | 0.0021977 | 0.0022284 | 0.0021772 | 0.002184 | 0.0022127 | 0.0021727 | 0.0021446 | 0.0021928
SW | 60322637 | F3253 | JELLICOE STREET | F3253_Jellicoe Street 33 kV | Power Factor | 0.017714 | 0.017714 | 0.017714 | 0.017714 | 0.017714 | 0.017714 | 0.017714 | 0.017714 | 0.017714 | 0.017714 | 0.017714 | 0.017714 | 0.017714 | 0.017714 | 0.017714
SW | 60322637 | F3253 | JELLICOE STREET | F3253_Jellicoe Street 33 kV | Rating (A) | 221 | 312 | 361 | 221 | 312 | 361 | 221 | 312 | 361 | 221 | 312 | 361 | 221 | 312 | 361
SW | 60322637 | F3253 | JELLICOE STREET | F3253_Jellicoe Street 33 kV | Time | 13:30 | 21:30 | 3:30 | 13:30 | 21:00 | 3:30 | 13:30 | 21:00 | 3:30 | 12:30 | 21:30 | 3:30 | 9:00 | 21:30 | 2:30
SW | 60322637 | F3253 | JELLICOE STREET | F3253_Jellicoe Street 33 kV | Voltage at Constrained Conductor | 33.7311 | 33.7882 | 33.9316 | 33.748 | 33.7035 | 33.94 | 33.7508 | 33.706 | 33.9408 | 33.5484 | 33.6008 | 33.8204 | 33.5137 | 33.296 | 33.6679
SW | 60327274 | F4132 | SHIRLEY ROAD FEEDER | F4132_Shirley Road 33 kV | % of Rated A | 62.3293 | 50.9069 | 23.2819 | 61.966 | 50.5891 | 23.1465 | 61.5984 | 50.3132 | 23.0311 | 62.0681 | 51.0751 | 23.2828 | 66.2182 | 54.8072 | 28.3595
SW | 60327274 | F4132 | SHIRLEY ROAD FEEDER | F4132_Shirley Road 33 kV | Limiting Line Name | TR_LINE 108727_1 | TR_CABLE 239_1 | TR_CABLE 239_1 | TR_LINE 108727_1 | TR_CABLE 239_1 | TR_CABLE 239_1 | TR_LINE 108727_1 | TR_CABLE 239_1 | TR_CABLE 239_1 | TR_LINE 108727_1 | TR_CABLE 239_1 | TR_CABLE 239_1 | TR_LINE 108727_1 | TR_CABLE 239_1 | TR_CABLE 239_1
SW | 60327274 | F4132 | SHIRLEY ROAD FEEDER | F4132_Shirley Road 33 kV | Loading (A) | 261.7829 | 343.6215 | 157.1529 | 260.2572 | 341.4761 | 156.2388 | 258.7133 | 339.6142 | 155.4598 | 260.6859 | 344.7572 | 157.1589 | 278.1164 | 369.9486 | 191.4267
SW | 60327274 | F4132 | SHIRLEY ROAD FEEDER | F4132_Shirley Road 33 kV | Loading (MVA) | 14.9349 | 20.1053 | 9.1726 | 14.8569 | 19.992 | 9.1218 | 14.7742 | 19.8866 | 9.0768 | 14.9347 | 20.1082 | 9.1727 | 15.7377 | 21.4118 | 11.2772
SW | 60327274 | F4132 | SHIRLEY ROAD FEEDER | F4132_Shirley Road 33 kV | Loading (MW) | 14.46 | 19.1295 | 8.9493 | 14.384 | 19.0239 | 8.8987 | 14.309 | 18.9278 | 8.8574 | 14.46 | 19.131 | 8.9493 | 14.8934 | 19.8385 | 10.7685
SW | 60327274 | F4132 | SHIRLEY ROAD FEEDER | F4132_Shirley Road 33 kV | Power Factor | 0.9682 | 0.95146 | 0.97566 | 0.96817 | 0.95158 | 0.97554 | 0.96851 | 0.95178 | 0.97583 | 0.96822 | 0.9514 | 0.97565 | 0.94635 | 0.92652 | 0.9549
SW | 60327274 | F4132 | SHIRLEY ROAD FEEDER | F4132_Shirley Road 33 kV | Rating (A) | 420 | 675 | 675 | 420 | 675 | 675 | 420 | 675 | 675 | 420 | 675 | 675 | 420 | 675 | 675
SW | 60327274 | F4132 | SHIRLEY ROAD FEEDER | F4132_Shirley Road 33 kV | Time | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00
SW | 60327274 | F4132 | SHIRLEY ROAD FEEDER | F4132_Shirley Road 33 kV | Voltage at Constrained Conductor | 32.9382 | 33.7808 | 33.6986 | 32.9582 | 33.8014 | 33.7079 | 32.9704 | 33.8077 | 33.7097 | 33.0764 | 33.6743 | 33.6973 | 32.6704 | 33.4157 | 34.0124
SW | 60330365 | 7235 | Bulli Creek - Waggamba 132 kV | 7235_Bulli Creek - Waggamba 132 kV | % of Rated A | 11.24 | 13.9029 | 12.46 | 11.2398 | 13.8985 | 12.46 | 11.8092 | 14.5643 | 12.9897 | 11.8132 | 14.5697 | 12.9901 | 11.8145 | 14.5711 | 12.9907
SW | 60330365 | 7235 | Bulli Creek - Waggamba 132 kV | 7235_Bulli Creek - Waggamba 132 kV | Limiting Line Name | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1
SW | 60330365 | 7235 | Bulli Creek - Waggamba 132 kV | 7235_Bulli Creek - Waggamba 132 kV | Loading (A) | 73.0599 | 91.6198 | 71.6453 | 73.059 | 91.5909 | 71.6448 | 76.7601 | 95.9789 | 74.691 | 76.7861 | 96.0146 | 74.6932 | 76.794 | 96.0233 | 74.6963
SW | 60330365 | 7235 | Bulli Creek - Waggamba 132 kV | 7235_Bulli Creek - Waggamba 132 kV | Loading (MVA) | 17.6411 | 21.8049 | 17.3253 | 17.6411 | 21.8058 | 17.3253 | 18.5291 | 22.8412 | 18.0574 | 18.5276 | 22.8403 | 18.0573 | 18.5271 | 22.8401 | 18.0571
SW | 60330365 | 7235 | Bulli Creek - Waggamba 132 kV | 7235_Bulli Creek - Waggamba 132 kV | Loading (MW) | 16.964 | 21.4805 | 16.5932 | 16.964 | 21.4803 | 16.5932 | 17.9456 | 22.5787 | 17.4076 | 17.9457 | 22.579 | 17.4076 | 17.9457 | 22.579 | 17.4076
SW | 60330365 | 7235 | Bulli Creek - Waggamba 132 kV | 7235_Bulli Creek - Waggamba 132 kV | Power Factor | 0.96162 | 0.98512 | 0.95775 | 0.96162 | 0.98508 | 0.95774 | 0.9685 | 0.98851 | 0.96401 | 0.96859 | 0.98856 | 0.96402 | 0.96862 | 0.98857 | 0.96403
SW | 60330365 | 7235 | Bulli Creek - Waggamba 132 kV | 7235_Bulli Creek - Waggamba 132 kV | Rating (A) | 650 | 659 | 575 | 650 | 659 | 575 | 650 | 659 | 575 | 650 | 659 | 575 | 650 | 659 | 575
SW | 60330365 | 7235 | Bulli Creek - Waggamba 132 kV | 7235_Bulli Creek - Waggamba 132 kV | Time | 16:30 | 19:00 | 22:30 | 16:30 | 19:00 | 22:30 | 16:30 | 19:00 | 22:30 | 16:30 | 19:00 | 22:30 | 16:30 | 19:00 | 22:30
SW | 60330365 | 7235 | Bulli Creek - Waggamba 132 kV | 7235_Bulli Creek - Waggamba 132 kV | Voltage at Constrained Conductor | 139.4072 | 137.4056 | 139.6152 | 139.4094 | 137.4543 | 139.6164 | 139.3668 | 137.3986 | 139.5812 | 139.3077 | 137.3425 | 139.5759 | 139.2897 | 137.3287 | 139.5685
SW | 60330908 | F7234 | 7234 MR - Torrington | 7234_Middle Ridge-Torrington 110 kV | % of Rated A | 24.498 | 22.2214 | 15.559 | 24.2557 | 22.0021 | 15.4065 | 24.2239 | 21.9687 | 15.3916 | 25.7163 | 23.2513 | 16.32 | 27.9523 | 25.0712 | 18.0227
SW | 60330908 | F7234 | 7234 MR - Torrington | 7234_Middle Ridge-Torrington 110 kV | Limiting Line Name | TR_LINE 27022_2 | TR_LINE 27022_2 | TR_LINE 27022_2 | TR_LINE 27022_2 | TR_LINE 27022_2 | TR_LINE 27022_2 | TR_LINE 27022_2 | TR_LINE 27022_2 | TR_LINE 27022_2 | TR_LINE 27022_2 | TR_LINE 27022_2 | TR_LINE 27022_2 | TR_LINE 27022_2 | TR_LINE 27022_2 | TR_LINE 27022_2
SW | 60330908 | F7234 | 7234 MR - Torrington | 7234_Middle Ridge-Torrington 110 kV | Loading (A) | 214.6276 | 213.7565 | 132.5358 | 212.5024 | 211.6441 | 131.2356 | 212.224 | 211.3236 | 131.1091 | 225.2939 | 223.6616 | 139.0078 | 244.8752 | 241.1561 | 153.4979
SW | 60330908 | F7234 | 7234 MR - Torrington | 7234_Middle Ridge-Torrington 110 kV | Loading (MVA) | 42.9214 | 43.0323 | 26.5044 | 42.4999 | 42.6149 | 26.2464 | 42.4479 | 42.5539 | 26.2213 | 45.3432 | 44.9888 | 27.8362 | 49.1919 | 48.431 | 30.7692
SW | 60330908 | F7234 | 7234 MR - Torrington | 7234_Middle Ridge-Torrington 110 kV | Loading (MW) | 40.7416 | 40.9416 | 25.8226 | 40.3674 | 40.5701 | 25.5815 | 40.3251 | 40.5209 | 25.5592 | 42.7565 | 42.5635 | 26.9978 | 45.7344 | 45.2235 | 29.553
SW | 60330908 | F7234 | 7234 MR - Torrington | 7234_Middle Ridge-Torrington 110 kV | Power Factor | 0.94922 | 0.95142 | 0.97428 | 0.94982 | 0.95202 | 0.97467 | 0.94999 | 0.95222 | 0.97475 | 0.94295 | 0.94609 | 0.96988 | 0.92971 | 0.93377 | 0.96047
SW | 60330908 | F7234 | 7234 MR - Torrington | 7234_Middle Ridge-Torrington 110 kV | Rating (A) | 878 | 964 | 854 | 878 | 964 | 854 | 878 | 964 | 854 | 878 | 964 | 854 | 878 | 964 | 854
SW | 60330908 | F7234 | 7234 MR - Torrington | 7234_Middle Ridge-Torrington 110 kV | Time | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00
SW | 60330908 | F7234 | 7234 MR - Torrington | 7234_Middle Ridge-Torrington 110 kV | Voltage at Constrained Conductor | 115.4589 | 116.2291 | 115.4579 | 115.4684 | 116.2506 | 115.4669 | 115.4784 | 116.2603 | 115.4676 | 116.1989 | 116.1321 | 115.614 | 115.9815 | 115.9483 | 115.7319
SW | 82639691 | 3900 | PERANGA | 3900_Peranga 33 kV | % of Rated A | 21.9343 | 29.299 | 22.6577 | 20.5646 | 27.4529 | 21.2411 | 20.3801 | 27.3077 | 21.061 | 20.7902 | 27.4594 | 21.2437 | 22.1853 | 28.9153 | 22.6636
SW | 82639691 | 3900 | PERANGA | 3900_Peranga 33 kV | Limiting Line Name | TR_CABLE 9120_1 | TR_CABLE 9120_1 | TR_CABLE 9120_1 | TR_CABLE 9120_1 | TR_CABLE 9120_1 | TR_CABLE 9120_1 | TR_CABLE 9120_1 | TR_CABLE 9120_1 | TR_CABLE 9120_1 | TR_CABLE 9120_1 | TR_CABLE 9120_1 | TR_CABLE 9120_1 | TR_CABLE 9120_1 | TR_CABLE 9120_1 | TR_CABLE 9120_1
SW | 82639691 | 3900 | PERANGA | 3900_Peranga 33 kV | Loading (A) | 21.9343 | 29.299 | 22.6577 | 20.5646 | 27.4529 | 21.2411 | 20.3801 | 27.3077 | 21.061 | 20.7902 | 27.4594 | 21.2437 | 22.1853 | 28.9153 | 22.6636
SW | 82639691 | 3900 | PERANGA | 3900_Peranga 33 kV | Loading (MVA) | 1.2892 | 1.7047 | 1.3274 | 1.2088 | 1.5975 | 1.2445 | 1.1979 | 1.5889 | 1.2339 | 1.2102 | 1.5976 | 1.2445 | 1.2907 | 1.7021 | 1.3274
SW | 82639691 | 3900 | PERANGA | 3900_Peranga 33 kV | Loading (MW) | 1.2528 | 1.6351 | 1.288 | 1.178 | 1.5368 | 1.211 | 1.1459 | 1.4952 | 1.178 | 1.1784 | 1.5368 | 1.211 | 1.2532 | 1.6342 | 1.288
SW | 82639691 | 3900 | PERANGA | 3900_Peranga 33 kV | Power Factor | 0.97176 | 0.95922 | 0.97031 | 0.97452 | 0.96199 | 0.97308 | 0.95662 | 0.94103 | 0.95476 | 0.97373 | 0.96197 | 0.97307 | 0.97093 | 0.96012 | 0.97029
SW | 82639691 | 3900 | PERANGA | 3900_Peranga 33 kV | Rating (A) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
SW | 82639691 | 3900 | PERANGA | 3900_Peranga 33 kV | Time | 16:30 | 18:00 | 6:30 | 16:30 | 18:00 | 6:30 | 16:30 | 18:00 | 6:30 | 16:30 | 18:00 | 6:30 | 16:30 | 18:00 | 6:30
SW | 82639691 | 3900 | PERANGA | 3900_Peranga 33 kV | Voltage at Constrained Conductor | 33.9335 | 33.5911 | 33.8239 | 33.9378 | 33.5973 | 33.8271 | 33.9358 | 33.5939 | 33.8238 | 33.6071 | 33.5902 | 33.8235 | 33.5895 | 33.9862 | 33.816
SW | 82640976 | EB10 | ACLAND | EB10_Acland 33 kV | % of Rated A | 12.3073 | 8.9193 | 11.0217 | 12.2122 | 8.9176 | 11.0207 | 12.3063 | 8.9184 | 11.0214 | 12.2128 | 9.0189 | 11.0222 | 12.2172 | 8.8979 | 11.0254
SW | 82640976 | EB10 | ACLAND | EB10_Acland 33 kV | Limiting Line Name | TR_CABLE 104_1 | TR_CABLE 104_1 | TR_CABLE 104_1 | TR_CABLE 104_1 | TR_CABLE 104_1 | TR_CABLE 104_1 | TR_CABLE 104_1 | TR_CABLE 104_1 | TR_CABLE 104_1 | TR_CABLE 104_1 | TR_CABLE 104_1 | TR_CABLE 104_1 | TR_CABLE 104_1 | TR_CABLE 104_1 | TR_CABLE 104_1
SW | 82640976 | EB10 | ACLAND | EB10_Acland 33 kV | Loading (A) | 11.4458 | 8.2949 | 10.2502 | 11.3573 | 8.2933 | 10.2492 | 11.4449 | 8.2941 | 10.2499 | 11.3579 | 8.3876 | 10.2507 | 11.362 | 8.275 | 10.2536
SW | 82640976 | EB10 | ACLAND | EB10_Acland 33 kV | Loading (MVA) | 0.66881 | 0.48738 | 0.60007 | 0.66797 | 0.48737 | 0.60006 | 0.66881 | 0.48737 | 0.60007 | 0.66798 | 0.48809 | 0.60007 | 0.66801 | 0.48722 | 0.6001
SW | 82640976 | EB10 | ACLAND | EB10_Acland 33 kV | Loading (MW) | 0.56125 | 0.41655 | 0.50685 | 0.56101 | 0.41655 | 0.50684 | 0.56124 | 0.41655 | 0.50685 | 0.56101 | 0.41669 | 0.50685 | 0.56103 | 0.41652 | 0.50685
SW | 82640976 | EB10 | ACLAND | EB10_Acland 33 kV | Power Factor | 0.83917 | 0.85468 | 0.84464 | 0.83988 | 0.8547 | 0.84465 | 0.83918 | 0.85469 | 0.84465 | 0.83987 | 0.85373 | 0.84464 | 0.83984 | 0.85488 | 0.84461
SW | 82640976 | EB10 | ACLAND | EB10_Acland 33 kV | Rating (A) | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93
SW | 82640976 | EB10 | ACLAND | EB10_Acland 33 kV | Time | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30 | 12:00 | 17:00 | 8:30
SW | 82640976 | EB10 | ACLAND | EB10_Acland 33 kV | Voltage at Constrained Conductor | 33.7365 | 33.9228 | 33.7993 | 33.9563 | 33.9285 | 33.8021 | 33.7386 | 33.9257 | 33.8002 | 33.9548 | 33.5969 | 33.7981 | 33.9445 | 33.9938 | 33.7898
SW | 83921739 | 3153 | CECIL PLAINS ROAD | 3153_Cecil Plains Road 33 kV | % of Rated A | 66.2046 | 60.5841 | 60.4459 | 66.1891 | 60.5481 | 60.4286 | 66.1597 | 60.5183 | 60.4158 | 66.1814 | 60.5409 | 60.4283 | 66.227 | 60.6085 | 60.4608
SW | 83921739 | 3153 | CECIL PLAINS ROAD | 3153_Cecil Plains Road 33 kV | Limiting Line Name | TR_LINE 183124_2 | TR_CABLE 5205_1 | TR_CABLE 5205_1 | TR_LINE 183124_2 | TR_CABLE 5205_1 | TR_CABLE 5205_1 | TR_LINE 183124_2 | TR_CABLE 5205_1 | TR_CABLE 5205_1 | TR_LINE 183124_2 | TR_CABLE 5205_1 | TR_CABLE 5205_1 | TR_LINE 183124_2 | TR_CABLE 5205_1 | TR_CABLE 5205_1
SW | 83921739 | 3153 | CECIL PLAINS ROAD | 3153_Cecil Plains Road 33 kV | Loading (A) | 61.5696 | 60.5841 | 60.4459 | 61.5552 | 60.5481 | 60.4286 | 61.5278 | 60.5183 | 60.4158 | 61.548 | 60.5409 | 60.4284 | 61.5905 | 60.6085 | 60.4608
SW | 83921739 | 3153 | CECIL PLAINS ROAD | 3153_Cecil Plains Road 33 kV | Loading (MVA) | 3.5645 | 3.4862 | 3.4983 | 3.5709 | 3.486 | 3.4982 | 3.5642 | 3.4859 | 3.4982 | 3.5708 | 3.486 | 3.4982 | 3.5716 | 3.4863 | 3.4984
SW | 83921739 | 3153 | CECIL PLAINS ROAD | 3153_Cecil Plains Road 33 kV | Loading (MW) | 3.3549 | 3.3017 | 3.3023 | 3.3604 | 3.3017 | 3.3023 | 3.3549 | 3.3017 | 3.3023 | 3.3604 | 3.3017 | 3.3023 | 3.3626 | 3.3018 | 3.3023
SW | 83921739 | 3153 | CECIL PLAINS ROAD | 3153_Cecil Plains Road 33 kV | Power Factor | 0.94121 | 0.94709 | 0.94398 | 0.94107 | 0.94712 | 0.944 | 0.94125 | 0.94715 | 0.94401 | 0.94107 | 0.94713 | 0.944 | 0.94148 | 0.94707 | 0.94396
SW | 83921739 | 3153 | CECIL PLAINS ROAD | 3153_Cecil Plains Road 33 kV | Rating (A) | 93 | 100 | 100 | 93 | 100 | 100 | 93 | 100 | 100 | 93 | 100 | 100 | 93 | 100 | 100
SW | 83921739 | 3153 | CECIL PLAINS ROAD | 3153_Cecil Plains Road 33 kV | Time | 12:30 | 18:00 | 8:00 | 12:00 | 18:00 | 8:00 | 12:30 | 18:00 | 8:00 | 12:00 | 18:00 | 8:00 | 11:30 | 18:00 | 8:00
SW | 83921739 | 3153 | CECIL PLAINS ROAD | 3153_Cecil Plains Road 33 kV | Voltage at Constrained Conductor | 33.4246 | 33.2226 | 33.4141 | 33.4925 | 33.2407 | 33.4229 | 33.4453 | 33.2558 | 33.4293 | 33.496 | 33.2444 | 33.423 | 33.4801 | 33.2103 | 33.4066
SW | 83921742 | 3154 | CENTRAL DALBY 1 | 3154_Central Dalby 1 33 kV | % of Rated A | 33.5528 | 34.1485 | 23.375 | 33.1159 | 33.7041 | 23.1027 | 32.8337 | 33.426 | 22.934 | 33.2732 | 33.4383 | 22.8042 | 33.5912 | 33.2744 | 22.9914
SW | 83921742 | 3154 | CENTRAL DALBY 1 | 3154_Central Dalby 1 33 kV | Limiting Line Name | TR_CABLE 4402_1 | TR_CABLE 4402_1 | TR_LINE 121841_1 | TR_CABLE 4402_1 | TR_CABLE 4402_1 | TR_LINE 121841_1 | TR_CABLE 4402_1 | TR_CABLE 4402_1 | TR_LINE 121841_1 | TR_CABLE 4402_1 | TR_CABLE 4402_1 | TR_LINE 121841_1 | TR_CABLE 4402_1 | TR_CABLE 4402_1 | TR_LINE 121841_1
SW | 83921742 | 3154 | CENTRAL DALBY 1 | 3154_Central Dalby 1 33 kV | Loading (A) | 150.9878 | 153.6683 | 95.8372 | 149.0218 | 151.6684 | 94.7207 | 147.7517 | 150.4168 | 94.0291 | 149.7293 | 150.4724 | 93.497 | 151.1604 | 149.7349 | 94.2647
SW | 83921742 | 3154 | CENTRAL DALBY 1 | 3154_Central Dalby 1 33 kV | Loading (MVA) | 8.6752 | 8.7184 | 5.519 | 8.5694 | 8.6127 | 5.4571 | 8.5016 | 8.5467 | 5.4189 | 8.5088 | 8.5468 | 5.419 | 8.5794 | 8.5077 | 5.4324
SW | 83921742 | 3154 | CENTRAL DALBY 1 | 3154_Central Dalby 1 33 kV | Loading (MW) | 8.4102 | 8.4493 | 5.4044 | 8.3101 | 8.3495 | 5.3446 | 8.2456 | 8.2869 | 5.3077 | 8.2478 | 8.2869 | 5.3077 | 8.3176 | 8.2451 | 5.3205
SW | 83921742 | 3154 | CENTRAL DALBY 1 | 3154_Central Dalby 1 33 kV | Power Factor | 0.96945 | 0.96913 | 0.97922 | 0.96974 | 0.96944 | 0.97939 | 0.96989 | 0.9696 | 0.97948 | 0.96933 | 0.96959 | 0.97947 | 0.96949 | 0.96913 | 0.9794
SW | 83921742 | 3154 | CENTRAL DALBY 1 | 3154_Central Dalby 1 33 kV | Rating (A) | 450 | 450 | 410 | 450 | 450 | 410 | 450 | 450 | 410 | 450 | 450 | 410 | 450 | 450 | 410
SW | 83921742 | 3154 | CENTRAL DALBY 1 | 3154_Central Dalby 1 33 kV | Time | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00 | 16:30 | 17:00 | 22:30
SW | 83921742 | 3154 | CENTRAL DALBY 1 | 3154_Central Dalby 1 33 kV | Voltage at Constrained Conductor | 33.1724 | 32.7561 | 33.2483 | 33.2002 | 32.7855 | 33.2627 | 33.2206 | 32.805 | 33.2725 | 32.8097 | 32.7935 | 33.4626 | 32.7685 | 32.8041 | 33.2723
SW | 84000793 | 3178 | WILKIE CREEK | 3178_Wilkie Creek 33 kV | % of Rated A | 4.1809 | 4.1588 | 4.1834 | 4.1818 | 4.1493 | 4.1839 | 4.1829 | 4.1513 | 4.1846 | 4.1821 | 4.1614 | 4.1842 | 4.1865 | 4.1574 | 4.1827
SW | 84000793 | 3178 | WILKIE CREEK | 3178_Wilkie Creek 33 kV | Limiting Line Name | TR_CABLE 3771_1 | TR_CABLE 3771_1 | TR_CABLE 3771_1 | TR_CABLE 3771_1 | TR_CABLE 3771_1 | TR_CABLE 3771_1 | TR_CABLE 3771_1 | TR_CABLE 3771_1 | TR_CABLE 3771_1 | TR_CABLE 3771_1 | TR_CABLE 3771_1 | TR_CABLE 3771_1 | TR_CABLE 3771_1 | TR_CABLE 3771_1 | TR_CABLE 3771_1
SW | 84000793 | 3178 | WILKIE CREEK | 3178_Wilkie Creek 33 kV | Loading (A) | 3.8883 | 3.8677 | 3.8906 | 3.8891 | 3.8588 | 3.8911 | 3.8901 | 3.8608 | 3.8917 | 3.8893 | 3.8701 | 3.8913 | 3.8934 | 3.8664 | 3.8899
SW | 84000793 | 3178 | WILKIE CREEK | 3178_Wilkie Creek 33 kV | Loading (MVA) | 0.22486 | 0.22392 | 0.22458 | 0.22496 | 0.22245 | 0.22463 | 0.22507 | 0.22267 | 0.22471 | 0.22498 | 0.22338 | 0.22466 | 0.22538 | 0.22377 | 0.2245
SW | 84000793 | 3178 | WILKIE CREEK | 3178_Wilkie Creek 33 kV | Loading (MW) | 0.0084527 | 0.013528 | 0.0065617 | 0.0084534 | 0.011818 | 0.006562 | 0.0084542 | 0.01182 | 0.0065626 | 0.0084536 | 0.010533 | 0.0065622 | 0.0082085 | 0.013527 | 0.0065611
SW | 84000793 | 3178 | WILKIE CREEK | 3178_Wilkie Creek 33 kV | Power Factor | 0.03759 | 0.060415 | 0.029218 | 0.037578 | 0.053129 | 0.029213 | 0.037562 | 0.053083 | 0.029205 | 0.037574 | 0.047153 | 0.02921 | 0.036421 | 0.060449 | 0.029226
SW | 84000793 | 3178 | WILKIE CREEK | 3178_Wilkie Creek 33 kV | Rating (A) | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93
SW | 84000793 | 3178 | WILKIE CREEK | 3178_Wilkie Creek 33 kV | Time | 10:00 | 20:30 | 4:00 | 10:00 | 17:30 | 4:00 | 10:00 | 17:30 | 4:00 | 10:00 | 17:00 | 4:00 | 12:30 | 20:30 | 4:00
SW | 84000793 | 3178 | WILKIE CREEK | 3178_Wilkie Creek 33 kV | Voltage at Constrained Conductor | 33.389 | 33.425 | 33.3262 | 33.3957 | 33.2823 | 33.3302 | 33.4043 | 33.2986 | 33.3358 | 33.3978 | 33.3242 | 33.3321 | 33.4217 | 33.4142 | 33.3204
SW | 84109456 | 7314 | 7314 DALBY EAST | 7314_Dalby East 110 kV | % of Rated A | 4.5126 | 4.287 | 4.8758 | 4.5137 | 4.2848 | 4.8764 | 4.511 | 4.2853 | 4.8834 | 4.5255 | 4.2869 | 4.8827 | 4.5205 | 4.2884 | 4.8749
SW | 84109456 | 7314 | 7314 DALBY EAST | 7314_Dalby East 110 kV | Limiting Line Name | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1
SW | 84109456 | 7314 | 7314 DALBY EAST | 7314_Dalby East 110 kV | Loading (A) | 12.5 | 12.6468 | 12.8234 | 12.503 | 12.6401 | 12.825 | 12.4953 | 12.6416 | 12.8433 | 12.5355 | 12.6463 | 12.8415 | 12.5218 | 12.6507 | 12.8209
SW | 84109456 | 7314 | 7314 DALBY EAST | 7314_Dalby East 110 kV | Loading (MVA) | 2.4286 | 2.4647 | 2.5252 | 2.4298 | 2.457 | 2.5259 | 2.4328 | 2.4579 | 2.5297 | 2.4339 | 2.4606 | 2.5291 | 2.4289 | 2.4608 | 2.5243
SW | 84109456 | 7314 | 7314 DALBY EAST | 7314_Dalby East 110 kV | Loading (MW) | 0.65722 | 0.86288 | 0.50466 | 0.65724 | 0.91076 | 0.50466 | 0.69194 | 0.86512 | 0.48164 | 0.82565 | 0.89166 | 0.48164 | 0.86884 | 0.9268 | 0.50465
SW | 84109456 | 7314 | 7314 DALBY EAST | 7314_Dalby East 110 kV | Power Factor | 0.27061 | 0.3501 | 0.19985 | 0.27049 | 0.37068 | 0.1998 | 0.28443 | 0.35197 | 0.19039 | 0.33923 | 0.36237 | 0.19044 | 0.35771 | 0.37662 | 0.19992
SW | 84109456 | 7314 | 7314 DALBY EAST | 7314_Dalby East 110 kV | Rating (A) | 277 | 295 | 263 | 277 | 295 | 263 | 277 | 295 | 263 | 277 | 295 | 263 | 277 | 295 | 263
SW | 84109456 | 7314 | 7314 DALBY EAST | 7314_Dalby East 110 kV | Time | 10:30 | 20:30 | 4:30 | 10:30 | 20:00 | 4:30 | 10:00 | 20:00 | 4:30 | 16:30 | 18:30 | 4:30 | 16:30 | 19:30 | 4:30
SW | 84109456 | 7314 | 7314 DALBY EAST | 7314_Dalby East 110 kV | Voltage at Constrained Conductor | 112.1747 | 112.5175 | 113.6942 | 112.1997 | 112.2259 | 113.7078 | 112.4066 | 112.2543 | 113.7185 | 112.0994 | 112.3367 | 113.7055 | 111.9905 | 112.3076 | 113.6736
SW | 84170804 | 3196 | TARA | 3196_Tara 33 kV | % of Rated A | 15.4996 | 13.671 | 11.185 | 15.495 | 13.6669 | 11.1839 | 14.799 | 13.0038 | 10.7789 | 14.7734 | 13.0066 | 10.8112 | 15.4679 | 13.6753 | 11.2007
SW | 84170804 | 3196 | TARA | 3196_Tara 33 kV | Limiting Line Name | TR_LINE 27355_1 | TR_LINE 24024_1 | TR_LINE 24024_1 | TR_LINE 27355_1 | TR_LINE 24024_1 | TR_LINE 24024_1 | TR_LINE 27355_1 | TR_LINE 24024_1 | TR_LINE 24024_1 | TR_LINE 27355_1 | TR_LINE 24024_1 | TR_LINE 24024_1 | TR_LINE 27355_1 | TR_LINE 24024_1 | TR_LINE 24024_1
SW | 84170804 | 3196 | TARA | 3196_Tara 33 kV | Loading (A) | 14.4146 | 15.8583 | 12.9746 | 14.4103 | 15.8537 | 12.9734 | 13.7631 | 15.0844 | 12.5035 | 13.7392 | 15.0876 | 12.541 | 14.3851 | 15.8633 | 12.9928
SW | 84170804 | 3196 | TARA | 3196_Tara 33 kV | Loading (MVA) | 0.82361 | 0.9107 | 0.74924 | 0.82376 | 0.91082 | 0.74936 | 0.78744 | 0.86743 | 0.72263 | 0.78874 | 0.86732 | 0.71813 | 0.82469 | 0.91057 | 0.74769
SW | 84170804 | 3196 | TARA | 3196_Tara 33 kV | Loading (MW) | 0.7847 | 0.88032 | 0.68456 | 0.7847 | 0.88032 | 0.68456 | 0.74092 | 0.82991 | 0.64923 | 0.74089 | 0.82991 | 0.64923 | 0.78466 | 0.88033 | 0.68457
SW | 84170804 | 3196 | TARA | 3196_Tara 33 kV | Power Factor | 0.95275 | 0.96665 | 0.91367 | 0.95258 | 0.96651 | 0.91353 | 0.94092 | 0.95674 | 0.89842 | 0.93934 | 0.95687 | 0.90405 | 0.95146 | 0.96679 | 0.91557
SW | 84170804 | 3196 | TARA | 3196_Tara 33 kV | Rating (A) | 93 | 116 | 116 | 93 | 116 | 116 | 93 | 116 | 116 | 93 | 116 | 116 | 93 | 116 | 116
SW | 84170804 | 3196 | TARA | 3196_Tara 33 kV | Time | 16:00 | 18:00 | 22:00 | 16:00 | 18:00 | 22:00 | 16:00 | 18:00 | 22:00 | 16:00 | 18:00 | 22:00 | 16:00 | 18:00 | 22:00
SW | 84170804 | 3196 | TARA | 3196_Tara 33 kV | Voltage at Constrained Conductor | 32.9882 | 33.1556 | 33.3401 | 33.0038 | 33.1698 | 33.3484 | 33.0326 | 33.2007 | 33.3677 | 33.1443 | 33.1894 | 33.0607 | 33.0991 | 33.1405 | 33.2247
SW | 84301618 | 3203 | MILES | 3203_Miles 33 kV | % of Rated A | 87.4762 | 92.334 | 66.5513 | 85.608 | 91.4966 | 65.1766 | 85.6081 | 91.4967 | 65.1767 | 85.6082 | 91.4968 | 65.1767 | 87.4763 | 92.3341 | 66.5513
SW | 84301618 | 3203 | MILES | 3203_Miles 33 kV | Limiting Line Name | TR_CABLE 8720_1 | TR_CABLE 8720_1 | TR_CABLE 8720_1 | TR_CABLE 8720_1 | TR_CABLE 8720_1 | TR_CABLE 8720_1 | TR_CABLE 8720_1 | TR_CABLE 8720_1 | TR_CABLE 8720_1 | TR_CABLE 8720_1 | TR_CABLE 8720_1 | TR_CABLE 8720_1 | TR_CABLE 8720_1 | TR_CABLE 8720_1 | TR_CABLE 8720_1
SW | 84301618 | 3203 | MILES | 3203_Miles 33 kV | Loading (A) | 158.3319 | 167.1245 | 120.4578 | 154.9505 | 165.6089 | 117.9697 | 154.9506 | 165.609 | 117.9698 | 154.9508 | 165.6092 | 117.9698 | 158.3322 | 167.1247 | 120.4578
SW | 84301618 | 3203 | MILES | 3203_Miles 33 kV | Loading (MVA) | 9.008 | 9.6145 | 6.9125 | 8.8216 | 9.4103 | 6.7729 | 8.8216 | 9.4103 | 6.7729 | 8.8216 | 9.4103 | 6.7729 | 9.008 | 9.6145 | 6.9125
SW | 84301618 | 3203 | MILES | 3203_Miles 33 kV | Loading (MW) | 8.9314 | 9.5331 | 6.888 | 8.7473 | 9.3324 | 6.7499 | 8.7473 | 9.3324 | 6.7499 | 8.7473 | 9.3324 | 6.7499 | 8.9314 | 9.5331 | 6.888
SW | 84301618 | 3203 | MILES | 3203_Miles 33 kV | Power Factor | 0.9915 | 0.99153 | 0.99646 | 0.99158 | 0.99172 | 0.9966 | 0.99158 | 0.99172 | 0.9966 | 0.99158 | 0.99172 | 0.9966 | 0.9915 | 0.99153 | 0.99646
SW | 84301618 | 3203 | MILES | 3203_Miles 33 kV | Rating (A) | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181
SW | 84301618 | 3203 | MILES | 3203_Miles 33 kV | Time | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00
SW | 84301618 | 3203 | MILES | 3203_Miles 33 kV | Voltage at Constrained Conductor | 32.8473 | 33.2143 | 33.1312 | 32.8694 | 32.8065 | 33.1472 | 32.8694 | 32.8064 | 33.1472 | 32.8694 | 32.8064 | 33.1472 | 32.8472 | 33.2143 | 33.1312
SW | 84976334 | 7448 | 7448 SOTO - TOCE 110KV | 7448_South Toowoomba-TWCE 110 kV | % of Rated A | 17.627 | 14.622 | 12.3527 | 17.2906 | 14.3441 | 12.1765 | 17.0391 | 14.1365 | 12.0455 | 16.8782 | 13.9044 | 11.9611 | 16.8069 | 13.8569 | 11.9209
SW | 84976334 | 7448 | 7448 SOTO - TOCE 110KV | 7448_South Toowoomba-TWCE 110 kV | Limiting Line Name | TR_CABLE 14006_1 | TR_CABLE 14006_1 | TR_CABLE 13760_1 | TR_CABLE 14006_1 | TR_CABLE 14006_1 | TR_CABLE 13760_1 | TR_CABLE 14006_1 | TR_CABLE 14006_1 | TR_CABLE 13760_1 | TR_CABLE 14006_1 | TR_CABLE 13760_1 | TR_CABLE 13760_1 | TR_CABLE 14006_1 | TR_CABLE 13760_1 | TR_CABLE 13760_1
SW | 84976334 | 7448 | 7448 SOTO - TOCE 110KV | 7448_South Toowoomba-TWCE 110 kV | Loading (A) | 74.0336 | 61.4122 | 51.8815 | 72.6206 | 60.2454 | 51.1415 | 71.5643 | 59.3733 | 50.5911 | 70.8884 | 58.3984 | 50.2365 | 70.589 | 58.1988 | 50.0679
SW | 84976334 | 7448 | 7448 SOTO - TOCE 110KV | 7448_South Toowoomba-TWCE 110 kV | Loading (MVA) | 14.8257 | 12.3332 | 10.4316 | 14.5445 | 12.1005 | 10.2835 | 14.3339 | 11.9262 | 10.1732 | 14.1939 | 11.8098 | 10.098 | 14.1243 | 11.7586 | 10.0588
SW | 84976334 | 7448 | 7448 SOTO - TOCE 110KV | 7448_South Toowoomba-TWCE 110 kV | Loading (MW) | 14.136 | 11.8051 | 9.856 | 13.8748 | 11.5871 | 9.6763 | 13.6789 | 11.4236 | 9.5416 | 13.5484 | 11.442 | 9.4517 | 13.4832 | 11.3873 | 9.4067
SW | 84976334 | 7448 | 7448 SOTO - TOCE 110KV | 7448_South Toowoomba-TWCE 110 kV | Power Factor | 0.95348 | 0.95719 | 0.94482 | 0.95395 | 0.95757 | 0.94096 | 0.95431 | 0.95786 | 0.93792 | 0.95452 | 0.96885 | 0.936 | 0.95461 | 0.96842 | 0.93516
SW | 84976334 | 7448 | 7448 SOTO - TOCE 110KV | 7448_South Toowoomba-TWCE 110 kV | Rating (A) | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420
SW | 84976334 | 7448 | 7448 SOTO - TOCE 110KV | 7448_South Toowoomba-TWCE 110 kV | Time | 14:30 | 17:00 | 8:30 | 14:30 | 17:00 | 8:30 | 14:30 | 17:00 | 8:30 | 14:30 | 17:00 | 8:30 | 14:30 | 17:00 | 8:30
SW | 84976334 | 7448 | 7448 SOTO - TOCE 110KV | 7448_South Toowoomba-TWCE 110 kV | Voltage at Constrained Conductor | 115.6179 | 115.9469 | 116.0857 | 115.6321 | 115.963 | 116.0932 | 115.6398 | 115.9712 | 116.0971 | 115.602 | 116.757 | 116.0527 | 115.5231 | 116.649 | 115.992
SW | 84976560 | 7449 | SOTO - TWCE 110KV 7449 FDR | 7449 South Toowoomba-TWCE 110 kV | % of Rated A | 9.9295 | 9.0189 | 8.3362 | 9.8217 | 8.9413 | 8.2833 | 9.7418 | 8.884 | 8.2442 | 9.6895 | 8.8532 | 8.2174 | 9.6641 | 8.8337 | 8.2031
SW | 84976560 | 7449 | SOTO - TWCE 110KV 7449 FDR | 7449 South Toowoomba-TWCE 110 kV | Limiting Line Name | TR_CABLE 13761_1 | TR_CABLE 13761_1 | TR_CABLE 13761_1 | TR_CABLE 13761_1 | TR_CABLE 13761_1 | TR_CABLE 13761_1 | TR_CABLE 13761_1 | TR_CABLE 13761_1 | TR_CABLE 13761_1 | TR_CABLE 13761_1 | TR_CABLE 13761_1 | TR_CABLE 13761_1 | TR_CABLE 13761_1 | TR_CABLE 13761_1 | TR_CABLE 13761_1
SW | 84976560 | 7449 | SOTO - TWCE 110KV 7449 FDR | 7449 South Toowoomba-TWCE 110 kV | Loading (A) | 41.704 | 37.8794 | 35.0119 | 41.2512 | 37.5536 | 34.7897 | 40.9158 | 37.3127 | 34.6258 | 40.696 | 37.1836 | 34.5131 | 40.5891 | 37.1014 | 34.453
SW | 84976560 | 7449 | SOTO - TWCE 110KV 7449 FDR | 7449 South Toowoomba-TWCE 110 kV | Loading (MVA) | 8.3531 | 7.6083 | 7.0397 | 8.2634 | 7.5439 | 6.9955 | 8.1967 | 7.496 | 6.9628 | 8.15 | 7.5196 | 6.9375 | 8.1231 | 7.496 | 6.9217
SW | 84976560 | 7449 | SOTO - TWCE 110KV 7449 FDR | 7449 South Toowoomba-TWCE 110 kV | Loading (MW) | 7.1842 | 6.0217 | 4.9862 | 7.054 | 5.9129 | 4.8965 | 6.9563 | 5.8313 | 4.8293 | 6.891 | 5.7785 | 4.7844 | 6.8583 | 5.7511 | 4.7618
SW | 84976560 | 7449 | SOTO - TWCE 110KV 7449 FDR | 7449 South Toowoomba-TWCE 110 kV | Power Factor | 0.86007 | 0.79146 | 0.7083 | 0.85364 | 0.7838 | 0.69996 | 0.84866 | 0.77792 | 0.69359 | 0.84553 | 0.76846 | 0.68964 | 0.8443 | 0.76722 | 0.68795
SW | 84976560 | 7449 | SOTO - TWCE 110KV 7449 FDR | 7449 South Toowoomba-TWCE 110 kV | Rating (A) | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420
SW | 84976560 | 7449 | SOTO - TWCE 110KV 7449 FDR | 7449 South Toowoomba-TWCE 110 kV | Time | 14:30 | 17:00 | 8:30 | 14:30 | 17:00 | 8:30 | 14:30 | 17:00 | 8:30 | 14:30 | 17:00 | 8:30 | 14:30 | 17:00 | 8:30
SW | 84976560 | 7449 | SOTO - TWCE 110KV 7449 FDR | 7449 South Toowoomba-TWCE 110 kV | Voltage at Constrained Conductor | 115.6404 | 115.9647 | 116.0857 | 115.6541 | 115.9804 | 116.0932 | 115.6614 | 115.9883 | 116.0971 | 115.6234 | 116.757 | 116.0527 | 115.5444 | 116.649 | 115.992
SW | 85177784 | 7374 | Roma Power Station 132 kV | 7374_Roma Power Station 132 kV | % of Rated A | 0.0072216 | 0.0071973 | 0.0073032 | 0.0072227 | 0.0071986 | 0.0073037 | 0.0072135 | 0.0071888 | 0.0072999 | 0.0072129 | 0.007188 | 0.0072996 | 0.0072065 | 0.0071866 | 0.007299
SW | 85177784 | 7374 | Roma Power Station 132 kV | 7374_Roma Power Station 132 kV | Limiting Line Name | 7374 ROPS-ROMA | 7374 ROPS-ROMA | 7374 ROPS-ROMA | 7374 ROPS-ROMA | 7374 ROPS-ROMA | 7374 ROPS-ROMA | 7374 ROPS-ROMA | 7374 ROPS-ROMA | 7374 ROPS-ROMA | 7374 ROPS-ROMA | 7374 ROPS-ROMA | 7374 ROPS-ROMA | 7374 ROPS-ROMA | 7374 ROPS-ROMA | 7374 ROPS-ROMA
SW | 85177784 | 7374 | Roma Power Station 132 kV | 7374_Roma Power Station 132 kV | Loading (A) | 0.031486 | 0.03138 | 0.031842 | 0.031491 | 0.031386 | 0.031844 | 0.031451 | 0.031343 | 0.031827 | 0.031448 | 0.03134 | 0.031826 | 0.03142 | 0.031333 | 0.031824
SW | 85177784 | 7374 | Roma Power Station 132 kV | 7374_Roma Power Station 132 kV | Loading (MVA) | 0.0070996 | 0.0070519 | 0.007261 | 0.0071019 | 0.0070546 | 0.007262 | 0.0070838 | 0.0070353 | 0.0072544 | 0.0070825 | 0.0070337 | 0.0072538 | 0.00707 | 0.007031 | 0.0072528
SW | 85177784 | 7374 | Roma Power Station 132 kV | 7374_Roma Power Station 132 kV | Loading (MW) | 2.1445e-08 | 2.1268e-08 | 2.1896e-08 | 2.1439e-08 | 2.129e-08 | 2.1894e-08 | 2.1362e-08 | 2.1219e-08 | 2.1875e-08 | 2.1369e-08 | 2.1243e-08 | 2.1924e-08 | 2.1325e-08 | 2.123e-08 | 2.1891e-08
SW | 85177784 | 7374 | Roma Power Station 132 kV | 7374_Roma Power Station 132 kV | Power Factor | 3.0206e-06 | 3.016e-06 | 3.0156e-06 | 3.0187e-06 | 3.018e-06 | 3.0149e-06 | 3.0156e-06 | 3.0161e-06 | 3.0154e-06 | 3.0172e-06 | 3.0202e-06 | 3.0225e-06 | 3.0163e-06 | 3.0195e-06 | 3.0183e-06
SW | 85177784 | 7374 | Roma Power Station 132 kV | 7374_Roma Power Station 132 kV | Rating (A) | 436 | 436 | 436 | 436 | 436 | 436 | 436 | 436 | 436 | 436 | 436 | 436 | 436 | 436 | 436
SW | 85177784 | 7374 | Roma Power Station 132 kV | 7374_Roma Power Station 132 kV | Time | 9:00 | 21:30 | 3:30 | 9:00 | 21:30 | 3:30 | 9:00 | 21:30 | 3:30 | 9:00 | 21:30 | 3:30 | 9:00 | 21:30 | 3:30
SW | 85177784 | 7374 | Roma Power Station 132 kV | 7374_Roma Power Station 132 kV | Voltage at Constrained Conductor | 130.1834 | 129.7456 | 131.6544 | 130.2046 | 129.7701 | 131.6635 | 130.0382 | 129.5926 | 131.5949 | 130.0263 | 129.578 | 131.5893 | 129.9119 | 129.5525 | 131.5801
WB | 40001217 | 7188 | Gin Gin - Korenan QR | 7188_Gin Gin - Korenan QR 132 kV | % of Rated A | 7.1815 | 7.2531 | 6.6596 | 7.1868 | 7.2754 | 6.6633 | 7.1873 | 7.2763 | 6.6635 | 7.1874 | 7.2761 | 6.6636 | 7.2636 | 7.3611 | 6.7284
WB | 40001217 | 7188 | Gin Gin - Korenan QR | 7188_Gin Gin - Korenan QR 132 kV | Limiting Line Name | TR_LINE 88330_1 | TR_LINE 88330_1 | TR_LINE 88330_1 | TR_LINE 88330_1 | TR_LINE 88330_1 | TR_LINE 88330_1 | TR_LINE 88330_1 | TR_LINE 88330_1 | TR_LINE 88330_1 | TR_LINE 88330_1 | TR_LINE 88330_1 | TR_LINE 88330_1 | TR_LINE 88330_1 | TR_LINE 88330_1 | TR_LINE 88330_1
WB | 40001217 | 7188 | Gin Gin - Korenan QR | 7188_Gin Gin - Korenan QR 132 kV | Loading (A) | 27.146 | 30.6082 | 25.7062 | 27.1663 | 30.7024 | 25.7202 | 27.1678 | 30.7059 | 25.721 | 27.1683 | 30.705 | 25.7213 | 27.4562 | 31.064 | 25.9716
WB | 40001217 | 7188 | Gin Gin - Korenan QR | 7188_Gin Gin - Korenan QR 132 kV | Loading (MVA) | 6.5607 | 7.4058 | 6.1704 | 6.5536 | 7.4038 | 6.1632 | 6.5531 | 7.4032 | 6.1628 | 6.5529 | 7.4033 | 6.1626 | 6.6213 | 7.4914 | 6.2278
WB | 40001217 | 7188 | Gin Gin - Korenan QR | 7188_Gin Gin - Korenan QR 132 kV | Loading (MW) | 5.851 | 6.8647 | 5.3552 | 5.8512 | 6.8641 | 5.3553 | 5.8512 | 6.8642 | 5.3553 | 5.8512 | 6.8642 | 5.3553 | 5.9357 | 6.9664 | 5.4334
WB | 40001217 | 7188 | Gin Gin - Korenan QR | 7188_Gin Gin - Korenan QR 132 kV | Power Factor | 0.89182 | 0.92694 | 0.86789 | 0.89281 | 0.92711 | 0.86893 | 0.89289 | 0.92719 | 0.86898 | 0.89291 | 0.92717 | 0.86901 | 0.89645 | 0.92992 | 0.87244
WB | 40001217 | 7188 | Gin Gin - Korenan QR | 7188_Gin Gin - Korenan QR 132 kV | Rating (A) | 378 | 422 | 386 | 378 | 422 | 386 | 378 | 422 | 386 | 378 | 422 | 386 | 378 | 422 | 386
WB | 40001217 | 7188 | Gin Gin - Korenan QR | 7188_Gin Gin - Korenan QR 132 kV | Time | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00
WB | 40001217 | 7188 | Gin Gin - Korenan QR | 7188_Gin Gin - Korenan QR 132 kV | Voltage at Constrained Conductor | 139.5359 | 139.6916 | 138.584 | 139.2807 | 139.2272 | 138.3463 | 139.2615 | 139.1987 | 138.3339 | 139.2551 | 139.2058 | 138.328 | 139.233 | 139.2339 | 138.4436
WB | 50000001 | 7187 | 7187 GIN GIN - BUNDABERG T/LINE | 7187_Gin Gin - Bundaberg 132 kV | % of Rated A | 55.4958 | 53.1546 | 50.5007 | 59.1175 | 56.4922 | 55.3232 | 59.323 | 56.7747 | 55.4633 | 59.47 | 56.9217 | 55.5704 | 59.7019 | 57.1814 | 55.7908
WB | 50000001 | 7187 | 7187 GIN GIN - BUNDABERG T/LINE | 7187_Gin Gin - Bundaberg 132 kV | Limiting Line Name | TR_LINE 6941_a | TR_LINE 6941_1 | TR_LINE 6941_1 | TR_LINE 6941_c | TR_LINE 6941_c | TR_LINE 6941_c | TR_LINE 6941_c | TR_LINE 6941_c | TR_LINE 6941_c | TR_LINE 6941_c | TR_LINE 6941_c | TR_LINE 6941_c | TR_LINE 6941_c | TR_LINE 6941_c | TR_LINE 6941_c
WB | 50000001 | 7187 | 7187 GIN GIN - BUNDABERG T/LINE | 7187_Gin Gin - Bundaberg 132 kV | Loading (A) | 376.8006 | 388.5602 | 334.8195 | 401.4075 | 412.9579 | 366.7927 | 402.8033 | 415.0234 | 367.722 | 403.8012 | 416.0978 | 368.4317 | 405.3758 | 417.9962 | 369.893
WB | 50000001 | 7187 | 7187 GIN GIN - BUNDABERG T/LINE | 7187_Gin Gin - Bundaberg 132 kV | Loading (MVA) | 91.0664 | 92.8222 | 80.4415 | 93.6538 | 96.2562 | 85.4304 | 93.9624 | 96.7088 | 85.6378 | 94.1891 | 96.9515 | 85.7976 | 94.5366 | 97.3662 | 86.1187
WB | 50000001 | 7187 | 7187 GIN GIN - BUNDABERG T/LINE | 7187_Gin Gin - Bundaberg 132 kV | Loading (MW) | 91.0542 | 92.8026 | 80.2288 | 90.9215 | 94.2231 | 81.8471 | 91.3515 | 94.8437 | 82.1403 | 91.6173 | 95.1244 | 82.351 | 92.0996 | 95.6911 | 82.8547
WB | 50000001 | 7187 | 7187 GIN GIN - BUNDABERG T/LINE | 7187_Gin Gin - Bundaberg 132 kV | Power Factor | 0.99987 | 0.99979 | 0.99736 | 0.97082 | 0.97888 | 0.95806 | 0.97221 | 0.98071 | 0.95916 | 0.9727 | 0.98115 | 0.95983 | 0.97422 | 0.9828 | 0.9621
WB | 50000001 | 7187 | 7187 GIN GIN - BUNDABERG T/LINE | 7187_Gin Gin - Bundaberg 132 kV | Rating (A) | 679 | 731 | 663 | 679 | 731 | 663 | 679 | 731 | 663 | 679 | 731 | 663 | 679 | 731 | 663
WB | 50000001 | 7187 | 7187 GIN GIN - BUNDABERG T/LINE | 7187_Gin Gin - Bundaberg 132 kV | Time | 16:30 | 18:00 | 22:30 | 16:30 | 18:30 | 22:30 | 16:30 | 18:30 | 22:30 | 16:30 | 18:00 | 22:30 | 16:30 | 18:30 | 22:30
WB | 50000001 | 7187 | 7187 GIN GIN - BUNDABERG T/LINE | 7187_Gin Gin - Bundaberg 132 kV | Voltage at Constrained Conductor | 139.5359 | 137.9217 | 138.7103 | 134.7037 | 134.5743 | 134.4717 | 134.6792 | 134.5342 | 134.4576 | 134.6704 | 134.5236 | 134.449 | 134.6423 | 134.4854 | 134.419
WB | 50000002 | 7190 | 7190 WOOLOOGA - MUNGAR T/LINE | 7190_Woolooga-Mungar 132 kV | % of Rated A | 3.176 | 2.414 | 2.6931 | 3.176 | 2.414 | 2.6931 | 3.176 | 2.414 | 2.6931 | 3.176 | 2.414 | 2.6931 | 3.176 | 2.414 | 2.6931
WB | 50000002 | 7190 | 7190 WOOLOOGA - MUNGAR T/LINE | 7190_Woolooga-Mungar 132 kV | Limiting Line Name | TR_LINE 223602_1 | TR_LINE 6802_2 | TR_LINE 6802_2 | TR_LINE 223602_1 | TR_LINE 6802_2 | TR_LINE 6802_2 | TR_LINE 223602_1 | TR_LINE 6802_2 | TR_LINE 6802_2 | TR_LINE 223602_1 | TR_LINE 6802_2 | TR_LINE 6802_2 | TR_LINE 223602_1 | TR_LINE 6802_2 | TR_LINE 6802_2
WB | 50000002 | 7190 | 7190 WOOLOOGA - MUNGAR T/LINE | 7190_Woolooga-Mungar 132 kV | Loading (A) | 7.9083 | 14.4839 | 14.5965 | 7.9083 | 14.4839 | 14.5965 | 7.9083 | 14.4839 | 14.5965 | 7.9083 | 14.4839 | 14.5965 | 7.9083 | 14.4839 | 14.5965
WB | 50000002 | 7190 | 7190 WOOLOOGA - MUNGAR T/LINE | 7190_Woolooga-Mungar 132 kV | Loading (MVA) | 1.9 | 3.477 | 3.5041 | 1.9 | 3.477 | 3.5041 | 1.9 | 3.477 | 3.5041 | 1.9 | 3.477 | 3.5041 | 1.9 | 3.477 | 3.5041
WB | 50000002 | 7190 | 7190 WOOLOOGA - MUNGAR T/LINE | 7190_Woolooga-Mungar 132 kV | Loading (MW) | 1.7955 | 0.50707 | 0.38356 | 1.7955 | 0.50707 | 0.38356 | 1.7955 | 0.50707 | 0.38356 | 1.7955 | 0.50707 | 0.38356 | 1.7955 | 0.50707 | 0.38356
WB | 50000002 | 7190 | 7190 WOOLOOGA - MUNGAR T/LINE | 7190_Woolooga-Mungar 132 kV | Power Factor | 0.945 | 0.14583 | 0.10946 | 0.945 | 0.14583 | 0.10946 | 0.945 | 0.14583 | 0.10946 | 0.945 | 0.14583 | 0.10946 | 0.945 | 0.14583 | 0.10946
WB | 50000002 | 7190 | 7190 WOOLOOGA - MUNGAR T/LINE | 7190_Woolooga-Mungar 132 kV | Rating (A) | 249 | 600 | 542 | 249 | 600 | 542 | 249 | 600 | 542 | 249 | 600 | 542 | 249 | 600 | 542
WB | 50000002 | 7190 | 7190 WOOLOOGA - MUNGAR T/LINE | 7190_Woolooga-Mungar 132 kV | Time | 11:30 | 19:30 | 8:30 | 11:30 | 19:30 | 8:30 | 11:30 | 19:30 | 8:30 | 11:30 | 19:30 | 8:30 | 11:30 | 19:30 | 8:30
WB | 50000002 | 7190 | 7190 WOOLOOGA - MUNGAR T/LINE | 7190_Woolooga-Mungar 132 kV | Voltage at Constrained Conductor | 138.7098 | 138.6 | 138.6 | 138.7098 | 138.6 | 138.6 | 138.7098 | 138.6 | 138.6 | 138.7098 | 138.6 | 138.6 | 138.7098 | 138.6 | 138.6
WB | 50000003 | 7215 | 7215 BUNDABERG - ISIS NO.1 | 7215_Bundaberg - ISIS No 1 132 kV | % of Rated A | 56.2578 | 34.1622 | 34.4742 | 62.6788 | 36.834 | 37.5959 | 63.2443 | 37.5271 | 37.9376 | 63.3899 | 37.6079 | 37.9993 | 63.2649 | 37.4603 | 37.9539
WB | 50000003 | 7215 | 7215 BUNDABERG - ISIS NO.1 | 7215_Bundaberg - ISIS No 1 132 kV | Limiting Line Name | TR_LINE 6780_2 | TR_LINE 6780_2 | TR_LINE 6780_2 | TR_LINE 6780_2 | TR_LINE 6780_2 | TR_LINE 6780_2 | TR_LINE 6780_2 | TR_LINE 6780_2 | TR_LINE 6780_2 | TR_LINE 6780_2 | TR_LINE 6780_2 | TR_LINE 6780_2 | TR_LINE 6780_2 | TR_LINE 6780_2 | TR_LINE 6780_2
WB | 50000003 | 7215 | 7215 BUNDABERG - ISIS NO.1 | 7215_Bundaberg - ISIS No 1 132 kV | Loading (A) | 139.5193 | 135.2824 | 135.4836 | 155.4435 | 145.8626 | 147.7519 | 156.846 | 148.6073 | 149.0947 | 157.207 | 148.9272 | 149.3374 | 156.897 | 148.3429 | 149.159
WB | 50000003 | 7215 | 7215 BUNDABERG - ISIS NO.1 | 7215_Bundaberg - ISIS No 1 132 kV | Loading (MVA) | 33.186 | 31.6747 | 32.4107 | 36.7095 | 33.9773 | 34.8726 | 37.0334 | 34.5913 | 35.1858 | 37.1167 | 34.6582 | 35.2416 | 37.0312 | 34.4987 | 35.1913
WB | 50000003 | 7215 | 7215 BUNDABERG - ISIS NO.1 | 7215_Bundaberg - ISIS No 1 132 kV | Loading (MW) | 31.7069 | 29.9718 | 30.8662 | 33.0181 | 31.2819 | 33.2151 | 33.4913 | 32.1946 | 33.5894 | 33.5852 | 32.2945 | 33.6519 | 33.5334 | 32.1866 | 33.6091
WB | 50000003 | 7215 | 7215 BUNDABERG - ISIS NO.1 | 7215_Bundaberg - ISIS No 1 132 kV | Power Factor | 0.95543 | 0.94624 | 0.95234 | 0.89944 | 0.92067 | 0.95247 | 0.90435 | 0.93071 | 0.95463 | 0.90485 | 0.9318 | 0.95489 | 0.90555 | 0.93298 | 0.95504
WB | 50000003 | 7215 | 7215 BUNDABERG - ISIS NO.1 | 7215_Bundaberg - ISIS No 1 132 kV | Rating (A) | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393
WB | 50000003 | 7215 | 7215 BUNDABERG - ISIS NO.1 | 7215_Bundaberg - ISIS No 1 132 kV | Time | 15:30 | 17:30 | 8:30 | 14:30 | 17:30 | 8:30 | 14:30 | 17:30 | 8:30 | 14:30 | 17:30 | 8:30 | 14:30 | 17:30 | 8:30
WB | 50000003 | 7215 | 7215 BUNDABERG - ISIS NO.1 | 7215_Bundaberg - ISIS No 1 132 kV | Voltage at Constrained Conductor | 137.3282 | 135.1794 | 138.1151 | 136.3469 | 134.4881 | 136.2669 | 136.3199 | 134.3898 | 136.2525 | 136.313 | 134.3603 | 136.2469 | 136.2676 | 134.2691 | 136.2151
WB | 50000006 | 786 | 786 GIN GIN - BUNDABERG T/LINE | 786_Gin Gin - Bundaberg 132 kV | % of Rated A | 133.2873 | 80.8638 | 69.5358 | 130.7967 | 80.0868 | 68.5675 | 131.4983 | 80.6952 | 68.8406 | 131.9141 | 80.9791 | 69.0352 | 132.704 | 81.5159 | 69.5117
WB | 50000006 | 786 | 786 GIN GIN - BUNDABERG T/LINE | 786_Gin Gin - Bundaberg 132 kV | Limiting Line Name | TR_LINE 112963_1 | TR_LINE 112963_1 | TR_LINE 112963_1 | TR_LINE 6770_1 | TR_LINE 6770_1 | TR_LINE 6770_1 | TR_LINE 6770_1 | TR_LINE 6770_1 | TR_LINE 6770_1 | TR_LINE 6770_1 | TR_LINE 6770_1 | TR_LINE 6770_1 | TR_LINE 6770_1 | TR_LINE 6770_1 | TR_LINE 6770_1
WB | 50000006 | 786 | 786 GIN GIN - BUNDABERG T/LINE | 786_Gin Gin - Bundaberg 132 kV | Loading (A) | 377.1835 | 388.9548 | 335.1625 | 369.6443 | 384.609 | 330.3857 | 371.6148 | 387.5098 | 331.6915 | 372.7904 | 388.8682 | 332.6246 | 375.0083 | 391.4307 | 334.895
WB | 50000006 | 786 | 786 GIN GIN - BUNDABERG T/LINE | 786_Gin Gin - Bundaberg 132 kV | Loading (MVA) | 91.1589 | 92.9164 | 80.5239 | 88.1812 | 91.6333 | 78.4632 | 88.6277 | 92.2841 | 78.7612 | 88.8996 | 92.5922 | 78.9754 | 89.4012 | 93.1682 | 79.4886
WB | 50000006 | 786 | 786 GIN GIN - BUNDABERG T/LINE | 786_Gin Gin - Bundaberg 132 kV | Loading (MW) | 91.1488 | 92.8939 | 80.3021 | 87.8898 | 91.2221 | 78.4279 | 88.3202 | 91.84 | 78.7225 | 88.5888 | 92.1371 | 78.9347 | 89.071 | 92.6857 | 79.4387
WB | 50000006 | 786 | 786 GIN GIN - BUNDABERG T/LINE | 786_Gin Gin - Bundaberg 132 kV | Power Factor | 0.99989 | 0.99976 | 0.99725 | 0.9967 | 0.99551 | 0.99955 | 0.99653 | 0.99519 | 0.99951 | 0.9965 | 0.99508 | 0.99949 | 0.99631 | 0.99482 | 0.99937
WB | 50000006 | 786 | 786 GIN GIN - BUNDABERG T/LINE | 786_Gin Gin - Bundaberg 132 kV | Rating (A) | 283 | 481 | 482 | 283 | 481 | 482 | 283 | 481 | 482 | 283 | 481 | 482 | 283 | 481 | 482
WB | 50000006 | 786 | 786 GIN GIN - BUNDABERG T/LINE | 786_Gin Gin - Bundaberg 132 kV | Time | 16:30 | 18:00 | 22:30 | 16:30 | 18:30 | 22:30 | 16:30 | 18:30 | 22:30 | 16:30 | 18:30 | 22:30 | 16:30 | 18:30 | 22:30
WB | 50000006 | 786 | 786 GIN GIN - BUNDABERG T/LINE | 786_Gin Gin - Bundaberg 132 kV | Voltage at Constrained Conductor | 139.5359 | 137.9217 | 138.7103 | 137.731 | 137.554 | 137.1147 | 137.6943 | 137.494 | 137.0936 | 137.6812 | 137.4711 | 137.0808 | 137.6391 | 137.4208 | 137.0363
WB | 50000008 | M029 | BUNDABERG - FARNSFIELD T/LINE | M029_Bundaberg - Farnsfield 66 kV | % of Rated A | 13.3463 | 18.7845 | 19.3445 | 13.133 | 18.4847 | 18.9565 | 13.1327 | 18.4904 | 18.9593 | 13.089 | 18.4955 | 18.9642 | 13.331 | 18.8571 | 19.2514
WB | 50000008 | M029 | BUNDABERG - FARNSFIELD T/LINE | M029_Bundaberg - Farnsfield 66 kV | Limiting Line Name | TR_LINE 8235_1 | TR_LINE 8235_1 | TR_LINE 8235_1 | TR_LINE 8235_1 | TR_LINE 8235_1 | TR_LINE 8235_1 | TR_LINE 8235_1 | TR_LINE 8235_1 | TR_LINE 8235_1 | TR_LINE 8235_1 | TR_LINE 8235_1 | TR_LINE 8235_1 | TR_LINE 8235_1 | TR_LINE 8235_1 | TR_LINE 8235_1
WB | 50000008 | M029 | BUNDABERG - FARNSFIELD T/LINE | M029_Bundaberg - Farnsfield 66 kV | Loading (A) | 25.7584 | 51.4694 | 51.6499 | 25.3467 | 50.6482 | 50.6139 | 25.3461 | 50.6636 | 50.6214 | 25.2618 | 50.6778 | 50.6345 | 25.7289 | 51.6683 | 51.4013
WB | 50000008 | M029 | BUNDABERG - FARNSFIELD T/LINE | M029_Bundaberg - Farnsfield 66 kV | Loading (MVA) | 2.9308 | 5.8177 | 5.8371 | 2.8787 | 5.7607 | 5.7308 | 2.8787 | 5.7608 | 5.7309 | 2.8785 | 5.7609 | 5.731 | 2.9307 | 5.8674 | 5.8354
WB | 50000008 | M029 | BUNDABERG - FARNSFIELD T/LINE | M029_Bundaberg - Farnsfield 66 kV | Loading (MW) | 2.5136 | 4.924 | 4.9399 | 2.4695 | 4.8788 | 4.853 | 2.4695 | 4.8788 | 4.853 | 2.4695 | 4.8788 | 4.853 | 2.5136 | 4.9662 | 4.9398
WB | 50000008 | M029 | BUNDABERG - FARNSFIELD T/LINE | M029_Bundaberg - Farnsfield 66 kV | Power Factor | 0.85767 | 0.84639 | 0.8463 | 0.85784 | 0.84691 | 0.84682 | 0.85784 | 0.84689 | 0.84681 | 0.85791 | 0.84688 | 0.8468 | 0.8577 | 0.84641 | 0.84652
WB | 50000008 | M029 | BUNDABERG - FARNSFIELD T/LINE | M029_Bundaberg - Farnsfield 66 kV | Rating (A) | 193 | 274 | 267 | 193 | 274 | 267 | 193 | 274 | 267 | 193 | 274 | 267 | 193 | 274 | 267
WB | 50000008 | M029 | BUNDABERG - FARNSFIELD T/LINE | M029_Bundaberg - Farnsfield 66 kV | Time | 13:30 | 21:00 | 22:00 | 13:30 | 21:30 | 22:00 | 13:30 | 21:30 | 22:00 | 13:30 | 21:30 | 22:00 | 13:30 | 21:30 | 22:00
WB | 50000008 | M029 | BUNDABERG - FARNSFIELD T/LINE | M029_Bundaberg - Farnsfield 66 kV | Voltage at Constrained Conductor | 65.6901 | 65.2586 | 65.2477 | 65.5722 | 65.6678 | 65.3715 | 65.5736 | 65.649 | 65.3623 | 65.7861 | 65.6317 | 65.3465 | 65.7632 | 65.5631 | 65.5447
WB | 50000009 | M036 | BBERG - STH BUNDABERG T/LINE | M036_Bundaberg-South Bundaberg 66 kV | % of Rated A | 57.1577 | 57.3254 | 65.5974 | 57.0883 | 57.7546 | 64.882 | 56.8353 | 57.5469 | 64.6303 | 57.0485 | 57.826 | 64.9255 | 57.7424 | 58.5646 | 65.754
WB | 50000009 | M036 | BBERG - STH BUNDABERG T/LINE | M036_Bundaberg-South Bundaberg 66 kV | Limiting Line Name | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1
WB | 50000009 | M036 | BBERG - STH BUNDABERG T/LINE | M036_Bundaberg-South Bundaberg 66 kV | Loading (A) | 250.9223 | 275.1617 | 255.1739 | 250.6177 | 277.222 | 252.3908 | 249.5068 | 276.225 | 251.4117 | 250.4431 | 277.5647 | 252.5602 | 253.4889 | 281.1101 | 255.7831
WB | 50000009 | M036 | BBERG - STH BUNDABERG T/LINE | M036_Bundaberg-South Bundaberg 66 kV | Loading (MVA) | 28.8679 | 31.7552 | 29.0936 | 28.822 | 31.7472 | 29.0614 | 28.6865 | 31.6128 | 28.9455 | 28.7871 | 31.7516 | 29.0698 | 29.1145 | 32.1254 | 29.4101
WB | 50000009 | M036 | BBERG - STH BUNDABERG T/LINE | M036_Bundaberg-South Bundaberg 66 kV | Loading (MW) | 28.5403 | 31.5397 | 28.8013 | 28.5436 | 31.5617 | 28.7844 | 28.4033 | 31.4248 | 28.6644 | 28.5086 | 31.5693 | 28.7949 | 28.8457 | 31.9522 | 29.1524
WB | 50000009 | M036 | BBERG - STH BUNDABERG T/LINE | M036_Bundaberg-South Bundaberg 66 kV | Power Factor | 0.98865 | 0.99321 | 0.98995 | 0.99034 | 0.99416 | 0.99047 | 0.99013 | 0.99405 | 0.99029 | 0.99033 | 0.99426 | 0.99054 | 0.99077 | 0.99461 | 0.99124
WB | 50000009 | M036 | BBERG - STH BUNDABERG T/LINE | M036_Bundaberg-South Bundaberg 66 kV | Rating (A) | 439 | 480 | 389 | 439 | 480 | 389 | 439 | 480 | 389 | 439 | 480 | 389 | 439 | 480 | 389
WB | 50000009 | M036 | BBERG - STH BUNDABERG T/LINE | M036_Bundaberg-South Bundaberg 66 kV | Time | 16:30 | 18:30 | 22:30 | 16:30 | 18:30 | 22:30 | 16:30 | 18:30 | 22:30 | 16:30 | 18:30 | 22:30 | 16:30 | 18:30 | 22:30
WB | 50000009 | M036 | BBERG - STH BUNDABERG T/LINE | M036_Bundaberg-South Bundaberg 66 kV | Voltage at Constrained Conductor | 66.4225 | 66.6294 | 65.8266 | 66.3975 | 66.1176 | 66.4786 | 66.3795 | 66.0754 | 66.4713 | 66.3633 | 66.0451 | 66.4533 | 66.3117 | 65.9798 | 66.3842
WB | 50000018 | M046 | TARONG-CABOONBAH T/LINE | M046_Tarong-Caboonbah 66 kV | % of Rated A | 22.9652 | 15.0747 | 15.4069 | 22.9597 | 15.0745 | 15.4082 | 22.9587 | 15.0733 | 15.4077 | 22.9585 | 15.0733 | 15.4076 | 22.9604 | 15.0753 | 15.4086
WB | 50000018 | M046 | TARONG-CABOONBAH T/LINE | M046_Tarong-Caboonbah 66 kV | Limiting Line Name | TR_LINE 9243_1 | TR_LINE 9243_1 | TR_LINE 168863_1 | TR_LINE 9243_1 | TR_LINE 9243_1 | TR_LINE 168863_1 | TR_LINE 9243_1 | TR_LINE 9243_1 | TR_LINE 168863_1 | TR_LINE 9243_1 | TR_LINE 9243_1 | TR_LINE 168863_1 | TR_LINE 9243_1 | TR_LINE 9243_1 | TR_LINE 168863_1
WB | 50000018 | M046 | TARONG-CABOONBAH T/LINE | M046_Tarong-Caboonbah 66 kV | Loading (A) | 57.1834 | 57.5853 | 57.0054 | 57.1697 | 57.5845 | 57.0102 | 57.1672 | 57.58 | 57.0085 | 57.1667 | 57.5802 | 57.008 | 57.1714 | 57.5878 | 57.0119
WB | 50000018 | M046 | TARONG-CABOONBAH T/LINE | M046_Tarong-Caboonbah 66 kV | Loading (MVA) | 6.7048 | 6.7101 | 6.6946 | 6.7089 | 6.7101 | 6.6947 | 6.7089 | 6.71 | 6.6947 | 6.7089 | 6.71 | 6.6947 | 6.709 | 6.7101 | 6.6947
WB | 50000018 | M046 | TARONG-CABOONBAH T/LINE | M046_Tarong-Caboonbah 66 kV | Loading (MW) | 6.0392 | 6.0398 | 6.0317 | 6.0433 | 6.0398 | 6.0317 | 6.0433 | 6.0398 | 6.0317 | 6.0433 | 6.0398 | 6.0317 | 6.0433 | 6.0399 | 6.0317
WB | 50000018 | M046 | TARONG-CABOONBAH T/LINE | M046_Tarong-Caboonbah 66 kV | Power Factor | 0.90073 | 0.90012 | 0.90098 | 0.90078 | 0.90012 | 0.90097 | 0.90078 | 0.90012 | 0.90098 | 0.90078 | 0.90012 | 0.90098 | 0.90078 | 0.90011 | 0.90097
WB | 50000018 | M046 | TARONG-CABOONBAH T/LINE | M046_Tarong-Caboonbah 66 kV | Rating (A) | 249 | 382 | 370 | 249 | 382 | 370 | 249 | 382 | 370 | 249 | 382 | 370 | 249 | 382 | 370
WB | 50000018 | M046 | TARONG-CABOONBAH T/LINE | M046_Tarong-Caboonbah 66 kV | Time | 9:30 | 17:30 | 7:30 | 13:00 | 17:30 | 7:30 | 13:00 | 17:30 | 7:30 | 13:00 | 17:30 | 7:30 | 13:00 | 17:30 | 7:30
WB | 50000018 | M046 | TARONG-CABOONBAH T/LINE | M046_Tarong-Caboonbah 66 kV | Voltage at Constrained Conductor | 67.6945 | 67.2753 | 67.8032 | 67.7529 | 67.2761 | 67.7982 | 67.7555 | 67.2807 | 67.8 | 67.756 | 67.2805 | 67.8005 | 67.7511 | 67.2727 | 67.7964
WB | 50000048 | M030 | FARNSFIELD - CHILDERS T/LINE | M030_Farnsfield - Childers 66 kV | % of Rated A | 43.1969 | 38.3166 | 34.0831 | 42.7639 | 38.1649 | 34.0236 | 42.2429 | 37.8031 | 33.6311 | 42.8278 | 38.3433 | 34.0991 | 42.8727 | 38.4142 | 33.8285
WB | 50000048 | M030 | FARNSFIELD - CHILDERS T/LINE | M030_Farnsfield - Childers 66 kV | Limiting Line Name | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1
WB | 50000048 | M030 | FARNSFIELD - CHILDERS T/LINE | M030_Farnsfield - Childers 66 kV | Loading (A) | 56.9624 | 63.9205 | 54.1412 | 56.3927 | 63.6677 | 54.047 | 55.7063 | 63.0645 | 53.4243 | 56.4768 | 63.9649 | 54.1666 | 56.5357 | 64.0832 | 53.7379
WB | 50000048 | M030 | FARNSFIELD - CHILDERS T/LINE | M030_Farnsfield - Childers 66 kV | Loading (MVA) | 6.5144 | 7.2844 | 6.212 | 6.5041 | 7.2794 | 6.2104 | 6.4179 | 7.1855 | 6.1289 | 6.5057 | 7.2853 | 6.2124 | 6.5067 | 7.2877 | 6.2052
WB | 50000048 | M030 | FARNSFIELD - CHILDERS T/LINE | M030_Farnsfield - Childers 66 kV | Loading (MW) | 6.3982 | 7.0984 | 6.1265 | 6.3974 | 7.098 | 6.1263 | 6.3179 | 7.0101 | 6.0503 | 6.3975 | 7.0985 | 6.1265 | 6.3976 | 7.0987 | 6.1259
WB | 50000048 | M030 | FARNSFIELD - CHILDERS T/LINE | M030_Farnsfield - Childers 66 kV | Power Factor | 0.98216 | 0.97447 | 0.98623 | 0.98359 | 0.97508 | 0.98646 | 0.98443 | 0.97559 | 0.98717 | 0.98338 | 0.97436 | 0.98616 | 0.98323 | 0.97407 | 0.98722
WB | 50000048 | M030 | FARNSFIELD - CHILDERS T/LINE | M030_Farnsfield - Childers 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
WB | 50000048 | M030 | FARNSFIELD - CHILDERS T/LINE | M030_Farnsfield - Childers 66 kV | Time | 15:00 | 18:00 | 22:00 | 15:00 | 18:00 | 22:00 | 15:00 | 18:00 | 22:00 | 15:00 | 18:00 | 22:00 | 15:00 | 18:00 | 22:00
WB | 50000048 | M030 | FARNSFIELD - CHILDERS T/LINE | M030_Farnsfield - Childers 66 kV | Voltage at Constrained Conductor | 66.0279 | 65.7954 | 66.2435 | 66.5897 | 66.0113 | 66.3419 | 66.5159 | 65.7826 | 66.2345 | 66.5059 | 65.7576 | 66.217 | 66.4474 | 65.6573 | 66.6676
WB | 50000069 | M024 | GAYNDAH - MUNDUBBERA T/LINE | M024_Gayndah - Mundubbera 66 kV | % of Rated A | 52.8739 | 42.1915 | 33.1999 | 52.7856 | 42.4798 | 33.2618 | 53.0501 | 42.6551 | 33.315 | 53.0501 | 42.6716 | 33.3184 | 52.964 | 42.6792 | 33.3795
WB | 50000069 | M024 | GAYNDAH - MUNDUBBERA T/LINE | M024_Gayndah - Mundubbera 66 kV | Limiting Line Name | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1
WB | 50000069 | M024 | GAYNDAH - MUNDUBBERA T/LINE | M024_Gayndah - Mundubbera 66 kV | Loading (A) | 69.7936 | 74.679 | 56.4398 | 69.677 | 75.1892 | 56.5451 | 70.0261 | 75.4995 | 56.6354 | 70.0261 | 75.5287 | 56.6413 | 69.9125 | 75.5422 | 56.7451
WB | 50000069 | M024 | GAYNDAH - MUNDUBBERA T/LINE | M024_Gayndah - Mundubbera 66 kV | Loading (MVA) | 8.0608 | 8.637 | 6.5078 | 8.0705 | 8.6529 | 6.5366 | 8.0834 | 8.647 | 6.5305 | 8.0834 | 8.6464 | 6.5301 | 8.0571 | 8.639 | 6.4884
WB | 50000069 | M024 | GAYNDAH - MUNDUBBERA T/LINE | M024_Gayndah - Mundubbera 66 kV | Loading (MW) | 7.7926 | 8.4221 | 6.0731 | 7.7978 | 8.4321 | 6.0783 | 7.8 | 8.4346 | 6.0789 | 7.8 | 8.4348 | 6.0789 | 7.7937 | 8.4285 | 6.075
WB | 50000069 | M024 | GAYNDAH - MUNDUBBERA T/LINE | M024_Gayndah - Mundubbera 66 kV | Power Factor | 0.96673 | 0.97512 | 0.93321 | 0.96622 | 0.97449 | 0.92989 | 0.96494 | 0.97543 | 0.93085 | 0.96494 | 0.97552 | 0.93091 | 0.9673 | 0.97563 | 0.93629
WB | 50000069 | M024 | GAYNDAH - MUNDUBBERA T/LINE | M024_Gayndah - Mundubbera 66 kV | Rating (A) | 132 | 177 | 170 | 132 | 177 | 170 | 132 | 177 | 170 | 132 | 177 | 170 | 132 | 177 | 170
WB | 50000069 | M024 | GAYNDAH - MUNDUBBERA T/LINE | M024_Gayndah - Mundubbera 66 kV | Time | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00
WB | 50000069 | M024 | GAYNDAH - MUNDUBBERA T/LINE | M024_Gayndah - Mundubbera 66 kV | Voltage at Constrained Conductor | 66.6807 | 66.7733 | 66.5714 | 66.8727 | 66.4422 | 66.7417 | 66.6455 | 66.124 | 66.5724 | 66.6455 | 66.0944 | 66.5615 | 66.5373 | 66.0258 | 66.0155
WB | 50000078 | M026 | ISIS - BUNDABERG 66KV FDR | M026_ISIS - Bundaberg 66 kV | % of Rated A | 16.3015 | 22.4691 | 13.81 | 16.3211 | 22.5215 | 13.8312 | 16.3589 | 22.6014 | 13.8544 | 16.1476 | 22.6096 | 13.8565 | 16.7948 | 23.5217 | 14.2986
WB | 50000078 | M026 | ISIS - BUNDABERG 66KV FDR | M026_ISIS - Bundaberg 66 kV | Limiting Line Name | TR_CABLE 3770_1 | TR_CABLE 3770_1 | TR_CABLE 3770_1 | TR_CABLE 3770_1 | TR_CABLE 3770_1 | TR_CABLE 3770_1 | TR_CABLE 3770_1 | TR_CABLE 3770_1 | TR_CABLE 3770_1 | TR_CABLE 3770_1 | TR_CABLE 3770_1 | TR_CABLE 3770_1 | TR_CABLE 3770_1 | TR_CABLE 3770_1 | TR_CABLE 3770_1
WB | 50000078 | M026 | ISIS - BUNDABERG 66KV FDR | M026_ISIS - Bundaberg 66 kV | Loading (A) | 16.3015 | 22.4691 | 13.81 | 16.3211 | 22.5215 | 13.8312 | 16.3589 | 22.6014 | 13.8544 | 16.1476 | 22.6096 | 13.8565 | 16.7948 | 23.5217 | 14.2986
WB | 50000078 | M026 | ISIS - BUNDABERG 66KV FDR | M026_ISIS - Bundaberg 66 kV | Loading (MVA) | 1.8909 | 2.6207 | 1.6156 | 1.891 | 2.6208 | 1.6157 | 1.891 | 2.621 | 1.6157 | 1.8907 | 2.621 | 1.6157 | 1.9639 | 2.7228 | 1.678
WB | 50000078 | M026 | ISIS - BUNDABERG 66KV FDR | M026_ISIS - Bundaberg 66 kV | Loading (MW) | 1.8661 | 2.5817 | 1.5956 | 1.8661 | 2.5818 | 1.5956 | 1.8661 | 2.5818 | 1.5956 | 1.8661 | 2.5818 | 1.5956 | 1.9379 | 2.6813 | 1.657
WB | 50000078 | M026 | ISIS - BUNDABERG 66KV FDR | M026_ISIS - Bundaberg 66 kV | Power Factor | 0.98687 | 0.98514 | 0.98758 | 0.98686 | 0.98511 | 0.98757 | 0.98683 | 0.98506 | 0.98756 | 0.98695 | 0.98505 | 0.98756 | 0.98677 | 0.98477 | 0.98746
WB | 50000078 | M026 | ISIS - BUNDABERG 66KV FDR | M026_ISIS - Bundaberg 66 kV | Rating (A) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
WB | 50000078 | M026 | ISIS - BUNDABERG 66KV FDR | M026_ISIS - Bundaberg 66 kV | Time | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00
WB | 50000078 | M026 | ISIS - BUNDABERG 66KV FDR | M026_ISIS - Bundaberg 66 kV | Voltage at Constrained Conductor | 66.9716 | 67.3397 | 67.5443 | 66.892 | 67.1856 | 67.4418 | 66.7393 | 66.9523 | 67.33 | 67.6022 | 66.9285 | 67.32 | 67.5133 | 66.8323 | 67.7564
WB | 50000079 | M027 | ISIS - CHILDERS 66KV FDR | M027_ISIS - Childers 66 kV | % of Rated A | 108.0354 | 111.6676 | 105.4875 | 77.7837 | 81.5601 | 81.6276 | 77.237 | 81.1354 | 81.0927 | 77.9231 | 81.8906 | 81.7852 | 77.9172 | 81.9454 | 81.1206
WB | 50000079 | M027 | ISIS - CHILDERS 66KV FDR | M027_ISIS - Childers 66 kV | Limiting Line Name | TR_LINE 172006_1 | TR_LINE 172006_1 | TR_LINE 172006_1 | TR_LINE 172006_1 | TR_LINE 172006_1 | TR_LINE 172006_1 | TR_LINE 172006_1 | TR_LINE 172006_1 | TR_LINE 172006_1 | TR_LINE 172006_1 | TR_LINE 172006_1 | TR_LINE 172006_1 | TR_LINE 172006_1 | TR_LINE 172006_1 | TR_LINE 172006_1
WB | 50000079 | M027 | ISIS - CHILDERS 66KV FDR | M027_ISIS - Childers 66 kV | Loading (A) | 278.7266 | 295.9121 | 246.8379 | 200.6705 | 216.1205 | 190.9977 | 199.2592 | 214.9945 | 189.7456 | 201.03 | 216.9964 | 191.3666 | 201.0138 | 217.1407 | 189.8108
WB | 50000079 | M027 | ISIS - CHILDERS 66KV FDR | M027_ISIS - Childers 66 kV | Loading (MVA) | 31.8185 | 33.969 | 28.4791 | 23.1074 | 24.8676 | 22.0595 | 22.9074 | 24.6517 | 21.8783 | 23.1082 | 24.8743 | 22.0612 | 23.0829 | 24.854 | 22.0285
WB | 50000079 | M027 | ISIS - CHILDERS 66KV FDR | M027_ISIS - Childers 66 kV | Loading (MW) | 31.7742 | 33.861 | 28.4645 | 22.9173 | 24.5802 | 21.9009 | 22.695 | 24.3314 | 21.7025 | 22.9175 | 24.5818 | 21.9012 | 22.8595 | 24.5181 | 21.8507
WB | 50000079 | M027 | ISIS - CHILDERS 66KV FDR | M027_ISIS - Childers 66 kV | Power Factor | 0.99861 | 0.99682 | 0.99948 | 0.99177 | 0.98844 | 0.99281 | 0.99073 | 0.98701 | 0.99197 | 0.99174 | 0.98824 | 0.99275 | 0.99032 | 0.98649 | 0.99193
WB | 50000079 | M027 | ISIS - CHILDERS 66KV FDR | M027_ISIS - Childers 66 kV | Rating (A) | 258 | 265 | 234 | 258 | 265 | 234 | 258 | 265 | 234 | 258 | 265 | 234 | 258 | 265 | 234
WB | 50000079 | M027 | ISIS - CHILDERS 66KV FDR | M027_ISIS - Childers 66 kV | Time | 16:30 | 18:30 | 22:00 | 15:30 | 18:00 | 22:00 | 15:30 | 18:00 | 22:00 | 15:30 | 18:00 | 22:00 | 15:30 | 18:00 | 22:00
WB | 50000079 | M027 | ISIS - CHILDERS 66KV FDR | M027_ISIS - Childers 66 kV | Voltage at Constrained Conductor | 65.9084 | 66.2765 | 66.6123 | 66.4825 | 66.4321 | 66.6818 | 66.3739 | 66.2002 | 66.5703 | 66.366 | 66.1816 | 66.5582 | 66.2984 | 66.0836 | 67.0045
WB | 50000080 | M049 | ISIS - GAYNDAH 66KV FDR | M049_ISIS - Gayndah 66 kV | % of Rated A | 41.5224 | 40.4489 | 35.9111 | 31.8879 | 30.9045 | 28.0647 | 32.2898 | 31.3585 | 28.2411 | 31.8214 | 31.372 | 28.2417 | 31.8643 | 31.4079 | 28.2469
WB | 50000080 | M049 | ISIS - GAYNDAH 66KV FDR | M049_ISIS - Gayndah 66 kV | Limiting Line Name | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2
WB | 50000080 | M049 | ISIS - GAYNDAH 66KV FDR | M049_ISIS - Gayndah 66 kV | Loading (A) | 164.9422 | 167.0798 | 132.4886 | 127.2287 | 128.228 | 103.8395 | 128.8207 | 130.0918 | 104.492 | 126.9674 | 130.1466 | 104.4942 | 127.1304 | 130.2925 | 104.5137
WB | 50000080 | M049 | ISIS - GAYNDAH 66KV FDR | M049_ISIS - Gayndah 66 kV | Loading (MVA) | 19.1801 | 19.5707 | 15.4371 | 14.787 | 14.9962 | 12.2225 | 14.9379 | 15.1617 | 12.292 | 14.912 | 15.1627 | 12.2921 | 14.9143 | 15.1623 | 12.29
WB | 50000080 | M049 | ISIS - GAYNDAH 66KV FDR | M049_ISIS - Gayndah 66 kV | Loading (MW) | 18.8476 | 19.1913 | 15.3657 | 14.7864 | 14.9948 | 12.1963 | 14.9368 | 15.1589 | 12.2664 | 14.9117 | 15.1599 | 12.2665 | 14.9137 | 15.1592 | 12.264
WB | 50000080 | M049 | ISIS - GAYNDAH 66KV FDR | M049_ISIS - Gayndah 66 kV | Power Factor | 0.98267 | 0.98061 | 0.99538 | 0.99996 | 0.99991 | 0.99786 | 0.99993 | 0.99982 | 0.99792 | 0.99998 | 0.99981 | 0.99792 | 0.99996 | 0.9998 | 0.99788
WB | 50000080 | M049 | ISIS - GAYNDAH 66KV FDR | M049_ISIS - Gayndah 66 kV | Rating (A) | 399 | 415 | 370 | 399 | 415 | 370 | 399 | 415 | 370 | 399 | 415 | 370 | 399 | 415 | 370
WB | 50000080 | M049 | ISIS - GAYNDAH 66KV FDR | M049_ISIS - Gayndah 66 kV | Time | 16:30 | 18:30 | 7:00 | 16:30 | 18:30 | 8:30 | 16:30 | 18:30 | 8:30 | 16:30 | 18:30 | 8:30 | 16:30 | 18:30 | 8:30
WB | 50000080 | M049 | ISIS - GAYNDAH 66KV FDR | M049_ISIS - Gayndah 66 kV | Voltage at Constrained Conductor | 67.1365 | 67.6273 | 67.2706 | 67.1017 | 67.5207 | 67.9573 | 66.9489 | 67.2879 | 67.9173 | 67.8082 | 67.2641 | 67.916 | 67.7319 | 67.1868 | 67.8921
WB | 50000081 | M022 | HOWARD TEE ISIS RIVER 66KV FDR | M022_Howard - ISIS 66 kV | % of Rated A | 11.0175 | 14.1155 | 9.8753 | 14.5773 | 18.757 | 13.0514 | 18.2222 | 23.5758 | 16.2787 | 18.096 | 23.7496 | 16.393 | 18.2586 | 23.9518 | 16.389
WB | 50000081 | M022 | HOWARD TEE ISIS RIVER 66KV FDR | M022_Howard - ISIS 66 kV | Limiting Line Name | TR_LINE 118970_1 | TR_LINE 118970_1 | TR_LINE 118970_1 | TR_LINE 118970_1 | TR_LINE 118970_1 | TR_LINE 118970_1 | TR_LINE 118970_1 | TR_LINE 118970_1 | TR_LINE 118970_1 | TR_LINE 118970_1 | TR_LINE 118970_1 | TR_LINE 118970_1 | TR_LINE 118970_1 | TR_LINE 118970_1 | TR_LINE 118970_1
WB | 50000081 | M022 | HOWARD TEE ISIS RIVER 66KV FDR | M022_Howard - ISIS 66 kV | Loading (A) | 60.3761 | 81.3717 | 51.4504 | 79.5315 | 108.1984 | 67.6652 | 99.4715 | 136.054 | 84.4489 | 98.7784 | 137.0584 | 85.0431 | 99.6627 | 138.2273 | 85.0211
WB | 50000081 | M022 | HOWARD TEE ISIS RIVER 66KV FDR | M022_Howard - ISIS 66 kV | Loading (MVA) | 6.974 | 9.5024 | 5.9976 | 9.2106 | 12.5839 | 7.9008 | 11.4784 | 15.7383 | 9.8337 | 11.5459 | 15.8494 | 9.901 | 11.6352 | 15.9627 | 9.964
WB | 50000081 | M022 | HOWARD TEE ISIS RIVER 66KV FDR | M022_Howard - ISIS 66 kV | Loading (MW) | 6.8595 | 9.3305 | 5.9064 | 9.0467 | 12.2729 | 7.7823 | 11.2192 | 15.235 | 9.6473 | 11.2912 | 15.3376 | 9.7118 | 11.368 | 15.4409 | 9.7751
WB | 50000081 | M022 | HOWARD TEE ISIS RIVER 66KV FDR | M022_Howard - ISIS 66 kV | Power Factor | 0.98359 | 0.98191 | 0.9848 | 0.98221 | 0.97528 | 0.98501 | 0.97742 | 0.96802 | 0.98105 | 0.97794 | 0.96771 | 0.98089 | 0.97704 | 0.96731 | 0.98104
WB | 50000081 | M022 | HOWARD TEE ISIS RIVER 66KV FDR | M022_Howard - ISIS 66 kV | Rating (A) | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521
WB | 50000081 | M022 | HOWARD TEE ISIS RIVER 66KV FDR | M022_Howard - ISIS 66 kV | Time | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00
WB | 50000081 | M022 | HOWARD TEE ISIS RIVER 66KV FDR | M022_Howard - ISIS 66 kV | Voltage at Constrained Conductor | 66.6889 | 67.4215 | 67.3018 | 66.8632 | 67.1483 | 67.413 | 66.6228 | 66.7859 | 67.2298 | 67.4848 | 66.7645 | 67.2173 | 67.4031 | 66.6731 | 67.6625
WB | 50000088 | M001 | TARONG - KINGAROY EAST T/LINE | M001_Tarong-Kingaroy East 66 kV | % of Rated A | 33.7322 | 31.4965 | 26.8061 | 33.785 | 31.5519 | 26.8881 | 33.5251 | 31.7491 | 26.6932 | 33.5167 | 31.7532 | 26.6926 | 33.7793 | 31.55 | 26.8941
WB | 50000088 | M001 | TARONG - KINGAROY EAST T/LINE | M001_Tarong-Kingaroy East 66 kV | Limiting Line Name | TR_LINE 7253_1 | TR_LINE 7253_1 | TR_LINE 7253_1 | TR_LINE 7253_1 | TR_LINE 7253_1 | TR_LINE 7253_1 | TR_LINE 7253_1 | TR_LINE 7253_1 | TR_LINE 7253_1 | TR_LINE 7253_1 | TR_LINE 7253_1 | TR_LINE 7253_1 | TR_LINE 7253_1 | TR_LINE 7253_1 | TR_LINE 7253_1
WB | 50000088 | M001 | TARONG - KINGAROY EAST T/LINE | M001_Tarong-Kingaroy East 66 kV | Loading (A) | 183.9788 | 181.5062 | 138.8858 | 184.2692 | 181.828 | 139.3131 | 182.8478 | 182.9635 | 138.3004 | 182.8024 | 182.9878 | 138.2977 | 184.2371 | 181.8158 | 139.3426
WB | 50000088 | M001 | TARONG - KINGAROY EAST T/LINE | M001_Tarong-Kingaroy East 66 kV | Loading (MVA) | 21.7016 | 21.4052 | 16.6723 | 21.7356 | 21.4432 | 16.7226 | 21.5707 | 21.5744 | 16.6023 | 21.5654 | 21.5772 | 16.6019 | 21.731 | 21.4407 | 16.7254
WB | 50000088 | M001 | TARONG - KINGAROY EAST T/LINE | M001_Tarong-Kingaroy East 66 kV | Loading (MW) | 20.7782 | 20.5274 | 16.1684 | 20.8126 | 20.565 | 16.2165 | 20.6625 | 20.6769 | 16.1043 | 20.6593 | 20.6808 | 16.1048 | 20.8061 | 20.5602 | 16.2169
WB | 50000088 | M001 | TARONG - KINGAROY EAST T/LINE | M001_Tarong-Kingaroy East 66 kV | Power Factor | 0.95745 | 0.95899 | 0.96978 | 0.95753 | 0.95904 | 0.96974 | 0.9579 | 0.9584 | 0.97 | 0.95798 | 0.95846 | 0.97006 | 0.95744 | 0.95894 | 0.9696
WB | 50000088 | M001 | TARONG - KINGAROY EAST T/LINE | M001_Tarong-Kingaroy East 66 kV | Rating (A) | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521
WB | 50000088 | M001 | TARONG - KINGAROY EAST T/LINE | M001_Tarong-Kingaroy East 66 kV | Time | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00 | 16:30 | 17:00 | 22:00 | 16:30 | 17:00 | 22:00 | 16:30 | 17:30 | 22:00
WB | 50000088 | M001 | TARONG - KINGAROY EAST T/LINE | M001_Tarong-Kingaroy East 66 kV | Voltage at Constrained Conductor | 68.1026 | 68.0875 | 69.3069 | 68.1018 | 68.0877 | 69.3027 | 68.1103 | 68.0791 | 69.3081 | 68.1107 | 68.0788 | 69.308 | 68.0991 | 68.0843 | 69.2998
WB | 50000089 | M002 | TARONG - KINGAROY WEST T/LINE | M002_Tarong-Kingaroy West 66 kV | % of Rated A | 33.7522 | 31.5152 | 26.8219 | 33.805 | 31.5706 | 26.904 | 33.545 | 31.7679 | 26.709 | 33.5365 | 31.772 | 26.7084 | 33.7994 | 31.5687 | 26.91
WB | 50000089 | M002 | TARONG - KINGAROY WEST T/LINE | M002_Tarong-Kingaroy West 66 kV | Limiting Line Name | TR_LINE 7252_1 | TR_LINE 7252_1 | TR_LINE 7252_1 | TR_LINE 7252_1 | TR_LINE 7252_1 | TR_LINE 7252_1 | TR_LINE 7252_1 | TR_LINE 7252_1 | TR_LINE 7252_1 | TR_LINE 7252_1 | TR_LINE 7252_1 | TR_LINE 7252_1 | TR_LINE 7252_1 | TR_LINE 7252_1 | TR_LINE 7252_1
WB | 50000089 | M002 | TARONG - KINGAROY WEST T/LINE | M002_Tarong-Kingaroy West 66 kV | Loading (A) | 184.9603 | 182.4709 | 139.7405 | 185.2498 | 182.7922 | 140.1682 | 183.8246 | 183.9346 | 139.1522 | 183.7784 | 183.9582 | 139.1488 | 185.2187 | 182.7811 | 140.1995
WB | 50000089 | M002 | TARONG - KINGAROY WEST T/LINE | M002_Tarong-Kingaroy West 66 kV | Loading (MVA) | 21.1463 | 20.8703 | 16.4121 | 21.1784 | 20.9062 | 16.4602 | 21.0243 | 21.0281 | 16.3453 | 21.0196 | 21.0309 | 16.345 | 21.1738 | 20.9036 | 16.4627
WB | 50000089 | M002 | TARONG - KINGAROY WEST T/LINE | M002_Tarong-Kingaroy West 66 kV | Loading (MW) | 20.3982 | 20.1577 | 15.9543 | 20.4314 | 20.194 | 16.0011 | 20.2872 | 20.3011 | 15.892 | 20.2842 | 20.305 | 15.8926 | 20.425 | 20.1893 | 16.0013
WB | 50000089 | M002 | TARONG - KINGAROY WEST T/LINE | M002_Tarong-Kingaroy West 66 kV | Power Factor | 0.96462 | 0.96585 | 0.97211 | 0.96472 | 0.96593 | 0.97211 | 0.96494 | 0.96543 | 0.97227 | 0.96502 | 0.96549 | 0.97232 | 0.96464 | 0.96583 | 0.97197
WB | 50000089 | M002 | TARONG - KINGAROY WEST T/LINE | M002_Tarong-Kingaroy West 66 kV | Rating (A) | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521
WB | 50000089 | M002 | TARONG - KINGAROY WEST T/LINE | M002_Tarong-Kingaroy West 66 kV | Time | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00 | 16:30 | 17:00 | 22:00 | 16:30 | 17:00 | 22:00 | 16:30 | 17:30 | 22:00
WB | 50000089 | M002 | TARONG - KINGAROY WEST T/LINE | M002_Tarong-Kingaroy West 66 kV | Voltage at Constrained Conductor | 66.0079 | 66.0351 | 67.8081 | 66.0048 | 66.0325 | 67.7991 | 66.0325 | 66.005 | 67.8174 | 66.0342 | 66.0051 | 67.8178 | 66.0015 | 66.0281 | 67.7946
WB | 50000099 | M015 | MARYBOROUGH-HOWARD No 1 | M015_Maryborough-Howard No 1 66 kV | % of Rated A | 1.8795 | 1.4778 | 1.5649 | 1.884 | 1.4882 | 1.5647 | 1.8828 | 1.4866 | 1.5641 | 1.8823 | 1.4857 | 1.5635 | 1.8844 | 1.4846 | 1.5652
WB | 50000099 | M015 | MARYBOROUGH-HOWARD No 1 | M015_Maryborough-Howard No 1 66 kV | Limiting Line Name | TR_LINE 112139_1 | TR_LINE 112139_1 | TR_LINE 112139_1 | TR_LINE 112139_1 | TR_LINE 112139_1 | TR_LINE 112139_1 | TR_LINE 112139_1 | TR_LINE 112139_1 | TR_LINE 112139_1 | TR_LINE 112139_1 | TR_LINE 112139_1 | TR_LINE 112139_1 | TR_LINE 112139_1 | TR_LINE 112139_1 | TR_LINE 112139_1
WB | 50000099 | M015 | MARYBOROUGH-HOWARD No 1 | M015_Maryborough-Howard No 1 66 kV | Loading (A) | 2.4809 | 2.468 | 2.4882 | 2.4868 | 2.4852 | 2.4878 | 2.4853 | 2.4826 | 2.487 | 2.4847 | 2.4811 | 2.486 | 2.4875 | 2.4793 | 2.4887
WB | 50000099 | M015 | MARYBOROUGH-HOWARD No 1 | M015_Maryborough-Howard No 1 66 kV | Loading (MVA) | 0.29255 | 0.28951 | 0.29427 | 0.29396 | 0.29357 | 0.29419 | 0.29359 | 0.29295 | 0.29399 | 0.29345 | 0.29261 | 0.29375 | 0.29411 | 0.29217 | 0.29439
WB | 50000099 | M015 | MARYBOROUGH-HOWARD No 1 | M015_Maryborough-Howard No 1 66 kV | Loading (MW) | 5.2921e-05 | 5.237e-05 | 5.3232e-05 | 5.3174e-05 | 5.3105e-05 | 5.3216e-05 | 5.3108e-05 | 5.2991e-05 | 5.3181e-05 | 5.3082e-05 | 5.2931e-05 | 5.3137e-05 | 5.3202e-05 | 5.2851e-05 | 5.3252e-05
WB | 50000099 | M015 | MARYBOROUGH-HOWARD No 1 | M015_Maryborough-Howard No 1 66 kV | Power Factor | 0.00018089 | 0.00018089 | 0.00018089 | 0.00018089 | 0.00018089 | 0.00018089 | 0.00018089 | 0.00018089 | 0.00018089 | 0.00018089 | 0.00018089 | 0.00018089 | 0.00018089 | 0.00018089 | 0.00018089
WB | 50000099 | M015 | MARYBOROUGH-HOWARD No 1 | M015_Maryborough-Howard No 1 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
WB | 50000099 | M015 | MARYBOROUGH-HOWARD No 1 | M015_Maryborough-Howard No 1 66 kV | Time | 13:00 | 21:00 | 4:30 | 10:30 | 21:00 | 22:00 | 10:30 | 21:00 | 23:30 | 10:30 | 21:00 | 23:30 | 13:30 | 21:00 | 22:30
WB | 50000099 | M015 | MARYBOROUGH-HOWARD No 1 | M015_Maryborough-Howard No 1 66 kV | Voltage at Constrained Conductor | 68.083 | 67.728 | 68.2829 | 68.2458 | 68.2016 | 68.2729 | 68.2036 | 68.1286 | 68.2503 | 68.187 | 68.09 | 68.2224 | 68.2637 | 68.0386 | 68.2962
WB | 50000100 | T014 | 66KV MARY-PIAL TEE HOWA FDR | T014_Maryborough-Pialba Tee Howard 66 kV | % of Rated A | 39.6709 | 36.885 | 27.8993 | 39.0721 | 36.1115 | 27.2462 | 38.8489 | 35.9394 | 27.1038 | 38.3699 | 36.0151 | 27.1444 | 38.6542 | 36.3352 | 27.4314
WB | 50000100 | T014 | 66KV MARY-PIAL TEE HOWA FDR | T014_Maryborough-Pialba Tee Howard 66 kV | Limiting Line Name | TR_LINE 43935_1 | TR_LINE 43935_1 | TR_LINE 224569_1 | TR_LINE 43935_1 | TR_LINE 43935_1 | TR_LINE 224569_1 | TR_LINE 43935_1 | TR_LINE 43935_1 | TR_LINE 224569_1 | TR_LINE 43935_1 | TR_LINE 43935_1 | TR_LINE 224569_1 | TR_LINE 43935_1 | TR_LINE 43935_1 | TR_LINE 224569_1
WB | 50000100 | T014 | 66KV MARY-PIAL TEE HOWA FDR | T014_Maryborough-Pialba Tee Howard 66 kV | Loading (A) | 240.0085 | 246.3911 | 152.609 | 236.3858 | 241.2243 | 149.0369 | 235.0356 | 240.0747 | 148.2579 | 232.1376 | 240.5802 | 148.48 | 233.8575 | 242.7186 | 150.0497
WB | 50000100 | T014 | 66KV MARY-PIAL TEE HOWA FDR | T014_Maryborough-Pialba Tee Howard 66 kV | Loading (MVA) | 27.2592 | 27.9211 | 17.7763 | 26.7532 | 27.4523 | 17.4828 | 26.5702 | 27.2835 | 17.3785 | 26.5628 | 27.3116 | 17.3952 | 26.7214 | 27.497 | 17.5108
WB | 50000100 | T014 | 66KV MARY-PIAL TEE HOWA FDR | T014_Maryborough-Pialba Tee Howard 66 kV | Loading (MW) | 27.228 | 27.8677 | 17.77 | 26.7261 | 27.4056 | 17.4732 | 26.5441 | 27.2391 | 17.3685 | 26.5371 | 27.2648 | 17.3856 | 26.6934 | 27.4418 | 17.5032
WB | 50000100 | T014 | 66KV MARY-PIAL TEE HOWA FDR | T014_Maryborough-Pialba Tee Howard 66 kV | Power Factor | 0.99885 | 0.99808 | 0.99965 | 0.99899 | 0.9983 | 0.99945 | 0.99902 | 0.99837 | 0.99942 | 0.99903 | 0.99829 | 0.99945 | 0.99895 | 0.99799 | 0.99956
WB | 50000100 | T014 | 66KV MARY-PIAL TEE HOWA FDR | T014_Maryborough-Pialba Tee Howard 66 kV | Rating (A) | 605 | 668 | 547 | 605 | 668 | 547 | 605 | 668 | 547 | 605 | 668 | 547 | 605 | 668 | 547
WB | 50000100 | T014 | 66KV MARY-PIAL TEE HOWA FDR | T014_Maryborough-Pialba Tee Howard 66 kV | Time | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00 | 16:30 | 17:30 | 22:00
WB | 50000100 | T014 | 66KV MARY-PIAL TEE HOWA FDR | T014_Maryborough-Pialba Tee Howard 66 kV | Voltage at Constrained Conductor | 65.5732 | 65.4256 | 67.2514 | 65.3422 | 65.7049 | 67.7262 | 65.2679 | 65.6136 | 67.6759 | 66.0644 | 65.543 | 67.6395 | 65.9702 | 65.4065 | 67.3769
WB | 50000102 | M012 | MARYBOROUGH- ROCKY ST T/LINE | M012_Maryborough-Rocky St 66 kV | % of Rated A | 34.5106 | 34.7244 | 33.519 | 35.019 | 34.8659 | 33.9666 | 35.7576 | 35.5495 | 34.7328 | 35.4012 | 35.6266 | 34.7883 | 35.7521 | 35.9913 | 35.0743
WB | 50000102 | M012 | MARYBOROUGH- ROCKY ST T/LINE | M012_Maryborough-Rocky St 66 kV | Limiting Line Name | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1
WB | 50000102 | M012 | MARYBOROUGH- ROCKY ST T/LINE | M012_Maryborough-Rocky St 66 kV | Loading (A) | 189.1183 | 201.0543 | 174.6341 | 191.9039 | 201.8734 | 176.9662 | 195.9515 | 205.8317 | 180.9578 | 193.9988 | 206.2779 | 181.2469 | 195.9216 | 208.3895 | 182.7373
WB | 50000102 | M012 | MARYBOROUGH- ROCKY ST T/LINE | M012_Maryborough-Rocky St 66 kV | Loading (MVA) | 22.0194 | 23.4176 | 20.5068 | 22.2532 | 23.6067 | 20.7865 | 22.6927 | 24.031 | 21.2416 | 22.7255 | 24.0637 | 21.2698 | 22.9263 | 24.2745 | 21.4358
WB | 50000102 | M012 | MARYBOROUGH- ROCKY ST T/LINE | M012_Maryborough-Rocky St 66 kV | Loading (MW) | 21.9262 | 23.3695 | 20.4823 | 22.1432 | 23.5459 | 20.7499 | 22.5917 | 23.9671 | 21.2093 | 22.6204 | 24.0027 | 21.239 | 22.8274 | 24.2188 | 21.4069
WB | 50000102 | M012 | MARYBOROUGH- ROCKY ST T/LINE | M012_Maryborough-Rocky St 66 kV | Power Factor | 0.99577 | 0.99795 | 0.99881 | 0.99506 | 0.99743 | 0.99824 | 0.99555 | 0.99734 | 0.99848 | 0.99538 | 0.99747 | 0.99855 | 0.99569 | 0.9977 | 0.99865
WB | 50000102 | M012 | MARYBOROUGH- ROCKY ST T/LINE | M012_Maryborough-Rocky St 66 kV | Rating (A) | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521
WB | 50000102 | M012 | MARYBOROUGH- ROCKY ST T/LINE | M012_Maryborough-Rocky St 66 kV | Time | 16:30 | 18:00 | 8:30 | 16:30 | 18:00 | 8:30 | 16:30 | 18:00 | 8:30 | 16:30 | 18:00 | 8:30 | 16:30 | 18:00 | 8:30
WB | 50000102 | M012 | MARYBOROUGH- ROCKY ST T/LINE | M012_Maryborough-Rocky St 66 kV | Voltage at Constrained Conductor | 67.222 | 67.2463 | 67.7965 | 66.9495 | 67.5143 | 67.8156 | 66.8617 | 67.4062 | 67.7719 | 67.6322 | 67.3517 | 67.7537 | 67.5603 | 67.2534 | 67.7255
WB | 50000103 | TORQUAY TEE | 66KV TORQUAY TEE FDR T015 | M020_Maryborough-Torquay 66 kV | % of Rated A | 49.8078 | 47.9174 | 36.0408 | 49.1342 | 46.9634 | 35.2453 | 48.8989 | 46.8099 | 35.0943 | 48.3625 | 46.9788 | 35.1996 | 48.7712 | 47.4636 | 35.6147
WB | 50000103 | TORQUAY TEE | 66KV TORQUAY TEE FDR T015 | M020_Maryborough-Torquay 66 kV | Limiting Line Name | TR_LINE 7933_2 | TR_LINE 7933_2 | TR_LINE 112154_1 | TR_LINE 7933_2 | TR_LINE 7933_2 | TR_LINE 112154_1 | TR_LINE 7933_2 | TR_LINE 7933_2 | TR_LINE 112154_1 | TR_LINE 7933_2 | TR_LINE 7933_2 | TR_LINE 112154_1 | TR_LINE 7933_2 | TR_LINE 7933_2 | TR_LINE 112154_1
WB | 50000103 | TORQUAY TEE | 66KV TORQUAY TEE FDR T015 | M020_Maryborough-Torquay 66 kV | Loading (A) | 302.8314 | 322.0051 | 198.5849 | 298.7357 | 315.5937 | 194.2016 | 297.3054 | 314.5622 | 193.3694 | 294.0437 | 315.6971 | 193.9499 | 296.5288 | 318.9553 | 196.2369
WB | 50000103 | TORQUAY TEE | 66KV TORQUAY TEE FDR T015 | M020_Maryborough-Torquay 66 kV | Loading (MVA) | 34.3937 | 36.4679 | 23.1786 | 33.8054 | 35.9193 | 22.8224 | 33.6038 | 35.7447 | 22.7069 | 33.6392 | 35.8389 | 22.7628 | 33.8746 | 36.1321 | 22.9436
WB | 50000103 | TORQUAY TEE | 66KV TORQUAY TEE FDR T015 | M020_Maryborough-Torquay 66 kV | Loading (MW) | 34.3904 | 36.4472 | 23.1639 | 33.8032 | 35.9026 | 22.803 | 33.6017 | 35.7273 | 22.6871 | 33.6372 | 35.821 | 22.7441 | 33.8718 | 36.109 | 22.9278
WB | 50000103 | TORQUAY TEE | 66KV TORQUAY TEE FDR T015 | M020_Maryborough-Torquay 66 kV | Power Factor | 0.9999 | 0.99943 | 0.99937 | 0.99993 | 0.99953 | 0.99915 | 0.99994 | 0.99951 | 0.99913 | 0.99994 | 0.9995 | 0.99918 | 0.99992 | 0.99936 | 0.99931
WB | 50000103 | TORQUAY TEE | 66KV TORQUAY TEE FDR T015 | M020_Maryborough-Torquay 66 kV | Rating (A) | 608 | 672 | 551 | 608 | 672 | 551 | 608 | 672 | 551 | 608 | 672 | 551 | 608 | 672 | 551
WB | 50000103 | TORQUAY TEE | 66KV TORQUAY TEE FDR T015 | M020_Maryborough-Torquay 66 kV | Time | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00
WB | 50000103 | TORQUAY TEE | 66KV TORQUAY TEE FDR T015 | M020_Maryborough-Torquay 66 kV | Voltage at Constrained Conductor | 65.5719 | 65.3863 | 67.3876 | 65.3339 | 65.7112 | 67.8497 | 65.2567 | 65.6062 | 67.7968 | 66.0501 | 65.5425 | 67.7603 | 65.9548 | 65.4037 | 67.5024
WB | 50000104 | M019 | MBOROUGH CITY-WALKERS T/LINE | M019_Maryborough City-Walkers 66 kV | % of Rated A | 7.3826 | 0.25357 | 12.7021 | 7.3076 | 0.25328 | 12.7071 | 7.3135 | 0.26342 | 12.7171 | 7.3156 | 0.25402 | 12.7216 | 7.3161 | 0.25378 | 12.7282
WB | 50000104 | M019 | MBOROUGH CITY-WALKERS T/LINE | M019_Maryborough City-Walkers 66 kV | Limiting Line Name | TR_LINE 34120_1 | TR_LINE 34120_1 | TR_LINE 34120_1 | TR_LINE 34120_1 | TR_LINE 34120_1 | TR_LINE 34120_1 | TR_LINE 34120_1 | TR_LINE 34120_1 | TR_LINE 34120_1 | TR_LINE 34120_1 | TR_LINE 34120_1 | TR_LINE 34120_1 | TR_LINE 34120_1 | TR_LINE 34120_1 | TR_LINE 34120_1
WB | 50000104 | M019 | MBOROUGH CITY-WALKERS T/LINE | M019_Maryborough City-Walkers 66 kV | Loading (A) | 40.4568 | 1.4681 | 66.1779 | 40.0454 | 1.4665 | 66.2038 | 40.0782 | 1.5252 | 66.2562 | 40.0896 | 1.4708 | 66.2794 | 40.0922 | 1.4694 | 66.3137
WB | 50000104 | M019 | MBOROUGH CITY-WALKERS T/LINE | M019_Maryborough City-Walkers 66 kV | Loading (MVA) | 4.7086 | 0.17146 | 7.734 | 4.7055 | 0.17107 | 7.7341 | 4.7054 | 0.17613 | 7.7341 | 4.7053 | 0.17209 | 7.7341 | 4.7053 | 0.17175 | 7.7341
WB | 50000104 | M019 | MBOROUGH CITY-WALKERS T/LINE | M019_Maryborough City-Walkers 66 kV | Loading (MW) | 3.8922 | 0.016907 | 6.4073 | 3.8918 | 0.016874 | 6.4073 | 3.8918 | 0.017302 | 6.4073 | 3.8918 | 0.01696 | 6.4073 | 3.8918 | 0.016932 | 6.4073
WB | 50000104 | M019 | MBOROUGH CITY-WALKERS T/LINE | M019_Maryborough City-Walkers 66 kV | Power Factor | 0.82662 | 0.098607 | 0.82846 | 0.82708 | 0.098639 | 0.82846 | 0.82709 | 0.098237 | 0.82845 | 0.82709 | 0.098556 | 0.82845 | 0.8271 | 0.098583 | 0.82845
WB | 50000104 | M019 | MBOROUGH CITY-WALKERS T/LINE | M019_Maryborough City-Walkers 66 kV | Rating (A) | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521
WB | 50000104 | M019 | MBOROUGH CITY-WALKERS T/LINE | M019_Maryborough City-Walkers 66 kV | Time | 11:00 | 20:00 | 7:30 | 11:00 | 20:00 | 7:30 | 11:00 | 19:00 | 7:30 | 11:00 | 20:30 | 7:30 | 11:00 | 20:30 | 7:30
WB | 50000104 | M019 | MBOROUGH CITY-WALKERS T/LINE | M019_Maryborough City-Walkers 66 kV | Voltage at Constrained Conductor | 67.195 | 67.4279 | 67.4734 | 67.8408 | 67.3502 | 67.4472 | 67.7838 | 66.6703 | 67.3942 | 67.7642 | 67.5516 | 67.3707 | 67.7596 | 67.4855 | 67.336
WB | 50000122 | M008 | KILKIVAN - MURGON NO1 T/LINE | M008_Kilkivan-Murgon No 1 66 kV | % of Rated A | 42.3894 | 32.8419 | 21.8981 | 42.8172 | 33.0025 | 21.9695 | 42.5688 | 32.8112 | 21.8477 | 42.7243 | 33.0052 | 21.9691 | 42.9772 | 33.2003 | 22.104
WB | 50000122 | M008 | KILKIVAN - MURGON NO1 T/LINE | M008_Kilkivan-Murgon No 1 66 kV | Limiting Line Name | TR_LINE 7214_1 | TR_LINE 7214_1 | TR_LINE 7214_1 | TR_LINE 7214_1 | TR_LINE 7214_1 | TR_LINE 7214_1 | TR_LINE 7214_1 | TR_LINE 7214_1 | TR_LINE 7214_1 | TR_LINE 7214_1 | TR_LINE 7214_1 | TR_LINE 7214_1 | TR_LINE 7214_1 | TR_LINE 7214_1 | TR_LINE 7214_1
WB | 50000122 | M008 | KILKIVAN - MURGON NO1 T/LINE | M008_Kilkivan-Murgon No 1 66 kV | Loading (A) | 76.6855 | 82.7204 | 53.6218 | 77.4591 | 83.1244 | 53.7965 | 77.0097 | 82.6425 | 53.4982 | 77.2909 | 83.1312 | 53.7955 | 77.7485 | 83.6226 | 54.1257
WB | 50000122 | M008 | KILKIVAN - MURGON NO1 T/LINE | M008_Kilkivan-Murgon No 1 66 kV | Loading (MVA) | 8.9448 | 9.6087 | 6.2659 | 9.1386 | 9.8102 | 6.3944 | 9.0872 | 9.755 | 6.3597 | 9.1361 | 9.8104 | 6.3944 | 9.1877 | 9.8653 | 6.4293
WB | 50000122 | M008 | KILKIVAN - MURGON NO1 T/LINE | M008_Kilkivan-Murgon No 1 66 kV | Loading (MW) | 8.6877 | 9.3009 | 6.1725 | 8.8728 | 9.496 | 6.3006 | 8.8254 | 9.4454 | 6.2678 | 8.8719 | 9.496 | 6.3006 | 8.9194 | 9.5465 | 6.3335
WB | 50000122 | M008 | KILKIVAN - MURGON NO1 T/LINE | M008_Kilkivan-Murgon No 1 66 kV | Power Factor | 0.97126 | 0.96797 | 0.98509 | 0.97091 | 0.96796 | 0.98534 | 0.9712 | 0.96826 | 0.98555 | 0.97109 | 0.96796 | 0.98534 | 0.9708 | 0.96768 | 0.9851
WB | 50000122 | M008 | KILKIVAN - MURGON NO1 T/LINE | M008_Kilkivan-Murgon No 1 66 kV | Rating (A) | 181 | 252 | 245 | 181 | 252 | 245 | 181 | 252 | 245 | 181 | 252 | 245 | 181 | 252 | 245
WB | 50000122 | M008 | KILKIVAN - MURGON NO1 T/LINE | M008_Kilkivan-Murgon No 1 66 kV | Time | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00
WB | 50000122 | M008 | KILKIVAN - MURGON NO1 T/LINE | M008_Kilkivan-Murgon No 1 66 kV | Voltage at Constrained Conductor | 67.3437 | 67.0643 | 67.4652 | 68.1158 | 68.1382 | 68.6252 | 68.1274 | 68.1494 | 68.6331 | 68.245 | 68.1334 | 68.6264 | 68.2266 | 68.1122 | 68.5803
WB | 50000123 | M009 | KILKIVAN - MURGON NO2 T/LINE | M009_Kilkivan-Murgon No 2 66 kV | % of Rated A | 40.7504 | 31.302 | 20.7199 | 41.2949 | 31.5515 | 20.8528 | 41.0241 | 31.3461 | 20.7216 | 41.2054 | 31.5541 | 20.8524 | 41.4806 | 31.7627 | 20.9957
WB | 50000123 | M009 | KILKIVAN - MURGON NO2 T/LINE | M009_Kilkivan-Murgon No 2 66 kV | Limiting Line Name | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1
WB | 50000123 | M009 | KILKIVAN - MURGON NO2 T/LINE | M009_Kilkivan-Murgon No 2 66 kV | Loading (A) | 67.7805 | 73.672 | 47.4653 | 68.6785 | 74.2462 | 47.7632 | 68.226 | 73.7604 | 47.4635 | 68.5281 | 74.2523 | 47.7622 | 68.988 | 74.7464 | 48.0903
WB | 50000123 | M009 | KILKIVAN - MURGON NO2 T/LINE | M009_Kilkivan-Murgon No 2 66 kV | Loading (MVA) | 7.9061 | 8.5577 | 5.5465 | 8.1027 | 8.7624 | 5.6772 | 8.0507 | 8.7065 | 5.6423 | 8.1003 | 8.7626 | 5.6772 | 8.1524 | 8.8181 | 5.7124
WB | 50000123 | M009 | KILKIVAN - MURGON NO2 T/LINE | M009_Kilkivan-Murgon No 2 66 kV | Loading (MW) | 7.733 | 8.3395 | 5.4992 | 7.9216 | 8.5382 | 5.6297 | 7.8733 | 8.4866 | 5.5962 | 7.9207 | 8.5383 | 5.6297 | 7.9691 | 8.5898 | 5.6632
WB | 50000123 | M009 | KILKIVAN - MURGON NO2 T/LINE | M009_Kilkivan-Murgon No 2 66 kV | Power Factor | 0.97811 | 0.97451 | 0.99148 | 0.97765 | 0.97441 | 0.99163 | 0.97796 | 0.97474 | 0.99184 | 0.97783 | 0.97441 | 0.99163 | 0.97751 | 0.9741 | 0.9914
WB | 50000123 | M009 | KILKIVAN - MURGON NO2 T/LINE | M009_Kilkivan-Murgon No 2 66 kV | Rating (A) | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233
WB | 50000123 | M009 | KILKIVAN - MURGON NO2 T/LINE | M009_Kilkivan-Murgon No 2 66 kV | Time | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00
WB | 50000123 | M009 | KILKIVAN - MURGON NO2 T/LINE | M009_Kilkivan-Murgon No 2 66 kV | Voltage at Constrained Conductor | 67.3437 | 67.0643 | 67.4652 | 68.1158 | 68.1382 | 68.6252 | 68.1274 | 68.1494 | 68.6331 | 68.245 | 68.1334 | 68.6264 | 68.2266 | 68.1122 | 68.5803
WB | 50000131 | M004 | MURGON - KINGAROY T/LINE | M004_Murgon-Kingaroy 66 kV | % of Rated A | 8.3579 | 6.9429 | 5.2073 | 8.3005 | 6.872 | 5.1737 | 8.2986 | 6.8701 | 5.1733 | 8.2909 | 6.8618 | 5.1737 | 8.2932 | 6.8645 | 5.177
WB | 50000131 | M004 | MURGON - KINGAROY T/LINE | M004_Murgon-Kingaroy 66 kV | Limiting Line Name | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1
WB | 50000131 | M004 | MURGON - KINGAROY T/LINE | M004_Murgon-Kingaroy 66 kV | Loading (A) | 14.1248 | 16.5936 | 12.133 | 14.0278 | 16.4242 | 12.0548 | 14.0247 | 16.4195 | 12.0538 | 14.0117 | 16.3998 | 12.0547 | 14.0156 | 16.4062 | 12.0623
WB | 50000131 | M004 | MURGON - KINGAROY T/LINE | M004_Murgon-Kingaroy 66 kV | Loading (MVA) | 1.6029 | 1.8756 | 1.3924 | 1.6099 | 1.8813 | 1.4075 | 1.6102 | 1.8814 | 1.4078 | 1.6113 | 1.8822 | 1.4076 | 1.611 | 1.882 | 1.4073
WB | 50000131 | M004 | MURGON - KINGAROY T/LINE | M004_Murgon-Kingaroy 66 kV | Loading (MW) | 1.4969 | 1.8141 | 1.2236 | 1.4965 | 1.8134 | 1.2234 | 1.4965 | 1.8134 | 1.2234 | 1.4964 | 1.8133 | 1.2234 | 1.4965 | 1.8133 | 1.2232
WB | 50000131 | M004 | MURGON - KINGAROY T/LINE | M004_Murgon-Kingaroy 66 kV | Power Factor | 0.93387 | 0.96719 | 0.87875 | 0.92957 | 0.96395 | 0.86918 | 0.9294 | 0.96384 | 0.86903 | 0.92869 | 0.96337 | 0.86917 | 0.92891 | 0.96352 | 0.86923
WB | 50000131 | M004 | MURGON - KINGAROY T/LINE | M004_Murgon-Kingaroy 66 kV | Rating (A) | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233
WB | 50000131 | M004 | MURGON - KINGAROY T/LINE | M004_Murgon-Kingaroy 66 kV | Time | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00
WB | 50000131 | M004 | MURGON - KINGAROY T/LINE | M004_Murgon-Kingaroy 66 kV | Voltage at Constrained Conductor | 65.5165 | 65.2591 | 66.2594 | 66.2607 | 66.1312 | 67.4124 | 66.2865 | 66.1565 | 67.4295 | 66.3951 | 66.2629 | 67.4137 | 66.3622 | 66.2283 | 67.3575
WB | 50000146 | M003 | KINGAROY - YARRAMAN T/LINE | M003_Kingaroy- Yarraman 66 kV | % of Rated A | 74.0574 | 67.0766 | 46.6778 | 74.0613 | 67.0815 | 46.6846 | 73.3924 | 66.5037 | 46.265 | 74.0237 | 67.0708 | 46.6704 | 74.0655 | 67.0875 | 46.6881
WB | 50000146 | M003 | KINGAROY - YARRAMAN T/LINE | M003_Kingaroy- Yarraman 66 kV | Limiting Line Name | TR_LINE 7742_1 | TR_LINE 7742_1 | TR_LINE 7742_1 | TR_LINE 7742_1 | TR_LINE 7742_1 | TR_LINE 7742_1 | TR_LINE 7742_1 | TR_LINE 7742_1 | TR_LINE 7742_1 | TR_LINE 7742_1 | TR_LINE 7742_1 | TR_LINE 7742_1 | TR_LINE 7742_1 | TR_LINE 7742_1 | TR_LINE 7742_1
WB | 50000146 | M003 | KINGAROY - YARRAMAN T/LINE | M003_Kingaroy- Yarraman 66 kV | Loading (A) | 97.7552 | 112.0174 | 74.2172 | 97.7603 | 112.0255 | 74.228 | 96.8774 | 111.0606 | 73.5608 | 97.7107 | 112.0076 | 74.2054 | 97.7659 | 112.0355 | 74.2335
WB | 50000146 | M003 | KINGAROY - YARRAMAN T/LINE | M003_Kingaroy- Yarraman 66 kV | Loading (MVA) | 10.8096 | 12.3383 | 8.509 | 10.8096 | 12.3383 | 8.509 | 10.7201 | 12.2405 | 8.4368 | 10.8093 | 12.3408 | 8.5089 | 10.8097 | 12.3384 | 8.5091
WB | 50000146 | M003 | KINGAROY - YARRAMAN T/LINE | M003_Kingaroy- Yarraman 66 kV | Loading (MW) | 10.5968 | 12.0733 | 8.3742 | 10.5968 | 12.0733 | 8.3742 | 10.5101 | 11.9753 | 8.304 | 10.5967 | 12.0741 | 8.3742 | 10.5969 | 12.0733 | 8.3742
WB | 50000146 | M003 | KINGAROY - YARRAMAN T/LINE | M003_Kingaroy- Yarraman 66 kV | Power Factor | 0.98032 | 0.97852 | 0.98416 | 0.98031 | 0.97852 | 0.98415 | 0.98041 | 0.97833 | 0.98425 | 0.98033 | 0.97839 | 0.98416 | 0.98031 | 0.97852 | 0.98415
WB | 50000146 | M003 | KINGAROY - YARRAMAN T/LINE | M003_Kingaroy- Yarraman 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
WB | 50000146 | M003 | KINGAROY - YARRAMAN T/LINE | M003_Kingaroy- Yarraman 66 kV | Time | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00
WB | 50000146 | M003 | KINGAROY - YARRAMAN T/LINE | M003_Kingaroy- Yarraman 66 kV | Voltage at Constrained Conductor | 63.8425 | 63.5929 | 66.1931 | 63.8393 | 63.5886 | 66.1839 | 63.8875 | 63.6326 | 66.2175 | 63.87 | 63.6116 | 66.2032 | 63.8359 | 63.5833 | 66.1793
WB | 50000176 | M037 | SOUTH - EAST BUNDABERG T/LINE | M037_South - East Bundaberg 66 kV | % of Rated A | 18.7278 | 12.7478 | 14.6123 | 18.1241 | 12.0206 | 14.1034 | 17.9753 | 12.0302 | 14.1043 | 17.8664 | 12.1454 | 14.2386 | 17.9966 | 12.4076 | 14.3716
WB | 50000176 | M037 | SOUTH - EAST BUNDABERG T/LINE | M037_South - East Bundaberg 66 kV | Limiting Line Name | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1
WB | 50000176 | M037 | SOUTH - EAST BUNDABERG T/LINE | M037_South - East Bundaberg 66 kV | Loading (A) | 42.3248 | 39.6457 | 37.6997 | 40.9604 | 37.3842 | 36.3868 | 40.6241 | 37.4139 | 36.3891 | 40.3781 | 37.7723 | 36.7355 | 40.6722 | 38.5876 | 37.0788
WB | 50000176 | M037 | SOUTH - EAST BUNDABERG T/LINE | M037_South - East Bundaberg 66 kV | Loading (MVA) | 4.8246 | 4.5039 | 4.2392 | 4.6808 | 4.2117 | 4.1326 | 4.6429 | 4.2128 | 4.1328 | 4.6147 | 4.2505 | 4.1705 | 4.646 | 4.3365 | 4.2035
WB | 50000176 | M037 | SOUTH - EAST BUNDABERG T/LINE | M037_South - East Bundaberg 66 kV | Loading (MW) | 4.2803 | 1.0493 | 1.2136 | 4.2866 | 1.0375 | 1.2172 | 4.2437 | 1.0693 | 1.2394 | 4.2086 | 1.1326 | 1.2994 | 4.2452 | 1.17 | 1.3273
WB | 50000176 | M037 | SOUTH - EAST BUNDABERG T/LINE | M037_South - East Bundaberg 66 kV | Power Factor | 0.88718 | 0.23299 | 0.28628 | 0.91578 | 0.24634 | 0.29454 | 0.91402 | 0.25381 | 0.2999 | 0.91202 | 0.26646 | 0.31157 | 0.91374 | 0.2698 | 0.31577
WB | 50000176 | M037 | SOUTH - EAST BUNDABERG T/LINE | M037_South - East Bundaberg 66 kV | Rating (A) | 226 | 311 | 258 | 226 | 311 | 258 | 226 | 311 | 258 | 226 | 311 | 258 | 226 | 311 | 258
WB | 50000176 | M037 | SOUTH - EAST BUNDABERG T/LINE | M037_South - East Bundaberg 66 kV | Time | 12:30 | 18:30 | 22:30 | 12:30 | 18:30 | 22:30 | 12:30 | 18:30 | 22:30 | 12:30 | 18:30 | 22:30 | 12:30 | 18:30 | 22:30
WB | 50000176 | M037 | SOUTH - EAST BUNDABERG T/LINE | M037_South - East Bundaberg 66 kV | Voltage at Constrained Conductor | 65.8121 | 65.5889 | 64.9204 | 65.9774 | 65.0447 | 65.5712 | 65.9846 | 65.0091 | 65.5706 | 65.9834 | 64.9694 | 65.5447 | 65.9502 | 64.883 | 65.4522
WB | 50000182 | M035 | BBERG - STH KOLAN NO2 T/LINE | M035_Bundaberg-South Kolan No 2 66 kV | % of Rated A | 10.0862 | 11.9627 | 11.1235 | 10.014 | 11.9482 | 11.0396 | 10.017 | 11.9557 | 11.0412 | 10.0959 | 12.0383 | 11.1077 | 10.2855 | 12.2761 | 11.2612
WB | 50000182 | M035 | BBERG - STH KOLAN NO2 T/LINE | M035_Bundaberg-South Kolan No 2 66 kV | Limiting Line Name | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1
WB | 50000182 | M035 | BBERG - STH KOLAN NO2 T/LINE | M035_Bundaberg-South Kolan No 2 66 kV | Loading (A) | 55.2361 | 69.1808 | 57.9089 | 54.8424 | 69.0957 | 57.4683 | 54.8584 | 69.1389 | 57.4768 | 55.2889 | 69.6156 | 57.8271 | 56.3278 | 70.9849 | 58.6183
WB | 50000182 | M035 | BBERG - STH KOLAN NO2 T/LINE | M035_Bundaberg-South Kolan No 2 66 kV | Loading (MVA) | 6.3448 | 7.964 | 6.5873 | 6.2974 | 7.9154 | 6.5483 | 6.2975 | 7.9159 | 6.5484 | 6.3452 | 7.9682 | 6.5868 | 6.4592 | 8.0932 | 6.6975
WB | 50000182 | M035 | BBERG - STH KOLAN NO2 T/LINE | M035_Bundaberg-South Kolan No 2 66 kV | Loading (MW) | 6.3421 | 7.9393 | 6.5823 | 6.295 | 7.8901 | 6.5426 | 6.295 | 7.8903 | 6.5426 | 6.3423 | 7.9414 | 6.582 | 6.4562 | 8.0602 | 6.6902
WB | 50000182 | M035 | BBERG - STH KOLAN NO2 T/LINE | M035_Bundaberg-South Kolan No 2 66 kV | Power Factor | 0.99957 | 0.9969 | 0.99924 | 0.99962 | 0.9968 | 0.99912 | 0.99962 | 0.99677 | 0.99912 | 0.99955 | 0.99663 | 0.99928 | 0.99953 | 0.99592 | 0.99891
WB | 50000182 | M035 | BBERG - STH KOLAN NO2 T/LINE | M035_Bundaberg-South Kolan No 2 66 kV | Rating (A) | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521
WB | 50000182 | M035 | BBERG - STH KOLAN NO2 T/LINE | M035_Bundaberg-South Kolan No 2 66 kV | Time | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 18:30 | 22:00
WB | 50000182 | M035 | BBERG - STH KOLAN NO2 T/LINE | M035_Bundaberg-South Kolan No 2 66 kV | Voltage at Constrained Conductor | 66.3188 | 66.4633 | 65.6752 | 66.2951 | 66.1399 | 65.7872 | 66.2769 | 66.1022 | 65.778 | 66.2593 | 66.0838 | 65.7627 | 66.2056 | 65.8257 | 65.9656
WB | 50000183 | M032 | BBERG - STH KOLAN NO1 T/LINE | M032_Bundaberg-South Kolan No 1 66 kV | % of Rated A | 65.0329 | 55.299 | 47.3796 | 64.4143 | 55.2422 | 46.4408 | 64.4325 | 55.2794 | 46.4458 | 65.0929 | 55.8126 | 46.9082 | 66.3016 | 56.9146 | 47.6759
WB | 50000183 | M032 | BBERG - STH KOLAN NO1 T/LINE | M032_Bundaberg-South Kolan No 1 66 kV | Limiting Line Name | TR_LINE 138990_1 | TR_LINE 7401_1 | TR_LINE 138990_1 | TR_LINE 138990_1 | TR_LINE 7401_1 | TR_LINE 138990_1 | TR_LINE 138990_1 | TR_LINE 7401_1 | TR_LINE 138990_1 | TR_LINE 138990_1 | TR_LINE 7401_1 | TR_LINE 138990_1 | TR_LINE 138990_1 | TR_LINE 7401_1 | TR_LINE 138990_1
WB | 50000183 | M032 | BBERG - STH KOLAN NO1 T/LINE | M032_Bundaberg-South Kolan No 1 66 kV | Loading (A) | 85.8434 | 97.8777 | 80.5453 | 85.0269 | 97.7729 | 78.9494 | 85.0508 | 97.8382 | 78.9579 | 85.9227 | 98.7781 | 79.744 | 87.5181 | 100.7185 | 81.049
WB | 50000183 | M032 | BBERG - STH KOLAN NO1 T/LINE | M032_Bundaberg-South Kolan No 1 66 kV | Loading (MVA) | 9.8402 | 11.2401 | 9.1491 | 9.7434 | 11.1407 | 9.0578 | 9.7434 | 11.1411 | 9.0578 | 9.8404 | 11.246 | 9.145 | 10.0146 | 11.45 | 9.2839
WB | 50000183 | M032 | BBERG - STH KOLAN NO1 T/LINE | M032_Bundaberg-South Kolan No 1 66 kV | Loading (MW) | 9.8361 | 11.2401 | 9.1209 | 9.7384 | 11.1406 | 9.027 | 9.7385 | 11.1409 | 9.027 | 9.8365 | 11.2456 | 9.1169 | 10.0105 | 11.4485 | 9.2606
WB | 50000183 | M032 | BBERG - STH KOLAN NO1 T/LINE | M032_Bundaberg-South Kolan No 1 66 kV | Power Factor | 0.99958 | 1 | 0.99692 | 0.99948 | 0.99999 | 0.9966 | 0.99949 | 0.99999 | 0.9966 | 0.9996 | 0.99997 | 0.99693 | 0.99959 | 0.99987 | 0.99749
WB | 50000183 | M032 | BBERG - STH KOLAN NO1 T/LINE | M032_Bundaberg-South Kolan No 1 66 kV | Rating (A) | 132 | 177 | 170 | 132 | 177 | 170 | 132 | 177 | 170 | 132 | 177 | 170 | 132 | 177 | 170
WB | 50000183 | M032 | BBERG - STH KOLAN NO1 T/LINE | M032_Bundaberg-South Kolan No 1 66 kV | Time | 16:30 | 18:00 | 22:30 | 16:30 | 18:00 | 22:30 | 16:30 | 18:00 | 22:30 | 16:30 | 18:00 | 22:30 | 16:30 | 18:00 | 22:30
WB | 50000183 | M032 | BBERG - STH KOLAN NO1 T/LINE | M032_Bundaberg-South Kolan No 1 66 kV | Voltage at Constrained Conductor | 66.1815 | 66.3018 | 65.5813 | 66.1595 | 65.7858 | 66.2391 | 66.1413 | 65.7443 | 66.2317 | 66.1217 | 65.732 | 66.2105 | 66.0653 | 65.6349 | 66.1335
WB | 50000197 | M014 | TORQUAY - PIALBA T/LINE | M014_Torquay-Pialba 66 kV | % of Rated A | 19.7085 | 13.8766 | 16.7928 | 19.1102 | 13.3942 | 16.3428 | 18.8626 | 13.1947 | 16.1563 | 18.6513 | 13.002 | 16.0163
WB | 50000197 | M014 | TORQUAY - PIALBA T/LINE | M014_Torquay-Pialba 66 kV | Limiting Line Name | TR_LINE 7168_1 | TR_LINE 7168_1 | TR_LINE 7168_1 | TR_LINE 7168_1 | TR_LINE 7168_1 | TR_LINE 7168_1 | TR_LINE 7168_1 | TR_LINE 7168_1 | TR_LINE 7168_1 | TR_LINE 7168_1 | TR_LINE 7168_1 | TR_LINE 7168_1
WB | 50000197 | M014 | TORQUAY - PIALBA T/LINE | M014_Torquay-Pialba 66 kV | Loading (A) | 119.8279 | 93.2505 | 92.5286 | 116.1897 | 90.0089 | 90.0487 | 114.6848 | 88.6683 | 89.0211 | 113.4002 | 87.3732 | 88.2499
WB | 50000197 | M014 | TORQUAY - PIALBA T/LINE | M014_Torquay-Pialba 66 kV | Loading (MVA) | 13.6875 | 10.5655 | 10.7737 | 13.2561 | 10.2276 | 10.4916 | 13.0686 | 10.0618 | 10.3663 | 12.9141 | 9.9056 | 10.2737
WB | 50000197 | M014 | TORQUAY - PIALBA T/LINE | M014_Torquay-Pialba 66 kV | Loading (MW) | 13.1777 | 9.5769 | 10.1515 | 12.7154 | 9.168 | 9.8393 | 12.5143 | 8.9738 | 9.7015 | 12.3444 | 8.7803 | 9.5974
WB | 50000197 | M014 | TORQUAY - PIALBA T/LINE | M014_Torquay-Pialba 66 kV | Power Factor | 0.96275 | 0.90644 | 0.94225 | 0.95921 | 0.8964 | 0.93782 | 0.95758 | 0.89188 | 0.93587 | 0.95589 | 0.8864 | 0.93417
WB | 50000197 | M014 | TORQUAY - PIALBA T/LINE | M014_Torquay-Pialba 66 kV | Rating (A) | 608 | 672 | 551 | 608 | 672 | 551 | 608 | 672 | 551 | 608 | 672 | 551
WB | 50000197 | M014 | TORQUAY - PIALBA T/LINE | M014_Torquay-Pialba 66 kV | Time | 16:00 | 17:00 | 8:30 | 16:00 | 17:00 | 8:30 | 16:00 | 17:00 | 8:30 | 16:00 | 17:00 | 8:30
WB | 50000197 | M014 | TORQUAY - PIALBA T/LINE | M014_Torquay-Pialba 66 kV | Voltage at Constrained Conductor | 65.9488 | 65.4151 | 67.2244 | 65.8699 | 65.6036 | 67.2675 | 65.7905 | 65.5156 | 67.2312 | 65.749 | 65.4549 | 67.2128
WB | 50000200 | M039 | BBERG - WST BBERG NO1 T/LINE | M039_Bundaberg-West Bundaberg No 1 66 kV | % of Rated A | 39.6338 | 36.6175 | 38.0853 | 39.085 | 36.4434 | 37.1498 | 38.755 | 36.1439 | 36.8659 | 38.7848 | 36.1921 | 36.9301 | 39.1215 | 36.5301 | 37.2678
WB | 50000200 | M039 | BBERG - WST BBERG NO1 T/LINE | M039_Bundaberg-West Bundaberg No 1 66 kV | Limiting Line Name | TR_LINE 200241_1 | TR_LINE 200241_1 | TR_LINE 200241_1 | TR_LINE 7853_1 | TR_LINE 7876_1 | TR_LINE 200241_1 | TR_LINE 200241_1 | TR_LINE 7876_1 | TR_LINE 200241_1 | TR_LINE 200241_1 | TR_LINE 7876_1 | TR_LINE 200241_1 | TR_LINE 200241_1 | TR_LINE 7876_1 | TR_LINE 200241_1
WB | 50000200 | M039 | BBERG - WST BBERG NO1 T/LINE | M039_Bundaberg-West Bundaberg No 1 66 kV | Loading (A) | 319.4486 | 330.6563 | 283.7355 | 315.0249 | 329.0839 | 276.7661 | 312.3649 | 326.3795 | 274.651 | 312.6057 | 326.8148 | 275.1291 | 315.3189 | 329.8666 | 277.6448
WB | 50000200 | M039 | BBERG - WST BBERG NO1 T/LINE | M039_Bundaberg-West Bundaberg No 1 66 kV | Loading (MVA) | 36.7516 | 38.1646 | 32.3501 | 36.2101 | 37.5913 | 31.8681 | 35.9134 | 37.2715 | 31.621 | 35.9324 | 37.3083 | 31.6675 | 36.216 | 37.6075 | 31.9238
WB | 50000200 | M039 | BBERG - WST BBERG NO1 T/LINE | M039_Bundaberg-West Bundaberg No 1 66 kV | Loading (MW) | 36.7029 | 38.1322 | 32.1819 | 36.2101 | 37.591 | 31.8104 | 35.9134 | 37.2715 | 31.5568 | 35.9323 | 37.3082 | 31.6045 | 36.216 | 37.6071 | 31.8679
WB | 50000200 | M039 | BBERG - WST BBERG NO1 T/LINE | M039_Bundaberg-West Bundaberg No 1 66 kV | Power Factor | 0.99867 | 0.99915 | 0.9948 | 1 | 0.99999 | 0.99819 | 1 | 1 | 0.99797 | 1 | 1 | 0.99801 | 1 | 0.99999 | 0.99825
WB | 50000200 | M039 | BBERG - WST BBERG NO1 T/LINE | M039_Bundaberg-West Bundaberg No 1 66 kV | Rating (A) | 806 | 903 | 745 | 806 | 903 | 745 | 806 | 903 | 745 | 806 | 903 | 745 | 806 | 903 | 745
WB | 50000200 | M039 | BBERG - WST BBERG NO1 T/LINE | M039_Bundaberg-West Bundaberg No 1 66 kV | Time | 16:30 | 17:00 | 22:30 | 16:30 | 17:00 | 22:30 | 16:30 | 17:00 | 22:30 | 16:30 | 17:00 | 22:30 | 16:30 | 17:00 | 22:30
WB | 50000200 | M039 | BBERG - WST BBERG NO1 T/LINE | M039_Bundaberg-West Bundaberg No 1 66 kV | Voltage at Constrained Conductor | 66.4225 | 66.6382 | 65.8266 | 66.3627 | 65.9507 | 66.4786 | 66.3795 | 65.9316 | 66.4713 | 66.3633 | 65.9087 | 66.4533 | 66.3117 | 65.8227 | 66.3842
WB | 50000201 | M040 | B'BERG - WEST B'BERG NO2 T/LINE | M040_Bundaberg-West Bundaberg No 2 66 kV | % of Rated A | 38.1601 | 35.256 | 36.6694 | 37.6315 | 35.0881 | 35.7686 | 37.3137 | 34.7998 | 35.4952 | 37.3425 | 34.8462 | 35.557 | 37.6666 | 35.1716 | 35.8821
WB | 50000201 | M040 | B'BERG - WEST B'BERG NO2 T/LINE | M040_Bundaberg-West Bundaberg No 2 66 kV | Limiting Line Name | TR_LINE 169764_1 | TR_LINE 169764_1 | TR_LINE 169764_1 | TR_LINE 169764_1 | TR_LINE 169764_1 | TR_LINE 169764_1 | TR_LINE 169764_1 | TR_LINE 169764_1 | TR_LINE 169764_1 | TR_LINE 169764_1 | TR_LINE 169764_1 | TR_LINE 169764_1 | TR_LINE 169764_1 | TR_LINE 169764_1 | TR_LINE 169764_1
WB | 50000201 | M040 | B'BERG - WEST B'BERG NO2 T/LINE | M040_Bundaberg-West Bundaberg No 2 66 kV | Loading (A) | 307.5707 | 318.3613 | 273.1874 | 303.3096 | 316.843 | 266.4758 | 300.7488 | 314.2404 | 264.4395 | 300.9806 | 314.6594 | 264.8997 | 303.5929 | 317.5965 | 267.3217
WB | 50000201 | M040 | B'BERG - WEST B'BERG NO2 T/LINE | M040_Bundaberg-West Bundaberg No 2 66 kV | Loading (MVA) | 35.3851 | 36.7455 | 31.1474 | 34.8818 | 36.271 | 30.6832 | 34.5779 | 35.961 | 30.4454 | 34.5961 | 35.9967 | 30.4901 | 34.8692 | 36.2872 | 30.7369
WB | 50000201 | M040 | B'BERG - WEST B'BERG NO2 T/LINE | M040_Bundaberg-West Bundaberg No 2 66 kV | Loading (MW) | 35.3377 | 36.7139 | 30.9847 | 34.8817 | 36.2686 | 30.6272 | 34.5779 | 35.9598 | 30.383 | 34.5961 | 35.9953 | 30.4289 | 34.8692 | 36.2845 | 30.6825
WB | 50000201 | M040 | B'BERG - WEST B'BERG NO2 T/LINE | M040_Bundaberg-West Bundaberg No 2 66 kV | Power Factor | 0.99866 | 0.99914 | 0.99477 | 1 | 0.99993 | 0.99818 | 1 | 0.99997 | 0.99795 | 1 | 0.99996 | 0.99799 | 1 | 0.99993 | 0.99823
WB | 50000201 | M040 | B'BERG - WEST B'BERG NO2 T/LINE | M040_Bundaberg-West Bundaberg No 2 66 kV | Rating (A) | 806 | 903 | 745 | 806 | 903 | 745 | 806 | 903 | 745 | 806 | 903 | 745 | 806 | 903 | 745
WB | 50000201 | M040 | B'BERG - WEST B'BERG NO2 T/LINE | M040_Bundaberg-West Bundaberg No 2 66 kV | Time | 16:30 | 17:00 | 22:30 | 16:30 | 17:00 | 22:30 | 16:30 | 17:00 | 22:30 | 16:30 | 17:00 | 22:30 | 16:30 | 17:00 | 22:30
WB | 50000201 | M040 | B'BERG - WEST B'BERG NO2 T/LINE | M040_Bundaberg-West Bundaberg No 2 66 kV | Voltage at Constrained Conductor | 66.4225 | 66.6382 | 65.8266 | 66.3975 | 66.093 | 66.4786 | 66.3795 | 66.0707 | 66.4713 | 66.3633 | 66.0482 | 66.4533 | 66.3117 | 65.9656 | 66.3842
WB | 50016424 | 764 | 764 WOOLOOGA - KILKIVAN NO1 T/LINE | 764_Woolooga-Kilkivan No 1 132 kV | % of Rated A | 14.5619 | 9.8726 | 6.3499 | 21.5184 | 14.1053 | 7.9404 | 21.5772 | 14.1636 | 7.9724 | 21.1973 | 14.3075 | 8.0619 | 21.4497 | 14.4886 | 8.2262
WB | 50016424 | 764 | 764 WOOLOOGA - KILKIVAN NO1 T/LINE | 764_Woolooga-Kilkivan No 1 132 kV | Limiting Line Name | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1
WB | 50016424 | 764 | 764 WOOLOOGA - KILKIVAN NO1 T/LINE | 764_Woolooga-Kilkivan No 1 132 kV | Loading (A) | 36.1134 | 39.0957 | 24.955 | 53.3657 | 55.8569 | 31.2056 | 53.5113 | 56.088 | 31.3316 | 52.5694 | 56.6578 | 31.6832 | 53.1952 | 57.3747 | 32.3289
WB | 50016424 | 764 | 764 WOOLOOGA - KILKIVAN NO1 T/LINE | 764_Woolooga-Kilkivan No 1 132 kV | Loading (MVA) | 8.651 | 9.3629 | 5.9837 | 12.7706 | 13.3656 | 7.4786 | 12.8056 | 13.421 | 7.5088 | 12.5824 | 13.5568 | 7.5929 | 12.7316 | 13.7276 | 7.747
WB | 50016424 | 764 | 764 WOOLOOGA - KILKIVAN NO1 T/LINE | 764_Woolooga-Kilkivan No 1 132 kV | Loading (MW) | 8.2414 | 8.8566 | 5.8509 | 12.255 | 12.8786 | 7.2064 | 12.3016 | 12.9456 | 7.2445 | 12.1702 | 13.0733 | 7.3261 | 12.3091 | 13.2304 | 7.4466
WB | 50016424 | 764 | 764 WOOLOOGA - KILKIVAN NO1 T/LINE | 764_Woolooga-Kilkivan No 1 132 kV | Power Factor | 0.95266 | 0.94593 | 0.97779 | 0.95962 | 0.96356 | 0.9636 | 0.96064 | 0.96458 | 0.9648 | 0.96724 | 0.96434 | 0.96487 | 0.96681 | 0.96378 | 0.96122
WB | 50016424 | 764 | 764 WOOLOOGA - KILKIVAN NO1 T/LINE | 764_Woolooga-Kilkivan No 1 132 kV | Rating (A) | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393
WB | 50016424 | 764 | 764 WOOLOOGA - KILKIVAN NO1 T/LINE | 764_Woolooga-Kilkivan No 1 132 kV | Time | 16:30 | 18:30 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00
WB | 50016424 | 764 | 764 WOOLOOGA - KILKIVAN NO1 T/LINE | 764_Woolooga-Kilkivan No 1 132 kV | Voltage at Constrained Conductor | 138.3048 | 138.2674 | 138.4378 | 138.1624 | 138.1503 | 138.3646 | 138.1635 | 138.151 | 138.3652 | 138.1882 | 138.1454 | 138.3623 | 138.1818 | 138.1377 | 138.3513
WB | 50016425 | 765 | 765 WOOLOOGA - KILKIVAN NO2 T/LINE | 765_Woolooga-Kilkivan No 2 132 kV | % of Rated A | 14.5609 | 9.872 | 6.3495 | 21.5183 | 14.1052 | 7.9403 | 21.577 | 14.1635 | 7.9724 | 21.1972 | 14.3074 | 8.0618 | 21.4496 | 14.4885 | 8.2261
WB | 50016425 | 765 | 765 WOOLOOGA - KILKIVAN NO2 T/LINE | 765_Woolooga-Kilkivan No 2 132 kV | Limiting Line Name | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1
WB | 50016425 | 765 | 765 WOOLOOGA - KILKIVAN NO2 T/LINE | 765_Woolooga-Kilkivan No 2 132 kV | Loading (A) | 36.1111 | 39.0932 | 24.9534 | 53.3653 | 55.8566 | 31.2054 | 53.511 | 56.0876 | 31.3314 | 52.5691 | 56.6575 | 31.683 | 53.1949 | 57.3743 | 32.3286
WB | 50016425 | 765 | 765 WOOLOOGA - KILKIVAN NO2 T/LINE | 765_Woolooga-Kilkivan No 2 132 kV | Loading (MVA) | 8.6505 | 9.3623 | 5.9834 | 12.7705 | 13.3655 | 7.4785 | 12.8055 | 13.4209 | 7.5087 | 12.5824 | 13.5567 | 7.5929 | 12.7315 | 13.7275 | 7.747
WB | 50016425 | 765 | 765 WOOLOOGA - KILKIVAN NO2 T/LINE | 765_Woolooga-Kilkivan No 2 132 kV | Loading (MW) | 8.2409 | 8.856 | 5.8505 | 12.2549 | 12.8785 | 7.2063 | 12.3015 | 12.9455 | 7.2444 | 12.1702 | 13.0732 | 7.3261 | 12.309 | 13.2303 | 7.4466
WB | 50016425 | 765 | 765 WOOLOOGA - KILKIVAN NO2 T/LINE | 765_Woolooga-Kilkivan No 2 132 kV | Power Factor | 0.95265 | 0.94593 | 0.97779 | 0.95962 | 0.96356 | 0.9636 | 0.96064 | 0.96458 | 0.9648 | 0.96724 | 0.96434 | 0.96487 | 0.96681 | 0.96378 | 0.96122
WB | 50016425 | 765 | 765 WOOLOOGA - KILKIVAN NO2 T/LINE | 765_Woolooga-Kilkivan No 2 132 kV | Rating (A) | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393
WB | 50016425 | 765 | 765 WOOLOOGA - KILKIVAN NO2 T/LINE | 765_Woolooga-Kilkivan No 2 132 kV | Time | 16:30 | 18:30 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00
WB | 50016425 | 765 | 765 WOOLOOGA - KILKIVAN NO2 T/LINE | 765_Woolooga-Kilkivan No 2 132 kV | Voltage at Constrained Conductor | 138.3048 | 138.2674 | 138.4378 | 138.1624 | 138.1502 | 138.3645 | 138.1635 | 138.1509 | 138.3652 | 138.1882 | 138.1453 | 138.3623 | 138.1817 | 138.1376 | 138.3513
WB | 50021248 | 7204 | 7204 BUNDABERG - CLAYTON T/LINE | 7204_Bundaberg - Clayton 132 kV | % of Rated A | 1.3268 | 0.88027 | 1.0596 | 1.3373 | 0.8863 | 1.067 | 1.3374 | 0.88665 | 1.0671 | 1.3374 | 0.88679 | 1.0672 | 1.3377 | 0.88712 | 1.0673
WB | 50021248 | 7204 | 7204 BUNDABERG - CLAYTON T/LINE | 7204_Bundaberg - Clayton 132 kV | Limiting Line Name | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1
WB | 50021248 | 7204 | 7204 BUNDABERG - CLAYTON T/LINE | 7204_Bundaberg - Clayton 132 kV | Loading (A) | 11.7558 | 8.6355 | 8.8904 | 11.8487 | 8.6946 | 8.9519 | 11.8495 | 8.698 | 8.9533 | 11.8497 | 8.6994 | 8.9537 | 11.852 | 8.7027 | 8.9548
WB | 50021248 | 7204 | 7204 BUNDABERG - CLAYTON T/LINE | 7204_Bundaberg - Clayton 132 kV | Loading (MVA) | 2.8039 | 2.0404 | 2.1207 | 2.7994 | 2.0358 | 2.116 | 2.7993 | 2.0355 | 2.1159 | 2.7993 | 2.0354 | 2.1158 | 2.7992 | 2.0351 | 2.1158
WB | 50021248 | 7204 | 7204 BUNDABERG - CLAYTON T/LINE | 7204_Bundaberg - Clayton 132 kV | Loading (MW) | 2.4466 | 1.7192 | 1.7919 | 2.4466 | 1.7192 | 1.7919 | 2.4466 | 1.7192 | 1.7919 | 2.4466 | 1.7192 | 1.7919 | 2.4466 | 1.7192 | 1.7919
WB | 50021248 | 7204 | 7204 BUNDABERG - CLAYTON T/LINE | 7204_Bundaberg - Clayton 132 kV | Power Factor | 0.87259 | 0.84258 | 0.84495 | 0.87398 | 0.84451 | 0.84683 | 0.87399 | 0.84462 | 0.84688 | 0.874 | 0.84466 | 0.84689 | 0.87403 | 0.84477 | 0.84692
WB | 50021248 | 7204 | 7204 BUNDABERG - CLAYTON T/LINE | 7204_Bundaberg - Clayton 132 kV | Rating (A) | 886 | 981 | 839 | 886 | 981 | 839 | 886 | 981 | 839 | 886 | 981 | 839 | 886 | 981 | 839
WB | 50021248 | 7204 | 7204 BUNDABERG - CLAYTON T/LINE | 7204_Bundaberg - Clayton 132 kV | Time | 10:00 | 21:00 | 5:30 | 10:00 | 21:00 | 5:30 | 10:00 | 21:00 | 5:30 | 10:00 | 21:00 | 5:30 | 10:00 | 21:00 | 5:30
WB | 50021248 | 7204 | 7204 BUNDABERG - CLAYTON T/LINE | 7204_Bundaberg - Clayton 132 kV | Voltage at Constrained Conductor | 137.7021 | 136.4186 | 137.7205 | 136.4045 | 135.182 | 136.4707 | 136.3943 | 135.1106 | 136.442 | 136.3907 | 135.0831 | 136.4328 | 136.359 | 135.0149 | 136.4106
WB | 50021251 | M045 | TARONG - PACIFIC COAL T/LINE | M045_Tarong-Pacific Coal 66 kV | % of Rated A | 52.5644 | 39.7102 | 44.8068 | 52.5649 | 39.7108 | 44.8038 | 52.5637 | 39.7088 | 44.8031 | 52.5633 | 39.709 | 44.8031 | 52.5664 | 39.7126 | 44.8044
WB | 50021251 | M045 | TARONG - PACIFIC COAL T/LINE | M045_Tarong-Pacific Coal 66 kV | Limiting Line Name | TR_LINE 7237_1 | TR_LINE 7237_1 | TR_LINE 7237_1 | TR_LINE 7237_1 | TR_LINE 7237_1 | TR_LINE 7237_1 | TR_LINE 7237_1 | TR_LINE 7237_1 | TR_LINE 7237_1 | TR_LINE 7237_1 | TR_LINE 7237_1 | TR_LINE 7237_1 | TR_LINE 7237_1 | TR_LINE 7237_1 | TR_LINE 7237_1
WB | 50021251 | M045 | TARONG - PACIFIC COAL T/LINE | M045_Tarong-Pacific Coal 66 kV | Loading (A) | 70.3649 | 71.8045 | 78.3409 | 70.3655 | 71.8055 | 78.3357 | 70.364 | 71.802 | 78.3344 | 70.3634 | 71.8023 | 78.3344 | 70.3675 | 71.8088 | 78.3366
WB | 50021251 | M045 | TARONG - PACIFIC COAL T/LINE | M045_Tarong-Pacific Coal 66 kV | Loading (MVA) | 8.4069 | 8.5322 | 9.311 | 8.4069 | 8.5322 | 9.311 | 8.4069 | 8.5322 | 9.311 | 8.4069 | 8.5322 | 9.311 | 8.4069 | 8.5322 | 9.311
WB | 50021251 | M045 | TARONG - PACIFIC COAL T/LINE | M045_Tarong-Pacific Coal 66 kV | Loading (MW) | 7.9165 | 8.0343 | 8.7666 | 7.9165 | 8.0343 | 8.7666 | 7.9165 | 8.0343 | 8.7666 | 7.9165 | 8.0343 | 8.7666 | 7.9165 | 8.0343 | 8.7666
WB | 50021251 | M045 | TARONG - PACIFIC COAL T/LINE | M045_Tarong-Pacific Coal 66 kV | Power Factor | 0.94167 | 0.94164 | 0.94153 | 0.94167 | 0.94164 | 0.94153 | 0.94167 | 0.94164 | 0.94153 | 0.94167 | 0.94164 | 0.94153 | 0.94167 | 0.94164 | 0.94153
WB | 50021251 | M045 | TARONG - PACIFIC COAL T/LINE | M045_Tarong-Pacific Coal 66 kV | Rating (A) | 134 | 181 | 175 | 134 | 181 | 175 | 134 | 181 | 175 | 134 | 181 | 175 | 134 | 181 | 175
WB | 50021251 | M045 | TARONG - PACIFIC COAL T/LINE | M045_Tarong-Pacific Coal 66 kV | Time | 9:00 | 20:00 | 3:00 | 9:00 | 20:00 | 3:00 | 9:00 | 20:00 | 3:00 | 9:00 | 20:00 | 3:00 | 9:00 | 20:00 | 3:00
WB | 50021251 | M045 | TARONG - PACIFIC COAL T/LINE | M045_Tarong-Pacific Coal 66 kV | Voltage at Constrained Conductor | 68.9792 | 68.6043 | 68.6192 | 68.9786 | 68.6033 | 68.6237 | 68.9801 | 68.6067 | 68.6248 | 68.9807 | 68.6064 | 68.6248 | 68.9767 | 68.6002 | 68.6229
WB | 50078755 | M028 | CHILDERS - GAYNDAH T/LINE | M028_Childers - Gayndah 66 kV | % of Rated A | 61.4144 | 49.6841 | 38.2993
WB | 50078755 | M028 | CHILDERS - GAYNDAH T/LINE | M028_Childers - Gayndah 66 kV | Limiting Line Name | TR_LINE 12103276_2 | TR_LINE 12103276_2 | TR_LINE 12103276_2
WB | 50078755 | M028 | CHILDERS - GAYNDAH T/LINE | M028_Childers - Gayndah 66 kV | Loading (A) | 81.067 | 82.9724 | 60.8958
WB | 50078755 | M028 | CHILDERS - GAYNDAH T/LINE | M028_Childers - Gayndah 66 kV | Loading (MVA) | 9.2274 | 9.4948 | 6.9847
WB | 50078755 | M028 | CHILDERS - GAYNDAH T/LINE | M028_Childers - Gayndah 66 kV | Loading (MW) | 9.125 | 9.406 | 6.7232
WB | 50078755 | M028 | CHILDERS - GAYNDAH T/LINE | M028_Childers - Gayndah 66 kV | Power Factor | 0.9889 | 0.99065 | 0.96257
WB | 50078755 | M028 | CHILDERS - GAYNDAH T/LINE | M028_Childers - Gayndah 66 kV | Rating (A) | 132 | 167 | 159
WB | 50078755 | M028 | CHILDERS - GAYNDAH T/LINE | M028_Childers - Gayndah 66 kV | Time | 16:30 | 18:30 | 7:00
WB | 50078755 | M028 | CHILDERS - GAYNDAH T/LINE | M028_Childers - Gayndah 66 kV | Voltage at Constrained Conductor | 65.7165 | 66.0681 | 66.2211
WB | 50078756 | 6205 | EAST B'BERG - B'BERG CENTRAL | 6205_East Bundaberg-BUCE 66 kV | % of Rated A | 36.3184 | 42.84 | 52.0771 | 36.1737 | 42.906 | 51.2804 | 36.2714 | 42.9937 | 51.3354 | 36.6195 | 43.3538 | 51.7455 | 37.2608 | 44.1063 | 52.6158
WB | 50078756 | 6205 | EAST B'BERG - B'BERG CENTRAL | 6205_East Bundaberg-BUCE 66 kV | Limiting Line Name | TR_LINE 7315_1 | TR_LINE 7315_1 | TR_LINE 7315_1 | TR_LINE 176527_1 | TR_LINE 7315_1 | TR_LINE 7315_1 | TR_LINE 176527_1 | TR_LINE 7315_1 | TR_LINE 7315_1 | TR_LINE 176527_1 | TR_LINE 7315_1 | TR_LINE 7315_1 | TR_LINE 176527_1 | TR_LINE 7315_1 | TR_LINE 7315_1
WB | 50078756 | 6205 | EAST B'BERG - B'BERG CENTRAL | 6205_East Bundaberg-BUCE 66 kV | Loading (A) | 144.1832 | 186.78 | 185.3926 | 143.6097 | 187.0693 | 182.5577 | 143.9974 | 187.4519 | 182.7534 | 145.3794 | 189.0219 | 184.2134 | 147.9255 | 192.3024 | 187.3114
WB | 50078756 | 6205 | EAST B'BERG - B'BERG CENTRAL | 6205_East Bundaberg-BUCE 66 kV | Loading (MVA) | 16.3896 | 21.2755 | 20.9011 | 16.3575 | 21.1291 | 20.7852 | 16.3994 | 21.1609 | 20.8073 | 16.5524 | 21.3259 | 20.9659 | 16.8266 | 21.6685 | 21.2892
WB | 50078756 | 6205 | EAST B'BERG - B'BERG CENTRAL | 6205_East Bundaberg-BUCE 66 kV | Loading (MW) | 16.3869 | 21.2323 | 20.8732 | 16.3521 | 21.1242 | 20.7828 | 16.394 | 21.156 | 20.8051 | 16.5479 | 21.3201 | 20.9631 | 16.8242 | 21.6596 | 21.2851
WB | 50078756 | 6205 | EAST B'BERG - B'BERG CENTRAL | 6205_East Bundaberg-BUCE 66 kV | Power Factor | 0.99984 | 0.99797 | 0.99867 | 0.99967 | 0.99977 | 0.99989 | 0.99967 | 0.99977 | 0.99989 | 0.99973 | 0.99973 | 0.99987 | 0.99986 | 0.99959 | 0.99981
WB | 50078756 | 6205 | EAST B'BERG - B'BERG CENTRAL | 6205_East Bundaberg-BUCE 66 kV | Rating (A) | 397 | 436 | 356 | 397 | 436 | 356 | 397 | 436 | 356 | 397 | 436 | 356 | 397 | 436 | 356
WB | 50078756 | 6205 | EAST B'BERG - B'BERG CENTRAL | 6205_East Bundaberg-BUCE 66 kV | Time | 16:30 | 18:30 | 22:30 | 16:30 | 18:30 | 22:30 | 16:30 | 18:30 | 22:30 | 16:30 | 18:30 | 22:30 | 16:30 | 18:30 | 22:30
WB | 50078756 | 6205 | EAST B'BERG - B'BERG CENTRAL | 6205_East Bundaberg-BUCE 66 kV | Voltage at Constrained Conductor | 65.6285 | 65.7641 | 65.0902 | 65.7615 | 65.2105 | 65.7345 | 65.7525 | 65.1754 | 65.734 | 65.735 | 65.1379 | 65.7102 | 65.6739 | 65.0555 | 65.6198
WB | 50079711 | M010 | MARYBOROUGH - OWANYILLA T/LINE | M010_Maryborough - Owanyilla 66 kV | % of Rated A | 48.4878 | 33.6657 | 18.5375 | 19.1744 | 14.5503 | 13.0101 | 20.1477 | 15.2975 | 13.1707 | 23.5243 | 16.5924 | 13.5405 | 23.5992 | 16.6563 | 13.5267
WB | 50079711 | M010 | MARYBOROUGH - OWANYILLA T/LINE | M010_Maryborough - Owanyilla 66 kV | Limiting Line Name | TR_LINE 199621_1 | TR_LINE 199621_1 | TR_LINE 7259_1 | TR_LINE 199621_1 | TR_LINE 199621_1 | TR_LINE 7259_1 | TR_LINE 199621_1 | TR_LINE 199621_1 | TR_LINE 7259_1 | TR_LINE 199621_1 | TR_LINE 199621_1 | TR_LINE 7259_1 | TR_LINE 199621_1 | TR_LINE 199621_1 | TR_LINE 7259_1
WB | 50079711 | M010 | MARYBOROUGH - OWANYILLA T/LINE | M010_Maryborough - Owanyilla 66 kV | Loading (A) | 120.7288 | 128.597 | 68.5847 | 47.7442 | 55.5823 | 48.1375 | 50.1677 | 58.4366 | 48.7317 | 58.5755 | 63.3831 | 50.1 | 58.762 | 63.6271 | 50.0489
WB | 50079711 | M010 | MARYBOROUGH - OWANYILLA T/LINE | M010_Maryborough - Owanyilla 66 kV | Loading (MVA) | 14.0213 | 14.9375 | 8.0579 | 5.5312 | 6.4912 | 5.6675 | 5.8038 | 6.8129 | 5.7344 | 6.8523 | 7.4161 | 5.92 | 6.8667 | 7.4361 | 5.9113
WB | 50079711 | M010 | MARYBOROUGH - OWANYILLA T/LINE | M010_Maryborough - Owanyilla 66 kV | Loading (MW) | 13.6065 | 14.4626 | 7.974 | 5.4551 | 6.2075 | 5.0489 | 5.6952 | 6.4689 | 5.1723 | 6.5547 | 7.0724 | 5.7656 | 6.5586 | 7.0796 | 5.7634
WB | 50079711 | M010 | MARYBOROUGH - OWANYILLA T/LINE | M010_Maryborough - Owanyilla 66 kV | Power Factor | 0.97042 | 0.96821 | 0.98959 | 0.98623 | 0.95629 | 0.89085 | 0.98128 | 0.94951 | 0.90198 | 0.95658 | 0.95366 | 0.97391 | 0.95513 | 0.95206 | 0.97498
WB | 50079711 | M010 | MARYBOROUGH - OWANYILLA T/LINE | M010_Maryborough - Owanyilla 66 kV | Rating (A) | 249 | 382 | 370 | 249 | 382 | 370 | 249 | 382 | 370 | 249 | 382 | 370 | 249 | 382 | 370
WB | 50079711 | M010 | MARYBOROUGH - OWANYILLA T/LINE | M010_Maryborough - Owanyilla 66 kV | Time | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 0:30 | 16:30 | 18:00 | 0:30 | 16:30 | 19:00 | 23:30 | 16:30 | 19:00 | 23:30
WB | 50079711 | M010 | MARYBOROUGH - OWANYILLA T/LINE | M010_Maryborough - Owanyilla 66 kV | Voltage at Constrained Conductor | 67.0527 | 67.0636 | 67.8316 | 66.8869 | 67.4262 | 67.975 | 66.7929 | 67.3109 | 67.9381 | 67.5393 | 67.5522 | 68.2221 | 67.4666 | 67.475 | 68.1916
WB | 50079712 | M011 | KILKIVAN-MARYBOROUGH | M011_Kilkivan-Maryborough 66 kV | % of Rated A | 34.1999 | 28.281 | 12.9266 | 51.3185 | 41.6732 | 19.0109 | 52.4291 | 42.6692 | 19.4256 | 49.1334 | 43.3938 | 19.7955 | 50.3375 | 44.4662 | 18.9427
WB | 50079712 | M011 | KILKIVAN-MARYBOROUGH | M011_Kilkivan-Maryborough 66 kV | Limiting Line Name | TR_LINE 33838_1 | TR_LINE 33838_1 | TR_LINE 33838_1 | TR_LINE 42252_1 | TR_LINE 42252_1 | TR_LINE 42252_1 | TR_LINE 42252_1 | TR_LINE 42252_1 | TR_LINE 42252_1 | TR_LINE 42252_1 | TR_LINE 42252_1 | TR_LINE 42252_1 | TR_LINE 42252_1 | TR_LINE 42252_1 | TR_LINE 42252_1
WB | 50079712 | M011 | KILKIVAN-MARYBOROUGH | M011_Kilkivan-Maryborough 66 kV | Loading (A) | 45.1435 | 47.2288 | 20.5534 | 67.7387 | 69.5931 | 30.2273 | 69.2048 | 71.2564 | 30.8867 | 64.8549 | 72.4666 | 31.4748 | 66.4443 | 74.2575 | 30.1189
WB | 50079712 | M011 | KILKIVAN-MARYBOROUGH | M011_Kilkivan-Maryborough 66 kV | Loading (MVA) | 4.8892 | 5.0997 | 2.3375 | 7.8704 | 8.0967 | 3.5621 | 8.0402 | 8.2892 | 3.6396 | 7.5606 | 8.4261 | 3.708 | 7.741 | 8.628 | 3.5508
WB | 50079712 | M011 | KILKIVAN-MARYBOROUGH | M011_Kilkivan-Maryborough 66 kV | Loading (MW) | 4.6938 | 4.8919 | 2.2618 | 7.6146 | 7.9762 | 2.5505 | 7.799 | 8.1768 | 2.6809 | 7.455 | 8.3137 | 2.7729 | 7.6323 | 8.5104 | 2.8769
WB | 50079712 | M011 | KILKIVAN-MARYBOROUGH | M011_Kilkivan-Maryborough 66 kV | Power Factor | 0.96002 | 0.95925 | 0.96763 | 0.96749 | 0.98511 | 0.71602 | 0.97001 | 0.98644 | 0.73661 | 0.98604 | 0.98666 | 0.74783 | 0.98595 | 0.98637 | 0.81022
WB | 50079712 | M011 | KILKIVAN-MARYBOROUGH | M011_Kilkivan-Maryborough 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
WB | 50079712 | M011 | KILKIVAN-MARYBOROUGH | M011_Kilkivan-Maryborough 66 kV | Time | 16:30 | 18:00 | 22:00 | 16:30 | 17:00 | 22:30 | 16:30 | 17:00 | 22:30 | 16:30 | 17:00 | 22:30 | 16:30 | 17:00 | 22:00
WB | 50079712 | M011 | KILKIVAN-MARYBOROUGH | M011_Kilkivan-Maryborough 66 kV | Voltage at Constrained Conductor | 62.5297 | 62.3419 | 65.6613 | 67.0813 | 67.1713 | 68.0368 | 67.076 | 67.1626 | 68.0328 | 67.3058 | 67.1319 | 68.0164 | 67.2638 | 67.0827 | 68.0653
WB | 50079714 | M017 | ROCKY ST - MBOROUGH CITY T/LINE | M017_Rocky St - Maryborough City 66 kV | % of Rated A | 10.8976 | 3.3592 | 11.7962 | 11.3112 | 3.687 | 12.2731 | 12.1208 | 4.2761 | 13.0255 | 12.179 | 4.3586 | 13.1008 | 12.2554 | 4.3726 | 13.1556
WB | 50079714 | M017 | ROCKY ST - MBOROUGH CITY T/LINE | M017_Rocky St - Maryborough City 66 kV | Limiting Line Name | TR_LINE 39141_1 | TR_LINE 39141_1 | TR_LINE 39141_1 | TR_LINE 39141_1 | TR_LINE 39141_1 | TR_LINE 39141_1 | TR_LINE 39141_1 | TR_LINE 39141_1 | TR_LINE 39141_1 | TR_LINE 39141_1 | TR_LINE 39141_1 | TR_LINE 39141_1 | TR_LINE 39141_1 | TR_LINE 39141_1 | TR_LINE 39141_1
WB | 50079714 | M017 | ROCKY ST - MBOROUGH CITY T/LINE | M017_Rocky St - Maryborough City 66 kV | Loading (A) | 59.7189 | 19.45 | 61.4583 | 61.9855 | 21.3479 | 63.9428 | 66.4218 | 24.7584 | 67.863 | 66.7406 | 25.2364 | 68.255 | 67.1593 | 25.3174 | 68.5409
WB | 50079714 | M017 | ROCKY ST - MBOROUGH CITY T/LINE | M017_Rocky St - Maryborough City 66 kV | Loading (MVA) | 6.9505 | 2.2715 | 7.1827 | 7.2837 | 2.4903 | 7.4701 | 7.7984 | 2.8839 | 7.9219 | 7.8336 | 2.9373 | 7.9649 | 7.8822 | 2.9439 | 7.9941
WB | 50079714 | M017 | ROCKY ST - MBOROUGH CITY T/LINE | M017_Rocky St - Maryborough City 66 kV | Loading (MW) | 6.4988 | 1.7951 | 6.3801 | 6.946 | 2.1722 | 6.7939 | 7.4684 | 2.5959 | 7.2686 | 7.4993 | 2.6382 | 7.3035 | 7.5487 | 2.6471 | 7.3347
WB | 50079714 | M017 | ROCKY ST - MBOROUGH CITY T/LINE | M017_Rocky St - Maryborough City 66 kV | Power Factor | 0.935 | 0.79024 | 0.88826 | 0.95364 | 0.87225 | 0.90947 | 0.95769 | 0.90012 | 0.91753 | 0.95734 | 0.89817 | 0.91697 | 0.9577 | 0.89918 | 0.91751
WB | 50079714 | M017 | ROCKY ST - MBOROUGH CITY T/LINE | M017_Rocky St - Maryborough City 66 kV | Rating (A) | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521
WB | 50079714 | M017 | ROCKY ST - MBOROUGH CITY T/LINE | M017_Rocky St - Maryborough City 66 kV | Time | 11:00 | 20:00 | 7:30 | 11:00 | 20:00 | 7:30 | 11:00 | 20:00 | 7:30 | 11:00 | 20:00 | 7:30 | 11:00 | 20:00 | 7:30
WB | 50079714 | M017 | ROCKY ST - MBOROUGH CITY T/LINE | M017_Rocky St - Maryborough City 66 kV | Voltage at Constrained Conductor | 67.1962 | 67.428 | 67.4755 | 67.842 | 67.3502 | 67.4492 | 67.785 | 67.2518 | 67.3962 | 67.7654 | 67.1994 | 67.3727 | 67.7608 | 67.1345 | 67.3381
WB | 50079715 | M018 | MBOROUGH - MBOROUGH CITY T/TUAN | M018_Maryborough-Maryborough City 66 kV | % of Rated A | 23.6465 | 22.7159 | 25.6287 | 24.2592 | 23.0939 | 26.1291 | 25.2805 | 23.8401 | 26.9003 | 25.4199 | 23.9134 | 26.9743 | 25.6674 | 24.1559 | 27.1736
WB | 50079715 | M018 | MBOROUGH - MBOROUGH CITY T/TUAN | M018_Maryborough-Maryborough City 66 kV | Limiting Line Name | TR_LINE 122162_1 | TR_LINE 122162_1 | TR_LINE 70964_2 | TR_LINE 122162_1 | TR_LINE 122162_1 | TR_LINE 70964_2 | TR_LINE 122162_1 | TR_LINE 122162_1 | TR_LINE 70964_2 | TR_LINE 122162_1 | TR_LINE 122162_1 | TR_LINE 70964_2 | TR_LINE 122162_1 | TR_LINE 122162_1 | TR_LINE 70964_2
WB | 50079715 | M018 | MBOROUGH - MBOROUGH CITY T/TUAN | M018_Maryborough-Maryborough City 66 kV | Loading (A) | 129.5828 | 131.5252 | 133.5252 | 132.9403 | 133.714 | 136.1323 | 138.537 | 138.0344 | 140.1501 | 139.3011 | 138.4587 | 140.5359 | 140.6575 | 139.8627 | 141.5745
WB | 50079715 | M018 | MBOROUGH - MBOROUGH CITY T/TUAN | M018_Maryborough-Maryborough City 66 kV | Loading (MVA) | 15.1506 | 15.3193 | 15.6056 | 15.6375 | 15.6363 | 15.9041 | 16.2786 | 16.1156 | 16.3607 | 16.3128 | 16.1521 | 16.4 | 16.4616 | 16.2921 | 16.5127
WB | 50079715 | M018 | MBOROUGH - MBOROUGH CITY T/TUAN | M018_Maryborough-Maryborough City 66 kV | Loading (MW) | 15.1299 | 15.3063 | 15.5795 | 15.5959 | 15.6129 | 15.8895 | 16.2453 | 16.0932 | 16.3447 | 16.284 | 16.1317 | 16.3826 | 16.4348 | 16.2738 | 16.4946
WB | 50079715 | M018 | MBOROUGH - MBOROUGH CITY T/TUAN | M018_Maryborough-Maryborough City 66 kV | Power Factor | 0.99863 | 0.99915 | 0.99833 | 0.99734 | 0.9985 | 0.99908 | 0.99795 | 0.99861 | 0.99902 | 0.99823 | 0.99874 | 0.99894 | 0.99837 | 0.99888 | 0.9989
WB | 50079715 | M018 | MBOROUGH - MBOROUGH CITY T/TUAN | M018_Maryborough-Maryborough City 66 kV | Rating (A) | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521
WB | 50079715 | M018 | MBOROUGH - MBOROUGH CITY T/TUAN | M018_Maryborough-Maryborough City 66 kV | Time | 14:00 | 18:00 | 7:30 | 14:00 | 18:00 | 7:30 | 14:00 | 18:00 | 7:30 | 14:00 | 18:00 | 7:30 | 14:00 | 18:00 | 7:30
WB | 50079715 | M018 | MBOROUGH - MBOROUGH CITY T/TUAN | M018_Maryborough-Maryborough City 66 kV | Voltage at Constrained Conductor | 67.5027 | 67.2463 | 67.4773 | 67.9125 | 67.5143 | 67.451 | 67.8408 | 67.4062 | 67.3982 | 67.6105 | 67.3517 | 67.3747 | 67.5692 | 67.2534 | 67.3401
WB | 50079735 | M007 | PROSTON T/LINE | M007_Proston 66 kV | % of Rated A | 13.6247 | 12.9535 | 8.9935 | 13.4695 | 12.7783 | 8.8396 | 13.464 | 12.7731 | 8.8372 | 13.4407 | 12.7511 | 8.8394 | 13.4477 | 12.7582 | 8.8436
WB | 50079735 | M007 | PROSTON T/LINE | M007_Proston 66 kV | Limiting Line Name | TR_LINE 7270_1 | TR_LINE 7270_1 | TR_LINE 7270_1 | TR_LINE 7270_1 | TR_LINE 7270_1 | TR_LINE 7270_1 | TR_LINE 7270_1 | TR_LINE 7270_1 | TR_LINE 7270_1 | TR_LINE 7270_1 | TR_LINE 7270_1 | TR_LINE 7270_1 | TR_LINE 7270_1 | TR_LINE 7270_1 | TR_LINE 7270_1
WB | 50079735 | M007 | PROSTON T/LINE | M007_Proston 66 kV | Loading (A) | 13.4884 | 16.4509 | 10.8821 | 13.3348 | 16.2285 | 10.6959 | 13.3293 | 16.2218 | 10.693 | 13.3063 | 16.1939 | 10.6956 | 13.3132 | 16.2029 | 10.7008
WB | 50079735 | M007 | PROSTON T/LINE | M007_Proston 66 kV | Loading (MVA) | 1.513 | 1.8327 | 1.2377 | 1.5131 | 1.8328 | 1.2381 | 1.5131 | 1.8328 | 1.2381 | 1.513 | 1.8327 | 1.2381 | 1.5131 | 1.8327 | 1.2376
WB | 50079735 | M007 | PROSTON T/LINE | M007_Proston 66 kV | Loading (MW) | 1.4797 | 1.7887 | 1.2124 | 1.4798 | 1.7887 | 1.2126 | 1.4798 | 1.7887 | 1.2126 | 1.4798 | 1.7887 | 1.2126 | 1.4798 | 1.7887 | 1.2124
WB | 50079735 | M007 | PROSTON T/LINE | M007_Proston 66 kV | Power Factor | 0.97805 | 0.97599 | 0.97961 | 0.97798 | 0.97595 | 0.97942 | 0.97799 | 0.97596 | 0.97943 | 0.97802 | 0.976 | 0.97942 | 0.97801 | 0.97598 | 0.97963
WB | 50079735 | M007 | PROSTON T/LINE | M007_Proston 66 kV | Rating (A) | 99 | 127 | 121 | 99 | 127 | 121 | 99 | 127 | 121 | 99 | 127 | 121 | 99 | 127 | 121
WB | 50079735 | M007 | PROSTON T/LINE | M007_Proston 66 kV | Time | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00
WB | 50079735 | M007 | PROSTON T/LINE | M007_Proston 66 kV | Voltage at Constrained Conductor | 64.7595 | 64.318 | 65.6637 | 65.5137 | 65.2046 | 66.829 | 65.5399 | 65.2304 | 66.8464 | 65.65 | 65.3386 | 66.8303 | 65.6167 | 65.3035 | 66.7739
WB | 50079738 | M051 | TARONG TIE 66KV T/LINE | M051_Tarong Tie 66 kV | % of Rated A | 37.6451 | 32.8734 | 22.2378 | 37.6472 | 32.8758 | 22.2411 | 37.6165 | 32.8719 | 22.2292 | 37.6276 | 32.8838 | 22.2343 | 37.6493 | 32.8788 | 22.2428
WB | 50079738 | M051 | TARONG TIE 66KV T/LINE | M051_Tarong Tie 66 kV | Limiting Line Name | TR_LINE 7733_1 | TR_LINE 7733_1 | TR_LINE 7733_1 | TR_LINE 7733_1 | TR_LINE 7733_1 | TR_LINE 7733_1 | TR_LINE 7733_1 | TR_LINE 7733_1 | TR_LINE 7733_1 | TR_LINE 7733_1 | TR_LINE 7733_1 | TR_LINE 7733_1 | TR_LINE 7733_1 | TR_LINE 7733_1 | TR_LINE 7733_1
WB | 50079738 | M051 | TARONG TIE 66KV T/LINE | M051_Tarong Tie 66 kV | Loading (A) | 40.1624 | 45.2449 | 29.354 | 40.1645 | 45.2483 | 29.3583 | 40.1317 | 45.2421 | 29.3425 | 40.1436 | 45.2586 | 29.3492 | 40.1669 | 45.2525 | 29.3605
WB | 50079738 | M051 | TARONG TIE 66KV T/LINE | M051_Tarong Tie 66 kV | Loading (MVA) | 4.3803 | 4.906 | 3.3235 | 4.3803 | 4.906 | 3.3235 | 4.3801 | 4.9088 | 3.3235 | 4.3802 | 4.9089 | 3.3235 | 4.3803 | 4.9061 | 3.3235
WB | 50079738 | M051 | TARONG TIE 66KV T/LINE | M051_Tarong Tie 66 kV | Loading (MW) | 4.2608 | 4.7638 | 3.2341 | 4.2608 | 4.7638 | 3.2341 | 4.2607 | 4.7646 | 3.2341 | 4.2607 | 4.7647 | 3.2341 | 4.2608 | 4.7639 | 3.2341
WB | 50079738 | M051 | TARONG TIE 66KV T/LINE | M051_Tarong Tie 66 kV | Power Factor | 0.97272 | 0.97102 | 0.97311 | 0.97272 | 0.97102 | 0.97311 | 0.97275 | 0.97063 | 0.97312 | 0.97274 | 0.97062 | 0.97311 | 0.97272 | 0.97102 | 0.97311
WB | 50079738 | M051 | TARONG TIE 66KV T/LINE | M051_Tarong Tie 66 kV | Rating (A) | 107 | 138 | 132 | 107 | 138 | 132 | 107 | 138 | 132 | 107 | 138 | 132 | 107 | 138 | 132
WB | 50079738 | M051 | TARONG TIE 66KV T/LINE | M051_Tarong Tie 66 kV | Time | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00
WB | 50079738 | M051 | TARONG TIE 66KV T/LINE | M051_Tarong Tie 66 kV | Voltage at Constrained Conductor | 62.9681 | 62.6033 | 65.3686 | 62.9648 | 62.5989 | 65.3592 | 63.0138 | 62.6426 | 65.3933 | 62.996 | 62.6211 | 65.3788 | 62.9614 | 62.5935 | 65.3545
WB | 50079742 | M033 | Wallaville 66 kV | M033_Wallaville 66 kV | % of Rated A | 27.1487 | 29.4579 | 29.698 | 26.8407 | 29.3468 | 29.0711 | 26.8476 | 29.3654 | 29.074 | 27.1717 | 29.718 | 29.3991 | 27.5455 | 30.0963 | 29.752
WB | 50079742 | M033 | Wallaville 66 kV | M033_Wallaville 66 kV | Limiting Line Name | TR_LINE 214482_2 | TR_LINE 214482_2 | TR_LINE 214482_2 | TR_LINE 214482_2 | TR_LINE 214482_2 | TR_LINE 214482_2 | TR_LINE 214482_2 | TR_LINE 214482_2 | TR_LINE 214482_2 | TR_LINE 214482_2 | TR_LINE 214482_2 | TR_LINE 214482_2 | TR_LINE 214482_2 | TR_LINE 214482_2 | TR_LINE 214482_2
WB | 50079742 | M033 | Wallaville 66 kV | M033_Wallaville 66 kV | Loading (A) | 70.0435 | 78.0636 | 69.4934 | 69.2491 | 77.7689 | 68.0264 | 69.2669 | 77.8182 | 68.0332 | 70.1029 | 78.7527 | 68.794 | 71.0674 | 79.7553 | 69.6196
WB | 50079742 | M033 | Wallaville 66 kV | M033_Wallaville 66 kV | Loading (MVA) | 7.9312 | 8.8369 | 7.8073 | 7.8399 | 8.734 | 7.722 | 7.8396 | 8.7337 | 7.7219 | 7.9305 | 8.8322 | 7.8045 | 8.0309 | 8.9305 | 7.8868
WB | 50079742 | M033 | Wallaville 66 kV | M033_Wallaville 66 kV | Loading (MW) | 7.8691 | 8.7877 | 7.7177 | 7.7737 | 8.6876 | 7.628 | 7.7737 | 8.6878 | 7.628 | 7.8692 | 8.7903 | 7.7158 | 7.9647 | 8.8931 | 7.8041
WB | 50079742 | M033 | Wallaville 66 kV | M033_Wallaville 66 kV | Power Factor | 0.99216 | 0.99443 | 0.98852 | 0.99156 | 0.99468 | 0.98783 | 0.99159 | 0.99475 | 0.98784 | 0.99227 | 0.99526 | 0.98864 | 0.99175 | 0.99581 | 0.98952
WB | 50079742 | M033 | Wallaville 66 kV | M033_Wallaville 66 kV | Rating (A) | 258 | 265 | 234 | 258 | 265 | 234 | 258 | 265 | 234 | 258 | 265 | 234 | 258 | 265 | 234
WB | 50079742 | M033 | Wallaville 66 kV | M033_Wallaville 66 kV | Time | 16:30 | 18:30 | 22:30 | 16:30 | 18:30 | 22:30 | 16:30 | 18:30 | 22:30 | 16:30 | 18:30 | 22:30 | 16:30 | 18:30 | 22:30
WB | 50079742 | M033 | Wallaville 66 kV | M033_Wallaville 66 kV | Voltage at Constrained Conductor | 65.3752 | 65.357 | 64.8631 | 65.3633 | 64.8407 | 65.5379 | 65.3446 | 64.7969 | 65.5304 | 65.314 | 64.7502 | 65.4992 | 65.2432 | 64.6484 | 65.4046
WB | 50079743 | M034 | Monduran Dam 66 kV | M034_Monduran Dam 66 kV | % of Rated A | 9.5637 | 10.046 | 9.2663 | 9.5547 | 10.0195 | 9.2486 | 9.5576 | 10.0235 | 9.25 | 9.5635 | 10.0307 | 9.2529 | 9.5749 | 10.0446 | 9.2278
WB | 50079743 | M034 | Monduran Dam 66 kV | M034_Monduran Dam 66 kV | Limiting Line Name | TR_LINE 209283_1 | TR_LINE 209283_1 | TR_LINE 209283_1 | TR_LINE 209283_1 | TR_LINE 209283_1 | TR_LINE 209283_1 | TR_LINE 209283_1 | TR_LINE 209283_1 | TR_LINE 209283_1 | TR_LINE 209283_1 | TR_LINE 209283_1 | TR_LINE 209283_1 | TR_LINE 209283_1 | TR_LINE 209283_1 | TR_LINE 209283_1
WB | 50079743 | M034 | Monduran Dam 66 kV | M034_Monduran Dam 66 kV | Loading (A) | 12.624 | 17.7814 | 15.7527 | 12.6122 | 17.7344 | 15.7226 | 12.616 | 17.7416 | 15.725 | 12.6238 | 17.7544 | 15.7299 | 12.6389 | 17.7789 | 15.6873
WB | 50079743 | M034 | Monduran Dam 66 kV | M034_Monduran Dam 66 kV | Loading (MVA) | 1.408 | 1.9704 | 1.7504 | 1.4126 | 1.9702 | 1.7503 | 1.4126 | 1.9702 | 1.7503 | 1.4126 | 1.9704 | 1.7503 | 1.4127 | 1.9704 | 1.7502
WB | 50079743 | M034 | Monduran Dam 66 kV | M034_Monduran Dam 66 kV | Loading (MW) | 1.1696 | 1.7843 | 1.5761 | 1.1756 | 1.7841 | 1.5761 | 1.1756 | 1.7841 | 1.5761 | 1.1756 | 1.7843 | 1.5761 | 1.1756 | 1.7843 | 1.5762
WB | 50079743 | M034 | Monduran Dam 66 kV | M034_Monduran Dam 66 kV | Power Factor | 0.83065 | 0.90553 | 0.90042 | 0.83224 | 0.90554 | 0.90047 | 0.83223 | 0.90553 | 0.90047 | 0.83221 | 0.90557 | 0.90046 | 0.83216 | 0.90553 | 0.90053
WB | 50079743 | M034 | Monduran Dam 66 kV | M034_Monduran Dam 66 kV | Rating (A) | 132 | 177 | 170 | 132 | 177 | 170 | 132 | 177 | 170 | 132 | 177 | 170 | 132 | 177 | 170
WB | 50079743 | M034 | Monduran Dam 66 kV | M034_Monduran Dam 66 kV | Time | 16:00 | 21:00 | 22:00 | 16:30 | 21:00 | 22:00 | 16:30 | 21:00 | 22:00 | 16:30 | 21:00 | 22:00 | 16:30 | 21:00 | 22:00
WB | 50079743 | M034 | Monduran Dam 66 kV | M034_Monduran Dam 66 kV | Voltage at Constrained Conductor | 64.3941 | 63.9787 | 64.1525 | 64.6638 | 64.1397 | 64.2731 | 64.6447 | 64.1141 | 64.2635 | 64.6057 | 64.0741 | 64.244 | 64.5306 | 63.9874 | 64.4156
WB | 50079744 | M041 | WST BBERG - MEADOWVALE T/LINE | M041_West Bundaberg-Meadowvale 66 kV | % of Rated A | 50.5705 | 42.8911 | 40.0571 | 50.6421 | 43.3187 | 40.024 | 49.9581 | 42.7292 | 39.385 | 50.6609 | 43.3442 | 40.035 | 51.1521 | 43.7027 | 40.0869
WB | 50079744 | M041 | WST BBERG - MEADOWVALE T/LINE | M041_West Bundaberg-Meadowvale 66 kV | Limiting Line Name | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1
WB | 50079744 | M041 | WST BBERG - MEADOWVALE T/LINE | M041_West Bundaberg-Meadowvale 66 kV | Loading (A) | 114.1714 | 133.2772 | 103.2237 | 114.3335 | 134.6077 | 103.1381 | 112.7871 | 132.7739 | 101.49 | 114.376 | 134.6869 | 103.1664 | 115.4856 | 135.8025 | 103.3013
WB | 50079744 | M041 | WST BBERG - MEADOWVALE T/LINE | M041_West Bundaberg-Meadowvale 66 kV | Loading (MVA) | 12.8716 | 15.0347 | 11.5676 | 12.8694 | 15.0444 | 11.5692 | 12.6961 | 14.8355 | 11.387 | 12.8689 | 15.0437 | 11.5687 | 12.9801 | 15.1441 | 11.6203
WB | 50079744 | M041 | WST BBERG - MEADOWVALE T/LINE | M041_West Bundaberg-Meadowvale 66 kV | Loading (MW) | 11.6411 | 13.6891 | 10.3314 | 11.6414 | 13.691 | 10.3312 | 11.4761 | 13.4943 | 10.1829 | 11.6415 | 13.6912 | 10.3313 | 11.7294 | 13.7925 | 10.4058
WB | 50079744 | M041 | WST BBERG - MEADOWVALE T/LINE | M041_West Bundaberg-Meadowvale 66 kV | Power Factor | 0.9044 | 0.9105 | 0.89313 | 0.90458 | 0.91004 | 0.89299 | 0.90391 | 0.9096 | 0.89426 | 0.90462 | 0.91009 | 0.89304 | 0.90365 | 0.91075 | 0.89549
WB | 50079744 | M041 | WST BBERG - MEADOWVALE T/LINE | M041_West Bundaberg-Meadowvale 66 kV | Rating (A) | 226 | 311 | 258 | 226 | 311 | 258 | 226 | 311 | 258 | 226 | 311 | 258 | 226 | 311 | 258
WB | 50079744 | M041 | WST BBERG - MEADOWVALE T/LINE | M041_West Bundaberg-Meadowvale 66 kV | Time | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00
WB | 50079744 | M041 | WST BBERG - MEADOWVALE T/LINE | M041_West Bundaberg-Meadowvale 66 kV | Voltage at Constrained Conductor | 65.0899 | 65.1297 | 64.6998 | 64.9868 | 64.5274 | 64.7625 | 64.9903 | 64.51 | 64.7776 | 64.9598 | 64.4867 | 64.7418 | 64.8917 | 64.3834 | 64.9456
WB | 50079745 | M042 | MEADOWVALE - GOOBURRUM T/LINE | M042_Meadowvale-Gooburrum 66 kV | % of Rated A | 35.7021 | 34.0774 | 32.0597 | 35.7622 | 34.4022 | 32.0269 | 35.0786 | 33.7514 | 31.409 | 35.7779 | 34.4417 | 32.0377 | 35.8191 | 34.4877 | 31.9314
WB | 50079745 | M042 | MEADOWVALE - GOOBURRUM T/LINE | M042_Meadowvale-Gooburrum 66 kV | Limiting Line Name | TR_LINE 7778_1 | TR_LINE 7778_1 | TR_LINE 7778_1 | TR_LINE 7778_1 | TR_LINE 7778_1 | TR_LINE 7778_1 | TR_LINE 7778_1 | TR_LINE 7778_1 | TR_LINE 7778_1 | TR_LINE 7778_1 | TR_LINE 7778_1 | TR_LINE 7778_1 | TR_LINE 7778_1 | TR_LINE 7778_1 | TR_LINE 7778_1
WB | 50079745 | M042 | MEADOWVALE - GOOBURRUM T/LINE | M042_Meadowvale-Gooburrum 66 kV | Loading (A) | 39.3574 | 49.476 | 37.8814 | 39.4245 | 49.9529 | 37.8421 | 38.6661 | 49.0033 | 37.3768 | 39.4421 | 50.0109 | 37.8551 | 39.4881 | 50.0783 | 37.7279
WB | 50079745 | M042 | MEADOWVALE - GOOBURRUM T/LINE | M042_Meadowvale-Gooburrum 66 kV | Loading (MVA) | 4.401 | 5.5264 | 4.2123 | 4.4014 | 5.5272 | 4.212 | 4.3175 | 5.4215 | 4.1323 | 4.4015 | 5.5276 | 4.2121 | 4.4018 | 5.5281 | 4.2114
WB | 50079745 | M042 | MEADOWVALE - GOOBURRUM T/LINE | M042_Meadowvale-Gooburrum 66 kV | Loading (MW) | 4.0653 | 5.082 | 3.8933 | 4.0654 | 5.0828 | 3.8933 | 3.9894 | 4.9875 | 3.7943 | 4.0655 | 5.0829 | 3.8933 | 4.0656 | 5.0831 | 3.8931
WB | 50079745 | M042 | MEADOWVALE - GOOBURRUM T/LINE | M042_Meadowvale-Gooburrum 66 kV | Power Factor | 0.92373 | 0.91959 | 0.92429 | 0.92367 | 0.91959 | 0.92432 | 0.92401 | 0.91995 | 0.91819 | 0.92366 | 0.91955 | 0.92431 | 0.92362 | 0.9195 | 0.92442
WB | 50079745 | M042 | MEADOWVALE - GOOBURRUM T/LINE | M042_Meadowvale-Gooburrum 66 kV | Rating (A) | 111 | 146 | 119 | 111 | 146 | 119 | 111 | 146 | 119 | 111 | 146 | 119 | 111 | 146 | 119
WB | 50079745 | M042 | MEADOWVALE - GOOBURRUM T/LINE | M042_Meadowvale-Gooburrum 66 kV | Time | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00
WB | 50079745 | M042 | MEADOWVALE - GOOBURRUM T/LINE | M042_Meadowvale-Gooburrum 66 kV | Voltage at Constrained Conductor | 64.5598 | 64.489 | 64.1991 | 64.4559 | 63.8832 | 64.2622 | 64.4682 | 63.8755 | 63.8311 | 64.4286 | 63.8138 | 64.2414 | 64.3578 | 63.7333 | 64.4465
WB | 50079747 | M025 | 66kV EIDSVOLD T/LINE | M025_Eidsvold 66 kV | % of Rated A | 13.2351 | 12.4476 | 8.8154 | 13.1935 | 12.5148 | 8.742 | 13.2403 | 12.5827 | 8.766 | 13.2403 | 12.589 | 8.7676 | 13.2715 | 12.6034 | 8.845
WB | 50079747 | M025 | 66kV EIDSVOLD T/LINE | M025_Eidsvold 66 kV | Limiting Line Name | TR_LINE 7673_1 | TR_LINE 7673_1 | TR_LINE 7673_1 | TR_LINE 7673_1 | TR_LINE 7673_1 | TR_LINE 7673_1 | TR_LINE 7673_1 | TR_LINE 7673_1 | TR_LINE 7673_1 | TR_LINE 7673_1 | TR_LINE 7673_1 | TR_LINE 7673_1 | TR_LINE 7673_1 | TR_LINE 7673_1 | TR_LINE 7673_1
WB | 50079747 | M025 | 66kV EIDSVOLD T/LINE | M025_Eidsvold 66 kV | Loading (A) | 14.1616 | 17.1777 | 11.6363 | 14.1171 | 17.2705 | 11.5394 | 14.1671 | 17.3641 | 11.5712 | 14.1671 | 17.3729 | 11.5732 | 14.2005 | 17.3927 | 11.6754
WB | 50079747 | M025 | 66kV EIDSVOLD T/LINE | M025_Eidsvold 66 kV | Loading (MVA) | 1.5934 | 1.9277 | 1.3079 | 1.5933 | 1.928 | 1.3101 | 1.5934 | 1.9284 | 1.3102 | 1.5934 | 1.9284 | 1.3102 | 1.594 | 1.9285 | 1.31
WB | 50079747 | M025 | 66kV EIDSVOLD T/LINE | M025_Eidsvold 66 kV | Loading (MW) | 1.5744 | 1.9017 | 1.2936 | 1.5743 | 1.9018 | 1.2958 | 1.5744 | 1.902 | 1.2958 | 1.5744 | 1.902 | 1.2958 | 1.5747 | 1.902 | 1.2957
WB | 50079747 | M025 | 66kV EIDSVOLD T/LINE | M025_Eidsvold 66 kV | Power Factor | 0.98806 | 0.98651 | 0.98912 | 0.9881 | 0.98641 | 0.98907 | 0.98805 | 0.98631 | 0.98904 | 0.98805 | 0.9863 | 0.98904 | 0.98784 | 0.98628 | 0.98909
WB | 50079747 | M025 | 66kV EIDSVOLD T/LINE | M025_Eidsvold 66 kV | Rating (A) | 107 | 138 | 132 | 107 | 138 | 132 | 107 | 138 | 132 | 107 | 138 | 132 | 107 | 138 | 132
WB | 50079747 | M025 | 66kV EIDSVOLD T/LINE | M025_Eidsvold 66 kV | Time | 16:30 | 19:00 | 7:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00
WB | 50079747 | M025 | 66kV EIDSVOLD T/LINE | M025_Eidsvold 66 kV | Voltage at Constrained Conductor | 64.9608 | 64.7913 | 64.8916 | 65.1604 | 64.4543 | 65.5472 | 64.9361 | 64.118 | 65.3709 | 64.936 | 64.0867 | 65.3595 | 64.8092 | 64.016 | 64.782
WB | 82554175 | M023 | 6242 PIALBA - POINT VERNON | M023_6242 (Pialba-Point Vernon) 66 kV | % of Rated A | 31.7727 | 24.7724 | 21.7097 | 30.8733 | 23.9503 | 21.0734 | 30.6343 | 23.7626 | 20.9039 | 30.5058 | 23.6733 | 20.8191 | 30.6851 | 23.8235 | 20.9166
WB | 82554175 | M023 | 6242 PIALBA - POINT VERNON | M023_6242 (Pialba-Point Vernon) 66 kV | Limiting Line Name | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1
WB | 82554175 | M023 | 6242 PIALBA - POINT VERNON | M023_6242 (Pialba-Point Vernon) 66 kV | Loading (A) | 192.225 | 165.4793 | 118.752 | 186.7833 | 159.988 | 115.2712 | 185.3373 | 158.7339 | 114.3442 | 184.5601 | 158.1377 | 113.8803 | 185.6447 | 159.1409 | 114.4138
WB | 82554175 | M023 | 6242 PIALBA - POINT VERNON | M023_6242 (Pialba-Point Vernon) 66 kV | Loading (MVA) | 22.0798 | 18.7588 | 13.8268 | 21.3871 | 18.1904 | 13.431 | 21.2073 | 18.0244 | 13.3162 | 21.1086 | 17.941 | 13.2588 | 21.2048 | 18.0191 | 13.3139
WB | 82554175 | M023 | 6242 PIALBA - POINT VERNON | M023_6242 (Pialba-Point Vernon) 66 kV | Loading (MW) | 21.9068 | 18.4842 | 13.2839 | 21.2003 | 17.8875 | 12.8561 | 20.9979 | 17.7174 | 12.7339 | 20.897 | 17.6324 | 12.6728 | 20.9983 | 17.7179 | 12.734
WB | 82554175 | M023 | 6242 PIALBA - POINT VERNON | M023_6242 (Pialba-Point Vernon) 66 kV | Power Factor | 0.99217 | 0.98536 | 0.96074 | 0.99126 | 0.98335 | 0.9572 | 0.99012 | 0.98297 | 0.95627 | 0.98997 | 0.9828 | 0.9558 | 0.99026 | 0.98328 | 0.95645
WB | 82554175 | M023 | 6242 PIALBA - POINT VERNON | M023_6242 (Pialba-Point Vernon) 66 kV | Rating (A) | 605 | 668 | 547 | 605 | 668 | 547 | 605 | 668 | 547 | 605 | 668 | 547 | 605 | 668 | 547
WB | 82554175 | M023 | 6242 PIALBA - POINT VERNON | M023_6242 (Pialba-Point Vernon) 66 kV | Time | 15:30 | 17:00 | 8:30 | 15:30 | 17:00 | 8:30 | 15:30 | 17:00 | 8:30 | 15:30 | 17:00 | 8:30 | 15:30 | 17:00 | 8:30
WB | 82554175 | M023 | 6242 PIALBA - POINT VERNON | M023_6242 (Pialba-Point Vernon) 66 kV | Voltage at Constrained Conductor | 66.3169 | 65.4486 | 67.2232 | 66.108 | 65.6439 | 67.2709 | 66.0637 | 65.5588 | 67.2365 | 66.033 | 65.5015 | 67.2197 | 65.9465 | 65.372 | 67.1839
WB | 82624538 | SOBU-BARG-1 | STH BUNDABERG-BARGARA 66KV FDR | SOBU-BARG-1_SOBU-Bargara-1 66 kV | % of Rated A | 22.6168 | 20.8912 | 22.5844 | 22.6348 | 21.0651 | 22.3581 | 22.6385 | 21.0771 | 22.3583 | 22.8012 | 21.2355 | 22.521 | 23.136 | 21.5555 | 22.8613
WB | 82624538 | SOBU-BARG-1 | STH BUNDABERG-BARGARA 66KV FDR | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Limiting Line Name | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1
WB | 82624538 | SOBU-BARG-1 | STH BUNDABERG-BARGARA 66KV FDR | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Loading (A) | 92.7117 | 132.2221 | 121.7118 | 92.7857 | 133.3234 | 120.4916 | 92.8009 | 133.3993 | 120.4929 | 93.468 | 134.4021 | 121.3697 | 94.8404 | 136.4273 | 123.2037
WB | 82624538 | SOBU-BARG-1 | STH BUNDABERG-BARGARA 66KV FDR | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Loading (MVA) | 10.4828 | 14.9341 | 13.6127 | 10.4829 | 14.933 | 13.6131 | 10.483 | 14.9332 | 13.6131 | 10.5544 | 15.0354 | 13.7061 | 10.6972 | 15.2399 | 13.8923
WB | 82624538 | SOBU-BARG-1 | STH BUNDABERG-BARGARA 66KV FDR | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Loading (MW) | 10.388 | 14.7655 | 13.4687 | 10.388 | 14.7653 | 13.4688 | 10.388 | 14.7653 | 13.4688 | 10.4584 | 14.8654 | 13.5601 | 10.5991 | 15.0656 | 13.7426
WB | 82624538 | SOBU-BARG-1 | STH BUNDABERG-BARGARA 66KV FDR | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Power Factor | 0.99095 | 0.98871 | 0.98942 | 0.99095 | 0.98877 | 0.9894 | 0.99094 | 0.98876 | 0.9894 | 0.99091 | 0.9887 | 0.98935 | 0.99083 | 0.98857 | 0.98923
WB | 82624538 | SOBU-BARG-1 | STH BUNDABERG-BARGARA 66KV FDR | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Rating (A) | 410 | 633 | 539 | 410 | 633 | 539 | 410 | 633 | 539 | 410 | 633 | 539 | 410 | 633 | 539
WB | 82624538 | SOBU-BARG-1 | STH BUNDABERG-BARGARA 66KV FDR | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Time | 16:30 | 18:30 | 22:30 | 16:30 | 18:30 | 22:30 | 16:30 | 18:30 | 22:30 | 16:30 | 18:30 | 22:30 | 16:30 | 18:30 | 22:30
WB | 82624538 | SOBU-BARG-1 | STH BUNDABERG-BARGARA 66KV FDR | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Voltage at Constrained Conductor | 65.2805 | 65.2099 | 64.573 | 65.2291 | 64.6667 | 65.2288 | 65.2186 | 64.6307 | 65.2282 | 65.1941 | 64.5875 | 65.1993 | 65.1203 | 64.4942 | 65.1012
WB | 83009518 | 6112 | 66KV 6112 AGNES WATER FDR | 6112_Agnes Water 66 kV | % of Rated A | 14.1666 | 10.0595 | 7.6719 | 14.1926 | 9.9709 | 7.6849 | 14.1945 | 9.973 | 7.6855 | 14.1952 | 9.9725 | 7.6859 | 14.4505 | 10.15 | 7.8156
WB | 83009518 | 6112 | 66KV 6112 AGNES WATER FDR | 6112_Agnes Water 66 kV | Limiting Line Name | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1
WB | 83009518 | 6112 | 66KV 6112 AGNES WATER FDR | 6112_Agnes Water 66 kV | Loading (A) | 40.2332 | 48.4869 | 37.0551 | 40.3069 | 48.0599 | 37.1179 | 40.3124 | 48.0699 | 37.1212 | 40.3143 | 48.0674 | 37.1228 | 41.0395 | 48.9228 | 37.7495
WB | 83009518 | 6112 | 66KV 6112 AGNES WATER FDR | 6112_Agnes Water 66 kV | Loading (MVA) | 4.678 | 5.6355 | 4.3345 | 4.6778 | 5.6356 | 4.3343 | 4.6778 | 5.6356 | 4.3342 | 4.6778 | 5.6356 | 4.3342 | 4.7606 | 5.7362 | 4.4107
WB | 83009518 | 6112 | 66KV 6112 AGNES WATER FDR | 6112_Agnes Water 66 kV | Loading (MW) | 4.6654 | 5.6315 | 4.3163 | 4.6655 | 5.6308 | 4.3164 | 4.6655 | 5.6309 | 4.3164 | 4.6655 | 5.6309 | 4.3164 | 4.7493 | 5.7321 | 4.3939
WB | 83009518 | 6112 | 66KV 6112 AGNES WATER FDR | 6112_Agnes Water 66 kV | Power Factor | 0.99731 | 0.99929 | 0.99582 | 0.99737 | 0.99916 | 0.99588 | 0.99737 | 0.99916 | 0.99589 | 0.99737 | 0.99916 | 0.99589 | 0.99763 | 0.99929 | 0.99619
WB | 83009518 | 6112 | 66KV 6112 AGNES WATER FDR | 6112_Agnes Water 66 kV | Rating (A) | 284 | 482 | 483 | 284 | 482 | 483 | 284 | 482 | 483 | 284 | 482 | 483 | 284 | 482 | 483
WB | 83009518 | 6112 | 66KV 6112 AGNES WATER FDR | 6112_Agnes Water 66 kV | Time | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00
WB | 83009518 | 6112 | 66KV 6112 AGNES WATER FDR | 6112_Agnes Water 66 kV | Voltage at Constrained Conductor | 67.1296 | 67.1043 | 67.5346 | 67.0047 | 67.7011 | 67.417 | 66.9954 | 67.6869 | 67.4109 | 66.9922 | 67.6904 | 67.408 | 66.9733 | 67.6939 | 67.4578
WB | 83859989 | 785 | 785 ISIS 132KV | 785_ISIS 132 kV | % of Rated A | 22.8243 | 17.3281 | 13.8807 | 32.0898 | 21.2414 | 18.4391 | 32.518 | 21.7484 | 18.7414 | 32.3997 | 21.7054 | 18.7256 | 32.5096 | 21.7481 | 21.5372
WB | 83859989 | 785 | 785 ISIS 132KV | 785_ISIS 132 kV | Limiting Line Name | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1
WB | 83859989 | 785 | 785 ISIS 132KV | 785_ISIS 132 kV | Loading (A) | 56.6042 | 68.6193 | 54.5512 | 79.5828 | 84.116 | 72.4657 | 80.6445 | 86.1238 | 73.6539 | 80.3512 | 85.9532 | 73.5914 | 80.6237 | 86.1224 | 84.641
WB | 83859989 | 785 | 785 ISIS 132KV | 785_ISIS 132 kV | Loading (MVA) | 13.3971 | 16.0549 | 13.0372 | 18.8733 | 19.735 | 17.0508 | 18.9041 | 20.1783 | 17.3173 | 19.0831 | 20.1323 | 17.2991 | 18.8834 | 20.1617 | 20.0293
WB | 83859989 | 785 | 785 ISIS 132KV | 785_ISIS 132 kV | Loading (MW) | 1.2374 | 3.8424 | 8.9302 | 6.8444 | 2.5885 | 2.9642 | 0.44342 | 3.2085 | 3.3538 | 7.0117 | 3.2901 | 3.4365 | 0.26465 | 3.4424 | 1.9654
WB | 83859989 | 785 | 785 ISIS 132KV | 785_ISIS 132 kV | Power Factor | 0.09236 | 0.23933 | 0.68498 | 0.36265 | 0.13116 | 0.17385 | 0.023456 | 0.15901 | 0.19367 | 0.36743 | 0.16342 | 0.19865 | 0.014015 | 0.17074 | 0.098128
WB | 83859989 | 785 | 785 ISIS 132KV | 785_ISIS 132 kV | Rating (A) | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393
WB | 83859989 | 785 | 785 ISIS 132KV | 785_ISIS 132 kV | Time | 16:00 | 18:30 | 8:30 | 14:30 | 20:00 | 22:30 | 16:00 | 20:00 | 22:30 | 14:00 | 20:00 | 22:30 | 16:00 | 20:00 | 22:00
WB | 83859989 | 785 | 785 ISIS 132KV | 785_ISIS 132 kV | Voltage at Constrained Conductor | 136.6476 | 135.083 | 137.9805 | 136.9204 | 135.4555 | 135.8474 | 135.3386 | 135.27 | 135.7447 | 137.1186 | 135.2293 | 135.7178 | 135.2249 | 135.1609 | 136.6232
WB | 83859994 | 784 | 784 ISIS 132KV | 784_ISIS 132 kV | % of Rated A | 22.5154 | 17.0902 | 13.6905 | 31.6465 | 20.9475 | 18.1856 | 32.0692 | 21.4471 | 18.4835 | 31.9519 | 21.4047 | 18.4678 | 32.0609 | 21.4467 | 21.2393
WB | 83859994 | 784 | 784 ISIS 132KV | 784_ISIS 132 kV | Limiting Line Name | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1
WB | 83859994 | 784 | 784 ISIS 132KV | 784_ISIS 132 kV | Loading (A) | 55.8382 | 67.6773 | 53.8037 | 78.4833 | 82.9522 | 71.4694 | 79.5315 | 84.9307 | 72.6402 | 79.2406 | 84.7624 | 72.5786 | 79.511 | 84.9291 | 83.4703
WB | 83859994 | 784 | 784 ISIS 132KV | 784_ISIS 132 kV | Loading (MVA) | 13.217 | 15.8364 | 12.8591 | 18.6146 | 19.4647 | 16.8185 | 18.6458 | 19.9018 | 17.0811 | 18.8215 | 19.8564 | 17.0633 | 18.6253 | 19.8854 | 19.7551
WB | 83859994 | 784 | 784 ISIS 132KV | 784_ISIS 132 kV | Loading (MW) | 1.2123 | 3.7958 | 8.7965 | 6.7357 | 2.5624 | 2.931 | 0.42622 | 3.1737 | 3.3151 | 6.9006 | 3.2541 | 3.3965 | 0.25004 | 3.4043 | 1.9486
WB | 83859994 | 784 | 784 ISIS 132KV | 784_ISIS 132 kV | Power Factor | 0.091719 | 0.23969 | 0.68406 | 0.36185 | 0.13164 | 0.17427 | 0.022859 | 0.15947 | 0.19408 | 0.36663 | 0.16388 | 0.19905 | 0.013425 | 0.17119 | 0.098636
WB | 83859994 | 784 | 784 ISIS 132KV | 784_ISIS 132 kV | Rating (A) | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393
WB | 83859994 | 784 | 784 ISIS 132KV | 784_ISIS 132 kV | Time | 16:00 | 18:30 | 8:30 | 14:30 | 20:00 | 22:30 | 16:00 | 20:00 | 22:30 | 14:00 | 20:00 | 22:30 | 16:00 | 20:00 | 22:00
WB | 83859994 | 784 | 784 ISIS 132KV | 784_ISIS 132 kV | Voltage at Constrained Conductor | 136.6602 | 135.0993 | 137.9872 | 136.9355 | 135.4753 | 135.8646 | 135.3569 | 135.2903 | 135.7622 | 137.1339 | 135.2497 | 135.7352 | 135.2433 | 135.1813 | 136.643
WB | 83859997 | 7330 | 7330 MBH 132KV | 7330_Maryborough 132 kV | % of Rated A | 44.5337 | 43.5142 | 30.4481 | 41.1736 | 40.5834 | 30.1002 | 41.5368 | 40.9336 | 30.44 | 41.9472 | 41.1782 | 30.5425 | 42.2894 | 41.5337 | 30.7345
WB | 83859997 | 7330 | 7330 MBH 132KV | 7330_Maryborough 132 kV | Limiting Line Name | TR_LINE 156755_1 | TR_LINE 156755_1 | TR_LINE 7684_1 | TR_LINE 156755_1 | TR_LINE 156755_1 | TR_LINE 7684_1 | TR_LINE 156755_1 | TR_LINE 156755_1 | TR_LINE 7684_1 | TR_LINE 156755_1 | TR_LINE 156755_1 | TR_LINE 7684_1 | TR_LINE 156755_1 | TR_LINE 156755_1 | TR_LINE 7684_1
WB | 83859997 | 7330 | 7330 MBH 132KV | 7330_Maryborough 132 kV | Loading (A) | 250.4475 | 260.2571 | 165.0287 | 231.6476 | 242.74 | 163.1431 | 233.6784 | 244.8252 | 164.9851 | 235.9535 | 246.273 | 165.5402 | 237.8637 | 248.3791 | 166.5812
WB | 83859997 | 7330 | 7330 MBH 132KV | 7330_Maryborough 132 kV | Loading (MVA) | 58.8782 | 61.2969 | 39.17 | 54.7324 | 57.1349 | 38.6038 | 55.161 | 57.5666 | 39.0268 | 55.6729 | 57.8854 | 39.1543 | 56.0873 | 58.3329 | 39.3918
WB | 83859997 | 7330 | 7330 MBH 132KV | 7330_Maryborough 132 kV | Loading (MW) | 58.4647 | 60.73 | 39.1573 | 54.5017 | 56.7005 | 38.5432 | 54.9127 | 57.1075 | 38.9751 | 55.3865 | 57.3991 | 39.1075 | 55.7787 | 57.8073 | 39.3498
WB | 83859997 | 7330 | 7330 MBH 132KV | 7330_Maryborough 132 kV | Power Factor | 0.99298 | 0.99075 | 0.99967 | 0.99579 | 0.9924 | 0.99843 | 0.9955 | 0.99202 | 0.99867 | 0.99486 | 0.9916 | 0.9988 | 0.9945 | 0.99099 | 0.99893
WB | 83859997 | 7330 | 7330 MBH 132KV | 7330_Maryborough 132 kV | Rating (A) | 564 | 600 | 542 | 564 | 600 | 542 | 564 | 600 | 542 | 564 | 600 | 542 | 564 | 600 | 542
WB | 83859997 | 7330 | 7330 MBH 132KV | 7330_Maryborough 132 kV | Time | 16:30 | 17:30 | 7:00 | 16:30 | 17:00 | 8:30 | 16:30 | 17:00 | 8:30 | 16:30 | 17:00 | 8:30 | 16:30 | 17:00 | 8:30
WB | 83859997 | 7330 | 7330 MBH 132KV | 7330_Maryborough 132 kV | Voltage at Constrained Conductor | 135.7303 | 135.9801 | 137.0357 | 136.4132 | 135.8937 | 136.6157 | 136.2865 | 135.7543 | 136.5709 | 136.225 | 135.7037 | 136.5575 | 136.1368 | 135.5931 | 136.5271
WB | 83860003 | 7329 | 7329 MBH 132KV | 7329_Maryborough 132 kV | % of Rated A | 44.5536 | 43.5336 | 30.4618 | 41.192 | 40.6014 | 30.1137 | 41.5553 | 40.9519 | 30.4537 | 41.9659 | 41.1965 | 30.5562 | 42.3083 | 41.5522 | 30.7484
WB | 83860003 | 7329 | 7329 MBH 132KV | 7329_Maryborough 132 kV | Limiting Line Name | TR_LINE 156753_1 | TR_LINE 156753_1 | TR_LINE 120325_1 | TR_LINE 156753_1 | TR_LINE 156753_1 | TR_LINE 120325_1 | TR_LINE 156753_1 | TR_LINE 156753_1 | TR_LINE 120325_1 | TR_LINE 156753_1 | TR_LINE 156753_1 | TR_LINE 120325_1 | TR_LINE 156753_1 | TR_LINE 156753_1 | TR_LINE 120325_1
WB | 83860003 | 7329 | 7329 MBH 132KV | 7329_Maryborough 132 kV | Loading (A) | 250.5602 | 260.3742 | 165.1029 | 231.7518 | 242.8492 | 163.2165 | 233.7835 | 244.9354 | 165.0593 | 236.0597 | 246.3839 | 165.6147 | 237.9708 | 248.4909 | 166.6562
WB | 83860003 | 7329 | 7329 MBH 132KV | 7329_Maryborough 132 kV | Loading (MVA) | 58.9046 | 61.3244 | 39.1878 | 54.7569 | 57.1605 | 38.6213 | 55.1857 | 57.5924 | 39.0445 | 55.6979 | 57.9113 | 39.1721 | 56.1124 | 58.359 | 39.4096
WB | 83860003 | 7329 | 7329 MBH 132KV | 7329_Maryborough 132 kV | Loading (MW) | 58.4913 | 60.7577 | 39.175 | 54.5265 | 56.7264 | 38.5605 | 54.9377 | 57.1335 | 38.9927 | 55.4117 | 57.4253 | 39.1251 | 55.8041 | 57.8337 | 39.3675
WB | 83860003 | 7329 | 7329 MBH 132KV | 7329_Maryborough 132 kV | Power Factor | 0.99298 | 0.99076 | 0.99967 | 0.99579 | 0.99241 | 0.99843 | 0.99551 | 0.99203 | 0.99867 | 0.99486 | 0.99161 | 0.9988 | 0.9945 | 0.991 | 0.99893
WB | 83860003 | 7329 | 7329 MBH 132KV | 7329_Maryborough 132 kV | Rating (A) | 564 | 600 | 542 | 564 | 600 | 542 | 564 | 600 | 542 | 564 | 600 | 542 | 564 | 600 | 542
WB | 83860003 | 7329 | 7329 MBH 132KV | 7329_Maryborough 132 kV | Time | 16:30 | 17:30 | 7:00 | 16:30 | 17:00 | 8:30 | 16:30 | 17:00 | 8:30 | 16:30 | 17:00 | 8:30 | 16:30 | 17:00 | 8:30
WB | 83860003 | 7329 | 7329 MBH 132KV | 7329_Maryborough 132 kV | Voltage at Constrained Conductor | 135.7301 | 135.9799 | 137.0363 | 136.4129 | 135.8935 | 136.6161 | 136.2863 | 135.7541 | 136.5714 | 136.2247 | 135.7034 | 136.558 | 136.1366 | 135.5929 | 136.5276
WB | 83860136 | 7316 | Aramara 132 kV | 7316_Aramara 132 kV | % of Rated A | 23.3463 | 23.7573 | 15.0491 | 23.0086 | 22.3869 | 14.9599 | 23.4226 | 22.8817 | 15.2621 | 23.625 | 23.047 | 15.3851 | 23.8823 | 23.3254 | 16.0076
WB | 83860136 | 7316 | Aramara 132 kV | 7316_Aramara 132 kV | Limiting Line Name | TR_LINE 88015_1 | TR_LINE 88015_1 | TR_LINE 88015_1 | TR_LINE 88015_1 | TR_LINE 88015_1 | TR_LINE 88015_1 | TR_LINE 88015_1 | TR_LINE 88015_1 | TR_LINE 88015_1 | TR_LINE 88015_1 | TR_LINE 88015_1 | TR_LINE 88015_1 | TR_LINE 88015_1 | TR_LINE 88015_1 | TR_LINE 88015_1
WB | 83860136 | 7316 | Aramara 132 kV | 7316_Aramara 132 kV | Loading (A) | 254.935 | 286.2663 | 166.593 | 251.2441 | 269.7514 | 165.6065 | 255.765 | 275.7142 | 168.952 | 257.9743 | 277.7058 | 170.3132 | 260.7847 | 281.0611 | 177.2036
WB | 83860136 | 7316 | Aramara 132 kV | 7316_Aramara 132 kV | Loading (MVA) | 60.1528 | 67.6857 | 39.8642 | 59.5519 | 63.7621 | 39.3811 | 60.5705 | 65.0935 | 40.1533 | 61.0713 | 65.5424 | 40.4686 | 61.7001 | 66.2827 | 42.4795
WB | 83860136 | 7316 | Aramara 132 kV | 7316_Aramara 132 kV | Loading (MW) | 58.4165 | 64.0315 | 39.1965 | 55.6141 | 59.5329 | 37.6535 | 56.5166 | 60.7007 | 38.3563 | 56.9782 | 61.1193 | 38.6522 | 57.521 | 61.7362 | 39.5908
WB | 83860136 | 7316 | Aramara 132 kV | 7316_Aramara 132 kV | Power Factor | 0.97114 | 0.94601 | 0.98325 | 0.93388 | 0.93367 | 0.95613 | 0.93307 | 0.93252 | 0.95525 | 0.93298 | 0.93251 | 0.95511 | 0.93227 | 0.93141 | 0.932
WB | 83860136 | 7316 | Aramara 132 kV | 7316_Aramara 132 kV | Rating (A) | 1092 | 1205 | 1107 | 1092 | 1205 | 1107 | 1092 | 1205 | 1107 | 1092 | 1205 | 1107 | 1092 | 1205 | 1107
WB | 83860136 | 7316 | Aramara 132 kV | 7316_Aramara 132 kV | Time | 16:30 | 18:00 | 22:30 | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00
WB | 83860136 | 7316 | Aramara 132 kV | 7316_Aramara 132 kV | Voltage at Constrained Conductor | 136.2278 | 136.5105 | 138.1547 | 136.8482 | 136.4704 | 137.2934 | 136.7287 | 136.3069 | 137.2137 | 136.6784 | 136.2627 | 137.186 | 136.5976 | 136.1565 | 138.4032
WB | 83860139 | 7315 | Aramara 132 kV | 7315_Aramara 132 kV | % of Rated A | 23.3496 | 23.7606 | 15.0512 | 23.0118 | 22.39 | 14.962 | 23.4259 | 22.8849 | 15.2643 | 23.6283 | 23.0502 | 15.3873 | 23.8857 | 23.3287 | 16.0098
WB | 83860139 | 7315 | Aramara 132 kV | 7315_Aramara 132 kV | Limiting Line Name | TR_LINE 86019_1 | TR_LINE 86019_1 | TR_LINE 86019_1 | TR_LINE 86019_1 | TR_LINE 86019_1 | TR_LINE 86019_1 | TR_LINE 86019_1 | TR_LINE 86019_1 | TR_LINE 86019_1 | TR_LINE 86019_1 | TR_LINE 86019_1 | TR_LINE 86019_1 | TR_LINE 86019_1 | TR_LINE 86019_1 | TR_LINE 86019_1
WB | 83860139 | 7315 | Aramara 132 kV | 7315_Aramara 132 kV | Loading (A) | 254.9707 | 286.3064 | 166.6163 | 251.2792 | 269.7891 | 165.6295 | 255.8007 | 275.7527 | 168.9755 | 258.0104 | 277.7446 | 170.3369 | 260.8211 | 281.1005 | 177.2282
WB | 83860139 | 7315 | Aramara 132 kV | 7315_Aramara 132 kV | Loading (MVA) | 60.1612 | 67.6952 | 39.8698 | 59.5602 | 63.771 | 39.3866 | 60.579 | 65.1025 | 40.1589 | 61.0798 | 65.5515 | 40.4743 | 61.7087 | 66.2919 | 42.4854
WB | 83860139 | 7315 | Aramara 132 kV | 7315_Aramara 132 kV | Loading (MW) | 58.4248 | 64.0405 | 39.202 | 55.622 | 59.5412 | 37.6588 | 56.5245 | 60.7092 | 38.3617 | 56.9863 | 61.1279 | 38.6576 | 57.5291 | 61.7449 | 39.5964
WB | 83860139 | 7315 | Aramara 132 kV | 7315_Aramara 132 kV | Power Factor | 0.97114 | 0.94601 | 0.98325 | 0.93388 | 0.93367 | 0.95613 | 0.93307 | 0.93252 | 0.95525 | 0.93298 | 0.93252 | 0.95511 | 0.93227 | 0.93141 | 0.932
WB | 83860139 | 7315 | Aramara 132 kV | 7315_Aramara 132 kV | Rating (A) | 1092 | 1205 | 1107 | 1092 | 1205 | 1107 | 1092 | 1205 | 1107 | 1092 | 1205 | 1107 | 1092 | 1205 | 1107
WB | 83860139 | 7315 | Aramara 132 kV | 7315_Aramara 132 kV | Time | 16:30 | 18:00 | 22:30 | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00 | 16:30 | 18:00 | 22:00
WB | 83860139 | 7315 | Aramara 132 kV | 7315_Aramara 132 kV | Voltage at Constrained Conductor | 136.2278 | 136.5104 | 138.1547 | 136.8481 | 136.4704 | 137.2934 | 136.7287 | 136.3068 | 137.2137 | 136.6783 | 136.2626 | 137.186 | 136.5975 | 136.1564 | 138.4032
WB | 83901293 | 6302 | BUNDABERG CENTRAL-WEST BUNDABERG | 6302_Bundaberg Central - WEBU 66 kV | % of Rated A | 69.7633 | 66.9786 | 75.7372 | 69.3201 | 67.1527 | 74.8529 | 69.2379 | 67.0898 | 74.789 | 69.3975 | 67.2805 | 75.0541 | 70.4727 | 68.2983 | 76.1285
WB | 83901293 | 6302 | BUNDABERG CENTRAL-WEST BUNDABERG | 6302_Bundaberg Central - WEBU 66 kV | Limiting Line Name | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1
WB | 83901293 | 6302 | BUNDABERG CENTRAL-WEST BUNDABERG | 6302_Bundaberg Central - WEBU 66 kV | Loading (A) | 276.9604 | 292.0266 | 269.6246 | 275.2008 | 292.7859 | 266.4764 | 274.8747 | 292.5114 | 266.2487 | 275.5081 | 293.3431 | 267.1924 | 279.7767 | 297.7807 | 271.0176
WB | 83901293 | 6302 | BUNDABERG CENTRAL-WEST BUNDABERG | 6302_Bundaberg Central - WEBU 66 kV | Loading (MVA) | 31.7399 | 33.5633 | 30.6652 | 31.4897 | 33.3333 | 30.5844 | 31.4476 | 33.2948 | 30.5578 | 31.5122 | 33.3775 | 30.6572 | 31.9732 | 33.8353 | 31.0604
WB | 83901293 | 6302 | BUNDABERG CENTRAL-WEST BUNDABERG | 6302_Bundaberg Central - WEBU 66 kV | Loading (MW) | 31.5523 | 33.4087 | 30.2927 | 31.1961 | 33.0612 | 30.0321 | 31.1486 | 33.0184 | 29.9997 | 31.2144 | 33.1039 | 30.1059 | 31.6741 | 33.5885 | 30.5448
WB | 83901293 | 6302 | BUNDABERG CENTRAL-WEST BUNDABERG | 6302_Bundaberg Central - WEBU 66 kV | Power Factor | 0.99409 | 0.99539 | 0.98785 | 0.99067 | 0.99184 | 0.98194 | 0.99049 | 0.9917 | 0.98174 | 0.99055 | 0.9918 | 0.98202 | 0.99064 | 0.9927 | 0.9834
WB | 83901293 | 6302 | BUNDABERG CENTRAL-WEST BUNDABERG | 6302_Bundaberg Central - WEBU 66 kV | Rating (A) | 397 | 436 | 356 | 397 | 436 | 356 | 397 | 436 | 356 | 397 | 436 | 356 | 397 | 436 | 356
WB | 83901293 | 6302 | BUNDABERG CENTRAL-WEST BUNDABERG | 6302_Bundaberg Central - WEBU 66 kV | Time | 16:30 | 17:00 | 22:30 | 16:30 | 17:00 | 22:30 | 16:30 | 17:00 | 22:30 | 16:30 | 17:00 | 22:30 | 16:30 | 17:00 | 22:30
WB | 83901293 | 6302 | BUNDABERG CENTRAL-WEST BUNDABERG | 6302_Bundaberg Central - WEBU 66 kV | Voltage at Constrained Conductor | 66.1649 | 66.3562 | 65.6639 | 66.0631 | 65.7305 | 66.2645 | 66.0529 | 65.7162 | 66.2634 | 66.0364 | 65.6927 | 66.2442 | 65.9803 | 65.6014 | 66.1682
WB | 84050534 | 7328 | S-FDTR132 | 7328_Bundaberg - ISIS No 2 132 kV | % of Rated A | 56.1394 | 34.0907 | 34.4018 | 62.5491 | 36.7574 | 37.5167 | 63.1132 | 37.4487 | 37.8576 | 63.2584 | 37.5293 | 37.9192 | 63.1337 | 37.382 | 37.8739
WB | 84050534 | 7328 | S-FDTR132 | 7328_Bundaberg - ISIS No 2 132 kV | Limiting Line Name | TR_LINE 98484_1 | TR_LINE 98484_1 | TR_LINE 98484_1 | TR_LINE 98484_1 | TR_LINE 98484_1 | TR_LINE 98484_1 | TR_LINE 98484_1 | TR_LINE 98484_1 | TR_LINE 98484_1 | TR_LINE 98484_1 | TR_LINE 98484_1 | TR_LINE 98484_1 | TR_LINE 98484_1 | TR_LINE 98484_1 | TR_LINE 98484_1
WB | 84050534 | 7328 | S-FDTR132 | 7328_Bundaberg - ISIS No 2 132 kV | Loading (A) | 139.2256 | 134.9991 | 135.1991 | 155.1217 | 145.5592 | 147.4406 | 156.5206 | 148.2969 | 148.7802 | 156.8809 | 148.6159 | 149.0223 | 156.5715 | 148.0327 | 148.8442
WB | 84050534 | 7328 | S-FDTR132 | 7328_Bundaberg - ISIS No 2 132 kV | Loading (MVA) | 33.1162 | 31.6083 | 32.3427 | 36.6332 | 33.9064 | 34.7991 | 36.9563 | 34.5189 | 35.1116 | 37.0394 | 34.5856 | 35.1673 | 36.9541 | 34.4265 | 35.1171
WB | 84050534 | 7328 | S-FDTR132 | 7328_Bundaberg - ISIS No 2 132 kV | Loading (MW) | 31.642 | 29.9109 | 30.8031 | 32.9534 | 31.2196 | 33.1474 | 33.4254 | 32.1301 | 33.5209 | 33.5192 | 32.2297 | 33.5832 | 33.4674 | 32.122 | 33.5405
WB | 84050534 | 7328 | S-FDTR132 | 7328_Bundaberg - ISIS No 2 132 kV | Power Factor | 0.95549 | 0.9463 | 0.9524 | 0.89955 | 0.92076 | 0.95253 | 0.90446 | 0.9308 | 0.95469 | 0.90496 | 0.93188 | 0.95496 | 0.90565 | 0.93306 | 0.9551
WB | 84050534 | 7328 | S-FDTR132 | 7328_Bundaberg - ISIS No 2 132 kV | Rating (A) | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393
WB | 84050534 | 7328 | S-FDTR132 | 7328_Bundaberg - ISIS No 2 132 kV | Time | 15:30 | 17:30 | 8:30 | 14:30 | 17:30 | 8:30 | 14:30 | 17:30 | 8:30 | 14:30 | 17:30 | 8:30 | 14:30 | 17:30 | 8:30
WB | 84050534 | 7328 | S-FDTR132 | 7328_Bundaberg - ISIS No 2 132 kV | Voltage at Constrained Conductor | 137.3284 | 135.1793 | 138.1152 | 136.3458 | 134.4875 | 136.2671 | 136.3188 | 134.3893 | 136.2527 | 136.3119 | 134.3599 | 136.2471 | 136.2665 | 134.2687 | 136.2153
WB | 85251782 | 6224 | 6366 66kV GOOTCHIE FDR | 6366_Gootchie 66 kV | % of Rated A | 62.3336 | 50.7619 | 26.1872 | 27.069 | 22.132 | 22.9029 | 27.0931 | 22.1563 | 22.4148 | 26.9173 | 22.1784 | 22.2197 | 26.9414 | 22.2035 | 21.9743
WB | 85251782 | 6224 | 6366 66kV GOOTCHIE FDR | 6366_Gootchie 66 kV | Limiting Line Name | TR_LINE 42255_1 | TR_LINE 42255_1 | TR_LINE 42255_1 | TR_LINE 7178_1 | TR_LINE 7178_1 | TR_LINE 7245_1 | TR_LINE 7178_1 | TR_LINE 7178_1 | TR_LINE 7245_1 | TR_LINE 7178_1 | TR_LINE 7178_1 | TR_LINE 7245_1 | TR_LINE 7178_1 | TR_LINE 7178_1 | TR_LINE 7245_1
WB | 85251782 | 6224 | 6366 66kV GOOTCHIE FDR | 6366_Gootchie 66 kV | Loading (A) | 82.2775 | 84.7695 | 41.6357 | 35.7311 | 36.9604 | 36.4156 | 35.7629 | 37.0011 | 35.6395 | 35.5308 | 37.0379 | 35.3293 | 35.5627 | 37.0798 | 34.9392
WB | 85251782 | 6224 | 6366 66kV GOOTCHIE FDR | 6366_Gootchie 66 kV | Loading (MVA) | 9.0778 | 9.3259 | 4.7706 | 4.1074 | 4.2606 | 4.3033 | 4.1075 | 4.2607 | 4.2088 | 4.1067 | 4.2608 | 4.1702 | 4.1068 | 4.261 | 4.125
WB | 85251782 | 6224 | 6366 66kV GOOTCHIE FDR | 6366_Gootchie 66 kV | Loading (MW) | 8.8446 | 9.0807 | 4.7199 | 3.9781 | 4.125 | 2.9914 | 3.9781 | 4.125 | 2.8698 | 3.978 | 4.125 | 2.8136 | 3.978 | 4.125 | 2.795
WB | 85251782 | 6224 | 6366 66kV GOOTCHIE FDR | 6366_Gootchie 66 kV | Power Factor | 0.97431 | 0.9737 | 0.98937 | 0.96854 | 0.96817 | 0.69513 | 0.96852 | 0.96815 | 0.68185 | 0.96866 | 0.96812 | 0.67469 | 0.96864 | 0.9681 | 0.67758
WB | 85251782 | 6224 | 6366 66kV GOOTCHIE FDR | 6366_Gootchie 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
WB | 85251782 | 6224 | 6366 66kV GOOTCHIE FDR | 6366_Gootchie 66 kV | Time | 16:30 | 17:00 | 22:00 | 16:30 | 17:30 | 3:30 | 16:30 | 17:30 | 3:30 | 16:30 | 17:30 | 3:30 | 16:30 | 17:30 | 3:30
WB | 85251782 | 6224 | 6366 66kV GOOTCHIE FDR | 6366_Gootchie 66 kV | Voltage at Constrained Conductor | 63.7001 | 63.5173 | 66.152 | 66.3675 | 66.5532 | 68.2263 | 66.3103 | 66.4823 | 68.1817 | 66.7306 | 66.4182 | 68.15 | 66.6725 | 66.3454 | 68.1635
NQ | 20003596 | CH-CC-1 | CHUMVALE-CLONCURRY | CH-CC-1_Chumvale-Cloncurry 66 kV | % of Rated A | 38.0492 | 36.9937 | 24.5571 | 37.0132 | 35.9911 | 23.896 | 37.0128 | 35.9907 | 23.8958 | 37.0132 | 35.9911 | 23.896 | 36.7156 | 36.1558 | 24.0078
NQ | 20003596 | CH-CC-1 | CHUMVALE-CLONCURRY | CH-CC-1_Chumvale-Cloncurry 66 kV | Limiting Line Name | TR_LINE 181845_1 | TR_LINE 181845_1 | TR_LINE 181845_1 | TR_LINE 181845_1 | TR_LINE 181845_1 | TR_LINE 181845_1 | TR_LINE 181845_1 | TR_LINE 181845_1 | TR_LINE 181845_1 | TR_LINE 181845_1 | TR_LINE 181845_1 | TR_LINE 181845_1 | TR_LINE 181845_1 | TR_LINE 181845_1 | TR_LINE 181845_1
NQ | 20003596 | CH-CC-1 | CHUMVALE-CLONCURRY | CH-CC-1_Chumvale-Cloncurry 66 kV | Loading (A) | 62.0095 | 67.3176 | 42.2285 | 60.3208 | 65.4929 | 41.0914 | 60.3202 | 65.4922 | 41.0911 | 60.3208 | 65.4929 | 41.0914 | 59.8357 | 65.7927 | 41.2838
NQ | 20003596 | CH-CC-1 | CHUMVALE-CLONCURRY | CH-CC-1_Chumvale-Cloncurry 66 kV | Loading (MVA) | 7.0019 | 7.6567 | 4.8118 | 6.815 | 7.4534 | 4.6839 | 6.815 | 7.4534 | 4.6839 | 6.815 | 7.4534 | 4.6839 | 6.815 | 7.4532 | 4.684
NQ | 20003596 | CH-CC-1 | CHUMVALE-CLONCURRY | CH-CC-1_Chumvale-Cloncurry 66 kV | Loading (MW) | 6.9143 | 7.5604 | 4.7634 | 6.7313 | 7.3608 | 4.6375 | 6.7313 | 7.3608 | 4.6375 | 6.7313 | 7.3608 | 4.6375 | 6.7312 | 7.3608 | 4.6375
NQ | 20003596 | CH-CC-1 | CHUMVALE-CLONCURRY | CH-CC-1_Chumvale-Cloncurry 66 kV | Power Factor | 0.98749 | 0.98743 | 0.98993 | 0.98771 | 0.98758 | 0.9901 | 0.98771 | 0.98758 | 0.9901 | 0.98771 | 0.98758 | 0.9901 | 0.98771 | 0.9876 | 0.99009
NQ | 20003596 | CH-CC-1 | CHUMVALE-CLONCURRY | CH-CC-1_Chumvale-Cloncurry 66 kV | Rating (A) | 163 | 182 | 172 | 163 | 182 | 172 | 163 | 182 | 172 | 163 | 182 | 172 | 163 | 182 | 172
NQ | 20003596 | CH-CC-1 | CHUMVALE-CLONCURRY | CH-CC-1_Chumvale-Cloncurry 66 kV | Time | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00 | 16:30 | 18:30 | 22:00
NQ | 20003596 | CH-CC-1 | CHUMVALE-CLONCURRY | CH-CC-1_Chumvale-Cloncurry 66 kV | Voltage at Constrained Conductor | 65.1926 | 65.6677 | 65.7876 | 65.2289 | 65.7054 | 65.8106 | 65.2296 | 65.7061 | 65.8111 | 65.2289 | 65.7054 | 65.8106 | 65.7573 | 65.4044 | 65.5049
NQ | 20005445 | DR-CC-1 | DUCHESSRD-CLONCURRY | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | % of Rated A | 14.3515 | 8.7334 | 8.462 | 14.3525 | 8.7345 | 8.4625 | 14.3527 | 8.7347 | 8.4626 | 14.3525 | 8.7345 | 8.4625 | 14.2938 | 8.6983 | 8.4285
NQ | 20005445 | DR-CC-1 | DUCHESSRD-CLONCURRY | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Limiting Line Name | TR_LINE 234732_1 | TR_LINE 234732_1 | TR_LINE 234732_1 | TR_LINE 234732_1 | TR_LINE 234732_1 | TR_LINE 234732_1 | TR_LINE 234732_1 | TR_LINE 234732_1 | TR_LINE 234732_1 | TR_LINE 234732_1 | TR_LINE 234732_1 | TR_LINE 234732_1 | TR_LINE 234732_1 | TR_LINE 234732_1 | TR_LINE 234732_1
NQ | 20005445 | DR-CC-1 | DUCHESSRD-CLONCURRY | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Loading (A) | 11.9118 | 11.8775 | 11.9315 | 11.9126 | 11.8789 | 11.9322 | 11.9128 | 11.8792 | 11.9323 | 11.9126 | 11.8789 | 11.9322 | 11.8639 | 11.8297 | 11.8842
NQ | 20005445 | DR-CC-1 | DUCHESSRD-CLONCURRY | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Loading (MVA) | 1.4264 | 1.4185 | 1.4309 | 1.4266 | 1.4188 | 1.4311 | 1.4266 | 1.4188 | 1.4311 | 1.4266 | 1.4188 | 1.4311 | 1.4153 | 1.4075 | 1.42
NQ | 20005445 | DR-CC-1 | DUCHESSRD-CLONCURRY | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Loading (MW) | 0.092879 | 0.092836 | 0.092904 | 0.09288 | 0.092838 | 0.092905 | 0.09288 | 0.092838 | 0.092905 | 0.09288 | 0.092838 | 0.092905 | 0.092819 | 0.092776 | 0.092844
NQ | 20005445 | DR-CC-1 | DUCHESSRD-CLONCURRY | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Power Factor | 0.065115 | 0.065449 | 0.064925 | 0.065108 | 0.065435 | 0.064918 | 0.065106 | 0.065432 | 0.064917 | 0.065108 | 0.065435 | 0.064918 | 0.065582 | 0.065917 | 0.065383
NQ | 20005445 | DR-CC-1 | DUCHESSRD-CLONCURRY | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Rating (A) | 83 | 136 | 141 | 83 | 136 | 141 | 83 | 136 | 141 | 83 | 136 | 141 | 83 | 136 | 141
NQ | 20005445 | DR-CC-1 | DUCHESSRD-CLONCURRY | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Time | 9:00 | 20:30 | 7:00 | 9:00 | 20:30 | 7:00 | 9:00 | 20:30 | 7:00 | 9:00 | 20:30 | 7:00 | 9:00 | 20:30 | 7:00
NQ | 20005445 | DR-CC-1 | DUCHESSRD-CLONCURRY | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Voltage at Constrained Conductor | 69.1349 | 68.9494 | 69.2416 | 69.1393 | 68.9569 | 69.2454 | 69.1403 | 68.9587 | 69.2462 | 69.1393 | 68.9569 | 69.2454 | 68.8757 | 68.691 | 68.9856
NQ | 20010431 | MICB - DURO 1 | MICA CK B - DUCHESS ROAD NO.01 | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | % of Rated A | 18.2598 | 14.9926 | 12.0919 | 18.0978 | 14.8596 | 11.9849 | 18.0441 | 14.8154 | 11.9493 | 18.0978 | 14.8596 | 11.9849 | 18.3825 | 15.0929 | 12.1732
NQ | 20010431 | MICB - DURO 1 | MICA CK B - DUCHESS ROAD NO.01 | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Limiting Line Name | TR_LINE 32596_1 | TR_LINE 32596_1 | TR_LINE 210013_1 | TR_LINE 32596_1 | TR_LINE 32596_1 | TR_LINE 210013_1 | TR_LINE 32596_1 | TR_LINE 32596_1 | TR_LINE 210013_1 | TR_LINE 32596_1 | TR_LINE 32596_1 | TR_LINE 210013_1 | TR_LINE 32596_1 | TR_LINE 32596_1 | TR_LINE 210013_1
NQ | 20010431 | MICB - DURO 1 | MICA CK B - DUCHESS ROAD NO.01 | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Loading (A) | 70.1176 | 73.6137 | 55.8648 | 69.4957 | 72.9605 | 55.37 | 69.2894 | 72.7438 | 55.2056 | 69.4957 | 72.9605 | 55.37 | 70.589 | 74.106 | 56.2403
NQ | 20010431 | MICB - DURO 1 | MICA CK B - DUCHESS ROAD NO.01 | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Loading (MVA) | 16.393 | 17.2346 | 13.0983 | 16.2489 | 17.0831 | 12.9829 | 16.2008 | 17.0326 | 12.9445 | 16.2489 | 17.0831 | 12.9829 | 16.4416 | 17.2859 | 13.1376
NQ | 20010431 | MICB - DURO 1 | MICA CK B - DUCHESS ROAD NO.01 | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Loading (MW) | 16.2368 | 17.0671 | 13.0304 | 16.0946 | 16.9177 | 12.9163 | 16.0472 | 16.8679 | 12.8782 | 16.0946 | 16.9177 | 12.9163 | 16.2843 | 17.1171 | 13.0686
NQ | 20010431 | MICB - DURO 1 | MICA CK B - DUCHESS ROAD NO.01 | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Power Factor | 0.99047 | 0.99028 | 0.99481 | 0.99051 | 0.99032 | 0.99487 | 0.99052 | 0.99033 | 0.99488 | 0.99051 | 0.99032 | 0.99487 | 0.99043 | 0.99024 | 0.99475
NQ | 20010431 | MICB - DURO 1 | MICA CK B - DUCHESS ROAD NO.01 | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Rating (A) | 384 | 491 | 462 | 384 | 491 | 462 | 384 | 491 | 462 | 384 | 491 | 462 | 384 | 491 | 462
NQ | 20010431 | MICB - DURO 1 | MICA CK B - DUCHESS ROAD NO.01 | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Time | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00
NQ | 20010431 | MICB - DURO 1 | MICA CK B - DUCHESS ROAD NO.01 | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Voltage at Constrained Conductor | 134.9802 | 135.1707 | 135.3685 | 134.9909 | 135.1815 | 135.3745 | 134.9925 | 135.1833 | 135.3754 | 134.9909 | 135.1815 | 135.3745 | 134.477 | 134.6719 | 134.8674
NQ | 20010432 | MICB - DURO 2 | MICA CREEKB-DUCHESSRD NO.02 | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | % of Rated A | 25.0684 | 21.2797 | 16.6679 | 24.8469 | 21.0915 | 16.5217 | 24.7734 | 21.029 | 16.4731 | 24.8469 | 21.0915 | 16.5217 | 25.237 | 21.4221 | 16.7791
NQ | 20010432 | MICB - DURO 2 | MICA CREEKB-DUCHESSRD NO.02 | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Limiting Line Name | TR_LINE 174420_1 | TR_LINE 174420_1 | TR_LINE 174420_1 | TR_LINE 174420_1 | TR_LINE 174420_1 | TR_LINE 174420_1 | TR_LINE 174420_1 | TR_LINE 174420_1 | TR_LINE 174420_1 | TR_LINE 174420_1 | TR_LINE 174420_1 | TR_LINE 174420_1 | TR_LINE 174420_1 | TR_LINE 174420_1 | TR_LINE 174420_1
NQ | 20010432 | MICB - DURO 2 | MICA CREEKB-DUCHESSRD NO.02 | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Loading (A) | 69.9402 | 73.4141 | 56.0038 | 69.3222 | 72.7648 | 55.5125 | 69.1172 | 72.5494 | 55.3493 | 69.3222 | 72.7648 | 55.5125 | 70.4104 | 73.9053 | 56.3775
NQ | 20010432 | MICB - DURO 2 | MICA CREEKB-DUCHESSRD NO.02 | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Loading (MVA) | 16.3552 | 17.1918 | 13.1216 | 16.2119 | 17.0411 | 13.0071 | 16.1642 | 16.9909 | 12.969 | 16.2119 | 17.0411 | 13.0071 | 16.4038 | 17.243 | 13.1601
NQ | 20010432 | MICB - DURO 2 | MICA CREEKB-DUCHESSRD NO.02 | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Loading (MW) | 16.3318 | 17.1622 | 13.1171 | 16.1897 | 17.0128 | 13.0031 | 16.1423 | 16.9629 | 12.9651 | 16.1897 | 17.0128 | 13.0031 | 16.3793 | 17.2121 | 13.1551
NQ | 20010432 | MICB - DURO 2 | MICA CREEKB-DUCHESSRD NO.02 | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Power Factor | 0.99857 | 0.99828 | 0.99966 | 0.99863 | 0.99833 | 0.99969 | 0.99865 | 0.99835 | 0.9997 | 0.99863 | 0.99833 | 0.99969 | 0.99851 | 0.99821 | 0.99962
NQ | 20010432 | MICB - DURO 2 | MICA CREEKB-DUCHESSRD NO.02 | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Rating (A) | 279 | 345 | 336 | 279 | 345 | 336 | 279 | 345 | 336 | 279 | 345 | 336 | 279 | 345 | 336
NQ | 20010432 | MICB - DURO 2 | MICA CREEKB-DUCHESSRD NO.02 | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Time | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00 | 16:30 | 19:00 | 22:00
NQ | 20010432 | MICB - DURO 2 | MICA CREEKB-DUCHESSRD NO.02 | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Voltage at Constrained Conductor | 135.0105 | 135.2018 | 135.2718 | 135.021 | 135.2125 | 135.2789 | 135.0227 | 135.2142 | 135.2802 | 135.021 | 135.2125 | 135.2789 | 134.5073 | 134.703 | 134.7696
NQ | 20010433 | CHUM | MICC - CHUM 220KV FDR 7018 | 7018_Mica Creek C - Chumvale 220 kV | % of Rated A | 24.8203 | 21.2299 | 22.8046 | 24.7603 | 21.1694 | 22.774 | 24.7601 | 21.1692 | 22.7739 | 24.7603 | 21.1694 | 22.774 | 24.8967 | 21.2828 | 22.8877
NQ | 20010433 | CHUM | MICC - CHUM 220KV FDR 7018 | 7018_Mica Creek C - Chumvale 220 kV | Limiting Line Name | TR_LINE 174437_1 | TR_LINE 174437_1 | TR_LINE 174437_1 | TR_LINE 174437_1 | TR_LINE 174437_1 | TR_LINE 174437_1 | TR_LINE 174437_1 | TR_LINE 174437_1 | TR_LINE 174437_1 | TR_LINE 174437_1 | TR_LINE 174437_1 | TR_LINE 174437_1 | TR_LINE 174437_1 | TR_LINE 174437_1 | TR_LINE 174437_1
NQ | 20010433 | CHUM | MICC - CHUM 220KV FDR 7018 | 7018_Mica Creek C - Chumvale 220 kV | Loading (A) | 212.2132 | 197.4384 | 198.8561 | 211.7009 | 196.8756 | 198.5894 | 211.6989 | 196.8733 | 198.5882 | 211.7009 | 196.8756 | 198.5894 | 212.8668 | 197.9299 | 199.581
NQ | 20010433 | CHUM | MICC - CHUM 220KV FDR 7018 | 7018_Mica Creek C - Chumvale 220 kV | Loading (MVA) | 80.304 | 75.598 | 75.7856 | 80.1264 | 75.3991 | 75.6912 | 80.1263 | 75.399 | 75.6912 | 80.1264 | 75.3991 | 75.6912 | 80.1871 | 75.4543 | 75.7279
NQ | 20010433 | CHUM | MICC - CHUM 220KV FDR 7018 | 7018_Mica Creek C - Chumvale 220 kV | Loading (MW) | 77.507 | 73.3556 | 73.2237 | 77.337 | 73.1653 | 73.1318 | 77.337 | 73.1653 | 73.1318 | 77.337 | 73.1653 | 73.1318 | 77.3407 | 73.1688 | 73.1346
NQ | 20010433 | CHUM | MICC - CHUM 220KV FDR 7018 | 7018_Mica Creek C - Chumvale 220 kV | Power Factor | 0.96517 | 0.97034 | 0.9662 | 0.96519 | 0.97037 | 0.96619 | 0.96519 | 0.97038 | 0.96619 | 0.96519 | 0.97037 | 0.96619 | 0.9645 | 0.96971 | 0.96575
NQ | 20010433 | CHUM | MICC - CHUM 220KV FDR 7018 | 7018_Mica Creek C - Chumvale 220 kV | Rating (A) | 855 | 930 | 872 | 855 | 930 | 872 | 855 | 930 | 872 | 855 | 930 | 872 | 855 | 930 | 872
NQ | 20010433 | CHUM | MICC - CHUM 220KV FDR 7018 | 7018_Mica Creek C - Chumvale 220 kV | Time | 15:30 | 17:00 | 0:00 | 15:30 | 17:00 | 0:00 | 15:30 | 17:00 | 0:00 | 15:30 | 17:00 | 0:00 | 15:30 | 17:00 | 0:00
NQ | 20010433 | CHUM | MICC - CHUM 220KV FDR 7018 | 7018_Mica Creek C - Chumvale 220 kV | Voltage at Constrained Conductor | 218.4763 | 221.064 | 220.0326 | 218.5205 | 221.1126 | 220.0538 | 218.5223 | 221.1148 | 220.055 | 218.5205 | 221.1126 | 220.0538 | 217.4882 | 220.0959 | 219.0666
NQ | 84431571 | MICC-MICB 1 | MICA CREEK 'C' TO MICA CREEK 'B' 1 | MICC-MICB No 1 132 kV | % of Rated A | 49.4417 | 33.8366 | 33.8813 | 49.3632 | 33.7916 | 33.8515 | 49.3628 | 33.7914 | 33.8514 | 49.3632 | 33.7916 | 33.8515 | 49.5921 | 33.9342 | 33.9958
NQ | 84431571 | MICC-MICB 1 | MICA CREEK 'C' TO MICA CREEK 'B' 1 | MICC-MICB No 1 132 kV | Limiting Line Name | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1
NQ | 84431571 | MICC-MICB 1 | MICA CREEK 'C' TO MICA CREEK 'B' 1 | MICC-MICB No 1 132 kV | Loading (A) | 258.0812 | 243.2828 | 243.9428 | 257.6715 | 242.9598 | 243.7287 | 257.6695 | 242.9581 | 243.7275 | 257.6715 | 242.9598 | 243.7287 | 258.8661 | 243.9844 | 244.7668
NQ | 84431571 | MICC-MICB 1 | MICA CREEK 'C' TO MICA CREEK 'B' 1 | MICC-MICB No 1 132 kV | Loading (MVA) | 60.3658 | 57.0174 | 57.1846 | 60.2735 | 56.9444 | 57.1362 | 60.2734 | 56.9443 | 57.1362 | 60.2735 | 56.9444 | 57.1362 | 60.3241 | 56.9711 | 57.166
NQ | 84431571 | MICC-MICB 1 | MICA CREEK 'C' TO MICA CREEK 'B' 1 | MICC-MICB No 1 132 kV | Loading (MW) | 60.0989 | 56.954 | 57.0981 | 60.0117 | 56.8829 | 57.0511 | 60.0116 | 56.8829 | 57.0511 | 60.0117 | 56.8829 | 57.0511 | 60.021 | 56.8908 | 57.059
NQ | 84431571 | MICC-MICB 1 | MICA CREEK 'C' TO MICA CREEK 'B' 1 | MICC-MICB No 1 132 kV | Power Factor | 0.99558 | 0.99889 | 0.99849 | 0.99566 | 0.99892 | 0.99851 | 0.99566 | 0.99892 | 0.99851 | 0.99566 | 0.99892 | 0.99851 | 0.99498 | 0.99859 | 0.99813
NQ | 84431571 | MICC-MICB 1 | MICA CREEK 'C' TO MICA CREEK 'B' 1 | MICC-MICB No 1 132 kV | Rating (A) | 522 | 719 | 720 | 522 | 719 | 720 | 522 | 719 | 720 | 522 | 719 | 720 | 522 | 719 | 720
NQ | 84431571 | MICC-MICB 1 | MICA CREEK 'C' TO MICA CREEK 'B' 1 | MICC-MICB No 1 132 kV | Time | 15:30 | 21:30 | 0:00 | 15:30 | 21:30 | 0:00 | 15:30 | 21:30 | 0:00 | 15:30 | 21:30 | 0:00 | 15:30 | 21:30 | 0:00
NQ | 84431571 | MICC-MICB 1 | MICA CREEK 'C' TO MICA CREEK 'B' 1 | MICC-MICB No 1 132 kV | Voltage at Constrained Conductor | 135.0435 | 135.3117 | 135.3414 | 135.0514 | 135.3181 | 135.3456 | 135.0522 | 135.3189 | 135.3462 | 135.0514 | 135.3181 | 135.3456 | 134.5411 | 134.8131 | 134.8418
NQ | 84431576 | MICC-MICB 2 | MICA CREEK 'C' TO MICA CREEK 'B' 2 | MICC-MICB No 2 132 kV | % of Rated A | 49.6141 | 33.9546 | 33.9995 | 49.5354 | 33.9095 | 33.9696 | 49.535 | 33.9093 | 33.9695 | 49.5354 | 33.9095 | 33.9696 | 49.7651 | 34.0526 | 34.1144
NQ | 84431576 | MICC-MICB 2 | MICA CREEK 'C' TO MICA CREEK 'B' 2 | MICC-MICB No 2 132 kV | Limiting Line Name | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1
NQ | 84431576 | MICC-MICB 2 | MICA CREEK 'C' TO MICA CREEK 'B' 2 | MICC-MICB No 2 132 kV | Loading (A) | 258.982 | 244.1317 | 244.794 | 258.5709 | 243.8076 | 244.5792 | 258.5688 | 243.8059 | 244.578 | 258.5709 | 243.8076 | 244.5792 | 259.7696 | 244.8358 | 245.621
NQ | 84431576 | MICC-MICB 2 | MICA CREEK 'C' TO MICA CREEK 'B' 2 | MICC-MICB No 2 132 kV | Loading (MVA) | 60.5765 | 57.2163 | 57.3842 | 60.4838 | 57.1431 | 57.3356 | 60.4837 | 57.143 | 57.3355 | 60.4838 | 57.1431 | 57.3356 | 60.5347 | 57.1699 | 57.3655
NQ | 84431576 | MICC-MICB 2 | MICA CREEK 'C' TO MICA CREEK 'B' 2 | MICC-MICB No 2 132 kV | Loading (MW) | 60.3086 | 57.1527 | 57.2974 | 60.2211 | 57.0814 | 57.2502 | 60.2211 | 57.0814 | 57.2502 | 60.2211 | 57.0814 | 57.2502 | 60.2305 | 57.0894 | 57.2582
NQ | 84431576 | MICC-MICB 2 | MICA CREEK 'C' TO MICA CREEK 'B' 2 | MICC-MICB No 2 132 kV | Power Factor | 0.99558 | 0.99889 | 0.99849 | 0.99566 | 0.99892 | 0.99851 | 0.99566 | 0.99892 | 0.99851 | 0.99566 | 0.99892 | 0.99851 | 0.99498 | 0.99859 | 0.99813
NQ | 84431576 | MICC-MICB 2 | MICA CREEK 'C' TO MICA CREEK 'B' 2 | MICC-MICB No 2 132 kV | Rating (A) | 522 | 719 | 720 | 522 | 719 | 720 | 522 | 719 | 720 | 522 | 719 | 720 | 522 | 719 | 720
NQ | 84431576 | MICC-MICB 2 | MICA CREEK 'C' TO MICA CREEK 'B' 2 | MICC-MICB No 2 132 kV | Time | 15:30 | 21:30 | 0:00 | 15:30 | 21:30 | 0:00 | 15:30 | 21:30 | 0:00 | 15:30 | 21:30 | 0:00 | 15:30 | 21:30 | 0:00
NQ | 84431576 | MICC-MICB 2 | MICA CREEK 'C' TO MICA CREEK 'B' 2 | MICC-MICB No 2 132 kV | Voltage at Constrained Conductor | 135.0435 | 135.3117 | 135.3414 | 135.0514 | 135.3181 | 135.3456 | 135.0522 | 135.3189 | 135.3462 | 135.0514 | 135.3181 | 135.3456 | 134.5411 | 134.8131 | 134.8418
SW |  |  | F049R_Roma North 33 kV |  | % of Rated A | 53.87% | 46.1% | 22.8% | 53.87% | 46.1% | 22.8% | 53.87% | 46.1% | 22.8% | 53.87% | 46.1% | 22.8% | 53.87% | 46.1% | 22.8%
SW |  |  | F049R_Roma North 33 kV |  | Limiting Line Name | TR_LINE 22900_1 | TR_LINE 22900_1 | TR_LINE 22900_1 | TR_LINE 22900_1 | TR_LINE 22900_1 | TR_LINE 22900_1 | TR_LINE 22900_1 | TR_LINE 22900_1 | TR_LINE 22900_1 | TR_LINE 22900_1 | TR_LINE 22900_1 | TR_LINE 22900_1 | TR_LINE 22900_1 | TR_LINE 22900_1 | TR_LINE 22900_1
SW |  |  | F049R_Roma North 33 kV |  | Loading (A) | 50.1031 | 55.8213 | 26.5116 | 50.1031 | 55.8213 | 26.5116 | 50.1031 | 55.8213 | 26.5116 | 50.1031 | 55.8213 | 26.5116 | 50.1031 | 55.8213 | 26.5116
SW |  |  | F049R_Roma North 33 kV |  | Loading (MVA) | 2.7993 | 3.1212 | 1.4878 | 2.7993 | 3.1212 | 1.4878 | 2.7993 | 3.1212 | 1.4878 | 2.7993 | 3.1212 | 1.4878 | 2.7993 | 3.1212 | 1.4878
SW |  |  | F049R_Roma North 33 kV |  | Loading (MW) | 2.6693 | 2.9812 | 1.4696 | 2.6693 | 2.9812 | 1.4696 | 2.6693 | 2.9812 | 1.4696 | 2.6693 | 2.9812 | 1.4696 | 2.6693 | 2.9812 | 1.4696
SW |  |  | F049R_Roma North 33 kV |  | Power Factor | 0.95355 | 0.95516 | 0.98773 | 0.95355 | 0.95516 | 0.98773 | 0.95355 | 0.95516 | 0.98773 | 0.95355 | 0.95516 | 0.98773 | 0.95355 | 0.95516 | 0.98773
SW |  |  | F049R_Roma North 33 kV |  | Rating (A) | 93 | 121 | 116 | 93 | 121 | 116 | 93 | 121 | 116 | 93 | 121 | 116 | 93 | 121 | 116
SW |  |  | F049R_Roma North 33 kV |  | Time | 16:30:00 | 19:00 | 5:30 | 16:30:00 | 19:00 | 5:30 | 16:30:00 | 19:00 | 5:30 | 16:30:00 | 19:00 | 5:30 | 16:30:00 | 19:00 | 5:30
SW |  |  | F049R_Roma North 33 kV |  | Voltage at Constrained Conductor | 32.2 | 32.2 | 32.4 | 32.2 | 32.2 | 32.4 | 32.2 | 32.2 | 32.4 | 32.2 | 32.2 | 32.4 | 32.2 | 32.2 | 32.4