## Disclaimer
Distribution Feeder Limitations
(Ergon Energy Distribution Annual Planning Report 2020)
This workbook forms part of the Ergon Energy Distribution Annual Planning Report 2020 (DAPR) and should be read in conjunction with the report document.
Readers are encouraged to take into account the details and content portrayed in the ‘Introduction & Notes’ section of this workbook when reviewing the associated data.
Disclaimer
Ergon Energy’s Distribution Annual Planning Report (DAPR) is prepared and made available solely for information purposes. While care was taken in the preparation of the information in the DAPR, and it is provided in good faith, Ergon Energy accepts no responsibility or liability (including without limitation, liability to any person by reason of negligence or negligent mis-statement) for any loss or damage that may be incurred by any person acting in reliance on this information or assumptions drawn from it, except to the extent that liability under any applicable Queensland or Commonwealth of Australia statute cannot be excluded.
It contains assumptions regarding, among other things, economic growth and load forecasts which may or may not prove to be correct. The forecasts included in the DAPR involve subjective judgements and analysis which are subject to significant uncertainties and contingencies, many of which are out of the control of Ergon Energy. Ergon Energy makes no representation or warranty as to the accuracy, reliability, completeness or suitability for any particular purpose of the information in this document. All information should be independently investigated, reviewed, analysed and verified, and must not be relied upon in connection with any investment proposal or decision. The information contained in the DAPR is subject to annual review. Ergon Energy is obligated to publish future editions by 31st December, in accordance with the National Electricity Rules.
All financials presented in the DAPR or within this document are correct at the time of writing and represent the existing organisational accounting treatment, which may be subject to change. Energy Queensland is finalising the alignment of its Cost Allocation Methodology between Ergon Energy and Energex, potentially impacting the treatment of some Capital and Operational Project costs.
Forecasted data is subject to ongoing variation due to COVID 19 impacts.
All presented project costings and milestones (as of October 2020) are subject to change.

## Introduction & Notes
Distribution Feeder Limitations
(Ergon Energy Distribution Annual Planning Report 2020)
This workbook presents primary distribution feeders which are currently experiencing overload or are forecast to experience an overload in the next 2 years.
This workbook forms part of the Ergon Energy Distribution Annual Planning Report 2020 (DAPR) and should be read in conjunction with the report document.
Forecasted data is subject to ongoing variation due to COVID 19 impacts.
Contents
The 'Distribution Feeder Limitations' tab of this workbook includes the following information for each constrained distribution feeder:
- Ergon Energy region
- Distribution feeder name, ID & location
- Load exceedance after 2 yrs (MVA)
- Forecast season that exceedance occurs (Summer / Winter)
- Forecast year that exceedance occurs
- Forecast month/s that exceedance occurs
- Load reduction needed to delay the exceedance by 12 months (MW)
(assumed power factor of 0.9)
1. Potential Solutions
Suggested solutions, in order or preference, are included under the 'Potential Solutions' tab.
2. Committed Solutions:
Committed investments to address current distribution network limitations are included under the 'Committed Solutions' tab.
Connection points for possible load reduction:
In all cases, the connection point to apply load reduction would be downsteam of the substation exit feeder cable and/or first section of line.
Exclusions:
Dedicated customer connection assets are excluded from the analysis.
NOTE: All financials presented in this document are correct at the time of writing (i.e. October 2020) and represent the existing organisational accounting treatment, which may be subject to change. Energy Queensland is still finalising the alignment of its Cost Allocation Methodology between Ergon and Energex, potentially impacting the treatment of some Capital and Operational Project costs.

## Potential Solutions
Solutions:
Distribution feeder capacity problems can be solved in a number of ways, depending on the local characteristics of the distribution feeder. The constraints identified in this document are a trigger for further planning studies and in many cases do not constitute plant risk, are acceptable, and do not require augmentation due to multiple factors such as:
- Minimal load growth on the feeder and/or adjacent feeders.
- Customer density or feeder topology constraints that do not allow for planning constraints to be met.
- Feeder topology that allows for simple switching in a contingency but for regional depot support is configured in a certain manner.
- Short term customer behaviour changes (such as abnormal weather conditions).
- Medium term network topology changes due to planned works in a region.
Where action is required to solve a feeder constraint, possible solutions (in approximate order of preference based on network cost) include:
Network Reconfiguration
- Transferring existing load to adjacent feeders if capacity is available; and
- Re-rating or dynamic rating of the underground exit cable or overhead feeder.
Demand Management initiatives that reduce customer loading
- Energy efficient appliances
- Power factor correction
- Shift loads (e.g. pool pumps, HW storage etc.) to control load tariff
- Shift loads to a time-of-use tariff
- Air conditioning ‘Peak Smart’
- Customer EG units
- Call off load
- Commercial and industrial demand management
- Customer embedded generation to ‘peak lop’
- Network embedded generation to ‘peak lop’
- Energy storage.
Network Augmentation
- Replacing the underground exit cable or overhead feeder
- Creating new substations and/or feeders and transferring existing load.
In each instance, actual solutions are subject to a detailed study and business case. In some cases, a committed project is already in place.

## Distribution Feeder Limit 2020
Distribution Feeder Limitations (Ergon Energy Distribution Annual Planning Report 2020)
Region | Feeder name | Feeder ID | Feeder Location | Load exceedance after 2 yrs (MVA) | Season of exceedance | Year of exceedance | Month of exceedance | Load reduction to defer exceedance by 12 mths (MW) @ 0.9pf | Connection Point | Potenital Solutions
Southern | GV-E | 50000062 | GIVELDA 66/11KV SUB (GV) | 2.3008 | Summer | 2019/2019 | Dec-Feb | 2.0707 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | MG-F | 50000128 | MURGON 66/11KV SUB (MG) | 0.89656 | Summer | 2019/2019 | Dec-Feb | 0.8069 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | GE-01 | 25273297 | GLENELG 66/19.1KV SUB (GLEE) | 0.049582 | Summer | 2019/2019 | Dec-Feb | 0.044624 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | DG-10 | 20004903 | DAN GLEESON 132/66/11KV SUB (DAGL) | 1.9075 | Summer | 2019/2019 | Dec-Feb | 1.6657 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | F3385 | 60026776 | PAMPAS 33/11KV SUB (ME027) | 0.35443 | Summer | 2019/2019 | Dec-Feb | 0.35226 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | RM-05 | 20011656 | RASMUSSEN 66/11KV SUB (RASM) | 1.3035 | Summer | 2019/2019 | Dec-Feb | 1.0952 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | F073C | 60026673 | CHINCHILLA 132/110/33KV SUB (T013) | 2.341 | Summer | 2019/2019 | Dec-Feb | 2.1069 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | KR-C | 50000092 | KINGAROY 66/11KV SUB (KING) | 1.6222 | Summer | 2019/2019 | Dec-Feb | 1.4095 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | RM-08 | 20011759 | RASMUSSEN 66/11KV SUB (RASM) | 1.0659 | Summer | 2019/2019 | Dec-Feb | 0.95932 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | GE-03 | 25273293 | GLENELG 66/19.1KV SUB (GLEE) | 0.016582 | Summer | 2019/2019 | Dec-Feb | 0.014924 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | RS109 | 40001146 | ROCKHAMPTON SOUTH 66/11KV SUB (RSSS) | 0.74497 | Summer | 2019/2019 | Dec-Feb | 0.70076 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | IN-08 | 25273220 | INGHAM 132/66/11KV SUB (INGH) | 0.42475 | Summer | 2019/2019 | Dec-Feb | 0.38228 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | BL-02 | 20002331 | BLUEWATER 66/11KV SUB (BLUE) | 0.63716 | Summer | 2019/2019 | Dec-Feb | 0.54084 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | F3521 | 82912904 | KEARNEYS SPRINGS 110/11KV SUB (KESP) | 2.0332 | Winter | 2019/2019 | Mar-Nov | 1.814 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | 2GO3 | 10020782 | EDMONTON 132/22KV SUB (EDMONTON) | 2.1625 | Summer | 2019/2019 | Dec-Feb | 1.7911 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | WB-J | 50000211 | WEST BUNDABERG 66/11KV SUB (WEBU) | 1.3583 | Summer | 2019/2019 | Dec-Feb | 1.1697 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | F3843 | 60026797 | OAKEY 33/11KV SUB (OAKE) | 1.2619 | Summer | 2019/2019 | Dec-Feb | 1.1467 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | BN-07 | 20002698 | BOWEN 66/11KV SUB (BOWE) | 0.86027 | Summer | 2019/2019 | Dec-Feb | 0.73882 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | WL-A | 50000229 | WOOLOOGA 66/11KV SUB (WL) | 0.17834 | Summer | 2019/2019 | Dec-Feb | 0.1605 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | F4610 | 60330968 | TORRINGTON (T116) 110/33/11KV SUB (T116) | 1.2249 | Winter | 2019/2019 | Mar-Nov | 0.96257 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | F3352 | 82991938 | HIGHFIELDS 33/0.415KV SUB (ME024) | 0.18709 | Summer | 2019/2019 | Dec-Feb | 0.12558 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | 2HAM | 83896573 | EDMONTON 132/22KV SUB (EDMONTON) | 1.4148 | Summer | 2019/2019 | Dec-Feb | 1.1537 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | BO-07 | 20003026 | BOHLE 66/11KV SUB (BOHL) | 0.80074 | Summer | 2019/2019 | Dec-Feb | 0.68055 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | RG114 | 40001135 | RTON GLENMORE RD 132/66/11KV SUB (RGBS) | 0.61072 | Summer | 2019/2019 | Dec-Feb | 0.54965 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | HP-04 | 20007334 | HERMIT PARK 66/11KV SUB (HP) | 0.40625 | Summer | 2019/2019 | Dec-Feb | 0.36562 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | F3215 | 60026768 | EAST TOOWOOMBA 33/11KV SUB (ME085) | 0.31193 | Winter | 2019/2019 | Mar-Nov | 0.31247 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | DG-06 | 20004751 | DAN GLEESON 132/66/11KV SUB (DAGL) | 0.55305 | Summer | 2019/2019 | Dec-Feb | 0.45717 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | DG-08 | 20004893 | DAN GLEESON 132/66/11KV SUB (DAGL) | 0.51496 | Summer | 2019/2019 | Dec-Feb | 0.46347 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | AL-10 | 25274650 | ALAN SHERRIFF 132/11KV SUB (ALSH) | 0.52117 | Summer | 2019/2019 | Dec-Feb | 0.46906 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | RS105 | 40001143 | ROCKHAMPTON SOUTH 66/11KV SUB (RSSS) | 0.31761 | Summer | 2019/2019 | Dec-Feb | 0.28585 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | BW210 | 40001035 | BLACKWATER 132/66/22KV SUB (BWBS) | 0.64223 | Summer | 2019/2019 | Dec-Feb | 0.57801 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | F4145 | 60026822 | SOUTH TOOWOOMBA 110/33/11KV SUB (T043) | 0.42616 | Winter | 2019/2019 | Mar-Nov | 0.39243 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | BLRI-08 | 82914276 | BLACKRIVER 66/11KV SUB (BLRI) | 0.5882 | Summer | 2019/2019 | Dec-Feb | 0.43074 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | PB-C | 50000154 | PIALBA 66/11KV SUB (PB) | 0.35627 | Summer | 2019/2019 | Dec-Feb | 0.28907 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | F3055 | 60026754 | NORTH STREET 33/11KV SUB (NOST) (ME020) | 0.30965 | Summer | 2019/2019 | Dec-Feb | 0.27868 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | F133R | 60026691 | ROMA WEST 33/11KV SUB (MW003) | 0.12632 | Summer | 2019/2019 | Dec-Feb | 0.11369 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | GA-02 | 20005832 | GARBUTT (TO46) 132/66/11KV SUB (GA) | 0.24143 | Summer | 2019/2019 | Dec-Feb | 0.21729 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | F4555 | 60026840 | WEST TOOWOOMBA 33/11KV SUB (ME005) | 0.39591 | Winter | 2019/2019 | Mar-Nov | 0.37353 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | MC-E | 50000110 | MARYBOROUGH CITY 66/11KV SUB (MC) | 0.24136 | Summer | 2019/2019 | Dec-Feb | 0.21722 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | WB-F | 50000207 | WEST BUNDABERG 66/11KV SUB (WEBU) | 0.28723 | Summer | 2019/2019 | Dec-Feb | 0.25851 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | AL-08 | 25274647 | ALAN SHERRIFF 132/11KV SUB (ALSH) | 0.13761 | Summer | 2019/2019 | Dec-Feb | 0.162 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | CN108 | 40001094 | CANNING STREET 66/11KV SUB (CNSS) | 0.22517 | Summer | 2019/2019 | Dec-Feb | 0.20266 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | HP-03 | 20007314 | HERMIT PARK 66/11KV SUB (HP) | 0.1118 | Summer | 2019/2019 | Dec-Feb | 0.10062 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | BLRI-05 | 84737242 | BLACKRIVER 66/11KV SUB (BLRI) | 0.38162 | Summer | 2019/2019 | Dec-Feb | 0.22146 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | 216 | 30053783 | MORANBAH 132/66/11KV SUB (MORA) | 0.20565 | Summer | 2019/2019 | Dec-Feb | 0.14506 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | WB-L | 50000213 | WEST BUNDABERG 66/11KV SUB (WEBU) | 0.021951 | Summer | 2019/2019 | Dec-Feb | 0.047885 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | BO-03 | 20002752 | BOHLE 66/11KV SUB (BOHL) | 0.34527 | Summer | 2019/2019 | Dec-Feb | 0.18932 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | RG104 | 40001128 | RTON GLENMORE RD 132/66/11KV SUB (RGBS) | 0.081485 | Summer | 2019/2019 | Dec-Feb | 0.073336 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | FV110 | 40001099 | FRENCHVILLE 66/11KV SUB (FVSS) | 0.18223 | Summer | 2019/2019 | Dec-Feb | 0.12419 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | 105 | 30053748 | CANNONVALE 66/11KV SUB (CANN) | 0.14085 | Summer | 2019/2019 | Dec-Feb | 0.094313 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | 325 | 30053835 | NORTH MACKAY 33/11KV SUB (NOMA) | 0.033963 | Summer | 2019/2019 | Dec-Feb | 0.030567 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Southern | CN103 | 40001091 | CANNING STREET 66/11KV SUB (CNSS) | 0.015174 | Summer | 2019/2019 | Dec-Feb | 0.013657 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | BO11 | 82982249 | BOHLE 66/11KV SUB (BOHL) | 0.016044 | Summer | 2019/2019 | Dec-Feb | 0.01444 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | BO-10 | 20003088 | BOHLE 66/11KV SUB (BOHL) | 0.098418 | Summer | 2019/2019 | Dec-Feb | 0.05472 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | 417 | 83909007 | MORANBAH 132/66/11KV SUB (MORA) | 0.014853 | Summer | 2019/2019 | Dec-Feb | -0.013544 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | BO-08 | 20003061 | BOHLE 66/11KV SUB (BOHL) | 0.0008724 | Summer | 2019/2019 | Dec-Feb | -0.050155 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | 2BLW | 10020826 | KAMERUNGA 132/22KV SUB (KAMERUNGA) | 0.19243 | Summer | 2019/2019 | Dec-Feb | -0.0067257 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | MF-12 | 20010376 | MAX FULTON 66/11KV SUB (MF) | 4.8561 | Summer | 2019/2019 | Dec-Feb | 1.5181 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet
Northern | ST05 | 20012587 | STUART 66/11KV SUB (STUA) | 0.055701 | Summer | 2019/2019 | Dec-Feb | -0.16126 | Refer to "Introduction & Notes" sheet | Refer to "Potential Solutions" sheet

## Committed Solutions 2020
WR Ref. | Limitation | Location | Committed Solution | Region
1178059 | Distribution Feeder Limitation Address capacity constraints | CLON - Cloncurry | Cloncurry 2.2km OH Reconductor - Target Comissioning: Jun-21 - Cost: $0.2M ± 30% | Northern
1236790 | Distribution Feeder Limitation Address voltage and capacity constraints | HEPA - Hermit Park | Hermit Park Substation Refurbishment - Target Comissioning: Feb-24 - Cost: $3.6M ± 30% | Northern
168413 | Distribution Feeder Limitation Address capacity constraints | KESP - Kearney Springs | Kerneys Spring Substation - 3x new feeders - Target Comissioning: Apr-22 - Cost: $1.5M ± 30% | Southern
328478 | Distribution Feeder Limitation Address capacity constraints | GRAC - Gracemere | Gracemere Substation - New Feeder 3x Exits and SKID - Target Comissioning: Jun-21 - Cost: $0.2M ± 30% | Southern
1183479 | Distribution Feeder Limitation Address capacity and voltage constraints | KAME - Kamerunga | Kamerunga Substation - 2JEN 22 kV OH Feeder Reconductor 1.1km - Target Comissioning: Nov-20 - Cost: $0.3M ± 30% | Northern
1183459 | Distribution Feeder Limitation Voltage quality of supply and voltage performance constraints | NOCL - North Cloncurry | North Cloncurry Substation - NC-02 Feeder Reconductor 21km - Target Comissioning: Dec-21 - Cost: $0.5M ± 30% | Northern
1422989 | Distribution Feeder Limitation Address voltage and capacity constraints | FD-1638 - Ballandean | Stanthorpe Town Substation - F4135 Short St 33 Feeder Ballandean 33kV Stage 2 - Target Comissioning: Oct-22 - Cost: $0.3M ± 30% | Southern
1186380 | Distribution Feeder Limitation Address capacity constraints | DURO - Duchess Road | Duchess Road Substation - DR-08 New Feeder Tie to DR-12 - Target Comissioning: Nov-21 - Cost: $0.3M ± 30% | Northern
1266685 | Distribution Feeder Limitation Address capacity constraints | KING - Kingaroy | Kingaroy Reinforcement Southern - Target Comissioning: Mar-24 - Cost: $4.8M ± 30% | Southern
1118136 | Distribution Feeder Limitation Address capacity constraints | PIAL - Pialba | Pialba Substation - FD-1547 Future Feeder - Target Comissioning: Apr-25 - Cost: $1.5M ± 30% | Southern
1401431 | Distribution Feeder Limitation Address capacity constraints | EDMO - Edmonton | Edmonton Substation - Feeder Augmentation - Target Comissioning: Jul-23 - Cost: $1.4M ± 30% | Northern
1401519 | Distribution Feeder Limitation Address capacity constraints | KAME - Kamerunga | Kamerunga to Kewarra Beach Substation - Feeder Capacity Augmentation - Target Comissioning: May-24 - Cost: $1.5M ± 30% | Northern
1401523 | Distribution Feeder Limitation Address capacity constraints | MOPA - Mona Park | Mona Park Substation - MP-06 and AYRZ-04 Feeder Augmentation - Target Comissioning: May-23 - Cost: $0.8M ± 30% | Northern
1387849 | Distribution Feeder Limitation Address voltage constraint | Multiple Locations | Arena Noja Synchrophasor - Target Comissioning: Nov-20 - Cost: $0.8M ± 30% | NA
1177748 | Distribution Feeder Limitation Address capacity and load transfer constraints | Multiple Locations | SafetyNet Implementation Central Stage 5TIER MIDD Motorised Isolator - Target Comissioning - Jul-18 - Cost: $0.5M ± 30% | NA