## Disclaimer & Introduction
1. Disclaimer and Introduction
1.1 Disclaimer
These set of Subtransmission load flow studies results are prepared and made available solely for information purposes as part of the Distribution Annual Planning Report (DAPR). Whilst care was taken in the preparation of the information in this report, and it is provided with the best intentions and good faith, the Network Modelling Team accepts no responsibility or liability (including without limitation, liability to any person by reason of negligence or negligent mis-statement) for any loss or damage that may be incurred by any person acting in reliance on this information or assumptions drawn from it, except to the extent that liability under any applicable Queensland or Commonwealth of Australia statute cannot be excluded.
Ergon Energy makes no representation or warranty as to the accuracy, reliability, completeness or suitability for any particular purpose of the information in this document. All information should be independently investigated, reviewed, analysed, and verified, and must not be relied upon in connection with any investment proposal or decision. The information contained in this report is subject to annual review.
The Known Issues section below outlines some factors that could affect the accuracy of the results presented in this studies summary and should be considered when making network augmentation or financial decisions based on these values. The basis of the disclosed studies results are the network demand forecasts obtained from the SIFT system/database. The Network Modelling Team obtain these forecast values as populated by the Strategic Forecasting Team following quality assurance processes for accuracy.
1.2 Introduction and Methodology
This load flow studies summary is prepared to provide a reference for Strategic Planners during the preparation of the DAPR. Engineers should carry out their own due diligence on the information provided by this summary prior to applying it to engineering activities. The results of these studies contained herein are produced as per the methodology described below.
In preparing the load flow summary results:
· The subtransmission network model was developed and prepared using Power Factory 2021 SP4. The results were calculated in Power Factory 2023 SP4.
· For the Ergon Energy network the model is connected to the Powerlink TAPR model at the common coupling points.
· All approved projects (in the form of variations) and new connection load/generators are incorporated into the model.
· Obtain 10 and 50 PoE demand forecasts from SIFT and minimum demand forecast from Tableau.
· Using Python automation to pull demand forecasts into Power Factory model.
· Run Load Flow studies for each of the following scenarios and document result summaries:
Ergon Energy Network (EE)
a) Time of Day conditions with SIFT 10% PoE profile (10PoE_EE_NNC);
b) Static normal conditions with minimum demand profile (MinLoad_EE_NNC);
c) N-1 conditions with SIFT 50% PoE profile (50PoE_EE_N-1);
d) N-1 conditions with minimum demand profile (MinLoad_EE_N-1);
1.3 High level Process Summary
1. Derive Master Model, Pack External Objects and Export
2. Activate Model
3. Activate Load Characteristic Application Study Case (ie. 2023TransLF-ErgonSubtrans-WithVars for EE, EnergexST_AppPrjs[DAPR2023] for EX)
4. Run Forecast Load script for required conditions (e.g. 10PoE Day SUMWIN for 10PoE peak conditions)
5. Run Power Factory Information Producer (ie. a Report Nearly Anything Sequential Creator and Task Automation of Report Nearly anything Scripts or SubtransFeederForecastProducer for 10PoE_EE_NNC)
6. Repeat steps 3-5 for other Load Characteristic Configurations if required
8. Run a Python Interpreter that reads the output files and produces the formatted document
1.4 Definition of Terms Feeder Capacity and Forecast Tables
Term | Definition
10 PoE Load (A) | Peak load forecast with 10% probability of being exceeded (one in every 10 years will be exceeded). Based on normal expected growth rates and weather corrected starting loads.
50 PoE Load (A) | Peak load forecast with 50% probability of being exceeded (one in every two years will be exceeded). Based on normal expected growth rates & weather corrected starting loads. This is the worst case (highest) load forecast between summer day and summer night.
NNC | Normal Network Configuration, Outages labelled "_NNC" indicate the limitations for the feeder were identical or worse under the Normal Network Configuration.
NCC Rating (A) | Normal Cyclic Capacity - the total capacity with all network components and equipment intact. This is the maximum permissible peak daily loading for a given load cycle that a feeder can supply each day of its life. For overhead feeders, the NCC is the conductor rating with an assumed 1m/s wind, orthogonal to the line. For underground cables, the NCC assumes that there are sufficient temperature and current operating margins from the thermal inertia of the cable and its surroundings.
Power Factor (System Normal) | Lowest power factor along the feeder at 10 PoE Peak Load. Where the Power Factor is either 0 or blank, the feeder is a normally open feeder that does not have load under System Normal conditions.
Security Standard | For security standard application, the general type of customer a sub-transmission, or transmission feeder is supplying.
Transfers | This is the total amount of load transfers that are available following the worst case network contingency. This includes automatic transfers that are controlled automatically through SCADA and are generally implemented within a minute, load transfers that can be implemented through screen switching by a network controller, manual transfers that are deployed via manually controlled switchgear locally by field staff, and mobile generation which can be deployed by field staff by moving generation to specific sites.
Note: It should be noted under the Safety Net in the Distribution Authority, it is generally assumed that 4MVA (70A) of generation is available for Urban feeders and 10MVA (170A) for Rural feeders to meet specific criteria. These values have been used as a default in the forecast tables where these are sufficient to reduce the 50PoE load below the ECC rating. Where the load is still above the ECC rating, specific load transfers have been calculated for the feeder to determine whether the Safety Net criteria is met.

## Important Info-50PoE_EE_N-1
2. Important Information
2.1 Study Information - 50PoE_EE_N-1
A summary of most information used as inputs is given in the Study Info Worksheet referenced below. This includes what Project Version was used, Study times, Variations, what Generators are included etc.
2.2 Results
The results of this study are referenced in the documented versions disclosed below.
Result Version: | 50PoE_EE_N-1_20231013_2228 50PoE_EE_N-1_20231016_1547
2.3 Known Issues and Limitations
· The List of Subtransmission Projects to be stored as Variations has been produced manually from Copperleaf and SIFT for the next 10 years.
· Automatic Outage Switching is not incorporated for both Ergon Energy and Energex N-1 Studies
· Ratings are the NCC (Normal Cyclic Capacity) Rating and do not consider increased capacity due to the outage (eg. Parallel cable runs where no load in another feeder increases trench capacity for the remaining feeders)
· N-1 Outages modelled take the entire feeder out of service.
· N-1 Outages that do not produce convergent results are ignored. The list of these can be seen in the Study Info worksheet.
· North West Power System (ie. The Network around Mount Isa) has been reported in a separate Spreadsheet this year.
· The Report is not suitable to determine "directionality" of the real or reactive power-flows due to the use of absolute value functions prior to the limits being calculated.
3. Additional Information
2.1 Information About Variables
The Values for a given timeslot shown are calculated as follows. All of the values will be for the line element in Power Factory with the Loading Constraint.
This means that the Power Factor and Voltage values are recorded at the line that is considered the most "limited" not the minimum voltage on the feeder or the minimum Power Factor on the feeder.
For each Contingency Event the values for each line are recorded with them eventually ending up in the following fields
% of Rated A: The % Utilisation called "loading" in Power Factory [c:loading]
Loading (A): Absolute Maximum Current for Both Ends in kA
Loading (MVA): Absolute Maximum Apparent Power for Both Ends in MVA
Loading (MW): Absolute Maximum Real Power for Both Ends in MW
Power Factor: Absolute Min Power Factor for Both Ends
Rating (A): Line Nominal Rating using [e:Inom_a]
Min Voltage at Constrained Conductor: Min Voltage seen on both sides of the feeder line
Once they are calculated for each feeder and Timeslot the Limiting entry is determined. This will be the values for a single line limited in the following order.
At each step all lines that share the "limiting" value will be recorded, provided their float representative is identical.
Minor differences in the float representation will result in the Min or Max value being utilised even if the value when considering real life significant figures are otherwise identical.
1. % of Rated A - Max
2. Rating (A) - Min
3. Loading (MVA) - Max
The following limit calculations are applied to ensure only 1 line's values are recorded even if all entries have the same electrical loading characteristics.
4. Contingency Outage: Alphabetical Max
Note that "_NNC" is used with is a "Normal Network Configuration" contingency where nothing is taken out of service. If it is displayed, then taking a feeder out of service did not make a recordable difference to the feeder loading.
If multiple feeder outage contingencies have the same effect on the feeder, then the higher alphabetical name will be recorded.
5. Limiting Line Name: Alphabetical Min: This is to ensure there is a unique value
6. Current Study Case Time: Alphabetical Min: This is a stopgap to ensure there is a unique value

## 50PoE_EE_N-1
Grid Association | Associated Feeders | Variable | 2024 SD | 2024 SE | 2024 SN | 2025 SD | 2025 SE | 2025 SN | 2026 SD | 2026 SE | 2026 SN | 2027 SD | 2027 SE | 2027 SN | 2028 SD | 2028 SE | 2028 SN
CA-Dysart | 6064_Dysart - Saraji Mine 66 kV | % of Rated A | 3.948% | 4.568% | 3.74% | 3.948% | 4.568% | 3.74% | 3.948% | 4.568% | 3.74% | 3.948% | 4.568% | 3.74% | 3.948% | 4.568% | 3.74%
CA-Dysart | 6064_Dysart - Saraji Mine 66 kV | Limiting Line Name | 3-Phase Link 66kV_Term7_6064 SARAJI MINE | 3-Phase Link 66kV_Term7_6064 SARAJI MINE | 3-Phase Link 66kV_Term7_6064 SARAJI MINE | 3-Phase Link 66kV_Term7_6064 SARAJI MINE | 3-Phase Link 66kV_Term7_6064 SARAJI MINE | 3-Phase Link 66kV_Term7_6064 SARAJI MINE | 3-Phase Link 66kV_Term7_6064 SARAJI MINE | 3-Phase Link 66kV_Term7_6064 SARAJI MINE | 3-Phase Link 66kV_Term7_6064 SARAJI MINE | 3-Phase Link 66kV_Term7_6064 SARAJI MINE | 3-Phase Link 66kV_Term7_6064 SARAJI MINE | 3-Phase Link 66kV_Term7_6064 SARAJI MINE | 3-Phase Link 66kV_Term7_6064 SARAJI MINE | 3-Phase Link 66kV_Term7_6064 SARAJI MINE | 3-Phase Link 66kV_Term7_6064 SARAJI MINE
CA-Dysart | 6064_Dysart - Saraji Mine 66 kV | Loading (A) | 197.3886 | 228.3794 | 187.0115 | 197.3886 | 228.3827 | 187.0115 | 197.3877 | 228.3783 | 187.0112 | 197.3886 | 228.3827 | 187.0115 | 197.3895 | 228.3838 | 187.0117
CA-Dysart | 6064_Dysart - Saraji Mine 66 kV | Loading (MVA) | 23.8024 | 27.5283 | 22.5575 | 23.8024 | 27.5287 | 22.5575 | 23.8024 | 27.5283 | 22.5575 | 23.8024 | 27.5287 | 22.5575 | 23.8024 | 27.5287 | 22.5575
CA-Dysart | 6064_Dysart - Saraji Mine 66 kV | Loading (MW) | 23.47 | 27.1437 | 22.2425 | 23.47 | 27.144 | 22.2425 | 23.47 | 27.1437 | 22.2425 | 23.47 | 27.144 | 22.2425 | 23.47 | 27.144 | 22.2425
CA-Dysart | 6064_Dysart - Saraji Mine 66 kV | Power Factor | 0.98603 | 0.98603 | 0.98603 | 0.98603 | 0.98603 | 0.98603 | 0.98603 | 0.98603 | 0.98603 | 0.98603 | 0.98603 | 0.98603 | 0.98603 | 0.98603 | 0.98603
CA-Dysart | 6064_Dysart - Saraji Mine 66 kV | Rating (A) | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000
CA-Dysart | 6064_Dysart - Saraji Mine 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Dysart | 6064_Dysart - Saraji Mine 66 kV | Min Voltage at Constrained Conductor | 69.6207 | 69.5923 | 69.6407 | 69.6207 | 69.5923 | 69.6407 | 69.621 | 69.5927 | 69.6408 | 69.6207 | 69.5923 | 69.6407 | 69.6204 | 69.5919 | 69.6406
CA-Dysart | 6064_Dysart - Saraji Mine 66 kV | Contingency Outage | 6063_Dysart - Norwich Park Mine 66 kV | 6063_Dysart - Norwich Park Mine 66 kV | 6063_Dysart - Norwich Park Mine 66 kV | 6063_Dysart - Norwich Park Mine 66 kV | 6063_Dysart - Norwich Park Mine 66 kV | 6063_Dysart - Norwich Park Mine 66 kV | 6063_Dysart - Norwich Park Mine 66 kV | 6063_Dysart - Norwich Park Mine 66 kV | 6063_Dysart - Norwich Park Mine 66 kV | 6063_Dysart - Norwich Park Mine 66 kV | 6063_Dysart - Norwich Park Mine 66 kV | 6063_Dysart - Norwich Park Mine 66 kV | 6063_Dysart - Norwich Park Mine 66 kV | 6063_Dysart - Norwich Park Mine 66 kV | 6063_Dysart - Norwich Park Mine 66 kV
CA-Dysart | 6130_Dysart - Vermont 66 kV | % of Rated A | 35.89% | 19.98% | 20.06% | 35.89% | 19.98% | 20.06% | 35.89% | 19.98% | 20.06% | 35.89% | 19.98% | 20.06% | 35.89% | 19.98% | 20.06%
CA-Dysart | 6130_Dysart - Vermont 66 kV | Limiting Line Name | TR_LINE 82005_1 | TR_LINE 82005_1 | TR_LINE 82005_1 | TR_LINE 82005_1 | TR_LINE 82005_1 | TR_LINE 82005_1 | TR_LINE 82005_1 | TR_LINE 82005_1 | TR_LINE 82005_1 | TR_LINE 82005_1 | TR_LINE 82005_1 | TR_LINE 82005_1 | TR_LINE 82005_1 | TR_LINE 82005_1 | TR_LINE 82005_1
CA-Dysart | 6130_Dysart - Vermont 66 kV | Loading (A) | 78.2398 | 76.9318 | 78.2261 | 78.2398 | 76.9318 | 78.2261 | 78.2394 | 76.9314 | 78.226 | 78.2398 | 76.9318 | 78.2261 | 78.2401 | 76.9322 | 78.2262
CA-Dysart | 6130_Dysart - Vermont 66 kV | Loading (MVA) | 9.38 | 9.2204 | 9.3811 | 9.38 | 9.2204 | 9.3811 | 9.38 | 9.2204 | 9.3811 | 9.38 | 9.2204 | 9.3811 | 9.38 | 9.2204 | 9.3811
CA-Dysart | 6130_Dysart - Vermont 66 kV | Loading (MW) | 8.6692 | 8.5232 | 8.6702 | 8.6692 | 8.5232 | 8.6702 | 8.6692 | 8.5232 | 8.6702 | 8.6692 | 8.5232 | 8.6702 | 8.6692 | 8.5232 | 8.6702
CA-Dysart | 6130_Dysart - Vermont 66 kV | Power Factor | 0.92155 | 0.92177 | 0.92156 | 0.92155 | 0.92177 | 0.92156 | 0.92156 | 0.92177 | 0.92156 | 0.92155 | 0.92177 | 0.92156 | 0.92155 | 0.92177 | 0.92156
CA-Dysart | 6130_Dysart - Vermont 66 kV | Rating (A) | 218 | 385 | 390 | 218 | 385 | 390 | 218 | 385 | 390 | 218 | 385 | 390 | 218 | 385 | 390
CA-Dysart | 6130_Dysart - Vermont 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Dysart | 6130_Dysart - Vermont 66 kV | Min Voltage at Constrained Conductor | 69.2175 | 69.1962 | 69.2375 | 69.2175 | 69.1962 | 69.2375 | 69.2178 | 69.1966 | 69.2376 | 69.2175 | 69.1962 | 69.2375 | 69.2172 | 69.1958 | 69.2374
CA-Dysart | 6130_Dysart - Vermont 66 kV | Contingency Outage | 6063_Dysart - Norwich Park Mine 66 kV | 6063_Dysart - Norwich Park Mine 66 kV | 6063_Dysart - Norwich Park Mine 66 kV | 6063_Dysart - Norwich Park Mine 66 kV | 6063_Dysart - Norwich Park Mine 66 kV | 6063_Dysart - Norwich Park Mine 66 kV | 6063_Dysart - Norwich Park Mine 66 kV | 6063_Dysart - Norwich Park Mine 66 kV | 6063_Dysart - Norwich Park Mine 66 kV | 6063_Dysart - Norwich Park Mine 66 kV | 6063_Dysart - Norwich Park Mine 66 kV | 6063_Dysart - Norwich Park Mine 66 kV | 6063_Dysart - Norwich Park Mine 66 kV | 6063_Dysart - Norwich Park Mine 66 kV | 6063_Dysart - Norwich Park Mine 66 kV
CA-Emerald | 6011_Blackwater - Comet 66 kV | % of Rated A | 157.6% | 140.6% | 67.88% | 233% | 138.3% | 67.48% | 61.26% | 144.8% | 68.56% | 61.54% | 146.5% | 68.83% | 61.88% | 149.4% | 69.24%
CA-Emerald | 6011_Blackwater - Comet 66 kV | Limiting Line Name | TR_LINE 22145_1 | TR_LINE 22145_1 | TR_LINE 22148_1 | TR_LINE 22145_1 | TR_LINE 22145_1 | TR_LINE 22148_1 | TR_LINE 22148_1 | TR_LINE 22145_1 | TR_LINE 22148_1 | TR_LINE 22148_1 | TR_LINE 22145_1 | TR_LINE 22148_1 | TR_LINE 22148_1 | TR_LINE 22145_1 | TR_LINE 22148_1
CA-Emerald | 6011_Blackwater - Comet 66 kV | Loading (A) | 436.4276 | 414.7572 | 178.5312 | 645.331 | 408.0941 | 177.4684 | 169.6962 | 427.0479 | 180.315 | 170.4614 | 432.211 | 181.0309 | 171.4075 | 440.6873 | 182.1132
CA-Emerald | 6011_Blackwater - Comet 66 kV | Loading (MVA) | 45.8215 | 43.9361 | 21.3212 | 58.8874 | 43.422 | 21.1954 | 20.112 | 44.8596 | 21.5322 | 20.2024 | 45.2474 | 21.6173 | 20.3135 | 45.8699 | 21.7456
CA-Emerald | 6011_Blackwater - Comet 66 kV | Loading (MW) | 45.4981 | 43.7743 | 20.1778 | 53.3182 | 43.3011 | 20.0226 | 18.7923 | 44.6059 | 20.4371 | 18.8994 | 44.9493 | 20.541 | 19.0344 | 45.4908 | 20.697
CA-Emerald | 6011_Blackwater - Comet 66 kV | Power Factor | 0.99294 | 0.99632 | 0.94633 | 0.90543 | 0.99722 | 0.94462 | 0.93433 | 0.99435 | 0.94909 | 0.93546 | 0.99341 | 0.95017 | 0.93698 | 0.99174 | 0.95174
CA-Emerald | 6011_Blackwater - Comet 66 kV | Rating (A) | 277 | 295 | 263 | 277 | 295 | 263 | 277 | 295 | 263 | 277 | 295 | 263 | 277 | 295 | 263
CA-Emerald | 6011_Blackwater - Comet 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Emerald | 6011_Blackwater - Comet 66 kV | Min Voltage at Constrained Conductor | 60.6088 | 61.1522 | 68.9466 | 52.6677 | 61.4238 | 68.9506 | 68.4231 | 60.6401 | 68.9402 | 68.4221 | 60.4335 | 68.9387 | 68.4187 | 60.0862 | 68.9356
CA-Emerald | 6011_Blackwater - Comet 66 kV | Contingency Outage | 6067 Lilyvale - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6015_Blackwater - Curragh Mine 66 kV | 6067 Lilyvale - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6015_Blackwater - Curragh Mine 66 kV | 6067 Lilyvale - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6015_Blackwater - Curragh Mine 66 kV | 6067 Lilyvale - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV
CA-Emerald | 6012_Blackwater - Bedford Weir 66 kV | % of Rated A | 28.7% | 35.35% | 15.06% | 28.68% | 35.33% | 15.08% | 28.38% | 35.06% | 14.92% | 28.38% | 35.06% | 14.92% | 28.7% | 35.35% | 15.06%
CA-Emerald | 6012_Blackwater - Bedford Weir 66 kV | Limiting Line Name | TR_LINE 22155_1 | TR_LINE 22155_1 | TR_LINE 22155_1 | TR_LINE 22155_1 | TR_LINE 22155_1 | TR_LINE 22155_1 | TR_LINE 22155_1 | TR_LINE 22155_1 | TR_LINE 22155_1 | TR_LINE 22155_1 | TR_LINE 22155_1 | TR_LINE 22155_1 | TR_LINE 22155_1 | TR_LINE 22155_1 | TR_LINE 22155_1
CA-Emerald | 6012_Blackwater - Bedford Weir 66 kV | Loading (A) | 79.7731 | 104.6223 | 39.7516 | 79.7396 | 104.5692 | 39.8013 | 78.9014 | 103.7751 | 39.3821 | 78.9026 | 103.7766 | 39.3821 | 79.7875 | 104.6422 | 39.7539
CA-Emerald | 6012_Blackwater - Bedford Weir 66 kV | Loading (MVA) | 9.3244 | 12.1297 | 4.7068 | 9.329 | 12.1259 | 4.7131 | 9.2231 | 12.0322 | 4.6632 | 9.2231 | 12.0322 | 4.6632 | 9.3245 | 12.1299 | 4.7069
CA-Emerald | 6012_Blackwater - Bedford Weir 66 kV | Loading (MW) | 9.0867 | 11.4799 | 4.672 | 9.1108 | 11.503 | 4.6826 | 8.9908 | 11.3882 | 4.6297 | 8.9908 | 11.3882 | 4.6297 | 9.0867 | 11.48 | 4.672
CA-Emerald | 6012_Blackwater - Bedford Weir 66 kV | Power Factor | 0.97449 | 0.94642 | 0.99256 | 0.97659 | 0.94863 | 0.99351 | 0.97479 | 0.94646 | 0.99278 | 0.97479 | 0.94646 | 0.99278 | 0.97449 | 0.94641 | 0.99255
CA-Emerald | 6012_Blackwater - Bedford Weir 66 kV | Rating (A) | 278 | 296 | 264 | 278 | 296 | 264 | 278 | 296 | 264 | 278 | 296 | 264 | 278 | 296 | 264
CA-Emerald | 6012_Blackwater - Bedford Weir 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Emerald | 6012_Blackwater - Bedford Weir 66 kV | Min Voltage at Constrained Conductor | 67.4807 | 66.9311 | 68.3619 | 67.5428 | 66.944 | 68.3672 | 67.4855 | 66.9351 | 68.364 | 67.4846 | 66.9343 | 68.364 | 67.4692 | 66.9192 | 68.3581
CA-Emerald | 6012_Blackwater - Bedford Weir 66 kV | Contingency Outage | 6015_Blackwater - Curragh Mine 66 kV | 6015_Blackwater - Curragh Mine 66 kV | 6056_Comet - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6015_Blackwater - Curragh Mine 66 kV | 6056_Comet - Emerald 66 kV | 6015_Blackwater - Curragh Mine 66 kV | 6015_Blackwater - Curragh Mine 66 kV | 6056_Comet - Emerald 66 kV | 6015_Blackwater - Curragh Mine 66 kV | 6015_Blackwater - Curragh Mine 66 kV | 6056_Comet - Emerald 66 kV | 6015_Blackwater - Curragh Mine 66 kV | 6015_Blackwater - Curragh Mine 66 kV | 6056_Comet - Emerald 66 kV
CA-Emerald | 6014_Blackwater - South Blackwater 66 kV | % of Rated A | 8.446% | 7.64% | 9.945% | 8.439% | 7.639% | 9.945% | 8.447% | 7.641% | 9.945% | 8.447% | 7.641% | 9.945% | 8.448% | 7.641% | 9.945%
CA-Emerald | 6014_Blackwater - South Blackwater 66 kV | Limiting Line Name | TR_LINE 18126_1 | TR_LINE 18126_1 | TR_LINE 18126_1 | TR_LINE 18126_1 | TR_LINE 18126_1 | TR_LINE 18126_1 | TR_LINE 18126_1 | TR_LINE 18126_1 | TR_LINE 18126_1 | TR_LINE 18126_1 | TR_LINE 18126_1 | TR_LINE 18126_1 | TR_LINE 18126_1 | TR_LINE 18126_1 | TR_LINE 18126_1
CA-Emerald | 6014_Blackwater - South Blackwater 66 kV | Loading (A) | 41.8925 | 41.9427 | 49.5258 | 41.859 | 41.9395 | 49.5244 | 41.897 | 41.9474 | 49.5279 | 41.8976 | 41.9479 | 49.5279 | 41.8997 | 41.95 | 49.5286
CA-Emerald | 6014_Blackwater - South Blackwater 66 kV | Loading (MVA) | 4.9099 | 4.906 | 5.8205 | 4.9099 | 4.906 | 5.8205 | 4.9099 | 4.906 | 5.8205 | 4.9099 | 4.906 | 5.8205 | 4.9099 | 4.906 | 5.8205
CA-Emerald | 6014_Blackwater - South Blackwater 66 kV | Loading (MW) | 4.5426 | 4.539 | 5.3845 | 4.5426 | 4.539 | 5.3845 | 4.5426 | 4.539 | 5.3845 | 4.5426 | 4.539 | 5.3845 | 4.5426 | 4.539 | 5.3845
CA-Emerald | 6014_Blackwater - South Blackwater 66 kV | Power Factor | 0.92353 | 0.92352 | 0.92312 | 0.92353 | 0.92352 | 0.92312 | 0.92353 | 0.92352 | 0.92312 | 0.92353 | 0.92352 | 0.92312 | 0.92352 | 0.92352 | 0.92312
CA-Emerald | 6014_Blackwater - South Blackwater 66 kV | Rating (A) | 496 | 549 | 498 | 496 | 549 | 498 | 496 | 549 | 498 | 496 | 549 | 498 | 496 | 549 | 498
CA-Emerald | 6014_Blackwater - South Blackwater 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Emerald | 6014_Blackwater - South Blackwater 66 kV | Min Voltage at Constrained Conductor | 67.6665 | 67.5319 | 67.853 | 67.7203 | 67.537 | 67.8549 | 67.6593 | 67.5244 | 67.8501 | 67.6584 | 67.5235 | 67.8501 | 67.655 | 67.5201 | 67.8492
CA-Emerald | 6014_Blackwater - South Blackwater 66 kV | Contingency Outage | 6015_Blackwater - Curragh Mine 66 kV | 6015_Blackwater - Curragh Mine 66 kV | 6056_Comet - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6015_Blackwater - Curragh Mine 66 kV | 6056_Comet - Emerald 66 kV | 6015_Blackwater - Curragh Mine 66 kV | 6015_Blackwater - Curragh Mine 66 kV | 6056_Comet - Emerald 66 kV | 6015_Blackwater - Curragh Mine 66 kV | 6015_Blackwater - Curragh Mine 66 kV | 6056_Comet - Emerald 66 kV | 6015_Blackwater - Curragh Mine 66 kV | 6015_Blackwater - Curragh Mine 66 kV | 6056_Comet - Emerald 66 kV
CA-Emerald | 6015_Blackwater - Curragh Mine 66 kV | % of Rated A | 57.02% | 57.8% | 56.26% | 57.38% | 57.75% | 56.26% | 57.02% | 57.88% | 56.26% | 57.02% | 57.91% | 56.26% | 57.02% | 57.96% | 56.26%
CA-Emerald | 6015_Blackwater - Curragh Mine 66 kV | Limiting Line Name | TR_LINE 18371_1 | TR_LINE 18371_1 | TR_LINE 18371_1 | TR_LINE 18371_1 | TR_LINE 18371_1 | TR_LINE 18371_1 | TR_LINE 18371_1 | TR_LINE 18371_1 | TR_LINE 18371_1 | TR_LINE 18371_1 | TR_LINE 18371_1 | TR_LINE 18371_1 | TR_LINE 18371_1 | TR_LINE 18371_1 | TR_LINE 18371_1
CA-Emerald | 6015_Blackwater - Curragh Mine 66 kV | Loading (A) | 317.0126 | 341.5794 | 297.0374 | 319.0096 | 341.3305 | 297.0292 | 317.0293 | 342.0765 | 297.0498 | 317.0333 | 342.2414 | 297.0498 | 317.0485 | 342.5443 | 297.0539
CA-Emerald | 6015_Blackwater - Curragh Mine 66 kV | Loading (MVA) | 37.8131 | 40.7151 | 35.3622 | 37.8185 | 40.7143 | 35.3622 | 37.8131 | 40.7165 | 35.3622 | 37.8131 | 40.717 | 35.3622 | 37.8132 | 40.7179 | 35.3622
CA-Emerald | 6015_Blackwater - Curragh Mine 66 kV | Loading (MW) | 36.6492 | 39.4455 | 34.285 | 36.652 | 39.4451 | 34.2849 | 36.6492 | 39.4463 | 34.285 | 36.6492 | 39.4465 | 34.285 | 36.6492 | 39.447 | 34.285
CA-Emerald | 6015_Blackwater - Curragh Mine 66 kV | Power Factor | 0.96922 | 0.96882 | 0.96954 | 0.96916 | 0.96883 | 0.96954 | 0.96922 | 0.9688 | 0.96954 | 0.96922 | 0.9688 | 0.96954 | 0.96922 | 0.96879 | 0.96954
CA-Emerald | 6015_Blackwater - Curragh Mine 66 kV | Rating (A) | 556 | 591 | 528 | 556 | 591 | 528 | 556 | 591 | 528 | 556 | 591 | 528 | 556 | 591 | 528
CA-Emerald | 6015_Blackwater - Curragh Mine 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Emerald | 6015_Blackwater - Curragh Mine 66 kV | Min Voltage at Constrained Conductor | 68.1849 | 68.0769 | 68.1012 | 67.7582 | 68.1265 | 68.1031 | 68.1813 | 67.978 | 68.0983 | 68.1804 | 67.9453 | 68.0983 | 68.1772 | 67.8852 | 68.0974
CA-Emerald | 6015_Blackwater - Curragh Mine 66 kV | Contingency Outage | 6069_Lilyvale - German Creek Mine 66 kV | 6067 Lilyvale - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6069_Lilyvale - German Creek Mine 66 kV | 6067 Lilyvale - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6069_Lilyvale - German Creek Mine 66 kV | 6067 Lilyvale - Emerald 66 kV | 6056_Comet - Emerald 66 kV | 6069_Lilyvale - German Creek Mine 66 kV | 6067 Lilyvale - Emerald 66 kV | 6056_Comet - Emerald 66 kV
CA-Emerald | 6055 Cook Colliery-Miniere Mining 66 kV | % of Rated A | 27.93% | 19.24% | 20.6% | 27.41% | 18.83% | 20.4% | 27.43% | 18.84% | 20.4% | 27.43% | 18.84% | 20.4% | 27.43% | 18.84% | 20.4%
CA-Emerald | 6055 Cook Colliery-Miniere Mining 66 kV | Limiting Line Name | TR_LINE 22527_1 | TR_LINE 22527_1 | TR_LINE 22527_1 | TR_LINE 22527_1 | TR_LINE 22527_1 | TR_LINE 22527_1 | TR_LINE 22527_1 | TR_LINE 22527_1 | TR_LINE 22527_1 | TR_LINE 22527_1 | TR_LINE 22527_1 | TR_LINE 22527_1 | TR_LINE 22527_1 | TR_LINE 22527_1 | TR_LINE 22527_1
CA-Emerald | 6055 Cook Colliery-Miniere Mining 66 kV | Loading (A) | 39.9356 | 40.5898 | 42.8563 | 39.1905 | 39.741 | 42.4364 | 39.2276 | 39.7487 | 42.4395 | 39.2282 | 39.7493 | 42.4395 | 39.2302 | 39.7514 | 42.4401
CA-Emerald | 6055 Cook Colliery-Miniere Mining 66 kV | Loading (MVA) | 4.6697 | 4.7379 | 5.0181 | 4.5875 | 4.6407 | 4.9698 | 4.5877 | 4.6407 | 4.9698 | 4.5877 | 4.6407 | 4.9698 | 4.5877 | 4.6407 | 4.9698
CA-Emerald | 6055 Cook Colliery-Miniere Mining 66 kV | Loading (MW) | 4.3073 | 4.3655 | 4.6355 | 4.2371 | 4.2825 | 4.5942 | 4.2371 | 4.2825 | 4.5942 | 4.2371 | 4.2825 | 4.5942 | 4.2371 | 4.2825 | 4.5942
CA-Emerald | 6055 Cook Colliery-Miniere Mining 66 kV | Power Factor | 0.92237 | 0.92137 | 0.92375 | 0.92361 | 0.9228 | 0.92441 | 0.92358 | 0.92279 | 0.92441 | 0.92358 | 0.92279 | 0.92441 | 0.92357 | 0.92279 | 0.92441
CA-Emerald | 6055 Cook Colliery-Miniere Mining 66 kV | Rating (A) | 143 | 211 | 208 | 143 | 211 | 208 | 143 | 211 | 208 | 143 | 211 | 208 | 143 | 211 | 208
CA-Emerald | 6055 Cook Colliery-Miniere Mining 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Emerald | 6055 Cook Colliery-Miniere Mining 66 kV | Min Voltage at Constrained Conductor | 67.5103 | 67.3927 | 67.6024 | 67.5821 | 67.419 | 67.6148 | 67.5209 | 67.4064 | 67.61 | 67.52 | 67.4055 | 67.61 | 67.5166 | 67.4021 | 67.6091
CA-Emerald | 6055 Cook Colliery-Miniere Mining 66 kV | Contingency Outage | 6015_Blackwater - Curragh Mine 66 kV | 6015_Blackwater - Curragh Mine 66 kV | 6056_Comet - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6015_Blackwater - Curragh Mine 66 kV | 6056_Comet - Emerald 66 kV | 6015_Blackwater - Curragh Mine 66 kV | 6015_Blackwater - Curragh Mine 66 kV | 6056_Comet - Emerald 66 kV | 6015_Blackwater - Curragh Mine 66 kV | 6015_Blackwater - Curragh Mine 66 kV | 6056_Comet - Emerald 66 kV | 6015_Blackwater - Curragh Mine 66 kV | 6015_Blackwater - Curragh Mine 66 kV | 6056_Comet - Emerald 66 kV
CA-Emerald | 6056_Comet - Emerald 66 kV | % of Rated A | 149.4% | 132.7% | 63.92% | 223% | 130.5% | 63.53% | 56.32% | 136.7% | 64.56% | 56.58% | 138.4% | 64.82% | 56.9% | 141.2% | 65.22%
CA-Emerald | 6056_Comet - Emerald 66 kV | Limiting Line Name | TR_LINE 21924_1 | TR_LINE 21924_1 | TR_LINE 22146_1 | TR_LINE 33421_1 | TR_LINE 21924_1 | TR_LINE 22146_1 | TR_LINE 22146_1 | TR_LINE 21924_1 | TR_LINE 22146_1 | TR_LINE 22146_1 | TR_LINE 21924_1 | TR_LINE 22146_1 | TR_LINE 22146_1 | TR_LINE 21924_1 | TR_LINE 22146_1
CA-Emerald | 6056_Comet - Emerald 66 kV | Loading (A) | 413.7159 | 391.4828 | 168.0999 | 617.6498 | 385.0479 | 167.0864 | 156.0169 | 403.3461 | 169.8027 | 156.73 | 408.3359 | 170.4871 | 157.6044 | 416.5263 | 171.5196
CA-Emerald | 6056_Comet - Emerald 66 kV | Loading (MVA) | 42.8768 | 40.9924 | 19.7381 | 36.7111 | 40.5148 | 19.6292 | 18.2347 | 41.8473 | 19.921 | 18.3129 | 42.2062 | 19.9948 | 18.4075 | 42.781 | 20.1058
CA-Emerald | 6056_Comet - Emerald 66 kV | Loading (MW) | 42.7386 | 40.9536 | 17.7771 | 36.6257 | 40.4948 | 17.632 | 15.7689 | 41.7577 | 18.0193 | 15.8692 | 42.0893 | 18.1162 | 15.9955 | 42.6111 | 18.2618
CA-Emerald | 6056_Comet - Emerald 66 kV | Power Factor | 0.99678 | 0.99905 | 0.90062 | 0.99767 | 0.99951 | 0.89823 | 0.86475 | 0.99786 | 0.90451 | 0.86653 | 0.99723 | 0.90602 | 0.86894 | 0.99603 | 0.90826
CA-Emerald | 6056_Comet - Emerald 66 kV | Rating (A) | 277 | 295 | 263 | 277 | 295 | 263 | 277 | 295 | 263 | 277 | 295 | 263 | 277 | 295 | 263
CA-Emerald | 6056_Comet - Emerald 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Emerald | 6056_Comet - Emerald 66 kV | Min Voltage at Constrained Conductor | 59.7513 | 60.3786 | 67.7912 | 34.2898 | 60.6752 | 67.8259 | 67.4784 | 59.8197 | 67.7332 | 67.4595 | 59.5933 | 67.7112 | 67.4316 | 59.2134 | 67.6772
CA-Emerald | 6056_Comet - Emerald 66 kV | Contingency Outage | 6067 Lilyvale - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6015_Blackwater - Curragh Mine 66 kV | 6067 Lilyvale - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6015_Blackwater - Curragh Mine 66 kV | 6067 Lilyvale - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6015_Blackwater - Curragh Mine 66 kV | 6067 Lilyvale - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV
CA-Emerald | 6058_Bedford Weir - Bingegang 66 kV | % of Rated A | 7.063% | 13.05% | 4.414% | 7.056% | 13.04% | 4.413% | 7.062% | 13.05% | 4.414% | 7.062% | 13.05% | 4.414% | 7.064% | 13.05% | 4.414%
CA-Emerald | 6058_Bedford Weir - Bingegang 66 kV | Limiting Line Name | TR_LINE 22171_1 | TR_LINE 99926_1 | TR_LINE 22171_1 | TR_LINE 22171_1 | TR_LINE 99926_1 | TR_LINE 22171_1 | TR_LINE 22171_1 | TR_LINE 99926_1 | TR_LINE 22171_1 | TR_LINE 22171_1 | TR_LINE 99926_1 | TR_LINE 22171_1 | TR_LINE 22171_1 | TR_LINE 99926_1 | TR_LINE 22171_1
CA-Emerald | 6058_Bedford Weir - Bingegang 66 kV | Loading (A) | 10.0996 | 38.621 | 9.1804 | 10.0898 | 38.6128 | 9.1797 | 10.0989 | 38.6184 | 9.1801 | 10.099 | 38.619 | 9.1801 | 10.1014 | 38.6286 | 9.1809
CA-Emerald | 6058_Bedford Weir - Bingegang 66 kV | Loading (MVA) | 1.176 | 4.4239 | 1.0835 | 1.1759 | 4.4239 | 1.0835 | 1.176 | 4.4239 | 1.0835 | 1.176 | 4.4239 | 1.0835 | 1.176 | 4.424 | 1.0835
CA-Emerald | 6058_Bedford Weir - Bingegang 66 kV | Loading (MW) | 1.1594 | 4.0301 | 1.0683 | 1.1594 | 4.0301 | 1.0683 | 1.1594 | 4.0301 | 1.0683 | 1.1594 | 4.0301 | 1.0683 | 1.1594 | 4.0301 | 1.0683
CA-Emerald | 6058_Bedford Weir - Bingegang 66 kV | Power Factor | 0.9859 | 0.91093 | 0.98602 | 0.98593 | 0.91094 | 0.98602 | 0.9859 | 0.91093 | 0.98602 | 0.9859 | 0.91093 | 0.98602 | 0.9859 | 0.91092 | 0.98602
CA-Emerald | 6058_Bedford Weir - Bingegang 66 kV | Rating (A) | 143 | 296 | 208 | 143 | 296 | 208 | 143 | 296 | 208 | 143 | 296 | 208 | 143 | 296 | 208
CA-Emerald | 6058_Bedford Weir - Bingegang 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Emerald | 6058_Bedford Weir - Bingegang 66 kV | Min Voltage at Constrained Conductor | 67.2238 | 66.1341 | 68.1388 | 67.2865 | 66.1471 | 68.1442 | 67.2286 | 66.1381 | 68.1409 | 67.2277 | 66.1373 | 68.1409 | 67.2122 | 66.122 | 68.135
CA-Emerald | 6058_Bedford Weir - Bingegang 66 kV | Contingency Outage | 6015_Blackwater - Curragh Mine 66 kV | 6015_Blackwater - Curragh Mine 66 kV | 6056_Comet - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6015_Blackwater - Curragh Mine 66 kV | 6056_Comet - Emerald 66 kV | 6015_Blackwater - Curragh Mine 66 kV | 6015_Blackwater - Curragh Mine 66 kV | 6056_Comet - Emerald 66 kV | 6015_Blackwater - Curragh Mine 66 kV | 6015_Blackwater - Curragh Mine 66 kV | 6056_Comet - Emerald 66 kV | 6015_Blackwater - Curragh Mine 66 kV | 6015_Blackwater - Curragh Mine 66 kV | 6056_Comet - Emerald 66 kV
CA-Emerald | 6059_Leichardt - Cook Colliery 66 kV | % of Rated A | 27.93% | 19.24% | 20.6% | 27.4% | 18.83% | 20.4% | 27.43% | 18.84% | 20.4% | 27.43% | 18.84% | 20.4% | 27.43% | 18.84% | 20.4%
CA-Emerald | 6059_Leichardt - Cook Colliery 66 kV | Limiting Line Name | TR_LINE 22402_1 | TR_LINE 22402_1 | TR_LINE 22402_1 | TR_LINE 22402_1 | TR_LINE 22402_1 | TR_LINE 22402_1 | TR_LINE 22402_1 | TR_LINE 22402_1 | TR_LINE 22402_1 | TR_LINE 22402_1 | TR_LINE 22402_1 | TR_LINE 22402_1 | TR_LINE 22402_1 | TR_LINE 22402_1 | TR_LINE 22402_1
CA-Emerald | 6059_Leichardt - Cook Colliery 66 kV | Loading (A) | 39.9331 | 40.5872 | 42.8538 | 39.188 | 39.7384 | 42.4338 | 39.225 | 39.7461 | 42.4369 | 39.2256 | 39.7467 | 42.4369 | 39.2277 | 39.7488 | 42.4375
CA-Emerald | 6059_Leichardt - Cook Colliery 66 kV | Loading (MVA) | 4.6695 | 4.7378 | 5.0179 | 4.5873 | 4.6405 | 4.9696 | 4.5875 | 4.6405 | 4.9697 | 4.5875 | 4.6405 | 4.9697 | 4.5875 | 4.6405 | 4.9697
CA-Emerald | 6059_Leichardt - Cook Colliery 66 kV | Loading (MW) | 4.3256 | 4.3845 | 4.6567 | 4.2548 | 4.3006 | 4.615 | 4.2548 | 4.3006 | 4.615 | 4.2548 | 4.3006 | 4.615 | 4.2548 | 4.3007 | 4.615
CA-Emerald | 6059_Leichardt - Cook Colliery 66 kV | Power Factor | 0.92242 | 0.92143 | 0.9238 | 0.92366 | 0.92285 | 0.92446 | 0.92363 | 0.92284 | 0.92446 | 0.92363 | 0.92284 | 0.92446 | 0.92363 | 0.92284 | 0.92446
CA-Emerald | 6059_Leichardt - Cook Colliery 66 kV | Rating (A) | 143 | 211 | 208 | 143 | 211 | 208 | 143 | 211 | 208 | 143 | 211 | 208 | 143 | 211 | 208
CA-Emerald | 6059_Leichardt - Cook Colliery 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Emerald | 6059_Leichardt - Cook Colliery 66 kV | Min Voltage at Constrained Conductor | 67.5119 | 67.3944 | 67.6042 | 67.5837 | 67.4206 | 67.6165 | 67.5226 | 67.408 | 67.6118 | 67.5217 | 67.4072 | 67.6118 | 67.5182 | 67.4038 | 67.6108
CA-Emerald | 6059_Leichardt - Cook Colliery 66 kV | Contingency Outage | 6015_Blackwater - Curragh Mine 66 kV | 6015_Blackwater - Curragh Mine 66 kV | 6056_Comet - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6015_Blackwater - Curragh Mine 66 kV | 6056_Comet - Emerald 66 kV | 6015_Blackwater - Curragh Mine 66 kV | 6015_Blackwater - Curragh Mine 66 kV | 6056_Comet - Emerald 66 kV | 6015_Blackwater - Curragh Mine 66 kV | 6015_Blackwater - Curragh Mine 66 kV | 6056_Comet - Emerald 66 kV | 6015_Blackwater - Curragh Mine 66 kV | 6015_Blackwater - Curragh Mine 66 kV | 6056_Comet - Emerald 66 kV
CA-Emerald | 6062_Thiess 66 kV | % of Rated A | 14.78% | 10.03% | 12.03% | 14.76% | 10.02% | 12.03% | 14.77% | 10.02% | 12.03% | 14.77% | 10.02% | 12.03% | 14.78% | 10.02% | 12.03%
CA-Emerald | 6062_Thiess 66 kV | Limiting Line Name | TR_LINE 22551_2 | TR_LINE 22551_2 | TR_LINE 22551_2 | TR_LINE 22551_2 | TR_LINE 22551_2 | TR_LINE 22551_2 | TR_LINE 22551_2 | TR_LINE 22551_2 | TR_LINE 22551_2 | TR_LINE 22551_2 | TR_LINE 22551_2 | TR_LINE 22551_2 | TR_LINE 22551_2 | TR_LINE 22551_2 | TR_LINE 22551_2
CA-Emerald | 6062_Thiess 66 kV | Loading (A) | 21.1337 | 21.1559 | 25.0188 | 21.1083 | 21.1442 | 25.0122 | 21.1275 | 21.1482 | 25.014 | 21.1278 | 21.1485 | 25.014 | 21.1289 | 21.1496 | 25.0143
CA-Emerald | 6062_Thiess 66 kV | Loading (MVA) | 2.4611 | 2.4592 | 2.9162 | 2.4611 | 2.4592 | 2.9162 | 2.4611 | 2.4592 | 2.9162 | 2.4611 | 2.4592 | 2.9162 | 2.4611 | 2.4592 | 2.9162
CA-Emerald | 6062_Thiess 66 kV | Loading (MW) | 2.2667 | 2.2649 | 2.6859 | 2.2667 | 2.2649 | 2.6859 | 2.2667 | 2.2649 | 2.6859 | 2.2667 | 2.2649 | 2.6859 | 2.2667 | 2.2649 | 2.6859
CA-Emerald | 6062_Thiess 66 kV | Power Factor | 0.921 | 0.921 | 0.921 | 0.921 | 0.921 | 0.921 | 0.921 | 0.921 | 0.921 | 0.921 | 0.921 | 0.921 | 0.921 | 0.921 | 0.921
CA-Emerald | 6062_Thiess 66 kV | Rating (A) | 143 | 211 | 208 | 143 | 211 | 208 | 143 | 211 | 208 | 143 | 211 | 208 | 143 | 211 | 208
CA-Emerald | 6062_Thiess 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Emerald | 6062_Thiess 66 kV | Min Voltage at Constrained Conductor | 67.2357 | 67.1112 | 67.2965 | 67.3168 | 67.1482 | 67.3142 | 67.2554 | 67.1356 | 67.3094 | 67.2544 | 67.1347 | 67.3094 | 67.251 | 67.1313 | 67.3084
CA-Emerald | 6062_Thiess 66 kV | Contingency Outage | 6015_Blackwater - Curragh Mine 66 kV | 6015_Blackwater - Curragh Mine 66 kV | 6056_Comet - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6015_Blackwater - Curragh Mine 66 kV | 6056_Comet - Emerald 66 kV | 6015_Blackwater - Curragh Mine 66 kV | 6015_Blackwater - Curragh Mine 66 kV | 6056_Comet - Emerald 66 kV | 6015_Blackwater - Curragh Mine 66 kV | 6015_Blackwater - Curragh Mine 66 kV | 6056_Comet - Emerald 66 kV | 6015_Blackwater - Curragh Mine 66 kV | 6015_Blackwater - Curragh Mine 66 kV | 6056_Comet - Emerald 66 kV
CA-Emerald | 6065_Lilyvale - Tieri Tee 66 kV | % of Rated A | 43.66% | 37.25% | 30.75% | 43.68% | 37.24% | 30.74% | 43.28% | 36.92% | 30.58% | 43.66% | 37.25% | 30.75% | 43.67% | 37.26% | 30.75%
CA-Emerald | 6065_Lilyvale - Tieri Tee 66 kV | Limiting Line Name | TR_LINE 155365_2 | TR_LINE 155365_2 | TR_LINE 155365_2 | TR_LINE 155365_2 | TR_LINE 155365_2 | TR_LINE 155365_2 | TR_LINE 155365_2 | TR_LINE 155365_2 | TR_LINE 155365_2 | TR_LINE 155365_2 | TR_LINE 155365_2 | TR_LINE 155365_2 | TR_LINE 155365_2 | TR_LINE 155365_2 | TR_LINE 155365_2
CA-Emerald | 6065_Lilyvale - Tieri Tee 66 kV | Loading (A) | 106.0896 | 101.3148 | 76.2482 | 106.139 | 101.2901 | 76.2458 | 105.1592 | 100.4138 | 75.8279 | 106.1043 | 101.3331 | 76.2512 | 106.1144 | 101.357 | 76.2531
CA-Emerald | 6065_Lilyvale - Tieri Tee 66 kV | Loading (MVA) | 12.5157 | 11.9551 | 8.9932 | 12.5163 | 11.9548 | 8.9931 | 12.4054 | 11.8457 | 8.9434 | 12.5159 | 11.9554 | 8.9932 | 12.516 | 11.9557 | 8.9932
CA-Emerald | 6065_Lilyvale - Tieri Tee 66 kV | Loading (MW) | 12.2703 | 11.7534 | 8.8114 | 12.2706 | 11.7532 | 8.8114 | 12.1634 | 11.647 | 8.7627 | 12.2704 | 11.7535 | 8.8114 | 12.2704 | 11.7536 | 8.8114
CA-Emerald | 6065_Lilyvale - Tieri Tee 66 kV | Power Factor | 0.98022 | 0.98285 | 0.97862 | 0.9802 | 0.98286 | 0.97862 | 0.9803 | 0.98294 | 0.9786 | 0.98021 | 0.98285 | 0.97862 | 0.98021 | 0.98284 | 0.97862
CA-Emerald | 6065_Lilyvale - Tieri Tee 66 kV | Rating (A) | 243 | 272 | 248 | 243 | 272 | 248 | 243 | 272 | 248 | 243 | 272 | 248 | 243 | 272 | 248
CA-Emerald | 6065_Lilyvale - Tieri Tee 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Emerald | 6065_Lilyvale - Tieri Tee 66 kV | Min Voltage at Constrained Conductor | 67.7564 | 67.7962 | 67.9133 | 67.7278 | 67.8113 | 67.9152 | 67.7586 | 67.7829 | 67.9146 | 67.7479 | 67.785 | 67.9109 | 67.742 | 67.7705 | 67.9093
CA-Emerald | 6065_Lilyvale - Tieri Tee 66 kV | Contingency Outage | 6069_Lilyvale - German Creek Mine 66 kV | 6011_Blackwater - Comet 66 kV | 6072_Lilyvale - Gordonstone Mine 66 kV | 6071_Lilyvale - Oaky Creek Mine 66 kV | 6011_Blackwater - Comet 66 kV | 6072_Lilyvale - Gordonstone Mine 66 kV | 6071_Lilyvale - Oaky Creek Mine 66 kV | 6011_Blackwater - Comet 66 kV | 6072_Lilyvale - Gordonstone Mine 66 kV | 6071_Lilyvale - Oaky Creek Mine 66 kV | 6011_Blackwater - Comet 66 kV | 6072_Lilyvale - Gordonstone Mine 66 kV | 6071_Lilyvale - Oaky Creek Mine 66 kV | 6011_Blackwater - Comet 66 kV | 6072_Lilyvale - Gordonstone Mine 66 kV
CA-Emerald | 6067 Lilyvale - Emerald 66 kV | % of Rated A | 102.2% | 76.67% | 44.36% | 101.5% | 76.08% | 44.18% | 103.6% | 77.67% | 44.66% | 104.1% | 78.09% | 44.77% | 104.9% | 78.69% | 44.95%
CA-Emerald | 6067 Lilyvale - Emerald 66 kV | Limiting Line Name | TR_LINE 17480_1 | TR_LINE 17480_1 | TR_LINE 17480_1 | TR_LINE 17480_1 | TR_LINE 17480_1 | TR_LINE 17480_1 | TR_LINE 17480_1 | TR_LINE 17480_1 | TR_LINE 17480_1 | TR_LINE 17480_1 | TR_LINE 17480_1 | TR_LINE 17480_1 | TR_LINE 17480_1 | TR_LINE 17480_1 | TR_LINE 17480_1
CA-Emerald | 6067 Lilyvale - Emerald 66 kV | Loading (A) | 348.6715 | 345.796 | 191.6332 | 346.1042 | 343.1057 | 190.8706 | 353.2152 | 350.2853 | 192.9122 | 355.0714 | 352.1842 | 193.427 | 357.8551 | 354.914 | 194.2021
CA-Emerald | 6067 Lilyvale - Emerald 66 kV | Loading (MVA) | 41.9784 | 40.8908 | 23.3508 | 41.6888 | 40.5815 | 23.2605 | 42.5138 | 41.4108 | 23.5028 | 42.7299 | 41.6394 | 23.5635 | 43.056 | 41.9533 | 23.655
CA-Emerald | 6067 Lilyvale - Emerald 66 kV | Loading (MW) | 41.8849 | 40.8047 | 19.1365 | 41.5471 | 40.478 | 18.9973 | 42.4471 | 41.3498 | 19.3687 | 42.6729 | 41.5662 | 19.4616 | 43.012 | 41.8949 | 19.601
CA-Emerald | 6067 Lilyvale - Emerald 66 kV | Power Factor | 0.96553 | 0.96538 | 0.78698 | 0.96184 | 0.96418 | 0.78432 | 0.96744 | 0.96728 | 0.79132 | 0.9682 | 0.96564 | 0.79305 | 0.96931 | 0.9668 | 0.7956
CA-Emerald | 6067 Lilyvale - Emerald 66 kV | Rating (A) | 341 | 451 | 432 | 341 | 451 | 432 | 341 | 451 | 432 | 341 | 451 | 432 | 341 | 451 | 432
CA-Emerald | 6067 Lilyvale - Emerald 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Emerald | 6067 Lilyvale - Emerald 66 kV | Min Voltage at Constrained Conductor | 67.6692 | 66.4368 | 69.3802 | 67.937 | 66.5487 | 69.3833 | 67.4874 | 66.2588 | 69.3773 | 67.4081 | 66.3413 | 69.3748 | 67.2927 | 66.2272 | 69.372
CA-Emerald | 6067 Lilyvale - Emerald 66 kV | Contingency Outage | 6011_Blackwater - Comet 66 kV | 6011_Blackwater - Comet 66 kV | 6011_Blackwater - Comet 66 kV | 6011_Blackwater - Comet 66 kV | 6011_Blackwater - Comet 66 kV | 6011_Blackwater - Comet 66 kV | 6011_Blackwater - Comet 66 kV | 6011_Blackwater - Comet 66 kV | 6011_Blackwater - Comet 66 kV | 6011_Blackwater - Comet 66 kV | 6011_Blackwater - Comet 66 kV | 6011_Blackwater - Comet 66 kV | 6011_Blackwater - Comet 66 kV | 6011_Blackwater - Comet 66 kV | 6011_Blackwater - Comet 66 kV
CA-Emerald | 6078_SOBL - Dragline South 66 kV | % of Rated A | 0.42% | 0.4205% | 0.4963% | 0.4196% | 0.4205% | 0.4963% | 0.42% | 0.4205% | 0.4963% | 0.42% | 0.4205% | 0.4963% | 0.4201% | 0.4206% | 0.4963%
CA-Emerald | 6078_SOBL - Dragline South 66 kV | Limiting Line Name | TR_LINE SOBL - SOBL Dragline South | TR_LINE SOBL - SOBL Dragline South | TR_LINE SOBL - SOBL Dragline South | TR_LINE SOBL - SOBL Dragline South | TR_LINE SOBL - SOBL Dragline South | TR_LINE SOBL - SOBL Dragline South | TR_LINE SOBL - SOBL Dragline South | TR_LINE SOBL - SOBL Dragline South | TR_LINE SOBL - SOBL Dragline South | TR_LINE SOBL - SOBL Dragline South | TR_LINE SOBL - SOBL Dragline South | TR_LINE SOBL - SOBL Dragline South | TR_LINE SOBL - SOBL Dragline South | TR_LINE SOBL - SOBL Dragline South | TR_LINE SOBL - SOBL Dragline South
CA-Emerald | 6078_SOBL - Dragline South 66 kV | Loading (A) | 20.9992 | 21.0241 | 24.8136 | 20.9825 | 21.0225 | 24.8129 | 21.0014 | 21.0264 | 24.8146 | 21.0017 | 21.0267 | 24.8146 | 21.0027 | 21.0278 | 24.815
CA-Emerald | 6078_SOBL - Dragline South 66 kV | Loading (MVA) | 2.4611 | 2.4592 | 2.9162 | 2.4611 | 2.4592 | 2.9162 | 2.4611 | 2.4592 | 2.9162 | 2.4611 | 2.4592 | 2.9162 | 2.4611 | 2.4592 | 2.9162
CA-Emerald | 6078_SOBL - Dragline South 66 kV | Loading (MW) | 2.2667 | 2.2649 | 2.6858 | 2.2667 | 2.2649 | 2.6858 | 2.2667 | 2.2649 | 2.6858 | 2.2667 | 2.2649 | 2.6858 | 2.2667 | 2.2649 | 2.6858
CA-Emerald | 6078_SOBL - Dragline South 66 kV | Power Factor | 0.921 | 0.921 | 0.921 | 0.921 | 0.921 | 0.921 | 0.921 | 0.921 | 0.921 | 0.921 | 0.921 | 0.921 | 0.921 | 0.921 | 0.921
CA-Emerald | 6078_SOBL - Dragline South 66 kV | Rating (A) | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000
CA-Emerald | 6078_SOBL - Dragline South 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Emerald | 6078_SOBL - Dragline South 66 kV | Min Voltage at Constrained Conductor | 67.6665 | 67.5319 | 67.853 | 67.7203 | 67.537 | 67.8549 | 67.6593 | 67.5244 | 67.8501 | 67.6584 | 67.5235 | 67.8501 | 67.655 | 67.5201 | 67.8492
CA-Emerald | 6078_SOBL - Dragline South 66 kV | Contingency Outage | 6015_Blackwater - Curragh Mine 66 kV | 6015_Blackwater - Curragh Mine 66 kV | 6056_Comet - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6015_Blackwater - Curragh Mine 66 kV | 6056_Comet - Emerald 66 kV | 6015_Blackwater - Curragh Mine 66 kV | 6015_Blackwater - Curragh Mine 66 kV | 6056_Comet - Emerald 66 kV | 6015_Blackwater - Curragh Mine 66 kV | 6015_Blackwater - Curragh Mine 66 kV | 6056_Comet - Emerald 66 kV | 6015_Blackwater - Curragh Mine 66 kV | 6015_Blackwater - Curragh Mine 66 kV | 6056_Comet - Emerald 66 kV
CA-Emerald | 6079_Barcaldine - Longreach 66 kV | % of Rated A | 77.74% | 78.91% | 41.62% | 75.99% | 76.93% | 40.78% | 75.86% | 76.91% | 40.77% | 75.9% | 76.93% | 40.78% | 75.98% | 76.98% | 40.78%
CA-Emerald | 6079_Barcaldine - Longreach 66 kV | Limiting Line Name | TR_CABLE 562_1 | TR_CABLE 562_1 | TR_CABLE 562_1 | TR_CABLE 562_1 | TR_CABLE 562_1 | TR_CABLE 562_1 | TR_CABLE 562_1 | TR_CABLE 562_1 | TR_CABLE 562_1 | TR_CABLE 562_1 | TR_CABLE 562_1 | TR_CABLE 562_1 | TR_CABLE 562_1 | TR_CABLE 562_1 | TR_CABLE 562_1
CA-Emerald | 6079_Barcaldine - Longreach 66 kV | Loading (A) | 77.7362 | 78.9068 | 41.6164 | 75.9932 | 76.9308 | 40.7756 | 75.8583 | 76.908 | 40.7728 | 75.9019 | 76.9338 | 40.7759 | 75.9829 | 76.9788 | 40.781
CA-Emerald | 6079_Barcaldine - Longreach 66 kV | Loading (MVA) | 9.2353 | 9.4349 | 4.9718 | 9.0278 | 9.2212 | 4.875 | 9.0266 | 9.2209 | 4.875 | 9.027 | 9.2212 | 4.875 | 9.0277 | 9.2216 | 4.8748
CA-Emerald | 6079_Barcaldine - Longreach 66 kV | Loading (MW) | 9.2341 | 9.4341 | 4.8145 | 9.0254 | 9.2191 | 4.7084 | 9.0239 | 9.2189 | 4.7084 | 9.0244 | 9.2192 | 4.7085 | 9.0253 | 9.2197 | 4.7085
CA-Emerald | 6079_Barcaldine - Longreach 66 kV | Power Factor | 0.99988 | 0.99992 | 0.96836 | 0.99974 | 0.99978 | 0.96584 | 0.99971 | 0.99978 | 0.96583 | 0.99972 | 0.99978 | 0.96585 | 0.99973 | 0.99979 | 0.96588
CA-Emerald | 6079_Barcaldine - Longreach 66 kV | Rating (A) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
CA-Emerald | 6079_Barcaldine - Longreach 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Emerald | 6079_Barcaldine - Longreach 66 kV | Min Voltage at Constrained Conductor | 68.5902 | 69.0329 | 68.9747 | 68.5873 | 69.2022 | 69.0254 | 68.6996 | 69.2211 | 69.0312 | 68.6633 | 69.1998 | 69.0247 | 68.5958 | 69.1626 | 69.0141
CA-Emerald | 6079_Barcaldine - Longreach 66 kV | Contingency Outage | 6073_Clermont - Blair Athol 66 kV | 6073_Clermont - Blair Athol 66 kV | 6080_Barcaldine - Blackall 66 kV | 6067 Lilyvale - Emerald 66 kV | 6073_Clermont - Blair Athol 66 kV | 6080_Barcaldine - Blackall 66 kV | 6011_Blackwater - Comet 66 kV | 6073_Clermont - Blair Athol 66 kV | 6080_Barcaldine - Blackall 66 kV | 6011_Blackwater - Comet 66 kV | 6073_Clermont - Blair Athol 66 kV | 6080_Barcaldine - Blackall 66 kV | 6080_Barcaldine - Blackall 66 kV | 6073_Clermont - Blair Athol 66 kV | 6080_Barcaldine - Blackall 66 kV
CA-Emerald | 6080_Barcaldine - Blackall 66 kV | % of Rated A | 9.691% | 10.04% | 6.137% | 9.702% | 10.02% | 6.136% | 9.702% | 10.02% | 6.136% | 9.701% | 10.02% | 6.136% | 9.701% | 10.03% | 6.137%
CA-Emerald | 6080_Barcaldine - Blackall 66 kV | Limiting Line Name | TR_LINE 225287_1 | TR_LINE 22558_1 | TR_LINE 22558_1 | TR_LINE 225287_1 | TR_LINE 22558_1 | TR_LINE 22558_1 | TR_LINE 225287_1 | TR_LINE 22558_1 | TR_LINE 22558_1 | TR_LINE 225287_1 | TR_LINE 22558_1 | TR_LINE 22558_1 | TR_LINE 225287_1 | TR_LINE 22558_1 | TR_LINE 22558_1
CA-Emerald | 6080_Barcaldine - Blackall 66 kV | Loading (A) | 36.2426 | 39.0555 | 20.7444 | 36.2843 | 38.981 | 20.7409 | 36.2847 | 38.9721 | 20.7404 | 36.2817 | 38.9823 | 20.7409 | 36.2805 | 39.0001 | 20.7417
CA-Emerald | 6080_Barcaldine - Blackall 66 kV | Loading (MVA) | 4.1889 | 4.5616 | 2.4844 | 4.1887 | 4.5623 | 2.4856 | 4.1887 | 4.5624 | 2.4858 | 4.1887 | 4.5623 | 2.4856 | 4.1887 | 4.562 | 2.4853
CA-Emerald | 6080_Barcaldine - Blackall 66 kV | Loading (MW) | 4.1586 | 4.4597 | 2.0441 | 4.1588 | 4.4594 | 2.0441 | 4.1588 | 4.4594 | 2.0441 | 4.1587 | 4.4595 | 2.0441 | 4.1587 | 4.4596 | 2.0441
CA-Emerald | 6080_Barcaldine - Blackall 66 kV | Power Factor | 0.99277 | 0.97767 | 0.82278 | 0.99284 | 0.97746 | 0.82237 | 0.99284 | 0.97741 | 0.82231 | 0.99284 | 0.97747 | 0.82237 | 0.99284 | 0.97755 | 0.82247
CA-Emerald | 6080_Barcaldine - Blackall 66 kV | Rating (A) | 374 | 389 | 338 | 374 | 389 | 338 | 374 | 389 | 338 | 374 | 389 | 338 | 374 | 389 | 338
CA-Emerald | 6080_Barcaldine - Blackall 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Emerald | 6080_Barcaldine - Blackall 66 kV | Min Voltage at Constrained Conductor | 66.4542 | 67.4321 | 69.1456 | 66.3745 | 67.5715 | 69.1903 | 66.3739 | 67.589 | 69.1971 | 66.3796 | 67.5689 | 69.1907 | 66.3818 | 67.534 | 69.1799
CA-Emerald | 6080_Barcaldine - Blackall 66 kV | Contingency Outage | 6072_Lilyvale - Gordonstone Mine 66 kV | 6073_Clermont - Blair Athol 66 kV | 6067 Lilyvale - Emerald 66 kV | 6086_Tieri Tee - Middlemount 66 kV | 6073_Clermont - Blair Athol 66 kV | 6067 Lilyvale - Emerald 66 kV | 6085_Tieri Tee - Tieri 66 kV | 6073_Clermont - Blair Athol 66 kV | 6067 Lilyvale - Emerald 66 kV | 6086_Tieri Tee - Middlemount 66 kV | 6073_Clermont - Blair Athol 66 kV | 6067 Lilyvale - Emerald 66 kV | 6068_Lilyvale - Ensham Mine 66 kV | 6073_Clermont - Blair Athol 66 kV | 6067 Lilyvale - Emerald 66 kV
CA-Emerald | 6085_Tieri Tee - Tieri 66 kV | % of Rated A | 6.407% | 5.481% | 2.757% | 6.41% | 5.479% | 2.757% | 6.407% | 5.482% | 2.757% | 6.408% | 5.481% | 2.757% | 6.408% | 5.483% | 2.757%
CA-Emerald | 6085_Tieri Tee - Tieri 66 kV | Limiting Line Name | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1
CA-Emerald | 6085_Tieri Tee - Tieri 66 kV | Loading (A) | 15.5691 | 14.9071 | 6.8382 | 15.5757 | 14.9037 | 6.838 | 15.5686 | 14.91 | 6.838 | 15.5711 | 14.9095 | 6.8384 | 15.5724 | 14.9128 | 6.8386
CA-Emerald | 6085_Tieri Tee - Tieri 66 kV | Loading (MVA) | 1.8253 | 1.7488 | 0.80403 | 1.8253 | 1.7488 | 0.80403 | 1.8253 | 1.7488 | 0.80403 | 1.8253 | 1.7488 | 0.80403 | 1.8253 | 1.7488 | 0.80403
CA-Emerald | 6085_Tieri Tee - Tieri 66 kV | Loading (MW) | 1.818 | 1.7418 | 0.80113 | 1.818 | 1.7418 | 0.80113 | 1.818 | 1.7418 | 0.80113 | 1.818 | 1.7418 | 0.80113 | 1.818 | 1.7418 | 0.80113
CA-Emerald | 6085_Tieri Tee - Tieri 66 kV | Power Factor | 0.99509 | 0.99516 | 0.996 | 0.99509 | 0.99516 | 0.996 | 0.99509 | 0.99515 | 0.996 | 0.99509 | 0.99515 | 0.996 | 0.99509 | 0.99515 | 0.996
CA-Emerald | 6085_Tieri Tee - Tieri 66 kV | Rating (A) | 243 | 272 | 248 | 243 | 272 | 248 | 243 | 272 | 248 | 243 | 272 | 248 | 243 | 272 | 248
CA-Emerald | 6085_Tieri Tee - Tieri 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Emerald | 6085_Tieri Tee - Tieri 66 kV | Min Voltage at Constrained Conductor | 67.6862 | 67.7292 | 67.8845 | 67.6575 | 67.7443 | 67.8865 | 67.6884 | 67.7158 | 67.8858 | 67.6776 | 67.718 | 67.8821 | 67.6718 | 67.7034 | 67.8806
CA-Emerald | 6085_Tieri Tee - Tieri 66 kV | Contingency Outage | 6069_Lilyvale - German Creek Mine 66 kV | 6011_Blackwater - Comet 66 kV | 6072_Lilyvale - Gordonstone Mine 66 kV | 6071_Lilyvale - Oaky Creek Mine 66 kV | 6011_Blackwater - Comet 66 kV | 6072_Lilyvale - Gordonstone Mine 66 kV | 6071_Lilyvale - Oaky Creek Mine 66 kV | 6011_Blackwater - Comet 66 kV | 6072_Lilyvale - Gordonstone Mine 66 kV | 6071_Lilyvale - Oaky Creek Mine 66 kV | 6011_Blackwater - Comet 66 kV | 6072_Lilyvale - Gordonstone Mine 66 kV | 6071_Lilyvale - Oaky Creek Mine 66 kV | 6011_Blackwater - Comet 66 kV | 6072_Lilyvale - Gordonstone Mine 66 kV
CA-Emerald | 6086_Tieri Tee - Middlemount 66 kV | % of Rated A | 37.87% | 34.06% | 28.62% | 37.88% | 34.05% | 28.61% | 37.48% | 33.71% | 28.45% | 37.87% | 34.07% | 28.62% | 37.87% | 34.08% | 28.62%
CA-Emerald | 6086_Tieri Tee - Middlemount 66 kV | Limiting Line Name | TR_LINE 17095_1 | TR_CABLE 10487_1 | TR_LINE 17095_1 | TR_LINE 17095_1 | TR_CABLE 10487_1 | TR_LINE 17095_1 | TR_LINE 17095_1 | TR_CABLE 10487_1 | TR_LINE 17095_1 | TR_LINE 17095_1 | TR_CABLE 10487_1 | TR_LINE 17095_1 | TR_LINE 17095_1 | TR_CABLE 10487_1 | TR_LINE 17095_1
CA-Emerald | 6086_Tieri Tee - Middlemount 66 kV | Loading (A) | 92.0138 | 87.5394 | 70.9663 | 92.0567 | 87.518 | 70.9641 | 91.0847 | 86.635 | 70.5491 | 92.0266 | 87.5553 | 70.969 | 92.0353 | 87.576 | 70.9708
CA-Emerald | 6086_Tieri Tee - Middlemount 66 kV | Loading (MVA) | 10.542 | 10.0773 | 8.1779 | 10.5422 | 10.0772 | 8.1779 | 10.4377 | 9.9733 | 8.1305 | 10.5421 | 10.0774 | 8.178 | 10.5421 | 10.0775 | 8.178
CA-Emerald | 6086_Tieri Tee - Middlemount 66 kV | Loading (MW) | 10.2134 | 9.7968 | 7.873 | 10.2135 | 9.7968 | 7.873 | 10.1112 | 9.6947 | 7.8258 | 10.2134 | 9.7968 | 7.873 | 10.2134 | 9.7969 | 7.873
CA-Emerald | 6086_Tieri Tee - Middlemount 66 kV | Power Factor | 0.96791 | 0.97186 | 0.96022 | 0.9679 | 0.97186 | 0.96022 | 0.96774 | 0.97176 | 0.96 | 0.9679 | 0.97185 | 0.96022 | 0.9679 | 0.97184 | 0.96022
CA-Emerald | 6086_Tieri Tee - Middlemount 66 kV | Rating (A) | 243 | 257 | 248 | 243 | 257 | 248 | 243 | 257 | 248 | 243 | 257 | 248 | 243 | 257 | 248
CA-Emerald | 6086_Tieri Tee - Middlemount 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Emerald | 6086_Tieri Tee - Middlemount 66 kV | Min Voltage at Constrained Conductor | 65.7743 | 66.4629 | 66.3664 | 65.7446 | 66.4784 | 66.3684 | 65.7963 | 66.4635 | 66.3762 | 65.7654 | 66.4515 | 66.3639 | 65.7594 | 66.4365 | 66.3623
CA-Emerald | 6086_Tieri Tee - Middlemount 66 kV | Contingency Outage | 6069_Lilyvale - German Creek Mine 66 kV | 6011_Blackwater - Comet 66 kV | 6072_Lilyvale - Gordonstone Mine 66 kV | 6071_Lilyvale - Oaky Creek Mine 66 kV | 6011_Blackwater - Comet 66 kV | 6072_Lilyvale - Gordonstone Mine 66 kV | 6071_Lilyvale - Oaky Creek Mine 66 kV | 6011_Blackwater - Comet 66 kV | 6072_Lilyvale - Gordonstone Mine 66 kV | 6071_Lilyvale - Oaky Creek Mine 66 kV | 6011_Blackwater - Comet 66 kV | 6072_Lilyvale - Gordonstone Mine 66 kV | 6071_Lilyvale - Oaky Creek Mine 66 kV | 6011_Blackwater - Comet 66 kV | 6072_Lilyvale - Gordonstone Mine 66 kV
CA-Emerald | 7153_Lilyvale - Clermont 132 kV | % of Rated A | 24.44% | 22.29% | 19.3% | 24.3% | 22.16% | 19.27% | 24.26% | 22.15% | 19.26% | 24.3% | 22.17% | 19.27% | 24.43% | 22.28% | 19.3%
CA-Emerald | 7153_Lilyvale - Clermont 132 kV | Limiting Line Name | TR_LINE 52800_1 | TR_LINE 52800_1 | TR_LINE 52800_1 | TR_LINE 52800_1 | TR_LINE 52800_1 | TR_LINE 52800_1 | TR_LINE 52800_1 | TR_LINE 52800_1 | TR_LINE 52800_1 | TR_LINE 52800_1 | TR_LINE 52800_1 | TR_LINE 52800_1 | TR_LINE 52800_1 | TR_LINE 52800_1 | TR_LINE 52800_1
CA-Emerald | 7153_Lilyvale - Clermont 132 kV | Loading (A) | 173.0274 | 161.3496 | 122.9415 | 172.0688 | 160.4733 | 122.7248 | 171.7813 | 160.3328 | 122.6852 | 172.0089 | 160.4779 | 122.7237 | 172.9923 | 161.2811 | 122.9489
CA-Emerald | 7153_Lilyvale - Clermont 132 kV | Loading (MVA) | 42.0931 | 39.3153 | 30.0863 | 41.8254 | 39.1038 | 30.0341 | 41.7892 | 39.0671 | 30.0242 | 41.8433 | 39.1026 | 30.0332 | 42.0811 | 39.2967 | 30.0879
CA-Emerald | 7153_Lilyvale - Clermont 132 kV | Loading (MW) | 39.6628 | 35.9539 | 19.6334 | 39.3445 | 35.6118 | 19.4804 | 39.2668 | 35.5609 | 19.4581 | 39.3415 | 35.612 | 19.4804 | 39.5924 | 35.8661 | 19.5885
CA-Emerald | 7153_Lilyvale - Clermont 132 kV | Power Factor | 0.94226 | 0.9145 | 0.65257 | 0.94069 | 0.9107 | 0.64861 | 0.93964 | 0.91025 | 0.64808 | 0.94021 | 0.91073 | 0.64863 | 0.94086 | 0.9127 | 0.65104
CA-Emerald | 7153_Lilyvale - Clermont 132 kV | Rating (A) | 708 | 724 | 637 | 708 | 724 | 637 | 708 | 724 | 637 | 708 | 724 | 637 | 708 | 724 | 637
CA-Emerald | 7153_Lilyvale - Clermont 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Emerald | 7153_Lilyvale - Clermont 132 kV | Min Voltage at Constrained Conductor | 140.4546 | 140.6802 | 141.2892 | 140.3386 | 140.6875 | 141.293 | 140.4519 | 140.6785 | 141.2923 | 140.4476 | 140.679 | 141.2904 | 140.4428 | 140.6736 | 141.2883
CA-Emerald | 7153_Lilyvale - Clermont 132 kV | Contingency Outage | 6011_Blackwater - Comet 66 kV | 6011_Blackwater - Comet 66 kV | 6071_Lilyvale - Oaky Creek Mine 66 kV | 6067 Lilyvale - Emerald 66 kV | 6011_Blackwater - Comet 66 kV | 6071_Lilyvale - Oaky Creek Mine 66 kV | 6011_Blackwater - Comet 66 kV | 6011_Blackwater - Comet 66 kV | 6071_Lilyvale - Oaky Creek Mine 66 kV | 6011_Blackwater - Comet 66 kV | 6011_Blackwater - Comet 66 kV | 6071_Lilyvale - Oaky Creek Mine 66 kV | 6011_Blackwater - Comet 66 kV | 6011_Blackwater - Comet 66 kV | 6071_Lilyvale - Oaky Creek Mine 66 kV
CA-Emerald | 7154_Clermont - Barcaldine 132 kV | % of Rated A | 26.66% | 23.78% | 23.25% | 26.5% | 23.7% | 23.24% | 26.45% | 23.67% | 23.24% | 26.5% | 23.7% | 23.24% | 26.6% | 23.73% | 23.25%
CA-Emerald | 7154_Clermont - Barcaldine 132 kV | Limiting Line Name | TR_LINE 52329_1 | TR_LINE 52329_1 | TR_LINE 52329_1 | TR_LINE 52329_1 | TR_LINE 52329_1 | TR_LINE 52329_1 | TR_LINE 52329_1 | TR_LINE 52329_1 | TR_LINE 52329_1 | TR_LINE 52329_1 | TR_LINE 52329_1 | TR_LINE 52329_1 | TR_LINE 52329_1 | TR_LINE 52329_1 | TR_LINE 52329_1
CA-Emerald | 7154_Clermont - Barcaldine 132 kV | Loading (A) | 95.9582 | 92.9838 | 81.6078 | 95.4081 | 92.6763 | 81.5853 | 95.2332 | 92.5659 | 81.564 | 95.4088 | 92.6754 | 81.5847 | 95.7711 | 92.7802 | 81.6017
CA-Emerald | 7154_Clermont - Barcaldine 132 kV | Loading (MVA) | 23.516 | 22.9614 | 20.6649 | 23.368 | 22.9 | 20.6628 | 23.3203 | 22.8739 | 20.6578 | 23.3692 | 22.899 | 20.6625 | 23.4484 | 22.9186 | 20.6652
CA-Emerald | 7154_Clermont - Barcaldine 132 kV | Loading (MW) | 19.276 | 18.2037 | 8.9498 | 19.0587 | 17.9685 | 8.8409 | 18.9873 | 17.9189 | 8.8189 | 19.0585 | 17.9686 | 8.8409 | 19.119 | 18.0187 | 8.8628
CA-Emerald | 7154_Clermont - Barcaldine 132 kV | Power Factor | 0.8197 | 0.7928 | 0.43309 | 0.81559 | 0.78465 | 0.42786 | 0.8142 | 0.78338 | 0.4269 | 0.81554 | 0.78469 | 0.42787 | 0.81536 | 0.7862 | 0.42888
CA-Emerald | 7154_Clermont - Barcaldine 132 kV | Rating (A) | 360 | 391 | 351 | 360 | 391 | 351 | 360 | 391 | 351 | 360 | 391 | 351 | 360 | 391 | 351
CA-Emerald | 7154_Clermont - Barcaldine 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Emerald | 7154_Clermont - Barcaldine 132 kV | Min Voltage at Constrained Conductor | 141.4882 | 142.5707 | 146.1981 | 141.4085 | 142.6614 | 146.2236 | 141.379 | 142.6688 | 146.226 | 141.4147 | 142.6565 | 146.2224 | 141.3573 | 142.6171 | 146.2109
CA-Emerald | 7154_Clermont - Barcaldine 132 kV | Contingency Outage | 6071_Lilyvale - Oaky Creek Mine 66 kV | 6069_Lilyvale - German Creek Mine 66 kV | 6073_Clermont - Blair Athol 66 kV | 6068_Lilyvale - Ensham Mine 66 kV | 6069_Lilyvale - German Creek Mine 66 kV | 6073_Clermont - Blair Athol 66 kV | 6091_Egan's Hill - Gavial 66 kV | 6069_Lilyvale - German Creek Mine 66 kV | 6073_Clermont - Blair Athol 66 kV | 6068_Lilyvale - Ensham Mine 66 kV | 6069_Lilyvale - German Creek Mine 66 kV | 6073_Clermont - Blair Athol 66 kV | 6085_Tieri Tee - Tieri 66 kV | 6069_Lilyvale - German Creek Mine 66 kV | 6073_Clermont - Blair Athol 66 kV
CA-Emerald | 7450_Memooloo - Rolleston 132 kV | % of Rated A | 9.149% | 10.24% | 9.834% | 9.175% | 10.19% | 9.8% | 9.683% | 10.79% | 10.18% | 9.683% | 10.79% | 10.18% | 9.74% | 10.85% | 10.22%
CA-Emerald | 7450_Memooloo - Rolleston 132 kV | Limiting Line Name | TR_LINE 200891_1 | TR_LINE 200891_1 | TR_LINE 200891_1 | TR_LINE 200891_1 | TR_LINE 200891_1 | TR_LINE 200891_1 | TR_LINE 200891_1 | TR_LINE 200891_1 | TR_LINE 200891_1 | TR_LINE 200891_1 | TR_LINE 200891_1 | TR_LINE 200891_1 | TR_LINE 200891_1 | TR_LINE 200891_1 | TR_LINE 200891_1
CA-Emerald | 7450_Memooloo - Rolleston 132 kV | Loading (A) | 64.5025 | 75.2861 | 64.1207 | 64.6822 | 74.8682 | 63.8929 | 68.2659 | 79.2785 | 66.4024 | 68.2659 | 79.2958 | 66.4024 | 68.6654 | 79.7235 | 66.631
CA-Emerald | 7450_Memooloo - Rolleston 132 kV | Loading (MVA) | 15.4983 | 17.9708 | 15.4407 | 15.4049 | 17.8787 | 15.3866 | 16.4436 | 18.892 | 15.9821 | 16.4436 | 18.892 | 15.9821 | 16.5383 | 18.9843 | 16.0363
CA-Emerald | 7450_Memooloo - Rolleston 132 kV | Loading (MW) | 15.0483 | 17.3629 | 14.8225 | 14.9533 | 17.2707 | 14.7679 | 15.9941 | 18.285 | 15.3689 | 15.9941 | 18.285 | 15.3689 | 16.0887 | 18.3772 | 15.4235
CA-Emerald | 7450_Memooloo - Rolleston 132 kV | Power Factor | 0.97097 | 0.96617 | 0.95996 | 0.97068 | 0.96599 | 0.95978 | 0.97266 | 0.96787 | 0.96163 | 0.97266 | 0.96787 | 0.96163 | 0.97281 | 0.96802 | 0.96179
CA-Emerald | 7450_Memooloo - Rolleston 132 kV | Rating (A) | 705 | 735 | 652 | 705 | 735 | 652 | 705 | 735 | 652 | 705 | 735 | 652 | 705 | 735 | 652
CA-Emerald | 7450_Memooloo - Rolleston 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Emerald | 7450_Memooloo - Rolleston 132 kV | Min Voltage at Constrained Conductor | 138.7222 | 137.8134 | 139.0301 | 137.5032 | 137.8728 | 139.0371 | 139.0697 | 137.5821 | 138.9594 | 139.0697 | 137.5523 | 138.9594 | 139.0569 | 137.4829 | 138.9523
CA-Emerald | 7450_Memooloo - Rolleston 132 kV | Contingency Outage | 6067 Lilyvale - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6063_Dysart - Norwich Park Mine 66 kV | 6067 Lilyvale - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6063_Dysart - Norwich Park Mine 66 kV | 6063_Dysart - Norwich Park Mine 66 kV | 6067 Lilyvale - Emerald 66 kV | 6063_Dysart - Norwich Park Mine 66 kV | 6063_Dysart - Norwich Park Mine 66 kV | 6067 Lilyvale - Emerald 66 kV | 6063_Dysart - Norwich Park Mine 66 kV | 6063_Dysart - Norwich Park Mine 66 kV | 6067 Lilyvale - Emerald 66 kV | 6063_Dysart - Norwich Park Mine 66 kV
CA-Gladstone Rockhampton | 6001_Glenmore - Parkhurst 66 kV | % of Rated A | 35.68% | 34.46% | 20.07% | 35.59% | 33.92% | 20.04% | 36.02% | 34.46% | 20.1% | 35.98% | 34.5% | 20.3% | 36.93% | 35.1% | 20.6%
CA-Gladstone Rockhampton | 6001_Glenmore - Parkhurst 66 kV | Limiting Line Name | TR_LINE 21203_1 | TR_LINE 21203_1 | TR_LINE 22133_1 | TR_LINE 21203_1 | TR_LINE 21203_1 | TR_LINE 22133_1 | TR_LINE 21203_1 | TR_LINE 21203_1 | TR_LINE 22133_1 | TR_LINE 21203_1 | TR_LINE 21203_1 | TR_LINE 22133_1 | TR_LINE 21203_1 | TR_LINE 21203_1 | TR_LINE 22133_1
CA-Gladstone Rockhampton | 6001_Glenmore - Parkhurst 66 kV | Loading (A) | 143.0812 | 144.0533 | 74.6505 | 142.726 | 141.7808 | 74.5555 | 144.4593 | 144.057 | 74.7843 | 144.2663 | 144.2243 | 75.5229 | 148.0775 | 146.7148 | 76.6427
CA-Gladstone Rockhampton | 6001_Glenmore - Parkhurst 66 kV | Loading (MVA) | 16.9969 | 16.9956 | 8.9179 | 16.9652 | 16.9728 | 8.9083 | 17.0447 | 16.9921 | 8.9314 | 17.1969 | 17.1503 | 9.0145 | 17.4678 | 17.4282 | 9.1447
CA-Gladstone Rockhampton | 6001_Glenmore - Parkhurst 66 kV | Loading (MW) | 16.9384 | 16.9481 | 8.8875 | 16.908 | 16.9248 | 8.8775 | 16.98 | 16.9447 | 8.9015 | 17.1346 | 17.1022 | 8.9839 | 17.3884 | 17.3679 | 9.1202
CA-Gladstone Rockhampton | 6001_Glenmore - Parkhurst 66 kV | Power Factor | 0.99656 | 0.9972 | 0.99659 | 0.99663 | 0.99717 | 0.99654 | 0.9962 | 0.99721 | 0.99665 | 0.99638 | 0.9972 | 0.9966 | 0.99546 | 0.99654 | 0.99732
CA-Gladstone Rockhampton | 6001_Glenmore - Parkhurst 66 kV | Rating (A) | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372
CA-Gladstone Rockhampton | 6001_Glenmore - Parkhurst 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Gladstone Rockhampton | 6001_Glenmore - Parkhurst 66 kV | Min Voltage at Constrained Conductor | 67.9739 | 67.5042 | 68.9696 | 68.0183 | 68.5146 | 68.9837 | 67.5015 | 67.4882 | 68.951 | 68.2045 | 68.0425 | 68.9117 | 67.4654 | 67.9549 | 68.8856
CA-Gladstone Rockhampton | 6001_Glenmore - Parkhurst 66 kV | Contingency Outage | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV
CA-Gladstone Rockhampton | 6003_Glenmore - Berserker 66 kV | % of Rated A | 102.3% | 95.55% | 58.79% | 101% | 93.54% | 58.18% | 102.7% | 94.65% | 57.93% | 101% | 95.07% | 57.87% | 105% | 96.08% | 58.43%
CA-Gladstone Rockhampton | 6003_Glenmore - Berserker 66 kV | Limiting Line Name | TR_LINE 22137_1 | TR_LINE 102404_1 | TR_LINE 22137_1 | TR_LINE 22137_1 | TR_LINE 200510_1 | TR_LINE 22137_1 | TR_LINE 200510_1 | TR_LINE 102404_1 | TR_LINE 22137_1 | TR_LINE 22137_1 | TR_LINE 200510_1 | TR_LINE 22137_1 | TR_LINE 200510_1 | TR_LINE 200510_1 | TR_LINE 22137_1
CA-Gladstone Rockhampton | 6003_Glenmore - Berserker 66 kV | Loading (A) | 410.2752 | 399.4108 | 218.6863 | 404.9626 | 391.007 | 216.4217 | 411.6903 | 395.6198 | 215.5134 | 404.8756 | 397.3862 | 215.2776 | 420.9401 | 401.6352 | 217.3697
CA-Gladstone Rockhampton | 6003_Glenmore - Berserker 66 kV | Loading (MVA) | 48.4449 | 46.8534 | 26.1326 | 47.8323 | 46.5316 | 25.8667 | 48.2751 | 46.4013 | 25.7484 | 48.6116 | 46.8433 | 25.7086 | 49.3313 | 47.6417 | 25.9504
CA-Gladstone Rockhampton | 6003_Glenmore - Berserker 66 kV | Loading (MW) | 48.4449 | 46.8525 | 24.3876 | 47.8313 | 46.5119 | 24.0911 | 48.2538 | 46.3999 | 23.9679 | 48.6088 | 46.821 | 23.9424 | 49.3145 | 47.5853 | 24.2345
CA-Gladstone Rockhampton | 6003_Glenmore - Berserker 66 kV | Power Factor | 1 | 0.99998 | 0.93316 | 0.99998 | 0.99958 | 0.93129 | 0.99956 | 0.99997 | 0.93078 | 0.99994 | 0.99953 | 0.93123 | 0.99966 | 0.99882 | 0.93381
CA-Gladstone Rockhampton | 6003_Glenmore - Berserker 66 kV | Rating (A) | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372
CA-Gladstone Rockhampton | 6003_Glenmore - Berserker 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Gladstone Rockhampton | 6003_Glenmore - Berserker 66 kV | Min Voltage at Constrained Conductor | 68.1575 | 67.7029 | 68.9897 | 68.1788 | 68.6854 | 69.0023 | 67.6773 | 67.6923 | 68.9764 | 69.3048 | 68.0348 | 68.9451 | 67.638 | 68.4617 | 68.9236
CA-Gladstone Rockhampton | 6003_Glenmore - Berserker 66 kV | Contingency Outage | 6082_Farnborough Tee - Yeppoon 66 kV | 6051_Parkhurst - Keppel 66 kV | 6096_Egan's Hill - Lakes Creek 66 kV | 6051_Parkhurst - Keppel 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6096_Egan's Hill - Lakes Creek 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6051_Parkhurst - Keppel 66 kV | 6096_Egan's Hill - Lakes Creek 66 kV | 6051_Parkhurst - Keppel 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6096_Egan's Hill - Lakes Creek 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6096_Egan's Hill - Lakes Creek 66 kV
CA-Gladstone Rockhampton | 6004_Glenmore - Rockhampton South 66 kV | % of Rated A | 33.02% | 27.06% | 19.17% | 32.24% | 26.99% | 18.81% | 37.89% | 27.12% | 19.27% | 36.69% | 27.78% | 19.79% | 39.31% | 27.95% | 19.89%
CA-Gladstone Rockhampton | 6004_Glenmore - Rockhampton South 66 kV | Limiting Line Name | TR_LINE 139203_1 | TR_CABLE 301_1 | TR_LINE 139203_1 | TR_LINE 139203_1 | TR_CABLE 301_1 | TR_LINE 139203_1 | TR_LINE 139201_1 | TR_CABLE 301_1 | TR_LINE 139203_1 | TR_LINE 139203_1 | TR_CABLE 301_1 | TR_LINE 139203_1 | TR_LINE 139201_1 | TR_CABLE 301_1 | TR_LINE 139203_1
CA-Gladstone Rockhampton | 6004_Glenmore - Rockhampton South 66 kV | Loading (A) | 121.1885 | 100.6572 | 64.8017 | 118.3109 | 100.3925 | 63.5664 | 139.0466 | 100.8976 | 65.1392 | 134.6633 | 103.3345 | 66.899 | 144.277 | 103.9677 | 67.2218
CA-Gladstone Rockhampton | 6004_Glenmore - Rockhampton South 66 kV | Loading (MVA) | 14.349 | 11.9477 | 7.7427 | 14.015 | 11.8811 | 7.5966 | 16.4759 | 11.9739 | 7.7811 | 16.0954 | 12.2513 | 7.9871 | 17.0968 | 12.3171 | 8.0234
CA-Gladstone Rockhampton | 6004_Glenmore - Rockhampton South 66 kV | Loading (MW) | 14.1567 | 11.3562 | 7.5232 | 13.8036 | 11.7982 | 7.3616 | 16.3048 | 11.4286 | 7.5859 | 15.5925 | 11.7868 | 7.8276 | 17.0765 | 11.8536 | 7.8612
CA-Gladstone Rockhampton | 6004_Glenmore - Rockhampton South 66 kV | Power Factor | 0.98658 | 0.95049 | 0.97166 | 0.9849 | 0.99302 | 0.96907 | 0.98962 | 0.95446 | 0.97492 | 0.96872 | 0.96208 | 0.98002 | 0.99881 | 0.96237 | 0.97978
CA-Gladstone Rockhampton | 6004_Glenmore - Rockhampton South 66 kV | Rating (A) | 367 | 372 | 338 | 367 | 372 | 338 | 367 | 372 | 338 | 367 | 372 | 338 | 367 | 372 | 338
CA-Gladstone Rockhampton | 6004_Glenmore - Rockhampton South 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Gladstone Rockhampton | 6004_Glenmore - Rockhampton South 66 kV | Min Voltage at Constrained Conductor | 68.3514 | 68.5252 | 68.9797 | 68.3845 | 68.3219 | 68.9933 | 68.4077 | 68.5121 | 68.9623 | 68.9994 | 68.4457 | 68.9263 | 68.4126 | 68.3941 | 68.9066
CA-Gladstone Rockhampton | 6004_Glenmore - Rockhampton South 66 kV | Contingency Outage | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV
CA-Gladstone Rockhampton | 6005_Rockhampton Glenmore-Canning 66 kV | % of Rated A | 47.51% | 44.51% | 31% | 46.99% | 44.73% | 30.74% | 50.71% | 44.51% | 31.04% | 51.22% | 45.48% | 31.68% | 53.2% | 45.85% | 31.9%
CA-Gladstone Rockhampton | 6005_Rockhampton Glenmore-Canning 66 kV | Limiting Line Name | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1
CA-Gladstone Rockhampton | 6005_Rockhampton Glenmore-Canning 66 kV | Loading (A) | 189.5735 | 184.7366 | 114.6936 | 187.4787 | 185.6173 | 113.741 | 202.3436 | 184.7132 | 114.854 | 204.3515 | 188.7468 | 117.2058 | 212.2571 | 190.258 | 118.0179
CA-Gladstone Rockhampton | 6005_Rockhampton Glenmore-Canning 66 kV | Loading (MVA) | 22.4721 | 21.9305 | 13.7105 | 22.2331 | 21.9724 | 13.599 | 24.0382 | 21.9237 | 13.7266 | 24.449 | 22.3813 | 14.0012 | 25.2119 | 22.5435 | 14.0942
CA-Gladstone Rockhampton | 6005_Rockhampton Glenmore-Canning 66 kV | Loading (MW) | 21.9317 | 21.4009 | 12.8837 | 21.6809 | 21.8282 | 12.758 | 24.0366 | 21.4286 | 12.9464 | 23.6349 | 21.9603 | 13.3024 | 25.1622 | 22.1339 | 13.4038
CA-Gladstone Rockhampton | 6005_Rockhampton Glenmore-Canning 66 kV | Power Factor | 0.97579 | 0.97569 | 0.93963 | 0.97499 | 0.99336 | 0.93811 | 0.99992 | 0.97727 | 0.94311 | 0.96648 | 0.98105 | 0.95003 | 0.99798 | 0.98169 | 0.95095
CA-Gladstone Rockhampton | 6005_Rockhampton Glenmore-Canning 66 kV | Rating (A) | 399 | 415 | 370 | 399 | 415 | 370 | 399 | 415 | 370 | 399 | 415 | 370 | 399 | 415 | 370
CA-Gladstone Rockhampton | 6005_Rockhampton Glenmore-Canning 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Gladstone Rockhampton | 6005_Rockhampton Glenmore-Canning 66 kV | Min Voltage at Constrained Conductor | 68.4141 | 68.5141 | 69.0075 | 68.4435 | 68.3119 | 69.0194 | 68.5461 | 68.5011 | 68.9916 | 69.0516 | 68.4344 | 68.9585 | 68.5372 | 68.3825 | 68.9386
CA-Gladstone Rockhampton | 6005_Rockhampton Glenmore-Canning 66 kV | Contingency Outage | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV
CA-Gladstone Rockhampton | 6006_Glenmore - Frenchville 66 kV | % of Rated A | 45.01% | 47.12% | 23.68% | 44.67% | 46.1% | 23.55% | 45.07% | 46.72% | 23.56% | 44.87% | 46.6% | 23.73% | 45.91% | 47.23% | 24.03%
CA-Gladstone Rockhampton | 6006_Glenmore - Frenchville 66 kV | Limiting Line Name | TR_LINE 22209_1 | TR_LINE 22209_1 | TR_LINE 22134_1 | TR_LINE 22209_1 | TR_LINE 22209_1 | TR_LINE 22134_1 | TR_LINE 22209_1 | TR_LINE 22209_1 | TR_LINE 22134_1 | TR_LINE 22209_1 | TR_LINE 22209_1 | TR_LINE 22134_1 | TR_LINE 22209_1 | TR_LINE 22209_1 | TR_LINE 22134_1
CA-Gladstone Rockhampton | 6006_Glenmore - Frenchville 66 kV | Loading (A) | 180.4857 | 196.9448 | 88.1011 | 179.1463 | 192.678 | 87.5916 | 180.732 | 195.2849 | 87.658 | 179.9388 | 194.7934 | 88.2819 | 184.1189 | 197.4043 | 89.4015
CA-Gladstone Rockhampton | 6006_Glenmore - Frenchville 66 kV | Loading (MVA) | 21.2954 | 23.0588 | 10.5247 | 21.1518 | 22.8974 | 10.466 | 21.1791 | 22.8609 | 10.469 | 21.3054 | 22.9913 | 10.5375 | 21.5681 | 23.2723 | 10.6671
CA-Gladstone Rockhampton | 6006_Glenmore - Frenchville 66 kV | Loading (MW) | 21.159 | 22.9 | 10.5241 | 21.0189 | 22.7407 | 10.4653 | 21.0387 | 22.7064 | 10.4683 | 21.1675 | 22.837 | 10.5367 | 21.4125 | 23.1028 | 10.6669
CA-Gladstone Rockhampton | 6006_Glenmore - Frenchville 66 kV | Power Factor | 0.9936 | 0.99312 | 0.99994 | 0.99372 | 0.99316 | 0.99993 | 0.99337 | 0.99324 | 0.99994 | 0.99353 | 0.99329 | 0.99993 | 0.99279 | 0.99272 | 0.99998
CA-Gladstone Rockhampton | 6006_Glenmore - Frenchville 66 kV | Rating (A) | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372
CA-Gladstone Rockhampton | 6006_Glenmore - Frenchville 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Gladstone Rockhampton | 6006_Glenmore - Frenchville 66 kV | Min Voltage at Constrained Conductor | 68.116 | 67.5919 | 68.9664 | 68.1626 | 68.6054 | 68.9804 | 67.6517 | 67.5815 | 68.9477 | 68.3552 | 68.1385 | 68.9084 | 67.6268 | 68.059 | 68.8823
CA-Gladstone Rockhampton | 6006_Glenmore - Frenchville 66 kV | Contingency Outage | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6053_Parkhurst - Pandoin 66 kV
CA-Gladstone Rockhampton | 6007_Biloela - Coominglah Tee 66 kV | % of Rated A | 36% | 32.84% | 18.88% | 36% | 32.84% | 18.88% | 35.45% | 32.3% | 18.67% | 36% | 32.84% | 18.88% | 36% | 32.84% | 18.88%
CA-Gladstone Rockhampton | 6007_Biloela - Coominglah Tee 66 kV | Limiting Line Name | TR_LINE 18121_1 | TR_LINE 18121_1 | TR_LINE 18121_1 | TR_LINE 18121_1 | TR_LINE 18121_1 | TR_LINE 18121_1 | TR_LINE 18121_1 | TR_LINE 18121_1 | TR_LINE 18121_1 | TR_LINE 18121_1 | TR_LINE 18121_1 | TR_LINE 18121_1 | TR_LINE 18121_1 | TR_LINE 18121_1 | TR_LINE 18121_1
CA-Gladstone Rockhampton | 6007_Biloela - Coominglah Tee 66 kV | Loading (A) | 47.525 | 54.8501 | 30.0149 | 47.5204 | 54.8448 | 30.0144 | 46.79 | 53.9464 | 29.6794 | 47.5207 | 54.8438 | 30.0141 | 47.5237 | 54.8473 | 30.0144
CA-Gladstone Rockhampton | 6007_Biloela - Coominglah Tee 66 kV | Loading (MVA) | 5.6332 | 6.5891 | 3.5861 | 5.6333 | 6.5892 | 3.5862 | 5.5469 | 6.4816 | 3.5463 | 5.6333 | 6.5892 | 3.5862 | 5.6332 | 6.5891 | 3.5862
CA-Gladstone Rockhampton | 6007_Biloela - Coominglah Tee 66 kV | Loading (MW) | 5.53 | 6.5353 | 3.2086 | 5.5299 | 6.5352 | 3.2086 | 5.4377 | 6.423 | 3.1596 | 5.5299 | 6.5352 | 3.2085 | 5.53 | 6.5353 | 3.2086
CA-Gladstone Rockhampton | 6007_Biloela - Coominglah Tee 66 kV | Power Factor | 0.98168 | 0.99183 | 0.89472 | 0.98166 | 0.99182 | 0.89469 | 0.98032 | 0.99096 | 0.89097 | 0.98166 | 0.99181 | 0.89468 | 0.98167 | 0.99182 | 0.89469
CA-Gladstone Rockhampton | 6007_Biloela - Coominglah Tee 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
CA-Gladstone Rockhampton | 6007_Biloela - Coominglah Tee 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Gladstone Rockhampton | 6007_Biloela - Coominglah Tee 66 kV | Min Voltage at Constrained Conductor | 68.4313 | 69.3536 | 68.9795 | 68.4387 | 69.3603 | 68.9822 | 68.441 | 69.3641 | 68.9841 | 68.4382 | 69.3615 | 68.9838 | 68.4334 | 69.3571 | 68.9824
CA-Gladstone Rockhampton | 6007_Biloela - Coominglah Tee 66 kV | Contingency Outage | 6027_TDM Mine 66 kV | 6027_TDM Mine 66 kV | 6010_Biloela - Callide Mine 66 kV | 6027_TDM Mine 66 kV | 6027_TDM Mine 66 kV | 6010_Biloela - Callide Mine 66 kV | 6027_TDM Mine 66 kV | 6027_TDM Mine 66 kV | 6010_Biloela - Callide Mine 66 kV | 6027_TDM Mine 66 kV | 6027_TDM Mine 66 kV | 6010_Biloela - Callide Mine 66 kV | 6027_TDM Mine 66 kV | 6027_TDM Mine 66 kV | 6010_Biloela - Callide Mine 66 kV
CA-Gladstone Rockhampton | 6008_Biloela - Wowan 66 kV | % of Rated A | 35.76% | 18.17% | 13.79% | 35.75% | 18.17% | 13.79% | 35.75% | 18.17% | 13.79% | 35.76% | 18.17% | 13.79% | 35.76% | 18.17% | 13.79%
CA-Gladstone Rockhampton | 6008_Biloela - Wowan 66 kV | Limiting Line Name | TR_LINE 14892_1 | TR_LINE 14892_1 | TR_LINE 21790_1 | TR_LINE 14892_1 | TR_LINE 14892_1 | TR_LINE 21790_1 | TR_LINE 14892_1 | TR_LINE 14892_1 | TR_LINE 21790_1 | TR_LINE 14892_1 | TR_LINE 14892_1 | TR_LINE 21790_1 | TR_LINE 14892_1 | TR_LINE 14892_1 | TR_LINE 21790_1
CA-Gladstone Rockhampton | 6008_Biloela - Wowan 66 kV | Loading (A) | 47.2024 | 30.3482 | 21.9255 | 47.1965 | 30.345 | 21.9247 | 47.1947 | 30.3432 | 21.9242 | 47.1969 | 30.3444 | 21.9242 | 47.2007 | 30.3465 | 21.9247
CA-Gladstone Rockhampton | 6008_Biloela - Wowan 66 kV | Loading (MVA) | 5.4525 | 3.5871 | 2.6196 | 5.4525 | 3.587 | 2.6196 | 5.4525 | 3.587 | 2.6196 | 5.4525 | 3.587 | 2.6196 | 5.4525 | 3.5871 | 2.6196
CA-Gladstone Rockhampton | 6008_Biloela - Wowan 66 kV | Loading (MW) | 5.3734 | 3.5684 | 2.5975 | 5.3733 | 3.5684 | 2.5975 | 5.3733 | 3.5684 | 2.5975 | 5.3733 | 3.5684 | 2.5975 | 5.3733 | 3.5684 | 2.5975
CA-Gladstone Rockhampton | 6008_Biloela - Wowan 66 kV | Power Factor | 0.98352 | 0.9925 | 0.99158 | 0.98352 | 0.9925 | 0.99157 | 0.98352 | 0.9925 | 0.99157 | 0.98352 | 0.9925 | 0.99157 | 0.98352 | 0.9925 | 0.99157
CA-Gladstone Rockhampton | 6008_Biloela - Wowan 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
CA-Gladstone Rockhampton | 6008_Biloela - Wowan 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Gladstone Rockhampton | 6008_Biloela - Wowan 66 kV | Min Voltage at Constrained Conductor | 66.5645 | 68.2342 | 68.9741 | 66.5722 | 68.2411 | 68.9768 | 66.5746 | 68.2448 | 68.9786 | 66.5718 | 68.2423 | 68.9784 | 66.5667 | 68.2378 | 68.977
CA-Gladstone Rockhampton | 6008_Biloela - Wowan 66 kV | Contingency Outage | 6027_TDM Mine 66 kV | 6027_TDM Mine 66 kV | 6010_Biloela - Callide Mine 66 kV | 6027_TDM Mine 66 kV | 6027_TDM Mine 66 kV | 6010_Biloela - Callide Mine 66 kV | 6027_TDM Mine 66 kV | 6027_TDM Mine 66 kV | 6010_Biloela - Callide Mine 66 kV | 6027_TDM Mine 66 kV | 6027_TDM Mine 66 kV | 6010_Biloela - Callide Mine 66 kV | 6027_TDM Mine 66 kV | 6027_TDM Mine 66 kV | 6010_Biloela - Callide Mine 66 kV
CA-Gladstone Rockhampton | 6019_Gladstone South - Friend St 66 kV | % of Rated A | 53.76% | 35.9% | 31.86% | 53.76% | 35.81% | 32.13% | 53.49% | 35.63% | 32% | 53.49% | 35.63% | 32% | 53.26% | 35.57% | 31.84%
CA-Gladstone Rockhampton | 6019_Gladstone South - Friend St 66 kV | Limiting Line Name | TR_LINE 22252_1 | TR_LINE 22252_1 | TR_LINE 22252_1 | TR_LINE 22252_1 | TR_LINE 22252_1 | TR_LINE 22252_1 | TR_LINE 22252_1 | TR_LINE 22252_1 | TR_LINE 22252_1 | TR_LINE 22252_1 | TR_LINE 22252_1 | TR_LINE 22252_1 | TR_LINE 22252_1 | TR_LINE 22252_1 | TR_LINE 22252_1
CA-Gladstone Rockhampton | 6019_Gladstone South - Friend St 66 kV | Loading (A) | 131.7114 | 122.7695 | 90.8096 | 131.7019 | 122.4588 | 91.5699 | 131.062 | 121.8672 | 91.2017 | 131.0528 | 121.8678 | 91.2002 | 130.4753 | 121.6351 | 90.7359
CA-Gladstone Rockhampton | 6019_Gladstone South - Friend St 66 kV | Loading (MVA) | 15.6071 | 14.6672 | 10.8257 | 15.6088 | 14.633 | 10.9187 | 15.53 | 14.5613 | 10.874 | 15.5305 | 14.5613 | 10.8743 | 15.447 | 14.5214 | 10.8148
CA-Gladstone Rockhampton | 6019_Gladstone South - Friend St 66 kV | Loading (MW) | 14.8303 | 13.7474 | 9.3706 | 14.5891 | 13.5241 | 9.2187 | 14.5029 | 13.4442 | 9.1643 | 14.5029 | 13.4442 | 9.1643 | 14.6582 | 13.588 | 9.2623
CA-Gladstone Rockhampton | 6019_Gladstone South - Friend St 66 kV | Power Factor | 0.9502 | 0.93726 | 0.86558 | 0.93463 | 0.92419 | 0.84429 | 0.93383 | 0.92325 | 0.84277 | 0.9338 | 0.92326 | 0.84275 | 0.94891 | 0.93569 | 0.85644
CA-Gladstone Rockhampton | 6019_Gladstone South - Friend St 66 kV | Rating (A) | 245 | 342 | 285 | 245 | 342 | 285 | 245 | 342 | 285 | 245 | 342 | 285 | 245 | 342 | 285
CA-Gladstone Rockhampton | 6019_Gladstone South - Friend St 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Gladstone Rockhampton | 6019_Gladstone South - Friend St 66 kV | Min Voltage at Constrained Conductor | 68.4099 | 68.9735 | 68.828 | 68.423 | 68.9875 | 68.8429 | 68.4099 | 68.983 | 68.8379 | 68.4169 | 68.9825 | 68.8409 | 68.3496 | 68.9249 | 68.8143
CA-Gladstone Rockhampton | 6019_Gladstone South - Friend St 66 kV | Contingency Outage | 6023_Friend St-Clinton Industrial 66 kV | 6023_Friend St-Clinton Industrial 66 kV | 6023_Friend St-Clinton Industrial 66 kV | 6023_Friend St-Clinton Industrial 66 kV | 6023_Friend St-Clinton Industrial 66 kV | 6023_Friend St-Clinton Industrial 66 kV | 6023_Friend St-Clinton Industrial 66 kV | 6023_Friend St-Clinton Industrial 66 kV | 6023_Friend St-Clinton Industrial 66 kV | 6023_Friend St-Clinton Industrial 66 kV | 6023_Friend St-Clinton Industrial 66 kV | 6023_Friend St-Clinton Industrial 66 kV | 6023_Friend St-Clinton Industrial 66 kV | 6023_Friend St-Clinton Industrial 66 kV | 6023_Friend St-Clinton Industrial 66 kV
CA-Gladstone Rockhampton | 6020_Gladstone South - BORE 66 kV | % of Rated A | 106.6% | 106.5% | 48.71% | 111.8% | 108.5% | 50.29% | 110.9% | 107.9% | 49.83% | 112.6% | 109.1% | 50.64% | 112.7% | 110.9% | 51.21%
CA-Gladstone Rockhampton | 6020_Gladstone South - BORE 66 kV | Limiting Line Name | TR_LINE 215688_1 | TR_LINE 215688_1 | TR_LINE 215689_1 | TR_LINE 215688_1 | TR_LINE 215688_1 | TR_LINE 215689_1 | TR_LINE 215688_1 | TR_LINE 215688_1 | TR_LINE 215689_1 | TR_LINE 215688_1 | TR_LINE 215688_1 | TR_LINE 215689_1 | TR_LINE 215688_1 | TR_LINE 215688_1 | TR_LINE 215689_1
CA-Gladstone Rockhampton | 6020_Gladstone South - BORE 66 kV | Loading (A) | 225.0178 | 314.2976 | 119.34 | 235.9853 | 319.9325 | 123.2042 | 234.0119 | 318.251 | 122.093 | 237.5071 | 321.9247 | 124.0571 | 237.8877 | 327.2162 | 125.4688
CA-Gladstone Rockhampton | 6020_Gladstone South - BORE 66 kV | Loading (MVA) | 26.224 | 36.5523 | 14.1211 | 27.4806 | 37.1997 | 14.5768 | 27.2465 | 37.0027 | 14.4447 | 27.6535 | 37.4227 | 14.6769 | 27.9305 | 37.9906 | 14.8369
CA-Gladstone Rockhampton | 6020_Gladstone South - BORE 66 kV | Loading (MW) | 26.0195 | 35.6091 | 14.1141 | 27.2248 | 36.2231 | 14.5741 | 26.95 | 35.9834 | 14.4437 | 27.3928 | 36.4354 | 14.6746 | 27.6216 | 36.9097 | 14.8367
CA-Gladstone Rockhampton | 6020_Gladstone South - BORE 66 kV | Power Factor | 0.9922 | 0.97419 | 0.9995 | 0.99069 | 0.97375 | 0.99981 | 0.98912 | 0.97245 | 0.99993 | 0.99057 | 0.97362 | 0.99984 | 0.98894 | 0.97155 | 0.99999
CA-Gladstone Rockhampton | 6020_Gladstone South - BORE 66 kV | Rating (A) | 211 | 295 | 245 | 211 | 295 | 245 | 211 | 295 | 245 | 211 | 295 | 245 | 211 | 295 | 245
CA-Gladstone Rockhampton | 6020_Gladstone South - BORE 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Gladstone Rockhampton | 6020_Gladstone South - BORE 66 kV | Min Voltage at Constrained Conductor | 67.1924 | 66.9996 | 68.2994 | 67.1337 | 66.9822 | 68.2917 | 67.123 | 66.9796 | 68.2883 | 67.1226 | 66.9656 | 68.2877 | 67.6862 | 66.8786 | 68.2546
CA-Gladstone Rockhampton | 6020_Gladstone South - BORE 66 kV | Contingency Outage | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV
CA-Gladstone Rockhampton | 6022_Gladstone South - Calliope 66 kV | % of Rated A | 35.72% | 45.85% | 19.83% | 37.47% | 46.68% | 20.47% | 37.16% | 46.45% | 20.29% | 37.71% | 46.97% | 20.61% | 37.77% | 47.7% | 20.85%
CA-Gladstone Rockhampton | 6022_Gladstone South - Calliope 66 kV | Limiting Line Name | TR_LINE 72664_1 | TR_LINE 72664_1 | TR_LINE 72653_1 | TR_LINE 72664_1 | TR_LINE 72664_1 | TR_LINE 72653_1 | TR_LINE 72664_1 | TR_LINE 72664_1 | TR_LINE 72653_1 | TR_LINE 72664_1 | TR_LINE 72664_1 | TR_LINE 72653_1 | TR_LINE 72664_1 | TR_LINE 72664_1 | TR_LINE 72653_1
CA-Gladstone Rockhampton | 6022_Gladstone South - Calliope 66 kV | Loading (A) | 222.5532 | 304.4403 | 118.7806 | 233.4268 | 309.9853 | 122.6226 | 231.5306 | 308.4295 | 121.5311 | 234.9074 | 311.8828 | 123.4683 | 235.2837 | 316.757 | 124.8693
CA-Gladstone Rockhampton | 6022_Gladstone South - Calliope 66 kV | Loading (MVA) | 25.8419 | 35.1755 | 14.0704 | 27.069 | 35.7999 | 14.5237 | 26.8387 | 35.6128 | 14.393 | 27.2355 | 36.0085 | 14.623 | 27.5025 | 36.5128 | 14.7812
CA-Gladstone Rockhampton | 6022_Gladstone South - Calliope 66 kV | Loading (MW) | 25.6981 | 34.5701 | 14.0606 | 26.8831 | 35.1693 | 14.519 | 26.6168 | 34.9437 | 14.3908 | 27.0466 | 35.3711 | 14.6189 | 27.274 | 35.8083 | 14.7803
CA-Gladstone Rockhampton | 6022_Gladstone South - Calliope 66 kV | Power Factor | 0.99444 | 0.98279 | 0.99929 | 0.99313 | 0.98238 | 0.99967 | 0.99173 | 0.98121 | 0.99984 | 0.99307 | 0.9823 | 0.99971 | 0.99169 | 0.98071 | 0.99993
CA-Gladstone Rockhampton | 6022_Gladstone South - Calliope 66 kV | Rating (A) | 623 | 664 | 599 | 623 | 664 | 599 | 623 | 664 | 599 | 623 | 664 | 599 | 623 | 664 | 599
CA-Gladstone Rockhampton | 6022_Gladstone South - Calliope 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Gladstone Rockhampton | 6022_Gladstone South - Calliope 66 kV | Min Voltage at Constrained Conductor | 67.0357 | 66.7019 | 68.3317 | 66.9476 | 66.6715 | 68.3181 | 66.9216 | 66.6575 | 68.3104 | 66.9347 | 66.6518 | 68.3134 | 67.483 | 66.5452 | 68.2738
CA-Gladstone Rockhampton | 6022_Gladstone South - Calliope 66 kV | Contingency Outage | 6020_Gladstone South - BORE 66 kV | 6020_Gladstone South - BORE 66 kV | 6020_Gladstone South - BORE 66 kV | 6020_Gladstone South - BORE 66 kV | 6020_Gladstone South - BORE 66 kV | 6020_Gladstone South - BORE 66 kV | 6020_Gladstone South - BORE 66 kV | 6020_Gladstone South - BORE 66 kV | 6020_Gladstone South - BORE 66 kV | 6020_Gladstone South - BORE 66 kV | 6020_Gladstone South - BORE 66 kV | 6020_Gladstone South - BORE 66 kV | 6020_Gladstone South - BORE 66 kV | 6020_Gladstone South - BORE 66 kV | 6020_Gladstone South - BORE 66 kV
CA-Gladstone Rockhampton | 6023_Friend St-Clinton Industrial 66 kV | % of Rated A | 32.93% | 37.96% | 26.55% | 33.7% | 38.38% | 26.93% | 33.62% | 38.29% | 26.86% | 34.07% | 38.68% | 27.11% | 35.84% | 38.9% | 27.14%
CA-Gladstone Rockhampton | 6023_Friend St-Clinton Industrial 66 kV | Limiting Line Name | TR_LINE 22275_1 | TR_LINE 22275_1 | TR_LINE 22275_1 | TR_LINE 22275_1 | TR_LINE 22275_1 | TR_LINE 22275_1 | TR_LINE 22275_1 | TR_LINE 22275_1 | TR_LINE 22275_1 | TR_LINE 22275_1 | TR_LINE 22275_1 | TR_LINE 22275_1 | TR_LINE 22275_1 | TR_LINE 22275_1 | TR_LINE 22275_1
CA-Gladstone Rockhampton | 6023_Friend St-Clinton Industrial 66 kV | Loading (A) | 144.5459 | 182.2002 | 103.263 | 147.9464 | 184.217 | 104.7482 | 147.5816 | 183.7736 | 104.4742 | 149.549 | 185.6458 | 105.4468 | 157.3162 | 186.7151 | 105.5682
CA-Gladstone Rockhampton | 6023_Friend St-Clinton Industrial 66 kV | Loading (MVA) | 17.0657 | 21.5879 | 12.2682 | 17.4734 | 21.8356 | 12.448 | 17.4295 | 21.783 | 12.4153 | 17.6634 | 22.0047 | 12.5313 | 18.6776 | 22.1143 | 12.5407
CA-Gladstone Rockhampton | 6023_Friend St-Clinton Industrial 66 kV | Loading (MW) | 15.826 | 19.2348 | 10.6652 | 16.1725 | 19.3889 | 10.7743 | 16.1719 | 19.3658 | 10.7643 | 16.3945 | 19.5999 | 10.8773 | 15.0931 | 19.9277 | 11.02
CA-Gladstone Rockhampton | 6023_Friend St-Clinton Industrial 66 kV | Power Factor | 0.92733 | 0.89095 | 0.86933 | 0.92553 | 0.8879 | 0.86554 | 0.92783 | 0.88899 | 0.86701 | 0.92814 | 0.89067 | 0.868 | 0.80804 | 0.90108 | 0.87873
CA-Gladstone Rockhampton | 6023_Friend St-Clinton Industrial 66 kV | Rating (A) | 439 | 480 | 389 | 439 | 480 | 389 | 439 | 480 | 389 | 439 | 480 | 389 | 439 | 480 | 389
CA-Gladstone Rockhampton | 6023_Friend St-Clinton Industrial 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Gladstone Rockhampton | 6023_Friend St-Clinton Industrial 66 kV | Min Voltage at Constrained Conductor | 68.1633 | 68.4065 | 68.5925 | 68.1876 | 68.434 | 68.6106 | 68.1842 | 68.4337 | 68.6097 | 68.1904 | 68.4329 | 68.6123 | 68.5467 | 68.3799 | 68.5845
CA-Gladstone Rockhampton | 6023_Friend St-Clinton Industrial 66 kV | Contingency Outage | 6039_Clinton Industrial - Beecher 66 kV | 6022_Gladstone South - Calliope 66 kV | 6039_Clinton Industrial - Beecher 66 kV | 6039_Clinton Industrial - Beecher 66 kV | 6022_Gladstone South - Calliope 66 kV | 6039_Clinton Industrial - Beecher 66 kV | 6039_Clinton Industrial - Beecher 66 kV | 6022_Gladstone South - Calliope 66 kV | 6039_Clinton Industrial - Beecher 66 kV | 6039_Clinton Industrial - Beecher 66 kV | 6022_Gladstone South - Calliope 66 kV | 6039_Clinton Industrial - Beecher 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6039_Clinton Industrial - Beecher 66 kV
CA-Gladstone Rockhampton | 6024_Awoonga - Calliope 66kV | % of Rated A | 75.95% | 76.39% | 29.6% | 82.84% | 75.69% | 31.5% | 82.27% | 75.28% | 31.3% | 83.29% | 76.12% | 31.69% | 83.33% | 77.54% | 32.04%
CA-Gladstone Rockhampton | 6024_Awoonga - Calliope 66kV | Limiting Line Name | TR_LINE 181307_1 | TR_LINE 18905_1 | TR_LINE 181307_1 | TR_LINE 181307_1 | TR_LINE 18905_1 | TR_LINE 181307_1 | TR_LINE 181307_1 | TR_LINE 18905_1 | TR_LINE 181307_1 | TR_LINE 181307_1 | TR_LINE 18905_1 | TR_LINE 181307_1 | TR_LINE 181307_1 | TR_LINE 18905_1 | TR_LINE 181307_1
CA-Gladstone Rockhampton | 6024_Awoonga - Calliope 66kV | Loading (A) | 128.3491 | 183.3249 | 69.261 | 139.9957 | 181.6443 | 73.7019 | 139.0295 | 180.6679 | 73.2367 | 140.7592 | 182.6857 | 74.159 | 140.8246 | 186.0976 | 74.9667
CA-Gladstone Rockhampton | 6024_Awoonga - Calliope 66kV | Loading (MVA) | 14.8694 | 19.9952 | 8.1595 | 16.198 | 19.7915 | 8.6792 | 16.0763 | 19.6864 | 8.6202 | 16.2835 | 19.892 | 8.7324 | 16.4207 | 20.2034 | 8.8187
CA-Gladstone Rockhampton | 6024_Awoonga - Calliope 66kV | Loading (MW) | 14.6216 | 19.5501 | 8.1024 | 15.8869 | 19.3583 | 8.6062 | 15.7029 | 19.2542 | 8.5297 | 15.9711 | 19.4551 | 8.6587 | 16.0391 | 19.7455 | 8.7242
CA-Gladstone Rockhampton | 6024_Awoonga - Calliope 66kV | Power Factor | 0.98333 | 0.97774 | 0.99134 | 0.98079 | 0.97811 | 0.99003 | 0.97677 | 0.97805 | 0.98773 | 0.98082 | 0.97803 | 0.99003 | 0.97676 | 0.97734 | 0.9876
CA-Gladstone Rockhampton | 6024_Awoonga - Calliope 66kV | Rating (A) | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234
CA-Gladstone Rockhampton | 6024_Awoonga - Calliope 66kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Gladstone Rockhampton | 6024_Awoonga - Calliope 66kV | Min Voltage at Constrained Conductor | 65.9973 | 62.9651 | 67.6828 | 65.8006 | 62.9005 | 67.619 | 65.7601 | 62.9046 | 67.6027 | 65.7817 | 62.8595 | 67.6091 | 66.3065 | 62.6726 | 67.5452
CA-Gladstone Rockhampton | 6024_Awoonga - Calliope 66kV | Contingency Outage | 6020_Gladstone South - BORE 66 kV | 6022_Gladstone South - Calliope 66 kV | 6020_Gladstone South - BORE 66 kV | 6020_Gladstone South - BORE 66 kV | 6022_Gladstone South - Calliope 66 kV | 6020_Gladstone South - BORE 66 kV | 6020_Gladstone South - BORE 66 kV | 6022_Gladstone South - Calliope 66 kV | 6020_Gladstone South - BORE 66 kV | 6020_Gladstone South - BORE 66 kV | 6022_Gladstone South - Calliope 66 kV | 6020_Gladstone South - BORE 66 kV | 6020_Gladstone South - BORE 66 kV | 6022_Gladstone South - Calliope 66 kV | 6020_Gladstone South - BORE 66 kV
CA-Gladstone Rockhampton | 6029_Littlemore - Miriam Vale 66 kV | % of Rated A | 10.9% | 11.16% | 5.533% | 10.93% | 11.17% | 5.537% | 10.39% | 10.6% | 5.276% | 10.94% | 11.18% | 5.538% | 10.85% | 11.21% | 5.543%
CA-Gladstone Rockhampton | 6029_Littlemore - Miriam Vale 66 kV | Limiting Line Name | TR_LINE 16162_1 | TR_LINE 16031_1 | TR_LINE 16162_1 | TR_LINE 16162_1 | TR_LINE 16031_1 | TR_LINE 16162_1 | TR_LINE 16162_1 | TR_LINE 16031_1 | TR_LINE 16162_1 | TR_LINE 16162_1 | TR_LINE 16031_1 | TR_LINE 16162_1 | TR_LINE 16162_1 | TR_LINE 16031_1 | TR_LINE 16162_1
CA-Gladstone Rockhampton | 6029_Littlemore - Miriam Vale 66 kV | Loading (A) | 14.3892 | 18.6346 | 8.7974 | 14.4292 | 18.6548 | 8.804 | 13.7131 | 17.6995 | 8.3893 | 14.4357 | 18.6658 | 8.8057 | 14.3176 | 18.7246 | 8.8136
CA-Gladstone Rockhampton | 6029_Littlemore - Miriam Vale 66 kV | Loading (MVA) | 1.6147 | 2.0056 | 1.0293 | 1.6146 | 2.0057 | 1.0291 | 1.5349 | 1.9051 | 0.98091 | 1.6146 | 2.0055 | 1.0291 | 1.6149 | 2.0055 | 1.029
CA-Gladstone Rockhampton | 6029_Littlemore - Miriam Vale 66 kV | Loading (MW) | 1.6074 | 2.0012 | 1.0044 | 1.6074 | 2.0012 | 1.0045 | 1.5266 | 1.901 | 0.95408 | 1.6075 | 2.0011 | 1.0045 | 1.6074 | 2.0011 | 1.0045
CA-Gladstone Rockhampton | 6029_Littlemore - Miriam Vale 66 kV | Power Factor | 0.99553 | 0.99775 | 0.9759 | 0.99558 | 0.99775 | 0.97601 | 0.99463 | 0.99783 | 0.97265 | 0.9956 | 0.99779 | 0.97603 | 0.99535 | 0.99778 | 0.97616
CA-Gladstone Rockhampton | 6029_Littlemore - Miriam Vale 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
CA-Gladstone Rockhampton | 6029_Littlemore - Miriam Vale 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Gladstone Rockhampton | 6029_Littlemore - Miriam Vale 66 kV | Min Voltage at Constrained Conductor | 64.7859 | 62.1403 | 67.5469 | 64.6024 | 62.0735 | 67.4889 | 64.621 | 62.1423 | 67.5051 | 64.5728 | 62.0318 | 67.4742 | 65.1179 | 61.8383 | 67.4055
CA-Gladstone Rockhampton | 6029_Littlemore - Miriam Vale 66 kV | Contingency Outage | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV
CA-Gladstone Rockhampton | 6030_Littlemore - Monto 66 kV | % of Rated A | 5.218% | 4.119% | 4.389% | 5.216% | 4.119% | 4.388% | 5.214% | 4.118% | 4.388% | 5.215% | 4.118% | 4.388% | 5.21% | 4.114% | 4.386%
CA-Gladstone Rockhampton | 6030_Littlemore - Monto 66 kV | Limiting Line Name | TR_LINE 19505_1 | TR_LINE 19505_1 | TR_LINE 19505_1 | TR_LINE 19505_1 | TR_LINE 19505_1 | TR_LINE 19505_1 | TR_LINE 19505_1 | TR_LINE 19505_1 | TR_LINE 19505_1 | TR_LINE 19505_1 | TR_LINE 19505_1 | TR_LINE 19505_1 | TR_LINE 19505_1 | TR_LINE 19505_1 | TR_LINE 19505_1
CA-Gladstone Rockhampton | 6030_Littlemore - Monto 66 kV | Loading (A) | 6.8883 | 6.8786 | 6.9781 | 6.8847 | 6.8786 | 6.9775 | 6.8828 | 6.8773 | 6.9767 | 6.8839 | 6.8774 | 6.9771 | 6.8769 | 6.8697 | 6.9735
CA-Gladstone Rockhampton | 6030_Littlemore - Monto 66 kV | Loading (MVA) | 0.81114 | 0.80887 | 0.83243 | 0.8103 | 0.80886 | 0.83227 | 0.80985 | 0.80856 | 0.83209 | 0.81011 | 0.80858 | 0.83218 | 0.80845 | 0.80677 | 0.83134
CA-Gladstone Rockhampton | 6030_Littlemore - Monto 66 kV | Loading (MW) | 0.0014833 | 0.0014791 | 0.0015222 | 0.0014818 | 0.0014791 | 0.0015219 | 0.0014809 | 0.0014786 | 0.0015216 | 0.0014814 | 0.0014786 | 0.0015218 | 0.0014784 | 0.0014753 | 0.0015202
CA-Gladstone Rockhampton | 6030_Littlemore - Monto 66 kV | Power Factor | 0.001768 | 0.001768 | 0.001768 | 0.001768 | 0.001768 | 0.001768 | 0.001768 | 0.001768 | 0.001768 | 0.001768 | 0.001768 | 0.001768 | 0.001768 | 0.001768 | 0.001768
CA-Gladstone Rockhampton | 6030_Littlemore - Monto 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
CA-Gladstone Rockhampton | 6030_Littlemore - Monto 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Gladstone Rockhampton | 6030_Littlemore - Monto 66 kV | Min Voltage at Constrained Conductor | 67.9866 | 67.8914 | 68.8731 | 67.9515 | 67.8909 | 68.8666 | 67.9325 | 67.8783 | 68.8591 | 67.9435 | 67.8791 | 68.8627 | 67.8739 | 67.8031 | 68.8279
CA-Gladstone Rockhampton | 6030_Littlemore - Monto 66 kV | Contingency Outage | 6029_Littlemore - Miriam Vale 66 kV | 6029_Littlemore - Miriam Vale 66 kV | 6029_Littlemore - Miriam Vale 66 kV | 6029_Littlemore - Miriam Vale 66 kV | 6029_Littlemore - Miriam Vale 66 kV | 6029_Littlemore - Miriam Vale 66 kV | 6029_Littlemore - Miriam Vale 66 kV | 6029_Littlemore - Miriam Vale 66 kV | 6029_Littlemore - Miriam Vale 66 kV | 6029_Littlemore - Miriam Vale 66 kV | 6029_Littlemore - Miriam Vale 66 kV | 6029_Littlemore - Miriam Vale 66 kV | 6029_Littlemore - Miriam Vale 66 kV | 6029_Littlemore - Miriam Vale 66 kV | 6029_Littlemore - Miriam Vale 66 kV
CA-Gladstone Rockhampton | 6031_Calliope - Littlemore 66 kV | % of Rated A | 16.3% | 14.77% | 11.6% | 16.3% | 14.77% | 11.6% | 15.92% | 14.31% | 11.48% | 16.3% | 14.78% | 11.6% | 16.29% | 14.8% | 11.6%
CA-Gladstone Rockhampton | 6031_Calliope - Littlemore 66 kV | Limiting Line Name | TR_LINE 13872_1 | TR_LINE 13872_1 | TR_LINE 13872_1 | TR_LINE 13872_1 | TR_LINE 13872_1 | TR_LINE 13872_1 | TR_LINE 13872_1 | TR_LINE 13872_1 | TR_LINE 13872_1 | TR_LINE 13872_1 | TR_LINE 13872_1 | TR_LINE 13872_1 | TR_LINE 13872_1 | TR_LINE 13872_1 | TR_LINE 13872_1
CA-Gladstone Rockhampton | 6031_Calliope - Littlemore 66 kV | Loading (A) | 21.5134 | 24.6628 | 18.4476 | 21.5215 | 24.6726 | 18.4477 | 21.0172 | 23.9009 | 18.2549 | 21.5222 | 24.6836 | 18.447 | 21.5063 | 24.7125 | 18.441
CA-Gladstone Rockhampton | 6031_Calliope - Littlemore 66 kV | Loading (MVA) | 2.4224 | 2.6897 | 2.1937 | 2.4167 | 2.688 | 2.1938 | 2.47 | 2.6041 | 2.1706 | 2.4157 | 2.6874 | 2.1936 | 2.4337 | 2.6826 | 2.1916
CA-Gladstone Rockhampton | 6031_Calliope - Littlemore 66 kV | Loading (MW) | 1.9389 | 2.3752 | 1.1863 | 1.939 | 2.3752 | 1.1863 | 1.8554 | 2.2712 | 1.1354 | 1.939 | 2.3752 | 1.1863 | 1.9388 | 2.3755 | 1.1863
CA-Gladstone Rockhampton | 6031_Calliope - Littlemore 66 kV | Power Factor | 0.80041 | 0.88306 | 0.54077 | 0.80235 | 0.88365 | 0.54076 | 0.75118 | 0.87216 | 0.52309 | 0.80269 | 0.88382 | 0.54082 | 0.79663 | 0.88551 | 0.54129
CA-Gladstone Rockhampton | 6031_Calliope - Littlemore 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
CA-Gladstone Rockhampton | 6031_Calliope - Littlemore 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Gladstone Rockhampton | 6031_Calliope - Littlemore 66 kV | Min Voltage at Constrained Conductor | 65.0064 | 62.9568 | 68.6574 | 64.8268 | 62.8922 | 68.6585 | 67.8494 | 62.8971 | 68.6512 | 64.7979 | 62.8512 | 68.6537 | 65.3309 | 62.6642 | 68.6161
CA-Gladstone Rockhampton | 6031_Calliope - Littlemore 66 kV | Contingency Outage | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6023_Friend St-Clinton Industrial 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6023_Friend St-Clinton Industrial 66 kV | 6024_Awoonga - Calliope 66kV | 6022_Gladstone South - Calliope 66 kV | 6023_Friend St-Clinton Industrial 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6023_Friend St-Clinton Industrial 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6023_Friend St-Clinton Industrial 66 kV
CA-Gladstone Rockhampton | 6032_Boyne Residential Tee-Awoonga 66 kV | % of Rated A | 69.68% | 73.72% | 29.11% | 75.18% | 75.92% | 30.81% | 74.26% | 75.37% | 30.33% | 75.55% | 76.28% | 30.97% | 75.39% | 77.44% | 31.14%
CA-Gladstone Rockhampton | 6032_Boyne Residential Tee-Awoonga 66 kV | Limiting Line Name | TR_LINE 22220_1 | TR_LINE 22220_1 | TR_LINE 69280_1 | TR_LINE 22220_1 | TR_LINE 22220_1 | TR_LINE 69280_1 | TR_LINE 22220_1 | TR_LINE 22220_1 | TR_LINE 69280_1 | TR_LINE 22220_1 | TR_LINE 22220_1 | TR_LINE 69280_1 | TR_LINE 22220_1 | TR_LINE 22220_1 | TR_LINE 69280_1
CA-Gladstone Rockhampton | 6032_Boyne Residential Tee-Awoonga 66 kV | Loading (A) | 147.034 | 217.4676 | 71.3074 | 158.6226 | 223.9551 | 75.4747 | 156.6811 | 222.3559 | 74.3052 | 159.411 | 225.0183 | 75.8782 | 159.0722 | 228.4586 | 76.2988
CA-Gladstone Rockhampton | 6032_Boyne Residential Tee-Awoonga 66 kV | Loading (MVA) | 16.7229 | 24.2996 | 8.3824 | 17.9906 | 24.993 | 8.8684 | 17.7648 | 24.813 | 8.7304 | 18.0739 | 25.0993 | 8.9147 | 18.1834 | 25.4227 | 8.9579
CA-Gladstone Rockhampton | 6032_Boyne Residential Tee-Awoonga 66 kV | Loading (MW) | 16.6269 | 23.6275 | 8.326 | 17.857 | 24.2992 | 8.831 | 17.5921 | 24.0711 | 8.7025 | 17.9379 | 24.4002 | 8.8786 | 18.0047 | 24.6419 | 8.9353
CA-Gladstone Rockhampton | 6032_Boyne Residential Tee-Awoonga 66 kV | Power Factor | 0.99426 | 0.97234 | 0.99327 | 0.99257 | 0.97224 | 0.99579 | 0.99028 | 0.9701 | 0.9968 | 0.99248 | 0.97214 | 0.99595 | 0.99017 | 0.96929 | 0.99748
CA-Gladstone Rockhampton | 6032_Boyne Residential Tee-Awoonga 66 kV | Rating (A) | 211 | 295 | 245 | 211 | 295 | 245 | 211 | 295 | 245 | 211 | 295 | 245 | 211 | 295 | 245
CA-Gladstone Rockhampton | 6032_Boyne Residential Tee-Awoonga 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Gladstone Rockhampton | 6032_Boyne Residential Tee-Awoonga 66 kV | Min Voltage at Constrained Conductor | 65.6609 | 64.5059 | 67.8561 | 65.4774 | 64.4245 | 67.8246 | 65.457 | 64.4207 | 67.8199 | 65.4553 | 64.3929 | 67.8163 | 65.992 | 64.2401 | 67.7685
CA-Gladstone Rockhampton | 6032_Boyne Residential Tee-Awoonga 66 kV | Contingency Outage | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV
CA-Gladstone Rockhampton | 6034_Boyne Residential Tee - BORE 66 kV | % of Rated A | 48.16% | 44.46% | 26.67% | 47.86% | 44.11% | 26.45% | 47.89% | 44.13% | 26.45% | 48.32% | 44.55% | 26.7% | 48.8% | 45.47% | 27.21%
CA-Gladstone Rockhampton | 6034_Boyne Residential Tee - BORE 66 kV | Limiting Line Name | TR_LINE 22222_1 | TR_LINE 22222_1 | TR_LINE 22222_1 | TR_LINE 22222_1 | TR_LINE 22222_1 | TR_LINE 22222_1 | TR_LINE 22222_1 | TR_LINE 22222_1 | TR_LINE 22222_1 | TR_LINE 22222_1 | TR_LINE 22222_1 | TR_LINE 22222_1 | TR_LINE 22222_1 | TR_LINE 22222_1 | TR_LINE 22222_1
CA-Gladstone Rockhampton | 6034_Boyne Residential Tee - BORE 66 kV | Loading (A) | 79.4567 | 99.1369 | 49.0653 | 78.9714 | 98.374 | 48.6652 | 79.022 | 98.4117 | 48.6771 | 79.7274 | 99.3359 | 49.12 | 80.5247 | 101.4004 | 50.0637
CA-Gladstone Rockhampton | 6034_Boyne Residential Tee - BORE 66 kV | Loading (MVA) | 8.9871 | 11.1203 | 5.7165 | 8.9059 | 11.0195 | 5.6649 | 8.906 | 11.0195 | 5.6649 | 8.9875 | 11.1208 | 5.7166 | 9.1496 | 11.3239 | 5.8202
CA-Gladstone Rockhampton | 6034_Boyne Residential Tee - BORE 66 kV | Loading (MW) | 8.914 | 11.0171 | 5.6799 | 8.8336 | 10.9176 | 5.6286 | 8.8336 | 10.9177 | 5.6286 | 8.9141 | 11.0173 | 5.6799 | 9.0748 | 11.2168 | 5.7824
CA-Gladstone Rockhampton | 6034_Boyne Residential Tee - BORE 66 kV | Power Factor | 0.99186 | 0.99072 | 0.99356 | 0.99187 | 0.99076 | 0.99358 | 0.99187 | 0.99075 | 0.99358 | 0.99182 | 0.99069 | 0.99355 | 0.99181 | 0.99054 | 0.9935
CA-Gladstone Rockhampton | 6034_Boyne Residential Tee - BORE 66 kV | Rating (A) | 165 | 223 | 184 | 165 | 223 | 184 | 165 | 223 | 184 | 165 | 223 | 184 | 165 | 223 | 184
CA-Gladstone Rockhampton | 6034_Boyne Residential Tee - BORE 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Gladstone Rockhampton | 6034_Boyne Residential Tee - BORE 66 kV | Min Voltage at Constrained Conductor | 65.2944 | 64.7521 | 67.2632 | 65.1022 | 64.6624 | 67.2031 | 65.0612 | 64.638 | 67.1867 | 65.0761 | 64.625 | 67.189 | 65.5938 | 64.465 | 67.1164
CA-Gladstone Rockhampton | 6034_Boyne Residential Tee - BORE 66 kV | Contingency Outage | 6020_Gladstone South - BORE 66 kV | 6020_Gladstone South - BORE 66 kV | 6020_Gladstone South - BORE 66 kV | 6020_Gladstone South - BORE 66 kV | 6020_Gladstone South - BORE 66 kV | 6020_Gladstone South - BORE 66 kV | 6020_Gladstone South - BORE 66 kV | 6020_Gladstone South - BORE 66 kV | 6020_Gladstone South - BORE 66 kV | 6020_Gladstone South - BORE 66 kV | 6020_Gladstone South - BORE 66 kV | 6020_Gladstone South - BORE 66 kV | 6020_Gladstone South - BORE 66 kV | 6020_Gladstone South - BORE 66 kV | 6020_Gladstone South - BORE 66 kV
CA-Gladstone Rockhampton | 6039_Clinton Industrial - Beecher 66 kV | % of Rated A | 3.904% | 1.554% | 2.001% | 3.903% | 1.554% | 2.002% | 3.902% | 1.554% | 2.002% | 3.902% | 1.555% | 2.002% | 3.903% | 1.554% | 2.001%
CA-Gladstone Rockhampton | 6039_Clinton Industrial - Beecher 66 kV | Limiting Line Name | TR_LINE 33766_1 | TR_LINE 16739_1 | TR_LINE 16739_1 | TR_LINE 33766_1 | TR_LINE 16739_1 | TR_LINE 16739_1 | TR_LINE 33766_1 | TR_LINE 16739_1 | TR_LINE 16739_1 | TR_LINE 33766_1 | TR_LINE 16739_1 | TR_LINE 16739_1 | TR_LINE 33766_1 | TR_LINE 16739_1 | TR_LINE 16739_1
CA-Gladstone Rockhampton | 6039_Clinton Industrial - Beecher 66 kV | Loading (A) | 9.5648 | 4.2882 | 4.6424 | 9.562 | 4.2901 | 4.6437 | 9.5607 | 4.2902 | 4.6438 | 9.5596 | 4.2905 | 4.6441 | 9.5615 | 4.2881 | 4.6425
CA-Gladstone Rockhampton | 6039_Clinton Industrial - Beecher 66 kV | Loading (MVA) | 1.1253 | 0.50963 | 0.55205 | 1.1252 | 0.51002 | 0.55233 | 1.1252 | 0.51004 | 0.55234 | 1.1252 | 0.51011 | 0.55241 | 1.1252 | 0.5096 | 0.55207
CA-Gladstone Rockhampton | 6039_Clinton Industrial - Beecher 66 kV | Loading (MW) | 1.0467 | 0.21745 | 0.1361 | 1.0467 | 0.21745 | 0.1361 | 1.0467 | 0.21745 | 0.1361 | 1.0467 | 0.21745 | 0.1361 | 1.0467 | 0.21745 | 0.1361
CA-Gladstone Rockhampton | 6039_Clinton Industrial - Beecher 66 kV | Power Factor | 0.9301 | 0.42669 | 0.24653 | 0.93018 | 0.42636 | 0.24641 | 0.93021 | 0.42635 | 0.2464 | 0.93025 | 0.42629 | 0.24637 | 0.93019 | 0.42671 | 0.24652
CA-Gladstone Rockhampton | 6039_Clinton Industrial - Beecher 66 kV | Rating (A) | 245 | 276 | 232 | 245 | 276 | 232 | 245 | 276 | 232 | 245 | 276 | 232 | 245 | 276 | 232
CA-Gladstone Rockhampton | 6039_Clinton Industrial - Beecher 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Gladstone Rockhampton | 6039_Clinton Industrial - Beecher 66 kV | Min Voltage at Constrained Conductor | 67.9278 | 68.6146 | 68.6554 | 67.9415 | 68.6371 | 68.6706 | 67.9477 | 68.638 | 68.6712 | 67.9533 | 68.6422 | 68.6748 | 67.9437 | 68.613 | 68.6568
CA-Gladstone Rockhampton | 6039_Clinton Industrial - Beecher 66 kV | Contingency Outage | 6023_Friend St-Clinton Industrial 66 kV | 6066_Bocoolima Tee -Wooderson 66 kV | 6110_Port Curtis 66 kV | 6023_Friend St-Clinton Industrial 66 kV | 6066_Bocoolima Tee -Wooderson 66 kV | 6110_Port Curtis 66 kV | 6023_Friend St-Clinton Industrial 66 kV | 6066_Bocoolima Tee -Wooderson 66 kV | 6110_Port Curtis 66 kV | 6023_Friend St-Clinton Industrial 66 kV | 6066_Bocoolima Tee -Wooderson 66 kV | 6110_Port Curtis 66 kV | 6023_Friend St-Clinton Industrial 66 kV | 6066_Bocoolima Tee -Wooderson 66 kV | 6110_Port Curtis 66 kV
CA-Gladstone Rockhampton | 6041_Yarwun - Boat Creek 66 kV | % of Rated A | 9.073% | 2.074% | 2.352% | 9.071% | 2.074% | 2.353% | 9.07% | 2.074% | 2.353% | 9.069% | 2.075% | 2.353% | 9.07% | 2.074% | 2.352%
CA-Gladstone Rockhampton | 6041_Yarwun - Boat Creek 66 kV | Limiting Line Name | TR_LINE 21443_1 | TR_LINE 15181_1 | TR_LINE 15181_1 | TR_LINE 21443_1 | TR_LINE 15181_1 | TR_LINE 15181_1 | TR_LINE 21443_1 | TR_LINE 15181_1 | TR_LINE 15181_1 | TR_LINE 21443_1 | TR_LINE 15181_1 | TR_LINE 15181_1 | TR_LINE 21443_1 | TR_LINE 15181_1 | TR_LINE 15181_1
CA-Gladstone Rockhampton | 6041_Yarwun - Boat Creek 66 kV | Loading (A) | 12.1572 | 3.4629 | 3.7397 | 12.1545 | 3.4643 | 3.7408 | 12.1534 | 3.4643 | 3.7409 | 12.1523 | 3.4646 | 3.7411 | 12.1541 | 3.4628 | 3.7398
CA-Gladstone Rockhampton | 6041_Yarwun - Boat Creek 66 kV | Loading (MVA) | 1.4206 | 0.4116 | 0.4448 | 1.4206 | 0.4119 | 0.44503 | 1.4206 | 0.41191 | 0.44504 | 1.4206 | 0.41197 | 0.44509 | 1.4206 | 0.41158 | 0.44482
CA-Gladstone Rockhampton | 6041_Yarwun - Boat Creek 66 kV | Loading (MW) | 1.0417 | 0.21737 | 0.136 | 1.0417 | 0.21737 | 0.136 | 1.0417 | 0.21737 | 0.136 | 1.0417 | 0.21737 | 0.136 | 1.0417 | 0.21737 | 0.136
CA-Gladstone Rockhampton | 6041_Yarwun - Boat Creek 66 kV | Power Factor | 0.73225 | 0.52811 | 0.30576 | 0.73226 | 0.52772 | 0.3056 | 0.73226 | 0.5277 | 0.30559 | 0.73227 | 0.52763 | 0.30556 | 0.73226 | 0.52814 | 0.30574
CA-Gladstone Rockhampton | 6041_Yarwun - Boat Creek 66 kV | Rating (A) | 134 | 167 | 159 | 134 | 167 | 159 | 134 | 167 | 159 | 134 | 167 | 159 | 134 | 167 | 159
CA-Gladstone Rockhampton | 6041_Yarwun - Boat Creek 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Gladstone Rockhampton | 6041_Yarwun - Boat Creek 66 kV | Min Voltage at Constrained Conductor | 67.4659 | 68.6241 | 68.6701 | 67.4797 | 68.6467 | 68.6853 | 67.4859 | 68.6476 | 68.6859 | 67.4916 | 68.6518 | 68.6895 | 67.4819 | 68.6226 | 68.6715
CA-Gladstone Rockhampton | 6041_Yarwun - Boat Creek 66 kV | Contingency Outage | 6023_Friend St-Clinton Industrial 66 kV | 6066_Bocoolima Tee -Wooderson 66 kV | 6110_Port Curtis 66 kV | 6023_Friend St-Clinton Industrial 66 kV | 6066_Bocoolima Tee -Wooderson 66 kV | 6110_Port Curtis 66 kV | 6023_Friend St-Clinton Industrial 66 kV | 6066_Bocoolima Tee -Wooderson 66 kV | 6110_Port Curtis 66 kV | 6023_Friend St-Clinton Industrial 66 kV | 6066_Bocoolima Tee -Wooderson 66 kV | 6110_Port Curtis 66 kV | 6023_Friend St-Clinton Industrial 66 kV | 6066_Bocoolima Tee -Wooderson 66 kV | 6110_Port Curtis 66 kV
CA-Gladstone Rockhampton | 6044_Raglan-East End Quarry/Yarwun 66 kV | % of Rated A | 1.484% | 1.173% | 1.243% | 1.484% | 1.174% | 1.243% | 1.483% | 1.173% | 1.242% | 1.491% | 1.172% | 1.242% | 1.491% | 1.172% | 1.242%
CA-Gladstone Rockhampton | 6044_Raglan-East End Quarry/Yarwun 66 kV | Limiting Line Name | TR_LINE 22122_1 | TR_LINE 22122_1 | TR_LINE 22122_1 | TR_LINE 22122_1 | TR_LINE 22122_1 | TR_LINE 22122_1 | TR_LINE 22122_1 | TR_LINE 22122_1 | TR_LINE 22122_1 | TR_LINE 22122_1 | TR_LINE 22122_1 | TR_LINE 22122_1 | TR_LINE 22122_1 | TR_LINE 22122_1 | TR_LINE 22122_1
CA-Gladstone Rockhampton | 6044_Raglan-East End Quarry/Yarwun 66 kV | Loading (A) | 1.9584 | 1.9588 | 1.976 | 1.9592 | 1.9598 | 1.9763 | 1.9577 | 1.9581 | 1.9749 | 1.9677 | 1.9577 | 1.9747 | 1.968 | 1.9567 | 1.9743
CA-Gladstone Rockhampton | 6044_Raglan-East End Quarry/Yarwun 66 kV | Loading (MVA) | 0.23112 | 0.23121 | 0.23531 | 0.23132 | 0.23145 | 0.23537 | 0.23097 | 0.23107 | 0.23504 | 0.23334 | 0.23097 | 0.235 | 0.23339 | 0.23072 | 0.23491
CA-Gladstone Rockhampton | 6044_Raglan-East End Quarry/Yarwun 66 kV | Loading (MW) | 3.4404e-05 | 3.4417e-05 | 3.5027e-05 | 3.4433e-05 | 3.4453e-05 | 3.5037e-05 | 3.4381e-05 | 3.4396e-05 | 3.4987e-05 | 3.4733e-05 | 3.4381e-05 | 3.4981e-05 | 3.4742e-05 | 3.4345e-05 | 3.4967e-05
CA-Gladstone Rockhampton | 6044_Raglan-East End Quarry/Yarwun 66 kV | Power Factor | 0.00014836 | 0.00014836 | 0.00014836 | 0.00014836 | 0.00014836 | 0.00014836 | 0.00014836 | 0.00014836 | 0.00014836 | 0.00014836 | 0.00014836 | 0.00014836 | 0.00014836 | 0.00014836 | 0.00014836
CA-Gladstone Rockhampton | 6044_Raglan-East End Quarry/Yarwun 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
CA-Gladstone Rockhampton | 6044_Raglan-East End Quarry/Yarwun 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Gladstone Rockhampton | 6044_Raglan-East End Quarry/Yarwun 66 kV | Min Voltage at Constrained Conductor | 68.1378 | 68.151 | 68.7516 | 68.1665 | 68.1865 | 68.7614 | 68.1152 | 68.1294 | 68.7123 | 68.463 | 68.1154 | 68.707 | 68.4715 | 68.0789 | 68.6935
CA-Gladstone Rockhampton | 6044_Raglan-East End Quarry/Yarwun 66 kV | Contingency Outage | 6094_Malchi Tee - Malchi 66 kV | 6094_Malchi Tee - Malchi 66 kV | 6094_Malchi Tee - Malchi 66 kV | 6094_Malchi Tee - Malchi 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6094_Malchi Tee - Malchi 66 kV | 6091_Egan's Hill - Gavial 66 kV | 6091_Egan's Hill - Gavial 66 kV | 6094_Malchi Tee - Malchi 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6091_Egan's Hill - Gavial 66 kV | 6091_Egan's Hill - Gavial 66 kV | 6091_Egan's Hill - Gavial 66 kV | 6091_Egan's Hill - Gavial 66 kV | 6091_Egan's Hill - Gavial 66 kV
CA-Gladstone Rockhampton | 6045_Coominglah Tee - Monto 66 kV | % of Rated A | 28.43% | 26.29% | 14.41% | 28.43% | 26.29% | 14.4% | 27.89% | 25.77% | 14.21% | 28.43% | 26.29% | 14.4% | 28.43% | 26.29% | 14.4%
CA-Gladstone Rockhampton | 6045_Coominglah Tee - Monto 66 kV | Limiting Line Name | TR_LINE 75765_1 | TR_LINE 75765_1 | TR_LINE 75765_1 | TR_LINE 75765_1 | TR_LINE 75765_1 | TR_LINE 75765_1 | TR_LINE 75765_1 | TR_LINE 75765_1 | TR_LINE 75765_1 | TR_LINE 75765_1 | TR_LINE 75765_1 | TR_LINE 75765_1 | TR_LINE 75765_1 | TR_LINE 75765_1 | TR_LINE 75765_1
CA-Gladstone Rockhampton | 6045_Coominglah Tee - Monto 66 kV | Loading (A) | 37.5304 | 43.9112 | 22.9042 | 37.5268 | 43.9071 | 22.9039 | 36.8163 | 43.0285 | 22.5868 | 37.5271 | 43.9063 | 22.9037 | 37.5294 | 43.9091 | 22.9039
CA-Gladstone Rockhampton | 6045_Coominglah Tee - Monto 66 kV | Loading (MVA) | 4.3486 | 5.1302 | 2.7116 | 4.3487 | 5.1302 | 2.7116 | 4.2688 | 5.0311 | 2.6749 | 4.3487 | 5.1302 | 2.7117 | 4.3487 | 5.1302 | 2.7116
CA-Gladstone Rockhampton | 6045_Coominglah Tee - Monto 66 kV | Loading (MW) | 4.1925 | 5.0289 | 2.3106 | 4.1925 | 5.0289 | 2.3106 | 4.105 | 4.9233 | 2.263 | 4.1925 | 5.0289 | 2.3106 | 4.1925 | 5.0289 | 2.3106
CA-Gladstone Rockhampton | 6045_Coominglah Tee - Monto 66 kV | Power Factor | 0.9641 | 0.98027 | 0.85212 | 0.96408 | 0.98025 | 0.8521 | 0.96161 | 0.97857 | 0.84603 | 0.96408 | 0.98025 | 0.85208 | 0.96409 | 0.98026 | 0.85209
CA-Gladstone Rockhampton | 6045_Coominglah Tee - Monto 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
CA-Gladstone Rockhampton | 6045_Coominglah Tee - Monto 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Gladstone Rockhampton | 6045_Coominglah Tee - Monto 66 kV | Min Voltage at Constrained Conductor | 66.8953 | 67.4489 | 68.3501 | 66.9031 | 67.456 | 68.3528 | 66.9413 | 67.5036 | 68.3728 | 66.9026 | 67.4573 | 68.3545 | 66.8975 | 67.4526 | 68.353
CA-Gladstone Rockhampton | 6045_Coominglah Tee - Monto 66 kV | Contingency Outage | 6027_TDM Mine 66 kV | 6027_TDM Mine 66 kV | 6010_Biloela - Callide Mine 66 kV | 6027_TDM Mine 66 kV | 6027_TDM Mine 66 kV | 6010_Biloela - Callide Mine 66 kV | 6027_TDM Mine 66 kV | 6027_TDM Mine 66 kV | 6010_Biloela - Callide Mine 66 kV | 6027_TDM Mine 66 kV | 6027_TDM Mine 66 kV | 6010_Biloela - Callide Mine 66 kV | 6027_TDM Mine 66 kV | 6027_TDM Mine 66 kV | 6010_Biloela - Callide Mine 66 kV
CA-Gladstone Rockhampton | 6046_Mt Morgan - Wowan 66 kV | % of Rated A | 3.559% | 2.869% | 3.078% | 3.561% | 2.855% | 3.079% | 42.92% | 9.836% | 7.065% | 85.63% | 19.24% | 13.82% | 85.56% | 19.25% | 13.83%
CA-Gladstone Rockhampton | 6046_Mt Morgan - Wowan 66 kV | Limiting Line Name | TR_LINE 15219_3 | TR_LINE 22233_1 | TR_LINE 22233_1 | TR_LINE 15219_3 | TR_LINE 22233_1 | TR_LINE 22233_1 | TR_LINE 76097_1 | TR_LINE 76097_1 | TR_LINE 76097_1 | TR_LINE 76097_1 | TR_LINE 76097_1 | TR_LINE 76097_1 | TR_LINE 76097_1 | TR_LINE 76097_1 | TR_LINE 76097_1
CA-Gladstone Rockhampton | 6046_Mt Morgan - Wowan 66 kV | Loading (A) | 4.6983 | 4.7908 | 4.8945 | 4.7002 | 4.7685 | 4.8952 | 56.6528 | 16.4254 | 11.2334 | 113.037 | 32.1246 | 21.9776 | 112.9429 | 32.1552 | 21.9858
CA-Gladstone Rockhampton | 6046_Mt Morgan - Wowan 66 kV | Loading (MVA) | 0.56336 | 0.57549 | 0.58798 | 0.56382 | 0.57047 | 0.58815 | 6.5086 | 1.9265 | 1.3359 | 12.6501 | 3.7459 | 2.5991 | 12.65 | 3.7459 | 2.5992
CA-Gladstone Rockhampton | 6046_Mt Morgan - Wowan 66 kV | Loading (MW) | 0.00044874 | 0.070775 | 0.049292 | 0.00044911 | 0.070772 | 0.049292 | 5.374 | 1.5941 | 1.107 | 10.439 | 3.095 | 2.1491 | 10.439 | 3.095 | 2.1491
CA-Gladstone Rockhampton | 6046_Mt Morgan - Wowan 66 kV | Power Factor | 0.00078431 | 0.12298 | 0.083833 | 0.00078431 | 0.12406 | 0.083808 | 0.82564 | 0.82747 | 0.82867 | 0.8252 | 0.82623 | 0.82685 | 0.8252 | 0.82622 | 0.82685
CA-Gladstone Rockhampton | 6046_Mt Morgan - Wowan 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
CA-Gladstone Rockhampton | 6046_Mt Morgan - Wowan 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Gladstone Rockhampton | 6046_Mt Morgan - Wowan 66 kV | Min Voltage at Constrained Conductor | 69.2292 | 69.354 | 69.358 | 69.2574 | 69.0701 | 69.3678 | 66.3297 | 67.7148 | 68.6579 | 64.6079 | 67.3213 | 68.2795 | 64.6615 | 67.2575 | 68.2542
CA-Gladstone Rockhampton | 6046_Mt Morgan - Wowan 66 kV | Contingency Outage | 6094_Malchi Tee - Malchi 66 kV | 6094_Malchi Tee - Malchi 66 kV | 6094_Malchi Tee - Malchi 66 kV | 6094_Malchi Tee - Malchi 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6094_Malchi Tee - Malchi 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6051_Parkhurst - Keppel 66 kV | 6051_Parkhurst - Keppel 66 kV | 6310_Lakes Creek - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6051_Parkhurst - Keppel 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6003_Glenmore - Berserker 66 kV | 6051_Parkhurst - Keppel 66 kV
CA-Gladstone Rockhampton | 6047_Coominglah Sub Tee 66 kV | % of Rated A | 7.271% | 5.907% | 3.884% | 7.27% | 5.907% | 3.884% | 7.266% | 5.902% | 3.883% | 7.27% | 5.907% | 3.884% | 7.271% | 5.907% | 3.884%
CA-Gladstone Rockhampton | 6047_Coominglah Sub Tee 66 kV | Limiting Line Name | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1
CA-Gladstone Rockhampton | 6047_Coominglah Sub Tee 66 kV | Loading (A) | 11.1976 | 12.2282 | 7.729 | 11.1962 | 12.2268 | 7.7287 | 11.1896 | 12.2178 | 7.7264 | 11.1963 | 12.2266 | 7.7285 | 11.1972 | 12.2275 | 7.7287
CA-Gladstone Rockhampton | 6047_Coominglah Sub Tee 66 kV | Loading (MVA) | 1.2974 | 1.4286 | 0.91501 | 1.2974 | 1.4286 | 0.91501 | 1.2974 | 1.4285 | 0.915 | 1.2974 | 1.4286 | 0.915 | 1.2974 | 1.4286 | 0.91501
CA-Gladstone Rockhampton | 6047_Coominglah Sub Tee 66 kV | Loading (MW) | 1.1889 | 1.307 | 0.84171 | 1.1889 | 1.307 | 0.84171 | 1.1889 | 1.307 | 0.84171 | 1.1889 | 1.307 | 0.84171 | 1.1889 | 1.307 | 0.84171
CA-Gladstone Rockhampton | 6047_Coominglah Sub Tee 66 kV | Power Factor | 0.91635 | 0.91489 | 0.91989 | 0.91635 | 0.91489 | 0.91989 | 0.91637 | 0.91491 | 0.9199 | 0.91635 | 0.91489 | 0.91989 | 0.91635 | 0.91489 | 0.91989
CA-Gladstone Rockhampton | 6047_Coominglah Sub Tee 66 kV | Rating (A) | 154 | 207 | 199 | 154 | 207 | 199 | 154 | 207 | 199 | 154 | 207 | 199 | 154 | 207 | 199
CA-Gladstone Rockhampton | 6047_Coominglah Sub Tee 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Gladstone Rockhampton | 6047_Coominglah Sub Tee 66 kV | Min Voltage at Constrained Conductor | 66.8968 | 67.451 | 68.3502 | 66.9045 | 67.4581 | 68.3529 | 66.9427 | 67.5056 | 68.3728 | 66.904 | 67.4593 | 68.3546 | 66.899 | 67.4547 | 68.3531
CA-Gladstone Rockhampton | 6047_Coominglah Sub Tee 66 kV | Contingency Outage | 6027_TDM Mine 66 kV | 6027_TDM Mine 66 kV | 6010_Biloela - Callide Mine 66 kV | 6027_TDM Mine 66 kV | 6027_TDM Mine 66 kV | 6010_Biloela - Callide Mine 66 kV | 6027_TDM Mine 66 kV | 6027_TDM Mine 66 kV | 6010_Biloela - Callide Mine 66 kV | 6027_TDM Mine 66 kV | 6027_TDM Mine 66 kV | 6010_Biloela - Callide Mine 66 kV | 6027_TDM Mine 66 kV | 6027_TDM Mine 66 kV | 6010_Biloela - Callide Mine 66 kV
CA-Gladstone Rockhampton | 6050_Parkhurst - Frenchville 66 kV | % of Rated A | 30.57% | 36.55% | 14.12% | 30.06% | 36.04% | 13.89% | 29.87% | 35.76% | 13.82% | 30.05% | 35.79% | 13.82% | 30.04% | 36.03% | 13.9%
CA-Gladstone Rockhampton | 6050_Parkhurst - Frenchville 66 kV | Limiting Line Name | TR_LINE 22210_1 | TR_LINE 22210_1 | TR_LINE 22210_1 | TR_LINE 22210_1 | TR_LINE 22210_1 | TR_LINE 22210_1 | TR_LINE 22210_1 | TR_LINE 22210_1 | TR_LINE 22210_1 | TR_LINE 22210_1 | TR_LINE 22210_1 | TR_LINE 22210_1 | TR_LINE 22210_1 | TR_LINE 22210_1 | TR_LINE 22210_1
CA-Gladstone Rockhampton | 6050_Parkhurst - Frenchville 66 kV | Loading (A) | 122.5973 | 152.786 | 52.5152 | 120.5383 | 150.668 | 51.6588 | 119.7813 | 149.4708 | 51.3952 | 120.4832 | 149.6154 | 51.4174 | 120.4709 | 150.6005 | 51.7205
CA-Gladstone Rockhampton | 6050_Parkhurst - Frenchville 66 kV | Loading (MVA) | 14.3626 | 17.8785 | 6.2469 | 14.1298 | 17.589 | 6.1463 | 14.0553 | 17.4911 | 6.1128 | 14.0536 | 17.4915 | 6.1128 | 14.1296 | 17.5888 | 6.1463
CA-Gladstone Rockhampton | 6050_Parkhurst - Frenchville 66 kV | Loading (MW) | 14.1216 | 17.5436 | 6.1672 | 13.8946 | 17.2616 | 6.0681 | 13.8195 | 17.1672 | 6.0351 | 13.8192 | 17.1673 | 6.0351 | 13.8945 | 17.2615 | 6.0681
CA-Gladstone Rockhampton | 6050_Parkhurst - Frenchville 66 kV | Power Factor | 0.98322 | 0.98127 | 0.98721 | 0.98335 | 0.98138 | 0.98726 | 0.98323 | 0.98148 | 0.98728 | 0.98332 | 0.98147 | 0.98727 | 0.98336 | 0.98139 | 0.98726
CA-Gladstone Rockhampton | 6050_Parkhurst - Frenchville 66 kV | Rating (A) | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372 | 401 | 418 | 372
CA-Gladstone Rockhampton | 6050_Parkhurst - Frenchville 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Gladstone Rockhampton | 6050_Parkhurst - Frenchville 66 kV | Min Voltage at Constrained Conductor | 67.6345 | 67.5543 | 68.6781 | 67.6745 | 67.395 | 68.6922 | 67.7434 | 67.5566 | 68.668 | 67.3405 | 67.493 | 68.6386 | 67.7117 | 67.4244 | 68.6109
CA-Gladstone Rockhampton | 6050_Parkhurst - Frenchville 66 kV | Contingency Outage | 6006_Glenmore - Frenchville 66 kV | 6006_Glenmore - Frenchville 66 kV | 6006_Glenmore - Frenchville 66 kV | 6006_Glenmore - Frenchville 66 kV | 6006_Glenmore - Frenchville 66 kV | 6006_Glenmore - Frenchville 66 kV | 6006_Glenmore - Frenchville 66 kV | 6006_Glenmore - Frenchville 66 kV | 6006_Glenmore - Frenchville 66 kV | 6006_Glenmore - Frenchville 66 kV | 6006_Glenmore - Frenchville 66 kV | 6006_Glenmore - Frenchville 66 kV | 6006_Glenmore - Frenchville 66 kV | 6006_Glenmore - Frenchville 66 kV | 6006_Glenmore - Frenchville 66 kV
CA-Gladstone Rockhampton | 6051_Parkhurst - Keppel 66 kV | % of Rated A | 171.8% | 135.1% | 72.69% | 171.2% | 133.2% | 72.49% | 171.4% | 134.3% | 72.72% | 170.4% | 136.6% | 73.73% | 177.6% | 138.9% | 75.12%
CA-Gladstone Rockhampton | 6051_Parkhurst - Keppel 66 kV | Limiting Line Name | TR_LINE 19655_1 | TR_LINE 19655_1 | TR_LINE 19655_1 | TR_LINE 19655_1 | TR_LINE 19655_1 | TR_LINE 19655_1 | TR_LINE 19655_1 | TR_LINE 19655_1 | TR_LINE 19655_1 | TR_LINE 19655_1 | TR_LINE 19655_1 | TR_LINE 19655_1 | TR_LINE 19655_1 | TR_LINE 19655_1 | TR_LINE 19655_1
CA-Gladstone Rockhampton | 6051_Parkhurst - Keppel 66 kV | Loading (A) | 364.3103 | 399.7856 | 178.8104 | 363.0206 | 394.3232 | 178.3354 | 363.4612 | 397.489 | 178.8974 | 361.15 | 404.3418 | 181.3751 | 376.6096 | 411.0987 | 184.7992
CA-Gladstone Rockhampton | 6051_Parkhurst - Keppel 66 kV | Loading (MVA) | 38.7173 | 41.9407 | 20.4554 | 38.6171 | 41.8119 | 20.4073 | 38.7056 | 41.9197 | 20.4611 | 39.1362 | 42.4766 | 20.7179 | 39.8762 | 43.2255 | 21.0769
CA-Gladstone Rockhampton | 6051_Parkhurst - Keppel 66 kV | Loading (MW) | 38.2939 | 41.3722 | 20.4349 | 38.1962 | 41.2489 | 20.3873 | 38.2825 | 41.3614 | 20.4401 | 38.7089 | 41.8836 | 20.6934 | 39.3969 | 42.5991 | 21.0471
CA-Gladstone Rockhampton | 6051_Parkhurst - Keppel 66 kV | Power Factor | 0.98906 | 0.98645 | 0.999 | 0.9891 | 0.98654 | 0.99902 | 0.98907 | 0.98668 | 0.99898 | 0.98908 | 0.98604 | 0.99882 | 0.98798 | 0.98551 | 0.99859
CA-Gladstone Rockhampton | 6051_Parkhurst - Keppel 66 kV | Rating (A) | 212 | 296 | 246 | 212 | 296 | 246 | 212 | 296 | 246 | 212 | 296 | 246 | 212 | 296 | 246
CA-Gladstone Rockhampton | 6051_Parkhurst - Keppel 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Gladstone Rockhampton | 6051_Parkhurst - Keppel 66 kV | Min Voltage at Constrained Conductor | 60.816 | 59.9621 | 65.8137 | 60.8767 | 60.6213 | 65.8349 | 60.9422 | 60.2861 | 65.7998 | 62.0277 | 60.0363 | 65.7113 | 60.566 | 60.0787 | 65.6049
CA-Gladstone Rockhampton | 6051_Parkhurst - Keppel 66 kV | Contingency Outage | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV
CA-Gladstone Rockhampton | 6053_Parkhurst - Pandoin 66 kV | % of Rated A | 57.63% | 47.6% | 26.26% | 57.17% | 48.55% | 26.1% | 57.88% | 49.76% | 26.3% | 61.28% | 50.57% | 26.73% | 59.63% | 54.21% | 27.06%
CA-Gladstone Rockhampton | 6053_Parkhurst - Pandoin 66 kV | Limiting Line Name | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1
CA-Gladstone Rockhampton | 6053_Parkhurst - Pandoin 66 kV | Loading (A) | 301.4057 | 281.7929 | 143.3593 | 299.0203 | 287.3994 | 142.5004 | 302.7164 | 294.5549 | 143.6039 | 320.506 | 299.3966 | 145.9708 | 311.86 | 320.8988 | 147.7383
CA-Gladstone Rockhampton | 6053_Parkhurst - Pandoin 66 kV | Loading (MVA) | 35.6018 | 33.2582 | 17.0989 | 35.3342 | 34.2269 | 16.9987 | 35.7967 | 34.9683 | 17.1259 | 38.56 | 35.5085 | 17.4014 | 36.8431 | 38.2575 | 17.6059
CA-Gladstone Rockhampton | 6053_Parkhurst - Pandoin 66 kV | Loading (MW) | 35.3533 | 33.0185 | 17.0601 | 35.0946 | 33.6087 | 16.9579 | 35.6662 | 33.997 | 17.0903 | 37.7804 | 34.4831 | 17.3731 | 36.7465 | 35.9701 | 17.5844
CA-Gladstone Rockhampton | 6053_Parkhurst - Pandoin 66 kV | Power Factor | 0.99302 | 0.99279 | 0.9975 | 0.99322 | 0.98194 | 0.99737 | 0.99635 | 0.97222 | 0.9977 | 0.97978 | 0.97112 | 0.99816 | 0.99738 | 0.94021 | 0.99859
CA-Gladstone Rockhampton | 6053_Parkhurst - Pandoin 66 kV | Rating (A) | 523 | 592 | 546 | 523 | 592 | 546 | 523 | 592 | 546 | 523 | 592 | 546 | 523 | 592 | 546
CA-Gladstone Rockhampton | 6053_Parkhurst - Pandoin 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Gladstone Rockhampton | 6053_Parkhurst - Pandoin 66 kV | Min Voltage at Constrained Conductor | 67.7115 | 67.6879 | 68.7285 | 67.7447 | 68.2291 | 68.7398 | 67.82 | 67.9535 | 68.7179 | 68.8537 | 67.8716 | 68.6844 | 67.7556 | 68.0737 | 68.6538
CA-Gladstone Rockhampton | 6053_Parkhurst - Pandoin 66 kV | Contingency Outage | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV
CA-Gladstone Rockhampton | 6066_Bocoolima Tee -Wooderson 66 kV | % of Rated A | 7.006% | 32.36% | 2.165% | 7.024% | 31.97% | 2.166% | 7.026% | 31.97% | 2.166% | 7.028% | 31.99% | 2.166% | 6.97% | 32.53% | 2.163%
CA-Gladstone Rockhampton | 6066_Bocoolima Tee -Wooderson 66 kV | Limiting Line Name | TR_LINE 21599_1 | TR_LINE 223719_1 | TR_LINE 22217_1 | TR_LINE 21599_1 | TR_LINE 223719_1 | TR_LINE 22217_1 | TR_LINE 21599_1 | TR_LINE 223719_1 | TR_LINE 22217_1 | TR_LINE 21599_1 | TR_LINE 223719_1 | TR_LINE 22217_1 | TR_LINE 21599_1 | TR_LINE 223719_1 | TR_LINE 22217_1
CA-Gladstone Rockhampton | 6066_Bocoolima Tee -Wooderson 66 kV | Loading (A) | 11.8403 | 77.6669 | 5.0651 | 11.8712 | 76.7301 | 5.0685 | 11.874 | 76.7244 | 5.0679 | 11.8766 | 76.7872 | 5.0682 | 11.7801 | 78.0813 | 5.0618
CA-Gladstone Rockhampton | 6066_Bocoolima Tee -Wooderson 66 kV | Loading (MVA) | 1.3301 | 8.3664 | 0.60233 | 1.3299 | 8.2563 | 0.60275 | 1.3299 | 8.2562 | 0.60261 | 1.3299 | 8.2572 | 0.60266 | 1.33 | 8.3726 | 0.60157
CA-Gladstone Rockhampton | 6066_Bocoolima Tee -Wooderson 66 kV | Loading (MW) | 1.225 | 7.644 | 0.11203 | 1.225 | 7.5488 | 0.11059 | 1.225 | 7.5488 | 0.11059 | 1.225 | 7.5491 | 0.11059 | 1.225 | 7.6458 | 0.11203
CA-Gladstone Rockhampton | 6066_Bocoolima Tee -Wooderson 66 kV | Power Factor | 0.92078 | 0.90799 | 0.18599 | 0.92093 | 0.90849 | 0.18347 | 0.92093 | 0.9085 | 0.18351 | 0.92093 | 0.90845 | 0.1835 | 0.92086 | 0.90766 | 0.18623
CA-Gladstone Rockhampton | 6066_Bocoolima Tee -Wooderson 66 kV | Rating (A) | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234
CA-Gladstone Rockhampton | 6066_Bocoolima Tee -Wooderson 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Gladstone Rockhampton | 6066_Bocoolima Tee -Wooderson 66 kV | Min Voltage at Constrained Conductor | 64.8581 | 61.7714 | 68.6569 | 64.6781 | 61.7224 | 68.658 | 64.6632 | 61.7265 | 68.6506 | 64.6491 | 61.6804 | 68.6531 | 65.1838 | 61.4719 | 68.6155
CA-Gladstone Rockhampton | 6066_Bocoolima Tee -Wooderson 66 kV | Contingency Outage | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6023_Friend St-Clinton Industrial 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6023_Friend St-Clinton Industrial 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6023_Friend St-Clinton Industrial 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6023_Friend St-Clinton Industrial 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6023_Friend St-Clinton Industrial 66 kV
CA-Gladstone Rockhampton | 6074_Lakes Creek - Tanby 66 kV | % of Rated A | 93.15% | 98.11% | 48.37% | 92.75% | 95.81% | 48.23% | 93.15% | 98.14% | 48.39% | 92.16% | 98.93% | 49.07% | 96.38% | 100.1% | 49.99%
CA-Gladstone Rockhampton | 6074_Lakes Creek - Tanby 66 kV | Limiting Line Name | TR_LINE 19802_1 | TR_LINE 19802_1 | TR_LINE 19802_1 | TR_LINE 19802_1 | TR_LINE 19802_1 | TR_LINE 19802_1 | TR_LINE 19802_1 | TR_LINE 19802_1 | TR_LINE 19802_1 | TR_LINE 19802_1 | TR_LINE 19802_1 | TR_LINE 19802_1 | TR_LINE 19802_1 | TR_LINE 19802_1 | TR_LINE 19802_1
CA-Gladstone Rockhampton | 6074_Lakes Creek - Tanby 66 kV | Loading (A) | 371.6544 | 407.1577 | 178.9582 | 370.0619 | 397.6031 | 178.4612 | 371.6496 | 407.2734 | 179.0585 | 367.7141 | 410.5644 | 181.576 | 384.5665 | 415.434 | 184.9696
CA-Gladstone Rockhampton | 6074_Lakes Creek - Tanby 66 kV | Loading (MVA) | 43.0324 | 47.0852 | 21.2383 | 42.881 | 46.6774 | 21.1845 | 43.0181 | 47.0838 | 21.2435 | 43.3133 | 47.7172 | 21.5241 | 44.4697 | 48.5587 | 21.9153
CA-Gladstone Rockhampton | 6074_Lakes Creek - Tanby 66 kV | Loading (MW) | 41.5611 | 45.2049 | 21.155 | 41.4312 | 44.8818 | 21.1029 | 41.5461 | 45.2008 | 21.1594 | 41.8863 | 45.7549 | 21.4305 | 42.8635 | 46.5356 | 21.8087
CA-Gladstone Rockhampton | 6074_Lakes Creek - Tanby 66 kV | Power Factor | 0.96578 | 0.96003 | 0.99604 | 0.96616 | 0.9615 | 0.99611 | 0.96575 | 0.95997 | 0.996 | 0.96702 | 0.95884 | 0.99562 | 0.96385 | 0.9583 | 0.9951
CA-Gladstone Rockhampton | 6074_Lakes Creek - Tanby 66 kV | Rating (A) | 399 | 415 | 370 | 399 | 415 | 370 | 399 | 415 | 370 | 399 | 415 | 370 | 399 | 415 | 370
CA-Gladstone Rockhampton | 6074_Lakes Creek - Tanby 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Gladstone Rockhampton | 6074_Lakes Creek - Tanby 66 kV | Min Voltage at Constrained Conductor | 66.8491 | 66.7669 | 68.5184 | 66.9006 | 67.7792 | 68.5353 | 66.8278 | 66.746 | 68.4968 | 68.0065 | 67.1017 | 68.4394 | 66.7624 | 67.4845 | 68.4049
CA-Gladstone Rockhampton | 6074_Lakes Creek - Tanby 66 kV | Contingency Outage | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV
CA-Gladstone Rockhampton | 6075_Keppel - Farnborough 66 kV | % of Rated A | 0.3118% | 0.2842% | 0.3537% | 0.312% | 0.288% | 0.3537% | 0.3123% | 0.2842% | 0.3536% | 0.3164% | 0.2857% | 0.3534% | 0.3121% | 0.2873% | 0.3533%
CA-Gladstone Rockhampton | 6075_Keppel - Farnborough 66 kV | Limiting Line Name | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2
CA-Gladstone Rockhampton | 6075_Keppel - Farnborough 66 kV | Loading (A) | 1.1787 | 1.1794 | 1.1919 | 1.1793 | 1.1953 | 1.1921 | 1.1805 | 1.1792 | 1.1916 | 1.1959 | 1.1856 | 1.191 | 1.1798 | 1.1922 | 1.1907
CA-Gladstone Rockhampton | 6075_Keppel - Farnborough 66 kV | Loading (MVA) | 0.13937 | 0.13954 | 0.1425 | 0.1395 | 0.14331 | 0.14254 | 0.13979 | 0.13949 | 0.14244 | 0.14347 | 0.141 | 0.14229 | 0.13962 | 0.14258 | 0.14221
CA-Gladstone Rockhampton | 6075_Keppel - Farnborough 66 kV | Loading (MW) | 3.4728e-06 | 3.4772e-06 | 3.5509e-06 | 3.4763e-06 | 3.5712e-06 | 3.5519e-06 | 3.4833e-06 | 3.4758e-06 | 3.5494e-06 | 3.575e-06 | 3.5136e-06 | 3.5456e-06 | 3.4792e-06 | 3.5528e-06 | 3.5437e-06
CA-Gladstone Rockhampton | 6075_Keppel - Farnborough 66 kV | Power Factor | 2.1904e-06 | 2.1926e-06 | 2.1914e-06 | 2.1924e-06 | 2.1919e-06 | 2.1888e-06 | 2.1906e-06 | 2.1907e-06 | 2.1912e-06 | 2.1873e-06 | 2.1909e-06 | 2.1885e-06 | 2.1895e-06 | 2.192e-06 | 2.1874e-06
CA-Gladstone Rockhampton | 6075_Keppel - Farnborough 66 kV | Rating (A) | 378 | 415 | 337 | 378 | 415 | 337 | 378 | 415 | 337 | 378 | 415 | 337 | 378 | 415 | 337
CA-Gladstone Rockhampton | 6075_Keppel - Farnborough 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Gladstone Rockhampton | 6075_Keppel - Farnborough 66 kV | Min Voltage at Constrained Conductor | 68.2637 | 68.3064 | 69.027 | 68.2976 | 69.224 | 69.0378 | 68.3674 | 68.2938 | 69.0122 | 69.262 | 68.6633 | 68.9768 | 68.327 | 69.0455 | 68.958
CA-Gladstone Rockhampton | 6075_Keppel - Farnborough 66 kV | Contingency Outage | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV
CA-Gladstone Rockhampton | 6077_Farnborough - Capricorn Resort 66kV | % of Rated A | 0.06877% | 0.06256% | 0.07795% | 0.06881% | 0.0634% | 0.07797% | 0.06888% | 0.06255% | 0.07794% | 0.06978% | 0.06289% | 0.0779% | 0.06884% | 0.06324% | 0.07788%
CA-Gladstone Rockhampton | 6077_Farnborough - Capricorn Resort 66kV | Limiting Line Name | TR_LINE FARB-FARE | TR_LINE FARB-FARE | TR_LINE FARB-FARE | TR_LINE FARB-FARE | TR_LINE FARB-FARE | TR_LINE FARB-FARE | TR_LINE FARB-FARE | TR_LINE FARB-FARE | TR_LINE FARB-FARE | TR_LINE FARB-FARE | TR_LINE FARB-FARE | TR_LINE FARB-FARE | TR_LINE FARB-FARE | TR_LINE FARB-FARE | TR_LINE FARB-FARE
CA-Gladstone Rockhampton | 6077_Farnborough - Capricorn Resort 66kV | Loading (A) | 0.26134 | 0.2615 | 0.26426 | 0.26147 | 0.26502 | 0.26431 | 0.26174 | 0.26146 | 0.26421 | 0.26516 | 0.26287 | 0.26407 | 0.26158 | 0.26433 | 0.264
CA-Gladstone Rockhampton | 6077_Farnborough - Capricorn Resort 66kV | Loading (MVA) | 0.030902 | 0.030941 | 0.031597 | 0.030933 | 0.031777 | 0.031607 | 0.030996 | 0.030929 | 0.031583 | 0.031812 | 0.031265 | 0.031551 | 0.030959 | 0.031614 | 0.031534
CA-Gladstone Rockhampton | 6077_Farnborough - Capricorn Resort 66kV | Loading (MW) | 4.3694e-08 | 4.375e-08 | 4.4677e-08 | 4.3737e-08 | 4.4932e-08 | 4.4691e-08 | 4.3827e-08 | 4.3733e-08 | 4.4657e-08 | 4.4981e-08 | 4.4207e-08 | 4.4612e-08 | 4.3776e-08 | 4.4701e-08 | 4.4588e-08
CA-Gladstone Rockhampton | 6077_Farnborough - Capricorn Resort 66kV | Power Factor | 1.414e-06 | 1.414e-06 | 1.414e-06 | 1.414e-06 | 1.414e-06 | 1.414e-06 | 1.4139e-06 | 1.414e-06 | 1.4139e-06 | 1.4139e-06 | 1.414e-06 | 1.414e-06 | 1.414e-06 | 1.414e-06 | 1.414e-06
CA-Gladstone Rockhampton | 6077_Farnborough - Capricorn Resort 66kV | Rating (A) | 380 | 418 | 339 | 380 | 418 | 339 | 380 | 418 | 339 | 380 | 418 | 339 | 380 | 418 | 339
CA-Gladstone Rockhampton | 6077_Farnborough - Capricorn Resort 66kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Gladstone Rockhampton | 6077_Farnborough - Capricorn Resort 66kV | Min Voltage at Constrained Conductor | 68.2677 | 68.3105 | 69.0311 | 68.3017 | 69.2281 | 69.0419 | 68.3715 | 68.2979 | 69.0164 | 69.2661 | 68.6674 | 68.9809 | 68.331 | 69.0497 | 68.9621
CA-Gladstone Rockhampton | 6077_Farnborough - Capricorn Resort 66kV | Contingency Outage | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV
CA-Gladstone Rockhampton | 6082_Farnborough Tee - Yeppoon 66 kV | % of Rated A | 171.9% | 135.1% | 72.72% | 171.3% | 133.3% | 72.52% | 171.5% | 134.4% | 72.75% | 170.4% | 136.7% | 73.76% | 177.7% | 139% | 75.15%
CA-Gladstone Rockhampton | 6082_Farnborough Tee - Yeppoon 66 kV | Limiting Line Name | TR_LINE 22238_1 | TR_LINE 22238_1 | TR_LINE 22238_1 | TR_LINE 22238_1 | TR_LINE 22238_1 | TR_LINE 22238_1 | TR_LINE 22238_1 | TR_LINE 22238_1 | TR_LINE 22238_1 | TR_LINE 22238_1 | TR_LINE 22238_1 | TR_LINE 22238_1 | TR_LINE 22238_1 | TR_LINE 22238_1 | TR_LINE 22238_1
CA-Gladstone Rockhampton | 6082_Farnborough Tee - Yeppoon 66 kV | Loading (A) | 364.5078 | 400.0016 | 178.8798 | 363.2179 | 394.5414 | 178.4041 | 363.6591 | 397.7045 | 178.9675 | 361.3519 | 404.5614 | 181.45 | 376.8157 | 411.3226 | 184.8805
CA-Gladstone Rockhampton | 6082_Farnborough Tee - Yeppoon 66 kV | Loading (MVA) | 37.9269 | 40.969 | 20.2899 | 37.8326 | 40.868 | 20.2428 | 37.9191 | 40.9609 | 20.2954 | 38.3606 | 41.4799 | 20.5472 | 39.0243 | 42.1915 | 20.899
CA-Gladstone Rockhampton | 6082_Farnborough Tee - Yeppoon 66 kV | Loading (MW) | 37.6127 | 40.552 | 20.2708 | 37.5199 | 40.4508 | 20.2241 | 37.6045 | 40.5505 | 20.2759 | 38.0395 | 41.0445 | 20.5246 | 38.669 | 41.7318 | 20.8719
CA-Gladstone Rockhampton | 6082_Farnborough Tee - Yeppoon 66 kV | Power Factor | 0.99172 | 0.98982 | 0.99906 | 0.99173 | 0.98979 | 0.99908 | 0.9917 | 0.98998 | 0.99904 | 0.99163 | 0.9895 | 0.9989 | 0.99089 | 0.9891 | 0.9987
CA-Gladstone Rockhampton | 6082_Farnborough Tee - Yeppoon 66 kV | Rating (A) | 212 | 296 | 246 | 212 | 296 | 246 | 212 | 296 | 246 | 212 | 296 | 246 | 212 | 296 | 246
CA-Gladstone Rockhampton | 6082_Farnborough Tee - Yeppoon 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Gladstone Rockhampton | 6082_Farnborough Tee - Yeppoon 66 kV | Min Voltage at Constrained Conductor | 60.0527 | 59.1107 | 65.4784 | 60.1163 | 59.7816 | 65.5006 | 60.1806 | 59.4407 | 65.4641 | 61.2706 | 59.1731 | 65.3695 | 59.7712 | 59.1983 | 65.2547
CA-Gladstone Rockhampton | 6082_Farnborough Tee - Yeppoon 66 kV | Contingency Outage | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV | 6074_Lakes Creek - Tanby 66 kV
CA-Gladstone Rockhampton | 6090_Egan's Hill - Raglan 66 kV | % of Rated A | 22.54% | 18.79% | 10.56% | 22.53% | 18.89% | 10.56% | 22.63% | 18.8% | 10.57% | 22.73% | 18.83% | 10.58% | 22.61% | 18.84% | 10.58%
CA-Gladstone Rockhampton | 6090_Egan's Hill - Raglan 66 kV | Limiting Line Name | TR_LINE 22121_1 | TR_LINE 22121_1 | TR_LINE 160589_1 | TR_LINE 22121_1 | TR_LINE 22121_1 | TR_LINE 160589_1 | TR_LINE 22121_1 | TR_LINE 22121_1 | TR_LINE 160589_1 | TR_LINE 22121_1 | TR_LINE 22121_1 | TR_LINE 160589_1 | TR_LINE 22121_1 | TR_LINE 22121_1 | TR_LINE 160589_1
CA-Gladstone Rockhampton | 6090_Egan's Hill - Raglan 66 kV | Loading (A) | 29.7548 | 31.3715 | 16.7958 | 29.7417 | 31.5438 | 16.7935 | 29.8674 | 31.3963 | 16.8043 | 30.0075 | 31.4404 | 16.8169 | 29.8508 | 31.4634 | 16.8218
CA-Gladstone Rockhampton | 6090_Egan's Hill - Raglan 66 kV | Loading (MVA) | 3.492 | 3.659 | 2.0055 | 3.492 | 3.682 | 2.0056 | 3.4918 | 3.659 | 2.0054 | 3.4919 | 3.6819 | 2.0052 | 3.4918 | 3.6819 | 2.0051
CA-Gladstone Rockhampton | 6090_Egan's Hill - Raglan 66 kV | Loading (MW) | 3.4617 | 3.6496 | 1.9646 | 3.4617 | 3.6495 | 1.9646 | 3.4616 | 3.6496 | 1.9646 | 3.4617 | 3.6495 | 1.9646 | 3.4616 | 3.6495 | 1.9646
CA-Gladstone Rockhampton | 6090_Egan's Hill - Raglan 66 kV | Power Factor | 0.99128 | 0.99741 | 0.97957 | 0.99128 | 0.99115 | 0.97955 | 0.99133 | 0.9974 | 0.97965 | 0.9913 | 0.99117 | 0.97977 | 0.99133 | 0.99116 | 0.97982
CA-Gladstone Rockhampton | 6090_Egan's Hill - Raglan 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
CA-Gladstone Rockhampton | 6090_Egan's Hill - Raglan 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Gladstone Rockhampton | 6090_Egan's Hill - Raglan 66 kV | Min Voltage at Constrained Conductor | 67.7583 | 67.3371 | 68.9216 | 67.7878 | 67.3917 | 68.9323 | 67.4976 | 67.2848 | 68.8817 | 67.1855 | 67.6109 | 68.8226 | 67.5348 | 67.562 | 68.7996
CA-Gladstone Rockhampton | 6090_Egan's Hill - Raglan 66 kV | Contingency Outage | 6044_Raglan-East End Quarry/Yarwun 66 kV | 6051_Parkhurst - Keppel 66 kV | 6051_Parkhurst - Keppel 66 kV | 6044_Raglan-East End Quarry/Yarwun 66 kV | 6044_Raglan-East End Quarry/Yarwun 66 kV | 6051_Parkhurst - Keppel 66 kV | 6044_Raglan-East End Quarry/Yarwun 66 kV | 6051_Parkhurst - Keppel 66 kV | 6051_Parkhurst - Keppel 66 kV | 6044_Raglan-East End Quarry/Yarwun 66 kV | 6044_Raglan-East End Quarry/Yarwun 66 kV | 6051_Parkhurst - Keppel 66 kV | 6044_Raglan-East End Quarry/Yarwun 66 kV | 6044_Raglan-East End Quarry/Yarwun 66 kV | 6051_Parkhurst - Keppel 66 kV
CA-Gladstone Rockhampton | 6091_Egan's Hill - Gavial 66 kV | % of Rated A | 69.46% | 52.31% | 21.94% | 69.43% | 52.48% | 21.94% | 105% | 59.73% | 26.77% | 144.5% | 68.09% | 32.29% | 145.5% | 69.02% | 32.66%
CA-Gladstone Rockhampton | 6091_Egan's Hill - Gavial 66 kV | Limiting Line Name | TR_LINE 13465_1 | TR_LINE 13465_1 | TR_LINE 13465_1 | TR_LINE 13465_1 | TR_LINE 13465_1 | TR_LINE 13465_1 | TR_LINE 13465_1 | TR_LINE 13465_1 | TR_LINE 13465_1 | TR_LINE 13465_1 | TR_LINE 13465_1 | TR_LINE 13465_1 | TR_LINE 13465_1 | TR_LINE 13465_1 | TR_LINE 13465_1
CA-Gladstone Rockhampton | 6091_Egan's Hill - Gavial 66 kV | Loading (A) | 99.3244 | 100.9608 | 40.8154 | 99.292 | 101.2808 | 40.8092 | 150.1874 | 115.2839 | 49.8012 | 206.6205 | 131.421 | 60.0514 | 208.0823 | 133.201 | 60.7416
CA-Gladstone Rockhampton | 6091_Egan's Hill - Gavial 66 kV | Loading (MVA) | 11.7741 | 11.9673 | 4.8785 | 11.7738 | 11.9696 | 4.8785 | 17.7353 | 13.6549 | 5.949 | 24.3827 | 15.5835 | 7.1673 | 24.5755 | 15.7814 | 7.2472
CA-Gladstone Rockhampton | 6091_Egan's Hill - Gavial 66 kV | Loading (MW) | 11.6902 | 11.887 | 4.8693 | 11.6901 | 11.8879 | 4.8693 | 16.9644 | 13.4281 | 5.9324 | 22.5778 | 15.1564 | 7.0657 | 22.7654 | 15.3495 | 7.144
CA-Gladstone Rockhampton | 6091_Egan's Hill - Gavial 66 kV | Power Factor | 0.99288 | 0.99328 | 0.99813 | 0.99289 | 0.99317 | 0.99812 | 0.95653 | 0.98339 | 0.9972 | 0.92598 | 0.9726 | 0.98582 | 0.92634 | 0.97264 | 0.98574
CA-Gladstone Rockhampton | 6091_Egan's Hill - Gavial 66 kV | Rating (A) | 143 | 193 | 186 | 143 | 193 | 186 | 143 | 193 | 186 | 143 | 193 | 186 | 143 | 193 | 186
CA-Gladstone Rockhampton | 6091_Egan's Hill - Gavial 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Gladstone Rockhampton | 6091_Egan's Hill - Gavial 66 kV | Min Voltage at Constrained Conductor | 68.4359 | 68.4318 | 69.0063 | 68.4569 | 68.2288 | 69.017 | 68.1714 | 68.3798 | 68.9661 | 68.1215 | 68.4547 | 68.9065 | 68.1777 | 68.3975 | 68.8836
CA-Gladstone Rockhampton | 6091_Egan's Hill - Gavial 66 kV | Contingency Outage | 6082_Farnborough Tee - Yeppoon 66 kV | 6051_Parkhurst - Keppel 66 kV | 6051_Parkhurst - Keppel 66 kV | 6051_Parkhurst - Keppel 66 kV | 6003_Glenmore - Berserker 66 kV | 6051_Parkhurst - Keppel 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6051_Parkhurst - Keppel 66 kV | 6051_Parkhurst - Keppel 66 kV | 6310_Lakes Creek - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6051_Parkhurst - Keppel 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6003_Glenmore - Berserker 66 kV | 6051_Parkhurst - Keppel 66 kV
CA-Gladstone Rockhampton | 6093_Gavial - Mt Morgan 66 kV | % of Rated A | 4.231% | 3.604% | 3.853% | 4.233% | 3.587% | 3.853% | 40.96% | 8.533% | 5.911% | 83.66% | 17.74% | 12.33% | 83.59% | 17.76% | 12.34%
CA-Gladstone Rockhampton | 6093_Gavial - Mt Morgan 66 kV | Limiting Line Name | TR_LINE 19113_1 | TR_LINE 19767_1 | TR_LINE 19767_1 | TR_LINE 19113_1 | TR_LINE 19767_1 | TR_LINE 19767_1 | TR_LINE 19767_1 | TR_LINE 19767_1 | TR_LINE 19767_1 | TR_LINE 19767_1 | TR_LINE 19767_1 | TR_LINE 19767_1 | TR_LINE 19767_1 | TR_LINE 19767_1 | TR_LINE 19767_1
CA-Gladstone Rockhampton | 6093_Gavial - Mt Morgan 66 kV | Loading (A) | 6.0499 | 6.0179 | 6.1257 | 6.0529 | 5.9905 | 6.1266 | 54.0631 | 14.2497 | 9.398 | 110.4294 | 29.6329 | 19.6112 | 110.3333 | 29.6652 | 19.6199
CA-Gladstone Rockhampton | 6093_Gavial - Mt Morgan 66 kV | Loading (MVA) | 0.72506 | 0.72246 | 0.73541 | 0.72571 | 0.71622 | 0.73562 | 6.2244 | 1.6723 | 1.118 | 12.6111 | 3.4594 | 2.3211 | 12.6099 | 3.4599 | 2.3213
CA-Gladstone Rockhampton | 6093_Gavial - Mt Morgan 66 kV | Loading (MW) | 0.23806 | 0.071261 | 0.049796 | 0.23806 | 0.071252 | 0.049797 | 5.4323 | 1.5986 | 1.1093 | 10.6803 | 3.1129 | 2.1573 | 10.6799 | 3.1129 | 2.1573
CA-Gladstone Rockhampton | 6093_Gavial - Mt Morgan 66 kV | Power Factor | 0.32833 | 0.098636 | 0.067713 | 0.32804 | 0.099484 | 0.067693 | 0.86505 | 0.954 | 0.99086 | 0.84432 | 0.8957 | 0.92672 | 0.84435 | 0.89558 | 0.92666
CA-Gladstone Rockhampton | 6093_Gavial - Mt Morgan 66 kV | Rating (A) | 143 | 167 | 159 | 143 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
CA-Gladstone Rockhampton | 6093_Gavial - Mt Morgan 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Gladstone Rockhampton | 6093_Gavial - Mt Morgan 66 kV | Min Voltage at Constrained Conductor | 69.1932 | 69.3115 | 69.3128 | 69.2213 | 69.0279 | 69.3225 | 66.4711 | 67.7548 | 68.6848 | 64.8913 | 67.4009 | 68.3335 | 64.9447 | 67.3371 | 68.3082
CA-Gladstone Rockhampton | 6093_Gavial - Mt Morgan 66 kV | Contingency Outage | 6094_Malchi Tee - Malchi 66 kV | 6094_Malchi Tee - Malchi 66 kV | 6094_Malchi Tee - Malchi 66 kV | 6094_Malchi Tee - Malchi 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6094_Malchi Tee - Malchi 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6051_Parkhurst - Keppel 66 kV | 6051_Parkhurst - Keppel 66 kV | 6310_Lakes Creek - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6051_Parkhurst - Keppel 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6003_Glenmore - Berserker 66 kV | 6051_Parkhurst - Keppel 66 kV
CA-Gladstone Rockhampton | 6094_Malchi Tee - Malchi 66 kV | % of Rated A | 58.33% | 42.39% | 17.46% | 58.31% | 42.53% | 17.46% | 58.79% | 42.48% | 17.49% | 60.08% | 43.18% | 17.8% | 61% | 43.91% | 18.09%
CA-Gladstone Rockhampton | 6094_Malchi Tee - Malchi 66 kV | Limiting Line Name | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1
CA-Gladstone Rockhampton | 6094_Malchi Tee - Malchi 66 kV | Loading (A) | 98.5708 | 101.742 | 40.8589 | 98.5389 | 102.0615 | 40.8524 | 99.3576 | 101.9468 | 40.9155 | 101.5278 | 103.6425 | 41.6515 | 103.0931 | 105.3931 | 42.3337
CA-Gladstone Rockhampton | 6094_Malchi Tee - Malchi 66 kV | Loading (MVA) | 11.6127 | 11.9856 | 4.8625 | 11.6125 | 11.9873 | 4.8625 | 11.6134 | 11.9867 | 4.8626 | 11.8078 | 12.1847 | 4.9415 | 11.9992 | 12.3794 | 5.0203
CA-Gladstone Rockhampton | 6094_Malchi Tee - Malchi 66 kV | Loading (MW) | 11.4147 | 11.7767 | 4.8128 | 11.4146 | 11.7774 | 4.8127 | 11.4156 | 11.7771 | 4.8128 | 11.6028 | 11.9691 | 4.8908 | 11.7888 | 12.1604 | 4.9688
CA-Gladstone Rockhampton | 6094_Malchi Tee - Malchi 66 kV | Power Factor | 0.9825 | 0.98223 | 0.98712 | 0.98251 | 0.98217 | 0.98712 | 0.98257 | 0.98219 | 0.98711 | 0.98234 | 0.98204 | 0.98705 | 0.98221 | 0.9821 | 0.987
CA-Gladstone Rockhampton | 6094_Malchi Tee - Malchi 66 kV | Rating (A) | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234
CA-Gladstone Rockhampton | 6094_Malchi Tee - Malchi 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Gladstone Rockhampton | 6094_Malchi Tee - Malchi 66 kV | Min Voltage at Constrained Conductor | 67.6029 | 67.5773 | 68.7095 | 67.6243 | 67.3709 | 68.7202 | 67.0611 | 67.4448 | 68.6153 | 66.7074 | 67.4255 | 68.4958 | 66.7493 | 67.3526 | 68.4669
CA-Gladstone Rockhampton | 6094_Malchi Tee - Malchi 66 kV | Contingency Outage | 6082_Farnborough Tee - Yeppoon 66 kV | 6051_Parkhurst - Keppel 66 kV | 6051_Parkhurst - Keppel 66 kV | 6051_Parkhurst - Keppel 66 kV | 6003_Glenmore - Berserker 66 kV | 6051_Parkhurst - Keppel 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6051_Parkhurst - Keppel 66 kV | 6051_Parkhurst - Keppel 66 kV | 6310_Lakes Creek - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6051_Parkhurst - Keppel 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6003_Glenmore - Berserker 66 kV | 6051_Parkhurst - Keppel 66 kV
CA-Gladstone Rockhampton | 6095_Egan's Hill-Rockhampton South 66 kV | % of Rated A | 47.13% | 43.03% | 22.7% | 46.34% | 38.82% | 22.32% | 35.5% | 40.47% | 21.05% | 34.28% | 38.56% | 19.75% | 33.15% | 38.96% | 19.91%
CA-Gladstone Rockhampton | 6095_Egan's Hill-Rockhampton South 66 kV | Limiting Line Name | TR_LINE 20972_1 | TR_LINE 20972_1 | TR_LINE 20983_1 | TR_LINE 20972_1 | TR_LINE 20972_1 | TR_LINE 20983_1 | TR_LINE 20983_1 | TR_LINE 20972_1 | TR_LINE 20983_1 | TR_LINE 20972_1 | TR_LINE 20972_1 | TR_LINE 20983_1 | TR_LINE 20972_1 | TR_LINE 20972_1 | TR_LINE 20983_1
CA-Gladstone Rockhampton | 6095_Egan's Hill-Rockhampton South 66 kV | Loading (A) | 116.8807 | 107.5633 | 49.9396 | 114.9326 | 97.0438 | 49.1112 | 88.0316 | 101.1805 | 46.3151 | 85.0226 | 96.3983 | 43.4548 | 82.2105 | 97.3962 | 43.7994
CA-Gladstone Rockhampton | 6095_Egan's Hill-Rockhampton South 66 kV | Loading (MVA) | 13.8961 | 12.8061 | 5.9764 | 13.6709 | 11.5064 | 5.8782 | 10.4605 | 12.0401 | 5.5401 | 10.1652 | 11.4569 | 5.1942 | 9.7036 | 11.5683 | 5.234
CA-Gladstone Rockhampton | 6095_Egan's Hill-Rockhampton South 66 kV | Loading (MW) | 13.4633 | 12.4122 | 5.9553 | 13.2446 | 11.4882 | 5.855 | 10.3169 | 11.6967 | 5.4967 | 6.566 | 11.1577 | 5.1213 | 8.9596 | 11.2624 | 5.1656
CA-Gladstone Rockhampton | 6095_Egan's Hill-Rockhampton South 66 kV | Power Factor | 0.96886 | 0.9692 | 0.99648 | 0.96882 | 0.99841 | 0.99606 | 0.98627 | 0.97141 | 0.99218 | 0.64517 | 0.97378 | 0.98595 | 0.92287 | 0.97346 | 0.98691
CA-Gladstone Rockhampton | 6095_Egan's Hill-Rockhampton South 66 kV | Rating (A) | 248 | 250 | 220 | 248 | 250 | 220 | 248 | 250 | 220 | 248 | 250 | 220 | 248 | 250 | 220
CA-Gladstone Rockhampton | 6095_Egan's Hill-Rockhampton South 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Gladstone Rockhampton | 6095_Egan's Hill-Rockhampton South 66 kV | Min Voltage at Constrained Conductor | 68.4717 | 68.5852 | 69.0657 | 68.5079 | 68.3206 | 69.0771 | 68.5613 | 68.5625 | 69.0366 | 69.0276 | 68.487 | 68.9906 | 68.0562 | 68.4421 | 68.9719
CA-Gladstone Rockhampton | 6095_Egan's Hill-Rockhampton South 66 kV | Contingency Outage | 6096_Egan's Hill - Lakes Creek 66 kV | 6096_Egan's Hill - Lakes Creek 66 kV | 6096_Egan's Hill - Lakes Creek 66 kV | 6096_Egan's Hill - Lakes Creek 66 kV | 6096_Egan's Hill - Lakes Creek 66 kV | 6096_Egan's Hill - Lakes Creek 66 kV | 6096_Egan's Hill - Lakes Creek 66 kV | 6096_Egan's Hill - Lakes Creek 66 kV | 6096_Egan's Hill - Lakes Creek 66 kV | 6003_Glenmore - Berserker 66 kV | 6096_Egan's Hill - Lakes Creek 66 kV | 6096_Egan's Hill - Lakes Creek 66 kV | 6004_Glenmore - Rockhampton South 66 kV | 6096_Egan's Hill - Lakes Creek 66 kV | 6096_Egan's Hill - Lakes Creek 66 kV
CA-Gladstone Rockhampton | 6097_Egan's Hill - Canning 66 kV | % of Rated A | 72.12% | 71.43% | 48.15% | 71.42% | 71.22% | 47.73% | 71.19% | 70.17% | 47.36% | 71.8% | 70.62% | 47.6% | 71.81% | 71% | 47.82%
CA-Gladstone Rockhampton | 6097_Egan's Hill - Canning 66 kV | Limiting Line Name | TR_LINE 21003_1 | TR_LINE 21003_1 | TR_LINE 20992_1 | TR_LINE 20992_1 | TR_LINE 21003_1 | TR_LINE 20992_1 | TR_LINE 20992_1 | TR_LINE 20992_1 | TR_LINE 20992_1 | TR_LINE 21003_1 | TR_LINE 20992_1 | TR_LINE 20992_1 | TR_LINE 21003_1 | TR_LINE 20992_1 | TR_LINE 20992_1
CA-Gladstone Rockhampton | 6097_Egan's Hill - Canning 66 kV | Loading (A) | 178.8497 | 178.5781 | 105.9237 | 177.124 | 178.0506 | 105.0135 | 176.5563 | 175.4319 | 104.1897 | 178.0744 | 176.5544 | 104.7203 | 178.1004 | 177.511 | 105.1942
CA-Gladstone Rockhampton | 6097_Egan's Hill - Canning 66 kV | Loading (MVA) | 21.1883 | 21.1764 | 12.6529 | 21.0216 | 20.9846 | 12.5466 | 20.829 | 20.8161 | 12.4386 | 20.9 | 20.9139 | 12.4901 | 20.9956 | 21.0115 | 12.5429
CA-Gladstone Rockhampton | 6097_Egan's Hill - Canning 66 kV | Loading (MW) | 21.1883 | 21.1763 | 12.4482 | 21.0216 | 20.9845 | 12.3346 | 20.829 | 20.816 | 12.221 | 20.8998 | 20.9139 | 12.2779 | 20.9956 | 21.0115 | 12.3348
CA-Gladstone Rockhampton | 6097_Egan's Hill - Canning 66 kV | Power Factor | 1 | 1 | 0.98378 | 1 | 1 | 0.98306 | 1 | 0.99999 | 0.98246 | 0.99999 | 1 | 0.98297 | 1 | 1 | 0.98337
CA-Gladstone Rockhampton | 6097_Egan's Hill - Canning 66 kV | Rating (A) | 248 | 250 | 220 | 248 | 250 | 220 | 248 | 250 | 220 | 248 | 250 | 220 | 248 | 250 | 220
CA-Gladstone Rockhampton | 6097_Egan's Hill - Canning 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Gladstone Rockhampton | 6097_Egan's Hill - Canning 66 kV | Min Voltage at Constrained Conductor | 68.1054 | 68.1713 | 68.9219 | 68.4308 | 67.7529 | 68.9356 | 68.0216 | 68.4166 | 68.8834 | 67.4693 | 68.3002 | 68.8176 | 67.7697 | 68.2483 | 68.7966
CA-Gladstone Rockhampton | 6097_Egan's Hill - Canning 66 kV | Contingency Outage | 6005_Rockhampton Glenmore-Canning 66 kV | 6005_Rockhampton Glenmore-Canning 66 kV | 6005_Rockhampton Glenmore-Canning 66 kV | 6005_Rockhampton Glenmore-Canning 66 kV | 6005_Rockhampton Glenmore-Canning 66 kV | 6005_Rockhampton Glenmore-Canning 66 kV | 6005_Rockhampton Glenmore-Canning 66 kV | 6005_Rockhampton Glenmore-Canning 66 kV | 6005_Rockhampton Glenmore-Canning 66 kV | 6005_Rockhampton Glenmore-Canning 66 kV | 6005_Rockhampton Glenmore-Canning 66 kV | 6005_Rockhampton Glenmore-Canning 66 kV | 6005_Rockhampton Glenmore-Canning 66 kV | 6005_Rockhampton Glenmore-Canning 66 kV | 6005_Rockhampton Glenmore-Canning 66 kV
CA-Gladstone Rockhampton | 6100_Boat Creek - ICI 66 kV | % of Rated A | 5.94% | 5.45% | 6.664% | 5.939% | 5.449% | 6.664% | 5.949% | 5.391% | 6.673% | 5.959% | 5.4% | 6.682% | 5.96% | 5.4% | 6.683%
CA-Gladstone Rockhampton | 6100_Boat Creek - ICI 66 kV | Limiting Line Name | TR_LINE 50343_1 | TR_LINE 50343_1 | TR_LINE 50343_1 | TR_LINE 50343_1 | TR_LINE 50343_1 | TR_LINE 50343_1 | TR_LINE 50343_1 | TR_LINE 50343_1 | TR_LINE 50343_1 | TR_LINE 50343_1 | TR_LINE 50343_1 | TR_LINE 50343_1 | TR_LINE 50343_1 | TR_LINE 50343_1 | TR_LINE 50343_1
CA-Gladstone Rockhampton | 6100_Boat Creek - ICI 66 kV | Loading (A) | 43.9571 | 43.9781 | 44.1179 | 43.9496 | 43.9735 | 44.1142 | 44.0232 | 43.5019 | 44.1725 | 44.0967 | 43.5751 | 44.2362 | 44.102 | 43.5807 | 44.2404
CA-Gladstone Rockhampton | 6100_Boat Creek - ICI 66 kV | Loading (MVA) | 5.1061 | 5.0537 | 5.1172 | 5.1061 | 5.0537 | 5.1172 | 5.1063 | 5.0539 | 5.1174 | 5.1065 | 5.0541 | 5.1176 | 5.1065 | 5.0541 | 5.1176
CA-Gladstone Rockhampton | 6100_Boat Creek - ICI 66 kV | Loading (MW) | 4.3586 | 4.3145 | 4.3679 | 4.3586 | 4.3145 | 4.3679 | 4.3587 | 4.3145 | 4.3679 | 4.3587 | 4.3145 | 4.368 | 4.3587 | 4.3145 | 4.368
CA-Gladstone Rockhampton | 6100_Boat Creek - ICI 66 kV | Power Factor | 0.85357 | 0.85369 | 0.85352 | 0.85357 | 0.85369 | 0.85352 | 0.85354 | 0.85366 | 0.8535 | 0.85351 | 0.85363 | 0.85348 | 0.85351 | 0.85363 | 0.85347
CA-Gladstone Rockhampton | 6100_Boat Creek - ICI 66 kV | Rating (A) | 740 | 807 | 662 | 740 | 807 | 662 | 740 | 807 | 662 | 740 | 807 | 662 | 740 | 807 | 662
CA-Gladstone Rockhampton | 6100_Boat Creek - ICI 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Gladstone Rockhampton | 6100_Boat Creek - ICI 66 kV | Min Voltage at Constrained Conductor | 67.0656 | 66.3452 | 66.9669 | 67.0766 | 66.3519 | 66.9725 | 66.9671 | 67.074 | 66.886 | 66.8582 | 66.9641 | 66.7921 | 66.8504 | 66.9557 | 66.7859
CA-Gladstone Rockhampton | 6100_Boat Creek - ICI 66 kV | Contingency Outage | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV
CA-Gladstone Rockhampton | 6101_Boat Creek - Orica 66 kV | % of Rated A | 12.36% | 10.06% | 16.65% | 12.36% | 10.06% | 16.65% | 12.38% | 9.95% | 16.67% | 12.4% | 9.967% | 16.7% | 12.4% | 9.968% | 16.7%
CA-Gladstone Rockhampton | 6101_Boat Creek - Orica 66 kV | Limiting Line Name | TR_LINE pole4158700 to ORIC | TR_LINE pole4158700 to ORIC | TR_LINE pole4158700 to ORIC | TR_LINE pole4158700 to ORIC | TR_LINE pole4158700 to ORIC | TR_LINE pole4158700 to ORIC | TR_LINE pole4158700 to ORIC | TR_LINE pole4158700 to ORIC | TR_LINE pole4158700 to ORIC | TR_LINE pole4158700 to ORIC | TR_LINE pole4158700 to ORIC | TR_LINE pole4158700 to ORIC | TR_LINE pole4158700 to ORIC | TR_LINE pole4158700 to ORIC | TR_LINE pole4158700 to ORIC
CA-Gladstone Rockhampton | 6101_Boat Creek - Orica 66 kV | Loading (A) | 91.4727 | 81.1813 | 110.2518 | 91.4577 | 81.173 | 110.2426 | 91.6074 | 80.2988 | 110.3851 | 91.7566 | 80.4307 | 110.5404 | 91.7674 | 80.4408 | 110.5508
CA-Gladstone Rockhampton | 6101_Boat Creek - Orica 66 kV | Loading (MVA) | 10.6231 | 9.3269 | 12.7849 | 10.6231 | 9.3269 | 12.7849 | 10.6232 | 9.3269 | 12.7849 | 10.6232 | 9.3269 | 12.7849 | 10.6232 | 9.3269 | 12.7849
CA-Gladstone Rockhampton | 6101_Boat Creek - Orica 66 kV | Loading (MW) | 9.7101 | 8.5253 | 11.6856 | 9.7101 | 8.5253 | 11.6856 | 9.7101 | 8.5253 | 11.6856 | 9.7101 | 8.5253 | 11.6856 | 9.7101 | 8.5253 | 11.6856
CA-Gladstone Rockhampton | 6101_Boat Creek - Orica 66 kV | Power Factor | 0.914 | 0.914 | 0.914 | 0.914 | 0.914 | 0.914 | 0.914 | 0.914 | 0.914 | 0.914 | 0.914 | 0.914 | 0.914 | 0.914 | 0.914
CA-Gladstone Rockhampton | 6101_Boat Creek - Orica 66 kV | Rating (A) | 740 | 807 | 662 | 740 | 807 | 662 | 740 | 807 | 662 | 740 | 807 | 662 | 740 | 807 | 662
CA-Gladstone Rockhampton | 6101_Boat Creek - Orica 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Gladstone Rockhampton | 6101_Boat Creek - Orica 66 kV | Min Voltage at Constrained Conductor | 67.0491 | 66.3315 | 66.9454 | 67.0602 | 66.3382 | 66.951 | 66.9506 | 67.0605 | 66.8645 | 66.8417 | 66.9505 | 66.7706 | 66.8339 | 66.9421 | 66.7643
CA-Gladstone Rockhampton | 6101_Boat Creek - Orica 66 kV | Contingency Outage | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV
CA-Gladstone Rockhampton | 6102_Boat Creek - Yarwun 66 kV | % of Rated A | 4.367% | 4.15% | 4.329% | 4.27% | 4.057% | 4.234% | 5.925% | 5.567% | 5.869% | 7.609% | 7.155% | 7.531% | 7.709% | 7.25% | 7.63%
CA-Gladstone Rockhampton | 6102_Boat Creek - Yarwun 66 kV | Limiting Line Name | TR_LINE 16861_2 | TR_LINE 16861_2 | TR_LINE 16861_2 | TR_LINE 16861_2 | TR_LINE 16861_2 | TR_LINE 16861_2 | TR_LINE 16861_2 | TR_LINE 16861_2 | TR_LINE 16861_2 | TR_LINE 16861_2 | TR_LINE 16861_2 | TR_LINE 16861_2 | TR_LINE 16861_2 | TR_LINE 16861_2 | TR_LINE 16861_2
CA-Gladstone Rockhampton | 6102_Boat Creek - Yarwun 66 kV | Loading (A) | 32.314 | 33.4884 | 28.6609 | 31.6009 | 32.7437 | 28.0276 | 43.8447 | 44.9221 | 38.8559 | 56.3034 | 57.7393 | 49.8533 | 57.0473 | 58.5054 | 50.5083
CA-Gladstone Rockhampton | 6102_Boat Creek - Yarwun 66 kV | Loading (MVA) | 3.7518 | 3.8458 | 3.3226 | 3.6692 | 3.7607 | 3.2495 | 5.0811 | 5.2141 | 4.498 | 6.5124 | 6.6888 | 5.7615 | 6.5975 | 6.7766 | 5.8366
CA-Gladstone Rockhampton | 6102_Boat Creek - Yarwun 66 kV | Loading (MW) | 2.946 | 3.0183 | 2.6161 | 2.8825 | 2.9529 | 2.5597 | 3.963 | 4.0646 | 3.5194 | 5.0454 | 5.1782 | 4.4807 | 5.1092 | 5.2438 | 4.5373
CA-Gladstone Rockhampton | 6102_Boat Creek - Yarwun 66 kV | Power Factor | 0.78499 | 0.78458 | 0.78714 | 0.78536 | 0.78496 | 0.78749 | 0.77964 | 0.7792 | 0.78215 | 0.77433 | 0.77374 | 0.77732 | 0.77399 | 0.77339 | 0.77702
CA-Gladstone Rockhampton | 6102_Boat Creek - Yarwun 66 kV | Rating (A) | 740 | 807 | 662 | 740 | 807 | 662 | 740 | 807 | 662 | 740 | 807 | 662 | 740 | 807 | 662
CA-Gladstone Rockhampton | 6102_Boat Creek - Yarwun 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Gladstone Rockhampton | 6102_Boat Creek - Yarwun 66 kV | Min Voltage at Constrained Conductor | 67.0334 | 66.3026 | 66.9318 | 67.0369 | 66.3104 | 66.9383 | 66.9083 | 67.0134 | 66.8351 | 66.7798 | 66.8833 | 66.7239 | 66.7708 | 66.8736 | 66.7166
CA-Gladstone Rockhampton | 6102_Boat Creek - Yarwun 66 kV | Contingency Outage | 7290_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV
CA-Gladstone Rockhampton | 6103_Fisherman Landing-Boat Creek 66 kV | % of Rated A | 83.25% | 72.67% | 84.36% | 83.23% | 72.66% | 84.35% | 83.37% | 71.87% | 84.46% | 83.51% | 71.99% | 84.58% | 83.52% | 72% | 84.59%
CA-Gladstone Rockhampton | 6103_Fisherman Landing-Boat Creek 66 kV | Limiting Line Name | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1
CA-Gladstone Rockhampton | 6103_Fisherman Landing-Boat Creek 66 kV | Loading (A) | 233.096 | 223.0953 | 231.9921 | 233.0571 | 223.0724 | 231.9725 | 233.4443 | 220.6353 | 232.2768 | 233.8304 | 221.0029 | 232.6085 | 233.8582 | 221.0311 | 232.6307
CA-Gladstone Rockhampton | 6103_Fisherman Landing-Boat Creek 66 kV | Loading (MVA) | 26.8745 | 25.4516 | 26.7086 | 26.8745 | 25.4516 | 26.7086 | 26.8745 | 25.4516 | 26.7086 | 26.8746 | 25.4516 | 26.7086 | 26.8746 | 25.4516 | 26.7086
CA-Gladstone Rockhampton | 6103_Fisherman Landing-Boat Creek 66 kV | Loading (MW) | 25.7723 | 24.4078 | 25.6131 | 25.7723 | 24.4078 | 25.6131 | 25.7723 | 24.4077 | 25.6131 | 25.7723 | 24.4077 | 25.6131 | 25.7723 | 24.4077 | 25.6131
CA-Gladstone Rockhampton | 6103_Fisherman Landing-Boat Creek 66 kV | Power Factor | 0.95898 | 0.95899 | 0.95898 | 0.95898 | 0.95899 | 0.95898 | 0.95898 | 0.95899 | 0.95898 | 0.95898 | 0.95899 | 0.95898 | 0.95898 | 0.95899 | 0.95898
CA-Gladstone Rockhampton | 6103_Fisherman Landing-Boat Creek 66 kV | Rating (A) | 280 | 307 | 275 | 280 | 307 | 275 | 280 | 307 | 275 | 280 | 307 | 275 | 280 | 307 | 275
CA-Gladstone Rockhampton | 6103_Fisherman Landing-Boat Creek 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Gladstone Rockhampton | 6103_Fisherman Landing-Boat Creek 66 kV | Min Voltage at Constrained Conductor | 66.5559 | 65.8579 | 66.4597 | 66.567 | 65.8647 | 66.4653 | 66.4566 | 66.5922 | 66.3782 | 66.3469 | 66.4814 | 66.2835 | 66.339 | 66.473 | 66.2772
CA-Gladstone Rockhampton | 6103_Fisherman Landing-Boat Creek 66 kV | Contingency Outage | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV
CA-Gladstone Rockhampton | 6106_Shale Oil Tee - Shale Oil 66kV | % of Rated A | 0.4201% | 0.369% | 0.4166% | 0.42% | 0.3689% | 0.4166% | 0.4208% | 0.365% | 0.4172% | 0.4217% | 0.3657% | 0.4179% | 0.4217% | 0.3658% | 0.418%
CA-Gladstone Rockhampton | 6106_Shale Oil Tee - Shale Oil 66kV | Limiting Line Name | TR_LINE 21402_1 | TR_LINE 21402_1 | TR_LINE 21402_1 | TR_LINE 21402_1 | TR_LINE 21402_1 | TR_LINE 21402_1 | TR_LINE 21402_1 | TR_LINE 21402_1 | TR_LINE 21402_1 | TR_LINE 21402_1 | TR_LINE 21402_1 | TR_LINE 21402_1 | TR_LINE 21402_1 | TR_LINE 21402_1 | TR_LINE 21402_1
CA-Gladstone Rockhampton | 6106_Shale Oil Tee - Shale Oil 66kV | Loading (A) | 1.8442 | 1.771 | 1.6207 | 1.8439 | 1.7708 | 1.6205 | 1.8475 | 1.7521 | 1.623 | 1.851 | 1.7556 | 1.6258 | 1.8513 | 1.7558 | 1.6259
CA-Gladstone Rockhampton | 6106_Shale Oil Tee - Shale Oil 66kV | Loading (MVA) | 0.21408 | 0.20336 | 0.18787 | 0.21408 | 0.20336 | 0.18787 | 0.21408 | 0.20335 | 0.18787 | 0.21409 | 0.20336 | 0.18787 | 0.21409 | 0.20336 | 0.18787
CA-Gladstone Rockhampton | 6106_Shale Oil Tee - Shale Oil 66kV | Loading (MW) | 0.15809 | 0.15018 | 0.13877 | 0.15809 | 0.15018 | 0.13877 | 0.15809 | 0.15018 | 0.13877 | 0.15809 | 0.15018 | 0.13877 | 0.15809 | 0.15018 | 0.13877
CA-Gladstone Rockhampton | 6106_Shale Oil Tee - Shale Oil 66kV | Power Factor | 0.73844 | 0.73848 | 0.73863 | 0.73844 | 0.73848 | 0.73863 | 0.73843 | 0.73852 | 0.73862 | 0.73843 | 0.73851 | 0.73862 | 0.73843 | 0.73851 | 0.73862
CA-Gladstone Rockhampton | 6106_Shale Oil Tee - Shale Oil 66kV | Rating (A) | 439 | 480 | 389 | 439 | 480 | 389 | 439 | 480 | 389 | 439 | 480 | 389 | 439 | 480 | 389
CA-Gladstone Rockhampton | 6106_Shale Oil Tee - Shale Oil 66kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Gladstone Rockhampton | 6106_Shale Oil Tee - Shale Oil 66kV | Min Voltage at Constrained Conductor | 67.0193 | 66.2973 | 66.927 | 67.0314 | 66.3052 | 66.9335 | 66.9027 | 67.0082 | 66.8303 | 66.7742 | 66.878 | 66.7191 | 66.7652 | 66.8684 | 66.7118
CA-Gladstone Rockhampton | 6106_Shale Oil Tee - Shale Oil 66kV | Contingency Outage | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV
CA-Gladstone Rockhampton | 6109_Gladstone North - Clinton 66 kV | % of Rated A | 89.73% | 59.07% | 41.49% | 89.66% | 58.95% | 41.5% | 89.01% | 58.6% | 41.25% | 89.09% | 58.75% | 41.33% | 89.64% | 59.11% | 41.46%
CA-Gladstone Rockhampton | 6109_Gladstone North - Clinton 66 kV | Limiting Line Name | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 60722_1
CA-Gladstone Rockhampton | 6109_Gladstone North - Clinton 66 kV | Loading (A) | 325.7171 | 321.9258 | 191.2666 | 325.4761 | 321.2512 | 191.296 | 323.092 | 319.3852 | 190.1846 | 323.3943 | 320.1751 | 190.552 | 325.4102 | 322.1457 | 191.1278
CA-Gladstone Rockhampton | 6109_Gladstone North - Clinton 66 kV | Loading (MVA) | 38.534 | 38.2028 | 22.7257 | 38.5164 | 38.1337 | 22.7332 | 38.234 | 37.9124 | 22.6012 | 38.2734 | 38.0079 | 22.6458 | 38.4967 | 38.2271 | 22.7094
CA-Gladstone Rockhampton | 6109_Gladstone North - Clinton 66 kV | Loading (MW) | 38.5136 | 37.5092 | 21.7527 | 38.4814 | 37.3656 | 21.6889 | 38.1981 | 37.1364 | 21.5497 | 38.2308 | 37.2146 | 21.5754 | 38.4719 | 37.5179 | 21.7156
CA-Gladstone Rockhampton | 6109_Gladstone North - Clinton 66 kV | Power Factor | 0.99937 | 0.98128 | 0.9568 | 0.99896 | 0.97927 | 0.95366 | 0.99893 | 0.97894 | 0.95307 | 0.99875 | 0.97853 | 0.95233 | 0.99925 | 0.98088 | 0.95584
CA-Gladstone Rockhampton | 6109_Gladstone North - Clinton 66 kV | Rating (A) | 363 | 545 | 461 | 363 | 545 | 461 | 363 | 545 | 461 | 363 | 545 | 461 | 363 | 545 | 461
CA-Gladstone Rockhampton | 6109_Gladstone North - Clinton 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Gladstone Rockhampton | 6109_Gladstone North - Clinton 66 kV | Min Voltage at Constrained Conductor | 68.2458 | 68.4924 | 68.5991 | 68.2673 | 68.5145 | 68.6111 | 68.2674 | 68.5152 | 68.6112 | 68.2748 | 68.5188 | 68.6141 | 68.2447 | 68.4897 | 68.5995
CA-Gladstone Rockhampton | 6109_Gladstone North - Clinton 66 kV | Contingency Outage | 6111_Gladstone North - Port Curtis 66 kV | 6111_Gladstone North - Port Curtis 66 kV | 6111_Gladstone North - Port Curtis 66 kV | 6111_Gladstone North - Port Curtis 66 kV | 6111_Gladstone North - Port Curtis 66 kV | 6111_Gladstone North - Port Curtis 66 kV | 6111_Gladstone North - Port Curtis 66 kV | 6111_Gladstone North - Port Curtis 66 kV | 6111_Gladstone North - Port Curtis 66 kV | 6111_Gladstone North - Port Curtis 66 kV | 6111_Gladstone North - Port Curtis 66 kV | 6111_Gladstone North - Port Curtis 66 kV | 6111_Gladstone North - Port Curtis 66 kV | 6111_Gladstone North - Port Curtis 66 kV | 6111_Gladstone North - Port Curtis 66 kV
CA-Gladstone Rockhampton | 6196_Callide Mine 66 kV | % of Rated A | 50.43% | 38% | 31.81% | 50.42% | 38% | 31.81% | 50.42% | 37.99% | 31.81% | 50.42% | 38% | 31.81% | 50.43% | 38% | 31.81%
CA-Gladstone Rockhampton | 6196_Callide Mine 66 kV | Limiting Line Name | TR_LINE 22328_1 | TR_LINE 22328_1 | TR_LINE 22328_1 | TR_LINE 22328_1 | TR_LINE 22328_1 | TR_LINE 22328_1 | TR_LINE 22328_1 | TR_LINE 22328_1 | TR_LINE 22328_1 | TR_LINE 22328_1 | TR_LINE 22328_1 | TR_LINE 22328_1 | TR_LINE 22328_1 | TR_LINE 22328_1 | TR_LINE 22328_1
CA-Gladstone Rockhampton | 6196_Callide Mine 66 kV | Loading (A) | 67.5763 | 68.7815 | 55.6665 | 67.5688 | 68.7747 | 55.6643 | 67.5665 | 68.7709 | 55.6627 | 67.5693 | 68.7735 | 55.6628 | 67.5742 | 68.778 | 55.6638
CA-Gladstone Rockhampton | 6196_Callide Mine 66 kV | Loading (MVA) | 7.9133 | 8.1627 | 6.6407 | 7.9133 | 8.1627 | 6.6407 | 7.9133 | 8.1627 | 6.6407 | 7.9133 | 8.1627 | 6.6407 | 7.9133 | 8.1627 | 6.6407
CA-Gladstone Rockhampton | 6196_Callide Mine 66 kV | Loading (MW) | 7.6287 | 7.8691 | 6.4019 | 7.6287 | 7.8691 | 6.4019 | 7.6287 | 7.8691 | 6.4019 | 7.6287 | 7.8691 | 6.4019 | 7.6287 | 7.8691 | 6.4019
CA-Gladstone Rockhampton | 6196_Callide Mine 66 kV | Power Factor | 0.964 | 0.964 | 0.964 | 0.964 | 0.964 | 0.964 | 0.964 | 0.964 | 0.964 | 0.964 | 0.964 | 0.964 | 0.964 | 0.964 | 0.964
CA-Gladstone Rockhampton | 6196_Callide Mine 66 kV | Rating (A) | 134 | 181 | 175 | 134 | 181 | 175 | 134 | 181 | 175 | 134 | 181 | 175 | 134 | 181 | 175
CA-Gladstone Rockhampton | 6196_Callide Mine 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Gladstone Rockhampton | 6196_Callide Mine 66 kV | Min Voltage at Constrained Conductor | 67.6054 | 68.5136 | 68.8731 | 67.6129 | 68.5204 | 68.8759 | 67.6153 | 68.5242 | 68.8779 | 67.6124 | 68.5216 | 68.8778 | 67.6076 | 68.5172 | 68.8765
CA-Gladstone Rockhampton | 6196_Callide Mine 66 kV | Contingency Outage | 6027_TDM Mine 66 kV | 6027_TDM Mine 66 kV | 6027_TDM Mine 66 kV | 6027_TDM Mine 66 kV | 6027_TDM Mine 66 kV | 6027_TDM Mine 66 kV | 6027_TDM Mine 66 kV | 6027_TDM Mine 66 kV | 6027_TDM Mine 66 kV | 6027_TDM Mine 66 kV | 6027_TDM Mine 66 kV | 6027_TDM Mine 66 kV | 6027_TDM Mine 66 kV | 6027_TDM Mine 66 kV | 6027_TDM Mine 66 kV
CA-Gladstone Rockhampton | 6298_Tanby - Yeppoon 66 kV | % of Rated A | 69.5% | 67.21% | 35.36% | 69.12% | 65.54% | 35.22% | 69.27% | 66.99% | 35.25% | 68.21% | 67.21% | 35.55% | 70.97% | 67.6% | 35.98%
CA-Gladstone Rockhampton | 6298_Tanby - Yeppoon 66 kV | Limiting Line Name | TR_LINE 22239_1 | TR_LINE 22239_1 | TR_LINE 112499_1 | TR_LINE 22239_1 | TR_LINE 22239_1 | TR_LINE 112499_1 | TR_LINE 22239_1 | TR_LINE 22239_1 | TR_LINE 112499_1 | TR_LINE 22239_1 | TR_LINE 22239_1 | TR_LINE 112499_1 | TR_LINE 22239_1 | TR_LINE 22239_1 | TR_LINE 112499_1
CA-Gladstone Rockhampton | 6298_Tanby - Yeppoon 66 kV | Loading (A) | 262.6941 | 278.9328 | 119.1494 | 261.2819 | 271.9741 | 118.6882 | 261.825 | 278.0235 | 118.7812 | 257.8208 | 278.9008 | 119.8012 | 268.2707 | 280.5322 | 121.2488
CA-Gladstone Rockhampton | 6298_Tanby - Yeppoon 66 kV | Loading (MVA) | 26.428 | 27.579 | 13.4757 | 26.3327 | 27.486 | 13.4297 | 26.3341 | 27.4811 | 13.4293 | 26.5167 | 27.6852 | 13.521 | 26.7995 | 27.9761 | 13.659
CA-Gladstone Rockhampton | 6298_Tanby - Yeppoon 66 kV | Loading (MW) | 26.3727 | 27.5157 | 13.4372 | 26.2795 | 27.4198 | 13.3902 | 26.2798 | 27.4189 | 13.3903 | 26.4645 | 27.6141 | 13.4844 | 26.7436 | 27.9039 | 13.6255
CA-Gladstone Rockhampton | 6298_Tanby - Yeppoon 66 kV | Power Factor | 0.99791 | 0.99771 | 0.99714 | 0.99798 | 0.99759 | 0.99705 | 0.99794 | 0.99774 | 0.99708 | 0.99803 | 0.99743 | 0.99728 | 0.99791 | 0.99742 | 0.99753
CA-Gladstone Rockhampton | 6298_Tanby - Yeppoon 66 kV | Rating (A) | 378 | 415 | 337 | 378 | 415 | 337 | 378 | 415 | 337 | 378 | 415 | 337 | 378 | 415 | 337
CA-Gladstone Rockhampton | 6298_Tanby - Yeppoon 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Gladstone Rockhampton | 6298_Tanby - Yeppoon 66 kV | Min Voltage at Constrained Conductor | 58.0783 | 57.0787 | 65.2844 | 58.1817 | 58.3421 | 65.3146 | 58.064 | 57.0621 | 65.2617 | 59.3748 | 57.305 | 65.1477 | 57.6701 | 57.5705 | 65.0266
CA-Gladstone Rockhampton | 6298_Tanby - Yeppoon 66 kV | Contingency Outage | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6051_Parkhurst - Keppel 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6051_Parkhurst - Keppel 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6051_Parkhurst - Keppel 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6051_Parkhurst - Keppel 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6051_Parkhurst - Keppel 66 kV
CA-Gladstone Rockhampton | 6310_Lakes Creek - Berserker 66 kV | % of Rated A | 66.32% | 74.72% | 37.9% | 66.22% | 74.45% | 37.76% | 69.81% | 75.43% | 37.83% | 68.65% | 77.17% | 38.12% | 73.05% | 78.85% | 38.74%
CA-Gladstone Rockhampton | 6310_Lakes Creek - Berserker 66 kV | Limiting Line Name | TR_CABLE 51_1 | TR_CABLE 51_1 | TR_LINE 20950_1 | TR_CABLE 51_1 | TR_CABLE 51_1 | TR_LINE 20950_1 | TR_CABLE 51_1 | TR_CABLE 51_1 | TR_LINE 20950_1 | TR_CABLE 51_1 | TR_CABLE 51_1 | TR_LINE 20950_1 | TR_CABLE 51_1 | TR_CABLE 51_1 | TR_LINE 20950_1
CA-Gladstone Rockhampton | 6310_Lakes Creek - Berserker 66 kV | Loading (A) | 246.7031 | 277.9408 | 140.9774 | 246.3393 | 276.9603 | 140.4501 | 259.6953 | 280.582 | 140.7435 | 255.3733 | 287.0575 | 141.7983 | 271.7503 | 293.3374 | 144.1205
CA-Gladstone Rockhampton | 6310_Lakes Creek - Berserker 66 kV | Loading (MVA) | 28.5655 | 32.143 | 16.8225 | 28.5454 | 32.5152 | 16.7636 | 30.0603 | 32.4383 | 16.7926 | 30.0813 | 33.3638 | 16.9106 | 31.4249 | 34.2882 | 17.1809
CA-Gladstone Rockhampton | 6310_Lakes Creek - Berserker 66 kV | Loading (MW) | 28.3014 | 31.7036 | 16.4939 | 28.2881 | 31.8559 | 16.4317 | 29.4537 | 31.9809 | 16.4641 | 29.8231 | 32.7279 | 16.5935 | 30.8743 | 33.4767 | 16.8833
CA-Gladstone Rockhampton | 6310_Lakes Creek - Berserker 66 kV | Power Factor | 0.99074 | 0.98632 | 0.98042 | 0.99097 | 0.97971 | 0.98015 | 0.97981 | 0.98589 | 0.98039 | 0.9914 | 0.98093 | 0.9812 | 0.98247 | 0.97632 | 0.98263
CA-Gladstone Rockhampton | 6310_Lakes Creek - Berserker 66 kV | Rating (A) | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372 | 372
CA-Gladstone Rockhampton | 6310_Lakes Creek - Berserker 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Gladstone Rockhampton | 6310_Lakes Creek - Berserker 66 kV | Min Voltage at Constrained Conductor | 66.8508 | 66.7688 | 68.8813 | 66.9023 | 67.7811 | 68.8981 | 66.8295 | 66.7479 | 68.8732 | 68.0082 | 67.1036 | 68.841 | 66.7642 | 67.4864 | 68.8139
CA-Gladstone Rockhampton | 6310_Lakes Creek - Berserker 66 kV | Contingency Outage | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6096_Egan's Hill - Lakes Creek 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6096_Egan's Hill - Lakes Creek 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6096_Egan's Hill - Lakes Creek 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6096_Egan's Hill - Lakes Creek 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6096_Egan's Hill - Lakes Creek 66 kV
CA-Gladstone Rockhampton | 7290_Boat Creek - Yarwun 132 kV | % of Rated A | 22.36% | 19% | 24.55% | 22.32% | 18.96% | 24.51% | 23.01% | 19.59% | 25.16% | 23.71% | 20.24% | 25.81% | 23.75% | 20.28% | 25.85%
CA-Gladstone Rockhampton | 7290_Boat Creek - Yarwun 132 kV | Limiting Line Name | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1
CA-Gladstone Rockhampton | 7290_Boat Creek - Yarwun 132 kV | Loading (A) | 198.8115 | 186.9219 | 205.9889 | 198.4445 | 186.5545 | 205.6711 | 204.5681 | 192.7866 | 211.0762 | 210.7838 | 199.1568 | 216.5766 | 211.1579 | 199.5416 | 216.9057
CA-Gladstone Rockhampton | 7290_Boat Creek - Yarwun 132 kV | Loading (MVA) | 47.2384 | 44.4265 | 48.9134 | 47.1557 | 44.3404 | 48.8389 | 48.5907 | 45.8037 | 50.1115 | 50.0489 | 47.3006 | 51.4022 | 50.1357 | 47.3898 | 51.4789
CA-Gladstone Rockhampton | 7290_Boat Creek - Yarwun 132 kV | Loading (MW) | 42.9674 | 40.4301 | 44.468 | 42.9037 | 40.3645 | 44.4113 | 43.9892 | 41.477 | 45.3756 | 45.0768 | 42.5957 | 46.3415 | 45.1409 | 42.6616 | 46.3984
CA-Gladstone Rockhampton | 7290_Boat Creek - Yarwun 132 kV | Power Factor | 0.90956 | 0.91001 | 0.9091 | 0.90981 | 0.9103 | 0.90932 | 0.90528 | 0.90551 | 0.90548 | 0.90064 | 0.90051 | 0.90154 | 0.90036 | 0.9002 | 0.9013
CA-Gladstone Rockhampton | 7290_Boat Creek - Yarwun 132 kV | Rating (A) | 889 | 984 | 839 | 889 | 984 | 839 | 889 | 984 | 839 | 889 | 984 | 839 | 889 | 984 | 839
CA-Gladstone Rockhampton | 7290_Boat Creek - Yarwun 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Gladstone Rockhampton | 7290_Boat Creek - Yarwun 132 kV | Min Voltage at Constrained Conductor | 137.1768 | 137.2192 | 137.0903 | 137.1897 | 137.2232 | 137.0932 | 137.132 | 137.1683 | 137.0623 | 137.0811 | 137.1193 | 137.0211 | 137.0756 | 137.1129 | 137.0174
CA-Gladstone Rockhampton | 7290_Boat Creek - Yarwun 132 kV | Contingency Outage | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV | 7291_Boat Creek - Yarwun 132 kV
CA-Gladstone Rockhampton | 7291_Boat Creek - Yarwun 132 kV | % of Rated A | 22.36% | 18.99% | 24.55% | 22.32% | 18.96% | 24.51% | 23.01% | 19.59% | 25.15% | 23.71% | 20.24% | 25.81% | 23.75% | 20.28% | 25.85%
CA-Gladstone Rockhampton | 7291_Boat Creek - Yarwun 132 kV | Limiting Line Name | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1
CA-Gladstone Rockhampton | 7291_Boat Creek - Yarwun 132 kV | Loading (A) | 198.7902 | 186.8977 | 205.9598 | 198.4178 | 186.5305 | 205.6421 | 204.539 | 192.7609 | 211.0451 | 210.752 | 199.1286 | 216.5432 | 211.126 | 199.5133 | 216.8721
CA-Gladstone Rockhampton | 7291_Boat Creek - Yarwun 132 kV | Loading (MVA) | 47.2357 | 44.423 | 48.909 | 47.1517 | 44.337 | 48.8346 | 48.5863 | 45.7999 | 50.1067 | 50.044 | 47.2964 | 51.397 | 50.1308 | 47.3856 | 51.4737
CA-Gladstone Rockhampton | 7291_Boat Creek - Yarwun 132 kV | Loading (MW) | 42.9669 | 40.4296 | 44.4673 | 42.9031 | 40.3639 | 44.4106 | 43.9886 | 41.4764 | 45.3749 | 45.0761 | 42.5951 | 46.3408 | 45.1402 | 42.661 | 46.3977
CA-Gladstone Rockhampton | 7291_Boat Creek - Yarwun 132 kV | Power Factor | 0.90961 | 0.91008 | 0.90917 | 0.90988 | 0.91036 | 0.9094 | 0.90535 | 0.90558 | 0.90555 | 0.90072 | 0.90058 | 0.90162 | 0.90044 | 0.90028 | 0.90138
CA-Gladstone Rockhampton | 7291_Boat Creek - Yarwun 132 kV | Rating (A) | 889 | 984 | 839 | 889 | 984 | 839 | 889 | 984 | 839 | 889 | 984 | 839 | 889 | 984 | 839
CA-Gladstone Rockhampton | 7291_Boat Creek - Yarwun 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Gladstone Rockhampton | 7291_Boat Creek - Yarwun 132 kV | Min Voltage at Constrained Conductor | 137.1846 | 137.2266 | 137.0985 | 137.1975 | 137.2305 | 137.1014 | 137.1403 | 137.176 | 137.0709 | 137.0897 | 137.1274 | 137.03 | 137.0842 | 137.121 | 137.0263
CA-Gladstone Rockhampton | 7291_Boat Creek - Yarwun 132 kV | Contingency Outage | 7290_Boat Creek - Yarwun 132 kV | 7290_Boat Creek - Yarwun 132 kV | 7290_Boat Creek - Yarwun 132 kV | 7290_Boat Creek - Yarwun 132 kV | 7290_Boat Creek - Yarwun 132 kV | 7290_Boat Creek - Yarwun 132 kV | 7290_Boat Creek - Yarwun 132 kV | 7290_Boat Creek - Yarwun 132 kV | 7290_Boat Creek - Yarwun 132 kV | 7290_Boat Creek - Yarwun 132 kV | 7290_Boat Creek - Yarwun 132 kV | 7290_Boat Creek - Yarwun 132 kV | 7290_Boat Creek - Yarwun 132 kV | 7290_Boat Creek - Yarwun 132 kV | 7290_Boat Creek - Yarwun 132 kV
CA-Gladstone Rockhampton | 7414_Gladstone North - Wiggins Is 132 kV | % of Rated A | 2.477% | 2.653% | 2.035% | 2.476% | 2.653% | 2.035% | 2.476% | 2.653% | 2.035% | 2.476% | 2.653% | 2.035% | 2.477% | 2.653% | 2.035%
CA-Gladstone Rockhampton | 7414_Gladstone North - Wiggins Is 132 kV | Limiting Line Name | TR_LINE 193931_1 | TR_LINE 193931_1 | TR_LINE 193931_1 | TR_LINE 193931_1 | TR_LINE 193931_1 | TR_LINE 193931_1 | TR_LINE 193931_1 | TR_LINE 193931_1 | TR_LINE 193931_1 | TR_LINE 193931_1 | TR_LINE 193931_1 | TR_LINE 193931_1 | TR_LINE 193931_1 | TR_LINE 193931_1 | TR_LINE 193931_1
CA-Gladstone Rockhampton | 7414_Gladstone North - Wiggins Is 132 kV | Loading (A) | 19.9607 | 23.9545 | 15.1626 | 19.9596 | 23.9528 | 15.1619 | 19.9601 | 23.9531 | 15.162 | 19.9598 | 23.9532 | 15.1619 | 19.9628 | 23.9568 | 15.1631
CA-Gladstone Rockhampton | 7414_Gladstone North - Wiggins Is 132 kV | Loading (MVA) | 4.8412 | 5.8073 | 3.6805 | 4.8412 | 5.8073 | 3.6805 | 4.8412 | 5.8073 | 3.6805 | 4.8412 | 5.8073 | 3.6805 | 4.8412 | 5.8073 | 3.6805
CA-Gladstone Rockhampton | 7414_Gladstone North - Wiggins Is 132 kV | Loading (MW) | 4.7983 | 5.7524 | 3.6509 | 4.7983 | 5.7524 | 3.6509 | 4.7983 | 5.7524 | 3.6509 | 4.7983 | 5.7524 | 3.6509 | 4.7983 | 5.7524 | 3.6509
CA-Gladstone Rockhampton | 7414_Gladstone North - Wiggins Is 132 kV | Power Factor | 0.99112 | 0.99055 | 0.99197 | 0.99112 | 0.99055 | 0.99197 | 0.99112 | 0.99055 | 0.99197 | 0.99112 | 0.99055 | 0.99197 | 0.99112 | 0.99055 | 0.99197
CA-Gladstone Rockhampton | 7414_Gladstone North - Wiggins Is 132 kV | Rating (A) | 806 | 903 | 745 | 806 | 903 | 745 | 806 | 903 | 745 | 806 | 903 | 745 | 806 | 903 | 745
CA-Gladstone Rockhampton | 7414_Gladstone North - Wiggins Is 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Gladstone Rockhampton | 7414_Gladstone North - Wiggins Is 132 kV | Min Voltage at Constrained Conductor | 140.0297 | 139.9667 | 140.1423 | 140.0375 | 139.9769 | 140.1481 | 140.0341 | 139.9751 | 140.1475 | 140.0356 | 139.9743 | 140.1482 | 140.0152 | 139.9536 | 140.1378
CA-Gladstone Rockhampton | 7414_Gladstone North - Wiggins Is 132 kV | Contingency Outage | 7415_Gladstone North - Wiggins Is 132 kV | 7415_Gladstone North - Wiggins Is 132 kV | 7415_Gladstone North - Wiggins Is 132 kV | 7415_Gladstone North - Wiggins Is 132 kV | 7415_Gladstone North - Wiggins Is 132 kV | 7415_Gladstone North - Wiggins Is 132 kV | 7415_Gladstone North - Wiggins Is 132 kV | 7415_Gladstone North - Wiggins Is 132 kV | 7415_Gladstone North - Wiggins Is 132 kV | 7415_Gladstone North - Wiggins Is 132 kV | 7415_Gladstone North - Wiggins Is 132 kV | 7415_Gladstone North - Wiggins Is 132 kV | 7415_Gladstone North - Wiggins Is 132 kV | 7415_Gladstone North - Wiggins Is 132 kV | 7415_Gladstone North - Wiggins Is 132 kV
CA-Gladstone Rockhampton | 7415_Gladstone North - Wiggins Is 132 kV | % of Rated A | 2.249% | 2.438% | 1.811% | 2.249% | 2.438% | 1.811% | 2.249% | 2.438% | 1.811% | 2.249% | 2.438% | 1.811% | 2.249% | 2.438% | 1.811%
CA-Gladstone Rockhampton | 7415_Gladstone North - Wiggins Is 132 kV | Limiting Line Name | TR_LINE 184976_2 | TR_LINE 184976_2 | TR_LINE 184976_2 | TR_LINE 184976_2 | TR_LINE 184976_2 | TR_LINE 184976_2 | TR_LINE 184976_2 | TR_LINE 184976_2 | TR_LINE 184976_2 | TR_LINE 184976_2 | TR_LINE 184976_2 | TR_LINE 184976_2 | TR_LINE 184976_2 | TR_LINE 184976_2 | TR_LINE 184976_2
CA-Gladstone Rockhampton | 7415_Gladstone North - Wiggins Is 132 kV | Loading (A) | 19.9946 | 23.9892 | 15.1953 | 19.9934 | 23.9875 | 15.1947 | 19.9939 | 23.9878 | 15.1948 | 19.9937 | 23.9879 | 15.1947 | 19.9966 | 23.9915 | 15.1958
CA-Gladstone Rockhampton | 7415_Gladstone North - Wiggins Is 132 kV | Loading (MVA) | 4.8493 | 5.8154 | 3.6883 | 4.8493 | 5.8154 | 3.6883 | 4.8493 | 5.8154 | 3.6883 | 4.8493 | 5.8154 | 3.6883 | 4.8493 | 5.8154 | 3.6883
CA-Gladstone Rockhampton | 7415_Gladstone North - Wiggins Is 132 kV | Loading (MW) | 4.7982 | 5.7524 | 3.6509 | 4.7982 | 5.7524 | 3.6509 | 4.7982 | 5.7524 | 3.6509 | 4.7982 | 5.7524 | 3.6509 | 4.7982 | 5.7524 | 3.6509
CA-Gladstone Rockhampton | 7415_Gladstone North - Wiggins Is 132 kV | Power Factor | 0.98945 | 0.98913 | 0.98984 | 0.98945 | 0.98913 | 0.98984 | 0.98945 | 0.98913 | 0.98984 | 0.98945 | 0.98913 | 0.98984 | 0.98945 | 0.98913 | 0.98984
CA-Gladstone Rockhampton | 7415_Gladstone North - Wiggins Is 132 kV | Rating (A) | 889 | 984 | 839 | 889 | 984 | 839 | 889 | 984 | 839 | 889 | 984 | 839 | 889 | 984 | 839
CA-Gladstone Rockhampton | 7415_Gladstone North - Wiggins Is 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Gladstone Rockhampton | 7415_Gladstone North - Wiggins Is 132 kV | Min Voltage at Constrained Conductor | 140.0248 | 139.9608 | 140.1386 | 140.0326 | 139.9709 | 140.1444 | 140.0292 | 139.9691 | 140.1438 | 140.0307 | 139.9684 | 140.1445 | 140.0103 | 139.9477 | 140.1341
CA-Gladstone Rockhampton | 7415_Gladstone North - Wiggins Is 132 kV | Contingency Outage | 7414_Gladstone North - Wiggins Is 132 kV | 7414_Gladstone North - Wiggins Is 132 kV | 7414_Gladstone North - Wiggins Is 132 kV | 7414_Gladstone North - Wiggins Is 132 kV | 7414_Gladstone North - Wiggins Is 132 kV | 7414_Gladstone North - Wiggins Is 132 kV | 7414_Gladstone North - Wiggins Is 132 kV | 7414_Gladstone North - Wiggins Is 132 kV | 7414_Gladstone North - Wiggins Is 132 kV | 7414_Gladstone North - Wiggins Is 132 kV | 7414_Gladstone North - Wiggins Is 132 kV | 7414_Gladstone North - Wiggins Is 132 kV | 7414_Gladstone North - Wiggins Is 132 kV | 7414_Gladstone North - Wiggins Is 132 kV | 7414_Gladstone North - Wiggins Is 132 kV
CA-Gladstone Rockhampton | AW113_Awoonga Rurals 11 kV | % of Rated A | 5.693% | 4.34% | 3.367% | 5.723% | 4.314% | 3.372% | 5.709% | 4.318% | 3.336% | 5.717% | 4.316% | 3.336% | 5.717% | 4.331% | 3.334%
CA-Gladstone Rockhampton | AW113_Awoonga Rurals 11 kV | Limiting Line Name | HV_LINE 235473_1 | HV_LINE 235473_1 | HV_LINE 235473_1 | HV_LINE 235473_1 | HV_LINE 235473_1 | HV_LINE 235473_1 | HV_LINE 235473_1 | HV_LINE 235473_1 | HV_LINE 235473_1 | HV_LINE 235473_1 | HV_LINE 235473_1 | HV_LINE 235473_1 | HV_LINE 235473_1 | HV_LINE 235473_1 | HV_LINE 235473_1
CA-Gladstone Rockhampton | AW113_Awoonga Rurals 11 kV | Loading (A) | 12.0698 | 12.8472 | 8.2821 | 12.1318 | 12.7701 | 8.2961 | 12.1041 | 12.7809 | 8.2056 | 12.1206 | 12.7767 | 8.2061 | 12.1203 | 12.8199 | 8.2025
CA-Gladstone Rockhampton | AW113_Awoonga Rurals 11 kV | Loading (MVA) | 0.23062 | 0.24475 | 0.15887 | 0.23067 | 0.2447 | 0.15887 | 0.23065 | 0.24471 | 0.15882 | 0.23066 | 0.2447 | 0.15882 | 0.23066 | 0.24473 | 0.15882
CA-Gladstone Rockhampton | AW113_Awoonga Rurals 11 kV | Loading (MW) | 0.19873 | 0.22086 | 0.14256 | 0.19874 | 0.22086 | 0.14256 | 0.19874 | 0.22086 | 0.14256 | 0.19874 | 0.22086 | 0.14256 | 0.19874 | 0.22086 | 0.14256
CA-Gladstone Rockhampton | AW113_Awoonga Rurals 11 kV | Power Factor | 0.86157 | 0.90227 | 0.89727 | 0.86141 | 0.90242 | 0.89722 | 0.86148 | 0.9024 | 0.89752 | 0.86144 | 0.90241 | 0.89751 | 0.86144 | 0.90233 | 0.89753
CA-Gladstone Rockhampton | AW113_Awoonga Rurals 11 kV | Rating (A) | 212 | 296 | 246 | 212 | 296 | 246 | 212 | 296 | 246 | 212 | 296 | 246 | 212 | 296 | 246
CA-Gladstone Rockhampton | AW113_Awoonga Rurals 11 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Gladstone Rockhampton | AW113_Awoonga Rurals 11 kV | Min Voltage at Constrained Conductor | 11.0315 | 10.9985 | 11.0747 | 10.9774 | 11.0627 | 11.0566 | 11.0016 | 11.0537 | 11.1747 | 10.9871 | 11.0572 | 11.174 | 10.9875 | 11.0211 | 11.1787
CA-Gladstone Rockhampton | AW113_Awoonga Rurals 11 kV | Contingency Outage | 6020_Gladstone South - BORE 66 kV | 6020_Gladstone South - BORE 66 kV | 6022_Gladstone South - Calliope 66 kV | 6020_Gladstone South - BORE 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV | 6032_Boyne Residential Tee-Awoonga 66 kV | 6022_Gladstone South - Calliope 66 kV | 6109_Gladstone North - Clinton 66 kV | 6024_Awoonga - Calliope 66kV | 6022_Gladstone South - Calliope 66 kV | 6102_Boat Creek - Yarwun 66 kV | 6032_Boyne Residential Tee-Awoonga 66 kV | 6022_Gladstone South - Calliope 66 kV | 6022_Gladstone South - Calliope 66 kV
CA-Gladstone Rockhampton | CN101_Base Hospital No.1 11kV | % of Rated A | 0.1947% | 0.1947% | 0.1948% | 0.1947% | 0.1941% | 0.1946% | 0.1947% | 0.1947% | 0.1947% | 0.1946% | 0.1947% | 0.1946% | 0.1947% | 0.1947% | 0.1945%
CA-Gladstone Rockhampton | CN101_Base Hospital No.1 11kV | Limiting Line Name | HV_CABLE 393680_1 | HV_CABLE 393680_1 | HV_CABLE 393680_1 | HV_CABLE 393680_1 | HV_CABLE 393680_1 | HV_CABLE 393680_1 | HV_CABLE 393680_1 | HV_CABLE 393680_1 | HV_CABLE 393680_1 | HV_CABLE 393680_1 | HV_CABLE 393680_1 | HV_CABLE 393680_1 | HV_CABLE 393680_1 | HV_CABLE 393680_1 | HV_CABLE 393680_1
CA-Gladstone Rockhampton | CN101_Base Hospital No.1 11kV | Loading (A) | 0.77889 | 0.77886 | 0.77901 | 0.77862 | 0.77647 | 0.77848 | 0.7788 | 0.77882 | 0.77889 | 0.77836 | 0.77862 | 0.77837 | 0.77892 | 0.77867 | 0.77811
CA-Gladstone Rockhampton | CN101_Base Hospital No.1 11kV | Loading (MVA) | 0.014686 | 0.014684 | 0.01469 | 0.014675 | 0.014595 | 0.01467 | 0.014682 | 0.014683 | 0.014686 | 0.014666 | 0.014676 | 0.014666 | 0.014687 | 0.014677 | 0.014656
CA-Gladstone Rockhampton | CN101_Base Hospital No.1 11kV | Loading (MW) | 0.0041161 | 0.0041158 | 0.0041174 | 0.0041133 | 0.0040906 | 0.0041118 | 0.0041152 | 0.0041154 | 0.0041161 | 0.0041105 | 0.0041133 | 0.0041106 | 0.0041165 | 0.0041138 | 0.0041079
CA-Gladstone Rockhampton | CN101_Base Hospital No.1 11kV | Power Factor | 0.27966 | 0.27966 | 0.27966 | 0.27966 | 0.27966 | 0.27966 | 0.27966 | 0.27966 | 0.27966 | 0.27966 | 0.27966 | 0.27966 | 0.27966 | 0.27966 | 0.27966
CA-Gladstone Rockhampton | CN101_Base Hospital No.1 11kV | Rating (A) | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400
CA-Gladstone Rockhampton | CN101_Base Hospital No.1 11kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Gladstone Rockhampton | CN101_Base Hospital No.1 11kV | Min Voltage at Constrained Conductor | 10.8857 | 10.8852 | 10.8873 | 10.8819 | 10.8519 | 10.8799 | 10.8845 | 10.8847 | 10.8857 | 10.8783 | 10.882 | 10.8784 | 10.8862 | 10.8826 | 10.8748
CA-Gladstone Rockhampton | CN101_Base Hospital No.1 11kV | Contingency Outage | 6089_QMAG Tee - QMAG 66 kV | 6089_QMAG Tee - QMAG 66 kV | 6089_QMAG Tee - QMAG 66 kV | 6094_Malchi Tee - Malchi 66 kV | 6094_Malchi Tee - Malchi 66 kV | 6094_Malchi Tee - Malchi 66 kV | 6094_Malchi Tee - Malchi 66 kV | 6089_QMAG Tee - QMAG 66 kV | 6089_QMAG Tee - QMAG 66 kV | 6091_Egan's Hill - Gavial 66 kV | 6053_Parkhurst - Pandoin 66 kV | 6089_QMAG Tee - QMAG 66 kV | 6094_Malchi Tee - Malchi 66 kV | 6091_Egan's Hill - Gavial 66 kV | 6089_QMAG Tee - QMAG 66 kV
CA-Gladstone Rockhampton | CN109_Base Hospital No.2 11kV | % of Rated A | 0.8539% | 1.298% | 0.7235% | 0.8555% | 1.302% | 0.7278% | 0.8582% | 1.298% | 0.7238% | 0.8616% | 1.298% | 0.7245% | 0.8579% | 1.298% | 0.7247%
CA-Gladstone Rockhampton | CN109_Base Hospital No.2 11kV | Limiting Line Name | HV_CABLE 536964_1 | HV_CABLE 536964_1 | HV_CABLE 536964_1 | HV_CABLE 536964_1 | HV_CABLE 536964_1 | HV_CABLE 536964_1 | HV_CABLE 536964_1 | HV_CABLE 536964_1 | HV_CABLE 536964_1 | HV_CABLE 536964_1 | HV_CABLE 536964_1 | HV_CABLE 536964_1 | HV_CABLE 536964_1 | HV_CABLE 536964_1 | HV_CABLE 536964_1
CA-Gladstone Rockhampton | CN109_Base Hospital No.2 11kV | Loading (A) | 4.1328 | 6.2828 | 3.5018 | 4.1407 | 6.3019 | 3.5223 | 4.1539 | 6.2828 | 3.503 | 4.17 | 6.2832 | 3.5064 | 4.1522 | 6.2828 | 3.5076
CA-Gladstone Rockhampton | CN109_Base Hospital No.2 11kV | Loading (MVA) | 0.077175 | 0.11707 | 0.065675 | 0.077166 | 0.11706 | 0.065648 | 0.077152 | 0.11707 | 0.065674 | 0.077134 | 0.11707 | 0.065669 | 0.077153 | 0.11707 | 0.065668
CA-Gladstone Rockhampton | CN109_Base Hospital No.2 11kV | Loading (MW) | 0.071183 | 0.10937 | 0.061012 | 0.07118 | 0.10937 | 0.061003 | 0.071176 | 0.10937 | 0.061012 | 0.07117 | 0.10937 | 0.06101 | 0.071176 | 0.10937 | 0.06101
CA-Gladstone Rockhampton | CN109_Base Hospital No.2 11kV | Power Factor | 0.92034 | 0.93288 | 0.92661 | 0.92042 | 0.93294 | 0.92689 | 0.92054 | 0.93288 | 0.92663 | 0.9207 | 0.93288 | 0.92667 | 0.92053 | 0.93288 | 0.92669
CA-Gladstone Rockhampton | CN109_Base Hospital No.2 11kV | Rating (A) | 484 | 484 | 484 | 484 | 484 | 484 | 484 | 484 | 484 | 484 | 484 | 484 | 484 | 484 | 484
CA-Gladstone Rockhampton | CN109_Base Hospital No.2 11kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Gladstone Rockhampton | CN109_Base Hospital No.2 11kV | Min Voltage at Constrained Conductor | 10.7812 | 10.7584 | 10.8279 | 10.7596 | 10.725 | 10.7604 | 10.7234 | 10.7584 | 10.8241 | 10.6796 | 10.7578 | 10.8129 | 10.7279 | 10.7584 | 10.8089
CA-Gladstone Rockhampton | CN109_Base Hospital No.2 11kV | Contingency Outage | 6005_Rockhampton Glenmore-Canning 66 kV | 6094_Malchi Tee - Malchi 66 kV | 6005_Rockhampton Glenmore-Canning 66 kV | 6089_QMAG Tee - QMAG 66 kV | 6005_Rockhampton Glenmore-Canning 66 kV | 6089_QMAG Tee - QMAG 66 kV | 6005_Rockhampton Glenmore-Canning 66 kV | 6094_Malchi Tee - Malchi 66 kV | 6005_Rockhampton Glenmore-Canning 66 kV | 6005_Rockhampton Glenmore-Canning 66 kV | 6091_Egan's Hill - Gavial 66 kV | 6005_Rockhampton Glenmore-Canning 66 kV | 6005_Rockhampton Glenmore-Canning 66 kV | 6005_Rockhampton Glenmore-Canning 66 kV | 6005_Rockhampton Glenmore-Canning 66 kV
CA-Gladstone Rockhampton | 6096_Egan's Hill - Lakes Creek 66 kV | % of Rated A | 118.1% | 105.4% | 65.36% | 116.4% | 104.5% | 64.69% | 115.3% | 103.5% | 64.37% | 113.6% | 103.5% | 64.26% | 115.9% | 104.9% | 64.92%
CA-Gladstone Rockhampton | 6096_Egan's Hill - Lakes Creek 66 kV | Limiting Line Name | TR_LINE 19756_1 | TR_LINE 19756_1 | TR_LINE 19756_1 | TR_LINE 19756_1 | TR_LINE 19756_1 | TR_LINE 19756_1 | TR_LINE 19756_1 | TR_LINE 19756_1 | TR_LINE 19756_1 | TR_LINE 19756_1 | TR_LINE 19756_1 | TR_LINE 19756_1 | TR_LINE 19756_1 | TR_LINE 19756_1 | TR_LINE 19756_1
CA-Gladstone Rockhampton | 6096_Egan's Hill - Lakes Creek 66 kV | Loading (A) | 379.2403 | 359.3995 | 200.6635 | 373.5919 | 356.2077 | 198.5876 | 370.1038 | 353.0473 | 197.6214 | 364.5906 | 352.9655 | 197.2929 | 371.8875 | 357.6893 | 199.3104
CA-Gladstone Rockhampton | 6096_Egan's Hill - Lakes Creek 66 kV | Loading (MVA) | 43.6561 | 41.5205 | 23.8326 | 43.0493 | 40.9455 | 23.5963 | 42.5 | 40.7906 | 23.4667 | 42.4271 | 40.7132 | 23.4079 | 42.7034 | 41.1934 | 23.6325
CA-Gladstone Rockhampton | 6096_Egan's Hill - Lakes Creek 66 kV | Loading (MW) | 43.4537 | 41.3156 | 22.2917 | 42.8467 | 40.7137 | 22.0283 | 42.2207 | 40.5723 | 21.8872 | 42.2246 | 40.5027 | 21.8332 | 42.4578 | 41.0045 | 22.1021
CA-Gladstone Rockhampton | 6096_Egan's Hill - Lakes Creek 66 kV | Power Factor | 0.99537 | 0.99506 | 0.93535 | 0.99529 | 0.99434 | 0.93355 | 0.99343 | 0.99465 | 0.93269 | 0.99523 | 0.99483 | 0.93273 | 0.99425 | 0.99542 | 0.93524
CA-Gladstone Rockhampton | 6096_Egan's Hill - Lakes Creek 66 kV | Rating (A) | 321 | 341 | 307 | 321 | 341 | 307 | 321 | 341 | 307 | 321 | 341 | 307 | 321 | 341 | 307
CA-Gladstone Rockhampton | 6096_Egan's Hill - Lakes Creek 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Gladstone Rockhampton | 6096_Egan's Hill - Lakes Creek 66 kV | Min Voltage at Constrained Conductor | 66.4594 | 66.6979 | 68.5706 | 66.5265 | 66.3637 | 68.6004 | 66.2967 | 66.7044 | 68.5573 | 67.1838 | 66.5933 | 68.4993 | 66.2944 | 66.4888 | 68.4565
CA-Gladstone Rockhampton | 6096_Egan's Hill - Lakes Creek 66 kV | Contingency Outage | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV | 6003_Glenmore - Berserker 66 kV
CA-Moura | 6026_Moura - Theodore 66 kV | % of Rated A | 14.77% | 13.59% | 11.94% | 14.64% | 13.48% | 11.84% | 14.52% | 13.36% | 11.74% | 14.52% | 13.36% | 11.74% | 14.64% | 13.48% | 11.84%
CA-Moura | 6026_Moura - Theodore 66 kV | Limiting Line Name | TR_LINE 59682_1 | TR_LINE 59682_1 | TR_LINE 59682_1 | TR_LINE 59682_1 | TR_LINE 59682_1 | TR_LINE 59682_1 | TR_LINE 59682_1 | TR_LINE 59682_1 | TR_LINE 59682_1 | TR_LINE 59682_1 | TR_LINE 59682_1 | TR_LINE 59682_1 | TR_LINE 59682_1 | TR_LINE 59682_1 | TR_LINE 59682_1
CA-Moura | 6026_Moura - Theodore 66 kV | Loading (A) | 107.6575 | 106.4094 | 84.7574 | 106.7511 | 105.5117 | 84.0467 | 105.8242 | 104.6001 | 83.3322 | 105.8243 | 104.6002 | 83.3322 | 106.7476 | 105.5124 | 84.0467
CA-Moura | 6026_Moura - Theodore 66 kV | Loading (MVA) | 12.2921 | 12.1984 | 9.7643 | 12.1913 | 12.0984 | 9.6845 | 12.0905 | 11.9983 | 9.6048 | 12.0905 | 11.9983 | 9.6048 | 12.1913 | 12.0984 | 9.6845
CA-Moura | 6026_Moura - Theodore 66 kV | Loading (MW) | 11.9455 | 11.8531 | 9.5107 | 11.8488 | 11.7571 | 9.4337 | 11.752 | 11.6611 | 9.3567 | 11.752 | 11.6611 | 9.3567 | 11.8488 | 11.7571 | 9.4337
CA-Moura | 6026_Moura - Theodore 66 kV | Power Factor | 0.9718 | 0.97169 | 0.97402 | 0.9719 | 0.97179 | 0.97409 | 0.972 | 0.97189 | 0.97417 | 0.972 | 0.97189 | 0.97417 | 0.9719 | 0.97179 | 0.97409
CA-Moura | 6026_Moura - Theodore 66 kV | Rating (A) | 729 | 783 | 710 | 729 | 783 | 710 | 729 | 783 | 710 | 729 | 783 | 710 | 729 | 783 | 710
CA-Moura | 6026_Moura - Theodore 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
CA-Moura | 6026_Moura - Theodore 66 kV | Min Voltage at Constrained Conductor | 65.9199 | 66.1846 | 66.5121 | 65.9345 | 66.2002 | 66.5266 | 65.9619 | 66.2249 | 66.5444 | 65.9618 | 66.2248 | 66.5444 | 65.9366 | 66.1998 | 66.5266
CA-Moura | 6026_Moura - Theodore 66 kV | Contingency Outage | 6067 Lilyvale - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6007_Biloela - Coominglah Tee 66 kV | 6067 Lilyvale - Emerald 66 kV | 6067 Lilyvale - Emerald 66 kV | 6007_Biloela - Coominglah Tee 66 kV | 6082_Farnborough Tee - Yeppoon 66 kV | 6067 Lilyvale - Emerald 66 kV | 6007_Biloela - Coominglah Tee 66 kV | 6051_Parkhurst - Keppel 66 kV | 6067 Lilyvale - Emerald 66 kV | 6007_Biloela - Coominglah Tee 66 kV | 6051_Parkhurst - Keppel 66 kV | 6067 Lilyvale - Emerald 66 kV | 6007_Biloela - Coominglah Tee 66 kV
FN-Cairns Area | 7206 Woree-Cairns Terminal-Cairns City | % of Rated A | 42.62% | 34.16% | 20.93% | 42.09% | 33.77% | 20.68% | 41.83% | 33.56% | 20.55% | 41.92% | 33.63% | 20.6% | 42.27% | 33.91% | 20.77%
FN-Cairns Area | 7206 Woree-Cairns Terminal-Cairns City | Limiting Line Name | TR_CABLE 11_1 | TR_CABLE 11_1 | TR_CABLE 11_1 | TR_CABLE 11_1 | TR_CABLE 11_1 | TR_CABLE 11_1 | TR_CABLE 11_1 | TR_CABLE 11_1 | TR_CABLE 11_1 | TR_CABLE 11_1 | TR_CABLE 11_1 | TR_CABLE 11_1 | TR_CABLE 11_1 | TR_CABLE 11_1 | TR_CABLE 11_1
FN-Cairns Area | 7206 Woree-Cairns Terminal-Cairns City | Loading (A) | 204.1438 | 163.6405 | 100.2677 | 201.6153 | 161.7463 | 99.052 | 200.3524 | 160.7451 | 98.4464 | 200.7732 | 161.0787 | 98.6531 | 202.4577 | 162.414 | 99.4699
FN-Cairns Area | 7206 Woree-Cairns Terminal-Cairns City | Loading (MVA) | 48.859 | 39.1938 | 24.9241 | 48.2562 | 38.741 | 24.6242 | 47.955 | 38.5019 | 24.4743 | 48.0554 | 38.5815 | 24.5243 | 48.457 | 38.9004 | 24.7242
FN-Cairns Area | 7206 Woree-Cairns Terminal-Cairns City | Loading (MW) | 47.8331 | 38.6162 | 24.7363 | 47.2632 | 38.1588 | 24.4422 | 46.9783 | 37.9289 | 24.2952 | 47.0733 | 38.0055 | 24.3442 | 47.4532 | 38.312 | 24.5403
FN-Cairns Area | 7206 Woree-Cairns Terminal-Cairns City | Power Factor | 0.9786 | 0.98477 | 0.99168 | 0.97901 | 0.98448 | 0.99181 | 0.97922 | 0.98462 | 0.99188 | 0.97915 | 0.98458 | 0.99185 | 0.97887 | 0.98438 | 0.99176
FN-Cairns Area | 7206 Woree-Cairns Terminal-Cairns City | Rating (A) | 479 | 479 | 479 | 479 | 479 | 479 | 479 | 479 | 479 | 479 | 479 | 479 | 479 | 479 | 479
FN-Cairns Area | 7206 Woree-Cairns Terminal-Cairns City | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
FN-Cairns Area | 7206 Woree-Cairns Terminal-Cairns City | Min Voltage at Constrained Conductor | 138.1809 | 138.2821 | 143.5152 | 138.1874 | 138.2851 | 143.5287 | 138.1907 | 138.2876 | 143.5326 | 138.1896 | 138.2868 | 143.5245 | 138.1853 | 138.2835 | 143.5062
FN-Cairns Area | 7206 Woree-Cairns Terminal-Cairns City | Contingency Outage | 7227 Woree-Cairns Terminal-Cairns City | 7227 Woree-Cairns Terminal-Cairns City | 7227 Woree-Cairns Terminal-Cairns City | 7227 Woree-Cairns Terminal-Cairns City | 7227 Woree-Cairns Terminal-Cairns City | 7227 Woree-Cairns Terminal-Cairns City | 7227 Woree-Cairns Terminal-Cairns City | 7227 Woree-Cairns Terminal-Cairns City | 7227 Woree-Cairns Terminal-Cairns City | 7227 Woree-Cairns Terminal-Cairns City | 7227 Woree-Cairns Terminal-Cairns City | 7227 Woree-Cairns Terminal-Cairns City | 7227 Woree-Cairns Terminal-Cairns City | 7227 Woree-Cairns Terminal-Cairns City | 7227 Woree-Cairns Terminal-Cairns City
FN-Cairns Area | 7227 Woree-Cairns Terminal-Cairns City | % of Rated A | 48.66% | 36.23% | 24.48% | 48.06% | 35.81% | 24.18% | 47.76% | 35.59% | 24.03% | 47.86% | 35.66% | 24.08% | 48.26% | 35.94% | 24.28%
FN-Cairns Area | 7227 Woree-Cairns Terminal-Cairns City | Limiting Line Name | TR_LINE 176513_1 | TR_LINE 176513_1 | TR_LINE 176513_1 | TR_LINE 176513_1 | TR_LINE 176513_1 | TR_LINE 176513_1 | TR_LINE 176513_1 | TR_LINE 176513_1 | TR_LINE 176513_1 | TR_LINE 176513_1 | TR_LINE 176513_1 | TR_LINE 176513_1 | TR_LINE 176513_1 | TR_LINE 176513_1 | TR_LINE 176513_1
FN-Cairns Area | 7227 Woree-Cairns Terminal-Cairns City | Loading (A) | 203.4096 | 163.0462 | 99.8733 | 200.8894 | 161.1446 | 98.6634 | 199.6307 | 160.1471 | 98.0606 | 200.0505 | 160.4797 | 98.2664 | 201.73 | 161.7179 | 99.0795
FN-Cairns Area | 7227 Woree-Cairns Terminal-Cairns City | Loading (MVA) | 48.7778 | 39.107 | 24.8445 | 48.1742 | 38.6511 | 24.5455 | 47.8727 | 38.4121 | 24.396 | 47.9732 | 38.4918 | 24.4459 | 48.3753 | 38.7885 | 24.6452
FN-Cairns Area | 7227 Woree-Cairns Terminal-Cairns City | Loading (MW) | 47.909 | 38.665 | 24.7546 | 47.3373 | 38.2064 | 24.4601 | 47.0514 | 37.976 | 24.3128 | 47.1467 | 38.0528 | 24.3619 | 47.5279 | 38.3577 | 24.5583
FN-Cairns Area | 7227 Woree-Cairns Terminal-Cairns City | Power Factor | 0.98219 | 0.98869 | 0.99636 | 0.98262 | 0.98848 | 0.9965 | 0.98284 | 0.98863 | 0.99657 | 0.98277 | 0.98858 | 0.99654 | 0.98248 | 0.98888 | 0.99645
FN-Cairns Area | 7227 Woree-Cairns Terminal-Cairns City | Rating (A) | 418 | 450 | 408 | 418 | 450 | 408 | 418 | 450 | 408 | 418 | 450 | 408 | 418 | 450 | 408
FN-Cairns Area | 7227 Woree-Cairns Terminal-Cairns City | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
FN-Cairns Area | 7227 Woree-Cairns Terminal-Cairns City | Min Voltage at Constrained Conductor | 138.4404 | 138.473 | 143.62 | 138.4426 | 138.4741 | 143.6317 | 138.4437 | 138.4749 | 143.6348 | 138.4431 | 138.4744 | 143.6268 | 138.4413 | 138.4735 | 143.6095
FN-Cairns Area | 7227 Woree-Cairns Terminal-Cairns City | Contingency Outage | 7206 Woree-Cairns Terminal-Cairns City | 7206 Woree-Cairns Terminal-Cairns City | 7206 Woree-Cairns Terminal-Cairns City | 7206 Woree-Cairns Terminal-Cairns City | 7206 Woree-Cairns Terminal-Cairns City | 7206 Woree-Cairns Terminal-Cairns City | 7206 Woree-Cairns Terminal-Cairns City | 7206 Woree-Cairns Terminal-Cairns City | 7206 Woree-Cairns Terminal-Cairns City | 7206 Woree-Cairns Terminal-Cairns City | 7206 Woree-Cairns Terminal-Cairns City | 7206 Woree-Cairns Terminal-Cairns City | 7206 Woree-Cairns Terminal-Cairns City | 7206 Woree-Cairns Terminal-Cairns City | 7206 Woree-Cairns Terminal-Cairns City
FN-Cairns Area | 7332_Cairns North 132 kV | % of Rated A | 43.03% | 39.16% | 29.55% | 42.26% | 38.48% | 29.15% | 42.03% | 38.27% | 29.03% | 42.11% | 38.34% | 29.07% | 42.42% | 38.61% | 29.23%
FN-Cairns Area | 7332_Cairns North 132 kV | Limiting Line Name | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2
FN-Cairns Area | 7332_Cairns North 132 kV | Loading (A) | 203.5351 | 194.6455 | 131.8035 | 199.8995 | 191.2234 | 129.995 | 198.8119 | 190.1997 | 129.4553 | 199.1743 | 190.5408 | 129.6374 | 200.6254 | 191.9066 | 130.3622
FN-Cairns Area | 7332_Cairns North 132 kV | Loading (MVA) | 48.8611 | 46.727 | 32.8142 | 47.9883 | 45.9055 | 32.3666 | 47.7272 | 45.6598 | 32.2328 | 47.8142 | 45.7417 | 32.2764 | 48.1626 | 46.0695 | 32.4531
FN-Cairns Area | 7332_Cairns North 132 kV | Loading (MW) | 47.9533 | 45.6193 | 28.7707 | 47.0017 | 44.7142 | 28.2013 | 46.7162 | 44.4427 | 28.0305 | 46.8113 | 44.5332 | 28.0874 | 47.192 | 44.8952 | 28.3151
FN-Cairns Area | 7332_Cairns North 132 kV | Power Factor | 0.98142 | 0.97629 | 0.87677 | 0.97944 | 0.97405 | 0.87131 | 0.97882 | 0.97335 | 0.86962 | 0.97903 | 0.97358 | 0.87021 | 0.97985 | 0.97451 | 0.87249
FN-Cairns Area | 7332_Cairns North 132 kV | Rating (A) | 473 | 497 | 446 | 473 | 497 | 446 | 473 | 497 | 446 | 473 | 497 | 446 | 473 | 497 | 446
FN-Cairns Area | 7332_Cairns North 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
FN-Cairns Area | 7332_Cairns North 132 kV | Min Voltage at Constrained Conductor | 138.5982 | 138.5985 | 143.7389 | 138.5983 | 138.5986 | 143.7505 | 138.5983 | 138.5986 | 143.7533 | 138.5983 | 138.5986 | 143.7455 | 138.5983 | 138.5985 | 143.729
FN-Cairns Area | 7332_Cairns North 132 kV | Contingency Outage | 7333_Cairns North 132 kV | 7333_Cairns North 132 kV | 7333_Cairns North 132 kV | 7333_Cairns North 132 kV | 7333_Cairns North 132 kV | 7333_Cairns North 132 kV | 7333_Cairns North 132 kV | 7333_Cairns North 132 kV | 7333_Cairns North 132 kV | 7333_Cairns North 132 kV | 7333_Cairns North 132 kV | 7333_Cairns North 132 kV | 7333_Cairns North 132 kV | 7333_Cairns North 132 kV | 7333_Cairns North 132 kV
FN-Cairns Area | 7333_Cairns North 132 kV | % of Rated A | 42.99% | 39.12% | 29.55% | 42.22% | 38.44% | 29.14% | 41.99% | 38.23% | 29.02% | 42.07% | 38.3% | 29.07% | 42.37% | 38.57% | 29.23%
FN-Cairns Area | 7333_Cairns North 132 kV | Limiting Line Name | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2
FN-Cairns Area | 7333_Cairns North 132 kV | Loading (A) | 203.3349 | 194.4496 | 131.7863 | 199.7005 | 191.0304 | 129.9865 | 198.6135 | 190.0077 | 129.4494 | 198.9757 | 190.3484 | 129.6305 | 200.4261 | 191.713 | 130.3518
FN-Cairns Area | 7333_Cairns North 132 kV | Loading (MVA) | 48.813 | 46.68 | 32.8098 | 47.9406 | 45.8592 | 32.3644 | 47.6796 | 45.6137 | 32.2313 | 47.7665 | 45.6955 | 32.2746 | 48.1147 | 46.023 | 32.4505
FN-Cairns Area | 7333_Cairns North 132 kV | Loading (MW) | 47.9566 | 45.6223 | 28.7727 | 47.0049 | 44.7172 | 28.2033 | 46.7194 | 44.4457 | 28.0324 | 46.8145 | 44.5362 | 28.0894 | 47.1952 | 44.8982 | 28.3171
FN-Cairns Area | 7333_Cairns North 132 kV | Power Factor | 0.98245 | 0.97734 | 0.87695 | 0.98048 | 0.9751 | 0.87143 | 0.97986 | 0.97439 | 0.86973 | 0.98007 | 0.97463 | 0.87032 | 0.98089 | 0.97556 | 0.87263
FN-Cairns Area | 7333_Cairns North 132 kV | Rating (A) | 473 | 497 | 446 | 473 | 497 | 446 | 473 | 497 | 446 | 473 | 497 | 446 | 473 | 497 | 446
FN-Cairns Area | 7333_Cairns North 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
FN-Cairns Area | 7333_Cairns North 132 kV | Min Voltage at Constrained Conductor | 138.598 | 138.5983 | 143.7384 | 138.5981 | 138.5984 | 143.7502 | 138.5981 | 138.5984 | 143.753 | 138.5981 | 138.5984 | 143.7453 | 138.5981 | 138.5984 | 143.7286
FN-Cairns Area | 7333_Cairns North 132 kV | Contingency Outage | 7332_Cairns North 132 kV | 7332_Cairns North 132 kV | 7332_Cairns North 132 kV | 7332_Cairns North 132 kV | 7332_Cairns North 132 kV | 7332_Cairns North 132 kV | 7332_Cairns North 132 kV | 7332_Cairns North 132 kV | 7332_Cairns North 132 kV | 7332_Cairns North 132 kV | 7332_Cairns North 132 kV | 7332_Cairns North 132 kV | 7332_Cairns North 132 kV | 7332_Cairns North 132 kV | 7332_Cairns North 132 kV
FN-Cairns Area | EDMO-2GO1_Gordonvale 1 22kV | % of Rated A | 53.86% | 54.1% | 55.06% | 53.86% | 54.1% | 55.06% | 53.86% | 54.1% | 55.06% | 53.85% | 54.08% | 55.06% | 53.82% | 54.05% | 55.04%
FN-Cairns Area | EDMO-2GO1_Gordonvale 1 22kV | Limiting Line Name | HV_LINE 1182348_1 | HV_LINE 1182348_1 | HV_LINE 1182348_1 | HV_LINE 1182348_1 | HV_LINE 1182348_1 | HV_LINE 1182348_1 | HV_LINE 1182348_1 | HV_LINE 1182348_1 | HV_LINE 1182348_1 | HV_LINE 1182348_1 | HV_LINE 1182348_1 | HV_LINE 1182348_1 | HV_LINE 1182348_1 | HV_LINE 1182348_1 | HV_LINE 1182348_1
FN-Cairns Area | EDMO-2GO1_Gordonvale 1 22kV | Loading (A) | 42.0091 | 42.195 | 42.9461 | 42.0113 | 42.1978 | 42.95 | 42.0094 | 42.1955 | 42.9499 | 41.9995 | 42.1829 | 42.9435 | 41.9834 | 42.1624 | 42.9319
FN-Cairns Area | EDMO-2GO1_Gordonvale 1 22kV | Loading (MVA) | 1.6722 | 1.6702 | 1.7495 | 1.6723 | 1.6704 | 1.7498 | 1.6722 | 1.6702 | 1.7498 | 1.6714 | 1.6692 | 1.7493 | 1.6701 | 1.6675 | 1.7483
FN-Cairns Area | EDMO-2GO1_Gordonvale 1 22kV | Loading (MW) | 0.059498 | 0.13601 | 0.0065729 | 0.059484 | 0.13599 | 0.0065506 | 0.059496 | 0.136 | 0.006551 | 0.059559 | 0.1361 | 0.0065879 | 0.059663 | 0.13624 | 0.006654
FN-Cairns Area | EDMO-2GO1_Gordonvale 1 22kV | Power Factor | 0.034659 | 0.080508 | 0.0028326 | 0.034647 | 0.080485 | 0.0028193 | 0.034657 | 0.080504 | 0.0028195 | 0.034712 | 0.080609 | 0.0028417 | 0.034802 | 0.08078 | 0.0028815
FN-Cairns Area | EDMO-2GO1_Gordonvale 1 22kV | Rating (A) | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78
FN-Cairns Area | EDMO-2GO1_Gordonvale 1 22kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
FN-Cairns Area | EDMO-2GO1_Gordonvale 1 22kV | Min Voltage at Constrained Conductor | 22.9791 | 22.8502 | 23.518 | 22.9803 | 22.8518 | 23.5201 | 22.9793 | 22.8504 | 23.5201 | 22.9737 | 22.8432 | 23.5165 | 22.9647 | 22.8314 | 23.5102
FN-Cairns Area | EDMO-2GO1_Gordonvale 1 22kV | Contingency Outage | EDMO-2GO3_Gordonvale 3 22kV | EDMO-2GO3_Gordonvale 3 22kV | EDMO-2GO3_Gordonvale 3 22kV | EDMO-2GO3_Gordonvale 3 22kV | EDMO-2GO3_Gordonvale 3 22kV | EDMO-2GO3_Gordonvale 3 22kV | EDMO-2GO3_Gordonvale 3 22kV | EDMO-2GO3_Gordonvale 3 22kV | EDMO-2GO3_Gordonvale 3 22kV | EDMO-2GO3_Gordonvale 3 22kV | EDMO-2GO3_Gordonvale 3 22kV | EDMO-2GO3_Gordonvale 3 22kV | EDMO-2GO3_Gordonvale 3 22kV | EDMO-2GO3_Gordonvale 3 22kV | EDMO-2GO3_Gordonvale 3 22kV
FN-Cairns Area | EDMO-2GO2_Gordonvale 2 22kV | % of Rated A | 44.83% | 45.32% | 46.7% | 44.83% | 45.32% | 46.7% | 44.83% | 45.32% | 46.7% | 44.82% | 45.3% | 46.7% | 44.8% | 45.28% | 46.68%
FN-Cairns Area | EDMO-2GO2_Gordonvale 2 22kV | Limiting Line Name | HV_LINE 650000_1 | HV_LINE 650000_1 | HV_LINE 650000_1 | HV_LINE 650000_1 | HV_LINE 650000_1 | HV_LINE 650000_1 | HV_LINE 650000_1 | HV_LINE 650000_1 | HV_LINE 650000_1 | HV_LINE 650000_1 | HV_LINE 650000_1 | HV_LINE 650000_1 | HV_LINE 650000_1 | HV_LINE 650000_1 | HV_LINE 650000_1
FN-Cairns Area | EDMO-2GO2_Gordonvale 2 22kV | Loading (A) | 34.9657 | 35.3473 | 36.4261 | 34.9676 | 35.3496 | 36.4296 | 34.966 | 35.3476 | 36.4296 | 34.9573 | 35.3371 | 36.4238 | 34.9431 | 35.3198 | 36.4134
FN-Cairns Area | EDMO-2GO2_Gordonvale 2 22kV | Loading (MVA) | 1.3905 | 1.3997 | 1.48 | 1.3907 | 1.3999 | 1.4802 | 1.3906 | 1.3997 | 1.4802 | 1.3899 | 1.3988 | 1.4798 | 1.3888 | 1.3974 | 1.479
FN-Cairns Area | EDMO-2GO2_Gordonvale 2 22kV | Loading (MW) | 0.36869 | 0.47667 | 0.23684 | 0.36868 | 0.47665 | 0.23683 | 0.36868 | 0.47666 | 0.23683 | 0.36873 | 0.47673 | 0.23685 | 0.36881 | 0.47685 | 0.2369
FN-Cairns Area | EDMO-2GO2_Gordonvale 2 22kV | Power Factor | 0.2611 | 0.33664 | 0.15574 | 0.26107 | 0.33658 | 0.15569 | 0.2611 | 0.33663 | 0.1557 | 0.26126 | 0.33689 | 0.15576 | 0.26153 | 0.33732 | 0.15588
FN-Cairns Area | EDMO-2GO2_Gordonvale 2 22kV | Rating (A) | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78
FN-Cairns Area | EDMO-2GO2_Gordonvale 2 22kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
FN-Cairns Area | EDMO-2GO2_Gordonvale 2 22kV | Min Voltage at Constrained Conductor | 22.9481 | 22.8413 | 23.4556 | 22.9493 | 22.8429 | 23.4577 | 22.9483 | 22.8416 | 23.4577 | 22.9428 | 22.8344 | 23.4541 | 22.9339 | 22.8228 | 23.4479
FN-Cairns Area | EDMO-2GO2_Gordonvale 2 22kV | Contingency Outage | EDMO-2GO3_Gordonvale 3 22kV | EDMO-2GO3_Gordonvale 3 22kV | EDMO-2GO3_Gordonvale 3 22kV | EDMO-2GO3_Gordonvale 3 22kV | EDMO-2GO3_Gordonvale 3 22kV | EDMO-2GO3_Gordonvale 3 22kV | EDMO-2GO3_Gordonvale 3 22kV | EDMO-2GO3_Gordonvale 3 22kV | EDMO-2GO3_Gordonvale 3 22kV | EDMO-2GO3_Gordonvale 3 22kV | EDMO-2GO3_Gordonvale 3 22kV | EDMO-2GO3_Gordonvale 3 22kV | EDMO-2GO3_Gordonvale 3 22kV | EDMO-2GO3_Gordonvale 3 22kV | EDMO-2GO3_Gordonvale 3 22kV
FN-Cairns Area | EDMO-2GO3_Gordonvale 3 22kV | % of Rated A | 39.48% | 31.19% | 34.14% | 39.48% | 31.2% | 34.15% | 39.48% | 31.19% | 34.15% | 39.47% | 31.18% | 34.14% | 39.45% | 31.17% | 33.95%
FN-Cairns Area | EDMO-2GO3_Gordonvale 3 22kV | Limiting Line Name | HV_LINE 36762_1 | HV_LINE 36762_1 | HV_LINE 58939_1 | HV_LINE 36762_1 | HV_LINE 36762_1 | HV_LINE 58939_1 | HV_LINE 36762_1 | HV_LINE 36762_1 | HV_LINE 58939_1 | HV_LINE 36762_1 | HV_LINE 36762_1 | HV_LINE 58939_1 | HV_LINE 36762_1 | HV_LINE 36762_1 | HV_LINE 58939_1
FN-Cairns Area | EDMO-2GO3_Gordonvale 3 22kV | Loading (A) | 52.1079 | 52.093 | 54.2869 | 52.1107 | 52.0967 | 54.292 | 52.1084 | 52.0937 | 54.292 | 52.0954 | 52.0769 | 54.2834 | 52.0744 | 52.0495 | 53.9744
FN-Cairns Area | EDMO-2GO3_Gordonvale 3 22kV | Loading (MVA) | 2.0857 | 2.0778 | 2.2285 | 2.0859 | 2.0781 | 2.2289 | 2.0857 | 2.0778 | 2.2289 | 2.0847 | 2.0765 | 2.2282 | 2.0831 | 2.0744 | 2.2038
FN-Cairns Area | EDMO-2GO3_Gordonvale 3 22kV | Loading (MW) | 0.15243 | 0.14177 | 0.29767 | 0.15244 | 0.14177 | 0.29768 | 0.15243 | 0.14177 | 0.29768 | 0.15241 | 0.14173 | 0.29766 | 0.15236 | 0.14168 | 0.29693
FN-Cairns Area | EDMO-2GO3_Gordonvale 3 22kV | Power Factor | 0.073012 | 0.068157 | 0.13338 | 0.073007 | 0.068151 | 0.13336 | 0.073011 | 0.068156 | 0.13336 | 0.073034 | 0.068182 | 0.13339 | 0.073072 | 0.068226 | 0.13454
FN-Cairns Area | EDMO-2GO3_Gordonvale 3 22kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
FN-Cairns Area | EDMO-2GO3_Gordonvale 3 22kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
FN-Cairns Area | EDMO-2GO3_Gordonvale 3 22kV | Min Voltage at Constrained Conductor | 23.1084 | 23.0276 | 23.6986 | 23.1096 | 23.0292 | 23.7007 | 23.1086 | 23.0279 | 23.7007 | 23.1032 | 23.0208 | 23.6972 | 23.0944 | 23.0093 | 23.5718
FN-Cairns Area | EDMO-2GO3_Gordonvale 3 22kV | Contingency Outage | EDMO-2GO1_Gordonvale 1 22kV | EDMO-2GO1_Gordonvale 1 22kV | EDMO-2GO1_Gordonvale 1 22kV | EDMO-2GO1_Gordonvale 1 22kV | EDMO-2GO1_Gordonvale 1 22kV | EDMO-2GO1_Gordonvale 1 22kV | EDMO-2GO1_Gordonvale 1 22kV | EDMO-2GO1_Gordonvale 1 22kV | EDMO-2GO1_Gordonvale 1 22kV | EDMO-2GO1_Gordonvale 1 22kV | EDMO-2GO1_Gordonvale 1 22kV | EDMO-2GO1_Gordonvale 1 22kV | EDMO-2GO1_Gordonvale 1 22kV | EDMO-2GO1_Gordonvale 1 22kV | EDMO-2GO1_Gordonvale 1 22kV
FN-Cairns Area | GORD-2RIV_Riverstone Rd 22kV | % of Rated A | 4.095% | 3.028% | 2.153% | 4.095% | 3.028% | 2.152% | 4.095% | 3.028% | 2.152% | 4.096% | 3.029% | 2.153% | 4.098% | 3.031% | 2.153%
FN-Cairns Area | GORD-2RIV_Riverstone Rd 22kV | Limiting Line Name | HV_LINE 53928_1 | HV_LINE 53928_1 | HV_LINE 53928_1 | HV_LINE 53928_1 | HV_LINE 53928_1 | HV_LINE 53928_1 | HV_LINE 53928_1 | HV_LINE 53928_1 | HV_LINE 53928_1 | HV_LINE 53928_1 | HV_LINE 53928_1 | HV_LINE 53928_1 | HV_LINE 53928_1 | HV_LINE 53928_1 | HV_LINE 53928_1
FN-Cairns Area | GORD-2RIV_Riverstone Rd 22kV | Loading (A) | 5.4054 | 5.0573 | 3.4227 | 5.4051 | 5.057 | 3.4224 | 5.4053 | 5.0572 | 3.4224 | 5.4066 | 5.0589 | 3.4229 | 5.4088 | 5.0615 | 3.4238
FN-Cairns Area | GORD-2RIV_Riverstone Rd 22kV | Loading (MVA) | 0.21499 | 0.20021 | 0.13916 | 0.21499 | 0.20021 | 0.13916 | 0.21499 | 0.20021 | 0.13916 | 0.21499 | 0.20021 | 0.13916 | 0.21499 | 0.20021 | 0.13916
FN-Cairns Area | GORD-2RIV_Riverstone Rd 22kV | Loading (MW) | 0.1871 | 0.17814 | 0.12336 | 0.1871 | 0.17814 | 0.12336 | 0.1871 | 0.17814 | 0.12336 | 0.1871 | 0.17814 | 0.12336 | 0.1871 | 0.17814 | 0.12336
FN-Cairns Area | GORD-2RIV_Riverstone Rd 22kV | Power Factor | 0.87025 | 0.88977 | 0.88649 | 0.87025 | 0.88977 | 0.88649 | 0.87025 | 0.88977 | 0.88649 | 0.87025 | 0.88977 | 0.88649 | 0.87024 | 0.88976 | 0.88649
FN-Cairns Area | GORD-2RIV_Riverstone Rd 22kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
FN-Cairns Area | GORD-2RIV_Riverstone Rd 22kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
FN-Cairns Area | GORD-2RIV_Riverstone Rd 22kV | Min Voltage at Constrained Conductor | 22.9634 | 22.8561 | 23.4737 | 22.9646 | 22.8577 | 23.476 | 22.9636 | 22.8564 | 23.476 | 22.9581 | 22.8491 | 23.4724 | 22.949 | 22.8373 | 23.466
FN-Cairns Area | GORD-2RIV_Riverstone Rd 22kV | Contingency Outage | 4KID_Ross - Kidston 132 kV | 4KID_Ross - Kidston 132 kV | 7206 Woree-Cairns Terminal-Cairns City | 4KID_Ross - Kidston 132 kV | 4KID_Ross - Kidston 132 kV | 7206 Woree-Cairns Terminal-Cairns City | 4KID_Ross - Kidston 132 kV | 4KID_Ross - Kidston 132 kV | 7206 Woree-Cairns Terminal-Cairns City | 4KID_Ross - Kidston 132 kV | 4KID_Ross - Kidston 132 kV | 7206 Woree-Cairns Terminal-Cairns City | 4KID_Ross - Kidston 132 kV | 4KID_Ross - Kidston 132 kV | 7206 Woree-Cairns Terminal-Cairns City
FN-Cairns Area | KAME-2CO1 Cook No 1 22kV | % of Rated A | 47.6% | 50.52% | 48.13% | 47.61% | 50.53% | 48.14% | 47.62% | 50.54% | 48.14% | 47.62% | 50.54% | 48.14% | 47.63% | 50.55% | 48.15%
FN-Cairns Area | KAME-2CO1 Cook No 1 22kV | Limiting Line Name | HV_CABLE_38741076_1 | HV_CABLE_38741076_1 | HV_CABLE_38741076_1 | HV_CABLE_38741076_1 | HV_CABLE_38741076_1 | HV_CABLE_38741076_1 | HV_CABLE_38741076_1 | HV_CABLE_38741076_1 | HV_CABLE_38741076_1 | HV_CABLE_38741076_1 | HV_CABLE_38741076_1 | HV_CABLE_38741076_1 | HV_CABLE_38741076_1 | HV_CABLE_38741076_1 | HV_CABLE_38741076_1
FN-Cairns Area | KAME-2CO1 Cook No 1 22kV | Loading (A) | 64.2646 | 68.2066 | 64.9798 | 64.2782 | 68.2196 | 64.9911 | 64.2818 | 68.2244 | 64.9919 | 64.2873 | 68.2317 | 64.9957 | 64.2975 | 68.2451 | 65.0032
FN-Cairns Area | KAME-2CO1 Cook No 1 22kV | Loading (MVA) | 2.5535 | 2.7065 | 2.6208 | 2.554 | 2.7069 | 2.6214 | 2.5539 | 2.7068 | 2.6214 | 2.5538 | 2.7067 | 2.6213 | 2.5535 | 2.7064 | 2.6211
FN-Cairns Area | KAME-2CO1 Cook No 1 22kV | Loading (MW) | 2.4564 | 2.6199 | 2.5117 | 2.4565 | 2.62 | 2.5118 | 2.4565 | 2.62 | 2.5118 | 2.4565 | 2.62 | 2.5118 | 2.4565 | 2.62 | 2.5118
FN-Cairns Area | KAME-2CO1 Cook No 1 22kV | Power Factor | 0.96198 | 0.968 | 0.95837 | 0.96183 | 0.96787 | 0.95818 | 0.96186 | 0.9679 | 0.95819 | 0.96192 | 0.96795 | 0.95823 | 0.96201 | 0.96805 | 0.9583
FN-Cairns Area | KAME-2CO1 Cook No 1 22kV | Rating (A) | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135
FN-Cairns Area | KAME-2CO1 Cook No 1 22kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
FN-Cairns Area | KAME-2CO1 Cook No 1 22kV | Min Voltage at Constrained Conductor | 22.9243 | 22.892 | 23.2693 | 22.9239 | 22.8915 | 23.2707 | 22.9217 | 22.8891 | 23.2702 | 22.9185 | 22.8854 | 23.2679 | 22.9126 | 22.8787 | 23.2634
FN-Cairns Area | KAME-2CO1 Cook No 1 22kV | Contingency Outage | KAME-2CO2 Cook No 2 22kV | KAME-2CO2 Cook No 2 22kV | KAME-2CO2 Cook No 2 22kV | KAME-2CO2 Cook No 2 22kV | KAME-2CO2 Cook No 2 22kV | KAME-2CO2 Cook No 2 22kV | KAME-2CO2 Cook No 2 22kV | KAME-2CO2 Cook No 2 22kV | KAME-2CO2 Cook No 2 22kV | KAME-2CO2 Cook No 2 22kV | KAME-2CO2 Cook No 2 22kV | KAME-2CO2 Cook No 2 22kV | KAME-2CO2 Cook No 2 22kV | KAME-2CO2 Cook No 2 22kV | KAME-2CO2 Cook No 2 22kV
FN-Cairns Area | KAME-2CO2 Cook No 2 22kV | % of Rated A | 25.58% | 25.53% | 26.08% | 25.6% | 25.56% | 26.11% | 25.6% | 25.55% | 26.11% | 25.59% | 25.55% | 26.11% | 25.59% | 25.54% | 26.1%
FN-Cairns Area | KAME-2CO2 Cook No 2 22kV | Limiting Line Name | HV_CABLE_12173517_1 | HV_CABLE_12173517_1 | HV_CABLE_12173517_1 | HV_CABLE_12173517_1 | HV_CABLE_12173517_1 | HV_CABLE_12173517_1 | HV_CABLE_12173517_1 | HV_CABLE_12173517_1 | HV_CABLE_12173517_1 | HV_CABLE_12173517_1 | HV_CABLE_12173517_1 | HV_CABLE_12173517_1 | HV_CABLE_12173517_1 | HV_CABLE_12173517_1 | HV_CABLE_12173517_1
FN-Cairns Area | KAME-2CO2 Cook No 2 22kV | Loading (A) | 34.5273 | 34.467 | 35.2107 | 34.56 | 34.5003 | 35.2467 | 34.5569 | 34.4974 | 35.2461 | 34.5522 | 34.4905 | 35.2427 | 34.5435 | 34.4807 | 35.2361
FN-Cairns Area | KAME-2CO2 Cook No 2 22kV | Loading (MVA) | 1.3758 | 1.3717 | 1.431 | 1.3771 | 1.373 | 1.4325 | 1.3769 | 1.3728 | 1.4325 | 1.3765 | 1.3722 | 1.4322 | 1.3758 | 1.3714 | 1.4316
FN-Cairns Area | KAME-2CO2 Cook No 2 22kV | Loading (MW) | 0.067763 | 0.15808 | 0.099529 | 0.06782 | 0.15814 | 0.099591 | 0.067818 | 0.15813 | 0.09959 | 0.067814 | 0.15813 | 0.099588 | 0.067808 | 0.15812 | 0.099583
FN-Cairns Area | KAME-2CO2 Cook No 2 22kV | Power Factor | 0.048881 | 0.11521 | 0.069285 | 0.048876 | 0.11514 | 0.069252 | 0.048883 | 0.11516 | 0.069254 | 0.048894 | 0.1152 | 0.069265 | 0.048914 | 0.11526 | 0.069288
FN-Cairns Area | KAME-2CO2 Cook No 2 22kV | Rating (A) | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135
FN-Cairns Area | KAME-2CO2 Cook No 2 22kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
FN-Cairns Area | KAME-2CO2 Cook No 2 22kV | Min Voltage at Constrained Conductor | 23.0059 | 22.9763 | 23.4635 | 23.0055 | 22.9765 | 23.4648 | 23.0034 | 22.9745 | 23.4644 | 23.0003 | 22.97 | 23.4622 | 22.9946 | 22.9635 | 23.4578
FN-Cairns Area | KAME-2CO2 Cook No 2 22kV | Contingency Outage | KAME-2CO1 Cook No 1 22kV | KAME-2CO1 Cook No 1 22kV | KAME-2CO1 Cook No 1 22kV | KAME-2CO1 Cook No 1 22kV | KAME-2CO1 Cook No 1 22kV | KAME-2CO1 Cook No 1 22kV | KAME-2CO1 Cook No 1 22kV | KAME-2CO1 Cook No 1 22kV | KAME-2CO1 Cook No 1 22kV | KAME-2CO1 Cook No 1 22kV | KAME-2CO1 Cook No 1 22kV | KAME-2CO1 Cook No 1 22kV | KAME-2CO1 Cook No 1 22kV | KAME-2CO1 Cook No 1 22kV | KAME-2CO1 Cook No 1 22kV
FN-Cairns Area | KAME-2CO3 Cook No 3 22kV | % of Rated A | 25.63% | 26.41% | 26.34% | 25.65% | 26.44% | 26.36% | 25.65% | 26.44% | 26.36% | 25.65% | 26.43% | 26.36% | 25.64% | 26.42% | 26.35%
FN-Cairns Area | KAME-2CO3 Cook No 3 22kV | Limiting Line Name | HV_CABLE_12128762_1 | HV_CABLE_12128762_1 | HV_CABLE_12128762_1 | HV_CABLE_12128762_1 | HV_CABLE_12128762_1 | HV_CABLE_12128762_1 | HV_CABLE_12128762_1 | HV_CABLE_12128762_1 | HV_CABLE_12128762_1 | HV_CABLE_12128762_1 | HV_CABLE_12128762_1 | HV_CABLE_12128762_1 | HV_CABLE_12128762_1 | HV_CABLE_12128762_1 | HV_CABLE_12128762_1
FN-Cairns Area | KAME-2CO3 Cook No 3 22kV | Loading (A) | 34.5977 | 35.658 | 35.5539 | 34.6298 | 35.6901 | 35.5891 | 34.6268 | 35.6875 | 35.5885 | 34.6222 | 35.6812 | 35.5852 | 34.6137 | 35.6723 | 35.5788
FN-Cairns Area | KAME-2CO3 Cook No 3 22kV | Loading (MVA) | 1.3786 | 1.4191 | 1.4449 | 1.3799 | 1.4203 | 1.4464 | 1.3796 | 1.4201 | 1.4464 | 1.3793 | 1.4196 | 1.4461 | 1.3786 | 1.4188 | 1.4456
FN-Cairns Area | KAME-2CO3 Cook No 3 22kV | Loading (MW) | 0.1834 | 0.39028 | 0.25398 | 0.18349 | 0.39037 | 0.25409 | 0.18348 | 0.39037 | 0.25408 | 0.18346 | 0.39035 | 0.25407 | 0.18344 | 0.39032 | 0.25406
FN-Cairns Area | KAME-2CO3 Cook No 3 22kV | Power Factor | 0.13303 | 0.27503 | 0.17578 | 0.13297 | 0.27485 | 0.17567 | 0.13299 | 0.27488 | 0.17567 | 0.13302 | 0.27497 | 0.1757 | 0.13306 | 0.2751 | 0.17575
FN-Cairns Area | KAME-2CO3 Cook No 3 22kV | Rating (A) | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135
FN-Cairns Area | KAME-2CO3 Cook No 3 22kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
FN-Cairns Area | KAME-2CO3 Cook No 3 22kV | Min Voltage at Constrained Conductor | 23.0059 | 22.9751 | 23.4633 | 23.0055 | 22.9752 | 23.4647 | 23.0034 | 22.9733 | 23.4643 | 23.0003 | 22.9687 | 23.462 | 22.9946 | 22.9622 | 23.4577
FN-Cairns Area | KAME-2CO3 Cook No 3 22kV | Contingency Outage | KAME-2CO1 Cook No 1 22kV | KAME-2CO1 Cook No 1 22kV | KAME-2CO1 Cook No 1 22kV | KAME-2CO1 Cook No 1 22kV | KAME-2CO1 Cook No 1 22kV | KAME-2CO1 Cook No 1 22kV | KAME-2CO1 Cook No 1 22kV | KAME-2CO1 Cook No 1 22kV | KAME-2CO1 Cook No 1 22kV | KAME-2CO1 Cook No 1 22kV | KAME-2CO1 Cook No 1 22kV | KAME-2CO1 Cook No 1 22kV | KAME-2CO1 Cook No 1 22kV | KAME-2CO1 Cook No 1 22kV | KAME-2CO1 Cook No 1 22kV
FN-Gulf | 3CRO_Croydon 66 kV | % of Rated A | 10.37% | 10.52% | 7.237% | 10.36% | 10.51% | 7.234% | 10.34% | 10.48% | 7.134% | 10.34% | 10.48% | 7.134% | 10.5% | 10.65% | 7.229%
FN-Gulf | 3CRO_Croydon 66 kV | Limiting Line Name | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1
FN-Gulf | 3CRO_Croydon 66 kV | Loading (A) | 47.384 | 51.2152 | 34.1573 | 47.3673 | 51.1978 | 34.1463 | 47.2387 | 51.0384 | 33.6706 | 47.2387 | 51.0384 | 33.6706 | 48.0075 | 51.8858 | 34.1223
FN-Gulf | 3CRO_Croydon 66 kV | Loading (MVA) | 5.6522 | 6.1006 | 4.0798 | 5.6508 | 6.0991 | 4.0787 | 5.6395 | 6.0856 | 4.0317 | 5.6395 | 6.0856 | 4.0317 | 5.7307 | 6.1859 | 4.0856
FN-Gulf | 3CRO_Croydon 66 kV | Loading (MW) | 4.7541 | 5.2277 | 3.0277 | 4.7541 | 5.2276 | 3.0276 | 4.7534 | 5.2266 | 3.0266 | 4.7534 | 5.2266 | 3.0266 | 4.8499 | 5.3323 | 3.0859
FN-Gulf | 3CRO_Croydon 66 kV | Power Factor | 0.84111 | 0.85692 | 0.74212 | 0.84131 | 0.85711 | 0.74231 | 0.84288 | 0.85884 | 0.75071 | 0.84287 | 0.85884 | 0.75071 | 0.84631 | 0.862 | 0.75532
FN-Gulf | 3CRO_Croydon 66 kV | Rating (A) | 457 | 487 | 472 | 457 | 487 | 472 | 457 | 487 | 472 | 457 | 487 | 472 | 457 | 487 | 472
FN-Gulf | 3CRO_Croydon 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
FN-Gulf | 3CRO_Croydon 66 kV | Min Voltage at Constrained Conductor | 68.8695 | 68.7722 | 68.959 | 68.876 | 68.7789 | 68.9629 | 68.9256 | 68.841 | 69.1317 | 68.9255 | 68.841 | 69.1317 | 68.9185 | 68.8327 | 69.1286
FN-Gulf | 3CRO_Croydon 66 kV | Contingency Outage | Kidston Solar Farm (Genex) | Kidston Solar Farm (Genex) | Kidston Solar Farm (Genex) | Kidston Solar Farm (Genex) | Kidston Solar Farm (Genex) | Kidston Solar Farm (Genex) | Kidston Solar Farm (Genex) | Kidston Solar Farm (Genex) | Kidston Solar Farm (Genex) | Kidston Solar Farm (Genex) | Kidston Solar Farm (Genex) | Kidston Solar Farm (Genex) | Kidston Solar Farm (Genex) | Kidston Solar Farm (Genex) | Kidston Solar Farm (Genex)
FN-Gulf | 3NOR_Normanton 66 kV | % of Rated A | 7.964% | 8.166% | 5.24% | 7.961% | 8.164% | 5.242% | 7.944% | 8.142% | 5.313% | 7.944% | 8.142% | 5.313% | 8.123% | 8.326% | 5.381%
FN-Gulf | 3NOR_Normanton 66 kV | Limiting Line Name | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1
FN-Gulf | 3NOR_Normanton 66 kV | Loading (A) | 36.3933 | 39.7691 | 24.7341 | 36.3829 | 39.7576 | 24.7417 | 36.3034 | 39.6528 | 25.0786 | 36.3035 | 39.6528 | 25.0786 | 37.1211 | 40.5473 | 25.4005
FN-Gulf | 3NOR_Normanton 66 kV | Loading (MVA) | 4.363 | 4.7582 | 2.9288 | 4.362 | 4.7571 | 2.9298 | 4.3544 | 4.7473 | 2.971 | 4.3544 | 4.7473 | 2.971 | 4.4515 | 4.8531 | 3.0089
FN-Gulf | 3NOR_Normanton 66 kV | Loading (MW) | 4.1409 | 4.4988 | 2.6191 | 4.1409 | 4.4988 | 2.6191 | 4.1408 | 4.4986 | 2.6195 | 4.1408 | 4.4986 | 2.6195 | 4.2329 | 4.599 | 2.677
FN-Gulf | 3NOR_Normanton 66 kV | Power Factor | 0.9491 | 0.94549 | 0.883 | 0.94931 | 0.9457 | 0.88272 | 0.95093 | 0.94761 | 0.8705 | 0.95093 | 0.94761 | 0.8705 | 0.95089 | 0.94764 | 0.87823
FN-Gulf | 3NOR_Normanton 66 kV | Rating (A) | 457 | 487 | 472 | 457 | 487 | 472 | 457 | 487 | 472 | 457 | 487 | 472 | 457 | 487 | 472
FN-Gulf | 3NOR_Normanton 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
FN-Gulf | 3NOR_Normanton 66 kV | Min Voltage at Constrained Conductor | 68.1437 | 68.0676 | 68.3656 | 68.1449 | 68.0689 | 68.3664 | 68.1545 | 68.0809 | 68.3983 | 68.1545 | 68.0809 | 68.3983 | 68.1409 | 68.0656 | 68.391
FN-Gulf | 3NOR_Normanton 66 kV | Contingency Outage | Kidston Solar Farm (Genex) | Kidston Solar Farm (Genex) | KAME-2CO1 Cook No 1 22kV | Kidston Solar Farm (Genex) | Kidston Solar Farm (Genex) | KAME-2CO1 Cook No 1 22kV | Kidston Solar Farm (Genex) | Kidston Solar Farm (Genex) | 3DIM_Dimbulah 66 kV | Kidston Solar Farm (Genex) | Kidston Solar Farm (Genex) | KAME-2CO1 Cook No 1 22kV | Kidston Solar Farm (Genex) | Kidston Solar Farm (Genex) | KAME-2CO1 Cook No 1 22kV
FN-Gulf | 4KID_Ross - Kidston 132 kV | % of Rated A | 20.56% | 19.51% | 20.12% | 20.54% | 19.49% | 20.11% | 20.92% | 19.74% | 19.99% | 20.92% | 19.74% | 19.99% | 20.99% | 19.81% | 20.02%
FN-Gulf | 4KID_Ross - Kidston 132 kV | Limiting Line Name | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1
FN-Gulf | 4KID_Ross - Kidston 132 kV | Loading (A) | 72.9738 | 75.1073 | 69.8125 | 72.9223 | 75.0475 | 69.7988 | 74.2783 | 75.9895 | 69.3513 | 74.2783 | 75.9896 | 69.3513 | 74.5226 | 76.2665 | 69.4835
FN-Gulf | 4KID_Ross - Kidston 132 kV | Loading (MVA) | 17.519 | 18.0316 | 16.7604 | 17.5066 | 18.0172 | 16.7571 | 17.8324 | 18.2436 | 16.6497 | 17.8324 | 18.2436 | 16.6497 | 17.891 | 18.3101 | 16.6815
FN-Gulf | 4KID_Ross - Kidston 132 kV | Loading (MW) | 9.519 | 10.3823 | 6.3967 | 9.4759 | 10.3373 | 6.3701 | 7.6258 | 8.4112 | 5.2039 | 7.6258 | 8.4112 | 5.2039 | 7.7289 | 8.5247 | 5.2661
FN-Gulf | 4KID_Ross - Kidston 132 kV | Power Factor | 0.54335 | 0.57578 | 0.38166 | 0.54127 | 0.57375 | 0.38014 | 0.42764 | 0.46105 | 0.31255 | 0.42764 | 0.46105 | 0.31255 | 0.432 | 0.46557 | 0.31569
FN-Gulf | 4KID_Ross - Kidston 132 kV | Rating (A) | 355 | 385 | 347 | 355 | 385 | 347 | 355 | 385 | 347 | 355 | 385 | 347 | 355 | 385 | 347
FN-Gulf | 4KID_Ross - Kidston 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
FN-Gulf | 4KID_Ross - Kidston 132 kV | Min Voltage at Constrained Conductor | 138.6059 | 138.609 | 138.6088 | 138.606 | 138.6091 | 138.6088 | 138.6076 | 138.6107 | 138.6092 | 138.6075 | 138.6106 | 138.6092 | 138.6074 | 138.6105 | 138.6091
FN-Gulf | 4KID_Ross - Kidston 132 kV | Contingency Outage | 3MA2_Mareeba No 2 66 kV | 3AT1_Atherton No 1 66 kV | 7206 Woree-Cairns Terminal-Cairns City | 3MA2_Mareeba No 2 66 kV | 3AT1_Atherton No 1 66 kV | 7206 Woree-Cairns Terminal-Cairns City | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7206 Woree-Cairns Terminal-Cairns City | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7206 Woree-Cairns Terminal-Cairns City | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7206 Woree-Cairns Terminal-Cairns City
FN-Gulf | 7216_4GEO (Georgetown) 132 kV | % of Rated A | 11.32% | 10.4% | 8.984% | 11.33% | 10.41% | 8.997% | 11.31% | 10.39% | 8.682% | 11.31% | 10.39% | 8.682% | 11.39% | 10.48% | 8.682%
FN-Gulf | 7216_4GEO (Georgetown) 132 kV | Limiting Line Name | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1
FN-Gulf | 7216_4GEO (Georgetown) 132 kV | Loading (A) | 33.7264 | 35.7779 | 30.7243 | 33.7705 | 35.818 | 30.7714 | 33.6962 | 35.7495 | 29.6931 | 33.6961 | 35.7494 | 29.693 | 33.9487 | 36.0519 | 29.6929
FN-Gulf | 7216_4GEO (Georgetown) 132 kV | Loading (MVA) | 8.1517 | 8.6299 | 7.4757 | 8.1635 | 8.6409 | 7.4878 | 8.2542 | 8.742 | 7.3024 | 8.2542 | 8.742 | 7.3023 | 8.3146 | 8.8141 | 7.3023
FN-Gulf | 7216_4GEO (Georgetown) 132 kV | Loading (MW) | 6.8184 | 7.549 | 1.6105 | 6.8184 | 7.549 | 1.6106 | 6.8175 | 7.5478 | 1.6078 | 6.8175 | 7.5478 | 1.6078 | 6.9149 | 7.6546 | 1.6078
FN-Gulf | 7216_4GEO (Georgetown) 132 kV | Power Factor | 0.83173 | 0.86951 | 0.21247 | 0.83051 | 0.8684 | 0.21213 | 0.82136 | 0.85829 | 0.21744 | 0.82136 | 0.85829 | 0.21744 | 0.82701 | 0.86326 | 0.21744
FN-Gulf | 7216_4GEO (Georgetown) 132 kV | Rating (A) | 298 | 344 | 342 | 298 | 344 | 342 | 298 | 344 | 342 | 298 | 344 | 342 | 298 | 344 | 342
FN-Gulf | 7216_4GEO (Georgetown) 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
FN-Gulf | 7216_4GEO (Georgetown) 132 kV | Min Voltage at Constrained Conductor | 139.5455 | 139.2605 | 140.478 | 139.5661 | 139.2821 | 140.4907 | 141.4274 | 141.1822 | 141.9867 | 141.4274 | 141.1821 | 141.9867 | 141.4019 | 141.1529 | 141.9867
FN-Gulf | 7216_4GEO (Georgetown) 132 kV | Contingency Outage | 3DIM_Dimbulah 66 kV | 3DIM_Dimbulah 66 kV | 3CRO_Croydon 66 kV | 3DIM_Dimbulah 66 kV | 3DIM_Dimbulah 66 kV | 3CRO_Croydon 66 kV | 3DIM_Dimbulah 66 kV | 3DIM_Dimbulah 66 kV | 3CRO_Croydon 66 kV | 3DIM_Dimbulah 66 kV | 3DIM_Dimbulah 66 kV | 3CRO_Croydon 66 kV | 3DIM_Dimbulah 66 kV | 3DIM_Dimbulah 66 kV | 3CRO_Croydon 66 kV
FN-Gulf | Kidston Solar Farm (Genex) | % of Rated A | 0.02856% | 0.02854% | 0.02872% | 0.02857% | 0.02855% | 0.02872% | 0.02892% | 0.02892% | 0.02894% | 0.02892% | 0.02892% | 0.02894% | 0.02892% | 0.02892% | 0.02894%
FN-Gulf | Kidston Solar Farm (Genex) | Limiting Line Name | Genex_Interconnection | Genex_Interconnection | Genex_Interconnection | Genex_Interconnection | Genex_Interconnection | Genex_Interconnection | Genex_Interconnection | Genex_Interconnection | Genex_Interconnection | Genex_Interconnection | Genex_Interconnection | Genex_Interconnection | Genex_Interconnection | Genex_Interconnection | Genex_Interconnection
FN-Gulf | Kidston Solar Farm (Genex) | Loading (A) | 0.28558 | 0.28543 | 0.2872 | 0.28566 | 0.28552 | 0.28725 | 0.28917 | 0.28915 | 0.28944 | 0.28917 | 0.28915 | 0.28944 | 0.28917 | 0.28915 | 0.28944
FN-Gulf | Kidston Solar Farm (Genex) | Loading (MVA) | 0.071052 | 0.070977 | 0.071859 | 0.071092 | 0.071019 | 0.071884 | 0.072849 | 0.07284 | 0.072983 | 0.072849 | 0.07284 | 0.072983 | 0.072849 | 0.07284 | 0.072983
FN-Gulf | Kidston Solar Farm (Genex) | Loading (MW) | 5.1632e-08 | 5.1577e-08 | 5.2215e-08 | 5.1661e-08 | 5.161e-08 | 5.2236e-08 | 5.2935e-08 | 5.2928e-08 | 5.3035e-08 | 5.2933e-08 | 5.2933e-08 | 5.3036e-08 | 5.2939e-08 | 5.2933e-08 | 5.3037e-08
FN-Gulf | Kidston Solar Farm (Genex) | Power Factor | 7.2668e-07 | 7.2667e-07 | 7.2663e-07 | 7.2668e-07 | 7.267e-07 | 7.2667e-07 | 7.2664e-07 | 7.2663e-07 | 7.2668e-07 | 7.2661e-07 | 7.267e-07 | 7.267e-07 | 7.2669e-07 | 7.267e-07 | 7.2671e-07
FN-Gulf | Kidston Solar Farm (Genex) | Rating (A) | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000
FN-Gulf | Kidston Solar Farm (Genex) | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
FN-Gulf | Kidston Solar Farm (Genex) | Min Voltage at Constrained Conductor | 143.6433 | 143.5681 | 144.4569 | 143.6843 | 143.6106 | 144.4823 | 145.4491 | 145.4397 | 145.5821 | 145.449 | 145.4397 | 145.5821 | 145.4489 | 145.4396 | 145.5821
FN-Gulf | Kidston Solar Farm (Genex) | Contingency Outage | 7216_4GEO (Georgetown) 132 kV | 7216_4GEO (Georgetown) 132 kV | 7216_4GEO (Georgetown) 132 kV | 7216_4GEO (Georgetown) 132 kV | 7216_4GEO (Georgetown) 132 kV | 7216_4GEO (Georgetown) 132 kV | 7216_4GEO (Georgetown) 132 kV | 7216_4GEO (Georgetown) 132 kV | 7216_4GEO (Georgetown) 132 kV | 7216_4GEO (Georgetown) 132 kV | 7216_4GEO (Georgetown) 132 kV | 7216_4GEO (Georgetown) 132 kV | 7216_4GEO (Georgetown) 132 kV | 7216_4GEO (Georgetown) 132 kV | 7216_4GEO (Georgetown) 132 kV
FN-Innisfail | 2BA1_Babinda No 1 22 kV | % of Rated A | 4.878% | 5.551% | 3.26% | 4.878% | 5.551% | 3.26% | 4.878% | 5.55% | 3.26% | 4.878% | 5.551% | 3.26% | 4.879% | 5.553% | 3.261%
FN-Innisfail | 2BA1_Babinda No 1 22 kV | Limiting Line Name | HV_LINE 20534_1 | HV_LINE 20534_1 | HV_LINE 20534_1 | HV_LINE 20534_1 | HV_LINE 20534_1 | HV_LINE 20534_1 | HV_LINE 20534_1 | HV_LINE 20534_1 | HV_LINE 20534_1 | HV_LINE 20534_1 | HV_LINE 20534_1 | HV_LINE 20534_1 | HV_LINE 20534_1 | HV_LINE 20534_1 | HV_LINE 20534_1
FN-Innisfail | 2BA1_Babinda No 1 22 kV | Loading (A) | 6.4396 | 9.8259 | 5.5426 | 6.439 | 9.8246 | 5.542 | 6.4388 | 9.8241 | 5.5418 | 6.4393 | 9.8252 | 5.5423 | 6.4406 | 9.8282 | 5.5433
FN-Innisfail | 2BA1_Babinda No 1 22 kV | Loading (MVA) | 0.25154 | 0.38586 | 0.22025 | 0.25153 | 0.38586 | 0.22025 | 0.25153 | 0.38585 | 0.22025 | 0.25153 | 0.38586 | 0.22025 | 0.25154 | 0.38586 | 0.22025
FN-Innisfail | 2BA1_Babinda No 1 22 kV | Loading (MW) | 0.24691 | 0.37737 | 0.21924 | 0.24691 | 0.37737 | 0.21924 | 0.24691 | 0.37737 | 0.21924 | 0.24691 | 0.37737 | 0.21924 | 0.24691 | 0.37737 | 0.21924
FN-Innisfail | 2BA1_Babinda No 1 22 kV | Power Factor | 0.98152 | 0.97788 | 0.99535 | 0.98153 | 0.97789 | 0.99535 | 0.98153 | 0.97789 | 0.99535 | 0.98152 | 0.97788 | 0.99535 | 0.98151 | 0.97786 | 0.99534
FN-Innisfail | 2BA1_Babinda No 1 22 kV | Rating (A) | 132 | 177 | 170 | 132 | 177 | 170 | 132 | 177 | 170 | 132 | 177 | 170 | 132 | 177 | 170
FN-Innisfail | 2BA1_Babinda No 1 22 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
FN-Innisfail | 2BA1_Babinda No 1 22 kV | Min Voltage at Constrained Conductor | 22.5518 | 22.6722 | 22.9426 | 22.5537 | 22.6751 | 22.9447 | 22.5544 | 22.6762 | 22.9455 | 22.5527 | 22.6738 | 22.9438 | 22.5485 | 22.6673 | 22.9396
FN-Innisfail | 2BA1_Babinda No 1 22 kV | Contingency Outage | 2BA2_Babinda No 2 22 kV | 2BA2_Babinda No 2 22 kV | 2BA2_Babinda No 2 22 kV | 2BA2_Babinda No 2 22 kV | 2BA2_Babinda No 2 22 kV | 2BA2_Babinda No 2 22 kV | 2BA2_Babinda No 2 22 kV | 2BA2_Babinda No 2 22 kV | 2BA2_Babinda No 2 22 kV | 2BA2_Babinda No 2 22 kV | 2BA2_Babinda No 2 22 kV | 2BA2_Babinda No 2 22 kV | 2BA2_Babinda No 2 22 kV | 2BA2_Babinda No 2 22 kV | 2BA2_Babinda No 2 22 kV
FN-Innisfail | 2BA2_Babinda No 2 22 kV | % of Rated A | 4.166% | 4.433% | 2.857% | 4.166% | 4.433% | 2.857% | 4.166% | 4.433% | 2.857% | 4.166% | 4.433% | 2.857% | 4.167% | 4.434% | 2.857%
FN-Innisfail | 2BA2_Babinda No 2 22 kV | Limiting Line Name | HV_LINE 38931_1 | HV_LINE 51735_1 | HV_LINE 38931_1 | HV_LINE 38931_1 | HV_LINE 51735_1 | HV_LINE 38931_1 | HV_LINE 38931_1 | HV_LINE 51735_1 | HV_LINE 38931_1 | HV_LINE 38931_1 | HV_LINE 51735_1 | HV_LINE 38931_1 | HV_LINE 38931_1 | HV_LINE 51735_1 | HV_LINE 38931_1
FN-Innisfail | 2BA2_Babinda No 2 22 kV | Loading (A) | 5.4993 | 7.4039 | 4.5423 | 5.4989 | 7.403 | 4.542 | 5.4987 | 7.4027 | 4.5419 | 5.4991 | 7.4034 | 4.5422 | 5.5 | 7.4055 | 4.5427
FN-Innisfail | 2BA2_Babinda No 2 22 kV | Loading (MVA) | 0.21485 | 0.29082 | 0.18056 | 0.21485 | 0.29082 | 0.18057 | 0.21486 | 0.29082 | 0.18057 | 0.21485 | 0.29082 | 0.18056 | 0.21485 | 0.29082 | 0.18055
FN-Innisfail | 2BA2_Babinda No 2 22 kV | Loading (MW) | 0.21452 | 0.29079 | 0.17499 | 0.21452 | 0.2908 | 0.17499 | 0.21452 | 0.2908 | 0.175 | 0.21452 | 0.2908 | 0.17499 | 0.21452 | 0.29079 | 0.17499
FN-Innisfail | 2BA2_Babinda No 2 22 kV | Power Factor | 0.99845 | 0.99991 | 0.96917 | 0.99845 | 0.99991 | 0.96915 | 0.99845 | 0.99991 | 0.96914 | 0.99845 | 0.99991 | 0.96916 | 0.99846 | 0.99991 | 0.96921
FN-Innisfail | 2BA2_Babinda No 2 22 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
FN-Innisfail | 2BA2_Babinda No 2 22 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
FN-Innisfail | 2BA2_Babinda No 2 22 kV | Min Voltage at Constrained Conductor | 22.556 | 22.677 | 22.9496 | 22.5578 | 22.6798 | 22.9517 | 22.5585 | 22.681 | 22.9525 | 22.5568 | 22.6786 | 22.9508 | 22.5526 | 22.672 | 22.9466
FN-Innisfail | 2BA2_Babinda No 2 22 kV | Contingency Outage | 2BA1_Babinda No 1 22 kV | 2BA1_Babinda No 1 22 kV | 2BA1_Babinda No 1 22 kV | 2BA1_Babinda No 1 22 kV | 2BA1_Babinda No 1 22 kV | 2BA1_Babinda No 1 22 kV | 2BA1_Babinda No 1 22 kV | 2BA1_Babinda No 1 22 kV | 2BA1_Babinda No 1 22 kV | 2BA1_Babinda No 1 22 kV | 2BA1_Babinda No 1 22 kV | 2BA1_Babinda No 1 22 kV | 2BA1_Babinda No 1 22 kV | 2BA1_Babinda No 1 22 kV | 2BA1_Babinda No 1 22 kV
FN-Innisfail | 2MOU_Mourilyan 22 kV | % of Rated A | 4.605% | 5.246% | 4.09% | 4.605% | 5.246% | 4.09% | 4.605% | 5.246% | 4.09% | 4.605% | 5.246% | 4.09% | 4.605% | 5.247% | 4.09%
FN-Innisfail | 2MOU_Mourilyan 22 kV | Limiting Line Name | HV_CABLE 1415_1 | HV_CABLE 1415_1 | HV_CABLE 1415_1 | HV_CABLE 1415_1 | HV_CABLE 1415_1 | HV_CABLE 1415_1 | HV_CABLE 1415_1 | HV_CABLE 1415_1 | HV_CABLE 1415_1 | HV_CABLE 1415_1 | HV_CABLE 1415_1 | HV_CABLE 1415_1 | HV_CABLE 1415_1 | HV_CABLE 1415_1 | HV_CABLE 1415_1
FN-Innisfail | 2MOU_Mourilyan 22 kV | Loading (A) | 4.6052 | 5.2464 | 4.0898 | 4.6052 | 5.2463 | 4.0899 | 4.6052 | 5.2462 | 4.0899 | 4.6052 | 5.2464 | 4.0898 | 4.6052 | 5.2467 | 4.0896
FN-Innisfail | 2MOU_Mourilyan 22 kV | Loading (MVA) | 0.17995 | 0.20613 | 0.16257 | 0.17996 | 0.20615 | 0.16259 | 0.17997 | 0.20616 | 0.1626 | 0.17995 | 0.20614 | 0.16258 | 0.17992 | 0.20609 | 0.16255
FN-Innisfail | 2MOU_Mourilyan 22 kV | Loading (MW) | 0.089991 | 0.12896 | 0.070107 | 0.089991 | 0.12896 | 0.070107 | 0.089991 | 0.12896 | 0.070107 | 0.089991 | 0.12896 | 0.070107 | 0.089992 | 0.12896 | 0.070107
FN-Innisfail | 2MOU_Mourilyan 22 kV | Power Factor | 0.50006 | 0.62559 | 0.43119 | 0.50002 | 0.62553 | 0.43114 | 0.5 | 0.6255 | 0.43112 | 0.50004 | 0.62556 | 0.43116 | 0.50014 | 0.6257 | 0.43126
FN-Innisfail | 2MOU_Mourilyan 22 kV | Rating (A) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
FN-Innisfail | 2MOU_Mourilyan 22 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
FN-Innisfail | 2MOU_Mourilyan 22 kV | Min Voltage at Constrained Conductor | 22.5597 | 22.6837 | 22.9503 | 22.5615 | 22.6866 | 22.9524 | 22.5622 | 22.6877 | 22.9533 | 22.5605 | 22.6853 | 22.9515 | 22.5564 | 22.6788 | 22.9474
FN-Innisfail | 2MOU_Mourilyan 22 kV | Contingency Outage | 2SI2_Silkwood No 2 22 kV | 2SI1_Silkwood No 1 22 kV | 2SI2_Silkwood No 2 22 kV | 2SI2_Silkwood No 2 22 kV | 2SI1_Silkwood No 1 22 kV | 2SI2_Silkwood No 2 22 kV | 2SI2_Silkwood No 2 22 kV | 2SI1_Silkwood No 1 22 kV | 2SI2_Silkwood No 2 22 kV | 2SI2_Silkwood No 2 22 kV | 2SI1_Silkwood No 1 22 kV | 2SI2_Silkwood No 2 22 kV | 2SI2_Silkwood No 2 22 kV | 2SI1_Silkwood No 1 22 kV | 2SI2_Silkwood No 2 22 kV
FN-Innisfail | 2SI1_Silkwood No 1 22 kV | % of Rated A | 1.275% | 1.252% | 0.8456% | 1.275% | 1.252% | 0.8456% | 1.275% | 1.252% | 0.8455% | 1.275% | 1.252% | 0.8456% | 1.276% | 1.252% | 0.8457%
FN-Innisfail | 2SI1_Silkwood No 1 22 kV | Limiting Line Name | HV_LINE 54592_1 | HV_LINE 54592_1 | HV_LINE 54592_1 | HV_LINE 54592_1 | HV_LINE 54592_1 | HV_LINE 54592_1 | HV_LINE 54592_1 | HV_LINE 54592_1 | HV_LINE 54592_1 | HV_LINE 54592_1 | HV_LINE 54592_1 | HV_LINE 54592_1 | HV_LINE 54592_1 | HV_LINE 54592_1 | HV_LINE 54592_1
FN-Innisfail | 2SI1_Silkwood No 1 22 kV | Loading (A) | 1.6835 | 2.0904 | 1.3445 | 1.6834 | 2.0902 | 1.3444 | 1.6834 | 2.0901 | 1.3444 | 1.6835 | 2.0903 | 1.3445 | 1.6837 | 2.0907 | 1.3446
FN-Innisfail | 2SI1_Silkwood No 1 22 kV | Loading (MVA) | 0.065762 | 0.0821 | 0.053432 | 0.065763 | 0.082102 | 0.053434 | 0.065764 | 0.082103 | 0.053435 | 0.065763 | 0.082101 | 0.053434 | 0.065759 | 0.082096 | 0.05343
FN-Innisfail | 2SI1_Silkwood No 1 22 kV | Loading (MW) | 0.056768 | 0.073847 | 0.045379 | 0.056769 | 0.073848 | 0.04538 | 0.056769 | 0.073848 | 0.04538 | 0.056769 | 0.073848 | 0.045379 | 0.056768 | 0.073846 | 0.045378
FN-Innisfail | 2SI1_Silkwood No 1 22 kV | Power Factor | 0.86324 | 0.89948 | 0.84928 | 0.86322 | 0.89946 | 0.84926 | 0.86322 | 0.89945 | 0.84925 | 0.86323 | 0.89947 | 0.84927 | 0.86327 | 0.89951 | 0.84931
FN-Innisfail | 2SI1_Silkwood No 1 22 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
FN-Innisfail | 2SI1_Silkwood No 1 22 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
FN-Innisfail | 2SI1_Silkwood No 1 22 kV | Min Voltage at Constrained Conductor | 22.5525 | 22.6754 | 22.9447 | 22.5543 | 22.6782 | 22.9468 | 22.555 | 22.6794 | 22.9476 | 22.5533 | 22.6769 | 22.9459 | 22.5492 | 22.6704 | 22.9418
FN-Innisfail | 2SI1_Silkwood No 1 22 kV | Contingency Outage | 2SI2_Silkwood No 2 22 kV | 2SI2_Silkwood No 2 22 kV | 2SI2_Silkwood No 2 22 kV | 2SI2_Silkwood No 2 22 kV | 2SI2_Silkwood No 2 22 kV | 2SI2_Silkwood No 2 22 kV | 2SI2_Silkwood No 2 22 kV | 2SI2_Silkwood No 2 22 kV | 2SI2_Silkwood No 2 22 kV | 2SI2_Silkwood No 2 22 kV | 2SI2_Silkwood No 2 22 kV | 2SI2_Silkwood No 2 22 kV | 2SI2_Silkwood No 2 22 kV | 2SI2_Silkwood No 2 22 kV | 2SI2_Silkwood No 2 22 kV
FN-Innisfail | 2SI2_Silkwood No 2 22 kV | % of Rated A | 1.781% | 2.48% | 1.422% | 1.78% | 2.48% | 1.421% | 1.78% | 2.48% | 1.421% | 1.781% | 2.48% | 1.421% | 1.781% | 2.481% | 1.422%
FN-Innisfail | 2SI2_Silkwood No 2 22 kV | Limiting Line Name | HV_CABLE 217_1 | HV_CABLE 217_1 | HV_CABLE 217_1 | HV_CABLE 217_1 | HV_CABLE 217_1 | HV_CABLE 217_1 | HV_CABLE 217_1 | HV_CABLE 217_1 | HV_CABLE 217_1 | HV_CABLE 217_1 | HV_CABLE 217_1 | HV_CABLE 217_1 | HV_CABLE 217_1 | HV_CABLE 217_1 | HV_CABLE 217_1
FN-Innisfail | 2SI2_Silkwood No 2 22 kV | Loading (A) | 1.7806 | 2.4801 | 1.4215 | 1.7804 | 2.4798 | 1.4214 | 1.7804 | 2.4796 | 1.4214 | 1.7805 | 2.4799 | 1.4215 | 1.7808 | 2.4806 | 1.4217
FN-Innisfail | 2SI2_Silkwood No 2 22 kV | Loading (MVA) | 0.069576 | 0.097442 | 0.056509 | 0.069576 | 0.097442 | 0.056509 | 0.069576 | 0.097442 | 0.056509 | 0.069576 | 0.097442 | 0.056509 | 0.069576 | 0.097442 | 0.056509
FN-Innisfail | 2SI2_Silkwood No 2 22 kV | Loading (MW) | 0.067578 | 0.095255 | 0.055878 | 0.067579 | 0.095256 | 0.055878 | 0.067579 | 0.095256 | 0.055878 | 0.067578 | 0.095256 | 0.055878 | 0.067578 | 0.095255 | 0.055877
FN-Innisfail | 2SI2_Silkwood No 2 22 kV | Power Factor | 0.96909 | 0.97597 | 0.98604 | 0.9691 | 0.97598 | 0.98604 | 0.9691 | 0.97598 | 0.98604 | 0.9691 | 0.97598 | 0.98604 | 0.96909 | 0.97597 | 0.98603
FN-Innisfail | 2SI2_Silkwood No 2 22 kV | Rating (A) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
FN-Innisfail | 2SI2_Silkwood No 2 22 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
FN-Innisfail | 2SI2_Silkwood No 2 22 kV | Min Voltage at Constrained Conductor | 22.5599 | 22.6839 | 22.9505 | 22.5617 | 22.6868 | 22.9526 | 22.5624 | 22.6879 | 22.9535 | 22.5607 | 22.6855 | 22.9517 | 22.5565 | 22.6789 | 22.9476
FN-Innisfail | 2SI2_Silkwood No 2 22 kV | Contingency Outage | 2SI1_Silkwood No 1 22 kV | 2SI1_Silkwood No 1 22 kV | 2SI1_Silkwood No 1 22 kV | 2SI1_Silkwood No 1 22 kV | 2SI1_Silkwood No 1 22 kV | 2SI1_Silkwood No 1 22 kV | 2SI1_Silkwood No 1 22 kV | 2SI1_Silkwood No 1 22 kV | 2SI1_Silkwood No 1 22 kV | 2SI1_Silkwood No 1 22 kV | 2SI1_Silkwood No 1 22 kV | 2SI1_Silkwood No 1 22 kV | 2SI1_Silkwood No 1 22 kV | 2SI1_Silkwood No 1 22 kV | 2SI1_Silkwood No 1 22 kV
FN-Tablelands Cooktown | 2HEL_Helenvale 22 kV | % of Rated A | 1.798% | 1.423% | 1.503% | 1.799% | 1.425% | 1.503% | 1.795% | 1.421% | 1.5% | 1.795% | 1.421% | 1.501% | 1.803% | 1.417% | 1.5%
FN-Tablelands Cooktown | 2HEL_Helenvale 22 kV | Limiting Line Name | HV_LINE 42881_2 | HV_LINE 42881_2 | HV_LINE 42881_2 | HV_LINE 42881_2 | HV_LINE 42881_2 | HV_LINE 42881_2 | HV_LINE 42881_2 | HV_LINE 42881_2 | HV_LINE 42881_2 | HV_LINE 42881_2 | HV_LINE 42881_2 | HV_LINE 42881_2 | HV_LINE 42881_2 | HV_LINE 42881_2 | HV_LINE 42881_2
FN-Tablelands Cooktown | 2HEL_Helenvale 22 kV | Loading (A) | 1.564 | 1.5654 | 1.5631 | 1.5653 | 1.5672 | 1.5635 | 1.5618 | 1.5628 | 1.5599 | 1.5619 | 1.5629 | 1.5613 | 1.5687 | 1.5584 | 1.5605
FN-Tablelands Cooktown | 2HEL_Helenvale 22 kV | Loading (MVA) | 0.060434 | 0.06054 | 0.060359 | 0.060531 | 0.060677 | 0.06039 | 0.060257 | 0.060339 | 0.060114 | 0.06027 | 0.060346 | 0.060223 | 0.060793 | 0.059996 | 0.060159
FN-Tablelands Cooktown | 2HEL_Helenvale 22 kV | Loading (MW) | 2.603e-05 | 2.6075e-05 | 2.5997e-05 | 2.6071e-05 | 2.6135e-05 | 2.6011e-05 | 2.5954e-05 | 2.5989e-05 | 2.5892e-05 | 2.5959e-05 | 2.5992e-05 | 2.5939e-05 | 2.6185e-05 | 2.5841e-05 | 2.5911e-05
FN-Tablelands Cooktown | 2HEL_Helenvale 22 kV | Power Factor | 0.00040912 | 0.00040912 | 0.00040912 | 0.00040912 | 0.00040912 | 0.00040912 | 0.00040912 | 0.00040912 | 0.00040912 | 0.00040912 | 0.00040912 | 0.00040912 | 0.00040912 | 0.00040912 | 0.00040912
FN-Tablelands Cooktown | 2HEL_Helenvale 22 kV | Rating (A) | 87 | 110 | 104 | 87 | 110 | 104 | 87 | 110 | 104 | 87 | 110 | 104 | 87 | 110 | 104
FN-Tablelands Cooktown | 2HEL_Helenvale 22 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
FN-Tablelands Cooktown | 2HEL_Helenvale 22 kV | Min Voltage at Constrained Conductor | 22.3084 | 22.3281 | 22.2946 | 22.3263 | 22.3534 | 22.3004 | 22.2758 | 22.2909 | 22.2494 | 22.2782 | 22.2923 | 22.2696 | 22.3747 | 22.2275 | 22.2577
FN-Tablelands Cooktown | 2HEL_Helenvale 22 kV | Contingency Outage | 7201_Craiglie No 1 132 kV | 7201_Craiglie No 1 132 kV | 3COO_Cooktown 66 kV | 7201_Craiglie No 1 132 kV | 7201_Craiglie No 1 132 kV | 3COO_Cooktown 66 kV | 2MOS_Mossman 22 kV | 3EVE_Evelyn 66 kV | 3CHI_Chillagoe 66 kV | 2MOS_Mossman 22 kV | 3EVE_Evelyn 66 kV | Mungana 66 kV | 7200_Craiglie No 2 132 kV | 3EVE_Evelyn 66 kV | 7200_Craiglie No 2 132 kV
FN-Tablelands Cooktown | 2KAT_Atherton 22 kV | % of Rated A | 1.826% | 2.897% | 1.541% | 1.824% | 2.893% | 1.541% | 1.826% | 2.896% | 1.542% | 1.826% | 2.895% | 1.542% | 1.826% | 2.898% | 1.543%
FN-Tablelands Cooktown | 2KAT_Atherton 22 kV | Limiting Line Name | HV_CABLE 122_1 | HV_CABLE 122_1 | HV_CABLE 122_1 | HV_CABLE 122_1 | HV_CABLE 122_1 | HV_CABLE 122_1 | HV_CABLE 122_1 | HV_CABLE 122_1 | HV_CABLE 122_1 | HV_CABLE 122_1 | HV_CABLE 122_1 | HV_CABLE 122_1 | HV_CABLE 122_1 | HV_CABLE 122_1 | HV_CABLE 122_1
FN-Tablelands Cooktown | 2KAT_Atherton 22 kV | Loading (A) | 1.8255 | 2.8966 | 1.5412 | 1.8241 | 2.8933 | 1.541 | 1.8261 | 2.8955 | 1.5422 | 1.8258 | 2.8954 | 1.542 | 1.8265 | 2.8976 | 1.5432
FN-Tablelands Cooktown | 2KAT_Atherton 22 kV | Loading (MVA) | 0.069621 | 0.11051 | 0.058893 | 0.069617 | 0.1105 | 0.058896 | 0.069622 | 0.11051 | 0.05888 | 0.069622 | 0.11051 | 0.058882 | 0.069623 | 0.11051 | 0.058866
FN-Tablelands Cooktown | 2KAT_Atherton 22 kV | Loading (MW) | 0.06837 | 0.10811 | 0.057796 | 0.068372 | 0.10812 | 0.057797 | 0.068369 | 0.10811 | 0.057792 | 0.06837 | 0.10811 | 0.057793 | 0.068369 | 0.10811 | 0.05779
FN-Tablelands Cooktown | 2KAT_Atherton 22 kV | Power Factor | 0.97695 | 0.97513 | 0.98137 | 0.97702 | 0.97519 | 0.98133 | 0.97693 | 0.97515 | 0.98153 | 0.97694 | 0.97515 | 0.98151 | 0.97691 | 0.97511 | 0.98172
FN-Tablelands Cooktown | 2KAT_Atherton 22 kV | Rating (A) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
FN-Tablelands Cooktown | 2KAT_Atherton 22 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
FN-Tablelands Cooktown | 2KAT_Atherton 22 kV | Min Voltage at Constrained Conductor | 22.019 | 22.0264 | 22.0614 | 22.0349 | 22.0509 | 22.0665 | 22.0125 | 22.034 | 22.0432 | 22.0157 | 22.0353 | 22.0459 | 22.0079 | 22.0187 | 22.0234
FN-Tablelands Cooktown | 2KAT_Atherton 22 kV | Contingency Outage | 3AT2_Atherton No 2 66 kV | 7285_4LAK (Lakeland) 132kV | 3DIM_Dimbulah 66 kV | 3AT2_Atherton No 2 66 kV | 7285_4LAK (Lakeland) 132kV | 3DIM_Dimbulah 66 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 3DIM_Dimbulah 66 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 3DIM_Dimbulah 66 kV | 7285_4LAK (Lakeland) 132kV | 3AT2_Atherton No 2 66 kV | 3DIM_Dimbulah 66 kV
FN-Tablelands Cooktown | 2MOS_Mossman 22 kV | % of Rated A | 4.906% | 3.916% | 2.815% | 4.904% | 3.912% | 2.815% | 4.833% | 3.863% | 2.691% | 4.833% | 3.863% | 2.691% | 4.843% | 3.874% | 2.693%
FN-Tablelands Cooktown | 2MOS_Mossman 22 kV | Limiting Line Name | HV_LINE 27084_1 | HV_LINE 27084_1 | HV_LINE 27084_1 | HV_LINE 27084_1 | HV_LINE 27084_1 | HV_LINE 27084_1 | HV_LINE 27084_1 | HV_LINE 27084_1 | HV_LINE 27084_1 | HV_LINE 27084_1 | HV_LINE 27084_1 | HV_LINE 27084_1 | HV_LINE 27084_1 | HV_LINE 27084_1 | HV_LINE 27084_1
FN-Tablelands Cooktown | 2MOS_Mossman 22 kV | Loading (A) | 6.4765 | 6.5393 | 4.476 | 6.4733 | 6.5325 | 4.4751 | 6.38 | 6.4511 | 4.2788 | 6.3802 | 6.4515 | 4.2787 | 6.3925 | 6.4694 | 4.2811
FN-Tablelands Cooktown | 2MOS_Mossman 22 kV | Loading (MVA) | 0.24571 | 0.24784 | 0.16967 | 0.24572 | 0.24787 | 0.16968 | 0.24612 | 0.24821 | 0.17106 | 0.24612 | 0.2482 | 0.17106 | 0.24606 | 0.24813 | 0.17104
FN-Tablelands Cooktown | 2MOS_Mossman 22 kV | Loading (MW) | 0.21619 | 0.22327 | 0.15142 | 0.2162 | 0.22329 | 0.15143 | 0.21653 | 0.22356 | 0.15252 | 0.21653 | 0.22356 | 0.15253 | 0.21648 | 0.2235 | 0.15251
FN-Tablelands Cooktown | 2MOS_Mossman 22 kV | Power Factor | 0.87987 | 0.90083 | 0.89244 | 0.87986 | 0.90082 | 0.89244 | 0.87975 | 0.9007 | 0.89164 | 0.87975 | 0.9007 | 0.89164 | 0.87976 | 0.90073 | 0.89165
FN-Tablelands Cooktown | 2MOS_Mossman 22 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
FN-Tablelands Cooktown | 2MOS_Mossman 22 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
FN-Tablelands Cooktown | 2MOS_Mossman 22 kV | Min Voltage at Constrained Conductor | 21.9037 | 21.8817 | 21.8855 | 21.9158 | 21.9068 | 21.8911 | 22.2721 | 22.2134 | 23.0815 | 22.2716 | 22.2121 | 23.0824 | 22.224 | 22.1438 | 23.0666
FN-Tablelands Cooktown | 2MOS_Mossman 22 kV | Contingency Outage | 3DIM_Dimbulah 66 kV | 3AT2_Atherton No 2 66 kV | Mungana 66 kV | 3DIM_Dimbulah 66 kV | 3AT2_Atherton No 2 66 kV | Mungana 66 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV
FN-Tablelands Cooktown | 2WH1_Ravenshoe 22 kV | % of Rated A | 0.8462% | 0.8454% | 0.8538% | 0.8467% | 0.8465% | 0.8517% | 0.8457% | 0.8438% | 0.8529% | 0.8459% | 0.8439% | 0.853% | 0.8441% | 0.8458% | 0.8521%
FN-Tablelands Cooktown | 2WH1_Ravenshoe 22 kV | Limiting Line Name | HV_CABLE 272_1 | HV_CABLE 272_1 | HV_CABLE 272_1 | HV_CABLE 272_1 | HV_CABLE 272_1 | HV_CABLE 272_1 | HV_CABLE 272_1 | HV_CABLE 272_1 | HV_CABLE 272_1 | HV_CABLE 272_1 | HV_CABLE 272_1 | HV_CABLE 272_1 | HV_CABLE 272_1 | HV_CABLE 272_1 | HV_CABLE 272_1
FN-Tablelands Cooktown | 2WH1_Ravenshoe 22 kV | Loading (A) | 0.84619 | 0.84538 | 0.85383 | 0.8467 | 0.84647 | 0.85173 | 0.84573 | 0.8438 | 0.85289 | 0.8459 | 0.84389 | 0.85301 | 0.84415 | 0.84578 | 0.85209
FN-Tablelands Cooktown | 2WH1_Ravenshoe 22 kV | Loading (MVA) | 0.032949 | 0.032886 | 0.033547 | 0.032989 | 0.032971 | 0.033382 | 0.032913 | 0.032763 | 0.033473 | 0.032926 | 0.032771 | 0.033482 | 0.03279 | 0.032917 | 0.03341
FN-Tablelands Cooktown | 2WH1_Ravenshoe 22 kV | Loading (MW) | 0.00065887 | 0.00065762 | 0.00067083 | 0.00065966 | 0.0006593 | 0.00066753 | 0.00065815 | 0.00065515 | 0.00066935 | 0.00065842 | 0.0006553 | 0.00066953 | 0.0006557 | 0.00065824 | 0.0006681
FN-Tablelands Cooktown | 2WH1_Ravenshoe 22 kV | Power Factor | 0.019997 | 0.019997 | 0.019997 | 0.019997 | 0.019997 | 0.019997 | 0.019997 | 0.019997 | 0.019997 | 0.019997 | 0.019997 | 0.019997 | 0.019997 | 0.019997 | 0.019997
FN-Tablelands Cooktown | 2WH1_Ravenshoe 22 kV | Rating (A) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
FN-Tablelands Cooktown | 2WH1_Ravenshoe 22 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
FN-Tablelands Cooktown | 2WH1_Ravenshoe 22 kV | Min Voltage at Constrained Conductor | 22.4808 | 22.4595 | 22.684 | 22.4944 | 22.4883 | 22.6281 | 22.4687 | 22.4173 | 22.659 | 22.4732 | 22.42 | 22.662 | 22.4267 | 22.4701 | 22.6378
FN-Tablelands Cooktown | 2WH1_Ravenshoe 22 kV | Contingency Outage | Mungana 66 kV | 7200_Craiglie No 2 132 kV | 3CHI_Chillagoe 66 kV | Mungana 66 kV | 7200_Craiglie No 2 132 kV | 3COO_Cooktown 66 kV | Mungana 66 kV | Mungana 66 kV | 3CHI_Chillagoe 66 kV | Mungana 66 kV | Mungana 66 kV | 3CHI_Chillagoe 66 kV | Mungana 66 kV | 3DIM_Dimbulah 66 kV | 3CHI_Chillagoe 66 kV
FN-Tablelands Cooktown | 2WH2_Ravenshoe 22kV | % of Rated A | 0.2368% | 0.1542% | 0.1574% | 0.237% | 0.1544% | 0.157% | 0.2367% | 0.1539% | 0.1572% | 0.2367% | 0.1539% | 0.1572% | 0.2362% | 0.1543% | 0.1571%
FN-Tablelands Cooktown | 2WH2_Ravenshoe 22kV | Limiting Line Name | HV_LINE 35947_1 | HV_LINE 35947_1 | HV_LINE 35947_1 | HV_LINE 35947_1 | HV_LINE 35947_1 | HV_LINE 35947_1 | HV_LINE 35947_1 | HV_LINE 35947_1 | HV_LINE 35947_1 | HV_LINE 35947_1 | HV_LINE 35947_1 | HV_LINE 35947_1 | HV_LINE 35947_1 | HV_LINE 35947_1 | HV_LINE 35947_1
FN-Tablelands Cooktown | 2WH2_Ravenshoe 22kV | Loading (A) | 0.58965 | 0.58909 | 0.59498 | 0.59001 | 0.58984 | 0.59351 | 0.58933 | 0.58798 | 0.59432 | 0.58945 | 0.58805 | 0.5944 | 0.58823 | 0.58937 | 0.59377
FN-Tablelands Cooktown | 2WH2_Ravenshoe 22kV | Loading (MVA) | 0.022959 | 0.022915 | 0.023375 | 0.022986 | 0.022974 | 0.02326 | 0.022934 | 0.022829 | 0.023324 | 0.022943 | 0.022834 | 0.02333 | 0.022848 | 0.022937 | 0.02328
FN-Tablelands Cooktown | 2WH2_Ravenshoe 22kV | Loading (MW) | 0.00036132 | 0.00036063 | 0.00036788 | 0.00036176 | 0.00036156 | 0.00036607 | 0.00036093 | 0.00035928 | 0.00036707 | 0.00036107 | 0.00035936 | 0.00036717 | 0.00035958 | 0.00036098 | 0.00036638
FN-Tablelands Cooktown | 2WH2_Ravenshoe 22kV | Power Factor | 0.015738 | 0.015738 | 0.015738 | 0.015738 | 0.015738 | 0.015738 | 0.015738 | 0.015738 | 0.015738 | 0.015738 | 0.015738 | 0.015738 | 0.015738 | 0.015738 | 0.015738
FN-Tablelands Cooktown | 2WH2_Ravenshoe 22kV | Rating (A) | 249 | 382 | 378 | 249 | 382 | 378 | 249 | 382 | 378 | 249 | 382 | 378 | 249 | 382 | 378
FN-Tablelands Cooktown | 2WH2_Ravenshoe 22kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
FN-Tablelands Cooktown | 2WH2_Ravenshoe 22kV | Min Voltage at Constrained Conductor | 22.4797 | 22.4584 | 22.6829 | 22.4933 | 22.4872 | 22.627 | 22.4676 | 22.4162 | 22.6579 | 22.4721 | 22.4189 | 22.6609 | 22.4256 | 22.4691 | 22.6367
FN-Tablelands Cooktown | 2WH2_Ravenshoe 22kV | Contingency Outage | Mungana 66 kV | 7200_Craiglie No 2 132 kV | 3CHI_Chillagoe 66 kV | Mungana 66 kV | 7200_Craiglie No 2 132 kV | 3COO_Cooktown 66 kV | Mungana 66 kV | Mungana 66 kV | 3CHI_Chillagoe 66 kV | Mungana 66 kV | Mungana 66 kV | 3CHI_Chillagoe 66 kV | Mungana 66 kV | 3DIM_Dimbulah 66 kV | 3CHI_Chillagoe 66 kV
FN-Tablelands Cooktown | 3AT1_Atherton No 1 66 kV | % of Rated A | 35.02% | 40.76% | 25.89% | 34.88% | 40.52% | 25.8% | 34.88% | 40.53% | 25.84% | 35.12% | 40.83% | 26.01% | 35.69% | 41.59% | 26.38%
FN-Tablelands Cooktown | 3AT1_Atherton No 1 66 kV | Limiting Line Name | TR_LINE 4642_1 | TR_CABLE 15_1 | TR_LINE 4407_1 | TR_LINE 4642_1 | TR_CABLE 15_1 | TR_LINE 4407_1 | TR_LINE 4642_1 | TR_CABLE 15_1 | TR_LINE 4407_1 | TR_LINE 4642_1 | TR_CABLE 15_1 | TR_LINE 4407_1 | TR_LINE 4642_1 | TR_CABLE 15_1 | TR_LINE 4407_1
FN-Tablelands Cooktown | 3AT1_Atherton No 1 66 kV | Loading (A) | 191.9169 | 228.2299 | 134.9062 | 191.1155 | 226.8955 | 134.4188 | 191.123 | 226.9675 | 134.6263 | 192.4367 | 228.6307 | 135.5075 | 195.577 | 232.91 | 137.4526
FN-Tablelands Cooktown | 3AT1_Atherton No 1 66 kV | Loading (MVA) | 22.8629 | 27.088 | 16.1976 | 22.7808 | 26.9591 | 16.1433 | 22.7688 | 26.9597 | 16.1485 | 22.9308 | 27.1619 | 16.257 | 23.2586 | 27.5993 | 16.474
FN-Tablelands Cooktown | 3AT1_Atherton No 1 66 kV | Loading (MW) | 22.8243 | 27.0294 | 16.1683 | 22.7433 | 26.9184 | 16.1132 | 22.7382 | 26.9188 | 16.1056 | 22.8989 | 27.1186 | 16.2156 | 23.2227 | 27.532 | 16.4362
FN-Tablelands Cooktown | 3AT1_Atherton No 1 66 kV | Power Factor | 0.99831 | 0.99691 | 0.99817 | 0.99835 | 0.99757 | 0.99811 | 0.99866 | 0.99756 | 0.99732 | 0.99861 | 0.99748 | 0.99743 | 0.99846 | 0.99665 | 0.99768
FN-Tablelands Cooktown | 3AT1_Atherton No 1 66 kV | Rating (A) | 548 | 560 | 521 | 548 | 560 | 521 | 548 | 560 | 521 | 548 | 560 | 521 | 548 | 560 | 521
FN-Tablelands Cooktown | 3AT1_Atherton No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
FN-Tablelands Cooktown | 3AT1_Atherton No 1 66 kV | Min Voltage at Constrained Conductor | 67.4588 | 68.5242 | 69.2947 | 67.5064 | 68.5991 | 69.3127 | 67.4788 | 68.5789 | 69.229 | 67.4841 | 68.5908 | 69.2409 | 67.3194 | 68.4147 | 69.1717
FN-Tablelands Cooktown | 3AT1_Atherton No 1 66 kV | Contingency Outage | 3AT2_Atherton No 2 66 kV | 3AT2_Atherton No 2 66 kV | 3AT2_Atherton No 2 66 kV | 3AT2_Atherton No 2 66 kV | 3AT2_Atherton No 2 66 kV | 3AT2_Atherton No 2 66 kV | 3AT2_Atherton No 2 66 kV | 3AT2_Atherton No 2 66 kV | 3AT2_Atherton No 2 66 kV | 3AT2_Atherton No 2 66 kV | 3AT2_Atherton No 2 66 kV | 3AT2_Atherton No 2 66 kV | 3AT2_Atherton No 2 66 kV | 3AT2_Atherton No 2 66 kV | 3AT2_Atherton No 2 66 kV
FN-Tablelands Cooktown | 3AT2_Atherton No 2 66 kV | % of Rated A | 35.02% | 40.76% | 25.89% | 34.87% | 40.52% | 25.8% | 34.88% | 40.53% | 25.84% | 35.12% | 40.83% | 26.01% | 35.69% | 41.59% | 26.38%
FN-Tablelands Cooktown | 3AT2_Atherton No 2 66 kV | Limiting Line Name | TR_LINE 4640_1 | TR_CABLE 14_1 | TR_LINE 4672_1 | TR_LINE 4640_1 | TR_CABLE 14_1 | TR_LINE 4672_1 | TR_LINE 4640_1 | TR_CABLE 14_1 | TR_LINE 4672_1 | TR_LINE 4640_1 | TR_CABLE 14_1 | TR_LINE 4672_1 | TR_LINE 4640_1 | TR_CABLE 14_1 | TR_LINE 4672_1
FN-Tablelands Cooktown | 3AT2_Atherton No 2 66 kV | Loading (A) | 191.9159 | 228.2289 | 134.9076 | 191.1145 | 226.8945 | 134.4202 | 191.1221 | 226.9665 | 134.628 | 192.4358 | 228.6297 | 135.5092 | 195.576 | 232.909 | 137.4542
FN-Tablelands Cooktown | 3AT2_Atherton No 2 66 kV | Loading (MVA) | 22.8629 | 27.088 | 16.1979 | 22.7808 | 26.9591 | 16.1435 | 22.7689 | 26.9597 | 16.1488 | 22.9308 | 27.162 | 16.2573 | 23.2586 | 27.5993 | 16.4743
FN-Tablelands Cooktown | 3AT2_Atherton No 2 66 kV | Loading (MW) | 22.8243 | 27.0295 | 16.1684 | 22.7433 | 26.9185 | 16.1132 | 22.7383 | 26.9189 | 16.1057 | 22.8989 | 27.1187 | 16.2157 | 23.2227 | 27.5322 | 16.4363
FN-Tablelands Cooktown | 3AT2_Atherton No 2 66 kV | Power Factor | 0.99831 | 0.99691 | 0.99816 | 0.99835 | 0.99757 | 0.9981 | 0.99866 | 0.99756 | 0.99731 | 0.99861 | 0.99748 | 0.99741 | 0.99846 | 0.99665 | 0.99766
FN-Tablelands Cooktown | 3AT2_Atherton No 2 66 kV | Rating (A) | 548 | 560 | 521 | 548 | 560 | 521 | 548 | 560 | 521 | 548 | 560 | 521 | 548 | 560 | 521
FN-Tablelands Cooktown | 3AT2_Atherton No 2 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
FN-Tablelands Cooktown | 3AT2_Atherton No 2 66 kV | Min Voltage at Constrained Conductor | 67.4591 | 68.5245 | 69.2952 | 67.5068 | 68.5994 | 69.3132 | 67.4791 | 68.5792 | 69.2294 | 67.4844 | 68.5911 | 69.2413 | 67.3197 | 68.415 | 69.1722
FN-Tablelands Cooktown | 3AT2_Atherton No 2 66 kV | Contingency Outage | 3AT1_Atherton No 1 66 kV | 3AT1_Atherton No 1 66 kV | 3AT1_Atherton No 1 66 kV | 3AT1_Atherton No 1 66 kV | 3AT1_Atherton No 1 66 kV | 3AT1_Atherton No 1 66 kV | 3AT1_Atherton No 1 66 kV | 3AT1_Atherton No 1 66 kV | 3AT1_Atherton No 1 66 kV | 3AT1_Atherton No 1 66 kV | 3AT1_Atherton No 1 66 kV | 3AT1_Atherton No 1 66 kV | 3AT1_Atherton No 1 66 kV | 3AT1_Atherton No 1 66 kV | 3AT1_Atherton No 1 66 kV
FN-Tablelands Cooktown | 3CHI_Chillagoe 66 kV | % of Rated A | 8.958% | 8.497% | 8.391% | 8.951% | 8.487% | 8.389% | 8.968% | 8.495% | 8.382% | 8.966% | 8.493% | 8.38% | 8.988% | 8.526% | 8.387%
FN-Tablelands Cooktown | 3CHI_Chillagoe 66 kV | Limiting Line Name | TR_LINE 104013_1 | TR_LINE 104013_1 | TR_LINE 104013_1 | TR_LINE 104013_1 | TR_LINE 104013_1 | TR_LINE 104013_1 | TR_LINE 104013_1 | TR_LINE 104013_1 | TR_LINE 104013_1 | TR_LINE 104013_1 | TR_LINE 104013_1 | TR_LINE 104013_1 | TR_LINE 104013_1 | TR_LINE 104013_1 | TR_LINE 104013_1
FN-Tablelands Cooktown | 3CHI_Chillagoe 66 kV | Loading (A) | 49.0873 | 49.2005 | 43.7166 | 49.0507 | 49.1406 | 43.7042 | 49.1471 | 49.1845 | 43.6696 | 49.1321 | 49.1729 | 43.6606 | 49.2553 | 49.3631 | 43.6968
FN-Tablelands Cooktown | 3CHI_Chillagoe 66 kV | Loading (MVA) | 5.4755 | 5.4665 | 4.9702 | 5.4754 | 5.4663 | 4.9702 | 5.4757 | 5.4664 | 4.9701 | 5.4756 | 5.4664 | 4.97 | 5.4761 | 5.467 | 4.9702
FN-Tablelands Cooktown | 3CHI_Chillagoe 66 kV | Loading (MW) | 5.1686 | 5.1702 | 4.6842 | 5.1686 | 5.1702 | 4.6842 | 5.1687 | 5.1702 | 4.6842 | 5.1687 | 5.1702 | 4.6842 | 5.1687 | 5.1703 | 4.6842
FN-Tablelands Cooktown | 3CHI_Chillagoe 66 kV | Power Factor | 0.94395 | 0.9458 | 0.94244 | 0.94397 | 0.94583 | 0.94245 | 0.94392 | 0.94581 | 0.94247 | 0.94393 | 0.94581 | 0.94247 | 0.94387 | 0.94572 | 0.94245
FN-Tablelands Cooktown | 3CHI_Chillagoe 66 kV | Rating (A) | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521
FN-Tablelands Cooktown | 3CHI_Chillagoe 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
FN-Tablelands Cooktown | 3CHI_Chillagoe 66 kV | Min Voltage at Constrained Conductor | 64.4014 | 64.1471 | 65.6403 | 64.448 | 64.2229 | 65.6583 | 64.3251 | 64.1672 | 65.7086 | 64.3442 | 64.182 | 65.7216 | 64.1884 | 63.9422 | 65.6691
FN-Tablelands Cooktown | 3CHI_Chillagoe 66 kV | Contingency Outage | 7201_Craiglie No 1 132 kV | 7285_4LAK (Lakeland) 132kV | 7200_Craiglie No 2 132 kV | 7201_Craiglie No 1 132 kV | 7285_4LAK (Lakeland) 132kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV
FN-Tablelands Cooktown | 3COO_Cooktown 66 kV | % of Rated A | 14.99% | 13.13% | 8.814% | 14.98% | 13.12% | 8.811% | 15.11% | 13.23% | 8.766% | 15.11% | 13.23% | 8.768% | 15.34% | 13.44% | 8.952%
FN-Tablelands Cooktown | 3COO_Cooktown 66 kV | Limiting Line Name | TR_CABLE 12_1 | TR_CABLE 12_1 | TR_CABLE 12_1 | TR_CABLE 12_1 | TR_CABLE 12_1 | TR_CABLE 12_1 | TR_CABLE 12_1 | TR_CABLE 12_1 | TR_CABLE 12_1 | TR_CABLE 12_1 | TR_CABLE 12_1 | TR_CABLE 12_1 | TR_CABLE 12_1 | TR_CABLE 12_1 | TR_CABLE 12_1
FN-Tablelands Cooktown | 3COO_Cooktown 66 kV | Loading (A) | 37.1845 | 32.5722 | 21.8588 | 37.154 | 32.5391 | 21.8514 | 37.4682 | 32.8001 | 21.74 | 37.4674 | 32.8007 | 21.7459 | 38.0394 | 33.3305 | 22.2022
FN-Tablelands Cooktown | 3COO_Cooktown 66 kV | Loading (MVA) | 4.2879 | 3.761 | 2.5307 | 4.2879 | 3.761 | 2.5307 | 4.2878 | 3.7613 | 2.5306 | 4.2878 | 3.7613 | 2.5306 | 4.386 | 3.847 | 2.5883
FN-Tablelands Cooktown | 3COO_Cooktown 66 kV | Loading (MW) | 4.2047 | 3.6903 | 2.4868 | 4.2047 | 3.6903 | 2.4868 | 4.2047 | 3.6903 | 2.4868 | 4.2047 | 3.6903 | 2.4868 | 4.3004 | 3.7742 | 2.5433
FN-Tablelands Cooktown | 3COO_Cooktown 66 kV | Power Factor | 0.97999 | 0.98051 | 0.98165 | 0.98 | 0.98051 | 0.98165 | 0.98002 | 0.98046 | 0.98168 | 0.98002 | 0.98046 | 0.98167 | 0.97989 | 0.98042 | 0.98163
FN-Tablelands Cooktown | 3COO_Cooktown 66 kV | Rating (A) | 248 | 248 | 248 | 248 | 248 | 248 | 248 | 248 | 248 | 248 | 248 | 248 | 248 | 248 | 248
FN-Tablelands Cooktown | 3COO_Cooktown 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
FN-Tablelands Cooktown | 3COO_Cooktown 66 kV | Min Voltage at Constrained Conductor | 66.5774 | 66.6653 | 66.8421 | 66.6314 | 66.7326 | 66.8645 | 66.0705 | 66.206 | 67.2048 | 66.072 | 66.2047 | 67.1869 | 66.5691 | 66.6372 | 67.3058
FN-Tablelands Cooktown | 3COO_Cooktown 66 kV | Contingency Outage | 7201_Craiglie No 1 132 kV | 3AT2_Atherton No 2 66 kV | 7201_Craiglie No 1 132 kV | 7201_Craiglie No 1 132 kV | 3AT2_Atherton No 2 66 kV | 7201_Craiglie No 1 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 3RA1_Ravenshoe No 1 66 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 2MOS_Mossman 22 kV | 3CHI_Chillagoe 66 kV | 3CHI_Chillagoe 66 kV | 3CHI_Chillagoe 66 kV
FN-Tablelands Cooktown | 3DIM_Dimbulah 66 kV | % of Rated A | 45.36% | 37.17% | 30.95% | 45.32% | 37.12% | 30.94% | 45.41% | 37.15% | 30.91% | 45.4% | 37.14% | 30.91% | 45.87% | 37.59% | 31.12%
FN-Tablelands Cooktown | 3DIM_Dimbulah 66 kV | Limiting Line Name | TR_LINE 2161_1 | TR_LINE 2161_1 | TR_LINE 2161_1 | TR_LINE 2161_1 | TR_LINE 2161_1 | TR_LINE 2161_1 | TR_LINE 2161_1 | TR_LINE 2161_1 | TR_LINE 2161_1 | TR_LINE 2161_1 | TR_LINE 2161_1 | TR_LINE 2161_1 | TR_LINE 2161_1 | TR_LINE 2161_1 | TR_LINE 2161_1
FN-Tablelands Cooktown | 3DIM_Dimbulah 66 kV | Loading (A) | 98.8813 | 99.9741 | 78.2995 | 98.8076 | 99.8526 | 78.2744 | 99.002 | 99.9417 | 78.2114 | 98.9718 | 99.9181 | 78.1951 | 100.0039 | 101.1082 | 78.723
FN-Tablelands Cooktown | 3DIM_Dimbulah 66 kV | Loading (MVA) | 11.6145 | 11.7007 | 9.2719 | 11.6132 | 11.6985 | 9.2712 | 11.6167 | 11.7001 | 9.2701 | 11.6161 | 11.6997 | 9.2698 | 11.7155 | 11.8035 | 9.3271
FN-Tablelands Cooktown | 3DIM_Dimbulah 66 kV | Loading (MW) | 11.1912 | 11.2763 | 8.9934 | 11.1908 | 11.2755 | 8.9931 | 11.1919 | 11.2761 | 8.9928 | 11.1917 | 11.2759 | 8.9927 | 11.283 | 11.37 | 9.0466
FN-Tablelands Cooktown | 3DIM_Dimbulah 66 kV | Power Factor | 0.96343 | 0.96362 | 0.96969 | 0.96351 | 0.96374 | 0.96973 | 0.96332 | 0.96365 | 0.96981 | 0.96335 | 0.96368 | 0.96983 | 0.96298 | 0.96317 | 0.96965
FN-Tablelands Cooktown | 3DIM_Dimbulah 66 kV | Rating (A) | 218 | 269 | 253 | 218 | 269 | 253 | 218 | 269 | 253 | 218 | 269 | 253 | 218 | 269 | 253
FN-Tablelands Cooktown | 3DIM_Dimbulah 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
FN-Tablelands Cooktown | 3DIM_Dimbulah 66 kV | Min Voltage at Constrained Conductor | 67.7522 | 67.5067 | 68.3308 | 67.7951 | 67.5766 | 68.3475 | 67.6818 | 67.5253 | 68.3945 | 67.6994 | 67.5389 | 68.4066 | 67.572 | 67.3346 | 68.367
FN-Tablelands Cooktown | 3DIM_Dimbulah 66 kV | Contingency Outage | 7201_Craiglie No 1 132 kV | 7285_4LAK (Lakeland) 132kV | 7200_Craiglie No 2 132 kV | 7201_Craiglie No 1 132 kV | 7285_4LAK (Lakeland) 132kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV
FN-Tablelands Cooktown | 3EVE_Evelyn 66 kV | % of Rated A | 13.37% | 8.424% | 6.895% | 13.36% | 8.408% | 6.893% | 13.36% | 8.411% | 6.886% | 13.36% | 8.411% | 6.9% | 13.4% | 8.445% | 6.892%
FN-Tablelands Cooktown | 3EVE_Evelyn 66 kV | Limiting Line Name | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1
FN-Tablelands Cooktown | 3EVE_Evelyn 66 kV | Loading (A) | 22.5923 | 20.3009 | 16.2041 | 22.575 | 20.2628 | 16.1993 | 22.585 | 20.2696 | 16.181 | 22.5831 | 20.2707 | 16.2143 | 22.6429 | 20.3513 | 16.1957
FN-Tablelands Cooktown | 3EVE_Evelyn 66 kV | Loading (MVA) | 2.6242 | 2.3382 | 1.8958 | 2.6241 | 2.338 | 1.8958 | 2.6241 | 2.338 | 1.8957 | 2.6241 | 2.338 | 1.8959 | 2.6245 | 2.3385 | 1.8958
FN-Tablelands Cooktown | 3EVE_Evelyn 66 kV | Loading (MW) | 2.5664 | 2.3011 | 1.8726 | 2.5664 | 2.3011 | 1.8726 | 2.5664 | 2.3011 | 1.8726 | 2.5664 | 2.3011 | 1.8726 | 2.5664 | 2.3011 | 1.8726
FN-Tablelands Cooktown | 3EVE_Evelyn 66 kV | Power Factor | 0.97797 | 0.98413 | 0.98773 | 0.97802 | 0.98423 | 0.98774 | 0.97799 | 0.98421 | 0.98781 | 0.978 | 0.98421 | 0.98769 | 0.97785 | 0.98399 | 0.98776
FN-Tablelands Cooktown | 3EVE_Evelyn 66 kV | Rating (A) | 169 | 241 | 235 | 169 | 241 | 235 | 169 | 241 | 235 | 169 | 241 | 235 | 169 | 241 | 235
FN-Tablelands Cooktown | 3EVE_Evelyn 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
FN-Tablelands Cooktown | 3EVE_Evelyn 66 kV | Min Voltage at Constrained Conductor | 67.0616 | 66.4979 | 67.5486 | 67.1097 | 66.6161 | 67.5675 | 67.0818 | 66.5949 | 67.6392 | 67.0872 | 66.5914 | 67.5087 | 66.9209 | 66.3425 | 67.5814
FN-Tablelands Cooktown | 3EVE_Evelyn 66 kV | Contingency Outage | 3AT2_Atherton No 2 66 kV | 3AT2_Atherton No 2 66 kV | Mungana 66 kV | 3AT2_Atherton No 2 66 kV | 3AT2_Atherton No 2 66 kV | Mungana 66 kV | 3AT2_Atherton No 2 66 kV | 3AT2_Atherton No 2 66 kV | 3DIM_Dimbulah 66 kV | 3AT2_Atherton No 2 66 kV | 3AT2_Atherton No 2 66 kV | Mungana 66 kV | 3AT2_Atherton No 2 66 kV | 3AT2_Atherton No 2 66 kV | 3DIM_Dimbulah 66 kV
FN-Tablelands Cooktown | 3HLA_Helenvale 66 kV | % of Rated A | 11.02% | 9.631% | 6.789% | 11.01% | 9.622% | 6.787% | 11.1% | 9.698% | 6.753% | 11.1% | 9.698% | 6.755% | 11.23% | 9.813% | 6.874%
FN-Tablelands Cooktown | 3HLA_Helenvale 66 kV | Limiting Line Name | TR_LINE 39200_1 | TR_LINE 39200_1 | TR_LINE 68493_1 | TR_LINE 39200_1 | TR_LINE 39200_1 | TR_LINE 68493_1 | TR_LINE 39200_1 | TR_LINE 39200_1 | TR_LINE 68493_1 | TR_LINE 39200_1 | TR_LINE 39200_1 | TR_LINE 68493_1 | TR_LINE 39200_1 | TR_LINE 39200_1 | TR_LINE 68493_1
FN-Tablelands Cooktown | 3HLA_Helenvale 66 kV | Loading (A) | 41.6399 | 38.4292 | 25.1205 | 41.6072 | 38.3923 | 25.112 | 41.9561 | 38.6933 | 24.9877 | 41.9552 | 38.694 | 24.9944 | 42.4592 | 39.1544 | 25.4323
FN-Tablelands Cooktown | 3HLA_Helenvale 66 kV | Loading (MVA) | 4.8965 | 4.5143 | 2.9198 | 4.8964 | 4.5143 | 2.9198 | 4.8979 | 4.5153 | 2.92 | 4.8979 | 4.5153 | 2.92 | 4.9949 | 4.5997 | 2.9767
FN-Tablelands Cooktown | 3HLA_Helenvale 66 kV | Loading (MW) | 4.895 | 4.5085 | 2.9193 | 4.8948 | 4.5084 | 2.9193 | 4.8968 | 4.5103 | 2.9197 | 4.8968 | 4.5103 | 2.9197 | 4.994 | 4.5952 | 2.9761
FN-Tablelands Cooktown | 3HLA_Helenvale 66 kV | Power Factor | 0.99968 | 0.99872 | 0.99977 | 0.99967 | 0.99869 | 0.99977 | 0.99977 | 0.99888 | 0.99983 | 0.99977 | 0.99888 | 0.99982 | 0.99982 | 0.99902 | 0.99975
FN-Tablelands Cooktown | 3HLA_Helenvale 66 kV | Rating (A) | 378 | 399 | 370 | 378 | 399 | 370 | 378 | 399 | 370 | 378 | 399 | 370 | 378 | 399 | 370
FN-Tablelands Cooktown | 3HLA_Helenvale 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
FN-Tablelands Cooktown | 3HLA_Helenvale 66 kV | Min Voltage at Constrained Conductor | 67.8299 | 67.7679 | 67.1015 | 67.8824 | 67.8333 | 67.1237 | 67.3365 | 67.3195 | 67.4622 | 67.3379 | 67.3183 | 67.4444 | 67.8561 | 67.7697 | 67.5697
FN-Tablelands Cooktown | 3HLA_Helenvale 66 kV | Contingency Outage | 7201_Craiglie No 1 132 kV | 3AT2_Atherton No 2 66 kV | 7201_Craiglie No 1 132 kV | 7201_Craiglie No 1 132 kV | 3AT2_Atherton No 2 66 kV | 7201_Craiglie No 1 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 3RA1_Ravenshoe No 1 66 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 2MOS_Mossman 22 kV | 3CHI_Chillagoe 66 kV | 3CHI_Chillagoe 66 kV | 3CHI_Chillagoe 66 kV
FN-Tablelands Cooktown | 3MA2_Mareeba No 2 66 kV | % of Rated A | 107.3% | 73% | 47.85% | 105.8% | 71.98% | 47.35% | 105.8% | 71.97% | 47.09% | 106.6% | 72.52% | 47.55% | 108.3% | 73.73% | 47.93%
FN-Tablelands Cooktown | 3MA2_Mareeba No 2 66 kV | Limiting Line Name | TR_LINE 5351_1 | TR_LINE 5351_1 | TR_LINE 5351_1 | TR_LINE 5351_1 | TR_LINE 5351_1 | TR_LINE 5351_1 | TR_LINE 5351_1 | TR_LINE 5351_1 | TR_LINE 5351_1 | TR_LINE 5351_1 | TR_LINE 5351_1 | TR_LINE 5351_1 | TR_LINE 5351_1 | TR_LINE 5351_1 | TR_LINE 5351_1
FN-Tablelands Cooktown | 3MA2_Mareeba No 2 66 kV | Loading (A) | 181.2663 | 175.9304 | 112.4381 | 178.7654 | 173.4598 | 111.2721 | 178.7406 | 173.441 | 110.6525 | 180.0753 | 174.7723 | 111.751 | 183.0726 | 177.6932 | 112.627
FN-Tablelands Cooktown | 3MA2_Mareeba No 2 66 kV | Loading (MVA) | 21.7128 | 21.0243 | 13.5346 | 21.4269 | 20.7515 | 13.3979 | 21.3486 | 20.6695 | 13.2954 | 21.5137 | 20.8324 | 13.4297 | 21.8271 | 21.1266 | 13.5214
FN-Tablelands Cooktown | 3MA2_Mareeba No 2 66 kV | Loading (MW) | 21.4577 | 20.7293 | 12.1622 | 21.15 | 20.4321 | 11.9893 | 21.1291 | 20.4119 | 11.9762 | 21.2541 | 20.5327 | 12.0471 | 21.6419 | 20.9073 | 12.2641
FN-Tablelands Cooktown | 3MA2_Mareeba No 2 66 kV | Power Factor | 0.98814 | 0.98585 | 0.8985 | 0.98696 | 0.98449 | 0.89477 | 0.98961 | 0.98743 | 0.90069 | 0.98782 | 0.9855 | 0.89695 | 0.99142 | 0.98952 | 0.90692
FN-Tablelands Cooktown | 3MA2_Mareeba No 2 66 kV | Rating (A) | 169 | 241 | 235 | 169 | 241 | 235 | 169 | 241 | 235 | 169 | 241 | 235 | 169 | 241 | 235
FN-Tablelands Cooktown | 3MA2_Mareeba No 2 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
FN-Tablelands Cooktown | 3MA2_Mareeba No 2 66 kV | Min Voltage at Constrained Conductor | 69.1227 | 68.9628 | 69.491 | 69.168 | 69.0388 | 69.5105 | 68.9235 | 68.7718 | 69.364 | 68.9421 | 68.7864 | 69.3768 | 68.799 | 68.6088 | 69.3059
FN-Tablelands Cooktown | 3MA2_Mareeba No 2 66 kV | Contingency Outage | 3MO1_Mossman No 1 66 kV | 3MO1_Mossman No 1 66 kV | 3MO1_Mossman No 1 66 kV | 3MO1_Mossman No 1 66 kV | 3MO1_Mossman No 1 66 kV | 3MO1_Mossman No 1 66 kV | 3MO1_Mossman No 1 66 kV | 3MO1_Mossman No 1 66 kV | 3MO1_Mossman No 1 66 kV | 3MO1_Mossman No 1 66 kV | 3MO1_Mossman No 1 66 kV | 3MO1_Mossman No 1 66 kV | 3MO1_Mossman No 1 66 kV | 3MO1_Mossman No 1 66 kV | 3MO1_Mossman No 1 66 kV
FN-Tablelands Cooktown | 3MO1_Mossman No 1 66 kV | % of Rated A | 138% | 106% | 70.58% | 136.1% | 104.5% | 69.84% | 135.6% | 104% | 69.41% | 136.6% | 104.8% | 70.1% | 138.9% | 106.6% | 70.66%
FN-Tablelands Cooktown | 3MO1_Mossman No 1 66 kV | Limiting Line Name | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1
FN-Tablelands Cooktown | 3MO1_Mossman No 1 66 kV | Loading (A) | 182.1455 | 177.0229 | 112.2266 | 179.6078 | 174.5063 | 111.0495 | 179.0065 | 173.7367 | 110.3655 | 180.3351 | 175.0619 | 111.4589 | 183.3734 | 178.0278 | 112.3535
FN-Tablelands Cooktown | 3MO1_Mossman No 1 66 kV | Loading (MVA) | 21.5785 | 20.8919 | 13.4758 | 21.2963 | 20.6223 | 13.3394 | 21.2272 | 20.555 | 13.2478 | 21.3924 | 20.718 | 13.3822 | 21.6983 | 21.0053 | 13.4731
FN-Tablelands Cooktown | 3MO1_Mossman No 1 66 kV | Loading (MW) | 21.3121 | 20.5926 | 12.1057 | 21.0084 | 20.2992 | 11.934 | 20.9865 | 20.2777 | 11.9214 | 21.1094 | 20.3965 | 11.9913 | 21.4924 | 20.7665 | 12.2073
FN-Tablelands Cooktown | 3MO1_Mossman No 1 66 kV | Power Factor | 0.98755 | 0.98557 | 0.8982 | 0.98638 | 0.98422 | 0.89451 | 0.98857 | 0.98641 | 0.89976 | 0.98667 | 0.98438 | 0.89593 | 0.99042 | 0.98854 | 0.90593
FN-Tablelands Cooktown | 3MO1_Mossman No 1 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
FN-Tablelands Cooktown | 3MO1_Mossman No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
FN-Tablelands Cooktown | 3MO1_Mossman No 1 66 kV | Min Voltage at Constrained Conductor | 68.353 | 68.0948 | 69.3103 | 68.4132 | 68.1865 | 69.3365 | 68.4196 | 68.2646 | 69.2867 | 68.4448 | 68.2854 | 69.3032 | 68.2708 | 68.0769 | 69.2173
FN-Tablelands Cooktown | 3MO1_Mossman No 1 66 kV | Contingency Outage | 3MA2_Mareeba No 2 66 kV | 3MA2_Mareeba No 2 66 kV | 3MA2_Mareeba No 2 66 kV | 3MA2_Mareeba No 2 66 kV | 3MA2_Mareeba No 2 66 kV | 3MA2_Mareeba No 2 66 kV | 3MA2_Mareeba No 2 66 kV | 3MA2_Mareeba No 2 66 kV | 3MA2_Mareeba No 2 66 kV | 3MA2_Mareeba No 2 66 kV | 3MA2_Mareeba No 2 66 kV | 3MA2_Mareeba No 2 66 kV | 3MA2_Mareeba No 2 66 kV | 3MA2_Mareeba No 2 66 kV | 3MA2_Mareeba No 2 66 kV
FN-Tablelands Cooktown | 3MO2_Mossman No 2 66 kV | % of Rated A | 22.4% | 21.69% | 11.41% | 22.38% | 21.66% | 11.4% | 3.693% | 2.605% | 2.681% | 3.694% | 2.605% | 2.682% | 3.688% | 2.612% | 2.679%
FN-Tablelands Cooktown | 3MO2_Mossman No 2 66 kV | Limiting Line Name | TR_LINE 167072_1 | TR_LINE 1063_1 | TR_LINE 167072_1 | TR_LINE 167072_1 | TR_LINE 1063_1 | TR_LINE 167072_1 | TR_LINE 2062_3 | TR_LINE 2062_3 | TR_LINE 2062_3 | TR_LINE 2062_3 | TR_LINE 2062_3 | TR_LINE 2062_3 | TR_LINE 2062_3 | TR_LINE 2062_3 | TR_LINE 2062_3
FN-Tablelands Cooktown | 3MO2_Mossman No 2 66 kV | Loading (A) | 29.5619 | 36.2148 | 18.1357 | 29.5463 | 36.176 | 18.1317 | 6.242 | 6.2258 | 6.2469 | 6.2437 | 6.2271 | 6.2481 | 6.2325 | 6.2437 | 6.2423
FN-Tablelands Cooktown | 3MO2_Mossman No 2 66 kV | Loading (MVA) | 3.4764 | 4.2397 | 2.1383 | 3.4764 | 4.2396 | 2.1383 | 0.75346 | 0.74956 | 0.75465 | 0.75387 | 0.74988 | 0.75493 | 0.75117 | 0.75387 | 0.75354
FN-Tablelands Cooktown | 3MO2_Mossman No 2 66 kV | Loading (MW) | 3.4749 | 4.2374 | 2.106 | 3.4748 | 4.2373 | 2.106 | 0.00059543 | 0.00059235 | 0.00059637 | 0.00059575 | 0.0005926 | 0.00059659 | 0.00059362 | 0.00059575 | 0.00059549
FN-Tablelands Cooktown | 3MO2_Mossman No 2 66 kV | Power Factor | 0.99956 | 0.9986 | 0.98489 | 0.99955 | 0.99862 | 0.98486 | 0.00078611 | 0.00078611 | 0.00078611 | 0.00078611 | 0.00078611 | 0.00078611 | 0.00078611 | 0.00078611 | 0.00078611
FN-Tablelands Cooktown | 3MO2_Mossman No 2 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233
FN-Tablelands Cooktown | 3MO2_Mossman No 2 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
FN-Tablelands Cooktown | 3MO2_Mossman No 2 66 kV | Min Voltage at Constrained Conductor | 67.797 | 67.407 | 68.0206 | 67.8326 | 67.477 | 68.0374 | 69.691 | 69.5104 | 69.746 | 69.7099 | 69.5254 | 69.759 | 69.585 | 69.7101 | 69.6946
FN-Tablelands Cooktown | 3MO2_Mossman No 2 66 kV | Contingency Outage | 3DIM_Dimbulah 66 kV | 7285_4LAK (Lakeland) 132kV | Mungana 66 kV | 3DIM_Dimbulah 66 kV | 7285_4LAK (Lakeland) 132kV | Mungana 66 kV | Mungana 66 kV | Mungana 66 kV | 3CHI_Chillagoe 66 kV | Mungana 66 kV | Mungana 66 kV | 3CHI_Chillagoe 66 kV | Mungana 66 kV | 3DIM_Dimbulah 66 kV | 3CHI_Chillagoe 66 kV
FN-Tablelands Cooktown | 3MTG_Mt Garnet 66 kV | % of Rated A | 7.994% | 5.578% | 5.455% | 7.991% | 5.573% | 5.453% | 7.993% | 5.574% | 5.454% | 7.992% | 5.574% | 5.454% | 8.003% | 5.586% | 5.453%
FN-Tablelands Cooktown | 3MTG_Mt Garnet 66 kV | Limiting Line Name | TR_LINE 169447_1 | TR_LINE 169447_1 | TR_LINE 12086527_1 | TR_LINE 169447_1 | TR_LINE 169447_1 | TR_LINE 12086527_1 | TR_LINE 169447_1 | TR_LINE 169447_1 | TR_LINE 12086527_1 | TR_LINE 169447_1 | TR_LINE 169447_1 | TR_LINE 12086527_1 | TR_LINE 169447_1 | TR_LINE 169447_1 | TR_LINE 12086527_1
FN-Tablelands Cooktown | 3MTG_Mt Garnet 66 kV | Loading (A) | 13.5096 | 13.444 | 15.0003 | 13.5042 | 13.4305 | 14.9949 | 13.5073 | 13.4329 | 14.9978 | 13.5067 | 13.4333 | 14.9981 | 13.5258 | 13.4617 | 14.9957
FN-Tablelands Cooktown | 3MTG_Mt Garnet 66 kV | Loading (MVA) | 1.5777 | 1.5556 | 1.804 | 1.5782 | 1.5568 | 1.7991 | 1.5779 | 1.5566 | 1.8017 | 1.5779 | 1.5566 | 1.802 | 1.5763 | 1.5541 | 1.7998
FN-Tablelands Cooktown | 3MTG_Mt Garnet 66 kV | Loading (MW) | 1.4779 | 1.4544 | 1.3597 | 1.4779 | 1.4544 | 1.3597 | 1.4779 | 1.4544 | 1.3597 | 1.4779 | 1.4544 | 1.3597 | 1.4779 | 1.4545 | 1.3597
FN-Tablelands Cooktown | 3MTG_Mt Garnet 66 kV | Power Factor | 0.93676 | 0.93496 | 0.75371 | 0.93646 | 0.93422 | 0.75577 | 0.93663 | 0.93435 | 0.75466 | 0.9366 | 0.93437 | 0.75455 | 0.93762 | 0.93593 | 0.75547
FN-Tablelands Cooktown | 3MTG_Mt Garnet 66 kV | Rating (A) | 169 | 241 | 275 | 169 | 241 | 275 | 169 | 241 | 275 | 169 | 241 | 275 | 169 | 241 | 275
FN-Tablelands Cooktown | 3MTG_Mt Garnet 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
FN-Tablelands Cooktown | 3MTG_Mt Garnet 66 kV | Min Voltage at Constrained Conductor | 67.3742 | 66.7571 | 69.4343 | 67.4223 | 66.8757 | 69.272 | 67.3944 | 66.8544 | 69.3593 | 67.3998 | 66.851 | 69.3686 | 67.2332 | 66.6014 | 69.2957
FN-Tablelands Cooktown | 3MTG_Mt Garnet 66 kV | Contingency Outage | 3AT2_Atherton No 2 66 kV | 3AT2_Atherton No 2 66 kV | 3CHI_Chillagoe 66 kV | 3AT2_Atherton No 2 66 kV | 3AT2_Atherton No 2 66 kV | 3RA1_Ravenshoe No 1 66 kV | 3AT2_Atherton No 2 66 kV | 3AT2_Atherton No 2 66 kV | 3CHI_Chillagoe 66 kV | 3AT2_Atherton No 2 66 kV | 3AT2_Atherton No 2 66 kV | 3CHI_Chillagoe 66 kV | 3AT2_Atherton No 2 66 kV | 3AT2_Atherton No 2 66 kV | 3CHI_Chillagoe 66 kV
FN-Tablelands Cooktown | 3RA1_Ravenshoe No 1 66 kV | % of Rated A | 7.559% | 4.073% | 3.946% | 7.553% | 4.065% | 3.945% | 7.557% | 4.067% | 3.941% | 7.556% | 4.067% | 3.949% | 7.577% | 4.084% | 3.944%
FN-Tablelands Cooktown | 3RA1_Ravenshoe No 1 66 kV | Limiting Line Name | TR_LINE 4408_1 | TR_LINE 4408_1 | TR_LINE 4408_1 | TR_LINE 4408_1 | TR_LINE 4408_1 | TR_LINE 4408_1 | TR_LINE 4408_1 | TR_LINE 4408_1 | TR_LINE 4408_1 | TR_LINE 4408_1 | TR_LINE 4408_1 | TR_LINE 4408_1 | TR_LINE 4408_1 | TR_LINE 4408_1 | TR_LINE 4408_1
FN-Tablelands Cooktown | 3RA1_Ravenshoe No 1 66 kV | Loading (A) | 12.7753 | 9.8166 | 9.2741 | 12.7653 | 9.7975 | 9.2713 | 12.7711 | 9.8009 | 9.2605 | 12.77 | 9.8014 | 9.2801 | 12.8045 | 9.8418 | 9.2692
FN-Tablelands Cooktown | 3RA1_Ravenshoe No 1 66 kV | Loading (MVA) | 1.4816 | 1.1294 | 1.0839 | 1.4815 | 1.1292 | 1.0839 | 1.4816 | 1.1292 | 1.0838 | 1.4816 | 1.1292 | 1.084 | 1.4819 | 1.1296 | 1.0839
FN-Tablelands Cooktown | 3RA1_Ravenshoe No 1 66 kV | Loading (MW) | 1.4093 | 1.0857 | 1.0454 | 1.4093 | 1.0857 | 1.0454 | 1.4093 | 1.0857 | 1.0454 | 1.4093 | 1.0857 | 1.0454 | 1.4093 | 1.0857 | 1.0454
FN-Tablelands Cooktown | 3RA1_Ravenshoe No 1 66 kV | Power Factor | 0.95007 | 0.96049 | 0.96366 | 0.95013 | 0.96065 | 0.96369 | 0.9501 | 0.96062 | 0.96379 | 0.95011 | 0.96062 | 0.96361 | 0.94991 | 0.96028 | 0.96371
FN-Tablelands Cooktown | 3RA1_Ravenshoe No 1 66 kV | Rating (A) | 169 | 241 | 235 | 169 | 241 | 235 | 169 | 241 | 235 | 169 | 241 | 235 | 169 | 241 | 235
FN-Tablelands Cooktown | 3RA1_Ravenshoe No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
FN-Tablelands Cooktown | 3RA1_Ravenshoe No 1 66 kV | Min Voltage at Constrained Conductor | 66.958 | 66.4221 | 67.4783 | 67.0062 | 66.5406 | 67.4972 | 66.9783 | 66.5193 | 67.569 | 66.9837 | 66.5159 | 67.4383 | 66.817 | 66.2665 | 67.5111
FN-Tablelands Cooktown | 3RA1_Ravenshoe No 1 66 kV | Contingency Outage | 3AT2_Atherton No 2 66 kV | 3AT2_Atherton No 2 66 kV | Mungana 66 kV | 3AT2_Atherton No 2 66 kV | 3AT2_Atherton No 2 66 kV | Mungana 66 kV | 3AT2_Atherton No 2 66 kV | 3AT2_Atherton No 2 66 kV | 3DIM_Dimbulah 66 kV | 3AT2_Atherton No 2 66 kV | 3AT2_Atherton No 2 66 kV | Mungana 66 kV | 3AT2_Atherton No 2 66 kV | 3AT2_Atherton No 2 66 kV | 3DIM_Dimbulah 66 kV
FN-Tablelands Cooktown | 7200_Craiglie No 2 132 kV | % of Rated A | 23.23% | 20.79% | 16.97% | 23.07% | 20.65% | 16.91% | 23.03% | 20.61% | 16.99% | 23.1% | 20.67% | 17.02% | 23.35% | 20.88% | 17.1%
FN-Tablelands Cooktown | 7200_Craiglie No 2 132 kV | Limiting Line Name | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1
FN-Tablelands Cooktown | 7200_Craiglie No 2 132 kV | Loading (A) | 105.0182 | 98.9516 | 72.4547 | 104.288 | 98.2843 | 72.215 | 104.0946 | 98.0963 | 72.5453 | 104.4321 | 98.4004 | 72.6666 | 105.5497 | 99.383 | 73.011
FN-Tablelands Cooktown | 7200_Craiglie No 2 132 kV | Loading (MVA) | 24.9459 | 23.4465 | 17.4771 | 24.786 | 23.3085 | 17.4235 | 24.8442 | 23.392 | 17.538 | 24.9277 | 23.4664 | 17.5691 | 25.1579 | 23.6583 | 17.6393
FN-Tablelands Cooktown | 7200_Craiglie No 2 132 kV | Loading (MW) | 23.5094 | 21.6944 | 12.7647 | 23.3072 | 21.5073 | 12.661 | 23.3058 | 21.5057 | 12.662 | 23.4065 | 21.5988 | 12.7139 | 23.7113 | 21.875 | 12.8757
FN-Tablelands Cooktown | 7200_Craiglie No 2 132 kV | Power Factor | 0.94241 | 0.92527 | 0.73037 | 0.94034 | 0.92272 | 0.72666 | 0.93808 | 0.91936 | 0.72198 | 0.93898 | 0.92042 | 0.72365 | 0.9425 | 0.92462 | 0.72994
FN-Tablelands Cooktown | 7200_Craiglie No 2 132 kV | Rating (A) | 452 | 476 | 427 | 452 | 476 | 427 | 452 | 476 | 427 | 452 | 476 | 427 | 452 | 476 | 427
FN-Tablelands Cooktown | 7200_Craiglie No 2 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
FN-Tablelands Cooktown | 7200_Craiglie No 2 132 kV | Min Voltage at Constrained Conductor | 137.1143 | 136.7875 | 139.2654 | 137.1907 | 136.9072 | 139.2985 | 137.7701 | 137.6633 | 139.5757 | 137.7857 | 137.6734 | 139.5898 | 137.5827 | 137.4241 | 139.4864
FN-Tablelands Cooktown | 7200_Craiglie No 2 132 kV | Contingency Outage | 7201_Craiglie No 1 132 kV | 7201_Craiglie No 1 132 kV | 7201_Craiglie No 1 132 kV | 7201_Craiglie No 1 132 kV | 7201_Craiglie No 1 132 kV | 7201_Craiglie No 1 132 kV | 7201_Craiglie No 1 132 kV | 7201_Craiglie No 1 132 kV | 7201_Craiglie No 1 132 kV | 7201_Craiglie No 1 132 kV | 7201_Craiglie No 1 132 kV | 7201_Craiglie No 1 132 kV | 7201_Craiglie No 1 132 kV | 7201_Craiglie No 1 132 kV | 7201_Craiglie No 1 132 kV
FN-Tablelands Cooktown | 7201_Craiglie No 1 132 kV | % of Rated A | 19.03% | 18.07% | 11.37% | 18.79% | 17.84% | 11.23% | 26.38% | 27.39% | 16.36% | 26.5% | 27.5% | 16.42% | 26.96% | 28.03% | 16.69%
FN-Tablelands Cooktown | 7201_Craiglie No 1 132 kV | Limiting Line Name | TR_LINE 38738_1 | TR_LINE 38738_1 | TR_LINE 38738_1 | TR_LINE 38738_1 | TR_LINE 38738_1 | TR_LINE 38738_1 | TR_LINE 38738_a | TR_LINE 38738_a | TR_LINE 38738_a | TR_LINE 38738_a | TR_LINE 38738_a | TR_LINE 38738_a | TR_LINE 38738_a | TR_LINE 38738_a | TR_LINE 38738_a
FN-Tablelands Cooktown | 7201_Craiglie No 1 132 kV | Loading (A) | 72.1242 | 66.8775 | 36.6007 | 71.2081 | 66.0128 | 36.1705 | 99.9857 | 101.3552 | 52.6652 | 100.4176 | 101.759 | 52.8762 | 102.1604 | 103.7039 | 53.7383
FN-Tablelands Cooktown | 7201_Craiglie No 1 132 kV | Loading (MVA) | 16.8538 | 15.6027 | 8.803 | 16.6517 | 15.4162 | 8.702 | 23.4766 | 23.7613 | 12.7292 | 23.5784 | 23.8556 | 12.7809 | 23.9434 | 24.2458 | 12.982
FN-Tablelands Cooktown | 7201_Craiglie No 1 132 kV | Loading (MW) | 16.7898 | 15.5618 | 8.7838 | 16.5924 | 15.3789 | 8.6812 | 23.3044 | 23.6015 | 12.7251 | 23.4033 | 23.6933 | 12.7766 | 23.7633 | 24.0772 | 12.9768
FN-Tablelands Cooktown | 7201_Craiglie No 1 132 kV | Power Factor | 0.99603 | 0.99722 | 0.99782 | 0.99626 | 0.99742 | 0.9976 | 0.99251 | 0.99313 | 0.9996 | 0.99242 | 0.99306 | 0.99958 | 0.99233 | 0.99291 | 0.99951
FN-Tablelands Cooktown | 7201_Craiglie No 1 132 kV | Rating (A) | 379 | 370 | 322 | 379 | 370 | 322 | 379 | 370 | 322 | 379 | 370 | 322 | 379 | 370 | 322
FN-Tablelands Cooktown | 7201_Craiglie No 1 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
FN-Tablelands Cooktown | 7201_Craiglie No 1 132 kV | Min Voltage at Constrained Conductor | 134.8871 | 134.6723 | 138.8368 | 134.9848 | 134.8054 | 138.8775 | 135.5132 | 135.3014 | 139.5208 | 135.5155 | 135.2986 | 139.5282 | 135.2638 | 134.931 | 139.4507
FN-Tablelands Cooktown | 7201_Craiglie No 1 132 kV | Contingency Outage | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV
FN-Tablelands Cooktown | 7285_4LAK (Lakeland) 132kV | % of Rated A | 8.322% | 7.602% | 8.253% | 8.324% | 7.606% | 8.241% | 8.311% | 7.595% | 8.213% | 8.311% | 7.596% | 8.214% | 8.334% | 7.607% | 8.213%
FN-Tablelands Cooktown | 7285_4LAK (Lakeland) 132kV | Limiting Line Name | TR_LINE 37686_1 | TR_LINE 37686_1 | TR_LINE 37686_1 | TR_LINE 37686_1 | TR_LINE 37686_1 | TR_LINE 37686_1 | TR_LINE 37686_1 | TR_LINE 37686_1 | TR_LINE 37686_1 | TR_LINE 37686_1 | TR_LINE 37686_1 | TR_LINE 37686_1 | TR_LINE 37686_1 | TR_LINE 37686_1 | TR_LINE 37686_1
FN-Tablelands Cooktown | 7285_4LAK (Lakeland) 132kV | Loading (A) | 42.2737 | 41.3532 | 39.6142 | 42.2856 | 41.378 | 39.5587 | 42.2193 | 41.3191 | 39.4217 | 42.2215 | 41.3206 | 39.4249 | 42.3362 | 41.3847 | 39.4235
FN-Tablelands Cooktown | 7285_4LAK (Lakeland) 132kV | Loading (MVA) | 10.2243 | 9.98 | 9.7661 | 10.2329 | 9.9962 | 9.7368 | 10.183 | 9.9519 | 9.6621 | 10.1846 | 9.9529 | 9.6638 | 10.2016 | 9.9529 | 9.6558
FN-Tablelands Cooktown | 7285_4LAK (Lakeland) 132kV | Loading (MW) | 6.4004 | 5.8518 | 3.8391 | 6.4003 | 5.8516 | 3.8391 | 6.4017 | 5.8529 | 3.8397 | 6.4017 | 5.8529 | 3.8397 | 6.5014 | 5.9397 | 3.8971
FN-Tablelands Cooktown | 7285_4LAK (Lakeland) 132kV | Power Factor | 0.62599 | 0.58635 | 0.3931 | 0.62546 | 0.58539 | 0.39429 | 0.62866 | 0.58812 | 0.39739 | 0.62857 | 0.58806 | 0.39732 | 0.63729 | 0.59678 | 0.40361
FN-Tablelands Cooktown | 7285_4LAK (Lakeland) 132kV | Rating (A) | 508 | 544 | 480 | 508 | 544 | 480 | 508 | 544 | 480 | 508 | 544 | 480 | 508 | 544 | 480
FN-Tablelands Cooktown | 7285_4LAK (Lakeland) 132kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
FN-Tablelands Cooktown | 7285_4LAK (Lakeland) 132kV | Min Voltage at Constrained Conductor | 139.6382 | 139.335 | 142.3349 | 139.7155 | 139.4773 | 142.1063 | 139.2534 | 139.0579 | 141.5068 | 139.2678 | 139.0668 | 141.52 | 139.1214 | 138.8515 | 141.4068
FN-Tablelands Cooktown | 7285_4LAK (Lakeland) 132kV | Contingency Outage | Mungana 66 kV | Mungana 66 kV | 3DIM_Dimbulah 66 kV | Mungana 66 kV | Mungana 66 kV | Mungana 66 kV | 3DIM_Dimbulah 66 kV | 3DIM_Dimbulah 66 kV | 3DIM_Dimbulah 66 kV | 3DIM_Dimbulah 66 kV | 3DIM_Dimbulah 66 kV | 3DIM_Dimbulah 66 kV | 3DIM_Dimbulah 66 kV | 3DIM_Dimbulah 66 kV | 3DIM_Dimbulah 66 kV
FN-Tablelands Cooktown | Mungana 66 kV | % of Rated A | 9.983% | 9.219% | 8.882% | 9.975% | 9.208% | 8.88% | 9.995% | 9.216% | 8.873% | 9.992% | 9.214% | 8.871% | 10.02% | 9.249% | 8.878%
FN-Tablelands Cooktown | Mungana 66 kV | Limiting Line Name | TR_LINE 104003_1 | TR_LINE 104003_1 | TR_LINE 104003_1 | TR_LINE 104003_1 | TR_LINE 104003_1 | TR_LINE 104003_1 | TR_LINE 104003_1 | TR_LINE 104003_1 | TR_LINE 104003_1 | TR_LINE 104003_1 | TR_LINE 104003_1 | TR_LINE 104003_1 | TR_LINE 104003_1 | TR_LINE 104003_1 | TR_LINE 104003_1
FN-Tablelands Cooktown | Mungana 66 kV | Loading (A) | 45.6203 | 44.8953 | 41.9242 | 45.587 | 44.8417 | 41.9127 | 45.675 | 44.881 | 41.8802 | 45.6614 | 44.8706 | 41.8719 | 45.7734 | 45.0406 | 41.9057
FN-Tablelands Cooktown | Mungana 66 kV | Loading (MVA) | 5.063 | 4.9632 | 4.7448 | 5.063 | 4.9632 | 4.7448 | 5.063 | 4.9632 | 4.7448 | 5.063 | 4.9632 | 4.7448 | 5.063 | 4.9632 | 4.7448
FN-Tablelands Cooktown | Mungana 66 kV | Loading (MW) | 4.6817 | 4.5894 | 4.3872 | 4.6817 | 4.5894 | 4.3872 | 4.6817 | 4.5894 | 4.3872 | 4.6817 | 4.5894 | 4.3872 | 4.6818 | 4.5894 | 4.3872
FN-Tablelands Cooktown | Mungana 66 kV | Power Factor | 0.92404 | 0.92404 | 0.92404 | 0.92404 | 0.92404 | 0.92404 | 0.92404 | 0.92404 | 0.92404 | 0.92404 | 0.92404 | 0.92404 | 0.92404 | 0.92404 | 0.92404
FN-Tablelands Cooktown | Mungana 66 kV | Rating (A) | 457 | 487 | 472 | 457 | 487 | 472 | 457 | 487 | 472 | 457 | 487 | 472 | 457 | 487 | 472
FN-Tablelands Cooktown | Mungana 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
FN-Tablelands Cooktown | Mungana 66 kV | Min Voltage at Constrained Conductor | 64.0756 | 63.8266 | 65.3419 | 64.1225 | 63.9028 | 65.3599 | 63.9989 | 63.8468 | 65.4105 | 64.0181 | 63.8617 | 65.4236 | 63.8614 | 63.6206 | 65.3708
FN-Tablelands Cooktown | Mungana 66 kV | Contingency Outage | 7201_Craiglie No 1 132 kV | 7285_4LAK (Lakeland) 132kV | 7200_Craiglie No 2 132 kV | 7201_Craiglie No 1 132 kV | 7285_4LAK (Lakeland) 132kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV
FN-Tablelands Cooktown | TURK_YALK (Ex 7201) | % of Rated A | [6 empty] | 28.81% | 27.22% | 19.4% | 28.89% | 27.3% | 19.43% | 29.34% | 27.75% | 19.61%
FN-Tablelands Cooktown | TURK_YALK (Ex 7201) | Limiting Line Name | [6 empty] | TR_LINE 3957_2 | TR_LINE 3957_2 | TR_LINE 3957_2 | TR_LINE 3957_2 | TR_LINE 3957_2 | TR_LINE 3957_2 | TR_LINE 3957_2 | TR_LINE 3957_2 | TR_LINE 3957_2
FN-Tablelands Cooktown | TURK_YALK (Ex 7201) | Loading (A) | [6 empty] | 130.2062 | 129.5851 | 82.8304 | 130.582 | 129.937 | 82.9809 | 132.6104 | 132.089 | 83.7551
FN-Tablelands Cooktown | TURK_YALK (Ex 7201) | Loading (MVA) | [6 empty] | 30.886 | 30.6802 | 19.9859 | 30.9786 | 30.7656 | 20.0241 | 31.4149 | 31.2055 | 20.204
FN-Tablelands Cooktown | TURK_YALK (Ex 7201) | Loading (MW) | [6 empty] | 30.2143 | 29.9568 | 16.7581 | 30.3163 | 30.0514 | 16.8103 | 30.7905 | 30.5381 | 17.072
FN-Tablelands Cooktown | TURK_YALK (Ex 7201) | Power Factor | [6 empty] | 0.97825 | 0.97642 | 0.83849 | 0.97862 | 0.97679 | 0.8395 | 0.98012 | 0.97861 | 0.84498
FN-Tablelands Cooktown | TURK_YALK (Ex 7201) | Rating (A) | [6 empty] | 452 | 476 | 427 | 452 | 476 | 427 | 452 | 476 | 427
FN-Tablelands Cooktown | TURK_YALK (Ex 7201) | Time | [6 empty] | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
FN-Tablelands Cooktown | TURK_YALK (Ex 7201) | Min Voltage at Constrained Conductor | [6 empty] | 136.9508 | 136.6903 | 139.3074 | 136.9658 | 136.6993 | 139.3202 | 136.7705 | 136.3948 | 139.2727
FN-Tablelands Cooktown | TURK_YALK (Ex 7201) | Contingency Outage | [6 empty] | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV | 7200_Craiglie No 2 132 kV
Interstitial Grid | 7194_Gladstone PS - Boat Creek 132 kV | % of Rated A | 3.62% | 3.655% | 2.191% | 3.617% | 3.648% | 2.19% | 3.594% | 3.63% | 2.179% | 3.597% | 3.637% | 2.183% | 3.617% | 3.658% | 2.189%
Interstitial Grid | 7194_Gladstone PS - Boat Creek 132 kV | Limiting Line Name | Subtrans_GLNO_CALI_LINE_1 | Subtrans_GLNO_CALI_LINE_1 | Subtrans_GLNO_CALI_LINE_1 | Subtrans_GLNO_CALI_LINE_1 | Subtrans_GLNO_CALI_LINE_1 | Subtrans_GLNO_CALI_LINE_1 | Subtrans_GLNO_CALI_LINE_1 | Subtrans_GLNO_CALI_LINE_1 | Subtrans_GLNO_CALI_LINE_1 | Subtrans_GLNO_CALI_LINE_1 | Subtrans_GLNO_CALI_LINE_1 | Subtrans_GLNO_CALI_LINE_1 | Subtrans_GLNO_CALI_LINE_1 | Subtrans_GLNO_CALI_LINE_1 | Subtrans_GLNO_CALI_LINE_1
Interstitial Grid | 7194_Gladstone PS - Boat Creek 132 kV | Loading (A) | 180.9767 | 182.774 | 109.5359 | 180.8616 | 182.4038 | 109.5236 | 179.6886 | 181.4791 | 108.9714 | 179.8386 | 181.861 | 109.1459 | 180.83 | 182.8775 | 109.4602
Interstitial Grid | 7194_Gladstone PS - Boat Creek 132 kV | Loading (MVA) | 43.8949 | 44.3187 | 26.5936 | 43.8699 | 44.2326 | 26.5919 | 43.5844 | 44.0078 | 26.4577 | 43.6214 | 44.1003 | 26.5003 | 43.8549 | 44.3397 | 26.5744
Interstitial Grid | 7194_Gladstone PS - Boat Creek 132 kV | Loading (MW) | 43.8912 | 43.8404 | 25.7346 | 43.8593 | 43.696 | 25.6705 | 43.5731 | 43.4645 | 25.5299 | 43.6065 | 43.5436 | 25.556 | 43.8493 | 43.8495 | 25.6973
Interstitial Grid | 7194_Gladstone PS - Boat Creek 132 kV | Power Factor | 0.99992 | 0.98921 | 0.9677 | 0.99976 | 0.98787 | 0.96535 | 0.99974 | 0.98765 | 0.96493 | 0.99966 | 0.98738 | 0.96437 | 0.99987 | 0.98894 | 0.96699
Interstitial Grid | 7194_Gladstone PS - Boat Creek 132 kV | Rating (A) | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000
Interstitial Grid | 7194_Gladstone PS - Boat Creek 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
Interstitial Grid | 7194_Gladstone PS - Boat Creek 132 kV | Min Voltage at Constrained Conductor | 140.0332 | 139.9948 | 140.1718 | 140.0423 | 140.0062 | 140.1784 | 140.0392 | 140.0047 | 140.178 | 140.0411 | 140.0042 | 140.1789 | 140.0192 | 139.9819 | 140.1676
Interstitial Grid | 7194_Gladstone PS - Boat Creek 132 kV | Contingency Outage | 7195_Gladstone PS - Boat Creek 132 kV | 7195_Gladstone PS - Boat Creek 132 kV | 7195_Gladstone PS - Boat Creek 132 kV | 7195_Gladstone PS - Boat Creek 132 kV | 7195_Gladstone PS - Boat Creek 132 kV | 7195_Gladstone PS - Boat Creek 132 kV | 7195_Gladstone PS - Boat Creek 132 kV | 7195_Gladstone PS - Boat Creek 132 kV | 7195_Gladstone PS - Boat Creek 132 kV | 7195_Gladstone PS - Boat Creek 132 kV | 7195_Gladstone PS - Boat Creek 132 kV | 7195_Gladstone PS - Boat Creek 132 kV | 7195_Gladstone PS - Boat Creek 132 kV | 7195_Gladstone PS - Boat Creek 132 kV | 7195_Gladstone PS - Boat Creek 132 kV
Interstitial Grid | 7195_Gladstone PS - Boat Creek 132 kV | % of Rated A | 3.625% | 3.661% | 2.194% | 3.622% | 3.653% | 2.194% | 3.599% | 3.635% | 2.183% | 3.602% | 3.643% | 2.186% | 3.622% | 3.663% | 2.192%
Interstitial Grid | 7195_Gladstone PS - Boat Creek 132 kV | Limiting Line Name | Subtrans_GLNO_CALI_LINE_2 | Subtrans_GLNO_CALI_LINE_2 | Subtrans_GLNO_CALI_LINE_2 | Subtrans_GLNO_CALI_LINE_2 | Subtrans_GLNO_CALI_LINE_2 | Subtrans_GLNO_CALI_LINE_2 | Subtrans_GLNO_CALI_LINE_2 | Subtrans_GLNO_CALI_LINE_2 | Subtrans_GLNO_CALI_LINE_2 | Subtrans_GLNO_CALI_LINE_2 | Subtrans_GLNO_CALI_LINE_2 | Subtrans_GLNO_CALI_LINE_2 | Subtrans_GLNO_CALI_LINE_2 | Subtrans_GLNO_CALI_LINE_2 | Subtrans_GLNO_CALI_LINE_2
Interstitial Grid | 7195_Gladstone PS - Boat Creek 132 kV | Loading (A) | 181.238 | 183.0414 | 109.6956 | 181.1229 | 182.6709 | 109.6833 | 179.9482 | 181.7447 | 109.1302 | 180.0985 | 182.1272 | 109.305 | 181.0911 | 183.145 | 109.6197
Interstitial Grid | 7195_Gladstone PS - Boat Creek 132 kV | Loading (MVA) | 43.9587 | 44.383 | 26.6319 | 43.9336 | 44.2968 | 26.6302 | 43.6477 | 44.0717 | 26.4958 | 43.6847 | 44.1642 | 26.5384 | 43.9187 | 44.4041 | 26.6127
Interstitial Grid | 7195_Gladstone PS - Boat Creek 132 kV | Loading (MW) | 43.9549 | 43.9028 | 25.7701 | 43.9228 | 43.7581 | 25.7059 | 43.6362 | 43.5262 | 25.5651 | 43.6696 | 43.6055 | 25.5912 | 43.9129 | 43.9118 | 25.7327
Interstitial Grid | 7195_Gladstone PS - Boat Creek 132 kV | Power Factor | 0.99991 | 0.98918 | 0.96764 | 0.99975 | 0.98784 | 0.96529 | 0.99974 | 0.98762 | 0.96487 | 0.99965 | 0.98735 | 0.96431 | 0.99987 | 0.98892 | 0.96693
Interstitial Grid | 7195_Gladstone PS - Boat Creek 132 kV | Rating (A) | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000
Interstitial Grid | 7195_Gladstone PS - Boat Creek 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
Interstitial Grid | 7195_Gladstone PS - Boat Creek 132 kV | Min Voltage at Constrained Conductor | 140.0345 | 139.9932 | 140.1694 | 140.0434 | 140.0045 | 140.1759 | 140.0402 | 140.0029 | 140.1755 | 140.0421 | 140.0024 | 140.1763 | 140.0204 | 139.9803 | 140.1651
Interstitial Grid | 7195_Gladstone PS - Boat Creek 132 kV | Contingency Outage | 7194_Gladstone PS - Boat Creek 132 kV | 7194_Gladstone PS - Boat Creek 132 kV | 7194_Gladstone PS - Boat Creek 132 kV | 7194_Gladstone PS - Boat Creek 132 kV | 7194_Gladstone PS - Boat Creek 132 kV | 7194_Gladstone PS - Boat Creek 132 kV | 7194_Gladstone PS - Boat Creek 132 kV | 7194_Gladstone PS - Boat Creek 132 kV | 7194_Gladstone PS - Boat Creek 132 kV | 7194_Gladstone PS - Boat Creek 132 kV | 7194_Gladstone PS - Boat Creek 132 kV | 7194_Gladstone PS - Boat Creek 132 kV | 7194_Gladstone PS - Boat Creek 132 kV | 7194_Gladstone PS - Boat Creek 132 kV | 7194_Gladstone PS - Boat Creek 132 kV
MK-Mackay Area | 14109_Marian Mill 11 kV | % of Rated A | 0.2706% | 0.2714% | 0.2718% | 0.2707% | 0.2712% | 0.2719% | 0.2708% | 0.2713% | 0.2719% | 0.2706% | 0.2711% | 0.2718% | 0.2715% | 0.2709% | 0.2717%
MK-Mackay Area | 14109_Marian Mill 11 kV | Limiting Line Name | HV_CABLE 461202_1 | HV_CABLE 461202_1 | HV_CABLE 461202_1 | HV_CABLE 461202_1 | HV_CABLE 461202_1 | HV_CABLE 461202_1 | HV_CABLE 461202_1 | HV_CABLE 461202_1 | HV_CABLE 461202_1 | HV_CABLE 461202_1 | HV_CABLE 461202_1 | HV_CABLE 461202_1 | HV_CABLE 461202_1 | HV_CABLE 461202_1 | HV_CABLE 461202_1
MK-Mackay Area | 14109_Marian Mill 11 kV | Loading (A) | 0.85236 | 0.85479 | 0.85627 | 0.85272 | 0.85431 | 0.85642 | 0.85311 | 0.85473 | 0.85662 | 0.85244 | 0.85382 | 0.85632 | 0.85533 | 0.85326 | 0.85586
MK-Mackay Area | 14109_Marian Mill 11 kV | Loading (MVA) | 0.01646 | 0.016554 | 0.016611 | 0.016474 | 0.016535 | 0.016617 | 0.016489 | 0.016552 | 0.016625 | 0.016463 | 0.016516 | 0.016613 | 0.016575 | 0.016495 | 0.016595
MK-Mackay Area | 14109_Marian Mill 11 kV | Loading (MW) | 0.00032537 | 0.00032723 | 0.00032837 | 0.00032565 | 0.00032687 | 0.00032848 | 0.00032595 | 0.00032719 | 0.00032864 | 0.00032544 | 0.00032649 | 0.00032841 | 0.00032765 | 0.00032607 | 0.00032805
MK-Mackay Area | 14109_Marian Mill 11 kV | Power Factor | 0.019651 | 0.019651 | 0.019651 | 0.019651 | 0.019651 | 0.019651 | 0.019651 | 0.019651 | 0.019651 | 0.019651 | 0.019651 | 0.019651 | 0.019651 | 0.019651 | 0.019651
MK-Mackay Area | 14109_Marian Mill 11 kV | Rating (A) | 315 | 315 | 315 | 315 | 315 | 315 | 315 | 315 | 315 | 315 | 315 | 315 | 315 | 315 | 315
MK-Mackay Area | 14109_Marian Mill 11 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
MK-Mackay Area | 14109_Marian Mill 11 kV | Min Voltage at Constrained Conductor | 11.1493 | 11.1811 | 11.2004 | 11.154 | 11.1748 | 11.2024 | 11.1591 | 11.1802 | 11.205 | 11.1504 | 11.1684 | 11.2011 | 11.1882 | 11.1611 | 11.1951
MK-Mackay Area | 14109_Marian Mill 11 kV | Contingency Outage | PV 6/5_Glenella No 1 66 kV | PV 6/5_Glenella No 1 66 kV | PV 6/5_Glenella No 1 66 kV | PV 6/5_Glenella No 1 66 kV | PV 6/5_Glenella No 1 66 kV | PV 6/5_Glenella No 1 66 kV | PV 6/5_Glenella No 1 66 kV | PV 6/5_Glenella No 1 66 kV | PV 6/5_Glenella No 1 66 kV | PV 6/5_Glenella No 1 66 kV | PV 6/5_Glenella No 1 66 kV | PV 6/5_Glenella No 1 66 kV | PV 6/4_Glenella No 2 66 kV | PV 6/5_Glenella No 1 66 kV | PV 6/5_Glenella No 1 66 kV
MK-Mackay Area | 231_Carmila 33 kV | % of Rated A | 27.66% | 35.75% | 17.39% | 27.64% | 35.71% | 17.39% | 27.64% | 35.71% | 17.39% | 27.66% | 35.75% | 17.39% | 27.73% | 35.85% | 17.41%
MK-Mackay Area | 231_Carmila 33 kV | Limiting Line Name | TR_LINE 11379_1 | TR_CABLE 34_1 | TR_CABLE 34_1 | TR_LINE 11379_1 | TR_CABLE 34_1 | TR_CABLE 34_1 | TR_LINE 11379_1 | TR_CABLE 34_1 | TR_CABLE 34_1 | TR_LINE 11379_1 | TR_CABLE 34_1 | TR_CABLE 34_1 | TR_LINE 11379_1 | TR_CABLE 34_1 | TR_CABLE 34_1
MK-Mackay Area | 231_Carmila 33 kV | Loading (A) | 42.0438 | 54.3434 | 26.4344 | 42.0068 | 54.2815 | 26.4262 | 42.0068 | 54.2815 | 26.4262 | 42.0444 | 54.3444 | 26.4346 | 42.1471 | 54.4973 | 26.4595
MK-Mackay Area | 231_Carmila 33 kV | Loading (MVA) | 2.2494 | 2.8781 | 1.5044 | 2.2492 | 2.8776 | 1.5044 | 2.2492 | 2.8776 | 1.5044 | 2.2494 | 2.8781 | 1.5044 | 2.2498 | 2.879 | 1.5045
MK-Mackay Area | 231_Carmila 33 kV | Loading (MW) | 2.1276 | 2.7228 | 1.453 | 2.1275 | 2.7225 | 1.453 | 2.1275 | 2.7225 | 1.453 | 2.1276 | 2.7228 | 1.453 | 2.1277 | 2.7234 | 1.453
MK-Mackay Area | 231_Carmila 33 kV | Power Factor | 0.94573 | 0.94594 | 0.96566 | 0.94577 | 0.946 | 0.96568 | 0.94577 | 0.946 | 0.96568 | 0.94573 | 0.94593 | 0.96565 | 0.94561 | 0.94584 | 0.96559
MK-Mackay Area | 231_Carmila 33 kV | Rating (A) | 152 | 152 | 152 | 152 | 152 | 152 | 152 | 152 | 152 | 152 | 152 | 152 | 152 | 152 | 152
MK-Mackay Area | 231_Carmila 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
MK-Mackay Area | 231_Carmila 33 kV | Min Voltage at Constrained Conductor | 30.8758 | 30.5773 | 32.8575 | 30.9009 | 30.6072 | 32.8668 | 30.9009 | 30.6072 | 32.8668 | 30.8754 | 30.5767 | 32.8572 | 30.8061 | 30.5008 | 32.829
MK-Mackay Area | 231_Carmila 33 kV | Contingency Outage | 3047_Sarina No 2 33 kV | 3047_Sarina No 2 33 kV | 3045_Sarina No 1 33 kV | 3047_Sarina No 2 33 kV | 3047_Sarina No 2 33 kV | 3045_Sarina No 1 33 kV | 3047_Sarina No 2 33 kV | 3047_Sarina No 2 33 kV | 3045_Sarina No 1 33 kV | 3047_Sarina No 2 33 kV | 3047_Sarina No 2 33 kV | 3045_Sarina No 1 33 kV | 3047_Sarina No 2 33 kV | 3047_Sarina No 2 33 kV | 3045_Sarina No 1 33 kV
MK-Mackay Area | 247_Mill 11 kV | % of Rated A | 1.464% | 0.9297% | 0.7172% | 1.473% | 0.9288% | 0.7169% | 1.473% | 0.9288% | 0.7169% | 1.464% | 0.9297% | 0.7172% | 1.467% | 0.9245% | 0.718%
MK-Mackay Area | 247_Mill 11 kV | Limiting Line Name | HV_LINE 141313_1 | HV_CABLE 2596_1 | HV_CABLE 2596_1 | HV_LINE 141313_1 | HV_CABLE 2596_1 | HV_CABLE 2596_1 | HV_LINE 141313_1 | HV_CABLE 2596_1 | HV_CABLE 2596_1 | HV_LINE 141313_1 | HV_CABLE 2596_1 | HV_CABLE 2596_1 | HV_LINE 141313_1 | HV_CABLE 2596_1 | HV_CABLE 2596_1
MK-Mackay Area | 247_Mill 11 kV | Loading (A) | 4.9496 | 3.7186 | 2.8688 | 4.9798 | 3.7151 | 2.8678 | 4.9798 | 3.7151 | 2.8678 | 4.9497 | 3.7187 | 2.8688 | 4.9573 | 3.6982 | 2.872
MK-Mackay Area | 247_Mill 11 kV | Loading (MVA) | 0.094909 | 0.070863 | 0.054851 | 0.0949 | 0.070866 | 0.054852 | 0.0949 | 0.070866 | 0.054852 | 0.094909 | 0.070863 | 0.054851 | 0.094907 | 0.070877 | 0.054848
MK-Mackay Area | 247_Mill 11 kV | Loading (MW) | 0.07907 | 0.058938 | 0.045415 | 0.079071 | 0.058938 | 0.045415 | 0.079071 | 0.058938 | 0.045415 | 0.07907 | 0.058938 | 0.045415 | 0.07907 | 0.05894 | 0.045414
MK-Mackay Area | 247_Mill 11 kV | Power Factor | 0.8331 | 0.8312 | 0.82729 | 0.83319 | 0.83117 | 0.82728 | 0.83319 | 0.83117 | 0.82728 | 0.8331 | 0.8312 | 0.82729 | 0.83312 | 0.83106 | 0.82733
MK-Mackay Area | 247_Mill 11 kV | Rating (A) | 338 | 400 | 400 | 338 | 400 | 400 | 338 | 400 | 400 | 338 | 400 | 400 | 338 | 400 | 400
MK-Mackay Area | 247_Mill 11 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
MK-Mackay Area | 247_Mill 11 kV | Min Voltage at Constrained Conductor | 11.0707 | 11.0021 | 11.0389 | 11.0026 | 11.0129 | 11.0431 | 11.0026 | 11.0129 | 11.0431 | 11.0706 | 11.002 | 11.0387 | 11.0533 | 11.0651 | 11.026
MK-Mackay Area | 247_Mill 11 kV | Contingency Outage | 342_South Mackay 33 kV | 3045_Sarina No 1 33 kV | 3045_Sarina No 1 33 kV | 3045_Sarina No 1 33 kV | 3045_Sarina No 1 33 kV | 3045_Sarina No 1 33 kV | 3045_Sarina No 1 33 kV | 3045_Sarina No 1 33 kV | 3045_Sarina No 1 33 kV | 6333_Hail Creek 66 kV | 3045_Sarina No 1 33 kV | 3045_Sarina No 1 33 kV | 6333_Hail Creek 66 kV | 3047_Sarina No 2 33 kV | 3045_Sarina No 1 33 kV
MK-Mackay Area | 3045_Sarina No 1 33 kV | % of Rated A | 79.33% | 80.46% | 38.45% | 78.81% | 79.92% | 38.22% | 78.81% | 79.92% | 38.22% | 79.33% | 80.46% | 38.45% | 80.89% | 82.03% | 39.13%
MK-Mackay Area | 3045_Sarina No 1 33 kV | Limiting Line Name | TR_LINE 136720_1 | TR_LINE 136720_1 | TR_LINE 136720_1 | TR_LINE 136720_1 | TR_LINE 136720_1 | TR_LINE 136720_1 | TR_LINE 136720_1 | TR_LINE 136720_1 | TR_LINE 136720_1 | TR_LINE 136720_1 | TR_LINE 136720_1 | TR_LINE 136720_1 | TR_LINE 136720_1 | TR_LINE 136720_1 | TR_LINE 136720_1
MK-Mackay Area | 3045_Sarina No 1 33 kV | Loading (A) | 299.8694 | 334.708 | 160.3339 | 297.8995 | 332.4866 | 159.3881 | 297.8995 | 332.4866 | 159.3881 | 299.8732 | 334.7137 | 160.3355 | 305.7488 | 341.2458 | 163.1551
MK-Mackay Area | 3045_Sarina No 1 33 kV | Loading (MVA) | 16.4757 | 18.118 | 9.2197 | 16.38 | 18.0145 | 9.1686 | 16.38 | 18.0145 | 9.1686 | 16.4758 | 18.118 | 9.2197 | 16.7632 | 18.428 | 9.3729
MK-Mackay Area | 3045_Sarina No 1 33 kV | Loading (MW) | 15.4719 | 16.9839 | 8.7774 | 15.385 | 16.8906 | 8.7297 | 15.385 | 16.8906 | 8.7297 | 15.4719 | 16.9839 | 8.7774 | 15.7328 | 17.2639 | 8.9202
MK-Mackay Area | 3045_Sarina No 1 33 kV | Power Factor | 0.93907 | 0.93741 | 0.95203 | 0.93926 | 0.93761 | 0.95213 | 0.93926 | 0.93761 | 0.95213 | 0.93907 | 0.93741 | 0.95203 | 0.93853 | 0.93683 | 0.9517
MK-Mackay Area | 3045_Sarina No 1 33 kV | Rating (A) | 378 | 416 | 417 | 378 | 416 | 417 | 378 | 416 | 417 | 378 | 416 | 417 | 378 | 416 | 417
MK-Mackay Area | 3045_Sarina No 1 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
MK-Mackay Area | 3045_Sarina No 1 33 kV | Min Voltage at Constrained Conductor | 31.7126 | 31.2425 | 33.1948 | 31.7368 | 31.2717 | 33.207 | 31.7368 | 31.2717 | 33.207 | 31.7122 | 31.242 | 33.1945 | 31.6451 | 31.168 | 33.1629
MK-Mackay Area | 3045_Sarina No 1 33 kV | Contingency Outage | 3047_Sarina No 2 33 kV | 3047_Sarina No 2 33 kV | 3047_Sarina No 2 33 kV | 3047_Sarina No 2 33 kV | 3047_Sarina No 2 33 kV | 3047_Sarina No 2 33 kV | 3047_Sarina No 2 33 kV | 3047_Sarina No 2 33 kV | 3047_Sarina No 2 33 kV | 3047_Sarina No 2 33 kV | 3047_Sarina No 2 33 kV | 3047_Sarina No 2 33 kV | 3047_Sarina No 2 33 kV | 3047_Sarina No 2 33 kV | 3047_Sarina No 2 33 kV
MK-Mackay Area | 3046_Rosella 33 kV | % of Rated A | 9.083% | 10.84% | 8.459% | 9.083% | 10.84% | 8.459% | 9.083% | 10.84% | 8.459% | 9.258% | 11.05% | 8.622% | 9.434% | 11.26% | 8.785%
MK-Mackay Area | 3046_Rosella 33 kV | Limiting Line Name | TR_CABLE 7121_1 | TR_CABLE 7121_1 | TR_CABLE 7121_1 | TR_CABLE 7121_1 | TR_CABLE 7121_1 | TR_CABLE 7121_1 | TR_CABLE 7121_1 | TR_CABLE 7121_1 | TR_CABLE 7121_1 | TR_CABLE 7121_1 | TR_CABLE 7121_1 | TR_CABLE 7121_1 | TR_CABLE 7121_1 | TR_CABLE 7121_1 | TR_CABLE 7121_1
MK-Mackay Area | 3046_Rosella 33 kV | Loading (A) | 37.1514 | 44.3391 | 34.5988 | 37.1502 | 44.3369 | 34.5982 | 37.1502 | 44.3369 | 34.5982 | 37.8656 | 45.1949 | 35.263 | 38.5848 | 46.0571 | 35.9296
MK-Mackay Area | 3046_Rosella 33 kV | Loading (MVA) | 2.2 | 2.6192 | 2.0556 | 2.2 | 2.6192 | 2.0556 | 2.2 | 2.6192 | 2.0556 | 2.2419 | 2.6692 | 2.0947 | 2.2838 | 2.7192 | 2.1338
MK-Mackay Area | 3046_Rosella 33 kV | Loading (MW) | 2.1169 | 2.5165 | 1.9787 | 2.1169 | 2.5165 | 1.9787 | 2.1169 | 2.5165 | 1.9787 | 2.1569 | 2.564 | 2.016 | 2.1969 | 2.6116 | 2.0534
MK-Mackay Area | 3046_Rosella 33 kV | Power Factor | 0.96212 | 0.96068 | 0.96246 | 0.96212 | 0.96068 | 0.96246 | 0.96212 | 0.96068 | 0.96246 | 0.96197 | 0.96051 | 0.96233 | 0.96183 | 0.96034 | 0.9622
MK-Mackay Area | 3046_Rosella 33 kV | Rating (A) | 409 | 409 | 409 | 409 | 409 | 409 | 409 | 409 | 409 | 409 | 409 | 409 | 409 | 409 | 409
MK-Mackay Area | 3046_Rosella 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
MK-Mackay Area | 3046_Rosella 33 kV | Min Voltage at Constrained Conductor | 34.1889 | 34.1052 | 34.3014 | 34.19 | 34.1068 | 34.3019 | 34.19 | 34.1068 | 34.3019 | 34.1829 | 34.0979 | 34.2958 | 34.173 | 34.0866 | 34.2886
MK-Mackay Area | 3046_Rosella 33 kV | Contingency Outage | 3045_Sarina No 1 33 kV | 3045_Sarina No 1 33 kV | 3045_Sarina No 1 33 kV | 3045_Sarina No 1 33 kV | 3045_Sarina No 1 33 kV | 3045_Sarina No 1 33 kV | 3045_Sarina No 1 33 kV | 3045_Sarina No 1 33 kV | 3045_Sarina No 1 33 kV | 3045_Sarina No 1 33 kV | 3045_Sarina No 1 33 kV | 3045_Sarina No 1 33 kV | 3045_Sarina No 1 33 kV | 3045_Sarina No 1 33 kV | 3045_Sarina No 1 33 kV
MK-Mackay Area | 3047_Sarina No 2 33 kV | % of Rated A | 78.81% | 79.66% | 38.2% | 78.34% | 79.15% | 37.98% | 78.34% | 79.15% | 37.98% | 78.82% | 79.66% | 38.2% | 80.31% | 81.12% | 38.87%
MK-Mackay Area | 3047_Sarina No 2 33 kV | Limiting Line Name | TR_LINE 11717_1 | TR_LINE 11717_1 | TR_LINE 11717_1 | TR_LINE 11717_1 | TR_LINE 11717_1 | TR_LINE 11717_1 | TR_LINE 11717_1 | TR_LINE 11717_1 | TR_LINE 11717_1 | TR_LINE 11717_1 | TR_LINE 11717_1 | TR_LINE 11717_1 | TR_LINE 11717_1 | TR_LINE 11717_1 | TR_LINE 11717_1
MK-Mackay Area | 3047_Sarina No 2 33 kV | Loading (A) | 299.4934 | 332.9851 | 160.4488 | 297.6943 | 330.8518 | 159.5165 | 297.6943 | 330.8518 | 159.5165 | 299.4972 | 332.9906 | 160.4504 | 305.1754 | 339.1014 | 163.2534
MK-Mackay Area | 3047_Sarina No 2 33 kV | Loading (MVA) | 16.6906 | 18.3846 | 9.2774 | 16.5979 | 18.278 | 9.2256 | 16.5979 | 18.278 | 9.2256 | 16.6906 | 18.3846 | 9.2774 | 16.9806 | 18.691 | 9.4327
MK-Mackay Area | 3047_Sarina No 2 33 kV | Loading (MW) | 15.6225 | 17.1686 | 8.8205 | 15.5345 | 17.073 | 8.7724 | 15.5345 | 17.073 | 8.7724 | 15.6225 | 17.1686 | 8.8205 | 15.8883 | 17.4535 | 8.9649
MK-Mackay Area | 3047_Sarina No 2 33 kV | Power Factor | 0.936 | 0.93385 | 0.95076 | 0.93593 | 0.93407 | 0.95088 | 0.93593 | 0.93407 | 0.95088 | 0.936 | 0.93385 | 0.95076 | 0.93567 | 0.93379 | 0.95041
MK-Mackay Area | 3047_Sarina No 2 33 kV | Rating (A) | 380 | 418 | 420 | 380 | 418 | 420 | 380 | 418 | 420 | 380 | 418 | 420 | 380 | 418 | 420
MK-Mackay Area | 3047_Sarina No 2 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
MK-Mackay Area | 3047_Sarina No 2 33 kV | Min Voltage at Constrained Conductor | 32.1093 | 31.8025 | 33.3497 | 32.1244 | 31.8224 | 33.3578 | 32.1244 | 31.8224 | 33.3578 | 32.1089 | 31.802 | 33.3494 | 32.0576 | 31.7478 | 33.3249
MK-Mackay Area | 3047_Sarina No 2 33 kV | Contingency Outage | 3045_Sarina No 1 33 kV | 3045_Sarina No 1 33 kV | 3045_Sarina No 1 33 kV | 3045_Sarina No 1 33 kV | 3045_Sarina No 1 33 kV | 3045_Sarina No 1 33 kV | 3045_Sarina No 1 33 kV | 3045_Sarina No 1 33 kV | 3045_Sarina No 1 33 kV | 3045_Sarina No 1 33 kV | 3045_Sarina No 1 33 kV | 3045_Sarina No 1 33 kV | 3045_Sarina No 1 33 kV | 3045_Sarina No 1 33 kV | 3045_Sarina No 1 33 kV
MK-Mackay Area | 3053_Mt Bassett 33 kV | % of Rated A | 91.08% | 68.86% | 44.62% | 90.26% | 68.25% | 44.25% | 89.49% | 67.67% | 43.88% | 89.51% | 67.69% | 43.88% | 91.08% | 68.88% | 44.62%
MK-Mackay Area | 3053_Mt Bassett 33 kV | Limiting Line Name | TR_LINE 11627_1 | TR_LINE 11627_1 | TR_LINE 11627_1 | TR_LINE 11627_1 | TR_LINE 11627_1 | TR_LINE 11627_1 | TR_LINE 11627_1 | TR_LINE 11627_1 | TR_LINE 11627_1 | TR_LINE 11627_1 | TR_LINE 11627_1 | TR_LINE 11627_1 | TR_LINE 11627_1 | TR_LINE 11627_1 | TR_LINE 11627_1
MK-Mackay Area | 3053_Mt Bassett 33 kV | Loading (A) | 214.0306 | 223.7791 | 144.1253 | 212.1147 | 221.8153 | 142.9149 | 210.2941 | 219.9205 | 141.7338 | 210.342 | 219.9882 | 141.7477 | 214.027 | 223.8545 | 144.1195
MK-Mackay Area | 3053_Mt Bassett 33 kV | Loading (MVA) | 12.5067 | 13.0784 | 8.4819 | 12.4059 | 12.973 | 8.4144 | 12.3054 | 12.8678 | 8.347 | 12.3055 | 12.868 | 8.3471 | 12.5067 | 13.0787 | 8.4819
MK-Mackay Area | 3053_Mt Bassett 33 kV | Loading (MW) | 12.1727 | 12.721 | 8.2913 | 12.0763 | 12.6202 | 8.226 | 11.98 | 12.5195 | 8.1607 | 11.9801 | 12.5196 | 8.1607 | 12.1727 | 12.7211 | 8.2913
MK-Mackay Area | 3053_Mt Bassett 33 kV | Power Factor | 0.9733 | 0.97267 | 0.97753 | 0.97344 | 0.97281 | 0.97761 | 0.97356 | 0.97294 | 0.97768 | 0.97355 | 0.97293 | 0.97768 | 0.9733 | 0.97266 | 0.97753
MK-Mackay Area | 3053_Mt Bassett 33 kV | Rating (A) | 235 | 325 | 323 | 235 | 325 | 323 | 235 | 325 | 323 | 235 | 325 | 323 | 235 | 325 | 323
MK-Mackay Area | 3053_Mt Bassett 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
MK-Mackay Area | 3053_Mt Bassett 33 kV | Min Voltage at Constrained Conductor | 33.3961 | 33.3848 | 33.756 | 33.4297 | 33.4124 | 33.7732 | 33.4493 | 33.4304 | 33.7838 | 33.4419 | 33.4204 | 33.7806 | 33.3966 | 33.3738 | 33.7573
MK-Mackay Area | 3053_Mt Bassett 33 kV | Contingency Outage | 347_Mt Bassett 33 kV | 347_Mt Bassett 33 kV | 347_Mt Bassett 33 kV | 347_Mt Bassett 33 kV | 347_Mt Bassett 33 kV | 347_Mt Bassett 33 kV | 347_Mt Bassett 33 kV | 347_Mt Bassett 33 kV | 347_Mt Bassett 33 kV | 347_Mt Bassett 33 kV | 347_Mt Bassett 33 kV | 347_Mt Bassett 33 kV | 347_Mt Bassett 33 kV | 347_Mt Bassett 33 kV | 347_Mt Bassett 33 kV
MK-Mackay Area | 340_MK3-1 Farleigh 33 kV | % of Rated A | 2.174% | 1.625% | 1.699% | 2.176% | 1.626% | 1.7% | 2.177% | 1.627% | 1.7% | 2.176% | 1.627% | 1.7% | 2.173% | 1.624% | 1.699%
MK-Mackay Area | 340_MK3-1 Farleigh 33 kV | Limiting Line Name | TR_LINE 11332_1 | TR_LINE 11330_1 | TR_LINE 11330_1 | TR_LINE 11332_1 | TR_LINE 11330_1 | TR_LINE 11330_1 | TR_LINE 11332_1 | TR_LINE 11330_1 | TR_LINE 11330_1 | TR_LINE 11332_1 | TR_LINE 11330_1 | TR_LINE 11330_1 | TR_LINE 11332_1 | TR_LINE 11330_1 | TR_LINE 11330_1
MK-Mackay Area | 340_MK3-1 Farleigh 33 kV | Loading (A) | 3.7397 | 3.6559 | 3.7723 | 3.7431 | 3.6591 | 3.774 | 3.7443 | 3.6603 | 3.7746 | 3.7435 | 3.6598 | 3.7742 | 3.7371 | 3.6532 | 3.7717
MK-Mackay Area | 340_MK3-1 Farleigh 33 kV | Loading (MVA) | 0.21464 | 0.20855 | 0.22204 | 0.21502 | 0.20892 | 0.22225 | 0.21517 | 0.20905 | 0.22231 | 0.21507 | 0.20899 | 0.22227 | 0.21434 | 0.20824 | 0.22197
MK-Mackay Area | 340_MK3-1 Farleigh 33 kV | Loading (MW) | 0.0039436 | 0.0038765 | 0.0041272 | 0.0039508 | 0.0038834 | 0.0041311 | 0.0039534 | 0.0038858 | 0.0041323 | 0.0039517 | 0.0038848 | 0.0041316 | 0.0039382 | 0.0038708 | 0.004126
MK-Mackay Area | 340_MK3-1 Farleigh 33 kV | Power Factor | 0.018374 | 0.018588 | 0.018588 | 0.018374 | 0.018588 | 0.018588 | 0.018374 | 0.018588 | 0.018588 | 0.018374 | 0.018588 | 0.018588 | 0.018374 | 0.018588 | 0.018588
MK-Mackay Area | 340_MK3-1 Farleigh 33 kV | Rating (A) | 172 | 225 | 222 | 172 | 225 | 222 | 172 | 225 | 222 | 172 | 225 | 222 | 172 | 225 | 222
MK-Mackay Area | 340_MK3-1 Farleigh 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
MK-Mackay Area | 340_MK3-1 Farleigh 33 kV | Min Voltage at Constrained Conductor | 33.1365 | 32.9348 | 33.9831 | 33.1664 | 32.964 | 33.9991 | 33.1776 | 32.9744 | 34.0043 | 33.1702 | 32.9699 | 34.001 | 33.1138 | 32.9107 | 33.9782
MK-Mackay Area | 340_MK3-1 Farleigh 33 kV | Contingency Outage | 364_West Mackay No 1 33 kV | 422_North Mackay No 1 33 kV | PV 6/5_Glenella No 1 66 kV | 364_West Mackay No 1 33 kV | 422_North Mackay No 1 33 kV | PV 6/5_Glenella No 1 66 kV | 364_West Mackay No 1 33 kV | 422_North Mackay No 1 33 kV | PV 6/5_Glenella No 1 66 kV | 364_West Mackay No 1 33 kV | 422_North Mackay No 1 33 kV | PV 6/5_Glenella No 1 66 kV | 364_West Mackay No 1 33 kV | 422_North Mackay No 1 33 kV | PV 6/5_Glenella No 1 66 kV
MK-Mackay Area | 341_Tennyson St No 2 33 kV | % of Rated A | 92.25% | 82.76% | 54.22% | 91.24% | 81.89% | 53.66% | 90.27% | 81.04% | 53.11% | 90.29% | 81.06% | 53.12% | 90.87% | 81.66% | 53.48%
MK-Mackay Area | 341_Tennyson St No 2 33 kV | Limiting Line Name | TR_CABLE 29_1 | TR_CABLE 29_1 | TR_CABLE 29_1 | TR_CABLE 29_1 | TR_CABLE 29_1 | TR_CABLE 29_1 | TR_CABLE 29_1 | TR_CABLE 29_1 | TR_CABLE 29_1 | TR_CABLE 29_1 | TR_CABLE 29_1 | TR_CABLE 29_1 | TR_CABLE 29_1 | TR_CABLE 29_1 | TR_CABLE 29_1
MK-Mackay Area | 341_Tennyson St No 2 33 kV | Loading (A) | 322.8736 | 289.6622 | 189.7681 | 319.3441 | 286.6086 | 187.8146 | 315.9485 | 283.6395 | 185.8985 | 316.0177 | 283.7228 | 185.9163 | 318.0581 | 285.8181 | 187.174
MK-Mackay Area | 341_Tennyson St No 2 33 kV | Loading (MVA) | 19.1188 | 17.1797 | 11.2694 | 18.9242 | 17.0083 | 11.1575 | 18.7299 | 16.8372 | 11.0456 | 18.7301 | 16.8374 | 11.0457 | 18.8354 | 16.9476 | 11.1162
MK-Mackay Area | 341_Tennyson St No 2 33 kV | Loading (MW) | 18.8712 | 16.9846 | 11.1664 | 18.681 | 16.8166 | 11.0562 | 18.4909 | 16.6487 | 10.9461 | 18.491 | 16.6489 | 10.9461 | 18.5952 | 16.7577 | 11.0163
MK-Mackay Area | 341_Tennyson St No 2 33 kV | Power Factor | 0.98416 | 0.98595 | 0.98862 | 0.98428 | 0.98605 | 0.98869 | 0.98439 | 0.98615 | 0.98876 | 0.98439 | 0.98614 | 0.98875 | 0.98439 | 0.98612 | 0.98877
MK-Mackay Area | 341_Tennyson St No 2 33 kV | Rating (A) | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350
MK-Mackay Area | 341_Tennyson St No 2 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
MK-Mackay Area | 341_Tennyson St No 2 33 kV | Min Voltage at Constrained Conductor | 34.1876 | 34.2424 | 34.286 | 34.2135 | 34.2619 | 34.2986 | 34.2262 | 34.2722 | 34.3048 | 34.2191 | 34.2625 | 34.3016 | 34.1907 | 34.2339 | 34.2887
MK-Mackay Area | 341_Tennyson St No 2 33 kV | Contingency Outage | 395_Tennyson Street-Alfred Street 33 kV | 395_Tennyson Street-Alfred Street 33 kV | 395_Tennyson Street-Alfred Street 33 kV | 395_Tennyson Street-Alfred Street 33 kV | 395_Tennyson Street-Alfred Street 33 kV | 395_Tennyson Street-Alfred Street 33 kV | 395_Tennyson Street-Alfred Street 33 kV | 395_Tennyson Street-Alfred Street 33 kV | 395_Tennyson Street-Alfred Street 33 kV | 395_Tennyson Street-Alfred Street 33 kV | 395_Tennyson Street-Alfred Street 33 kV | 395_Tennyson Street-Alfred Street 33 kV | 395_Tennyson Street-Alfred Street 33 kV | 395_Tennyson Street-Alfred Street 33 kV | 395_Tennyson Street-Alfred Street 33 kV
MK-Mackay Area | 342_South Mackay 33 kV | % of Rated A | 93.52% | 55.54% | 54.65% | 92.23% | 54.94% | 54.06% | 91.59% | 54.64% | 53.77% | 91.73% | 54.74% | 53.84% | 92.21% | 54.99% | 54.06%
MK-Mackay Area | 342_South Mackay 33 kV | Limiting Line Name | TR_LINE 12122806_1 | TR_LINE 12122806_1 | TR_LINE 12122806_1 | TR_LINE 12122806_1 | TR_LINE 12122806_1 | TR_LINE 12122806_1 | TR_LINE 12122806_1 | TR_LINE 12122806_1 | TR_LINE 12122806_1 | TR_LINE 12122806_1 | TR_LINE 12122806_1 | TR_LINE 12122806_1 | TR_LINE 12122806_1 | TR_LINE 12122806_1 | TR_LINE 12122806_1
MK-Mackay Area | 342_South Mackay 33 kV | Loading (A) | 316.1106 | 272.1663 | 268.3373 | 311.7301 | 269.2149 | 265.4448 | 309.5604 | 267.7555 | 264.0099 | 310.0506 | 268.2273 | 264.3689 | 311.6649 | 269.4656 | 265.4536
MK-Mackay Area | 342_South Mackay 33 kV | Loading (MVA) | 18.7914 | 16.1908 | 15.9728 | 18.5444 | 16.0273 | 15.8059 | 18.4212 | 15.9444 | 15.7228 | 18.446 | 15.9693 | 15.7428 | 18.529 | 16.024 | 15.8018
MK-Mackay Area | 342_South Mackay 33 kV | Loading (MW) | 16.4158 | 13.1019 | 12.6792 | 16.095 | 12.8657 | 12.4404 | 15.9347 | 12.7476 | 12.321 | 15.9755 | 12.796 | 12.3589 | 16.0966 | 12.9035 | 12.4566
MK-Mackay Area | 342_South Mackay 33 kV | Power Factor | 0.87338 | 0.80905 | 0.79363 | 0.86772 | 0.80257 | 0.78691 | 0.86483 | 0.79934 | 0.78347 | 0.86588 | 0.80112 | 0.78489 | 0.86853 | 0.80509 | 0.78814
MK-Mackay Area | 342_South Mackay 33 kV | Rating (A) | 338 | 490 | 491 | 338 | 490 | 491 | 338 | 490 | 491 | 338 | 490 | 491 | 338 | 490 | 491
MK-Mackay Area | 342_South Mackay 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
MK-Mackay Area | 342_South Mackay 33 kV | Min Voltage at Constrained Conductor | 34.3188 | 34.3422 | 34.3629 | 34.3435 | 34.368 | 34.3743 | 34.3543 | 34.3765 | 34.3795 | 34.3463 | 34.3697 | 34.3765 | 34.3222 | 34.329 | 34.3643
MK-Mackay Area | 342_South Mackay 33 kV | Contingency Outage | PV 6/4_Glenella No 2 66 kV | PV 6/4_Glenella No 2 66 kV | 341_Tennyson St No 2 33 kV | PV 6/4_Glenella No 2 66 kV | PV 6/4_Glenella No 2 66 kV | 423_North Mackay No 2 33 kV | PV 6/4_Glenella No 2 66 kV | PV 6/4_Glenella No 2 66 kV | 423_North Mackay No 2 33 kV | PV 6/4_Glenella No 2 66 kV | PV 6/4_Glenella No 2 66 kV | 423_North Mackay No 2 33 kV | PV 6/4_Glenella No 2 66 kV | PV 6/4_Glenella No 2 66 kV | 341_Tennyson St No 2 33 kV
MK-Mackay Area | 343_Pleystowe 33 kV | % of Rated A | 76.55% | 94.63% | 35.6% | 75.84% | 93.71% | 35.22% | 75.81% | 93.68% | 35.21% | 75.83% | 93.71% | 35.21% | 77.32% | 95.55% | 35.81%
MK-Mackay Area | 343_Pleystowe 33 kV | Limiting Line Name | TR_CABLE 4169_1 | TR_CABLE 4169_1 | TR_CABLE 4169_1 | TR_CABLE 4169_1 | TR_CABLE 4169_1 | TR_CABLE 4169_1 | TR_CABLE 4169_1 | TR_CABLE 4169_1 | TR_CABLE 4169_1 | TR_CABLE 4169_1 | TR_CABLE 4169_1 | TR_CABLE 4169_1 | TR_CABLE 4169_1 | TR_CABLE 4169_1 | TR_CABLE 4169_1
MK-Mackay Area | 343_Pleystowe 33 kV | Loading (A) | 168.4165 | 208.1883 | 78.3286 | 166.8375 | 206.166 | 77.4748 | 166.7766 | 206.1039 | 77.4624 | 166.8165 | 206.1726 | 77.47 | 170.1 | 210.2198 | 78.7777
MK-Mackay Area | 343_Pleystowe 33 kV | Loading (MVA) | 9.5782 | 11.7115 | 4.5764 | 9.4999 | 11.6113 | 4.5291 | 9.4998 | 11.6112 | 4.5291 | 9.4998 | 11.6114 | 4.5291 | 9.669 | 11.8146 | 4.6022
MK-Mackay Area | 343_Pleystowe 33 kV | Loading (MW) | 9.4805 | 11.5713 | 4.5598 | 9.4036 | 11.4732 | 4.513 | 9.4035 | 11.4731 | 4.513 | 9.4036 | 11.4732 | 4.513 | 9.5688 | 11.672 | 4.5853
MK-Mackay Area | 343_Pleystowe 33 kV | Power Factor | 0.98973 | 0.98797 | 0.99632 | 0.98979 | 0.98804 | 0.99639 | 0.9898 | 0.98805 | 0.99639 | 0.9898 | 0.98804 | 0.99639 | 0.98957 | 0.98787 | 0.99627
MK-Mackay Area | 343_Pleystowe 33 kV | Rating (A) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
MK-Mackay Area | 343_Pleystowe 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
MK-Mackay Area | 343_Pleystowe 33 kV | Min Voltage at Constrained Conductor | 32.8348 | 32.4771 | 33.732 | 32.8744 | 32.5152 | 33.7514 | 32.886 | 32.5246 | 33.7568 | 32.8784 | 32.5142 | 33.7535 | 32.8179 | 32.4463 | 33.7291
MK-Mackay Area | 343_Pleystowe 33 kV | Contingency Outage | 346_Ritchies Rd 33 kV | 346_Ritchies Rd 33 kV | 346_Ritchies Rd 33 kV | 346_Ritchies Rd 33 kV | 346_Ritchies Rd 33 kV | 346_Ritchies Rd 33 kV | 346_Ritchies Rd 33 kV | 346_Ritchies Rd 33 kV | 346_Ritchies Rd 33 kV | 346_Ritchies Rd 33 kV | 346_Ritchies Rd 33 kV | 346_Ritchies Rd 33 kV | 346_Ritchies Rd 33 kV | 346_Ritchies Rd 33 kV | 346_Ritchies Rd 33 kV
MK-Mackay Area | 344_West Mackay 2 33 kV | % of Rated A | 23.17% | 21.27% | 14.44% | 22.92% | 21.03% | 14.28% | 22.91% | 21.03% | 14.28% | 22.92% | 21.03% | 14.28% | 23.18% | 21.28% | 14.44%
MK-Mackay Area | 344_West Mackay 2 33 kV | Limiting Line Name | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1
MK-Mackay Area | 344_West Mackay 2 33 kV | Loading (A) | 144.837 | 132.9511 | 90.2633 | 143.246 | 131.4468 | 89.2725 | 143.2111 | 131.4198 | 89.2628 | 143.2369 | 131.4502 | 89.269 | 144.8531 | 132.9994 | 90.2651
MK-Mackay Area | 344_West Mackay 2 33 kV | Loading (MVA) | 8.5706 | 7.8653 | 5.3362 | 8.481 | 7.7805 | 5.2789 | 8.481 | 7.7804 | 5.2789 | 8.481 | 7.7805 | 5.2789 | 8.5706 | 7.8654 | 5.3362
MK-Mackay Area | 344_West Mackay 2 33 kV | Loading (MW) | 8.3869 | 7.7018 | 5.2422 | 8.298 | 7.6196 | 5.1863 | 8.298 | 7.6196 | 5.1863 | 8.298 | 7.6196 | 5.1863 | 8.3869 | 7.7018 | 5.2422
MK-Mackay Area | 344_West Mackay 2 33 kV | Power Factor | 0.97831 | 0.97896 | 0.98213 | 0.97816 | 0.97908 | 0.9822 | 0.97817 | 0.97908 | 0.9822 | 0.97816 | 0.97908 | 0.9822 | 0.97831 | 0.97895 | 0.98213
MK-Mackay Area | 344_West Mackay 2 33 kV | Rating (A) | 625 | 625 | 625 | 625 | 625 | 625 | 625 | 625 | 625 | 625 | 625 | 625 | 625 | 625 | 625
MK-Mackay Area | 344_West Mackay 2 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
MK-Mackay Area | 344_West Mackay 2 33 kV | Min Voltage at Constrained Conductor | 34.1642 | 34.1559 | 34.1317 | 34.1827 | 34.1739 | 34.1402 | 34.1908 | 34.1807 | 34.1438 | 34.1848 | 34.173 | 34.1415 | 34.1605 | 34.1438 | 34.131
MK-Mackay Area | 344_West Mackay 2 33 kV | Contingency Outage | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV
MK-Mackay Area | 346_Ritchies Rd 33 kV | % of Rated A | 77.92% | 70.12% | 26.02% | 77.17% | 69.41% | 25.74% | 77.16% | 69.39% | 25.73% | 77.16% | 69.42% | 25.74% | 78.72% | 70.84% | 26.17%
MK-Mackay Area | 346_Ritchies Rd 33 kV | Limiting Line Name | TR_LINE 11327_1 | TR_LINE 11327_1 | TR_LINE 11327_1 | TR_LINE 11327_1 | TR_LINE 11327_1 | TR_LINE 11327_1 | TR_LINE 11327_1 | TR_LINE 11327_1 | TR_LINE 11327_1 | TR_LINE 11327_1 | TR_LINE 11327_1 | TR_LINE 11327_1 | TR_LINE 11327_1 | TR_LINE 11327_1 | TR_LINE 11327_1
MK-Mackay Area | 346_Ritchies Rd 33 kV | Loading (A) | 171.4216 | 213.1569 | 78.8478 | 169.7746 | 211.0168 | 77.9846 | 169.7421 | 210.9492 | 77.9719 | 169.7522 | 211.0239 | 77.9797 | 173.1794 | 215.3629 | 79.3037
MK-Mackay Area | 346_Ritchies Rd 33 kV | Loading (MVA) | 9.584 | 11.7225 | 4.5771 | 9.5055 | 11.622 | 4.5299 | 9.5067 | 11.6219 | 4.5299 | 9.5054 | 11.6221 | 4.5299 | 9.675 | 11.828 | 4.6029
MK-Mackay Area | 346_Ritchies Rd 33 kV | Loading (MW) | 9.4852 | 11.5796 | 4.5604 | 9.4081 | 11.4813 | 4.5137 | 9.4086 | 11.4812 | 4.5137 | 9.4081 | 11.4813 | 4.5137 | 9.5736 | 11.6814 | 4.586
MK-Mackay Area | 346_Ritchies Rd 33 kV | Power Factor | 0.98969 | 0.98781 | 0.99636 | 0.98975 | 0.98789 | 0.99641 | 0.98968 | 0.98789 | 0.99642 | 0.98976 | 0.98789 | 0.99641 | 0.98952 | 0.98761 | 0.99632
MK-Mackay Area | 346_Ritchies Rd 33 kV | Rating (A) | 220 | 304 | 303 | 220 | 304 | 303 | 220 | 304 | 303 | 220 | 304 | 303 | 220 | 304 | 303
MK-Mackay Area | 346_Ritchies Rd 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
MK-Mackay Area | 346_Ritchies Rd 33 kV | Min Voltage at Constrained Conductor | 32.275 | 31.746 | 33.5132 | 32.3212 | 31.7933 | 33.5352 | 32.3314 | 31.803 | 33.5406 | 32.3253 | 31.7923 | 33.5373 | 32.2508 | 31.7036 | 33.5087
MK-Mackay Area | 346_Ritchies Rd 33 kV | Contingency Outage | 343_Pleystowe 33 kV | 343_Pleystowe 33 kV | 343_Pleystowe 33 kV | 343_Pleystowe 33 kV | 343_Pleystowe 33 kV | 343_Pleystowe 33 kV | 343_Pleystowe 33 kV | 343_Pleystowe 33 kV | 343_Pleystowe 33 kV | 343_Pleystowe 33 kV | 343_Pleystowe 33 kV | 343_Pleystowe 33 kV | 343_Pleystowe 33 kV | 343_Pleystowe 33 kV | 343_Pleystowe 33 kV
MK-Mackay Area | 347_Mt Bassett 33 kV | % of Rated A | 82.98% | 86.66% | 56.07% | 82.25% | 85.91% | 55.6% | 81.55% | 85.19% | 55.14% | 81.57% | 85.22% | 55.15% | 82.98% | 86.69% | 56.06%
MK-Mackay Area | 347_Mt Bassett 33 kV | Limiting Line Name | TR_CABLE 4883_1 | TR_CABLE 4883_1 | TR_CABLE 4883_1 | TR_CABLE 4883_1 | TR_CABLE 4883_1 | TR_CABLE 4883_1 | TR_CABLE 4883_1 | TR_CABLE 4883_1 | TR_CABLE 4883_1 | TR_CABLE 4883_1 | TR_CABLE 4883_1 | TR_CABLE 4883_1 | TR_CABLE 4883_1 | TR_CABLE 4883_1 | TR_CABLE 4883_1
MK-Mackay Area | 347_Mt Bassett 33 kV | Loading (A) | 211.6064 | 220.9907 | 142.9661 | 209.7368 | 219.0781 | 141.7746 | 207.9582 | 217.2333 | 140.6122 | 208.0044 | 217.2983 | 140.6258 | 211.5922 | 221.0537 | 142.9568
MK-Mackay Area | 347_Mt Bassett 33 kV | Loading (MVA) | 12.5247 | 13.0975 | 8.489 | 12.4236 | 12.9917 | 8.4214 | 12.3229 | 12.8863 | 8.3539 | 12.323 | 12.8865 | 8.3539 | 12.5247 | 13.0977 | 8.489
MK-Mackay Area | 347_Mt Bassett 33 kV | Loading (MW) | 12.1843 | 12.7332 | 8.297 | 12.0877 | 12.6323 | 8.2316 | 11.9912 | 12.5314 | 8.1662 | 11.9913 | 12.5315 | 8.1662 | 12.1843 | 12.7333 | 8.297
MK-Mackay Area | 347_Mt Bassett 33 kV | Power Factor | 0.97271 | 0.97208 | 0.97728 | 0.97285 | 0.97222 | 0.97736 | 0.97298 | 0.97235 | 0.97743 | 0.97297 | 0.97234 | 0.97743 | 0.97271 | 0.97207 | 0.97728
MK-Mackay Area | 347_Mt Bassett 33 kV | Rating (A) | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255
MK-Mackay Area | 347_Mt Bassett 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
MK-Mackay Area | 347_Mt Bassett 33 kV | Min Voltage at Constrained Conductor | 34.1726 | 34.2179 | 34.2819 | 34.1989 | 34.2379 | 34.2947 | 34.2117 | 34.2484 | 34.3009 | 34.2045 | 34.2387 | 34.2978 | 34.1748 | 34.2087 | 34.2841
MK-Mackay Area | 347_Mt Bassett 33 kV | Contingency Outage | 3053_Mt Bassett 33 kV | 3053_Mt Bassett 33 kV | 3053_Mt Bassett 33 kV | 3053_Mt Bassett 33 kV | 3053_Mt Bassett 33 kV | 3053_Mt Bassett 33 kV | 3053_Mt Bassett 33 kV | 3053_Mt Bassett 33 kV | 3053_Mt Bassett 33 kV | 3053_Mt Bassett 33 kV | 3053_Mt Bassett 33 kV | 3053_Mt Bassett 33 kV | 3053_Mt Bassett 33 kV | 3053_Mt Bassett 33 kV | 3053_Mt Bassett 33 kV
MK-Mackay Area | 348_Farleigh 33 kV | % of Rated A | 36.2% | 31.5% | 7.68% | 36.15% | 31.45% | 7.675% | 36.15% | 31.44% | 7.674% | 36.14% | 31.45% | 7.675% | 37.07% | 32.28% | 7.85%
MK-Mackay Area | 348_Farleigh 33 kV | Limiting Line Name | TR_LINE 11976_1 | TR_LINE 11976_1 | TR_LINE 13162_1 | TR_LINE 11976_1 | TR_LINE 11976_1 | TR_LINE 13162_1 | TR_LINE 11976_1 | TR_LINE 11976_1 | TR_LINE 13162_1 | TR_LINE 11976_1 | TR_LINE 11976_1 | TR_LINE 13162_1 | TR_LINE 11976_1 | TR_LINE 11976_1 | TR_LINE 13162_1
MK-Mackay Area | 348_Farleigh 33 kV | Loading (A) | 70.2352 | 81.8989 | 19.8152 | 70.1268 | 81.7658 | 19.8025 | 70.1259 | 81.7384 | 19.7994 | 70.1173 | 81.7686 | 19.8013 | 71.9155 | 83.9267 | 20.2522
MK-Mackay Area | 348_Farleigh 33 kV | Loading (MVA) | 3.8877 | 4.45 | 1.1495 | 3.8874 | 4.4496 | 1.1495 | 3.8885 | 4.4495 | 1.1495 | 3.8873 | 4.4496 | 1.1495 | 3.9767 | 4.5526 | 1.1746
MK-Mackay Area | 348_Farleigh 33 kV | Loading (MW) | 3.8538 | 4.4005 | 1.1467 | 3.8537 | 4.4003 | 1.1467 | 3.8542 | 4.4003 | 1.1467 | 3.8537 | 4.4003 | 1.1467 | 3.9406 | 4.5 | 1.1723
MK-Mackay Area | 348_Farleigh 33 kV | Power Factor | 0.99129 | 0.98888 | 0.99764 | 0.99134 | 0.98893 | 0.99762 | 0.99118 | 0.98894 | 0.99761 | 0.99134 | 0.98893 | 0.99762 | 0.99094 | 0.98845 | 0.99799
MK-Mackay Area | 348_Farleigh 33 kV | Rating (A) | 194 | 260 | 258 | 194 | 260 | 258 | 194 | 260 | 258 | 194 | 260 | 258 | 194 | 260 | 258
MK-Mackay Area | 348_Farleigh 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
MK-Mackay Area | 348_Farleigh 33 kV | Min Voltage at Constrained Conductor | 31.9143 | 31.3186 | 33.4897 | 31.9613 | 31.3668 | 33.5118 | 31.9711 | 31.3767 | 33.5171 | 31.9654 | 31.3658 | 33.5138 | 31.8808 | 31.2648 | 33.4846
MK-Mackay Area | 348_Farleigh 33 kV | Contingency Outage | 343_Pleystowe 33 kV | 343_Pleystowe 33 kV | 343_Pleystowe 33 kV | 343_Pleystowe 33 kV | 343_Pleystowe 33 kV | 343_Pleystowe 33 kV | 343_Pleystowe 33 kV | 343_Pleystowe 33 kV | 343_Pleystowe 33 kV | 343_Pleystowe 33 kV | 343_Pleystowe 33 kV | 343_Pleystowe 33 kV | 343_Pleystowe 33 kV | 343_Pleystowe 33 kV | 343_Pleystowe 33 kV
MK-Mackay Area | 349_Pioneer Valley - Pinnacle 66 kV | % of Rated A | 37.99% | 34.07% | 16.29% | 37.97% | 34.41% | 16.29% | 37.64% | 34.12% | 16.16% | 38.31% | 34.71% | 16.41% | 38.84% | 34.97% | 16.66%
MK-Mackay Area | 349_Pioneer Valley - Pinnacle 66 kV | Limiting Line Name | TR_LINE 10055_2 | TR_LINE 10055_2 | TR_LINE 10055_2 | TR_LINE 10055_2 | TR_LINE 10055_2 | TR_LINE 10055_2 | TR_LINE 10055_2 | TR_LINE 10055_2 | TR_LINE 10055_2 | TR_LINE 10055_2 | TR_LINE 10055_2 | TR_LINE 10055_2 | TR_LINE 10055_2 | TR_LINE 10055_2 | TR_LINE 10055_2
MK-Mackay Area | 349_Pioneer Valley - Pinnacle 66 kV | Loading (A) | 83.5682 | 103.5623 | 49.3617 | 83.5299 | 104.606 | 49.3535 | 82.8148 | 103.7371 | 48.9707 | 84.2858 | 105.5212 | 49.7322 | 85.4569 | 106.2946 | 50.4808
MK-Mackay Area | 349_Pioneer Valley - Pinnacle 66 kV | Loading (MVA) | 9.8527 | 12.2922 | 5.8854 | 9.8524 | 12.2995 | 5.8854 | 9.77 | 12.1995 | 5.8403 | 9.9381 | 12.4011 | 5.93 | 10.0874 | 12.5979 | 6.017
MK-Mackay Area | 349_Pioneer Valley - Pinnacle 66 kV | Loading (MW) | 9.7458 | 12.0952 | 5.8786 | 9.7458 | 12.0967 | 5.8786 | 9.6662 | 12.0009 | 5.8341 | 9.8283 | 12.1939 | 5.9226 | 9.9726 | 12.386 | 6.0084
MK-Mackay Area | 349_Pioneer Valley - Pinnacle 66 kV | Power Factor | 0.98915 | 0.98397 | 0.99884 | 0.98917 | 0.98351 | 0.99885 | 0.98937 | 0.98372 | 0.99893 | 0.98896 | 0.98329 | 0.99876 | 0.98862 | 0.98318 | 0.99856
MK-Mackay Area | 349_Pioneer Valley - Pinnacle 66 kV | Rating (A) | 220 | 304 | 303 | 220 | 304 | 303 | 220 | 304 | 303 | 220 | 304 | 303 | 220 | 304 | 303
MK-Mackay Area | 349_Pioneer Valley - Pinnacle 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
MK-Mackay Area | 349_Pioneer Valley - Pinnacle 66 kV | Min Voltage at Constrained Conductor | 68.0679 | 68.5252 | 68.8367 | 68.0971 | 67.8818 | 68.8477 | 68.1103 | 67.894 | 68.8546 | 68.073 | 67.8491 | 68.841 | 68.1489 | 68.4244 | 68.8162
MK-Mackay Area | 349_Pioneer Valley - Pinnacle 66 kV | Contingency Outage | PV 6/4_Glenella No 2 66 kV | PV 6/4_Glenella No 2 66 kV | 423_North Mackay No 2 33 kV | PV 6/4_Glenella No 2 66 kV | 343_Pleystowe 33 kV | 423_North Mackay No 2 33 kV | PV 6/4_Glenella No 2 66 kV | 343_Pleystowe 33 kV | 423_North Mackay No 2 33 kV | PV 6/4_Glenella No 2 66 kV | 343_Pleystowe 33 kV | 423_North Mackay No 2 33 kV | 342_South Mackay 33 kV | PV 6/4_Glenella No 2 66 kV | 423_North Mackay No 2 33 kV
MK-Mackay Area | 351_Alligator Creek 33 kV | % of Rated A | 15.83% | 18.8% | 14.72% | 15.81% | 18.78% | 14.71% | 15.8% | 18.77% | 14.71% | 16.11% | 19.14% | 14.99% | 16.43% | 19.52% | 15.28%
MK-Mackay Area | 351_Alligator Creek 33 kV | Limiting Line Name | TR_CABLE 7120_1 | TR_CABLE 7120_1 | TR_CABLE 7120_1 | TR_CABLE 7120_1 | TR_CABLE 7120_1 | TR_CABLE 7120_1 | TR_CABLE 7120_1 | TR_CABLE 7120_1 | TR_CABLE 7120_1 | TR_CABLE 7120_1 | TR_CABLE 7120_1 | TR_CABLE 7120_1 | TR_CABLE 7120_1 | TR_CABLE 7120_1 | TR_CABLE 7120_1
MK-Mackay Area | 351_Alligator Creek 33 kV | Loading (A) | 37.0373 | 43.985 | 34.4456 | 37 | 43.9425 | 34.4277 | 36.9831 | 43.9272 | 34.4192 | 37.7009 | 44.7807 | 35.0809 | 38.4408 | 45.6845 | 35.7548
MK-Mackay Area | 351_Alligator Creek 33 kV | Loading (MVA) | 2.2004 | 2.6194 | 2.0554 | 2.2003 | 2.6194 | 2.0554 | 2.2003 | 2.6194 | 2.0554 | 2.2422 | 2.6694 | 2.0945 | 2.2842 | 2.7195 | 2.1337
MK-Mackay Area | 351_Alligator Creek 33 kV | Loading (MW) | 2.1169 | 2.5165 | 1.9786 | 2.1169 | 2.5165 | 1.9786 | 2.1169 | 2.5165 | 1.9786 | 2.1569 | 2.5641 | 2.016 | 2.1969 | 2.6116 | 2.0534
MK-Mackay Area | 351_Alligator Creek 33 kV | Power Factor | 0.96198 | 0.96061 | 0.96252 | 0.96199 | 0.96062 | 0.96253 | 0.962 | 0.96063 | 0.96253 | 0.96186 | 0.96045 | 0.9624 | 0.9617 | 0.96026 | 0.96227
MK-Mackay Area | 351_Alligator Creek 33 kV | Rating (A) | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234 | 234
MK-Mackay Area | 351_Alligator Creek 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
MK-Mackay Area | 351_Alligator Creek 33 kV | Min Voltage at Constrained Conductor | 34.3 | 34.383 | 34.4513 | 34.334 | 34.4155 | 34.469 | 34.3494 | 34.4272 | 34.4773 | 34.3373 | 34.4158 | 34.4708 | 34.3066 | 34.3679 | 34.4533
MK-Mackay Area | 351_Alligator Creek 33 kV | Contingency Outage | PV 6/4_Glenella No 2 66 kV | PV 6/4_Glenella No 2 66 kV | 341_Tennyson St No 2 33 kV | PV 6/4_Glenella No 2 66 kV | PV 6/4_Glenella No 2 66 kV | 423_North Mackay No 2 33 kV | PV 6/4_Glenella No 2 66 kV | PV 6/4_Glenella No 2 66 kV | 423_North Mackay No 2 33 kV | PV 6/4_Glenella No 2 66 kV | PV 6/4_Glenella No 2 66 kV | 423_North Mackay No 2 33 kV | PV 6/4_Glenella No 2 66 kV | PV 6/4_Glenella No 2 66 kV | 341_Tennyson St No 2 33 kV
MK-Mackay Area | 360_Pinnacle-Crediton/Eungella Dam 66 kV | % of Rated A | 11.15% | 9.828% | 7.684% | 11.14% | 9.935% | 7.682% | 11.14% | 9.933% | 7.682% | 11.15% | 9.942% | 7.684% | 11.13% | 9.848% | 7.688%
MK-Mackay Area | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Limiting Line Name | TR_LINE 9915_1 | TR_LINE 9915_1 | TR_LINE 9915_1 | TR_LINE 9915_1 | TR_LINE 9915_1 | TR_LINE 9915_1 | TR_LINE 9915_1 | TR_LINE 9915_1 | TR_LINE 9915_1 | TR_LINE 9915_1 | TR_LINE 9915_1 | TR_LINE 9915_1 | TR_LINE 9915_1 | TR_LINE 9915_1 | TR_LINE 9915_1
MK-Mackay Area | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Loading (A) | 10.2541 | 11.6955 | 8.6828 | 10.2491 | 11.8226 | 8.6812 | 10.2468 | 11.8202 | 8.6802 | 10.2544 | 11.8306 | 8.6826 | 10.2429 | 11.7197 | 8.6872
MK-Mackay Area | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Loading (MVA) | 1.1933 | 1.3653 | 1.0261 | 1.1932 | 1.3666 | 1.0261 | 1.1932 | 1.3666 | 1.0261 | 1.1933 | 1.3667 | 1.0261 | 1.1931 | 1.3655 | 1.0262
MK-Mackay Area | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Loading (MW) | 1.1639 | 1.3374 | 0.99609 | 1.1639 | 1.3375 | 0.99609 | 1.1639 | 1.3375 | 0.99609 | 1.1639 | 1.3375 | 0.99609 | 1.1639 | 1.3374 | 0.9961
MK-Mackay Area | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Power Factor | 0.97535 | 0.97951 | 0.97075 | 0.97539 | 0.97867 | 0.97077 | 0.97541 | 0.97868 | 0.97078 | 0.97534 | 0.97861 | 0.97075 | 0.97545 | 0.97935 | 0.97069
MK-Mackay Area | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Rating (A) | 92 | 119 | 113 | 92 | 119 | 113 | 92 | 119 | 113 | 92 | 119 | 113 | 92 | 119 | 113
MK-Mackay Area | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
MK-Mackay Area | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Min Voltage at Constrained Conductor | 67.186 | 67.3978 | 68.2286 | 67.2159 | 66.7372 | 68.2398 | 67.2294 | 66.7497 | 68.2468 | 67.185 | 66.696 | 68.2298 | 67.2521 | 67.2706 | 68.1981
MK-Mackay Area | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Contingency Outage | PV 6/4_Glenella No 2 66 kV | PV 6/4_Glenella No 2 66 kV | 423_North Mackay No 2 33 kV | PV 6/4_Glenella No 2 66 kV | 343_Pleystowe 33 kV | 423_North Mackay No 2 33 kV | PV 6/4_Glenella No 2 66 kV | 343_Pleystowe 33 kV | 423_North Mackay No 2 33 kV | PV 6/4_Glenella No 2 66 kV | 343_Pleystowe 33 kV | 423_North Mackay No 2 33 kV | 342_South Mackay 33 kV | PV 6/4_Glenella No 2 66 kV | 423_North Mackay No 2 33 kV
MK-Mackay Area | 364_West Mackay No 1 33 kV | % of Rated A | 49.96% | 32.36% | 22.02% | 49.41% | 31.99% | 21.78% | 49.4% | 31.98% | 21.78% | 49.41% | 31.99% | 21.78% | 49.96% | 32.37% | 22.02%
MK-Mackay Area | 364_West Mackay No 1 33 kV | Limiting Line Name | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1
MK-Mackay Area | 364_West Mackay No 1 33 kV | Loading (A) | 144.8776 | 132.9852 | 90.2785 | 143.2858 | 131.48 | 89.2874 | 143.2509 | 131.453 | 89.2776 | 143.2766 | 131.4834 | 89.2838 | 144.8938 | 133.0335 | 90.2803
MK-Mackay Area | 364_West Mackay No 1 33 kV | Loading (MVA) | 8.5711 | 7.8657 | 5.3363 | 8.4815 | 7.7808 | 5.2791 | 8.4814 | 7.7808 | 5.279 | 8.4815 | 7.7808 | 5.2791 | 8.5711 | 7.8658 | 5.3363
MK-Mackay Area | 364_West Mackay No 1 33 kV | Loading (MW) | 8.385 | 7.7001 | 5.2409 | 8.2961 | 7.6179 | 5.1851 | 8.2961 | 7.6179 | 5.1851 | 8.2961 | 7.6179 | 5.1851 | 8.385 | 7.7001 | 5.2409
MK-Mackay Area | 364_West Mackay No 1 33 kV | Power Factor | 0.97829 | 0.97894 | 0.98212 | 0.97814 | 0.97907 | 0.9822 | 0.97815 | 0.97907 | 0.9822 | 0.97815 | 0.97906 | 0.9822 | 0.97829 | 0.97894 | 0.98212
MK-Mackay Area | 364_West Mackay No 1 33 kV | Rating (A) | 290 | 411 | 410 | 290 | 411 | 410 | 290 | 411 | 410 | 290 | 411 | 410 | 290 | 411 | 410
MK-Mackay Area | 364_West Mackay No 1 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
MK-Mackay Area | 364_West Mackay No 1 33 kV | Min Voltage at Constrained Conductor | 34.1549 | 34.1473 | 34.126 | 34.1735 | 34.1655 | 34.1346 | 34.1816 | 34.1723 | 34.1383 | 34.1756 | 34.1646 | 34.1359 | 34.1512 | 34.1353 | 34.1254
MK-Mackay Area | 364_West Mackay No 1 33 kV | Contingency Outage | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV | 342_South Mackay 33 kV
MK-Mackay Area | 365_Tennyson St No 1 33 kV | % of Rated A | 12.16% | 10.91% | 7.151% | 12.02% | 10.79% | 7.077% | 11.9% | 10.68% | 7.005% | 11.9% | 10.68% | 7.006% | 12% | 10.76% | 7.053%
MK-Mackay Area | 365_Tennyson St No 1 33 kV | Limiting Line Name | TR_CABLE 30_1 | TR_CABLE 30_1 | TR_CABLE 30_1 | TR_CABLE 30_1 | TR_CABLE 30_1 | TR_CABLE 30_1 | TR_CABLE 30_1 | TR_CABLE 30_1 | TR_CABLE 30_1 | TR_CABLE 30_1 | TR_CABLE 30_1 | TR_CABLE 30_1 | TR_CABLE 30_1 | TR_CABLE 30_1 | TR_CABLE 30_1
MK-Mackay Area | 365_Tennyson St No 1 33 kV | Loading (A) | 80.8495 | 72.5335 | 47.5518 | 79.9511 | 71.7699 | 47.0635 | 79.1429 | 71.0275 | 46.5846 | 79.1605 | 71.0483 | 46.589 | 79.7706 | 71.5726 | 46.9039
MK-Mackay Area | 365_Tennyson St No 1 33 kV | Loading (MVA) | 4.7864 | 4.3019 | 2.8239 | 4.7379 | 4.2591 | 2.7959 | 4.6907 | 4.2163 | 2.7679 | 4.6908 | 4.2163 | 2.768 | 4.7229 | 4.2439 | 2.7856
MK-Mackay Area | 365_Tennyson St No 1 33 kV | Loading (MW) | 4.0337 | 3.4484 | 2.307 | 3.7654 | 3.4161 | 2.2853 | 3.9649 | 3.3837 | 2.2637 | 3.9648 | 3.3837 | 2.2636 | 3.9881 | 3.4052 | 2.2779
MK-Mackay Area | 365_Tennyson St No 1 33 kV | Power Factor | 0.84272 | 0.80156 | 0.81691 | 0.79472 | 0.80204 | 0.81734 | 0.84524 | 0.80251 | 0.81776 | 0.84519 | 0.80248 | 0.81776 | 0.84439 | 0.80233 | 0.81771
MK-Mackay Area | 365_Tennyson St No 1 33 kV | Rating (A) | 665 | 665 | 665 | 665 | 665 | 665 | 665 | 665 | 665 | 665 | 665 | 665 | 665 | 665 | 665
MK-Mackay Area | 365_Tennyson St No 1 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
MK-Mackay Area | 365_Tennyson St No 1 33 kV | Min Voltage at Constrained Conductor | 34.1798 | 34.2424 | 34.286 | 34.2135 | 34.2619 | 34.2986 | 34.2189 | 34.2722 | 34.3048 | 34.2117 | 34.2625 | 34.3016 | 34.1829 | 34.2339 | 34.2887
MK-Mackay Area | 365_Tennyson St No 1 33 kV | Contingency Outage | 341_Tennyson St No 2 33 kV | 395_Tennyson Street-Alfred Street 33 kV | 395_Tennyson Street-Alfred Street 33 kV | 395_Tennyson Street-Alfred Street 33 kV | 395_Tennyson Street-Alfred Street 33 kV | 395_Tennyson Street-Alfred Street 33 kV | 341_Tennyson St No 2 33 kV | 395_Tennyson Street-Alfred Street 33 kV | 395_Tennyson Street-Alfred Street 33 kV | 341_Tennyson St No 2 33 kV | 395_Tennyson Street-Alfred Street 33 kV | 395_Tennyson Street-Alfred Street 33 kV | 341_Tennyson St No 2 33 kV | 395_Tennyson Street-Alfred Street 33 kV | 395_Tennyson Street-Alfred Street 33 kV
MK-Mackay Area | 367_Pioneer Valley - Greenmount 66 kV | % of Rated A | 0.06441% | 0.0471% | 0.04698% | 0.06443% | 0.04714% | 0.04699% | 0.06444% | 0.04714% | 0.04699% | 0.06442% | 0.04713% | 0.04699% | 0.06465% | 0.04709% | 0.04697%
MK-Mackay Area | 367_Pioneer Valley - Greenmount 66 kV | Limiting Line Name | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1
MK-Mackay Area | 367_Pioneer Valley - Greenmount 66 kV | Loading (A) | 0.16231 | 0.16438 | 0.1635 | 0.16238 | 0.16452 | 0.16353 | 0.1624 | 0.16453 | 0.16354 | 0.16234 | 0.16449 | 0.16351 | 0.16292 | 0.16435 | 0.16346
MK-Mackay Area | 367_Pioneer Valley - Greenmount 66 kV | Loading (MVA) | 0.019429 | 0.019929 | 0.019715 | 0.019445 | 0.019962 | 0.019722 | 0.01945 | 0.019965 | 0.019725 | 0.019436 | 0.019954 | 0.019719 | 0.019576 | 0.01992 | 0.019706
MK-Mackay Area | 367_Pioneer Valley - Greenmount 66 kV | Loading (MW) | 7.9012e-08 | 8.1115e-08 | 8.0252e-08 | 7.9165e-08 | 8.1263e-08 | 8.0304e-08 | 7.9246e-08 | 8.1331e-08 | 8.0263e-08 | 7.9208e-08 | 8.1229e-08 | 8.0304e-08 | 7.9699e-08 | 8.1041e-08 | 8.0242e-08
MK-Mackay Area | 367_Pioneer Valley - Greenmount 66 kV | Power Factor | 4.0666e-06 | 4.0702e-06 | 4.0705e-06 | 4.0712e-06 | 4.0709e-06 | 4.0718e-06 | 4.0743e-06 | 4.0736e-06 | 4.0691e-06 | 4.0754e-06 | 4.0708e-06 | 4.0724e-06 | 4.0712e-06 | 4.0683e-06 | 4.0719e-06
MK-Mackay Area | 367_Pioneer Valley - Greenmount 66 kV | Rating (A) | 252 | 349 | 348 | 252 | 349 | 348 | 252 | 349 | 348 | 252 | 349 | 348 | 252 | 349 | 348
MK-Mackay Area | 367_Pioneer Valley - Greenmount 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
MK-Mackay Area | 367_Pioneer Valley - Greenmount 66 kV | Min Voltage at Constrained Conductor | 69.1124 | 69.9949 | 69.6191 | 69.1404 | 70.0534 | 69.6313 | 69.1491 | 70.0591 | 69.6356 | 69.1237 | 70.0395 | 69.6257 | 69.373 | 69.9793 | 69.603
MK-Mackay Area | 367_Pioneer Valley - Greenmount 66 kV | Contingency Outage | PV 6/5_Glenella No 1 66 kV | 422_North Mackay No 1 33 kV | PV 6/5_Glenella No 1 66 kV | PV 6/5_Glenella No 1 66 kV | PV 6/4_Glenella No 2 66 kV | PV 6/5_Glenella No 1 66 kV | PV 6/5_Glenella No 1 66 kV | PV 6/4_Glenella No 2 66 kV | PV 6/5_Glenella No 1 66 kV | PV 6/5_Glenella No 1 66 kV | PV 6/4_Glenella No 2 66 kV | PV 6/5_Glenella No 1 66 kV | PV 6/4_Glenella No 2 66 kV | 422_North Mackay No 1 33 kV | PV 6/5_Glenella No 1 66 kV
MK-Mackay Area | 372_Pioneer Valley-McKinley Creek 33 kV | % of Rated A | 13.17% | 10.71% | 4.492% | 13.16% | 10.81% | 4.491% | 13.16% | 10.81% | 4.491% | 13.16% | 10.82% | 4.492% | 13.52% | 11.03% | 4.618%
MK-Mackay Area | 372_Pioneer Valley-McKinley Creek 33 kV | Limiting Line Name | TR_LINE 12781_1 | TR_LINE 12781_1 | TR_LINE 12781_1 | TR_LINE 12781_1 | TR_LINE 12781_1 | TR_LINE 12781_1 | TR_LINE 12781_1 | TR_LINE 12781_1 | TR_LINE 12781_1 | TR_LINE 12781_1 | TR_LINE 12781_1 | TR_LINE 12781_1 | TR_LINE 12781_1 | TR_LINE 12781_1 | TR_LINE 12781_1
MK-Mackay Area | 372_Pioneer Valley-McKinley Creek 33 kV | Loading (A) | 25.6752 | 29.7825 | 12.1287 | 25.6642 | 30.0606 | 12.1267 | 25.6609 | 30.0576 | 12.1259 | 25.6716 | 30.0726 | 12.1275 | 26.3586 | 30.6562 | 12.4694
MK-Mackay Area | 372_Pioneer Valley-McKinley Creek 33 kV | Loading (MVA) | 3.0362 | 3.5498 | 1.4488 | 3.0361 | 3.5497 | 1.4488 | 3.0361 | 3.5497 | 1.4488 | 3.0362 | 3.5497 | 1.4488 | 3.1209 | 3.6491 | 1.4891
MK-Mackay Area | 372_Pioneer Valley-McKinley Creek 33 kV | Loading (MW) | 2.9921 | 3.4962 | 1.4306 | 2.9921 | 3.4962 | 1.4306 | 2.9921 | 3.4962 | 1.4306 | 2.9921 | 3.4962 | 1.4306 | 3.0753 | 3.5935 | 1.4703
MK-Mackay Area | 372_Pioneer Valley-McKinley Creek 33 kV | Power Factor | 0.98547 | 0.98489 | 0.98742 | 0.98547 | 0.98491 | 0.98742 | 0.98547 | 0.98491 | 0.98742 | 0.98547 | 0.98491 | 0.98742 | 0.98537 | 0.98475 | 0.98737
MK-Mackay Area | 372_Pioneer Valley-McKinley Creek 33 kV | Rating (A) | 195 | 278 | 270 | 195 | 278 | 270 | 195 | 278 | 270 | 195 | 278 | 270 | 195 | 278 | 270
MK-Mackay Area | 372_Pioneer Valley-McKinley Creek 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
MK-Mackay Area | 372_Pioneer Valley-McKinley Creek 33 kV | Min Voltage at Constrained Conductor | 68.273 | 68.8157 | 68.9652 | 68.3021 | 68.1769 | 68.9762 | 68.3108 | 68.1834 | 68.9806 | 68.2827 | 68.15 | 68.9719 | 68.359 | 68.7238 | 68.9484
MK-Mackay Area | 372_Pioneer Valley-McKinley Creek 33 kV | Contingency Outage | PV 6/4_Glenella No 2 66 kV | PV 6/4_Glenella No 2 66 kV | 423_North Mackay No 2 33 kV | PV 6/4_Glenella No 2 66 kV | 343_Pleystowe 33 kV | 423_North Mackay No 2 33 kV | PV 6/4_Glenella No 2 66 kV | 343_Pleystowe 33 kV | 423_North Mackay No 2 33 kV | PV 6/4_Glenella No 2 66 kV | 343_Pleystowe 33 kV | 423_North Mackay No 2 33 kV | 342_South Mackay 33 kV | PV 6/4_Glenella No 2 66 kV | 423_North Mackay No 2 33 kV
MK-Mackay Area | 387_Mackay-Alfred Street 1 33 kV | % of Rated A | 97.36% | 87.39% | 55.38% | 96.13% | 86.33% | 54.83% | 95.44% | 85.73% | 54.5% | 95.45% | 85.75% | 54.51% | 96.26% | 86.49% | 54.88%
MK-Mackay Area | 387_Mackay-Alfred Street 1 33 kV | Limiting Line Name | TR_CABLE 2967_1 | TR_CABLE 2967_1 | TR_CABLE 2967_1 | TR_CABLE 2967_1 | TR_CABLE 2967_1 | TR_CABLE 2967_1 | TR_CABLE 2967_1 | TR_CABLE 2967_1 | TR_CABLE 2967_1 | TR_CABLE 2967_1 | TR_CABLE 2967_1 | TR_CABLE 2967_1 | TR_CABLE 2967_1 | TR_CABLE 2967_1 | TR_CABLE 2967_1
MK-Mackay Area | 387_Mackay-Alfred Street 1 33 kV | Loading (A) | 419.6314 | 376.6563 | 238.6882 | 414.3163 | 372.0839 | 236.3082 | 411.3286 | 369.5019 | 234.9077 | 411.4107 | 369.5997 | 234.9216 | 414.8735 | 372.7789 | 236.5119
MK-Mackay Area | 387_Mackay-Alfred Street 1 33 kV | Loading (MVA) | 24.9581 | 22.4264 | 14.2091 | 24.6594 | 22.1658 | 14.0722 | 24.4892 | 22.0176 | 13.9909 | 24.4892 | 22.0172 | 13.9904 | 24.6755 | 22.1888 | 14.0801
MK-Mackay Area | 387_Mackay-Alfred Street 1 33 kV | Loading (MW) | 24.9191 | 22.3112 | 13.4058 | 24.6134 | 22.0395 | 13.2442 | 24.4392 | 21.8851 | 13.1484 | 24.4394 | 21.8853 | 13.1484 | 24.6306 | 22.065 | 13.2544
MK-Mackay Area | 387_Mackay-Alfred Street 1 33 kV | Power Factor | 0.99844 | 0.99486 | 0.94346 | 0.99814 | 0.9943 | 0.94116 | 0.99796 | 0.99398 | 0.93978 | 0.99797 | 0.99401 | 0.93982 | 0.99818 | 0.99442 | 0.94136
MK-Mackay Area | 387_Mackay-Alfred Street 1 33 kV | Rating (A) | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431 | 431
MK-Mackay Area | 387_Mackay-Alfred Street 1 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
MK-Mackay Area | 387_Mackay-Alfred Street 1 33 kV | Min Voltage at Constrained Conductor | 34.2307 | 34.2835 | 34.3276 | 34.2569 | 34.3032 | 34.3401 | 34.2687 | 34.3128 | 34.3459 | 34.2618 | 34.3032 | 34.3427 | 34.233 | 34.2745 | 34.3298
MK-Mackay Area | 387_Mackay-Alfred Street 1 33 kV | Contingency Outage | 430_Mackay-Alfred Street 2 33 kV | 430_Mackay-Alfred Street 2 33 kV | 430_Mackay-Alfred Street 2 33 kV | 430_Mackay-Alfred Street 2 33 kV | 430_Mackay-Alfred Street 2 33 kV | 430_Mackay-Alfred Street 2 33 kV | 430_Mackay-Alfred Street 2 33 kV | 430_Mackay-Alfred Street 2 33 kV | 430_Mackay-Alfred Street 2 33 kV | 430_Mackay-Alfred Street 2 33 kV | 430_Mackay-Alfred Street 2 33 kV | 430_Mackay-Alfred Street 2 33 kV | 430_Mackay-Alfred Street 2 33 kV | 430_Mackay-Alfred Street 2 33 kV | 430_Mackay-Alfred Street 2 33 kV
MK-Mackay Area | 395_Tennyson Street-Alfred Street 33 kV | % of Rated A | 47.59% | 42.67% | 28.13% | 47.08% | 42.23% | 27.84% | 46.55% | 41.77% | 27.54% | 46.56% | 41.78% | 27.54% | 46.85% | 42.08% | 27.73%
MK-Mackay Area | 395_Tennyson Street-Alfred Street 33 kV | Limiting Line Name | TR_CABLE 2960_1 | TR_CABLE 2960_1 | TR_CABLE 2960_1 | TR_CABLE 2960_1 | TR_CABLE 2960_1 | TR_CABLE 2960_1 | TR_CABLE 2960_1 | TR_CABLE 2960_1 | TR_CABLE 2960_1 | TR_CABLE 2960_1 | TR_CABLE 2960_1 | TR_CABLE 2960_1 | TR_CABLE 2960_1 | TR_CABLE 2960_1 | TR_CABLE 2960_1
MK-Mackay Area | 395_Tennyson Street-Alfred Street 33 kV | Loading (A) | 319.817 | 286.7322 | 189.0018 | 316.3739 | 283.761 | 187.0767 | 312.831 | 280.663 | 185.067 | 312.901 | 280.7475 | 185.0852 | 314.8524 | 282.7811 | 186.3163
MK-Mackay Area | 395_Tennyson Street-Alfred Street 33 kV | Loading (MVA) | 18.9335 | 17.0029 | 11.2249 | 18.7442 | 16.8365 | 11.1146 | 18.5412 | 16.6576 | 10.9972 | 18.5414 | 16.6579 | 10.9973 | 18.6413 | 16.7646 | 11.0662
MK-Mackay Area | 395_Tennyson Street-Alfred Street 33 kV | Loading (MW) | 18.5806 | 16.7028 | 10.9927 | 18.3946 | 16.5389 | 10.8837 | 18.1967 | 16.3641 | 10.7685 | 18.1969 | 16.3644 | 10.7686 | 18.297 | 16.4707 | 10.8378
MK-Mackay Area | 395_Tennyson Street-Alfred Street 33 kV | Power Factor | 0.9795 | 0.98061 | 0.97786 | 0.9795 | 0.98059 | 0.97778 | 0.97959 | 0.98066 | 0.97776 | 0.97959 | 0.98066 | 0.97776 | 0.97969 | 0.98075 | 0.97791
MK-Mackay Area | 395_Tennyson Street-Alfred Street 33 kV | Rating (A) | 672 | 672 | 672 | 672 | 672 | 672 | 672 | 672 | 672 | 672 | 672 | 672 | 672 | 672 | 672
MK-Mackay Area | 395_Tennyson Street-Alfred Street 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
MK-Mackay Area | 395_Tennyson Street-Alfred Street 33 kV | Min Voltage at Constrained Conductor | 34.1798 | 34.2363 | 34.289 | 34.2064 | 34.2562 | 34.3017 | 34.2189 | 34.2663 | 34.3078 | 34.2117 | 34.2566 | 34.3046 | 34.1829 | 34.2281 | 34.2916
MK-Mackay Area | 395_Tennyson Street-Alfred Street 33 kV | Contingency Outage | 341_Tennyson St No 2 33 kV | 341_Tennyson St No 2 33 kV | 341_Tennyson St No 2 33 kV | 341_Tennyson St No 2 33 kV | 341_Tennyson St No 2 33 kV | 341_Tennyson St No 2 33 kV | 341_Tennyson St No 2 33 kV | 341_Tennyson St No 2 33 kV | 341_Tennyson St No 2 33 kV | 341_Tennyson St No 2 33 kV | 341_Tennyson St No 2 33 kV | 341_Tennyson St No 2 33 kV | 341_Tennyson St No 2 33 kV | 341_Tennyson St No 2 33 kV | 341_Tennyson St No 2 33 kV
MK-Mackay Area | 422_North Mackay No 1 33 kV | % of Rated A | 67.69% | 77.99% | 37.25% | 67.64% | 78.03% | 37.24% | 68.03% | 78.48% | 37.45% | 69.21% | 79.61% | 38.09% | 70.74% | 81.46% | 38.81%
MK-Mackay Area | 422_North Mackay No 1 33 kV | Limiting Line Name | TR_LINE 11650_2 | TR_LINE 11650_2 | TR_LINE 11650_2 | TR_LINE 11650_2 | TR_LINE 11650_2 | TR_LINE 11650_2 | TR_LINE 11650_2 | TR_LINE 11650_2 | TR_LINE 11650_2 | TR_LINE 11650_2 | TR_LINE 11650_2 | TR_LINE 11650_2 | TR_LINE 11650_2 | TR_LINE 11650_2 | TR_LINE 11650_2
MK-Mackay Area | 422_North Mackay No 1 33 kV | Loading (A) | 248.4053 | 319.7662 | 149.0068 | 248.252 | 319.9219 | 148.9595 | 249.6582 | 321.7566 | 149.7875 | 253.9847 | 326.4206 | 152.3461 | 259.6062 | 333.9749 | 155.2238
MK-Mackay Area | 422_North Mackay No 1 33 kV | Loading (MVA) | 14.3772 | 18.3304 | 8.7297 | 14.3771 | 18.3307 | 8.7297 | 14.4559 | 18.4316 | 8.7773 | 14.6896 | 18.7333 | 8.9204 | 15.0051 | 19.1377 | 9.1109
MK-Mackay Area | 422_North Mackay No 1 33 kV | Loading (MW) | 14.283 | 18.1798 | 8.6909 | 14.283 | 18.1798 | 8.6908 | 14.3608 | 18.279 | 8.7382 | 14.5935 | 18.5763 | 8.8801 | 14.9049 | 18.9732 | 9.0693
MK-Mackay Area | 422_North Mackay No 1 33 kV | Power Factor | 0.99345 | 0.99178 | 0.99555 | 0.99346 | 0.99177 | 0.99555 | 0.99342 | 0.99172 | 0.99554 | 0.99346 | 0.99162 | 0.99548 | 0.99332 | 0.9914 | 0.99543
MK-Mackay Area | 422_North Mackay No 1 33 kV | Rating (A) | 367 | 410 | 400 | 367 | 410 | 400 | 367 | 410 | 400 | 367 | 410 | 400 | 367 | 410 | 400
MK-Mackay Area | 422_North Mackay No 1 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
MK-Mackay Area | 422_North Mackay No 1 33 kV | Min Voltage at Constrained Conductor | 33.4112 | 33.0901 | 33.8218 | 33.4315 | 33.0744 | 33.8325 | 33.4255 | 33.0668 | 33.8292 | 33.3871 | 33.1279 | 33.8031 | 33.3656 | 33.0773 | 33.8849
MK-Mackay Area | 422_North Mackay No 1 33 kV | Contingency Outage | 349_Pioneer Valley - Pinnacle 66 kV | 372_Pioneer Valley-McKinley Creek 33 kV | PV 6/4_Glenella No 2 66 kV | 349_Pioneer Valley - Pinnacle 66 kV | 372_Pioneer Valley-McKinley Creek 33 kV | PV 6/4_Glenella No 2 66 kV | 349_Pioneer Valley - Pinnacle 66 kV | 348_Farleigh 33 kV | PV 6/4_Glenella No 2 66 kV | 349_Pioneer Valley - Pinnacle 66 kV | 349_Pioneer Valley - Pinnacle 66 kV | PV 6/4_Glenella No 2 66 kV | PV 6/4_Glenella No 2 66 kV | PV 6/5_Glenella No 1 66 kV | 423_North Mackay No 2 33 kV
MK-Mackay Area | 423_North Mackay No 2 33 kV | % of Rated A | 29.21% | 33.49% | 19.19% | 28.99% | 33.24% | 19.09% | 28.99% | 33.24% | 19.09% | 29.1% | 33.39% | 19.14% | 29.44% | 33.77% | 19.3%
MK-Mackay Area | 423_North Mackay No 2 33 kV | Limiting Line Name | TR_CABLE 6563_1 | TR_CABLE 6563_1 | TR_CABLE 6563_1 | TR_CABLE 6563_1 | TR_CABLE 6563_1 | TR_CABLE 6563_1 | TR_CABLE 6563_1 | TR_CABLE 6563_1 | TR_CABLE 6563_1 | TR_CABLE 6563_1 | TR_CABLE 6563_1 | TR_CABLE 6563_1 | TR_CABLE 6563_1 | TR_CABLE 6563_1 | TR_CABLE 6563_1
MK-Mackay Area | 423_North Mackay No 2 33 kV | Loading (A) | 178.7644 | 204.9405 | 117.4645 | 177.4211 | 203.4525 | 116.8114 | 177.3976 | 203.4561 | 116.8106 | 178.0703 | 204.3492 | 117.1452 | 180.1657 | 206.6852 | 118.1259
MK-Mackay Area | 423_North Mackay No 2 33 kV | Loading (MVA) | 10.6717 | 12.2056 | 7.017 | 10.5961 | 12.1129 | 6.98 | 10.5966 | 12.1129 | 6.9802 | 10.6344 | 12.1571 | 6.9975 | 10.7463 | 12.2948 | 7.0533
MK-Mackay Area | 423_North Mackay No 2 33 kV | Loading (MW) | 10.1643 | 11.8411 | 5.8942 | 10.0794 | 11.7422 | 5.845 | 10.0794 | 11.7422 | 5.845 | 10.1218 | 11.7917 | 5.8696 | 10.2492 | 11.9401 | 5.9433
MK-Mackay Area | 423_North Mackay No 2 33 kV | Power Factor | 0.95245 | 0.97014 | 0.83999 | 0.95124 | 0.96939 | 0.83739 | 0.95119 | 0.9694 | 0.83738 | 0.9518 | 0.96995 | 0.83882 | 0.95374 | 0.97115 | 0.84262
MK-Mackay Area | 423_North Mackay No 2 33 kV | Rating (A) | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612 | 612
MK-Mackay Area | 423_North Mackay No 2 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
MK-Mackay Area | 423_North Mackay No 2 33 kV | Min Voltage at Constrained Conductor | 34.4659 | 34.3847 | 34.4891 | 34.4807 | 34.3732 | 34.4993 | 34.487 | 34.3724 | 34.5001 | 34.4791 | 34.3471 | 34.4869 | 34.4368 | 34.3436 | 34.4737
MK-Mackay Area | 423_North Mackay No 2 33 kV | Contingency Outage | 422_North Mackay No 1 33 kV | 349_Pioneer Valley - Pinnacle 66 kV | PV 6/4_Glenella No 2 66 kV | 422_North Mackay No 1 33 kV | 349_Pioneer Valley - Pinnacle 66 kV | PV 6/4_Glenella No 2 66 kV | 422_North Mackay No 1 33 kV | 349_Pioneer Valley - Pinnacle 66 kV | PV 6/4_Glenella No 2 66 kV | 422_North Mackay No 1 33 kV | 349_Pioneer Valley - Pinnacle 66 kV | PV 6/4_Glenella No 2 66 kV | 342_South Mackay 33 kV | PV 6/5_Glenella No 1 66 kV | PV 6/4_Glenella No 2 66 kV
MK-Mackay Area | 430_Mackay-Alfred Street 2 33 kV | % of Rated A | 71.77% | 64.42% | 40.83% | 70.86% | 63.64% | 40.43% | 70.35% | 63.19% | 40.19% | 70.36% | 63.21% | 40.19% | 70.95% | 63.75% | 40.46%
MK-Mackay Area | 430_Mackay-Alfred Street 2 33 kV | Limiting Line Name | TR_CABLE 8887_1 | TR_CABLE 8887_1 | TR_CABLE 8887_1 | TR_CABLE 8887_1 | TR_CABLE 8887_1 | TR_CABLE 8887_1 | TR_CABLE 8887_1 | TR_CABLE 8887_1 | TR_CABLE 8887_1 | TR_CABLE 8887_1 | TR_CABLE 8887_1 | TR_CABLE 8887_1 | TR_CABLE 8887_1 | TR_CABLE 8887_1 | TR_CABLE 8887_1
MK-Mackay Area | 430_Mackay-Alfred Street 2 33 kV | Loading (A) | 415.5198 | 372.9754 | 236.417 | 410.2579 | 368.449 | 234.062 | 407.3 | 365.893 | 232.6763 | 407.3813 | 365.9898 | 232.69 | 410.8095 | 369.1369 | 234.2635
MK-Mackay Area | 430_Mackay-Alfred Street 2 33 kV | Loading (MVA) | 24.7138 | 22.2075 | 14.0741 | 24.4181 | 21.9495 | 13.9386 | 24.2497 | 21.8028 | 13.8582 | 24.2496 | 21.8024 | 13.8577 | 24.4341 | 21.9723 | 13.9465
MK-Mackay Area | 430_Mackay-Alfred Street 2 33 kV | Loading (MW) | 24.6738 | 22.0909 | 13.2716 | 24.371 | 21.8218 | 13.1115 | 24.1985 | 21.6689 | 13.0167 | 24.1987 | 21.6691 | 13.0167 | 24.388 | 21.847 | 13.1217
MK-Mackay Area | 430_Mackay-Alfred Street 2 33 kV | Power Factor | 0.99838 | 0.99475 | 0.94298 | 0.99807 | 0.99418 | 0.94066 | 0.99789 | 0.99386 | 0.93927 | 0.9979 | 0.99388 | 0.93931 | 0.99812 | 0.9943 | 0.94086
MK-Mackay Area | 430_Mackay-Alfred Street 2 33 kV | Rating (A) | 579 | 579 | 579 | 579 | 579 | 579 | 579 | 579 | 579 | 579 | 579 | 579 | 579 | 579 | 579
MK-Mackay Area | 430_Mackay-Alfred Street 2 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
MK-Mackay Area | 430_Mackay-Alfred Street 2 33 kV | Min Voltage at Constrained Conductor | 34.3312 | 34.3697 | 34.3672 | 34.3557 | 34.3878 | 34.3788 | 34.3665 | 34.3966 | 34.3841 | 34.3596 | 34.387 | 34.3809 | 34.3319 | 34.3594 | 34.3686
MK-Mackay Area | 430_Mackay-Alfred Street 2 33 kV | Contingency Outage | 387_Mackay-Alfred Street 1 33 kV | 387_Mackay-Alfred Street 1 33 kV | 387_Mackay-Alfred Street 1 33 kV | 387_Mackay-Alfred Street 1 33 kV | 387_Mackay-Alfred Street 1 33 kV | 387_Mackay-Alfred Street 1 33 kV | 387_Mackay-Alfred Street 1 33 kV | 387_Mackay-Alfred Street 1 33 kV | 387_Mackay-Alfred Street 1 33 kV | 387_Mackay-Alfred Street 1 33 kV | 387_Mackay-Alfred Street 1 33 kV | 387_Mackay-Alfred Street 1 33 kV | 387_Mackay-Alfred Street 1 33 kV | 387_Mackay-Alfred Street 1 33 kV | 387_Mackay-Alfred Street 1 33 kV
MK-Mackay Area | PV 6/4_Glenella No 2 66 kV | % of Rated A | 50% | 53.2% | 25.46% | 49.79% | 53.73% | 25.37% | 49.88% | 53.84% | 25.41% | 50.36% | 54.41% | 25.62% | 51.24% | 54.66% | 26%
MK-Mackay Area | PV 6/4_Glenella No 2 66 kV | Limiting Line Name | TR_LINE 105595_3 | TR_LINE 105543_1 | TR_LINE 105536_1 | TR_LINE 105595_1 | TR_LINE 105543_1 | TR_LINE 105536_1 | TR_LINE 105595_2 | TR_LINE 105543_1 | TR_LINE 105536_1 | TR_LINE 105595_5 | TR_LINE 105543_1 | TR_LINE 105536_1 | TR_LINE 105598_2 | TR_LINE 105543_1 | TR_LINE 105536_1
MK-Mackay Area | PV 6/4_Glenella No 2 66 kV | Loading (A) | 404.5189 | 483.0767 | 226.8282 | 402.827 | 487.904 | 226.0142 | 403.5009 | 488.8695 | 226.3822 | 407.3824 | 494.0638 | 228.266 | 414.5222 | 496.2756 | 231.6836
MK-Mackay Area | PV 6/4_Glenella No 2 66 kV | Loading (MVA) | 47.8512 | 56.607 | 27.3518 | 47.7062 | 56.4094 | 27.2584 | 47.7742 | 56.5175 | 27.3045 | 48.1582 | 57.0453 | 27.5278 | 48.8452 | 57.981 | 27.9309
MK-Mackay Area | PV 6/4_Glenella No 2 66 kV | Loading (MW) | 47.8512 | 56.584 | 26.8506 | 47.7061 | 56.3863 | 26.7497 | 47.7742 | 56.4931 | 26.7995 | 48.1582 | 57.0137 | 27.0416 | 48.8451 | 57.9382 | 27.477
MK-Mackay Area | PV 6/4_Glenella No 2 66 kV | Power Factor | 1 | 0.99959 | 0.98167 | 1 | 0.99959 | 0.98133 | 1 | 0.99957 | 0.9815 | 1 | 0.99944 | 0.98233 | 1 | 0.99926 | 0.98374
MK-Mackay Area | PV 6/4_Glenella No 2 66 kV | Rating (A) | 809 | 908 | 891 | 809 | 908 | 891 | 809 | 908 | 891 | 809 | 908 | 891 | 809 | 908 | 891
MK-Mackay Area | PV 6/4_Glenella No 2 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
MK-Mackay Area | PV 6/4_Glenella No 2 66 kV | Min Voltage at Constrained Conductor | 68.282 | 67.6482 | 69.619 | 68.3525 | 66.7449 | 69.6312 | 68.3369 | 66.7407 | 69.6355 | 68.2245 | 66.6557 | 69.6255 | 68.0016 | 67.447 | 69.6028
MK-Mackay Area | PV 6/4_Glenella No 2 66 kV | Contingency Outage | PV 6/5_Glenella No 1 66 kV | PV 6/5_Glenella No 1 66 kV | PV 6/5_Glenella No 1 66 kV | PV 6/5_Glenella No 1 66 kV | PV 6/5_Glenella No 1 66 kV | PV 6/5_Glenella No 1 66 kV | PV 6/5_Glenella No 1 66 kV | PV 6/5_Glenella No 1 66 kV | PV 6/5_Glenella No 1 66 kV | PV 6/5_Glenella No 1 66 kV | PV 6/5_Glenella No 1 66 kV | PV 6/5_Glenella No 1 66 kV | PV 6/5_Glenella No 1 66 kV | PV 6/5_Glenella No 1 66 kV | PV 6/5_Glenella No 1 66 kV
MK-Mackay Area | PV 6/5_Glenella No 1 66 kV | % of Rated A | 59.47% | 60.95% | 31.39% | 59.25% | 59.88% | 31.28% | 59.33% | 59.98% | 31.33% | 59.86% | 60.48% | 31.57% | 59.94% | 62.49% | 31.98%
MK-Mackay Area | PV 6/5_Glenella No 1 66 kV | Limiting Line Name | TR_LINE 105119_4 | TR_LINE 105119_4 | TR_LINE 105107_2 | TR_LINE 105119_4 | TR_LINE 105119_4 | TR_LINE 105107_1 | TR_LINE 105119_4 | TR_LINE 105119_4 | TR_LINE 105107_2 | TR_LINE 105119_4 | TR_LINE 105119_4 | TR_LINE 105107_5 | TR_LINE 105119_4 | TR_LINE 105119_4 | TR_LINE 105107_3
MK-Mackay Area | PV 6/5_Glenella No 1 66 kV | Loading (A) | 481.1521 | 553.3913 | 279.6517 | 479.2937 | 543.6661 | 278.7449 | 480.0104 | 544.6539 | 279.1494 | 484.2476 | 549.1492 | 281.2484 | 484.9393 | 567.4088 | 284.9216
MK-Mackay Area | PV 6/5_Glenella No 1 66 kV | Loading (MVA) | 55.3755 | 63.8154 | 33.247 | 55.1967 | 63.6308 | 33.1544 | 55.282 | 63.7439 | 33.1963 | 55.7202 | 64.2366 | 33.4157 | 56.4978 | 65.2423 | 33.8561
MK-Mackay Area | PV 6/5_Glenella No 1 66 kV | Loading (MW) | 55.095 | 63.3531 | 33.247 | 54.922 | 63.1635 | 33.1544 | 55.0047 | 63.2711 | 33.1963 | 55.4278 | 63.77 | 33.4157 | 56.188 | 64.7145 | 33.8561
MK-Mackay Area | PV 6/5_Glenella No 1 66 kV | Power Factor | 0.99493 | 0.99276 | 1 | 0.99502 | 0.99266 | 1 | 0.99498 | 0.99258 | 1 | 0.99475 | 0.99274 | 1 | 0.99452 | 0.99191 | 1
MK-Mackay Area | PV 6/5_Glenella No 1 66 kV | Rating (A) | 809 | 908 | 891 | 809 | 908 | 891 | 809 | 908 | 891 | 809 | 908 | 891 | 809 | 908 | 891
MK-Mackay Area | PV 6/5_Glenella No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
MK-Mackay Area | PV 6/5_Glenella No 1 66 kV | Min Voltage at Constrained Conductor | 66.4126 | 66.5366 | 68.625 | 66.455 | 67.5323 | 68.6556 | 66.4583 | 67.5295 | 68.6439 | 66.3984 | 67.4942 | 68.578 | 67.2292 | 66.342 | 68.5946
MK-Mackay Area | PV 6/5_Glenella No 1 66 kV | Contingency Outage | PV 6/4_Glenella No 2 66 kV | PV 6/4_Glenella No 2 66 kV | PV 6/4_Glenella No 2 66 kV | PV 6/4_Glenella No 2 66 kV | PV 6/4_Glenella No 2 66 kV | PV 6/4_Glenella No 2 66 kV | PV 6/4_Glenella No 2 66 kV | PV 6/4_Glenella No 2 66 kV | PV 6/4_Glenella No 2 66 kV | PV 6/4_Glenella No 2 66 kV | PV 6/4_Glenella No 2 66 kV | PV 6/4_Glenella No 2 66 kV | PV 6/4_Glenella No 2 66 kV | PV 6/4_Glenella No 2 66 kV | PV 6/4_Glenella No 2 66 kV
MK-Moranbah | 6328_Broadlea - Moorvale 66 kV | % of Rated A | 12.57% | 12.91% | 11.13% | 12.57% | 12.91% | 11.13% | 12.57% | 12.91% | 11.13% | 12.57% | 12.91% | 11.13% | 12.57% | 12.91% | 11.13%
MK-Moranbah | 6328_Broadlea - Moorvale 66 kV | Limiting Line Name | TR_LINE 36093_1 | TR_LINE 36093_1 | TR_LINE 36093_1 | TR_LINE 36093_1 | TR_LINE 36093_1 | TR_LINE 36093_1 | TR_LINE 36093_1 | TR_LINE 36093_1 | TR_LINE 36093_1 | TR_LINE 36093_1 | TR_LINE 36093_1 | TR_LINE 36093_1 | TR_LINE 36093_1 | TR_LINE 36093_1 | TR_LINE 36093_1
MK-Moranbah | 6328_Broadlea - Moorvale 66 kV | Loading (A) | 48.5045 | 50.2076 | 37.6245 | 48.5045 | 50.2076 | 37.6245 | 48.5045 | 50.2076 | 37.6245 | 48.5045 | 50.2076 | 37.6245 | 48.5045 | 50.2076 | 37.6245
MK-Moranbah | 6328_Broadlea - Moorvale 66 kV | Loading (MVA) | 5.7681 | 5.9766 | 4.4762 | 5.7681 | 5.9766 | 4.4762 | 5.7681 | 5.9766 | 4.4762 | 5.7681 | 5.9766 | 4.4762 | 5.7681 | 5.9766 | 4.4762
MK-Moranbah | 6328_Broadlea - Moorvale 66 kV | Loading (MW) | 5.6461 | 5.8469 | 4.3906 | 5.6461 | 5.8469 | 4.3906 | 5.6461 | 5.8469 | 4.3906 | 5.6461 | 5.8469 | 4.3906 | 5.6461 | 5.8469 | 4.3906
MK-Moranbah | 6328_Broadlea - Moorvale 66 kV | Power Factor | 0.97884 | 0.97829 | 0.98086 | 0.97884 | 0.97829 | 0.98086 | 0.97884 | 0.97829 | 0.98086 | 0.97884 | 0.97829 | 0.98086 | 0.97884 | 0.97829 | 0.98086
MK-Moranbah | 6328_Broadlea - Moorvale 66 kV | Rating (A) | 386 | 389 | 338 | 386 | 389 | 338 | 386 | 389 | 338 | 386 | 389 | 338 | 386 | 389 | 338
MK-Moranbah | 6328_Broadlea - Moorvale 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
MK-Moranbah | 6328_Broadlea - Moorvale 66 kV | Min Voltage at Constrained Conductor | 68.6573 | 68.7262 | 68.6872 | 68.6573 | 68.7262 | 68.6872 | 68.6573 | 68.7262 | 68.6872 | 68.6573 | 68.7262 | 68.6872 | 68.6573 | 68.7262 | 68.6872
MK-Moranbah | 6328_Broadlea - Moorvale 66 kV | Contingency Outage | 6333_Hail Creek 66 kV | 6326_Millennium - Daunia 66 kV | 6333_Hail Creek 66 kV | 6333_Hail Creek 66 kV | 6326_Millennium - Daunia 66 kV | 6333_Hail Creek 66 kV | 6333_Hail Creek 66 kV | 6326_Millennium - Daunia 66 kV | 6333_Hail Creek 66 kV | 6333_Hail Creek 66 kV | 6326_Millennium - Daunia 66 kV | 6333_Hail Creek 66 kV | 6333_Hail Creek 66 kV | 6326_Millennium - Daunia 66 kV | 347_Mt Bassett 33 kV
MK-Moranbah | 6330 Broadlea - Millennium 66 kV | % of Rated A | 32.34% | 34.94% | 37.34% | 32.34% | 34.94% | 37.34% | 32.34% | 34.94% | 37.34% | 32.34% | 34.94% | 37.34% | 32.34% | 34.94% | 37.34%
MK-Moranbah | 6330 Broadlea - Millennium 66 kV | Limiting Line Name | TR_LINE 63688_1 | TR_LINE 63688_1 | TR_LINE 63688_1 | TR_LINE 63688_1 | TR_LINE 63688_1 | TR_LINE 63688_1 | TR_LINE 63688_1 | TR_LINE 63688_1 | TR_LINE 63688_1 | TR_LINE 63688_1 | TR_LINE 63688_1 | TR_LINE 63688_1 | TR_LINE 63688_1 | TR_LINE 63688_1 | TR_LINE 63688_1
MK-Moranbah | 6330 Broadlea - Millennium 66 kV | Loading (A) | 228.0177 | 256.7827 | 243.4675 | 228.0177 | 256.7827 | 243.4675 | 228.0177 | 256.7827 | 243.4675 | 228.0177 | 256.7827 | 243.4675 | 228.0177 | 256.7827 | 243.4675
MK-Moranbah | 6330 Broadlea - Millennium 66 kV | Loading (MVA) | 27.1928 | 30.6989 | 29.0223 | 27.1928 | 30.6989 | 29.0223 | 27.1928 | 30.6989 | 29.0223 | 27.1928 | 30.6989 | 29.0223 | 27.1928 | 30.6989 | 29.0223
MK-Moranbah | 6330 Broadlea - Millennium 66 kV | Loading (MW) | 25.2091 | 28.4976 | 26.859 | 25.2091 | 28.4976 | 26.859 | 25.2091 | 28.4976 | 26.859 | 25.2091 | 28.4976 | 26.859 | 25.2091 | 28.4976 | 26.859
MK-Moranbah | 6330 Broadlea - Millennium 66 kV | Power Factor | 0.92705 | 0.92829 | 0.92546 | 0.92705 | 0.92829 | 0.92546 | 0.92705 | 0.92829 | 0.92546 | 0.92705 | 0.92829 | 0.92546 | 0.92705 | 0.92829 | 0.92546
MK-Moranbah | 6330 Broadlea - Millennium 66 kV | Rating (A) | 705 | 735 | 652 | 705 | 735 | 652 | 705 | 735 | 652 | 705 | 735 | 652 | 705 | 735 | 652
MK-Moranbah | 6330 Broadlea - Millennium 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
MK-Moranbah | 6330 Broadlea - Millennium 66 kV | Min Voltage at Constrained Conductor | 68.75 | 68.9029 | 68.709 | 68.75 | 68.9029 | 68.709 | 68.75 | 68.9029 | 68.709 | 68.75 | 68.9029 | 68.709 | 68.75 | 68.9029 | 68.709
MK-Moranbah | 6330 Broadlea - Millennium 66 kV | Contingency Outage | 6333_Hail Creek 66 kV | 6329_Broadlea - Coppabella 66 kV | 6333_Hail Creek 66 kV | 6333_Hail Creek 66 kV | 6329_Broadlea - Coppabella 66 kV | 6333_Hail Creek 66 kV | 6333_Hail Creek 66 kV | 6329_Broadlea - Coppabella 66 kV | 6333_Hail Creek 66 kV | 6333_Hail Creek 66 kV | 6329_Broadlea - Coppabella 66 kV | 6333_Hail Creek 66 kV | 6333_Hail Creek 66 kV | 6329_Broadlea - Coppabella 66 kV | 347_Mt Bassett 33 kV
MK-Moranbah | 7366_Moranbah - Broadlea 132 kV | % of Rated A | 37.11% | 38.02% | 39.95% | 37.11% | 38.02% | 39.95% | 37.11% | 38.02% | 39.95% | 37.11% | 38.02% | 39.95% | 37.11% | 38.02% | 39.95%
MK-Moranbah | 7366_Moranbah - Broadlea 132 kV | Limiting Line Name | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1
MK-Moranbah | 7366_Moranbah - Broadlea 132 kV | Loading (A) | 261.6129 | 279.4129 | 260.4729 | 261.6129 | 279.4129 | 260.4729 | 261.6129 | 279.4129 | 260.4729 | 261.6129 | 279.4129 | 260.4729 | 261.6129 | 279.4129 | 260.4729
MK-Moranbah | 7366_Moranbah - Broadlea 132 kV | Loading (MVA) | 62.2741 | 66.3984 | 61.9915 | 62.2741 | 66.3984 | 61.9915 | 62.2741 | 66.3984 | 61.9915 | 62.2741 | 66.3984 | 61.9915 | 62.2741 | 66.3984 | 61.9915
MK-Moranbah | 7366_Moranbah - Broadlea 132 kV | Loading (MW) | 60.3128 | 64.1272 | 59.9172 | 60.3128 | 64.1272 | 59.9172 | 60.3128 | 64.1272 | 59.9172 | 60.3128 | 64.1272 | 59.9172 | 60.3128 | 64.1272 | 59.9172
MK-Moranbah | 7366_Moranbah - Broadlea 132 kV | Power Factor | 0.96851 | 0.96579 | 0.96654 | 0.96851 | 0.96579 | 0.96654 | 0.96851 | 0.96579 | 0.96654 | 0.96851 | 0.96579 | 0.96654 | 0.96851 | 0.96579 | 0.96654
MK-Moranbah | 7366_Moranbah - Broadlea 132 kV | Rating (A) | 705 | 735 | 652 | 705 | 735 | 652 | 705 | 735 | 652 | 705 | 735 | 652 | 705 | 735 | 652
MK-Moranbah | 7366_Moranbah - Broadlea 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
MK-Moranbah | 7366_Moranbah - Broadlea 132 kV | Min Voltage at Constrained Conductor | 137.4265 | 137.1925 | 137.4015 | 137.4265 | 137.1925 | 137.4015 | 137.4265 | 137.1925 | 137.4015 | 137.4265 | 137.1925 | 137.4015 | 137.4265 | 137.1925 | 137.4015
MK-Moranbah | 7366_Moranbah - Broadlea 132 kV | Contingency Outage | 6333_Hail Creek 66 kV | 247_Mill 11 kV | 6333_Hail Creek 66 kV | 6333_Hail Creek 66 kV | 247_Mill 11 kV | 6333_Hail Creek 66 kV | 6333_Hail Creek 66 kV | 247_Mill 11 kV | 6333_Hail Creek 66 kV | 6333_Hail Creek 66 kV | 247_Mill 11 kV | 6333_Hail Creek 66 kV | 6333_Hail Creek 66 kV | 247_Mill 11 kV | 347_Mt Bassett 33 kV
MK-Newlands | 232_Newlands-Glenden 66 kV | % of Rated A | 10.87% | 8.417% | 4.841% | 10.26% | 7.935% | 4.609% | 10.26% | 7.935% | 4.609% | 10.26% | 7.935% | 4.609% | 10.87% | 8.417% | 4.841%
MK-Newlands | 232_Newlands-Glenden 66 kV | Limiting Line Name | TR_LINE 10181_1 | TR_LINE 10187_1 | TR_LINE 10181_1 | TR_LINE 10181_1 | TR_LINE 10181_1 | TR_LINE 10181_1 | TR_LINE 10181_1 | TR_LINE 10181_1 | TR_LINE 10181_1 | TR_LINE 10181_1 | TR_LINE 10181_1 | TR_LINE 10181_1 | TR_LINE 10181_1 | TR_LINE 10187_1 | TR_LINE 10181_1
MK-Newlands | 232_Newlands-Glenden 66 kV | Loading (A) | 12.6052 | 13.4669 | 7.5514 | 11.903 | 12.6956 | 7.1898 | 11.9029 | 12.6956 | 7.1898 | 11.903 | 12.6956 | 7.1898 | 12.6052 | 13.4669 | 7.5514
MK-Newlands | 232_Newlands-Glenden 66 kV | Loading (MVA) | 1.5121 | 1.6035 | 0.89559 | 1.4281 | 1.5168 | 0.85278 | 1.4281 | 1.5168 | 0.85278 | 1.4281 | 1.5168 | 0.85278 | 1.5121 | 1.6035 | 0.89559
MK-Newlands | 232_Newlands-Glenden 66 kV | Loading (MW) | 1.5048 | 1.5965 | 0.87084 | 1.4133 | 1.5042 | 0.81795 | 1.4133 | 1.5042 | 0.81795 | 1.4133 | 1.5042 | 0.81795 | 1.5048 | 1.5965 | 0.87084
MK-Newlands | 232_Newlands-Glenden 66 kV | Power Factor | 0.99514 | 0.99562 | 0.97236 | 0.98963 | 0.99169 | 0.95916 | 0.98963 | 0.99169 | 0.95916 | 0.98963 | 0.99169 | 0.95916 | 0.99514 | 0.99562 | 0.97236
MK-Newlands | 232_Newlands-Glenden 66 kV | Rating (A) | 116 | 160 | 156 | 116 | 160 | 156 | 116 | 160 | 156 | 116 | 160 | 156 | 116 | 160 | 156
MK-Newlands | 232_Newlands-Glenden 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
MK-Newlands | 232_Newlands-Glenden 66 kV | Min Voltage at Constrained Conductor | 69.2592 | 68.7465 | 68.4738 | 69.2685 | 68.9781 | 68.4791 | 69.2685 | 68.9781 | 68.4791 | 69.2684 | 68.978 | 68.479 | 69.259 | 68.7462 | 68.4737
MK-Newlands | 232_Newlands-Glenden 66 kV | Contingency Outage | NL-WR-1_Newlands-Wirralie 1 66 kV | NL-NM-1 Newlands-Newlands Mine 1 66 kV | PV 6/4_Glenella No 2 66 kV | NL-WR-1_Newlands-Wirralie 1 66 kV | NL-NM-1 Newlands-Newlands Mine 1 66 kV | PV 6/4_Glenella No 2 66 kV | NL-WR-1_Newlands-Wirralie 1 66 kV | NL-NM-1 Newlands-Newlands Mine 1 66 kV | PV 6/4_Glenella No 2 66 kV | NL-WR-1_Newlands-Wirralie 1 66 kV | NL-NM-1 Newlands-Newlands Mine 1 66 kV | PV 6/4_Glenella No 2 66 kV | NL-WR-1_Newlands-Wirralie 1 66 kV | NL-NM-1 Newlands-Newlands Mine 1 66 kV | PV 6/4_Glenella No 2 66 kV
MK-Newlands | NL-WR-1_Newlands-Wirralie 1 66 kV | % of Rated A | 4.729% | 4.291% | 4.864% | 4.73% | 4.291% | 4.865% | 4.73% | 4.291% | 4.865% | 4.73% | 4.291% | 4.865% | 4.729% | 4.291% | 4.864%
MK-Newlands | NL-WR-1_Newlands-Wirralie 1 66 kV | Limiting Line Name | TR_LINE 180753_1 | TR_LINE 180753_1 | TR_LINE 180753_1 | TR_LINE 180753_1 | TR_LINE 180753_1 | TR_LINE 180753_1 | TR_LINE 180753_1 | TR_LINE 180753_1 | TR_LINE 180753_1 | TR_LINE 180753_1 | TR_LINE 180753_1 | TR_LINE 180753_1 | TR_LINE 180753_1 | TR_LINE 180753_1 | TR_LINE 180753_1
MK-Newlands | NL-WR-1_Newlands-Wirralie 1 66 kV | Loading (A) | 8.8911 | 8.7966 | 8.9991 | 8.8924 | 8.7968 | 8.9998 | 8.8924 | 8.7968 | 8.9998 | 8.8924 | 8.7968 | 8.9998 | 8.8911 | 8.7966 | 8.9991
MK-Newlands | NL-WR-1_Newlands-Wirralie 1 66 kV | Loading (MVA) | 1.0779 | 1.0676 | 1.0759 | 1.0782 | 1.0676 | 1.0761 | 1.0782 | 1.0676 | 1.0761 | 1.0782 | 1.0676 | 1.0761 | 1.0779 | 1.0676 | 1.0759
MK-Newlands | NL-WR-1_Newlands-Wirralie 1 66 kV | Loading (MW) | 0.30676 | 0.3548 | 0.21419 | 0.30676 | 0.3548 | 0.21419 | 0.30676 | 0.3548 | 0.21419 | 0.30676 | 0.3548 | 0.21419 | 0.30676 | 0.3548 | 0.21419
MK-Newlands | NL-WR-1_Newlands-Wirralie 1 66 kV | Power Factor | 0.28458 | 0.33234 | 0.19908 | 0.2845 | 0.33232 | 0.19905 | 0.2845 | 0.33232 | 0.19905 | 0.2845 | 0.33232 | 0.19905 | 0.28458 | 0.33234 | 0.19908
MK-Newlands | NL-WR-1_Newlands-Wirralie 1 66 kV | Rating (A) | 188 | 205 | 185 | 188 | 205 | 185 | 188 | 205 | 185 | 188 | 205 | 185 | 188 | 205 | 185
MK-Newlands | NL-WR-1_Newlands-Wirralie 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
MK-Newlands | NL-WR-1_Newlands-Wirralie 1 66 kV | Min Voltage at Constrained Conductor | 69.9971 | 70.0686 | 69.0259 | 70.0061 | 70.0701 | 69.031 | 70.0061 | 70.0701 | 69.031 | 70.006 | 70.07 | 69.0309 | 69.9969 | 70.0683 | 69.0258
MK-Newlands | NL-WR-1_Newlands-Wirralie 1 66 kV | Contingency Outage | NL-NM-1 Newlands-Newlands Mine 1 66 kV | 232_Newlands-Glenden 66 kV | NL-NM-1 Newlands-Newlands Mine 1 66 kV | NL-NM-1 Newlands-Newlands Mine 1 66 kV | 7366_Moranbah - Broadlea 132 kV | NL-NM-1 Newlands-Newlands Mine 1 66 kV | NL-NM-1 Newlands-Newlands Mine 1 66 kV | 7366_Moranbah - Broadlea 132 kV | NL-NM-1 Newlands-Newlands Mine 1 66 kV | NL-NM-1 Newlands-Newlands Mine 1 66 kV | 7366_Moranbah - Broadlea 132 kV | NL-NM-1 Newlands-Newlands Mine 1 66 kV | NL-NM-1 Newlands-Newlands Mine 1 66 kV | 232_Newlands-Glenden 66 kV | NL-NM-1 Newlands-Newlands Mine 1 66 kV
NQ-Collinsville | 2031 Collinsville-PS-Collinsville 33 kV | % of Rated A | 15.49% | 20.16% | 16.51% | 15.44% | 20.08% | 16.45% | 15.39% | 20.01% | 16.4% | 15.39% | 20.01% | 16.4% | 15.44% | 20.09% | 16.46%
NQ-Collinsville | 2031 Collinsville-PS-Collinsville 33 kV | Limiting Line Name | TR_CABLE 4177_1 | TR_CABLE 4177_1 | TR_CABLE 4177_1 | TR_CABLE 4177_1 | TR_CABLE 4177_1 | TR_CABLE 4177_1 | TR_CABLE 4177_1 | TR_CABLE 4177_1 | TR_CABLE 4177_1 | TR_CABLE 4177_1 | TR_CABLE 4177_1 | TR_CABLE 4177_1 | TR_CABLE 4177_1 | TR_CABLE 4177_1 | TR_CABLE 4177_1
NQ-Collinsville | 2031 Collinsville-PS-Collinsville 33 kV | Loading (A) | 107.3789 | 139.7409 | 114.4457 | 107.0151 | 139.1823 | 114.0287 | 106.6642 | 138.6429 | 113.628 | 106.6673 | 138.6478 | 113.6261 | 107.0324 | 139.2108 | 114.0386
NQ-Collinsville | 2031 Collinsville-PS-Collinsville 33 kV | Loading (MVA) | 6.2537 | 8.25 | 6.8005 | 6.2336 | 8.2187 | 6.7767 | 6.2134 | 8.1873 | 6.7529 | 6.2134 | 8.1873 | 6.7529 | 6.2336 | 8.2187 | 6.7767
NQ-Collinsville | 2031 Collinsville-PS-Collinsville 33 kV | Loading (MW) | 5.8841 | 7.707 | 6.377 | 5.8663 | 7.6793 | 6.356 | 5.8484 | 7.6516 | 6.3349 | 5.8484 | 7.6516 | 6.3349 | 5.8663 | 7.6793 | 6.356
NQ-Collinsville | 2031 Collinsville-PS-Collinsville 33 kV | Power Factor | 0.94062 | 0.93391 | 0.93745 | 0.9408 | 0.9341 | 0.93764 | 0.94098 | 0.93429 | 0.93782 | 0.94098 | 0.93429 | 0.93782 | 0.9408 | 0.9341 | 0.93764
NQ-Collinsville | 2031 Collinsville-PS-Collinsville 33 kV | Rating (A) | 693 | 693 | 693 | 693 | 693 | 693 | 693 | 693 | 693 | 693 | 693 | 693 | 693 | 693 | 693
NQ-Collinsville | 2031 Collinsville-PS-Collinsville 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Collinsville | 2031 Collinsville-PS-Collinsville 33 kV | Min Voltage at Constrained Conductor | 33.6248 | 34.0855 | 34.3069 | 33.6304 | 34.0923 | 34.3119 | 33.632 | 34.0945 | 34.312 | 33.631 | 34.0933 | 34.3126 | 33.6249 | 34.0854 | 34.3089
NQ-Collinsville | 2031 Collinsville-PS-Collinsville 33 kV | Contingency Outage | COLL-02 Collinsville No 2 (33 kV) | COLL-02 Collinsville No 2 (33 kV) | COLL-02 Collinsville No 2 (33 kV) | COLL-02 Collinsville No 2 (33 kV) | COLL-02 Collinsville No 2 (33 kV) | COLL-02 Collinsville No 2 (33 kV) | COLL-02 Collinsville No 2 (33 kV) | COLL-02 Collinsville No 2 (33 kV) | COLL-02 Collinsville No 2 (33 kV) | COLL-02 Collinsville No 2 (33 kV) | COLL-02 Collinsville No 2 (33 kV) | COLL-02 Collinsville No 2 (33 kV) | COLL-02 Collinsville No 2 (33 kV) | COLL-02 Collinsville No 2 (33 kV) | COLL-02 Collinsville No 2 (33 kV)
NQ-Collinsville | 3000 Collinsville No 1 33 kV | % of Rated A | 1.053e-07% | 1.414e-07% | 1.137e-07% | 1.048e-07% | 1.407e-07% | 1.132e-07% | 1.044e-07% | 1.401e-07% | 1.127e-07% | 1.044e-07% | 1.401e-07% | 1.127e-07% | 1.048e-07% | 1.408e-07% | 1.132e-07%
NQ-Collinsville | 3000 Collinsville No 1 33 kV | Limiting Line Name | Link_COLL_EB04Q02_COLLINSVILLE NO 1 | Link_COLL_EB04Q02_COLLINSVILLE NO 1 | Link_COLL_EB04Q02_COLLINSVILLE NO 1 | Link_COLL_EB04Q02_COLLINSVILLE NO 1 | Link_COLL_EB04Q02_COLLINSVILLE NO 1 | Link_COLL_EB04Q02_COLLINSVILLE NO 1 | Link_COLL_EB04Q02_COLLINSVILLE NO 1 | Link_COLL_EB04Q02_COLLINSVILLE NO 1 | Link_COLL_EB04Q02_COLLINSVILLE NO 1 | Link_COLL_EB04Q02_COLLINSVILLE NO 1 | Link_COLL_EB04Q02_COLLINSVILLE NO 1 | Link_COLL_EB04Q02_COLLINSVILLE NO 1 | Link_COLL_EB04Q02_COLLINSVILLE NO 1 | Link_COLL_EB04Q02_COLLINSVILLE NO 1 | Link_COLL_EB04Q02_COLLINSVILLE NO 1
NQ-Collinsville | 3000 Collinsville No 1 33 kV | Loading (A) | 5.2628e-06 | 7.0703e-06 | 5.6839e-06 | 5.2409e-06 | 7.0366e-06 | 5.6586e-06 | 5.2196e-06 | 7.0039e-06 | 5.6343e-06 | 5.2197e-06 | 7.0042e-06 | 5.6342e-06 | 5.2418e-06 | 7.0381e-06 | 5.6592e-06
NQ-Collinsville | 3000 Collinsville No 1 33 kV | Loading (MVA) | 3.0651e-07 | 4.1742e-07 | 3.3774e-07 | 3.0528e-07 | 4.1551e-07 | 3.3629e-07 | 3.0405e-07 | 4.136e-07 | 3.3485e-07 | 3.0405e-07 | 4.1361e-07 | 3.3485e-07 | 3.0528e-07 | 4.1551e-07 | 3.3629e-07
NQ-Collinsville | 3000 Collinsville No 1 33 kV | Loading (MW) | 2.8453e-07 | 3.8485e-07 | 3.1239e-07 | 2.8345e-07 | 3.8317e-07 | 3.1111e-07 | 2.8237e-07 | 3.8149e-07 | 3.0984e-07 | 2.8237e-07 | 3.8149e-07 | 3.0984e-07 | 2.8345e-07 | 3.8317e-07 | 3.1111e-07
NQ-Collinsville | 3000 Collinsville No 1 33 kV | Power Factor | 0.92831 | 0.92198 | 0.92493 | 0.9285 | 0.92217 | 0.92512 | 0.92869 | 0.92236 | 0.92531 | 0.92869 | 0.92236 | 0.92531 | 0.9285 | 0.92217 | 0.92512
NQ-Collinsville | 3000 Collinsville No 1 33 kV | Rating (A) | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000
NQ-Collinsville | 3000 Collinsville No 1 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Collinsville | 3000 Collinsville No 1 33 kV | Min Voltage at Constrained Conductor | 33.6248 | 34.0855 | 34.3069 | 33.6304 | 34.0923 | 34.3119 | 33.632 | 34.0945 | 34.312 | 33.631 | 34.0933 | 34.3126 | 33.6249 | 34.0854 | 34.3089
NQ-Collinsville | 3000 Collinsville No 1 33 kV | Contingency Outage | COLL-02 Collinsville No 2 (33 kV) | COLL-02 Collinsville No 2 (33 kV) | COLL-02 Collinsville No 2 (33 kV) | COLL-02 Collinsville No 2 (33 kV) | COLL-02 Collinsville No 2 (33 kV) | COLL-02 Collinsville No 2 (33 kV) | COLL-02 Collinsville No 2 (33 kV) | COLL-02 Collinsville No 2 (33 kV) | COLL-02 Collinsville No 2 (33 kV) | COLL-02 Collinsville No 2 (33 kV) | COLL-02 Collinsville No 2 (33 kV) | COLL-02 Collinsville No 2 (33 kV) | COLL-02 Collinsville No 2 (33 kV) | COLL-02 Collinsville No 2 (33 kV) | COLL-02 Collinsville No 2 (33 kV)
NQ-Collinsville | 3001 Collinsville No 1 33 kV | % of Rated A | 1.283% | 1.469% | 1.289% | 1.283% | 1.469% | 1.289% | 1.283% | 1.469% | 1.289% | 1.283% | 1.469% | 1.289% | 1.283% | 1.469% | 1.289%
NQ-Collinsville | 3001 Collinsville No 1 33 kV | Limiting Line Name | Link_COLL_EB06Q02_COLLINSVILLE NO 3 | Link_COLL_EB06Q02_COLLINSVILLE NO 3 | Link_COLL_EB06Q02_COLLINSVILLE NO 3 | Link_COLL_EB06Q02_COLLINSVILLE NO 3 | Link_COLL_EB06Q02_COLLINSVILLE NO 3 | Link_COLL_EB06Q02_COLLINSVILLE NO 3 | Link_COLL_EB06Q02_COLLINSVILLE NO 3 | Link_COLL_EB06Q02_COLLINSVILLE NO 3 | Link_COLL_EB06Q02_COLLINSVILLE NO 3 | Link_COLL_EB06Q02_COLLINSVILLE NO 3 | Link_COLL_EB06Q02_COLLINSVILLE NO 3 | Link_COLL_EB06Q02_COLLINSVILLE NO 3 | Link_COLL_EB06Q02_COLLINSVILLE NO 3 | Link_COLL_EB06Q02_COLLINSVILLE NO 3 | Link_COLL_EB06Q02_COLLINSVILLE NO 3
NQ-Collinsville | 3001 Collinsville No 1 33 kV | Loading (A) | 64.1631 | 73.4579 | 64.4517 | 64.1524 | 73.4433 | 64.4423 | 64.1494 | 73.4386 | 64.442 | 64.1513 | 73.4412 | 64.4409 | 64.1628 | 73.4583 | 64.4478
NQ-Collinsville | 3001 Collinsville No 1 33 kV | Loading (MVA) | 3.7368 | 4.3368 | 3.8298 | 3.7368 | 4.3368 | 3.8298 | 3.7368 | 4.3368 | 3.8298 | 3.7368 | 4.3368 | 3.8298 | 3.7368 | 4.3368 | 3.8298
NQ-Collinsville | 3001 Collinsville No 1 33 kV | Loading (MW) | 3.6322 | 4.2154 | 3.7226 | 3.6322 | 4.2154 | 3.7226 | 3.6322 | 4.2154 | 3.7226 | 3.6322 | 4.2154 | 3.7226 | 3.6322 | 4.2154 | 3.7226
NQ-Collinsville | 3001 Collinsville No 1 33 kV | Power Factor | 0.972 | 0.972 | 0.972 | 0.972 | 0.972 | 0.972 | 0.972 | 0.972 | 0.972 | 0.972 | 0.972 | 0.972 | 0.972 | 0.972 | 0.972
NQ-Collinsville | 3001 Collinsville No 1 33 kV | Rating (A) | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000
NQ-Collinsville | 3001 Collinsville No 1 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Collinsville | 3001 Collinsville No 1 33 kV | Min Voltage at Constrained Conductor | 33.6248 | 34.0855 | 34.3069 | 33.6304 | 34.0923 | 34.3119 | 33.632 | 34.0945 | 34.312 | 33.631 | 34.0933 | 34.3126 | 33.6249 | 34.0854 | 34.3089
NQ-Collinsville | 3001 Collinsville No 1 33 kV | Contingency Outage | COLL-02 Collinsville No 2 (33 kV) | COLL-02 Collinsville No 2 (33 kV) | COLL-02 Collinsville No 2 (33 kV) | COLL-02 Collinsville No 2 (33 kV) | COLL-02 Collinsville No 2 (33 kV) | COLL-02 Collinsville No 2 (33 kV) | COLL-02 Collinsville No 2 (33 kV) | COLL-02 Collinsville No 2 (33 kV) | COLL-02 Collinsville No 2 (33 kV) | COLL-02 Collinsville No 2 (33 kV) | COLL-02 Collinsville No 2 (33 kV) | COLL-02 Collinsville No 2 (33 kV) | COLL-02 Collinsville No 2 (33 kV) | COLL-02 Collinsville No 2 (33 kV) | COLL-02 Collinsville No 2 (33 kV)
NQ-Collinsville | 3218 Collinsville No 4 33 kV | % of Rated A | 1.053e-07% | 1.414e-07% | 1.137e-07% | 1.048e-07% | 1.407e-07% | 1.132e-07% | 1.044e-07% | 1.401e-07% | 1.127e-07% | 1.044e-07% | 1.401e-07% | 1.127e-07% | 1.048e-07% | 1.408e-07% | 1.132e-07%
NQ-Collinsville | 3218 Collinsville No 4 33 kV | Limiting Line Name | Link_COLL_EB02Q02_COLLINSVILLE NO 4 | Link_COLL_EB02Q02_COLLINSVILLE NO 4 | Link_COLL_EB02Q02_COLLINSVILLE NO 4 | Link_COLL_EB02Q02_COLLINSVILLE NO 4 | Link_COLL_EB02Q02_COLLINSVILLE NO 4 | Link_COLL_EB02Q02_COLLINSVILLE NO 4 | Link_COLL_EB02Q02_COLLINSVILLE NO 4 | Link_COLL_EB02Q02_COLLINSVILLE NO 4 | Link_COLL_EB02Q02_COLLINSVILLE NO 4 | Link_COLL_EB02Q02_COLLINSVILLE NO 4 | Link_COLL_EB02Q02_COLLINSVILLE NO 4 | Link_COLL_EB02Q02_COLLINSVILLE NO 4 | Link_COLL_EB02Q02_COLLINSVILLE NO 4 | Link_COLL_EB02Q02_COLLINSVILLE NO 4 | Link_COLL_EB02Q02_COLLINSVILLE NO 4
NQ-Collinsville | 3218 Collinsville No 4 33 kV | Loading (A) | 5.2628e-06 | 7.0703e-06 | 5.6839e-06 | 5.2409e-06 | 7.0366e-06 | 5.6586e-06 | 5.2196e-06 | 7.0039e-06 | 5.6343e-06 | 5.2197e-06 | 7.0042e-06 | 5.6342e-06 | 5.2418e-06 | 7.0381e-06 | 5.6592e-06
NQ-Collinsville | 3218 Collinsville No 4 33 kV | Loading (MVA) | 3.0651e-07 | 4.1742e-07 | 3.3774e-07 | 3.0528e-07 | 4.1551e-07 | 3.3629e-07 | 3.0405e-07 | 4.136e-07 | 3.3485e-07 | 3.0405e-07 | 4.1361e-07 | 3.3485e-07 | 3.0528e-07 | 4.1551e-07 | 3.3629e-07
NQ-Collinsville | 3218 Collinsville No 4 33 kV | Loading (MW) | 2.8453e-07 | 3.8485e-07 | 3.1239e-07 | 2.8345e-07 | 3.8317e-07 | 3.1111e-07 | 2.8237e-07 | 3.8149e-07 | 3.0984e-07 | 2.8237e-07 | 3.8149e-07 | 3.0984e-07 | 2.8345e-07 | 3.8317e-07 | 3.1111e-07
NQ-Collinsville | 3218 Collinsville No 4 33 kV | Power Factor | 0.92831 | 0.92198 | 0.92493 | 0.9285 | 0.92217 | 0.92512 | 0.92869 | 0.92236 | 0.92531 | 0.92869 | 0.92236 | 0.92531 | 0.9285 | 0.92217 | 0.92512
NQ-Collinsville | 3218 Collinsville No 4 33 kV | Rating (A) | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000
NQ-Collinsville | 3218 Collinsville No 4 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Collinsville | 3218 Collinsville No 4 33 kV | Min Voltage at Constrained Conductor | 33.6248 | 34.0855 | 34.3069 | 33.6304 | 34.0923 | 34.3119 | 33.632 | 34.0945 | 34.312 | 33.631 | 34.0933 | 34.3126 | 33.6249 | 34.0854 | 34.3089
NQ-Collinsville | 3218 Collinsville No 4 33 kV | Contingency Outage | COLL-02 Collinsville No 2 (33 kV) | COLL-02 Collinsville No 2 (33 kV) | COLL-02 Collinsville No 2 (33 kV) | COLL-02 Collinsville No 2 (33 kV) | COLL-02 Collinsville No 2 (33 kV) | COLL-02 Collinsville No 2 (33 kV) | COLL-02 Collinsville No 2 (33 kV) | COLL-02 Collinsville No 2 (33 kV) | COLL-02 Collinsville No 2 (33 kV) | COLL-02 Collinsville No 2 (33 kV) | COLL-02 Collinsville No 2 (33 kV) | COLL-02 Collinsville No 2 (33 kV) | COLL-02 Collinsville No 2 (33 kV) | COLL-02 Collinsville No 2 (33 kV) | COLL-02 Collinsville No 2 (33 kV)
NQ-Collinsville | 7308_Stony Creek - Havilah 132 kV | % of Rated A | 0.9285% | 0.909% | 1.003% | 0.9285% | 0.909% | 1.003% | 0.9285% | 0.909% | 1.003% | 0.9285% | 0.909% | 1.003% | 0.9285% | 0.909% | 1.003%
NQ-Collinsville | 7308_Stony Creek - Havilah 132 kV | Limiting Line Name | TR_LINE 67629_1 | TR_LINE 67629_1 | TR_LINE 67629_1 | TR_LINE 67629_1 | TR_LINE 67629_1 | TR_LINE 67629_1 | TR_LINE 67629_1 | TR_LINE 67629_1 | TR_LINE 67629_1 | TR_LINE 67629_1 | TR_LINE 67629_1 | TR_LINE 67629_1 | TR_LINE 67629_1 | TR_LINE 67629_1 | TR_LINE 67629_1
NQ-Collinsville | 7308_Stony Creek - Havilah 132 kV | Loading (A) | 4.0576 | 4.0542 | 3.9225 | 4.0576 | 4.0542 | 3.9227 | 4.0575 | 4.0541 | 3.9225 | 4.0575 | 4.0541 | 3.9225 | 4.0575 | 4.054 | 3.9224
NQ-Collinsville | 7308_Stony Creek - Havilah 132 kV | Loading (MVA) | 0.98672 | 0.98506 | 0.95423 | 0.98672 | 0.98506 | 0.95435 | 0.98665 | 0.985 | 0.95427 | 0.98665 | 0.985 | 0.95426 | 0.98665 | 0.98498 | 0.95422
NQ-Collinsville | 7308_Stony Creek - Havilah 132 kV | Loading (MW) | 5.6503e-05 | 5.6408e-05 | 0.10316 | 5.6503e-05 | 5.6408e-05 | 0.10316 | 5.6499e-05 | 5.6405e-05 | 0.10316 | 5.6499e-05 | 5.6405e-05 | 0.10316 | 5.6499e-05 | 5.6403e-05 | 0.10316
NQ-Collinsville | 7308_Stony Creek - Havilah 132 kV | Power Factor | 2.7065e-05 | 2.7065e-05 | 0.10811 | 2.7065e-05 | 2.7065e-05 | 0.1081 | 2.7065e-05 | 2.7065e-05 | 0.10811 | 2.7065e-05 | 2.7065e-05 | 0.10811 | 2.7065e-05 | 2.7065e-05 | 0.10811
NQ-Collinsville | 7308_Stony Creek - Havilah 132 kV | Rating (A) | 437 | 446 | 391 | 437 | 446 | 391 | 437 | 446 | 391 | 437 | 446 | 391 | 437 | 446 | 391
NQ-Collinsville | 7308_Stony Creek - Havilah 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Collinsville | 7308_Stony Creek - Havilah 132 kV | Min Voltage at Constrained Conductor | 140.3988 | 140.281 | 140.4543 | 140.3984 | 140.2808 | 140.4626 | 140.3938 | 140.2767 | 140.457 | 140.3939 | 140.2766 | 140.4565 | 140.3937 | 140.2748 | 140.4533
NQ-Collinsville | 7308_Stony Creek - Havilah 132 kV | Contingency Outage | 119_Cannonvale No 1 66 kV | 119_Cannonvale No 1 66 kV | 426_Mt Rooper 66 kV | 119_Cannonvale No 1 66 kV | 119_Cannonvale No 1 66 kV | 426_Mt Rooper 66 kV | 119_Cannonvale No 1 66 kV | 119_Cannonvale No 1 66 kV | 426_Mt Rooper 66 kV | 119_Cannonvale No 1 66 kV | 119_Cannonvale No 1 66 kV | 426_Mt Rooper 66 kV | 119_Cannonvale No 1 66 kV | 119_Cannonvale No 1 66 kV | 426_Mt Rooper 66 kV
NQ-Collinsville | 7309_Stony Creek - Fig Tree 132 kV | % of Rated A | 1.179% | 1.12% | 1.243% | 1.179% | 1.12% | 1.243% | 1.179% | 1.12% | 1.243% | 1.179% | 1.12% | 1.243% | 1.179% | 1.12% | 1.243%
NQ-Collinsville | 7309_Stony Creek - Fig Tree 132 kV | Limiting Line Name | TR_LINE 67630_1 | TR_LINE 67630_1 | TR_LINE 67630_1 | TR_LINE 67630_1 | TR_LINE 67630_1 | TR_LINE 67630_1 | TR_LINE 67630_1 | TR_LINE 67630_1 | TR_LINE 67630_1 | TR_LINE 67630_1 | TR_LINE 67630_1 | TR_LINE 67630_1 | TR_LINE 67630_1 | TR_LINE 67630_1 | TR_LINE 67630_1
NQ-Collinsville | 7309_Stony Creek - Fig Tree 132 kV | Loading (A) | 5.3278 | 5.3301 | 5.3082 | 5.3278 | 5.3301 | 5.3083 | 5.3278 | 5.3301 | 5.3082 | 5.3278 | 5.3301 | 5.3082 | 5.3278 | 5.3301 | 5.3082
NQ-Collinsville | 7309_Stony Creek - Fig Tree 132 kV | Loading (MVA) | 1.2956 | 1.2951 | 1.2914 | 1.2956 | 1.2951 | 1.2914 | 1.2956 | 1.295 | 1.2914 | 1.2956 | 1.295 | 1.2914 | 1.2956 | 1.295 | 1.2913
NQ-Collinsville | 7309_Stony Creek - Fig Tree 132 kV | Loading (MW) | 0.97909 | 0.97998 | 0.97167 | 0.97909 | 0.97998 | 0.97167 | 0.97909 | 0.97998 | 0.97167 | 0.97909 | 0.97998 | 0.97167 | 0.97909 | 0.97998 | 0.97167
NQ-Collinsville | 7309_Stony Creek - Fig Tree 132 kV | Power Factor | 0.7557 | 0.7567 | 0.75245 | 0.75571 | 0.7567 | 0.7524 | 0.75573 | 0.75673 | 0.75243 | 0.75573 | 0.75673 | 0.75243 | 0.75573 | 0.75674 | 0.75245
NQ-Collinsville | 7309_Stony Creek - Fig Tree 132 kV | Rating (A) | 452 | 476 | 427 | 452 | 476 | 427 | 452 | 476 | 427 | 452 | 476 | 427 | 452 | 476 | 427
NQ-Collinsville | 7309_Stony Creek - Fig Tree 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Collinsville | 7309_Stony Creek - Fig Tree 132 kV | Min Voltage at Constrained Conductor | 140.398 | 140.2802 | 140.4536 | 140.3976 | 140.28 | 140.4619 | 140.3931 | 140.2759 | 140.4563 | 140.3931 | 140.2758 | 140.4558 | 140.3929 | 140.274 | 140.4526
NQ-Collinsville | 7309_Stony Creek - Fig Tree 132 kV | Contingency Outage | 119_Cannonvale No 1 66 kV | 119_Cannonvale No 1 66 kV | 426_Mt Rooper 66 kV | 119_Cannonvale No 1 66 kV | 119_Cannonvale No 1 66 kV | 426_Mt Rooper 66 kV | 119_Cannonvale No 1 66 kV | 119_Cannonvale No 1 66 kV | 426_Mt Rooper 66 kV | 119_Cannonvale No 1 66 kV | 119_Cannonvale No 1 66 kV | 426_Mt Rooper 66 kV | 119_Cannonvale No 1 66 kV | 119_Cannonvale No 1 66 kV | 426_Mt Rooper 66 kV
NQ-Collinsville | COLL-02 Collinsville No 2 (33 kV) | % of Rated A | 2.599% | 1.849% | 1.915% | 2.6% | 1.85% | 1.916% | 2.6% | 1.85% | 1.916% | 2.6% | 1.85% | 1.916% | 2.599% | 1.849% | 1.915%
NQ-Collinsville | COLL-02 Collinsville No 2 (33 kV) | Limiting Line Name | HV_LINE 2010332_1 | HV_LINE 2010332_1 | HV_LINE 2010332_1 | HV_LINE 2010332_1 | HV_LINE 2010332_1 | HV_LINE 2010332_1 | HV_LINE 2010332_1 | HV_LINE 2010332_1 | HV_LINE 2010332_1 | HV_LINE 2010332_1 | HV_LINE 2010332_1 | HV_LINE 2010332_1 | HV_LINE 2010332_1 | HV_LINE 2010332_1 | HV_LINE 2010332_1
NQ-Collinsville | COLL-02 Collinsville No 2 (33 kV) | Loading (A) | 5.0689 | 5.1407 | 5.1714 | 5.0696 | 5.1418 | 5.172 | 5.0699 | 5.1421 | 5.1722 | 5.0697 | 5.1419 | 5.1721 | 5.0689 | 5.1407 | 5.1717
NQ-Collinsville | COLL-02 Collinsville No 2 (33 kV) | Loading (MVA) | 0.29643 | 0.30489 | 0.30854 | 0.29651 | 0.30501 | 0.30861 | 0.29654 | 0.30505 | 0.30863 | 0.29652 | 0.30503 | 0.30862 | 0.29643 | 0.30489 | 0.30858
NQ-Collinsville | COLL-02 Collinsville No 2 (33 kV) | Loading (MW) | 0.00048834 | 0.00050228 | 0.00050829 | 0.00048848 | 0.00050248 | 0.00050841 | 0.00048852 | 0.00050254 | 0.00050844 | 0.00048849 | 0.0005025 | 0.00050843 | 0.00048834 | 0.00050227 | 0.00050835
NQ-Collinsville | COLL-02 Collinsville No 2 (33 kV) | Power Factor | 0.0015748 | 0.0015748 | 0.0015748 | 0.0015748 | 0.0015748 | 0.0015748 | 0.0015748 | 0.0015748 | 0.0015748 | 0.0015748 | 0.0015748 | 0.0015748 | 0.0015748 | 0.0015748 | 0.0015748
NQ-Collinsville | COLL-02 Collinsville No 2 (33 kV) | Rating (A) | 195 | 278 | 270 | 195 | 278 | 270 | 195 | 278 | 270 | 195 | 278 | 270 | 195 | 278 | 270
NQ-Collinsville | COLL-02 Collinsville No 2 (33 kV) | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Collinsville | COLL-02 Collinsville No 2 (33 kV) | Min Voltage at Constrained Conductor | 33.7634 | 34.2417 | 34.4461 | 33.768 | 34.2485 | 34.4501 | 33.7696 | 34.2506 | 34.4512 | 33.7686 | 34.2494 | 34.4508 | 33.7632 | 34.2415 | 34.4482
NQ-Collinsville | COLL-02 Collinsville No 2 (33 kV) | Contingency Outage | 119_Cannonvale No 1 66 kV | 3001 Collinsville No 1 33 kV | 3001 Collinsville No 1 33 kV | 3001 Collinsville No 1 33 kV | 3001 Collinsville No 1 33 kV | 3001 Collinsville No 1 33 kV | 3001 Collinsville No 1 33 kV | 3001 Collinsville No 1 33 kV | 3001 Collinsville No 1 33 kV | 3001 Collinsville No 1 33 kV | 3001 Collinsville No 1 33 kV | 3001 Collinsville No 1 33 kV | 119_Cannonvale No 1 66 kV | 3001 Collinsville No 1 33 kV | 3001 Collinsville No 1 33 kV
NQ-Ingham | 6321_Lucinda 66 kV | % of Rated A | 14.73% | 21.17% | 18.33% | 14.73% | 21.16% | 18.33% | 14.34% | 20.79% | 18.07% | 14.34% | 20.79% | 18.07% | 14.75% | 21.2% | 18.34%
NQ-Ingham | 6321_Lucinda 66 kV | Limiting Line Name | TR_LINE 90734_2 | TR_LINE 90734_2 | TR_LINE 90734_2 | TR_LINE 90734_2 | TR_LINE 90734_2 | TR_LINE 90734_2 | TR_LINE 90734_2 | TR_LINE 90734_2 | TR_LINE 90734_2 | TR_LINE 90734_2 | TR_LINE 90734_2 | TR_LINE 90734_2 | TR_LINE 90734_2 | TR_LINE 90734_2 | TR_LINE 90734_2
NQ-Ingham | 6321_Lucinda 66 kV | Loading (A) | 29.3148 | 47.2062 | 37.3873 | 29.3096 | 47.1974 | 37.3851 | 28.5314 | 46.3728 | 36.8693 | 28.5293 | 46.3693 | 36.8682 | 29.3579 | 47.2659 | 37.4213
NQ-Ingham | 6321_Lucinda 66 kV | Loading (MVA) | 3.4693 | 5.5604 | 4.3769 | 3.4692 | 5.5603 | 4.3769 | 3.3731 | 5.4566 | 4.3137 | 3.3731 | 5.4565 | 4.3136 | 3.4695 | 5.5593 | 4.3772
NQ-Ingham | 6321_Lucinda 66 kV | Loading (MW) | 3.2821 | 5.0727 | 3.9635 | 3.2821 | 5.0727 | 3.9635 | 3.1923 | 4.9768 | 3.9037 | 3.1923 | 4.9768 | 3.9037 | 3.2822 | 5.0725 | 3.9636
NQ-Ingham | 6321_Lucinda 66 kV | Power Factor | 0.94592 | 0.91206 | 0.90536 | 0.94593 | 0.91207 | 0.90536 | 0.94624 | 0.91185 | 0.90478 | 0.94624 | 0.91185 | 0.90478 | 0.94585 | 0.91221 | 0.90531
NQ-Ingham | 6321_Lucinda 66 kV | Rating (A) | 199 | 223 | 204 | 199 | 223 | 204 | 199 | 223 | 204 | 199 | 223 | 204 | 199 | 223 | 204
NQ-Ingham | 6321_Lucinda 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Ingham | 6321_Lucinda 66 kV | Min Voltage at Constrained Conductor | 68.3265 | 68.0056 | 67.5905 | 68.338 | 68.0174 | 67.5942 | 68.2574 | 67.9351 | 67.5491 | 68.2622 | 67.9399 | 67.5509 | 68.2315 | 67.9063 | 67.5336
NQ-Ingham | 6321_Lucinda 66 kV | Contingency Outage | IN-GR_Ingham-Black River/Greenvale 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV
NQ-Ingham | 6322 66kV VICTORIA SUGAR MILL FDR | % of Rated A | 1.216e-08% | 1.22e-08% | 1.208e-08% | 1.216e-08% | 1.22e-08% | 1.209e-08% | 1.214e-08% | 1.219e-08% | 1.207e-08% | 1.214e-08% | 1.219e-08% | 1.208e-08% | 1.214e-08% | 1.218e-08% | 1.207e-08%
NQ-Ingham | 6322 66kV VICTORIA SUGAR MILL FDR | Limiting Line Name | Line | Line | Line | Line | Line | Line | Line | Line | Line | Line | Line | Line | Line | Line | Line
NQ-Ingham | 6322 66kV VICTORIA SUGAR MILL FDR | Loading (A) | 6.0784e-07 | 6.0993e-07 | 6.0423e-07 | 6.0794e-07 | 6.1002e-07 | 6.0426e-07 | 6.0703e-07 | 6.0926e-07 | 6.0374e-07 | 6.0707e-07 | 6.093e-07 | 6.0375e-07 | 6.0701e-07 | 6.0923e-07 | 6.0374e-07
NQ-Ingham | 6322 66kV VICTORIA SUGAR MILL FDR | Loading (MVA) | 1.2192e-08 | 1.2276e-08 | 1.2048e-08 | 1.2196e-08 | 1.228e-08 | 1.2049e-08 | 1.216e-08 | 1.2249e-08 | 1.2028e-08 | 1.2162e-08 | 1.2251e-08 | 1.2029e-08 | 1.2159e-08 | 1.2248e-08 | 1.2028e-08
NQ-Ingham | 6322 66kV VICTORIA SUGAR MILL FDR | Loading (MW) | 1.2192e-08 | 1.2276e-08 | 1.2048e-08 | 1.2196e-08 | 1.228e-08 | 1.2049e-08 | 1.216e-08 | 1.2249e-08 | 1.2028e-08 | 1.2162e-08 | 1.2251e-08 | 1.2029e-08 | 1.2159e-08 | 1.2248e-08 | 1.2028e-08
NQ-Ingham | 6322 66kV VICTORIA SUGAR MILL FDR | Power Factor | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
NQ-Ingham | 6322 66kV VICTORIA SUGAR MILL FDR | Rating (A) | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000
NQ-Ingham | 6322 66kV VICTORIA SUGAR MILL FDR | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Ingham | 6322 66kV VICTORIA SUGAR MILL FDR | Min Voltage at Constrained Conductor | 11.5809 | 11.6207 | 11.5121 | 11.5827 | 11.6225 | 11.5127 | 11.5654 | 11.6079 | 11.5027 | 11.5662 | 11.6087 | 11.503 | 11.5651 | 11.6074 | 11.5027
NQ-Ingham | 6322 66kV VICTORIA SUGAR MILL FDR | Contingency Outage | 6321_Lucinda 66 kV | 6321_Lucinda 66 kV | 6321_Lucinda 66 kV | 6321_Lucinda 66 kV | 6321_Lucinda 66 kV | 6321_Lucinda 66 kV | 6321_Lucinda 66 kV | 6321_Lucinda 66 kV | 6321_Lucinda 66 kV | 6321_Lucinda 66 kV | 6321_Lucinda 66 kV | 6321_Lucinda 66 kV | 6321_Lucinda 66 kV | 6321_Lucinda 66 kV | 6321_Lucinda 66 kV
NQ-Ingham | IN-GR_Ingham-Black River/Greenvale 66 kV | % of Rated A | 23.01% | 18.34% | 19.12% | 23.02% | 18.35% | 19.12% | 22.99% | 18.34% | 19.11% | 22.99% | 18.34% | 19.11% | 22.99% | 18.34% | 19.11%
NQ-Ingham | IN-GR_Ingham-Black River/Greenvale 66 kV | Limiting Line Name | TR_LINE 217286_1 | TR_LINE 217286_1 | TR_LINE 217286_1 | TR_LINE 217286_1 | TR_LINE 217286_1 | TR_LINE 217286_1 | TR_LINE 217286_1 | TR_LINE 217286_1 | TR_LINE 217286_1 | TR_LINE 217286_1 | TR_LINE 217286_1 | TR_LINE 217286_1 | TR_LINE 217286_1 | TR_LINE 217286_1 | TR_LINE 217286_1
NQ-Ingham | IN-GR_Ingham-Black River/Greenvale 66 kV | Loading (A) | 15.8793 | 15.959 | 15.6784 | 15.8816 | 15.9613 | 15.6792 | 15.8601 | 15.9586 | 15.6698 | 15.861 | 15.9595 | 15.6701 | 15.8597 | 15.958 | 15.6697
NQ-Ingham | IN-GR_Ingham-Black River/Greenvale 66 kV | Loading (MVA) | 1.9188 | 1.9309 | 1.8898 | 1.9194 | 1.9314 | 1.89 | 1.9139 | 1.9307 | 1.8877 | 1.9141 | 1.931 | 1.8878 | 1.9138 | 1.9306 | 1.8877
NQ-Ingham | IN-GR_Ingham-Black River/Greenvale 66 kV | Loading (MW) | 0.65059 | 0.70218 | 0.39929 | 0.65059 | 0.70219 | 0.39929 | 0.65057 | 0.70218 | 0.39928 | 0.65057 | 0.70218 | 0.39928 | 0.65057 | 0.70218 | 0.39928
NQ-Ingham | IN-GR_Ingham-Black River/Greenvale 66 kV | Power Factor | 0.33907 | 0.36367 | 0.21128 | 0.33896 | 0.36356 | 0.21126 | 0.33992 | 0.36369 | 0.21151 | 0.33988 | 0.36364 | 0.2115 | 0.33994 | 0.36371 | 0.21151
NQ-Ingham | IN-GR_Ingham-Black River/Greenvale 66 kV | Rating (A) | 69 | 87 | 82 | 69 | 87 | 82 | 69 | 87 | 82 | 69 | 87 | 82 | 69 | 87 | 82
NQ-Ingham | IN-GR_Ingham-Black River/Greenvale 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Ingham | IN-GR_Ingham-Black River/Greenvale 66 kV | Min Voltage at Constrained Conductor | 69.7637 | 69.8524 | 69.5923 | 69.7748 | 69.8637 | 69.5958 | 69.6708 | 69.8504 | 69.5536 | 69.6754 | 69.855 | 69.5552 | 69.6687 | 69.8475 | 69.5535
NQ-Ingham | IN-GR_Ingham-Black River/Greenvale 66 kV | Contingency Outage | 6321_Lucinda 66 kV | 6321_Lucinda 66 kV | IN-VC-1_Ingham-Victoria No 1 66 kV | 6321_Lucinda 66 kV | 6321_Lucinda 66 kV | IN-VC-1_Ingham-Victoria No 1 66 kV | 6321_Lucinda 66 kV | IN-VC-1_Ingham-Victoria No 1 66 kV | IN-VC-1_Ingham-Victoria No 1 66 kV | 6321_Lucinda 66 kV | IN-VC-1_Ingham-Victoria No 1 66 kV | IN-VC-1_Ingham-Victoria No 1 66 kV | 6321_Lucinda 66 kV | IN-VC-1_Ingham-Victoria No 1 66 kV | IN-VC-1_Ingham-Victoria No 1 66 kV
NQ-Ingham | IN-LA-1_Ingham-Lannercost No 1 66 kV | % of Rated A | 5.294% | 8.799% | 3.11% | 5.293% | 8.798% | 3.11% | 5.241% | 8.81% | 3.112% | 5.241% | 8.81% | 3.112% | 5.242% | 8.812% | 3.112%
NQ-Ingham | IN-LA-1_Ingham-Lannercost No 1 66 kV | Limiting Line Name | TR_LINE 32824_1 | TR_LINE 32824_1 | TR_LINE 32824_1 | TR_LINE 32824_1 | TR_LINE 32824_1 | TR_LINE 32824_1 | TR_LINE 32824_1 | TR_LINE 32824_1 | TR_LINE 32824_1 | TR_LINE 32824_1 | TR_LINE 32824_1 | TR_LINE 32824_1 | TR_LINE 32824_1 | TR_LINE 32824_1 | TR_LINE 32824_1
NQ-Ingham | IN-LA-1_Ingham-Lannercost No 1 66 kV | Loading (A) | 7.094 | 15.9266 | 5.442 | 7.0929 | 15.9238 | 5.4417 | 7.0235 | 15.9469 | 5.4458 | 7.023 | 15.9458 | 5.4457 | 7.0246 | 15.9499 | 5.4463
NQ-Ingham | IN-LA-1_Ingham-Lannercost No 1 66 kV | Loading (MVA) | 0.83775 | 1.897 | 0.64449 | 0.83775 | 1.897 | 0.64449 | 0.83786 | 1.8971 | 0.64447 | 0.83786 | 1.8971 | 0.64447 | 0.83786 | 1.8971 | 0.64447
NQ-Ingham | IN-LA-1_Ingham-Lannercost No 1 66 kV | Loading (MW) | 0.83709 | 1.8918 | 0.64145 | 0.83709 | 1.8918 | 0.64145 | 0.83707 | 1.8918 | 0.64145 | 0.83707 | 1.8918 | 0.64145 | 0.83708 | 1.8918 | 0.64145
NQ-Ingham | IN-LA-1_Ingham-Lannercost No 1 66 kV | Power Factor | 0.99921 | 0.99709 | 0.99528 | 0.99921 | 0.99709 | 0.99528 | 0.99906 | 0.99707 | 0.99532 | 0.99906 | 0.99707 | 0.99532 | 0.99907 | 0.99707 | 0.99532
NQ-Ingham | IN-LA-1_Ingham-Lannercost No 1 66 kV | Rating (A) | 134 | 181 | 175 | 134 | 181 | 175 | 134 | 181 | 175 | 134 | 181 | 175 | 134 | 181 | 175
NQ-Ingham | IN-LA-1_Ingham-Lannercost No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Ingham | IN-LA-1_Ingham-Lannercost No 1 66 kV | Min Voltage at Constrained Conductor | 68.1764 | 68.7692 | 68.3724 | 68.1873 | 68.7809 | 68.3761 | 68.8707 | 68.6834 | 68.3218 | 68.8755 | 68.6881 | 68.3236 | 68.8599 | 68.6707 | 68.3163
NQ-Ingham | IN-LA-1_Ingham-Lannercost No 1 66 kV | Contingency Outage | IN-VC-1_Ingham-Victoria No 1 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV | IN-VC-1_Ingham-Victoria No 1 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV
NQ-Ingham | IN-VC-1_Ingham-Victoria No 1 66 kV | % of Rated A | 25.11% | 24.04% | 26.54% | 25.1% | 24.03% | 26.53% | 24.73% | 23.67% | 26.29% | 24.73% | 23.67% | 26.29% | 25.14% | 24.07% | 26.56%
NQ-Ingham | IN-VC-1_Ingham-Victoria No 1 66 kV | Limiting Line Name | TR_LINE 135530_1 | TR_LINE 135530_1 | TR_LINE 135530_1 | TR_LINE 135530_1 | TR_LINE 135530_1 | TR_LINE 135530_1 | TR_LINE 135530_1 | TR_LINE 135530_1 | TR_LINE 135530_1 | TR_LINE 135530_1 | TR_LINE 135530_1 | TR_LINE 135530_1 | TR_LINE 135530_1 | TR_LINE 135530_1 | TR_LINE 135530_1
NQ-Ingham | IN-VC-1_Ingham-Victoria No 1 66 kV | Loading (A) | 49.9637 | 53.6019 | 54.1319 | 49.9547 | 53.5918 | 54.1287 | 49.2089 | 52.7776 | 53.6308 | 49.2052 | 52.7736 | 53.6292 | 50.0376 | 53.672 | 54.1811
NQ-Ingham | IN-VC-1_Ingham-Victoria No 1 66 kV | Loading (MVA) | 5.939 | 6.3608 | 6.375 | 5.9389 | 6.3607 | 6.375 | 5.8427 | 6.2557 | 6.3116 | 5.8427 | 6.2557 | 6.3116 | 5.9396 | 6.3599 | 6.3755
NQ-Ingham | IN-VC-1_Ingham-Victoria No 1 66 kV | Loading (MW) | 5.2843 | 5.7481 | 5.5679 | 5.2843 | 5.7481 | 5.5679 | 5.1938 | 5.6511 | 5.5076 | 5.1937 | 5.6511 | 5.5076 | 5.2843 | 5.748 | 5.568
NQ-Ingham | IN-VC-1_Ingham-Victoria No 1 66 kV | Power Factor | 0.88972 | 0.90364 | 0.87336 | 0.88973 | 0.90365 | 0.87337 | 0.8889 | 0.90331 | 0.87257 | 0.8889 | 0.90332 | 0.87257 | 0.88964 | 0.90374 | 0.87331
NQ-Ingham | IN-VC-1_Ingham-Victoria No 1 66 kV | Rating (A) | 199 | 223 | 204 | 199 | 223 | 204 | 199 | 223 | 204 | 199 | 223 | 204 | 199 | 223 | 204
NQ-Ingham | IN-VC-1_Ingham-Victoria No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Ingham | IN-VC-1_Ingham-Victoria No 1 66 kV | Min Voltage at Constrained Conductor | 68.6276 | 68.5126 | 67.9933 | 68.639 | 68.5244 | 67.9971 | 68.5502 | 68.4333 | 67.9466 | 68.555 | 68.438 | 67.9483 | 68.5331 | 68.414 | 67.9369
NQ-Ingham | IN-VC-1_Ingham-Victoria No 1 66 kV | Contingency Outage | IN-GR_Ingham-Black River/Greenvale 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV | IN-GR_Ingham-Black River/Greenvale 66 kV
NQ-Ingham | MACN-02_Macknade Mill 11 kV | % of Rated A | 0.06997% | 0.07047% | 0.07039% | 0.06998% | 0.07048% | 0.07039% | 0.06993% | 0.07042% | 0.07036% | 0.06993% | 0.07043% | 0.07036% | 0.06987% | 0.07036% | 0.07032%
NQ-Ingham | MACN-02_Macknade Mill 11 kV | Limiting Line Name | HV_CABLE MACN-02 12148046 | HV_CABLE MACN-02 12148046 | HV_CABLE MACN-02 12148046 | HV_CABLE MACN-02 12148046 | HV_CABLE MACN-02 12148046 | HV_CABLE MACN-02 12148046 | HV_CABLE MACN-02 12148046 | HV_CABLE MACN-02 12148046 | HV_CABLE MACN-02 12148046 | HV_CABLE MACN-02 12148046 | HV_CABLE MACN-02 12148046 | HV_CABLE MACN-02 12148046 | HV_CABLE MACN-02 12148046 | HV_CABLE MACN-02 12148046 | HV_CABLE MACN-02 12148046
NQ-Ingham | MACN-02_Macknade Mill 11 kV | Loading (A) | 0.27988 | 0.28188 | 0.28155 | 0.27993 | 0.28193 | 0.28157 | 0.2797 | 0.2817 | 0.28143 | 0.27973 | 0.28172 | 0.28143 | 0.27948 | 0.28146 | 0.28129
NQ-Ingham | MACN-02_Macknade Mill 11 kV | Loading (MVA) | 0.0053526 | 0.0054294 | 0.0054166 | 0.0053545 | 0.0054313 | 0.0054172 | 0.0053458 | 0.0054223 | 0.0054117 | 0.0053466 | 0.0054231 | 0.005412 | 0.0053372 | 0.0054129 | 0.0054064
NQ-Ingham | MACN-02_Macknade Mill 11 kV | Loading (MW) | 0.00010553 | 0.00010704 | 0.00010679 | 0.00010556 | 0.00010708 | 0.0001068 | 0.00010539 | 0.0001069 | 0.00010669 | 0.00010541 | 0.00010691 | 0.0001067 | 0.00010522 | 0.00010671 | 0.00010658
NQ-Ingham | MACN-02_Macknade Mill 11 kV | Power Factor | 0.019005 | 0.019005 | 0.019005 | 0.019005 | 0.019005 | 0.019005 | 0.019005 | 0.019005 | 0.019005 | 0.019005 | 0.019005 | 0.019005 | 0.019005 | 0.019005 | 0.019005
NQ-Ingham | MACN-02_Macknade Mill 11 kV | Rating (A) | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400
NQ-Ingham | MACN-02_Macknade Mill 11 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Ingham | MACN-02_Macknade Mill 11 kV | Min Voltage at Constrained Conductor | 11.0415 | 11.1204 | 11.1072 | 11.0434 | 11.1224 | 11.1079 | 11.0344 | 11.1131 | 11.1023 | 11.0352 | 11.1139 | 11.1026 | 11.0256 | 11.1035 | 11.0968
NQ-Ingham | MACN-02_Macknade Mill 11 kV | Contingency Outage | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | IN-LA-1_Ingham-Lannercost No 1 66 kV | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | IN-LA-1_Ingham-Lannercost No 1 66 kV | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | IN-LA-1_Ingham-Lannercost No 1 66 kV | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | IN-LA-1_Ingham-Lannercost No 1 66 kV | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | IN-LA-1_Ingham-Lannercost No 1 66 kV | GA-HP-1_Garbutt-Hermit Park No 1 66 kV
NQ-King Creek | 7307_King Creek - Blue Valley 132 kV | % of Rated A | 2.807% | 2.693% | 2.959% | 2.806% | 2.693% | 2.958% | 2.806% | 2.692% | 2.958% | 2.806% | 2.693% | 2.958% | 2.807% | 2.693% | 2.958%
NQ-King Creek | 7307_King Creek - Blue Valley 132 kV | Limiting Line Name | TR_LINE 62480_1 | TR_LINE 62480_1 | TR_LINE 62480_1 | TR_LINE 62480_1 | TR_LINE 62480_1 | TR_LINE 62480_1 | TR_LINE 62480_1 | TR_LINE 62480_1 | TR_LINE 62480_1 | TR_LINE 62480_1 | TR_LINE 62480_1 | TR_LINE 62480_1 | TR_LINE 62480_1 | TR_LINE 62480_1 | TR_LINE 62480_1
NQ-King Creek | 7307_King Creek - Blue Valley 132 kV | Loading (A) | 12.6859 | 12.8175 | 12.6329 | 12.6849 | 12.8164 | 12.6321 | 12.6847 | 12.8161 | 12.6322 | 12.6849 | 12.8163 | 12.6322 | 12.686 | 12.8177 | 12.6325
NQ-King Creek | 7307_King Creek - Blue Valley 132 kV | Loading (MVA) | 3.0811 | 3.1107 | 3.0729 | 3.0811 | 3.1107 | 3.0729 | 3.0811 | 3.1107 | 3.0729 | 3.0811 | 3.1107 | 3.0729 | 3.0811 | 3.1107 | 3.0729
NQ-King Creek | 7307_King Creek - Blue Valley 132 kV | Loading (MW) | 2.8662 | 2.8935 | 2.8586 | 2.8662 | 2.8935 | 2.8586 | 2.8662 | 2.8935 | 2.8586 | 2.8662 | 2.8935 | 2.8586 | 2.8662 | 2.8935 | 2.8586
NQ-King Creek | 7307_King Creek - Blue Valley 132 kV | Power Factor | 0.92972 | 0.92966 | 0.92975 | 0.92972 | 0.92966 | 0.92975 | 0.92972 | 0.92966 | 0.92975 | 0.92972 | 0.92966 | 0.92975 | 0.92972 | 0.92966 | 0.92975
NQ-King Creek | 7307_King Creek - Blue Valley 132 kV | Rating (A) | 452 | 476 | 427 | 452 | 476 | 427 | 452 | 476 | 427 | 452 | 476 | 427 | 452 | 476 | 427
NQ-King Creek | 7307_King Creek - Blue Valley 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-King Creek | 7307_King Creek - Blue Valley 132 kV | Min Voltage at Constrained Conductor | 140.2244 | 140.1169 | 140.4375 | 140.2354 | 140.1292 | 140.4453 | 140.2379 | 140.1322 | 140.4448 | 140.2355 | 140.1293 | 140.4445 | 140.2234 | 140.1147 | 140.441
NQ-King Creek | 7307_King Creek - Blue Valley 132 kV | Contingency Outage | ME-PR-1_Merinda - Proserpine No 1 66 kV | PR-BN-1_Proserpine - Bowen No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | PR-BN-1_Proserpine - Bowen No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | PR-BN-1_Proserpine - Bowen No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | PR-BN-1_Proserpine - Bowen No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV
NQ-MK-Proserpine Bowen | 118_Cannonvale No 2 66 kV | % of Rated A | 78.86% | 82.73% | 58.29% | 73.91% | 75.11% | 49.83% | 73.69% | 74.91% | 49.71% | 73.9% | 75.13% | 49.82% | 75.16% | 76.47% | 50.48%
NQ-MK-Proserpine Bowen | 118_Cannonvale No 2 66 kV | Limiting Line Name | TR_CABLE 7280_1 | TR_CABLE 7280_1 | TR_CABLE 7280_1 | TR_CABLE 7280_1 | TR_CABLE 7280_1 | TR_CABLE 7280_1 | TR_CABLE 7280_1 | TR_CABLE 7280_1 | TR_CABLE 7280_1 | TR_CABLE 7280_1 | TR_CABLE 7280_1 | TR_CABLE 7280_1 | TR_CABLE 7280_1 | TR_CABLE 7280_1 | TR_CABLE 7280_1
NQ-MK-Proserpine Bowen | 118_Cannonvale No 2 66 kV | Loading (A) | 152.1909 | 159.6719 | 112.5025 | 142.6516 | 144.9631 | 96.1647 | 142.2232 | 144.5766 | 95.9337 | 142.627 | 145.0101 | 96.1453 | 145.0556 | 147.5811 | 97.4238
NQ-MK-Proserpine Bowen | 118_Cannonvale No 2 66 kV | Loading (MVA) | 17.603 | 18.4046 | 13.0864 | 16.5154 | 16.7264 | 11.0731 | 16.468 | 16.6839 | 11.0471 | 16.5118 | 16.7305 | 11.0709 | 16.7758 | 17.0068 | 11.2131
NQ-MK-Proserpine Bowen | 118_Cannonvale No 2 66 kV | Loading (MW) | 16.4063 | 17.4254 | 10.1902 | 16.3679 | 16.5913 | 10.3748 | 16.3175 | 16.5463 | 10.3437 | 16.3644 | 16.596 | 10.3722 | 16.645 | 16.8892 | 10.5404
NQ-MK-Proserpine Bowen | 118_Cannonvale No 2 66 kV | Power Factor | 0.93202 | 0.9468 | 0.77869 | 0.99107 | 0.99192 | 0.93693 | 0.99086 | 0.99175 | 0.93632 | 0.99107 | 0.99196 | 0.93689 | 0.99221 | 0.99308 | 0.94001
NQ-MK-Proserpine Bowen | 118_Cannonvale No 2 66 kV | Rating (A) | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193
NQ-MK-Proserpine Bowen | 118_Cannonvale No 2 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-MK-Proserpine Bowen | 118_Cannonvale No 2 66 kV | Min Voltage at Constrained Conductor | 66.7759 | 66.5451 | 67.1571 | 66.8385 | 66.613 | 66.4785 | 66.8474 | 66.6213 | 66.4822 | 66.8356 | 66.6079 | 66.4784 | 66.7671 | 66.5282 | 66.4487
NQ-MK-Proserpine Bowen | 118_Cannonvale No 2 66 kV | Contingency Outage | ME-PR-1_Merinda - Proserpine No 1 66 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | 426_Mt Rooper 66 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV
NQ-MK-Proserpine Bowen | 119_Cannonvale No 1 66 kV | % of Rated A | 77.33% | 53.61% | 36.73% | 77.31% | 56.27% | 37.94% | 77.07% | 56.12% | 37.85% | 77.3% | 56.29% | 37.93% | 78.66% | 57.32% | 38.45%
NQ-MK-Proserpine Bowen | 119_Cannonvale No 1 66 kV | Limiting Line Name | TR_LINE 13013_1 | TR_LINE 13013_1 | TR_LINE 9922_1 | TR_LINE 13015_1 | TR_LINE 13015_1 | TR_LINE 13015_1 | TR_LINE 13015_1 | TR_LINE 13015_1 | TR_LINE 13015_1 | TR_LINE 13015_1 | TR_LINE 13015_1 | TR_LINE 13015_1 | TR_LINE 13015_1 | TR_LINE 13015_1 | TR_LINE 13015_1
NQ-MK-Proserpine Bowen | 119_Cannonvale No 1 66 kV | Loading (A) | 143.0543 | 138.8565 | 127.4684 | 143.0238 | 145.7476 | 95.6073 | 142.5797 | 145.3463 | 95.3706 | 142.9978 | 145.7959 | 95.5873 | 145.5145 | 148.4634 | 96.8991
NQ-MK-Proserpine Bowen | 119_Cannonvale No 1 66 kV | Loading (MVA) | 16.4049 | 15.8747 | 14.6008 | 16.4714 | 16.7283 | 10.9789 | 16.4228 | 16.6846 | 10.9525 | 16.4677 | 16.7325 | 10.9766 | 16.7382 | 17.0158 | 11.1215
NQ-MK-Proserpine Bowen | 119_Cannonvale No 1 66 kV | Loading (MW) | 16.3095 | 15.8001 | 14.4096 | 16.2252 | 16.5036 | 10.0834 | 16.1727 | 16.4567 | 10.0509 | 16.2216 | 16.5086 | 10.0807 | 16.514 | 16.8141 | 10.2563
NQ-MK-Proserpine Bowen | 119_Cannonvale No 1 66 kV | Power Factor | 0.99418 | 0.9953 | 0.9869 | 0.98487 | 0.98638 | 0.91837 | 0.98458 | 0.98616 | 0.91762 | 0.98487 | 0.98644 | 0.91832 | 0.98642 | 0.98796 | 0.92213
NQ-MK-Proserpine Bowen | 119_Cannonvale No 1 66 kV | Rating (A) | 185 | 259 | 347 | 185 | 259 | 252 | 185 | 259 | 252 | 185 | 259 | 252 | 185 | 259 | 252
NQ-MK-Proserpine Bowen | 119_Cannonvale No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-MK-Proserpine Bowen | 119_Cannonvale No 1 66 kV | Min Voltage at Constrained Conductor | 66.1917 | 65.9892 | 66.1272 | 66.4367 | 66.2095 | 66.284 | 66.4475 | 66.2193 | 66.2887 | 66.4339 | 66.204 | 66.2839 | 66.3548 | 66.113 | 66.2488
NQ-MK-Proserpine Bowen | 119_Cannonvale No 1 66 kV | Contingency Outage | ME-PR-1_Merinda - Proserpine No 1 66 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV
NQ-MK-Proserpine Bowen | 120_Prosperpine - Calen 66 kV | % of Rated A | 22.1% | 21.17% | 11.95% | 22.09% | 21.14% | 11.95% | 22.09% | 21.14% | 11.95% | 22.09% | 21.15% | 11.95% | 22.51% | 21.68% | 12.25%
NQ-MK-Proserpine Bowen | 120_Prosperpine - Calen 66 kV | Limiting Line Name | TR_LINE 89457_1 | TR_LINE 10511_1 | TR_LINE 89457_1 | TR_LINE 89457_1 | TR_LINE 10511_1 | TR_LINE 89457_1 | TR_LINE 89457_1 | TR_LINE 10511_1 | TR_LINE 89457_1 | TR_LINE 89457_1 | TR_LINE 10511_1 | TR_LINE 89457_1 | TR_LINE 89457_1 | TR_LINE 10511_1 | TR_LINE 89457_1
NQ-MK-Proserpine Bowen | 120_Prosperpine - Calen 66 kV | Loading (A) | 29.167 | 37.4652 | 20.321 | 29.1633 | 37.4239 | 20.3084 | 29.1635 | 37.4189 | 20.3075 | 29.1647 | 37.427 | 20.3085 | 29.7128 | 38.3691 | 20.8257
NQ-MK-Proserpine Bowen | 120_Prosperpine - Calen 66 kV | Loading (MVA) | 3.3548 | 4.264 | 2.3381 | 3.3548 | 4.2639 | 2.3385 | 3.3548 | 4.2638 | 2.3385 | 3.3548 | 4.2639 | 2.3385 | 3.4171 | 4.3643 | 2.397
NQ-MK-Proserpine Bowen | 120_Prosperpine - Calen 66 kV | Loading (MW) | 3.3443 | 4.2581 | 2.2682 | 3.3443 | 4.258 | 2.2681 | 3.3443 | 4.258 | 2.2681 | 3.3443 | 4.258 | 2.2681 | 3.4076 | 4.3577 | 2.3308
NQ-MK-Proserpine Bowen | 120_Prosperpine - Calen 66 kV | Power Factor | 0.99686 | 0.99859 | 0.97007 | 0.99686 | 0.99861 | 0.96992 | 0.99686 | 0.99861 | 0.96991 | 0.99686 | 0.9986 | 0.96992 | 0.9972 | 0.99847 | 0.97242
NQ-MK-Proserpine Bowen | 120_Prosperpine - Calen 66 kV | Rating (A) | 132 | 177 | 170 | 132 | 177 | 170 | 132 | 177 | 170 | 132 | 177 | 170 | 132 | 177 | 170
NQ-MK-Proserpine Bowen | 120_Prosperpine - Calen 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-MK-Proserpine Bowen | 120_Prosperpine - Calen 66 kV | Min Voltage at Constrained Conductor | 66.4057 | 65.7066 | 66.4291 | 66.4143 | 65.7766 | 66.4796 | 66.4139 | 65.7849 | 66.4832 | 66.4111 | 65.7713 | 66.4794 | 66.3971 | 65.6677 | 66.4497
NQ-MK-Proserpine Bowen | 120_Prosperpine - Calen 66 kV | Contingency Outage | 119_Cannonvale No 1 66 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | 119_Cannonvale No 1 66 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | 119_Cannonvale No 1 66 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | 119_Cannonvale No 1 66 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | 119_Cannonvale No 1 66 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV
NQ-MK-Proserpine Bowen | 122_Daydream/South Molle 11 kV | % of Rated A | 2.444% | 2.436% | 2.435% | 2.434% | 2.426% | 2.427% | 2.435% | 2.426% | 2.428% | 2.434% | 2.426% | 2.427% | 2.43% | 2.423% | 2.425%
NQ-MK-Proserpine Bowen | 122_Daydream/South Molle 11 kV | Limiting Line Name | HV_LINE 2563705_1 | HV_LINE 2563705_1 | HV_LINE 2563705_1 | HV_LINE 2563705_1 | HV_LINE 2563705_1 | HV_LINE 2563705_1 | HV_LINE 2563705_1 | HV_LINE 2563705_1 | HV_LINE 2563705_1 | HV_LINE 2563705_1 | HV_LINE 2563705_1 | HV_LINE 2563705_1 | HV_LINE 2563705_1 | HV_LINE 2563705_1 | HV_LINE 2563705_1
NQ-MK-Proserpine Bowen | 122_Daydream/South Molle 11 kV | Loading (A) | 1.9066 | 1.9004 | 1.8992 | 1.8988 | 1.892 | 1.8933 | 1.8994 | 1.8925 | 1.8936 | 1.8988 | 1.8919 | 1.8934 | 1.8955 | 1.8898 | 1.8916
NQ-MK-Proserpine Bowen | 122_Daydream/South Molle 11 kV | Loading (MVA) | 0.037131 | 0.036889 | 0.036845 | 0.036827 | 0.036564 | 0.036617 | 0.036851 | 0.036586 | 0.036629 | 0.036829 | 0.036561 | 0.036618 | 0.036701 | 0.03648 | 0.036548
NQ-MK-Proserpine Bowen | 122_Daydream/South Molle 11 kV | Loading (MW) | 0.0007441 | 0.00073925 | 0.00073838 | 0.00073802 | 0.00073274 | 0.0007338 | 0.00073849 | 0.00073317 | 0.00073404 | 0.00073805 | 0.00073269 | 0.00073382 | 0.00073548 | 0.00073106 | 0.00073242
NQ-MK-Proserpine Bowen | 122_Daydream/South Molle 11 kV | Power Factor | 0.020029 | 0.020029 | 0.020029 | 0.020029 | 0.020029 | 0.020029 | 0.020029 | 0.020029 | 0.020029 | 0.020029 | 0.020029 | 0.020029 | 0.020029 | 0.020029 | 0.020029
NQ-MK-Proserpine Bowen | 122_Daydream/South Molle 11 kV | Rating (A) | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78
NQ-MK-Proserpine Bowen | 122_Daydream/South Molle 11 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-MK-Proserpine Bowen | 122_Daydream/South Molle 11 kV | Min Voltage at Constrained Conductor | 11.2439 | 11.2072 | 11.2006 | 11.1979 | 11.1578 | 11.1658 | 11.2015 | 11.1611 | 11.1677 | 11.1982 | 11.1574 | 11.166 | 11.1786 | 11.145 | 11.1553
NQ-MK-Proserpine Bowen | 122_Daydream/South Molle 11 kV | Contingency Outage | 125_Hayman Island 22 kV | 125_Hayman Island 22 kV | 125_Hayman Island 22 kV | 125_Hayman Island 22 kV | PROS-KECR-2_Proserpine No 2 66 kV | 125_Hayman Island 22 kV | 125_Hayman Island 22 kV | PROS-KECR-2_Proserpine No 2 66 kV | 125_Hayman Island 22 kV | 125_Hayman Island 22 kV | PROS-KECR-2_Proserpine No 2 66 kV | 125_Hayman Island 22 kV | 125_Hayman Island 22 kV | PROS-KECR-2_Proserpine No 2 66 kV | 125_Hayman Island 22 kV
NQ-MK-Proserpine Bowen | 124_Hamilton Island 22 kV | % of Rated A | 1.595% | 1.591% | 1.591% | 1.588% | 1.605% | 1.586% | 1.589% | 1.605% | 1.587% | 1.588% | 1.605% | 1.586% | 1.606% | 1.601% | 1.586%
NQ-MK-Proserpine Bowen | 124_Hamilton Island 22 kV | Limiting Line Name | HV_LINE 136005_1 | HV_LINE 136005_1 | HV_LINE 136005_1 | HV_LINE 136005_1 | HV_LINE 136005_1 | HV_LINE 136005_1 | HV_LINE 136005_1 | HV_LINE 136005_1 | HV_LINE 136005_1 | HV_LINE 136005_1 | HV_LINE 136005_1 | HV_LINE 136005_1 | HV_LINE 136005_1 | HV_LINE 136005_1 | HV_LINE 136005_1
NQ-MK-Proserpine Bowen | 124_Hamilton Island 22 kV | Loading (A) | 1.2438 | 1.2413 | 1.2413 | 1.2387 | 1.2517 | 1.2374 | 1.2392 | 1.2521 | 1.2376 | 1.2388 | 1.2517 | 1.2375 | 1.2528 | 1.2491 | 1.237
NQ-MK-Proserpine Bowen | 124_Hamilton Island 22 kV | Loading (MVA) | 0.048273 | 0.048078 | 0.048074 | 0.047876 | 0.048883 | 0.047775 | 0.047913 | 0.048917 | 0.047795 | 0.047885 | 0.048885 | 0.04778 | 0.048973 | 0.048684 | 0.047743
NQ-MK-Proserpine Bowen | 124_Hamilton Island 22 kV | Loading (MW) | 0.00096497 | 0.00096107 | 0.000961 | 0.00095703 | 0.00097717 | 0.00095502 | 0.00095778 | 0.00097785 | 0.00095542 | 0.00095721 | 0.0009772 | 0.00095513 | 0.00097897 | 0.00097318 | 0.00095438
NQ-MK-Proserpine Bowen | 124_Hamilton Island 22 kV | Power Factor | 0.01999 | 0.01999 | 0.01999 | 0.01999 | 0.01999 | 0.01999 | 0.01999 | 0.01999 | 0.01999 | 0.01999 | 0.01999 | 0.01999 | 0.01999 | 0.01999 | 0.01999
NQ-MK-Proserpine Bowen | 124_Hamilton Island 22 kV | Rating (A) | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78
NQ-MK-Proserpine Bowen | 124_Hamilton Island 22 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-MK-Proserpine Bowen | 124_Hamilton Island 22 kV | Min Voltage at Constrained Conductor | 22.4071 | 22.3618 | 22.361 | 22.3147 | 22.5483 | 22.2913 | 22.3235 | 22.5562 | 22.2959 | 22.3168 | 22.5487 | 22.2925 | 22.569 | 22.5023 | 22.2838
NQ-MK-Proserpine Bowen | 124_Hamilton Island 22 kV | Contingency Outage | 125_Hayman Island 22 kV | 125_Hayman Island 22 kV | 125_Hayman Island 22 kV | 125_Hayman Island 22 kV | 125_Hayman Island 22 kV | 125_Hayman Island 22 kV | 125_Hayman Island 22 kV | 125_Hayman Island 22 kV | 125_Hayman Island 22 kV | 125_Hayman Island 22 kV | 125_Hayman Island 22 kV | 125_Hayman Island 22 kV | 125_Hayman Island 22 kV | 125_Hayman Island 22 kV | ME-BN-1_Merinda - Bowen No 1 66 kV
NQ-MK-Proserpine Bowen | 125_Hayman Island 22 kV | % of Rated A | 81.82% | 72.99% | 59.73% | 81.82% | 72.26% | 59.74% | 81.78% | 72.23% | 59.73% | 81.81% | 72.26% | 59.73% | 80.97% | 72.44% | 59.7%
NQ-MK-Proserpine Bowen | 125_Hayman Island 22 kV | Limiting Line Name | HV_LINE 11597319_1 | HV_LINE 11597319_1 | HV_LINE 11597319_1 | HV_LINE 11597319_1 | HV_LINE 11597319_1 | HV_LINE 11597319_1 | HV_LINE 11597319_1 | HV_LINE 11597319_1 | HV_LINE 11597319_1 | HV_LINE 11597319_1 | HV_LINE 11597319_1 | HV_LINE 11597319_1 | HV_LINE 11597319_1 | HV_LINE 11597319_1 | HV_LINE 11597319_1
NQ-MK-Proserpine Bowen | 125_Hayman Island 22 kV | Loading (A) | 63.8187 | 56.9343 | 46.588 | 63.8187 | 56.3654 | 46.5976 | 63.7888 | 56.3417 | 46.5864 | 63.8107 | 56.3631 | 46.5927 | 63.1588 | 56.5001 | 46.5644
NQ-MK-Proserpine Bowen | 125_Hayman Island 22 kV | Loading (MVA) | 2.4321 | 2.1696 | 1.7768 | 2.4321 | 2.1678 | 1.7769 | 2.432 | 2.1678 | 1.7768 | 2.432 | 2.1678 | 1.7769 | 2.4298 | 2.1682 | 1.7768
NQ-MK-Proserpine Bowen | 125_Hayman Island 22 kV | Loading (MW) | 2.2932 | 2.0501 | 1.685 | 2.2932 | 2.0491 | 1.685 | 2.2931 | 2.0491 | 1.685 | 2.2931 | 2.0491 | 1.685 | 2.2919 | 2.0493 | 1.6849
NQ-MK-Proserpine Bowen | 125_Hayman Island 22 kV | Power Factor | 0.94281 | 0.94485 | 0.94824 | 0.94281 | 0.94518 | 0.94823 | 0.94283 | 0.94519 | 0.94824 | 0.94282 | 0.94518 | 0.94823 | 0.94317 | 0.9451 | 0.94825
NQ-MK-Proserpine Bowen | 125_Hayman Island 22 kV | Rating (A) | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78
NQ-MK-Proserpine Bowen | 125_Hayman Island 22 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-MK-Proserpine Bowen | 125_Hayman Island 22 kV | Min Voltage at Constrained Conductor | 21.9814 | 21.9825 | 22.0048 | 21.9814 | 22.1868 | 22.0006 | 21.9908 | 22.1954 | 22.0055 | 21.9839 | 22.1876 | 22.0027 | 22.1912 | 22.138 | 22.0152
NQ-MK-Proserpine Bowen | 125_Hayman Island 22 kV | Contingency Outage | 6308_Merinda - Abbot Point 66 kV | 124_Hamilton Island 22 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | 124_Hamilton Island 22 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | 124_Hamilton Island 22 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | 124_Hamilton Island 22 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV
NQ-MK-Proserpine Bowen | 426_Mt Rooper 66 kV | % of Rated A | 43.96% | 35.98% | 25.79% | 43.39% | 35.58% | 25.47% | 43.02% | 35.29% | 25.27% | 43.03% | 35.3% | 25.28% | 43.47% | 35.66% | 25.48%
NQ-MK-Proserpine Bowen | 426_Mt Rooper 66 kV | Limiting Line Name | TR_LINE 97526_1 | TR_CABLE 11763_1 | TR_CABLE 11763_1 | TR_LINE 97526_1 | TR_CABLE 11763_1 | TR_CABLE 11763_1 | TR_LINE 97526_1 | TR_CABLE 11763_1 | TR_CABLE 11763_1 | TR_LINE 97526_1 | TR_CABLE 11763_1 | TR_CABLE 11763_1 | TR_LINE 97526_1 | TR_CABLE 11763_1 | TR_CABLE 11763_1
NQ-MK-Proserpine Bowen | 426_Mt Rooper 66 kV | Loading (A) | 109.4613 | 100.7346 | 72.2223 | 108.0338 | 99.6305 | 71.3205 | 107.1194 | 98.8145 | 70.7611 | 107.1538 | 98.8495 | 70.7701 | 108.2442 | 99.8526 | 71.3563
NQ-MK-Proserpine Bowen | 426_Mt Rooper 66 kV | Loading (MVA) | 12.2162 | 11.1886 | 8.1231 | 12.2126 | 11.1887 | 8.1226 | 12.1128 | 11.1002 | 8.0602 | 12.113 | 11.1004 | 8.0602 | 12.214 | 11.1896 | 8.12
NQ-MK-Proserpine Bowen | 426_Mt Rooper 66 kV | Loading (MW) | 12.0489 | 10.9905 | 7.9976 | 12.0477 | 10.9904 | 7.9975 | 11.9502 | 10.9037 | 7.936 | 11.9502 | 10.9038 | 7.936 | 12.0482 | 10.9908 | 7.9965
NQ-MK-Proserpine Bowen | 426_Mt Rooper 66 kV | Power Factor | 0.98631 | 0.98179 | 0.98389 | 0.9865 | 0.98177 | 0.98391 | 0.98657 | 0.98178 | 0.98391 | 0.98656 | 0.98177 | 0.98391 | 0.98643 | 0.98172 | 0.98411
NQ-MK-Proserpine Bowen | 426_Mt Rooper 66 kV | Rating (A) | 249 | 280 | 280 | 249 | 280 | 280 | 249 | 280 | 280 | 249 | 280 | 280 | 249 | 280 | 280
NQ-MK-Proserpine Bowen | 426_Mt Rooper 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-MK-Proserpine Bowen | 426_Mt Rooper 66 kV | Min Voltage at Constrained Conductor | 64.433 | 64.1266 | 64.9367 | 65.2651 | 64.8373 | 65.7539 | 65.2844 | 64.8562 | 65.7644 | 65.2646 | 64.8341 | 65.7563 | 65.1454 | 64.6987 | 65.6998
NQ-MK-Proserpine Bowen | 426_Mt Rooper 66 kV | Contingency Outage | ME-PR-1_Merinda - Proserpine No 1 66 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV
NQ-MK-Proserpine Bowen | CANN_JUPO (Ex119&118) | % of Rated A |  |  |  | 50.75% | 49.34% | 32.06% | 50.42% | 49.04% | 31.86% | 50.44% | 49.06% | 31.86% | 51.11% | 49.75% | 32.23%
NQ-MK-Proserpine Bowen | CANN_JUPO (Ex119&118) | Limiting Line Name |  |  |  | TR_CABLE 17_1 | TR_CABLE 17_1 | TR_CABLE 17_1 | TR_CABLE 17_1 | TR_CABLE 17_1 | TR_CABLE 17_1 | TR_CABLE 17_1 | TR_CABLE 17_1 | TR_CABLE 17_1 | TR_CABLE 17_1 | TR_CABLE 17_1 | TR_CABLE 17_1
NQ-MK-Proserpine Bowen | CANN_JUPO (Ex119&118) | Loading (A) |  |  |  | 142.1075 | 138.1457 | 89.7657 | 141.1845 | 137.3212 | 89.2054 | 141.2292 | 137.3695 | 89.2168 | 143.1166 | 139.2956 | 90.2335
NQ-MK-Proserpine Bowen | CANN_JUPO (Ex119&118) | Loading (MVA) |  |  |  | 16.1 | 15.5897 | 10.2561 | 15.9999 | 15.5006 | 10.1935 | 16.0001 | 15.5008 | 10.1936 | 16.1849 | 15.6864 | 10.3012
NQ-MK-Proserpine Bowen | CANN_JUPO (Ex119&118) | Loading (MW) |  |  |  | 15.9614 | 15.4727 | 10.2221 | 15.8634 | 15.3853 | 10.1602 | 15.8635 | 15.3854 | 10.1603 | 16.0446 | 15.5674 | 10.2675
NQ-MK-Proserpine Bowen | CANN_JUPO (Ex119&118) | Power Factor |  |  |  | 0.99028 | 0.99137 | 0.99514 | 0.99035 | 0.99143 | 0.9952 | 0.99034 | 0.99142 | 0.99519 | 0.99022 | 0.99129 | 0.99521
NQ-MK-Proserpine Bowen | CANN_JUPO (Ex119&118) | Rating (A) |  |  |  | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280
NQ-MK-Proserpine Bowen | CANN_JUPO (Ex119&118) | Time |  |  |  | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-MK-Proserpine Bowen | CANN_JUPO (Ex119&118) | Min Voltage at Constrained Conductor |  |  |  | 65.4107 | 65.1538 | 65.9649 | 65.4289 | 65.1703 | 65.9739 | 65.4092 | 65.1483 | 65.9658 | 65.2921 | 65.0169 | 65.9111
NQ-MK-Proserpine Bowen | CANN_JUPO (Ex119&118) | Contingency Outage |  |  |  | ME-PR-1_Merinda - Proserpine No 1 66 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV
NQ-MK-Proserpine Bowen | ME-BN-1_Merinda - Bowen No 1 66 kV | % of Rated A | 57.96% | 55.72% | 43.78% | 57.95% | 55.72% | 43.77% | 57.95% | 55.72% | 43.41% | 58.3% | 56.07% | 43.97% | 59% | 56.78% | 44.37%
NQ-MK-Proserpine Bowen | ME-BN-1_Merinda - Bowen No 1 66 kV | Limiting Line Name | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1
NQ-MK-Proserpine Bowen | ME-BN-1_Merinda - Bowen No 1 66 kV | Loading (A) | 113.0154 | 121.4778 | 87.1126 | 113.0052 | 121.4636 | 87.1038 | 113.0055 | 121.4637 | 86.3945 | 113.6808 | 122.2292 | 87.4962 | 115.0414 | 123.7748 | 88.2896
NQ-MK-Proserpine Bowen | ME-BN-1_Merinda - Bowen No 1 66 kV | Loading (MVA) | 12.9738 | 14.1448 | 10.1669 | 12.9748 | 14.1457 | 10.1718 | 12.9747 | 14.1457 | 10.0867 | 13.0511 | 14.2334 | 10.2169 | 13.204 | 14.4087 | 10.3057
NQ-MK-Proserpine Bowen | ME-BN-1_Merinda - Bowen No 1 66 kV | Loading (MW) | 11.8807 | 13.2274 | 8.256 | 11.8807 | 13.2273 | 8.256 | 11.8807 | 13.2273 | 8.2546 | 11.9722 | 13.3294 | 8.3192 | 12.1553 | 13.5337 | 8.4456
NQ-MK-Proserpine Bowen | ME-BN-1_Merinda - Bowen No 1 66 kV | Power Factor | 0.91573 | 0.93513 | 0.81203 | 0.91566 | 0.93506 | 0.81164 | 0.91566 | 0.93506 | 0.81835 | 0.91732 | 0.93648 | 0.81425 | 0.92057 | 0.93925 | 0.8195
NQ-MK-Proserpine Bowen | ME-BN-1_Merinda - Bowen No 1 66 kV | Rating (A) | 195 | 218 | 199 | 195 | 218 | 199 | 195 | 218 | 199 | 195 | 218 | 199 | 195 | 218 | 199
NQ-MK-Proserpine Bowen | ME-BN-1_Merinda - Bowen No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-MK-Proserpine Bowen | ME-BN-1_Merinda - Bowen No 1 66 kV | Min Voltage at Constrained Conductor | 66.2755 | 67.2233 | 67.3818 | 66.2863 | 67.2357 | 67.4209 | 66.2861 | 67.2356 | 67.4057 | 66.2799 | 67.2284 | 67.416 | 66.2631 | 67.2068 | 67.3907
NQ-MK-Proserpine Bowen | ME-BN-1_Merinda - Bowen No 1 66 kV | Contingency Outage | 119_Cannonvale No 1 66 kV | 119_Cannonvale No 1 66 kV | CHTO_Clare South - Charters Towers 66 kV | 119_Cannonvale No 1 66 kV | 119_Cannonvale No 1 66 kV | CHTO_Clare South - Charters Towers 66 kV | 119_Cannonvale No 1 66 kV | 119_Cannonvale No 1 66 kV | CHTO_Clare South - Charters Towers 66 kV | 119_Cannonvale No 1 66 kV | 119_Cannonvale No 1 66 kV | CHTO_Clare South - Charters Towers 66 kV | 119_Cannonvale No 1 66 kV | 119_Cannonvale No 1 66 kV | CHTO_Clare South - Charters Towers 66 kV
NQ-MK-Proserpine Bowen | ME-PR-1_Merinda - Proserpine No 1 66 kV | % of Rated A | 12.25% | 10.34% | 9.295% | 12.25% | 10.32% | 9.297% | 12.23% | 10.3% | 9.286% | 12.26% | 10.32% | 9.302% | 12.47% | 10.54% | 9.431%
NQ-MK-Proserpine Bowen | ME-PR-1_Merinda - Proserpine No 1 66 kV | Limiting Line Name | TR_LINE 175208_1 | TR_LINE 112170_1 | TR_LINE 112170_1 | TR_LINE 175208_1 | TR_LINE 112170_1 | TR_LINE 112170_1 | TR_LINE 175208_1 | TR_LINE 112170_1 | TR_LINE 112170_1 | TR_LINE 175208_1 | TR_LINE 112170_1 | TR_LINE 112170_1 | TR_LINE 175208_1 | TR_LINE 112170_1 | TR_LINE 112170_1
NQ-MK-Proserpine Bowen | ME-PR-1_Merinda - Proserpine No 1 66 kV | Loading (A) | 23.6427 | 24.7103 | 20.2638 | 23.6449 | 24.6576 | 20.268 | 23.6013 | 24.6135 | 20.2439 | 23.654 | 24.6762 | 20.2779 | 24.0644 | 25.1883 | 20.5593
NQ-MK-Proserpine Bowen | ME-PR-1_Merinda - Proserpine No 1 66 kV | Loading (MVA) | 2.7549 | 2.8855 | 2.3528 | 2.7572 | 2.8816 | 2.3547 | 2.7523 | 2.8767 | 2.3519 | 2.7582 | 2.8838 | 2.3558 | 2.8044 | 2.9417 | 2.3879
NQ-MK-Proserpine Bowen | ME-PR-1_Merinda - Proserpine No 1 66 kV | Loading (MW) | 2.7304 | 2.885 | 2.3512 | 2.7276 | 2.8816 | 2.3516 | 2.7219 | 2.8767 | 2.3488 | 2.7285 | 2.8837 | 2.3528 | 2.7795 | 2.9413 | 2.3856
NQ-MK-Proserpine Bowen | ME-PR-1_Merinda - Proserpine No 1 66 kV | Power Factor | 0.99112 | 0.9998 | 0.99931 | 0.98927 | 0.99998 | 0.99872 | 0.98894 | 0.99999 | 0.99866 | 0.98923 | 0.99998 | 0.99871 | 0.99112 | 0.99983 | 0.99904
NQ-MK-Proserpine Bowen | ME-PR-1_Merinda - Proserpine No 1 66 kV | Rating (A) | 193 | 239 | 218 | 193 | 239 | 218 | 193 | 239 | 218 | 193 | 239 | 218 | 193 | 239 | 218
NQ-MK-Proserpine Bowen | ME-PR-1_Merinda - Proserpine No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-MK-Proserpine Bowen | ME-PR-1_Merinda - Proserpine No 1 66 kV | Min Voltage at Constrained Conductor | 66.8092 | 67.4163 | 67.0311 | 66.8701 | 67.4679 | 67.0702 | 66.8783 | 67.4728 | 67.0723 | 66.8704 | 67.4672 | 67.07 | 66.8128 | 67.425 | 67.0527
NQ-MK-Proserpine Bowen | ME-PR-1_Merinda - Proserpine No 1 66 kV | Contingency Outage | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV
NQ-MK-Proserpine Bowen | PR-BN-1_Proserpine - Bowen No 1 66 kV | % of Rated A | 2.686% | 2.342% | 2.547% | 2.688% | 2.343% | 2.547% | 2.688% | 2.343% | 2.547% | 2.688% | 2.342% | 2.547% | 2.686% | 2.341% | 2.546%
NQ-MK-Proserpine Bowen | PR-BN-1_Proserpine - Bowen No 1 66 kV | Limiting Line Name | TR_LINE 175048_1 | TR_LINE 175048_1 | TR_LINE 175048_1 | TR_LINE 175048_1 | TR_LINE 175048_1 | TR_LINE 175048_1 | TR_LINE 175048_1 | TR_LINE 175048_1 | TR_LINE 175048_1 | TR_LINE 175048_1 | TR_LINE 175048_1 | TR_LINE 175048_1 | TR_LINE 175048_1 | TR_LINE 175048_1 | TR_LINE 175048_1
NQ-MK-Proserpine Bowen | PR-BN-1_Proserpine - Bowen No 1 66 kV | Loading (A) | 7.9514 | 7.9378 | 7.9707 | 7.9579 | 7.9418 | 7.9734 | 7.9579 | 7.9418 | 7.9736 | 7.9558 | 7.9394 | 7.9724 | 7.9496 | 7.9352 | 7.9684
NQ-MK-Proserpine Bowen | PR-BN-1_Proserpine - Bowen No 1 66 kV | Loading (MVA) | 0.92997 | 0.9268 | 0.93449 | 0.9315 | 0.92773 | 0.93513 | 0.93149 | 0.92773 | 0.93518 | 0.93101 | 0.92717 | 0.93489 | 0.92955 | 0.92619 | 0.93395
NQ-MK-Proserpine Bowen | PR-BN-1_Proserpine - Bowen No 1 66 kV | Loading (MW) | 0.0010978 | 0.001094 | 0.0011031 | 0.0010996 | 0.0010951 | 0.0011039 | 0.0010996 | 0.0010951 | 0.0011039 | 0.001099 | 0.0010945 | 0.0011036 | 0.0010973 | 0.0010933 | 0.0011025
NQ-MK-Proserpine Bowen | PR-BN-1_Proserpine - Bowen No 1 66 kV | Power Factor | 0.0011794 | 0.0011794 | 0.0011794 | 0.0011794 | 0.0011794 | 0.0011794 | 0.0011794 | 0.0011794 | 0.0011794 | 0.0011794 | 0.0011794 | 0.0011794 | 0.0011794 | 0.0011794 | 0.0011794
NQ-MK-Proserpine Bowen | PR-BN-1_Proserpine - Bowen No 1 66 kV | Rating (A) | 296 | 339 | 313 | 296 | 339 | 313 | 296 | 339 | 313 | 296 | 339 | 313 | 296 | 339 | 313
NQ-MK-Proserpine Bowen | PR-BN-1_Proserpine - Bowen No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-MK-Proserpine Bowen | PR-BN-1_Proserpine - Bowen No 1 66 kV | Min Voltage at Constrained Conductor | 67.5251 | 67.41 | 67.6889 | 67.5806 | 67.4438 | 67.712 | 67.5804 | 67.4437 | 67.7139 | 67.5629 | 67.4235 | 67.7034 | 67.5098 | 67.3877 | 67.6695
NQ-MK-Proserpine Bowen | PR-BN-1_Proserpine - Bowen No 1 66 kV | Contingency Outage | 426_Mt Rooper 66 kV | 426_Mt Rooper 66 kV | 6308_Merinda - Abbot Point 66 kV | 426_Mt Rooper 66 kV | 426_Mt Rooper 66 kV | 6308_Merinda - Abbot Point 66 kV | 426_Mt Rooper 66 kV | 426_Mt Rooper 66 kV | 6308_Merinda - Abbot Point 66 kV | 426_Mt Rooper 66 kV | 426_Mt Rooper 66 kV | 6308_Merinda - Abbot Point 66 kV | 426_Mt Rooper 66 kV | 426_Mt Rooper 66 kV | 6308_Merinda - Abbot Point 66 kV
NQ-MK-Proserpine Bowen | PROS-KECR-1_Proserpine No 1 66 kV | % of Rated A | 15.02% | 14.6% | 9.019% | 14.89% | 14.46% | 8.935% | 14.89% | 14.45% | 8.934% | 14.89% | 14.46% | 8.935% | 15.02% | 14.6% | 9.016%
NQ-MK-Proserpine Bowen | PROS-KECR-1_Proserpine No 1 66 kV | Limiting Line Name | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1
NQ-MK-Proserpine Bowen | PROS-KECR-1_Proserpine No 1 66 kV | Loading (A) | 26.5827 | 34.4465 | 20.3819 | 26.3523 | 34.1158 | 20.1927 | 26.3525 | 34.1115 | 20.1916 | 26.3536 | 34.1185 | 20.1928 | 26.5862 | 34.455 | 20.3755
NQ-MK-Proserpine Bowen | PROS-KECR-1_Proserpine No 1 66 kV | Loading (MVA) | 3.0574 | 3.9702 | 2.3451 | 3.0313 | 3.9362 | 2.3251 | 3.0313 | 3.9362 | 2.3251 | 3.0313 | 3.9362 | 2.3251 | 3.0574 | 3.9702 | 2.3451
NQ-MK-Proserpine Bowen | PROS-KECR-1_Proserpine No 1 66 kV | Loading (MW) | 2.9453 | 3.8163 | 2.2628 | 2.9203 | 3.784 | 2.2437 | 2.9203 | 3.784 | 2.2437 | 2.9203 | 3.784 | 2.2437 | 2.9453 | 3.8163 | 2.2628
NQ-MK-Proserpine Bowen | PROS-KECR-1_Proserpine No 1 66 kV | Power Factor | 0.96331 | 0.96122 | 0.96493 | 0.96337 | 0.96132 | 0.96498 | 0.96337 | 0.96132 | 0.96498 | 0.96337 | 0.96132 | 0.96498 | 0.9633 | 0.96121 | 0.96493
NQ-MK-Proserpine Bowen | PROS-KECR-1_Proserpine No 1 66 kV | Rating (A) | 177 | 236 | 226 | 177 | 236 | 226 | 177 | 236 | 226 | 177 | 236 | 226 | 177 | 236 | 226
NQ-MK-Proserpine Bowen | PROS-KECR-1_Proserpine No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-MK-Proserpine Bowen | PROS-KECR-1_Proserpine No 1 66 kV | Min Voltage at Constrained Conductor | 66.4039 | 66.5441 | 66.4275 | 66.4125 | 66.6128 | 66.4779 | 66.4122 | 66.621 | 66.4816 | 66.4093 | 66.6076 | 66.4778 | 66.3954 | 66.528 | 66.4481
NQ-MK-Proserpine Bowen | PROS-KECR-1_Proserpine No 1 66 kV | Contingency Outage | 119_Cannonvale No 1 66 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | 119_Cannonvale No 1 66 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | 119_Cannonvale No 1 66 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | 119_Cannonvale No 1 66 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | 119_Cannonvale No 1 66 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV
NQ-MK-Proserpine Bowen | PROS-KECR-2_Proserpine No 2 66 kV | % of Rated A | 30.08% | 29.25% | 18.06% | 29.82% | 28.97% | 17.89% | 29.82% | 28.96% | 17.89% | 29.82% | 28.97% | 17.89% | 30.09% | 29.26% | 18.05%
NQ-MK-Proserpine Bowen | PROS-KECR-2_Proserpine No 2 66 kV | Limiting Line Name | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1
NQ-MK-Proserpine Bowen | PROS-KECR-2_Proserpine No 2 66 kV | Loading (A) | 53.2444 | 69.0258 | 40.8101 | 52.7821 | 68.3616 | 40.4308 | 52.7825 | 68.353 | 40.4285 | 52.7847 | 68.3671 | 40.4309 | 53.2513 | 69.0429 | 40.7973
NQ-MK-Proserpine Bowen | PROS-KECR-2_Proserpine No 2 66 kV | Loading (MVA) | 6.1237 | 7.9555 | 4.6953 | 6.0713 | 7.8871 | 4.6552 | 6.0713 | 7.887 | 4.6552 | 6.0713 | 7.8871 | 4.6552 | 6.1237 | 7.9555 | 4.6953
NQ-MK-Proserpine Bowen | PROS-KECR-2_Proserpine No 2 66 kV | Loading (MW) | 5.8996 | 7.6478 | 4.531 | 5.8495 | 7.5828 | 4.4925 | 5.8495 | 7.5828 | 4.4925 | 5.8495 | 7.5828 | 4.4925 | 5.8996 | 7.6478 | 4.531
NQ-MK-Proserpine Bowen | PROS-KECR-2_Proserpine No 2 66 kV | Power Factor | 0.96338 | 0.96131 | 0.96499 | 0.96344 | 0.96141 | 0.96504 | 0.96344 | 0.96141 | 0.96504 | 0.96344 | 0.96141 | 0.96504 | 0.96338 | 0.96131 | 0.96499
NQ-MK-Proserpine Bowen | PROS-KECR-2_Proserpine No 2 66 kV | Rating (A) | 177 | 236 | 226 | 177 | 236 | 226 | 177 | 236 | 226 | 177 | 236 | 226 | 177 | 236 | 226
NQ-MK-Proserpine Bowen | PROS-KECR-2_Proserpine No 2 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-MK-Proserpine Bowen | PROS-KECR-2_Proserpine No 2 66 kV | Min Voltage at Constrained Conductor | 66.4014 | 66.5408 | 66.4256 | 66.41 | 66.6095 | 66.476 | 66.4097 | 66.6178 | 66.4797 | 66.4068 | 66.6044 | 66.4759 | 66.3929 | 66.5247 | 66.4462
NQ-MK-Proserpine Bowen | PROS-KECR-2_Proserpine No 2 66 kV | Contingency Outage | 119_Cannonvale No 1 66 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | 119_Cannonvale No 1 66 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | 119_Cannonvale No 1 66 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | 119_Cannonvale No 1 66 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV | 119_Cannonvale No 1 66 kV | ME-PR-1_Merinda - Proserpine No 1 66 kV | ME-BN-1_Merinda - Bowen No 1 66 kV
NQ-Townsville Burdekin West | 6127_Bohle-Black River 1 66 kV | % of Rated A | 31.05% | 39.27% | 20.74% | 31.31% | 39.62% | 20.91% | 31.43% | 39.57% | 21.27% | 31.97% | 40.27% | 21.62% | 32.62% | 41.11% | 22.03%
NQ-Townsville Burdekin West | 6127_Bohle-Black River 1 66 kV | Limiting Line Name | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1
NQ-Townsville Burdekin West | 6127_Bohle-Black River 1 66 kV | Loading (A) | 226.3349 | 307.5013 | 147.2619 | 228.2566 | 310.2059 | 148.4711 | 229.1376 | 309.8077 | 150.9964 | 233.0883 | 315.3337 | 153.4807 | 237.7812 | 321.9279 | 156.3913
NQ-Townsville Burdekin West | 6127_Bohle-Black River 1 66 kV | Loading (MVA) | 26.4737 | 35.7044 | 17.522 | 26.6996 | 36.0159 | 17.6663 | 26.9223 | 36.3154 | 17.8135 | 27.3748 | 36.9398 | 18.1023 | 27.9035 | 37.6701 | 18.4375
NQ-Townsville Burdekin West | 6127_Bohle-Black River 1 66 kV | Loading (MW) | 26.2982 | 35.3252 | 17.4588 | 26.5202 | 35.6278 | 17.6017 | 26.7413 | 35.9271 | 17.7455 | 27.1855 | 36.5328 | 18.0315 | 27.704 | 37.2398 | 18.3646
NQ-Townsville Burdekin West | 6127_Bohle-Black River 1 66 kV | Power Factor | 0.99337 | 0.98938 | 0.99639 | 0.99328 | 0.98922 | 0.99635 | 0.99328 | 0.98931 | 0.99619 | 0.99309 | 0.98898 | 0.99609 | 0.99285 | 0.98857 | 0.99605
NQ-Townsville Burdekin West | 6127_Bohle-Black River 1 66 kV | Rating (A) | 729 | 783 | 710 | 729 | 783 | 710 | 729 | 783 | 710 | 729 | 783 | 710 | 729 | 783 | 710
NQ-Townsville Burdekin West | 6127_Bohle-Black River 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Townsville Burdekin West | 6127_Bohle-Black River 1 66 kV | Min Voltage at Constrained Conductor | 67.5306 | 67.0363 | 68.6961 | 67.5334 | 67.0317 | 68.6975 | 67.8348 | 67.6759 | 68.1114 | 67.806 | 67.6332 | 68.0954 | 67.7515 | 67.5577 | 68.0656
NQ-Townsville Burdekin West | 6127_Bohle-Black River 1 66 kV | Contingency Outage | 6266_Bohle-Black River No 2 66 kV | 6266_Bohle-Black River No 2 66 kV | 6266_Bohle-Black River No 2 66 kV | 6266_Bohle-Black River No 2 66 kV | 6266_Bohle-Black River No 2 66 kV | 6266_Bohle-Black River No 2 66 kV | 6266_Bohle-Black River No 2 66 kV | 6266_Bohle-Black River No 2 66 kV | 6266_Bohle-Black River No 2 66 kV | 6266_Bohle-Black River No 2 66 kV | 6266_Bohle-Black River No 2 66 kV | 6266_Bohle-Black River No 2 66 kV | 6266_Bohle-Black River No 2 66 kV | 6266_Bohle-Black River No 2 66 kV | 6266_Bohle-Black River No 2 66 kV
NQ-Townsville Burdekin West | 6266_Bohle-Black River No 2 66 kV | % of Rated A | 31.05% | 39.27% | 20.74% | 31.31% | 39.62% | 20.91% | 31.43% | 39.57% | 21.27% | 31.97% | 40.27% | 21.62% | 32.62% | 41.12% | 22.03%
NQ-Townsville Burdekin West | 6266_Bohle-Black River No 2 66 kV | Limiting Line Name | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1
NQ-Townsville Burdekin West | 6266_Bohle-Black River No 2 66 kV | Loading (A) | 226.3412 | 307.5071 | 147.2666 | 228.263 | 310.2116 | 148.4758 | 229.1439 | 309.8134 | 151.0012 | 233.0947 | 315.3393 | 153.4856 | 237.7876 | 321.9333 | 156.3963
NQ-Townsville Burdekin West | 6266_Bohle-Black River No 2 66 kV | Loading (MVA) | 26.4749 | 35.7065 | 17.5226 | 26.7008 | 36.0181 | 17.6669 | 26.9235 | 36.3175 | 17.8141 | 27.3761 | 36.942 | 18.1029 | 27.9049 | 37.6725 | 18.4382
NQ-Townsville Burdekin West | 6266_Bohle-Black River No 2 66 kV | Loading (MW) | 26.299 | 35.3267 | 17.4591 | 26.5211 | 35.6293 | 17.6021 | 26.7421 | 35.9287 | 17.7459 | 27.1864 | 36.5344 | 18.0319 | 27.7049 | 37.2414 | 18.365
NQ-Townsville Burdekin West | 6266_Bohle-Black River No 2 66 kV | Power Factor | 0.99336 | 0.98936 | 0.99638 | 0.99327 | 0.98921 | 0.99633 | 0.99326 | 0.98929 | 0.99617 | 0.99307 | 0.98896 | 0.99608 | 0.99283 | 0.98856 | 0.99603
NQ-Townsville Burdekin West | 6266_Bohle-Black River No 2 66 kV | Rating (A) | 729 | 783 | 710 | 729 | 783 | 710 | 729 | 783 | 710 | 729 | 783 | 710 | 729 | 783 | 710
NQ-Townsville Burdekin West | 6266_Bohle-Black River No 2 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Townsville Burdekin West | 6266_Bohle-Black River No 2 66 kV | Min Voltage at Constrained Conductor | 67.5266 | 67.0312 | 68.6934 | 67.5294 | 67.0266 | 68.6948 | 67.8308 | 67.6708 | 68.1087 | 67.8019 | 67.628 | 68.0926 | 67.7474 | 67.5524 | 68.0627
NQ-Townsville Burdekin West | 6266_Bohle-Black River No 2 66 kV | Contingency Outage | 6127_Bohle-Black River 1 66 kV | 6127_Bohle-Black River 1 66 kV | 6127_Bohle-Black River 1 66 kV | 6127_Bohle-Black River 1 66 kV | 6127_Bohle-Black River 1 66 kV | 6127_Bohle-Black River 1 66 kV | 6127_Bohle-Black River 1 66 kV | 6127_Bohle-Black River 1 66 kV | 6127_Bohle-Black River 1 66 kV | 6127_Bohle-Black River 1 66 kV | 6127_Bohle-Black River 1 66 kV | 6127_Bohle-Black River 1 66 kV | 6127_Bohle-Black River 1 66 kV | 6127_Bohle-Black River 1 66 kV | 6127_Bohle-Black River 1 66 kV
NQ-Townsville Burdekin West | 6299_Townsville Port 66 kV | % of Rated A | 44.33% | 40.91% | 31.35% | 44.5% | 41.07% | 31.41% | 42.49% | 38.96% | 29.82% | 42.66% | 39.14% | 29.93% | 43.17% | 39.61% | 30.24%
NQ-Townsville Burdekin West | 6299_Townsville Port 66 kV | Limiting Line Name | TR_LINE 96490_1 | TR_LINE 96490_1 | TR_LINE 96490_1 | TR_LINE 96490_1 | TR_LINE 96490_1 | TR_LINE 96490_1 | TR_LINE 96490_1 | TR_LINE 96490_1 | TR_LINE 96490_1 | TR_LINE 96490_1 | TR_LINE 96490_1 | TR_LINE 96490_1 | TR_LINE 96490_1 | TR_LINE 96490_1 | TR_LINE 96490_1
NQ-Townsville Burdekin West | 6299_Townsville Port 66 kV | Loading (A) | 484.0396 | 492.955 | 347.0373 | 485.9764 | 494.9017 | 347.7485 | 464.0211 | 469.5011 | 330.0545 | 465.8517 | 471.6477 | 331.3287 | 471.3784 | 477.3369 | 334.7858
NQ-Townsville Burdekin West | 6299_Townsville Port 66 kV | Loading (MVA) | 57.6971 | 58.7466 | 41.7551 | 57.916 | 58.967 | 41.8353 | 55.4717 | 56.255 | 39.4467 | 55.6832 | 56.5026 | 39.5959 | 56.3195 | 57.1589 | 40.0014
NQ-Townsville Burdekin West | 6299_Townsville Port 66 kV | Loading (MW) | 57.3357 | 58.3789 | 40.3224 | 57.5707 | 58.6136 | 40.4286 | 54.8895 | 55.401 | 39.0217 | 55.1114 | 55.6659 | 39.1773 | 55.783 | 56.3669 | 39.5988
NQ-Townsville Burdekin West | 6299_Townsville Port 66 kV | Power Factor | 0.99373 | 0.99374 | 0.96568 | 0.99403 | 0.994 | 0.96637 | 0.9895 | 0.98481 | 0.98922 | 0.98973 | 0.98519 | 0.98942 | 0.99047 | 0.98614 | 0.98993
NQ-Townsville Burdekin West | 6299_Townsville Port 66 kV | Rating (A) | 1092 | 1205 | 1107 | 1092 | 1205 | 1107 | 1092 | 1205 | 1107 | 1092 | 1205 | 1107 | 1092 | 1205 | 1107
NQ-Townsville Burdekin West | 6299_Townsville Port 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Townsville Burdekin West | 6299_Townsville Port 66 kV | Min Voltage at Constrained Conductor | 68.8196 | 68.8041 | 69.4659 | 68.8054 | 68.7906 | 69.4569 | 69.0197 | 69.1772 | 69.0024 | 69.0106 | 69.1655 | 68.9971 | 68.9808 | 69.1349 | 68.9838
NQ-Townsville Burdekin West | 6299_Townsville Port 66 kV | Contingency Outage | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV
NQ-Townsville Burdekin West | 6312_Merinda - Home Hill 66 kV | % of Rated A | 8.136% | 7.259% | 5.242% | 7.068% | 6.072% | 4.995% | 7.067% | 6.071% | 4.995% | 7.068% | 6.072% | 4.995% | 7.072% | 6.074% | 4.995%
NQ-Townsville Burdekin West | 6312_Merinda - Home Hill 66 kV | Limiting Line Name | TR_LINE 77683_1 | TR_LINE 77683_1 | TR_LINE 32515_1 | TR_LINE 180012_1 | TR_LINE 77683_1 | TR_LINE 32515_1 | TR_LINE 180012_1 | TR_LINE 77683_1 | TR_LINE 32515_1 | TR_LINE 180012_1 | TR_LINE 77683_1 | TR_LINE 32515_1 | TR_LINE 180012_1 | TR_LINE 77683_1 | TR_LINE 32515_1
NQ-Townsville Burdekin West | 6312_Merinda - Home Hill 66 kV | Loading (A) | 20.0149 | 19.8177 | 13.7335 | 12.3685 | 16.5768 | 13.0873 | 12.3676 | 16.575 | 13.0876 | 12.3685 | 16.5763 | 13.0877 | 12.3756 | 16.5831 | 13.0861
NQ-Townsville Burdekin West | 6312_Merinda - Home Hill 66 kV | Loading (MVA) | 2.2405 | 2.2382 | 1.6004 | 1.3855 | 1.8513 | 1.5261 | 1.3856 | 1.8516 | 1.5262 | 1.3855 | 1.8514 | 1.5262 | 1.3852 | 1.8505 | 1.5257
NQ-Townsville Burdekin West | 6312_Merinda - Home Hill 66 kV | Loading (MW) | 2.1597 | 2.1506 | 1.124 | 1.2512 | 1.6582 | 0.88173 | 1.2512 | 1.6581 | 0.88173 | 1.2512 | 1.6582 | 0.88173 | 1.2512 | 1.6582 | 0.88173
NQ-Townsville Burdekin West | 6312_Merinda - Home Hill 66 kV | Power Factor | 0.96393 | 0.96087 | 0.70233 | 0.90303 | 0.89565 | 0.57776 | 0.90297 | 0.89553 | 0.57772 | 0.90303 | 0.89561 | 0.57772 | 0.90324 | 0.89606 | 0.57792
NQ-Townsville Burdekin West | 6312_Merinda - Home Hill 66 kV | Rating (A) | 246 | 273 | 262 | 175 | 273 | 262 | 175 | 273 | 262 | 175 | 273 | 262 | 175 | 273 | 262
NQ-Townsville Burdekin West | 6312_Merinda - Home Hill 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Townsville Burdekin West | 6312_Merinda - Home Hill 66 kV | Min Voltage at Constrained Conductor | 64.4514 | 65.0309 | 67.2807 | 64.675 | 64.3972 | 67.3246 | 64.6841 | 64.4128 | 67.3274 | 64.6748 | 64.4015 | 67.3279 | 64.6216 | 64.3431 | 67.3124
NQ-Townsville Burdekin West | 6312_Merinda - Home Hill 66 kV | Contingency Outage | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV
NQ-Townsville Burdekin West | 6325_Oonoonba-Stuart 66 kV | % of Rated A | 82.19% | 83.18% | 63.01% | 81.91% | 82.64% | 62.69% | 84.99% | 85.73% | 64.11% | 85.14% | 85.96% | 64.17% | 85.9% | 86.78% | 64.6%
NQ-Townsville Burdekin West | 6325_Oonoonba-Stuart 66 kV | Limiting Line Name | TR_LINE 31738_1 | TR_LINE 31738_1 | TR_LINE 31738_1 | TR_LINE 31738_1 | TR_LINE 31738_1 | TR_LINE 31738_1 | TR_LINE 31738_1 | TR_LINE 31738_1 | TR_LINE 31738_1 | TR_LINE 31738_1 | TR_LINE 31738_1 | TR_LINE 31738_1 | TR_LINE 31738_1 | TR_LINE 31738_1 | TR_LINE 31738_1
NQ-Townsville Burdekin West | 6325_Oonoonba-Stuart 66 kV | Loading (A) | 267.1279 | 276.1637 | 184.6301 | 266.2208 | 274.3786 | 183.6817 | 276.2059 | 284.628 | 187.843 | 276.6989 | 285.3842 | 188.0317 | 279.1846 | 288.1066 | 189.2797
NQ-Townsville Burdekin West | 6325_Oonoonba-Stuart 66 kV | Loading (MVA) | 31.8352 | 32.7897 | 22.0939 | 31.7272 | 32.5775 | 21.9808 | 33.0448 | 34.0872 | 22.4209 | 33.0996 | 34.1724 | 22.4414 | 33.3865 | 34.486 | 22.5858
NQ-Townsville Burdekin West | 6325_Oonoonba-Stuart 66 kV | Loading (MW) | 31.0545 | 31.461 | 19.0111 | 30.9297 | 31.2306 | 18.8735 | 32.2547 | 33.2471 | 21.8733 | 32.313 | 33.3397 | 21.8937 | 32.6206 | 33.6797 | 22.0449
NQ-Townsville Burdekin West | 6325_Oonoonba-Stuart 66 kV | Power Factor | 0.97544 | 0.95942 | 0.86041 | 0.97482 | 0.9586 | 0.85857 | 0.97605 | 0.97531 | 0.97555 | 0.9762 | 0.97559 | 0.97557 | 0.97702 | 0.97658 | 0.97603
NQ-Townsville Burdekin West | 6325_Oonoonba-Stuart 66 kV | Rating (A) | 325 | 332 | 293 | 325 | 332 | 293 | 325 | 332 | 293 | 325 | 332 | 293 | 325 | 332 | 293
NQ-Townsville Burdekin West | 6325_Oonoonba-Stuart 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Townsville Burdekin West | 6325_Oonoonba-Stuart 66 kV | Min Voltage at Constrained Conductor | 68.8001 | 68.5452 | 69.088 | 68.8005 | 68.5447 | 69.0895 | 69.0669 | 69.1374 | 68.908 | 69.0581 | 69.1264 | 68.9019 | 69.0365 | 69.1015 | 68.8879
NQ-Townsville Burdekin West | 6325_Oonoonba-Stuart 66 kV | Contingency Outage | ST-RP-1_Stuart-Ross Plains 66 kV | GA-TP-1_Garbutt-Townsville Port 1 66 kV | GA-TP-1_Garbutt-Townsville Port 1 66 kV | ST-RP-1_Stuart-Ross Plains 66 kV | GA-TP-1_Garbutt-Townsville Port 1 66 kV | GA-TP-1_Garbutt-Townsville Port 1 66 kV | ST-RP-1_Stuart-Ross Plains 66 kV | ST-RP-1_Stuart-Ross Plains 66 kV | GA-TP-1_Garbutt-Townsville Port 1 66 kV | ST-RP-1_Stuart-Ross Plains 66 kV | ST-RP-1_Stuart-Ross Plains 66 kV | GA-TP-1_Garbutt-Townsville Port 1 66 kV | ST-RP-1_Stuart-Ross Plains 66 kV | ST-RP-1_Stuart-Ross Plains 66 kV | GA-TP-1_Garbutt-Townsville Port 1 66 kV
NQ-Townsville Burdekin West | 6382 JACR-HUGH 132kV | % of Rated A | 57.31% | 67.07% | 46.13% | 56.35% | 65.91% | 45.68% | 68.63% | 81.35% | 51.36% | 68.61% | 81.34% | 51.34% | 68.29% | 81.09% | 51.07%
NQ-Townsville Burdekin West | 6382 JACR-HUGH 132kV | Limiting Line Name | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line
NQ-Townsville Burdekin West | 6382 JACR-HUGH 132kV | Loading (A) | 81.3872 | 95.2426 | 65.4983 | 80.0152 | 93.5916 | 64.8655 | 97.4568 | 115.5196 | 72.9321 | 97.4258 | 115.4964 | 72.9042 | 96.974 | 115.1473 | 72.5201
NQ-Townsville Burdekin West | 6382 JACR-HUGH 132kV | Loading (MVA) | 9.5064 | 11.1023 | 7.674 | 9.348 | 10.9118 | 7.6011 | 11.3528 | 13.4205 | 8.53 | 11.3491 | 13.4177 | 8.5265 | 11.2943 | 13.3742 | 8.4805
NQ-Townsville Burdekin West | 6382 JACR-HUGH 132kV | Loading (MW) | 8.9448 | 10.8364 | 6.4154 | 8.7483 | 10.6213 | 6.3051 | 11.1656 | 13.3861 | 7.687 | 11.1629 | 13.3836 | 7.6852 | 11.1309 | 13.3499 | 7.6667
NQ-Townsville Burdekin West | 6382 JACR-HUGH 132kV | Power Factor | 0.94092 | 0.97605 | 0.83599 | 0.93584 | 0.97337 | 0.82949 | 0.98348 | 0.99681 | 0.90117 | 0.98357 | 0.99685 | 0.90132 | 0.98553 | 0.99768 | 0.90403
NQ-Townsville Burdekin West | 6382 JACR-HUGH 132kV | Rating (A) | 142 | 142 | 142 | 142 | 142 | 142 | 142 | 142 | 142 | 142 | 142 | 142 | 142 | 142 | 142
NQ-Townsville Burdekin West | 6382 JACR-HUGH 132kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Townsville Burdekin West | 6382 JACR-HUGH 132kV | Min Voltage at Constrained Conductor | 67.0107 | 66.5656 | 67.6176 | 67.055 | 66.6123 | 67.6446 | 66.4327 | 65.8638 | 67.2955 | 66.4313 | 65.8624 | 67.2937 | 66.4009 | 65.8278 | 67.2766
NQ-Townsville Burdekin West | 6382 JACR-HUGH 132kV | Contingency Outage | CR-HU-1_Cape River-Hughenden No 1 66 kV | CR-HU-1_Cape River-Hughenden No 1 66 kV | CR-HU-1_Cape River-Hughenden No 1 66 kV | CR-HU-1_Cape River-Hughenden No 1 66 kV | CR-HU-1_Cape River-Hughenden No 1 66 kV | CR-HU-1_Cape River-Hughenden No 1 66 kV | CR-HU-1_Cape River-Hughenden No 1 66 kV | CR-HU-1_Cape River-Hughenden No 1 66 kV | CR-HU-1_Cape River-Hughenden No 1 66 kV | CR-HU-1_Cape River-Hughenden No 1 66 kV | CR-HU-1_Cape River-Hughenden No 1 66 kV | CR-HU-1_Cape River-Hughenden No 1 66 kV | CR-HU-1_Cape River-Hughenden No 1 66 kV | CR-HU-1_Cape River-Hughenden No 1 66 kV | CR-HU-1_Cape River-Hughenden No 1 66 kV
NQ-Townsville Burdekin West | 6383 CARI-CPRE 66kV | % of Rated A | 26.76% | 29.12% | 22.36% | 57.03% | 28.76% | 21.49% | 34.39% | 41.21% | 28% | 34.4% | 41.28% | 28.12% | 34.35% | 41.29% | 28.52%
NQ-Townsville Burdekin West | 6383 CARI-CPRE 66kV | Limiting Line Name | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1
NQ-Townsville Burdekin West | 6383 CARI-CPRE 66kV | Loading (A) | 83.5021 | 104.2444 | 73.5555 | 177.9264 | 102.9744 | 70.6899 | 107.2824 | 147.548 | 92.1233 | 107.3346 | 147.7984 | 92.5299 | 107.1664 | 147.8132 | 93.8382
NQ-Townsville Burdekin West | 6383 CARI-CPRE 66kV | Loading (MVA) | 9.4866 | 11.8242 | 8.3058 | 19.0044 | 11.6773 | 7.9853 | 12.1678 | 16.5363 | 10.3803 | 12.1734 | 16.5635 | 10.4254 | 12.1534 | 16.5625 | 10.5704
NQ-Townsville Burdekin West | 6383 CARI-CPRE 66kV | Loading (MW) | 9.209 | 11.1675 | 5.159 | 7.8932 | 10.9449 | 5.0753 | 11.5086 | 10.1608 | 6.0815 | 11.5058 | 10.1594 | 6.0814 | 11.4722 | 10.129 | 6.0716
NQ-Townsville Burdekin West | 6383 CARI-CPRE 66kV | Power Factor | 0.97073 | 0.94445 | 0.62114 | 0.41524 | 0.93727 | 0.63557 | 0.94581 | 0.61437 | 0.58585 | 0.94516 | 0.61329 | 0.58331 | 0.94394 | 0.61148 | 0.57438
NQ-Townsville Burdekin West | 6383 CARI-CPRE 66kV | Rating (A) | 312 | 358 | 329 | 312 | 358 | 329 | 312 | 358 | 329 | 312 | 358 | 329 | 312 | 358 | 329
NQ-Townsville Burdekin West | 6383 CARI-CPRE 66kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Townsville Burdekin West | 6383 CARI-CPRE 66kV | Min Voltage at Constrained Conductor | 65.591 | 65.4866 | 65.1935 | 61.6619 | 65.4709 | 65.2191 | 65.4812 | 64.7051 | 65.0549 | 65.4792 | 64.7017 | 65.0506 | 65.4743 | 64.6915 | 65.0354
NQ-Townsville Burdekin West | 6383 CARI-CPRE 66kV | Contingency Outage | CR-HU-1_Cape River-Hughenden No 1 66 kV | CR-HU-1_Cape River-Hughenden No 1 66 kV | 7182 Ross - Milchester | 7182 Ross - Milchester | CR-HU-1_Cape River-Hughenden No 1 66 kV | 7182 Ross - Milchester | CR-HU-1_Cape River-Hughenden No 1 66 kV | MR-CR-1_Millchester-Cape River 1 66 kV | 7182 Ross - Milchester | CR-HU-1_Cape River-Hughenden No 1 66 kV | MR-CR-1_Millchester-Cape River 1 66 kV | 7182 Ross - Milchester | CR-HU-1_Cape River-Hughenden No 1 66 kV | MR-CR-1_Millchester-Cape River 1 66 kV | 7182 Ross - Milchester
NQ-Townsville Burdekin West | 7182 Ross - Milchester | % of Rated A | 47.48% | 44.55% | 35.43% | 46.94% | 44.61% | 35.14% | 49.96% | 47.77% | 36.7% | 50.02% | 47.82% | 36.71% | 50.18% | 47.97% | 36.81%
NQ-Townsville Burdekin West | 7182 Ross - Milchester | Limiting Line Name | TR_LINE 76326_1 | TR_LINE 76326_1 | TR_LINE 76326_1 | TR_LINE 76326_1 | TR_LINE 76326_1 | TR_LINE 76326_1 | TR_LINE 76326_1 | TR_LINE 76326_1 | TR_LINE 76326_1 | TR_LINE 76326_1 | TR_LINE 76326_1 | TR_LINE 76326_1 | TR_LINE 76326_1 | TR_LINE 76326_1 | TR_LINE 76326_1
NQ-Townsville Burdekin West | 7182 Ross - Milchester | Loading (A) | 148.1224 | 159.505 | 116.5587 | 146.4455 | 159.7133 | 115.5962 | 155.8905 | 171.0019 | 120.7437 | 156.0607 | 171.2124 | 120.7672 | 156.5722 | 171.7403 | 121.1067
NQ-Townsville Burdekin West | 7182 Ross - Milchester | Loading (MVA) | 35.0718 | 37.6942 | 27.9902 | 34.6891 | 37.6359 | 27.7658 | 36.8604 | 40.2187 | 28.976 | 36.8969 | 40.2635 | 28.9799 | 37.009 | 40.3777 | 29.056
NQ-Townsville Burdekin West | 7182 Ross - Milchester | Loading (MW) | 34.2927 | 36.9043 | 25.6946 | 33.8956 | 37.1354 | 25.4431 | 36.059 | 39.6805 | 26.668 | 36.1035 | 39.732 | 26.684 | 36.2314 | 39.8584 | 26.7898
NQ-Townsville Burdekin West | 7182 Ross - Milchester | Power Factor | 0.97779 | 0.97904 | 0.91799 | 0.97712 | 0.9867 | 0.91634 | 0.97826 | 0.98662 | 0.92035 | 0.9785 | 0.9868 | 0.92078 | 0.97899 | 0.98714 | 0.92201
NQ-Townsville Burdekin West | 7182 Ross - Milchester | Rating (A) | 312 | 358 | 329 | 312 | 358 | 329 | 312 | 358 | 329 | 312 | 358 | 329 | 312 | 358 | 329
NQ-Townsville Burdekin West | 7182 Ross - Milchester | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Townsville Burdekin West | 7182 Ross - Milchester | Min Voltage at Constrained Conductor | 136.0804 | 135.7576 | 138.5465 | 136.1512 | 135.2524 | 138.5892 | 135.8574 | 134.9416 | 138.4406 | 135.8396 | 134.9215 | 138.4299 | 135.7989 | 134.8793 | 138.3972
NQ-Townsville Burdekin West | 7182 Ross - Milchester | Contingency Outage | ST-WO-1_Stuart-Woodstock South 1 66 kV | ST-WO-1_Stuart-Woodstock South 1 66 kV | ST-WO-1_Stuart-Woodstock South 1 66 kV | ST-WO-1_Stuart-Woodstock South 1 66 kV | ST-WO-1_Stuart-Woodstock South 1 66 kV | ST-WO-1_Stuart-Woodstock South 1 66 kV | ST-WO-1_Stuart-Woodstock South 1 66 kV | ST-WO-1_Stuart-Woodstock South 1 66 kV | ST-WO-1_Stuart-Woodstock South 1 66 kV | ST-WO-1_Stuart-Woodstock South 1 66 kV | ST-WO-1_Stuart-Woodstock South 1 66 kV | ST-WO-1_Stuart-Woodstock South 1 66 kV | ST-WO-1_Stuart-Woodstock South 1 66 kV | ST-WO-1_Stuart-Woodstock South 1 66 kV | ST-WO-1_Stuart-Woodstock South 1 66 kV
NQ-Townsville Burdekin West | 7460 CPRE-JACR 132kV | % of Rated A | 33.15% | 23.3% | 16.66% | 32.71% | 23.03% | 16.44% | 38.11% | 27.04% | 18.85% | 38.1% | 27.04% | 18.86% | 38% | 26.97% | 18.86%
NQ-Townsville Burdekin West | 7460 CPRE-JACR 132kV | Limiting Line Name | TR_LINE 51339257_1 | TR_LINE 51339257_1 | TR_LINE 51339257_1 | TR_LINE 51339257_1 | TR_LINE 51339257_1 | TR_LINE 51339257_1 | TR_LINE 51339257_1 | TR_LINE 51339257_1 | TR_LINE 51339257_1 | TR_LINE 51339257_1 | TR_LINE 51339257_1 | TR_LINE 51339257_1 | TR_LINE 51339257_1 | TR_LINE 51339257_1 | TR_LINE 51339257_1
NQ-Townsville Burdekin West | 7460 CPRE-JACR 132kV | Loading (A) | 57.3463 | 64.7682 | 46.3082 | 56.5797 | 64.0148 | 45.7 | 65.9255 | 75.1791 | 52.4035 | 65.9192 | 75.1763 | 52.4356 | 65.7382 | 74.9813 | 52.428
NQ-Townsville Burdekin West | 7460 CPRE-JACR 132kV | Loading (MVA) | 13.1211 | 14.8135 | 10.6243 | 12.9464 | 14.6394 | 10.4878 | 15.0774 | 17.1806 | 11.9961 | 15.0758 | 17.1796 | 12.0028 | 15.0334 | 17.1338 | 11.9992
NQ-Townsville Burdekin West | 7460 CPRE-JACR 132kV | Loading (MW) | 9.1621 | 11.1191 | 6.5564 | 8.9594 | 10.8967 | 6.4427 | 11.4599 | 13.7763 | 7.8664 | 11.4571 | 13.7738 | 7.8647 | 11.4235 | 13.7382 | 7.846
NQ-Townsville Burdekin West | 7460 CPRE-JACR 132kV | Power Factor | 0.69828 | 0.75061 | 0.61711 | 0.69204 | 0.74434 | 0.6143 | 0.76007 | 0.80185 | 0.65574 | 0.75997 | 0.80175 | 0.65524 | 0.75988 | 0.80182 | 0.65388
NQ-Townsville Burdekin West | 7460 CPRE-JACR 132kV | Rating (A) | 173 | 278 | 278 | 173 | 278 | 278 | 173 | 278 | 278 | 173 | 278 | 278 | 173 | 278 | 278
NQ-Townsville Burdekin West | 7460 CPRE-JACR 132kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Townsville Burdekin West | 7460 CPRE-JACR 132kV | Min Voltage at Constrained Conductor | 132.0999 | 132.0485 | 132.4586 | 132.1071 | 132.0329 | 132.4973 | 132.0426 | 131.941 | 132.1658 | 132.0407 | 131.9386 | 132.1583 | 132.0319 | 131.929 | 132.1375
NQ-Townsville Burdekin West | 7460 CPRE-JACR 132kV | Contingency Outage | CR-HU-1_Cape River-Hughenden No 1 66 kV | CR-HU-1_Cape River-Hughenden No 1 66 kV | CR-HU-1_Cape River-Hughenden No 1 66 kV | CR-HU-1_Cape River-Hughenden No 1 66 kV | CR-HU-1_Cape River-Hughenden No 1 66 kV | CR-HU-1_Cape River-Hughenden No 1 66 kV | CR-HU-1_Cape River-Hughenden No 1 66 kV | CR-HU-1_Cape River-Hughenden No 1 66 kV | CR-HU-1_Cape River-Hughenden No 1 66 kV | CR-HU-1_Cape River-Hughenden No 1 66 kV | CR-HU-1_Cape River-Hughenden No 1 66 kV | CR-HU-1_Cape River-Hughenden No 1 66 kV | CR-HU-1_Cape River-Hughenden No 1 66 kV | CR-HU-1_Cape River-Hughenden No 1 66 kV | CR-HU-1_Cape River-Hughenden No 1 66 kV
NQ-Townsville Burdekin West | AV-CB-1_Aitkenvale-Cranbrook 66 kV | % of Rated A | 56.45% | 43.01% | 27.83% | 55.66% | 42.42% | 27.47% | 54.78% | 41.74% | 27.33% | 54.53% | 41.56% | 27.21% | 54.81% | 41.77% | 27.34%
NQ-Townsville Burdekin West | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Limiting Line Name | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1
NQ-Townsville Burdekin West | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Loading (A) | 187.9916 | 167.7472 | 101.0255 | 185.3599 | 165.4246 | 99.7069 | 182.4213 | 162.7944 | 99.2167 | 181.5953 | 162.0728 | 98.7867 | 182.5334 | 162.9189 | 99.2451
NQ-Townsville Burdekin West | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Loading (MVA) | 22.0666 | 19.8196 | 12.0635 | 21.7656 | 19.5511 | 11.9081 | 21.5657 | 19.3743 | 11.7994 | 21.4655 | 19.2849 | 11.7474 | 21.5657 | 19.3741 | 11.7989
NQ-Townsville Burdekin West | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Loading (MW) | 22.0628 | 19.8 | 11.8681 | 21.7605 | 19.5289 | 11.706 | 21.5586 | 19.3479 | 11.5978 | 21.4579 | 19.2576 | 11.5438 | 21.5588 | 19.348 | 11.5978
NQ-Townsville Burdekin West | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Power Factor | 0.99982 | 0.999 | 0.98381 | 0.99976 | 0.99886 | 0.98303 | 0.99966 | 0.99863 | 0.98292 | 0.99964 | 0.99858 | 0.98266 | 0.99967 | 0.99865 | 0.98296
NQ-Townsville Burdekin West | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Rating (A) | 333 | 390 | 363 | 333 | 390 | 363 | 333 | 390 | 363 | 333 | 390 | 363 | 333 | 390 | 363
NQ-Townsville Burdekin West | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Townsville Burdekin West | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Min Voltage at Constrained Conductor | 67.7576 | 68.2046 | 68.9373 | 67.7825 | 68.2255 | 68.9492 | 68.2423 | 68.7012 | 68.6574 | 68.2343 | 68.6885 | 68.6528 | 68.2004 | 68.6479 | 68.6352
NQ-Townsville Burdekin West | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Contingency Outage | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV
NQ-Townsville Burdekin West | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | % of Rated A | 64.85% | 53.78% | 35.72% | 63.95% | 53.04% | 35.29% | 63.26% | 52.37% | 35.41% | 63.09% | 52.24% | 35.32% | 63.47% | 52.56% | 35.5%
NQ-Townsville Burdekin West | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Limiting Line Name | TR_LINE 34618_1 | TR_LINE 34618_1 | TR_LINE 34618_1 | TR_LINE 34618_1 | TR_LINE 34618_1 | TR_LINE 34618_1 | TR_LINE 34618_1 | TR_LINE 34618_1 | TR_LINE 34618_1 | TR_LINE 34618_1 | TR_LINE 34618_1 | TR_LINE 34618_1 | TR_LINE 34618_1 | TR_LINE 34618_1 | TR_LINE 34618_1
NQ-Townsville Burdekin West | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Loading (A) | 298.332 | 277.5031 | 169.2926 | 294.189 | 273.6963 | 167.2583 | 290.9973 | 270.2442 | 167.8201 | 290.1989 | 269.5501 | 167.415 | 291.9548 | 271.1969 | 168.2611
NQ-Townsville Burdekin West | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Loading (MVA) | 35.399 | 32.9058 | 20.3564 | 34.9147 | 32.4593 | 20.114 | 34.6265 | 32.2008 | 19.9398 | 34.5272 | 32.1121 | 19.8903 | 34.7186 | 32.2895 | 19.9856
NQ-Townsville Burdekin West | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Loading (MW) | 35.2815 | 32.7283 | 19.3651 | 34.785 | 32.2675 | 19.0938 | 34.4856 | 31.9902 | 18.9325 | 34.3842 | 31.8994 | 18.8783 | 34.5818 | 32.0844 | 18.9868
NQ-Townsville Burdekin West | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Power Factor | 0.99656 | 0.99447 | 0.95112 | 0.99616 | 0.99395 | 0.94909 | 0.9958 | 0.99331 | 0.94929 | 0.99573 | 0.99323 | 0.94893 | 0.99593 | 0.9935 | 0.94983
NQ-Townsville Burdekin West | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Rating (A) | 460 | 516 | 474 | 460 | 516 | 474 | 460 | 516 | 474 | 460 | 516 | 474 | 460 | 516 | 474
NQ-Townsville Burdekin West | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Townsville Burdekin West | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Min Voltage at Constrained Conductor | 68.4751 | 68.4344 | 69.4206 | 68.4903 | 68.4457 | 69.4289 | 68.6708 | 68.769 | 68.5971 | 68.6624 | 68.7563 | 68.5925 | 68.6275 | 68.7158 | 68.5744
NQ-Townsville Burdekin West | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Contingency Outage | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV
NQ-Townsville Burdekin West | AY-EA-1_Ayr - East Ayr No 1 66 kV | % of Rated A | 30.51% | 28.99% | 24.4% | 29.78% | 28.81% | 23.94% | 29.71% | 28.72% | 23.9% | 29.76% | 28.79% | 23.94% | 30.22% | 29.19% | 24.28%
NQ-Townsville Burdekin West | AY-EA-1_Ayr - East Ayr No 1 66 kV | Limiting Line Name | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1
NQ-Townsville Burdekin West | AY-EA-1_Ayr - East Ayr No 1 66 kV | Loading (A) | 79.015 | 85.8052 | 66.8527 | 77.1243 | 85.2646 | 65.6077 | 76.9569 | 85.0027 | 65.4739 | 77.0678 | 85.2079 | 65.6004 | 78.2652 | 86.3946 | 66.5265
NQ-Townsville Burdekin West | AY-EA-1_Ayr - East Ayr No 1 66 kV | Loading (MVA) | 8.7184 | 9.5516 | 7.5773 | 8.5241 | 9.3761 | 7.4447 | 8.5068 | 9.3497 | 7.4302 | 8.5169 | 9.3695 | 7.4434 | 8.6417 | 9.4883 | 7.5426
NQ-Townsville Burdekin West | AY-EA-1_Ayr - East Ayr No 1 66 kV | Loading (MW) | 6.9315 | 7.7692 | 6.2731 | 6.7846 | 7.6107 | 6.1601 | 6.7602 | 7.5785 | 6.1414 | 6.7634 | 7.5894 | 6.1497 | 6.8427 | 7.6826 | 6.2291
NQ-Townsville Burdekin West | AY-EA-1_Ayr - East Ayr No 1 66 kV | Power Factor | 0.79447 | 0.81293 | 0.82727 | 0.79533 | 0.81126 | 0.82684 | 0.79408 | 0.8101 | 0.82596 | 0.79351 | 0.80955 | 0.82559 | 0.79124 | 0.80925 | 0.82525
NQ-Townsville Burdekin West | AY-EA-1_Ayr - East Ayr No 1 66 kV | Rating (A) | 259 | 296 | 274 | 259 | 296 | 274 | 259 | 296 | 274 | 259 | 296 | 274 | 259 | 296 | 274
NQ-Townsville Burdekin West | AY-EA-1_Ayr - East Ayr No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Townsville Burdekin West | AY-EA-1_Ayr - East Ayr No 1 66 kV | Min Voltage at Constrained Conductor | 63.6901 | 64.2423 | 65.4384 | 63.8008 | 63.4609 | 65.5139 | 63.8101 | 63.4781 | 65.5193 | 63.794 | 63.4584 | 65.5097 | 63.7365 | 63.3783 | 65.4585
NQ-Townsville Burdekin West | AY-EA-1_Ayr - East Ayr No 1 66 kV | Contingency Outage | MOPA_Clare South - Mona Park 66 kV | MOPA_Clare South - Mona Park 66 kV | MOPA_Clare South - Mona Park 66 kV | MOPA_Clare South - Mona Park 66 kV | MOPA_Clare South - Mona Park 66 kV | MOPA_Clare South - Mona Park 66 kV | MOPA_Clare South - Mona Park 66 kV | MOPA_Clare South - Mona Park 66 kV | MOPA_Clare South - Mona Park 66 kV | MOPA_Clare South - Mona Park 66 kV | MOPA_Clare South - Mona Park 66 kV | MOPA_Clare South - Mona Park 66 kV | MOPA_Clare South - Mona Park 66 kV | MOPA_Clare South - Mona Park 66 kV | MOPA_Clare South - Mona Park 66 kV
NQ-Townsville Burdekin West | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | % of Rated A | 65.65% | 58.91% | 42.83% | 65.15% | 59.23% | 42.39% | 65.04% | 59.09% | 42.31% | 65.36% | 59.4% | 42.5% | 66.24% | 60.27% | 43.11%
NQ-Townsville Burdekin West | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Limiting Line Name | TR_LINE 31671_1 | TR_LINE 31671_1 | TR_LINE 31671_1 | TR_LINE 31671_1 | TR_LINE 31671_1 | TR_LINE 31671_1 | TR_LINE 31671_1 | TR_LINE 31671_1 | TR_LINE 31671_1 | TR_LINE 31671_1 | TR_LINE 31671_1 | TR_LINE 31671_1 | TR_LINE 31671_1 | TR_LINE 31671_1 | TR_LINE 31671_1
NQ-Townsville Burdekin West | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Loading (A) | 169.3879 | 173.7913 | 116.5097 | 168.0872 | 174.7164 | 115.3011 | 167.7946 | 174.3026 | 115.0879 | 168.6234 | 175.2319 | 115.5913 | 170.8888 | 177.782 | 117.2465
NQ-Townsville Burdekin West | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Loading (MVA) | 18.8531 | 19.5162 | 13.2885 | 18.7389 | 19.3842 | 13.1645 | 18.7087 | 19.3431 | 13.1411 | 18.7973 | 19.4413 | 13.197 | 19.0354 | 19.703 | 13.3772
NQ-Townsville Burdekin West | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Loading (MW) | 18.7165 | 19.3573 | 13.2493 | 18.6002 | 19.2278 | 13.1294 | 18.5692 | 19.1864 | 13.1057 | 18.6558 | 19.2817 | 13.1607 | 18.894 | 19.5342 | 13.3362
NQ-Townsville Burdekin West | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Power Factor | 0.99275 | 0.99186 | 0.99705 | 0.9926 | 0.99193 | 0.99733 | 0.99254 | 0.9919 | 0.99731 | 0.99247 | 0.99179 | 0.99725 | 0.99257 | 0.99143 | 0.99694
NQ-Townsville Burdekin West | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Rating (A) | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272
NQ-Townsville Burdekin West | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Townsville Burdekin West | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Min Voltage at Constrained Conductor | 64.2543 | 64.8288 | 65.846 | 64.3592 | 64.0493 | 65.9152 | 64.3677 | 64.065 | 65.9199 | 64.3545 | 64.0489 | 65.9123 | 64.3058 | 63.9798 | 65.8689
NQ-Townsville Burdekin West | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Contingency Outage | MOPA_Clare South - Mona Park 66 kV | MOPA_Clare South - Mona Park 66 kV | MOPA_Clare South - Mona Park 66 kV | MOPA_Clare South - Mona Park 66 kV | MOPA_Clare South - Mona Park 66 kV | MOPA_Clare South - Mona Park 66 kV | MOPA_Clare South - Mona Park 66 kV | MOPA_Clare South - Mona Park 66 kV | MOPA_Clare South - Mona Park 66 kV | MOPA_Clare South - Mona Park 66 kV | MOPA_Clare South - Mona Park 66 kV | MOPA_Clare South - Mona Park 66 kV | MOPA_Clare South - Mona Park 66 kV | MOPA_Clare South - Mona Park 66 kV | MOPA_Clare South - Mona Park 66 kV
NQ-Townsville Burdekin West | BC-IN-1_Black River - Ingham No 1 66 kV | % of Rated A | 26.72% | 31.63% | 19.44% | 26.72% | 31.63% | 19.44% | 26.54% | 31.47% | 19.57% | 26.56% | 31.49% | 19.57% | 26.59% | 31.54% | 19.59%
NQ-Townsville Burdekin West | BC-IN-1_Black River - Ingham No 1 66 kV | Limiting Line Name | TR_LINE 128321_1 | TR_LINE 128321_1 | TR_LINE 128321_1 | TR_LINE 128321_1 | TR_LINE 128321_1 | TR_LINE 128321_1 | TR_LINE 128321_1 | TR_LINE 128321_1 | TR_LINE 128321_1 | TR_LINE 128321_1 | TR_LINE 128321_1 | TR_LINE 128321_1 | TR_LINE 128321_1 | TR_LINE 128321_1 | TR_LINE 128321_1
NQ-Townsville Burdekin West | BC-IN-1_Black River - Ingham No 1 66 kV | Loading (A) | 50.5039 | 65.1552 | 36.1622 | 50.5053 | 65.1634 | 36.1629 | 50.1616 | 64.8229 | 36.393 | 50.1938 | 64.8796 | 36.4046 | 50.2505 | 64.972 | 36.4283
NQ-Townsville Burdekin West | BC-IN-1_Black River - Ingham No 1 66 kV | Loading (MVA) | 5.8227 | 7.4674 | 4.2593 | 5.8227 | 7.4674 | 4.2593 | 5.8214 | 7.466 | 4.2598 | 5.8215 | 7.4663 | 4.2598 | 5.8216 | 7.4665 | 4.2599
NQ-Townsville Burdekin West | BC-IN-1_Black River - Ingham No 1 66 kV | Loading (MW) | 5.7775 | 7.3868 | 4.2301 | 5.7775 | 7.3868 | 4.2301 | 5.7771 | 7.3863 | 4.2301 | 5.7772 | 7.3864 | 4.2301 | 5.7772 | 7.3865 | 4.2301
NQ-Townsville Burdekin West | BC-IN-1_Black River - Ingham No 1 66 kV | Power Factor | 0.9922 | 0.98917 | 0.99308 | 0.9922 | 0.98917 | 0.99308 | 0.99236 | 0.98929 | 0.99297 | 0.99234 | 0.98927 | 0.99296 | 0.99233 | 0.98926 | 0.99294
NQ-Townsville Burdekin West | BC-IN-1_Black River - Ingham No 1 66 kV | Rating (A) | 189 | 206 | 186 | 189 | 206 | 186 | 189 | 206 | 186 | 189 | 206 | 186 | 189 | 206 | 186
NQ-Townsville Burdekin West | BC-IN-1_Black River - Ingham No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Townsville Burdekin West | BC-IN-1_Black River - Ingham No 1 66 kV | Min Voltage at Constrained Conductor | 66.557 | 66.1596 | 67.9999 | 66.5552 | 66.1517 | 67.9985 | 66.9968 | 66.4869 | 67.5763 | 66.9554 | 66.4314 | 67.5555 | 66.8801 | 66.338 | 67.5129
NQ-Townsville Burdekin West | BC-IN-1_Black River - Ingham No 1 66 kV | Contingency Outage | GA-BO-1_Garbutt-Bohle No 1 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV
NQ-Townsville Burdekin West | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | % of Rated A | 14.34% | 15.77% | 8.371% | 14.34% | 15.77% | 8.371% | 14.39% | 15.79% | 8.501% | 14.6% | 16.01% | 8.607% | 15% | 16.46% | 8.823%
NQ-Townsville Burdekin West | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | Limiting Line Name | TR_CABLE 4815_1 | TR_CABLE 4815_1 | TR_CABLE 4808_1 | TR_CABLE 4815_1 | TR_CABLE 4815_1 | TR_CABLE 4808_1 | TR_CABLE 4815_1 | TR_CABLE 4815_1 | TR_CABLE 4808_1 | TR_CABLE 4815_1 | TR_CABLE 4815_1 | TR_CABLE 4808_1 | TR_CABLE 4815_1 | TR_CABLE 4815_1 | TR_CABLE 4808_1
NQ-Townsville Burdekin West | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | Loading (A) | 113.8866 | 125.2085 | 66.4696 | 113.8667 | 125.1931 | 66.4644 | 114.2921 | 125.3524 | 67.4955 | 115.8942 | 127.1226 | 68.3432 | 119.1284 | 130.6922 | 70.052
NQ-Townsville Burdekin West | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | Loading (MVA) | 13.4947 | 14.8195 | 7.9776 | 13.4946 | 14.8194 | 7.9778 | 13.5872 | 14.9268 | 8.0128 | 13.7756 | 15.1343 | 8.1129 | 14.1528 | 15.55 | 8.3136
NQ-Townsville Burdekin West | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | Loading (MW) | 13.2952 | 14.5831 | 7.8 | 13.2951 | 14.5831 | 7.8 | 13.3862 | 14.6838 | 7.8523 | 13.5688 | 14.8842 | 7.9586 | 13.9341 | 15.285 | 8.1712
NQ-Townsville Burdekin West | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | Power Factor | 0.98472 | 0.98359 | 0.97773 | 0.98473 | 0.98359 | 0.97772 | 0.98472 | 0.98327 | 0.97996 | 0.98451 | 0.98302 | 0.98098 | 0.98407 | 0.98252 | 0.98287
NQ-Townsville Burdekin West | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | Rating (A) | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794
NQ-Townsville Burdekin West | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Townsville Burdekin West | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | Min Voltage at Constrained Conductor | 68.4117 | 68.3344 | 69.2904 | 68.4233 | 68.3425 | 69.2969 | 68.6363 | 68.75 | 68.5383 | 68.6259 | 68.7352 | 68.5331 | 68.5911 | 68.6943 | 68.5157
NQ-Townsville Burdekin West | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | Contingency Outage | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | BEGA 2_Garbutt-Belgian Gardens No2 66 kV
NQ-Townsville Burdekin West | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | % of Rated A | 14.34% | 15.77% | 8.367% | 14.34% | 15.77% | 8.367% | 14.4% | 15.79% | 8.497% | 14.6% | 16.01% | 8.604% | 15% | 16.46% | 8.819%
NQ-Townsville Burdekin West | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | Limiting Line Name | TR_CABLE 4806_1 | TR_CABLE 4806_1 | TR_CABLE 16086_1 | TR_CABLE 4806_1 | TR_CABLE 4806_1 | TR_CABLE 16086_1 | TR_CABLE 4806_1 | TR_CABLE 4806_1 | TR_CABLE 16086_1 | TR_CABLE 4806_1 | TR_CABLE 4806_1 | TR_CABLE 16086_1 | TR_CABLE 4806_1 | TR_CABLE 4806_1 | TR_CABLE 16086_1
NQ-Townsville Burdekin West | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | Loading (A) | 113.8926 | 125.2156 | 66.4375 | 113.8728 | 125.2002 | 66.4324 | 114.2982 | 125.3596 | 67.4654 | 115.9004 | 127.1301 | 68.3139 | 119.135 | 130.7001 | 70.0243
NQ-Townsville Burdekin West | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | Loading (MVA) | 13.4954 | 14.8203 | 7.9737 | 13.4953 | 14.8203 | 7.9739 | 13.5879 | 14.9276 | 8.0092 | 13.7763 | 15.1352 | 8.1093 | 14.1536 | 15.5509 | 8.3103
NQ-Townsville Burdekin West | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | Loading (MW) | 13.2952 | 14.5832 | 7.7998 | 13.2952 | 14.5832 | 7.7998 | 13.3862 | 14.684 | 7.8521 | 13.5689 | 14.8843 | 7.9584 | 13.9342 | 15.2852 | 8.1711
NQ-Townsville Burdekin West | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | Power Factor | 0.98472 | 0.98358 | 0.97819 | 0.98472 | 0.98358 | 0.97817 | 0.98471 | 0.98326 | 0.98038 | 0.9845 | 0.98301 | 0.98139 | 0.98406 | 0.98251 | 0.98325
NQ-Townsville Burdekin West | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | Rating (A) | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794
NQ-Townsville Burdekin West | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Townsville Burdekin West | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | Min Voltage at Constrained Conductor | 68.4116 | 68.3343 | 69.2897 | 68.4231 | 68.3423 | 69.2962 | 68.6361 | 68.7498 | 68.5376 | 68.6257 | 68.7351 | 68.5324 | 68.5909 | 68.6941 | 68.515
NQ-Townsville Burdekin West | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | Contingency Outage | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | BEGA 1_Garbutt-Belgian Gardens No1 66 kV
NQ-Townsville Burdekin West | BO-DG-1_Bohle-Dan Gleeson 66 kV | % of Rated A | 89.31% | 111.7% | 58.65% | 89.74% | 112.3% | 58.92% | 89.58% | 113.1% | 59.48% | 90.84% | 114.7% | 60.27% | 92.8% | 117.3% | 61.51%
NQ-Townsville Burdekin West | BO-DG-1_Bohle-Dan Gleeson 66 kV | Limiting Line Name | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1
NQ-Townsville Burdekin West | BO-DG-1_Bohle-Dan Gleeson 66 kV | Loading (A) | 399.2132 | 499.2959 | 262.1435 | 401.1588 | 502.0248 | 263.3582 | 400.4136 | 505.4451 | 265.8535 | 406.0401 | 512.796 | 269.3951 | 414.824 | 524.1865 | 274.9338
NQ-Townsville Burdekin West | BO-DG-1_Bohle-Dan Gleeson 66 kV | Loading (MVA) | 46.9127 | 59.262 | 31.2263 | 47.1452 | 59.587 | 31.3721 | 47.3603 | 59.924 | 31.5222 | 48.0109 | 60.7721 | 31.9362 | 49.0173 | 62.0702 | 32.5818
NQ-Townsville Burdekin West | BO-DG-1_Bohle-Dan Gleeson 66 kV | Loading (MW) | 46.6744 | 58.6737 | 31.2178 | 46.9018 | 58.9859 | 31.363 | 47.1211 | 59.3023 | 31.5109 | 47.7557 | 60.1282 | 31.9226 | 48.7358 | 61.3715 | 32.5638
NQ-Townsville Burdekin West | BO-DG-1_Bohle-Dan Gleeson 66 kV | Power Factor | 0.99466 | 0.9898 | 0.99952 | 0.99458 | 0.98963 | 0.99949 | 0.99469 | 0.98935 | 0.99941 | 0.99442 | 0.98912 | 0.99932 | 0.994 | 0.98846 | 0.99919
NQ-Townsville Burdekin West | BO-DG-1_Bohle-Dan Gleeson 66 kV | Rating (A) | 447 | 447 | 447 | 447 | 447 | 447 | 447 | 447 | 447 | 447 | 447 | 447 | 447 | 447 | 447
NQ-Townsville Burdekin West | BO-DG-1_Bohle-Dan Gleeson 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Townsville Burdekin West | BO-DG-1_Bohle-Dan Gleeson 66 kV | Min Voltage at Constrained Conductor | 67.8461 | 68.5263 | 68.7701 | 67.8517 | 68.5276 | 68.7729 | 68.288 | 68.4488 | 68.4545 | 68.2669 | 68.4226 | 68.443 | 68.222 | 68.3654 | 68.4204
NQ-Townsville Burdekin West | BO-DG-1_Bohle-Dan Gleeson 66 kV | Contingency Outage | GA-BO-1_Garbutt-Bohle No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV
NQ-Townsville Burdekin West | CHTO_Clare South - Charters Towers 66 kV | % of Rated A | 67.8% | 59.14% | 84.59% | 136.5% | 59.11% | 83.7% | 67.77% | 59.09% | 88.88% | 67.79% | 59.11% | 89.04% | 67.81% | 59.14% | 89.55%
NQ-Townsville Burdekin West | CHTO_Clare South - Charters Towers 66 kV | Limiting Line Name | TR_LINE 33612_1 | TR_LINE 33612_1 | TR_LINE 102293_1 | TR_LINE 102293_1 | TR_LINE 33612_1 | TR_LINE 102293_1 | TR_LINE 33612_1 | TR_LINE 33612_1 | TR_LINE 102293_1 | TR_LINE 33612_1 | TR_LINE 33612_1 | TR_LINE 102293_1 | TR_LINE 33612_1 | TR_LINE 33612_1 | TR_LINE 102293_1
NQ-Townsville Burdekin West | CHTO_Clare South - Charters Towers 66 kV | Loading (A) | 134.9224 | 131.8831 | 230.0874 | 352.2616 | 131.8079 | 227.6731 | 134.8627 | 131.7788 | 241.7663 | 134.8957 | 131.8159 | 242.1769 | 134.9513 | 131.8822 | 243.5673
NQ-Townsville Burdekin West | CHTO_Clare South - Charters Towers 66 kV | Loading (MVA) | 14.5072 | 14.327 | 27.0314 | 41.6174 | 14.3266 | 26.7531 | 14.5069 | 14.3264 | 28.4068 | 14.5071 | 14.3266 | 28.4551 | 14.5074 | 14.327 | 28.6137
NQ-Townsville Burdekin West | CHTO_Clare South - Charters Towers 66 kV | Loading (MW) | 12.5013 | 12.3499 | 27.0204 | 41.0652 | 12.3499 | 26.7424 | 12.5013 | 12.3499 | 28.3944 | 12.5013 | 12.3499 | 28.4423 | 12.5013 | 12.3499 | 28.5999
NQ-Townsville Burdekin West | CHTO_Clare South - Charters Towers 66 kV | Power Factor | 0.86172 | 0.86199 | 0.99959 | 0.98673 | 0.86202 | 0.9996 | 0.86174 | 0.86202 | 0.99956 | 0.86173 | 0.86201 | 0.99955 | 0.86171 | 0.86199 | 0.99952
NQ-Townsville Burdekin West | CHTO_Clare South - Charters Towers 66 kV | Rating (A) | 199 | 223 | 272 | 258 | 223 | 272 | 199 | 223 | 272 | 199 | 223 | 272 | 199 | 223 | 272
NQ-Townsville Burdekin West | CHTO_Clare South - Charters Towers 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Townsville Burdekin West | CHTO_Clare South - Charters Towers 66 kV | Min Voltage at Constrained Conductor | 62.0595 | 62.7017 | 66.7072 | 66.2132 | 62.7358 | 66.7328 | 62.0857 | 62.749 | 66.6573 | 62.0712 | 62.7322 | 66.6547 | 62.0469 | 62.7021 | 66.6353
NQ-Townsville Burdekin West | CHTO_Clare South - Charters Towers 66 kV | Contingency Outage | CT-MR-1_Millchester-CHTO No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | 7182 Ross - Milchester | 7182 Ross - Milchester | CT-MR-1_Millchester-CHTO No 1 66 kV | 7182 Ross - Milchester | CT-MR-1_Millchester-CHTO No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | 7182 Ross - Milchester | CT-MR-1_Millchester-CHTO No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | 7182 Ross - Milchester | CT-MR-1_Millchester-CHTO No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | 7182 Ross - Milchester
NQ-Townsville Burdekin West | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | % of Rated A | 48.45% | 44.06% | 28.46% | 47.11% | 43.5% | 27.81% | 47.05% | 43.43% | 27.77% | 47.2% | 43.57% | 27.85% | 47.74% | 44.08% | 28.18%
NQ-Townsville Burdekin West | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Limiting Line Name | TR_LINE 35632_1 | TR_LINE 35632_1 | TR_LINE 35632_1 | TR_LINE 35632_1 | TR_LINE 35632_1 | TR_LINE 35632_1 | TR_LINE 35632_1 | TR_LINE 35632_1 | TR_LINE 35632_1 | TR_LINE 35632_1 | TR_LINE 35632_1 | TR_LINE 35632_1 | TR_LINE 35632_1 | TR_LINE 35632_1 | TR_LINE 35632_1
NQ-Townsville Burdekin West | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Loading (A) | 151.15 | 159.9501 | 95.918 | 146.9798 | 157.9058 | 93.7179 | 146.8083 | 157.6664 | 93.5953 | 147.2527 | 158.1633 | 93.8631 | 148.9592 | 160.0189 | 94.9649
NQ-Townsville Burdekin West | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Loading (MVA) | 16.9936 | 18.1453 | 11.0155 | 16.5549 | 17.7034 | 10.7731 | 16.5379 | 17.6807 | 10.7599 | 16.5857 | 17.7335 | 10.7899 | 16.765 | 17.9263 | 10.911
NQ-Townsville Burdekin West | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Loading (MW) | 16.6845 | 17.7633 | 10.9438 | 16.2758 | 17.346 | 10.7119 | 16.2593 | 17.3244 | 10.6989 | 16.3058 | 17.3752 | 10.7283 | 16.4759 | 17.5568 | 10.845
NQ-Townsville Burdekin West | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Power Factor | 0.98181 | 0.97895 | 0.99346 | 0.98314 | 0.97981 | 0.99428 | 0.98315 | 0.97985 | 0.9943 | 0.98312 | 0.97979 | 0.99425 | 0.98276 | 0.97939 | 0.99391
NQ-Townsville Burdekin West | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Rating (A) | 312 | 363 | 337 | 312 | 363 | 337 | 312 | 363 | 337 | 312 | 363 | 337 | 312 | 363 | 337
NQ-Townsville Burdekin West | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Townsville Burdekin West | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Min Voltage at Constrained Conductor | 64.8466 | 65.4273 | 66.2713 | 64.9679 | 64.6607 | 66.3359 | 64.9768 | 64.6759 | 66.3411 | 64.968 | 64.6653 | 66.3364 | 64.9169 | 64.6089 | 66.3018
NQ-Townsville Burdekin West | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Contingency Outage | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV
NQ-Townsville Burdekin West | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | % of Rated A | 87.7% | 65.63% | 40.33% | 85.28% | 64.8% | 39.41% | 85.18% | 64.7% | 39.36% | 85.44% | 64.9% | 39.47% | 86.43% | 65.67% | 39.93%
NQ-Townsville Burdekin West | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Limiting Line Name | TR_LINE 147761_1 | TR_LINE 147761_1 | TR_LINE 147761_1 | TR_LINE 147761_1 | TR_LINE 147761_1 | TR_LINE 147761_1 | TR_LINE 147761_1 | TR_LINE 147761_1 | TR_LINE 147761_1 | TR_LINE 147761_1 | TR_LINE 147761_1 | TR_LINE 147761_1 | TR_LINE 147761_1 | TR_LINE 147761_1 | TR_LINE 147761_1
NQ-Townsville Burdekin West | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Loading (A) | 148.2164 | 156.8651 | 93.9747 | 144.1236 | 154.8681 | 91.8191 | 143.9549 | 154.6324 | 91.6989 | 144.392 | 155.1213 | 91.9614 | 146.0652 | 156.9404 | 93.0416
NQ-Townsville Burdekin West | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Loading (MVA) | 16.8783 | 18.0409 | 10.867 | 16.4336 | 17.6008 | 10.6254 | 16.4163 | 17.5776 | 10.6122 | 16.4647 | 17.6313 | 10.6421 | 16.646 | 17.8269 | 10.7628
NQ-Townsville Burdekin West | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Loading (MW) | 16.6288 | 17.7229 | 10.8302 | 16.212 | 17.3042 | 10.5962 | 16.1952 | 17.2821 | 10.5832 | 16.2423 | 17.3337 | 10.6126 | 16.4149 | 17.5185 | 10.7301
NQ-Townsville Burdekin West | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Power Factor | 0.98522 | 0.98238 | 0.9965 | 0.98652 | 0.98314 | 0.99713 | 0.98653 | 0.98319 | 0.99714 | 0.98649 | 0.98312 | 0.99711 | 0.98612 | 0.9827 | 0.99684
NQ-Townsville Burdekin West | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Rating (A) | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233
NQ-Townsville Burdekin West | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Townsville Burdekin West | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Min Voltage at Constrained Conductor | 65.2969 | 65.9159 | 66.5157 | 65.3995 | 65.1389 | 66.5709 | 65.4078 | 65.1532 | 66.5757 | 65.4005 | 65.1444 | 66.5719 | 65.3563 | 65.0957 | 66.5417
NQ-Townsville Burdekin West | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Contingency Outage | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV
NQ-Townsville Burdekin West | CR-HU-1_Cape River-Hughenden No 1 66 kV | % of Rated A | 77.38% | 60.59% | 40.35% | 75.88% | 58.28% | 39.82% | 92.77% | 79.44% | 46.48% | 92.82% | 79.5% | 46.47% | 92.62% | 79.37% | 46.35%
NQ-Townsville Burdekin West | CR-HU-1_Cape River-Hughenden No 1 66 kV | Limiting Line Name | TR_LINE 53284_2 | TR_LINE 53284_2 | TR_LINE 53284_2 | TR_LINE 53284_2 | TR_LINE 53284_2 | TR_LINE 53284_2 | TR_LINE 53284_2 | TR_LINE 53284_2 | TR_LINE 53284_2 | TR_LINE 53284_2 | TR_LINE 53284_2 | TR_LINE 53284_2 | TR_LINE 53284_2 | TR_LINE 53284_2 | TR_LINE 53284_2
NQ-Townsville Burdekin West | CR-HU-1_Cape River-Hughenden No 1 66 kV | Loading (A) | 110.6555 | 128.4606 | 84.3252 | 108.502 | 123.5623 | 83.2137 | 132.6594 | 168.4185 | 97.1394 | 132.7279 | 168.5398 | 97.1249 | 132.4421 | 168.2548 | 96.8775
NQ-Townsville Burdekin West | CR-HU-1_Cape River-Hughenden No 1 66 kV | Loading (MVA) | 12.5314 | 14.6659 | 9.5727 | 12.2905 | 14.1911 | 9.4477 | 15.1403 | 18.9477 | 11.0169 | 15.1445 | 18.9555 | 11.0151 | 15.1051 | 18.9143 | 10.9864
NQ-Townsville Burdekin West | CR-HU-1_Cape River-Hughenden No 1 66 kV | Loading (MW) | 10.2867 | 12.7328 | 7.1515 | 10.0338 | 12.364 | 7.0199 | 13.1954 | 16.8576 | 8.694 | 13.1954 | 16.8613 | 8.692 | 13.1585 | 16.8228 | 8.6694
NQ-Townsville Burdekin West | CR-HU-1_Cape River-Hughenden No 1 66 kV | Power Factor | 0.82085 | 0.86816 | 0.74706 | 0.81636 | 0.87123 | 0.74303 | 0.87151 | 0.88964 | 0.78913 | 0.87127 | 0.88947 | 0.78908 | 0.8711 | 0.88937 | 0.78908
NQ-Townsville Burdekin West | CR-HU-1_Cape River-Hughenden No 1 66 kV | Rating (A) | 143 | 212 | 209 | 143 | 212 | 209 | 143 | 212 | 209 | 143 | 212 | 209 | 143 | 212 | 209
NQ-Townsville Burdekin West | CR-HU-1_Cape River-Hughenden No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Townsville Burdekin West | CR-HU-1_Cape River-Hughenden No 1 66 kV | Min Voltage at Constrained Conductor | 65.3831 | 65.9134 | 65.5417 | 65.3992 | 66.308 | 65.5495 | 65.8918 | 64.9528 | 65.4795 | 65.876 | 64.933 | 65.4781 | 65.8466 | 64.9015 | 65.4745
NQ-Townsville Burdekin West | CR-HU-1_Cape River-Hughenden No 1 66 kV | Contingency Outage | 7460 CPRE-JACR 132kV | 6383 CARI-CPRE 66kV | 7460 CPRE-JACR 132kV | 7460 CPRE-JACR 132kV | 6383 CARI-CPRE 66kV | 7460 CPRE-JACR 132kV | 6383 CARI-CPRE 66kV | 6383 CARI-CPRE 66kV | 7460 CPRE-JACR 132kV | 6383 CARI-CPRE 66kV | 6383 CARI-CPRE 66kV | 7460 CPRE-JACR 132kV | 6383 CARI-CPRE 66kV | 6383 CARI-CPRE 66kV | 7460 CPRE-JACR 132kV
NQ-Townsville Burdekin West | CS-ML-1_Clare South - Millaroo 66 kV | % of Rated A | 44.37% | 39.41% | 36.54% | 43.86% | 39.48% | 36.12% | 43.37% | 39.04% | 35.72% | 42.88% | 38.6% | 35.3% | 43.39% | 39.06% | 35.74%
NQ-Townsville Burdekin West | CS-ML-1_Clare South - Millaroo 66 kV | Limiting Line Name | TR_LINE 128012_1 | TR_LINE 128012_1 | TR_LINE 128012_1 | TR_LINE 128012_1 | TR_LINE 128012_1 | TR_LINE 128012_1 | TR_LINE 128012_1 | TR_LINE 128012_1 | TR_LINE 128012_1 | TR_LINE 128012_1 | TR_LINE 128012_1 | TR_LINE 128012_1 | TR_LINE 128012_1 | TR_LINE 128012_1 | TR_LINE 128012_1
NQ-Townsville Burdekin West | CS-ML-1_Clare South - Millaroo 66 kV | Loading (A) | 86.5141 | 85.9148 | 72.7082 | 85.5337 | 86.0701 | 71.8689 | 84.5671 | 85.0973 | 71.0873 | 83.6152 | 84.1419 | 70.2561 | 84.6138 | 85.1526 | 71.1184
NQ-Townsville Burdekin West | CS-ML-1_Clare South - Millaroo 66 kV | Loading (MVA) | 9.9639 | 10.0152 | 8.4276 | 9.8551 | 9.92 | 8.3386 | 9.7467 | 9.811 | 8.2436 | 9.6386 | 9.7024 | 8.1485 | 9.7505 | 9.8149 | 8.246
NQ-Townsville Burdekin West | CS-ML-1_Clare South - Millaroo 66 kV | Loading (MW) | 8.3543 | 8.4064 | 7.1064 | 8.2698 | 8.3232 | 7.032 | 8.1854 | 8.2385 | 6.9572 | 8.1011 | 8.1537 | 6.8823 | 8.1659 | 8.2186 | 6.9433
NQ-Townsville Burdekin West | CS-ML-1_Clare South - Millaroo 66 kV | Power Factor | 0.83842 | 0.83933 | 0.84318 | 0.83911 | 0.839 | 0.84327 | 0.83978 | 0.83968 | 0.84391 | 0.84045 | 0.84035 | 0.84457 | 0.83745 | 0.83732 | 0.84198
NQ-Townsville Burdekin West | CS-ML-1_Clare South - Millaroo 66 kV | Rating (A) | 195 | 218 | 199 | 195 | 218 | 199 | 195 | 218 | 199 | 195 | 218 | 199 | 195 | 218 | 199
NQ-Townsville Burdekin West | CS-ML-1_Clare South - Millaroo 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Townsville Burdekin West | CS-ML-1_Clare South - Millaroo 66 kV | Min Voltage at Constrained Conductor | 66.4901 | 67.2986 | 66.919 | 66.5183 | 66.5385 | 66.9852 | 66.5385 | 66.5602 | 66.9504 | 66.5496 | 66.5711 | 66.9609 | 66.5274 | 66.5436 | 66.9408
NQ-Townsville Burdekin West | CS-ML-1_Clare South - Millaroo 66 kV | Contingency Outage | CT-MR-1_Millchester-CHTO No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | EAAY_Clare South - East Ayr 66 kV | EAAY_Clare South - East Ayr 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | EAAY_Clare South - East Ayr 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | EAAY_Clare South - East Ayr 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | EAAY_Clare South - East Ayr 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV
NQ-Townsville Burdekin West | CT-CR-1_Charters Towers-CARI No 1 66 kV | % of Rated A | 65.74% | 77.21% | 44.77% | 63.94% | 76.44% | 43.84% | 85.31% | 102.9% | 54.77% | 85.39% | 103% | 54.8% | 85.25% | 102.8% | 54.75%
NQ-Townsville Burdekin West | CT-CR-1_Charters Towers-CARI No 1 66 kV | Limiting Line Name | TR_LINE 31871_1 | TR_LINE 31871_1 | TR_LINE 31871_1 | TR_LINE 31871_1 | TR_LINE 31871_1 | TR_LINE 31871_1 | TR_LINE 31871_1 | TR_LINE 31871_1 | TR_LINE 31871_1 | TR_LINE 31871_1 | TR_LINE 31871_1 | TR_LINE 31871_1 | TR_LINE 31871_1 | TR_LINE 31871_1 | TR_LINE 31871_1
NQ-Townsville Burdekin West | CT-CR-1_Charters Towers-CARI No 1 66 kV | Loading (A) | 120.9636 | 154.4278 | 80.584 | 117.6438 | 152.8754 | 78.9106 | 156.9624 | 205.715 | 98.5853 | 157.1155 | 205.9481 | 98.6434 | 156.8654 | 205.6072 | 98.5576
NQ-Townsville Burdekin West | CT-CR-1_Charters Towers-CARI No 1 66 kV | Loading (MVA) | 14.1202 | 18.0276 | 9.4172 | 13.738 | 17.8006 | 9.2237 | 18.3295 | 23.9139 | 11.5243 | 18.343 | 23.9343 | 11.5296 | 18.3061 | 23.8828 | 11.5159
NQ-Townsville Burdekin West | CT-CR-1_Charters Towers-CARI No 1 66 kV | Loading (MW) | 11.6834 | 15.0802 | 7.815 | 11.3725 | 14.7922 | 7.6665 | 15.3594 | 20.3112 | 9.552 | 15.3633 | 20.3221 | 9.5517 | 15.3184 | 20.2649 | 9.53
NQ-Townsville Burdekin West | CT-CR-1_Charters Towers-CARI No 1 66 kV | Power Factor | 0.82688 | 0.83566 | 0.8298 | 0.8273 | 0.83014 | 0.83114 | 0.83709 | 0.8481 | 0.82857 | 0.83668 | 0.84783 | 0.82816 | 0.83592 | 0.84727 | 0.82726
NQ-Townsville Burdekin West | CT-CR-1_Charters Towers-CARI No 1 66 kV | Rating (A) | 184 | 200 | 180 | 184 | 200 | 180 | 184 | 200 | 180 | 184 | 200 | 180 | 184 | 200 | 180
NQ-Townsville Burdekin West | CT-CR-1_Charters Towers-CARI No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Townsville Burdekin West | CT-CR-1_Charters Towers-CARI No 1 66 kV | Min Voltage at Constrained Conductor | 67.3708 | 67.366 | 67.4541 | 67.3974 | 67.1948 | 67.4691 | 67.3873 | 67.0677 | 67.4706 | 67.3711 | 67.0488 | 67.4617 | 67.3431 | 67.0157 | 67.4407
NQ-Townsville Burdekin West | CT-CR-1_Charters Towers-CARI No 1 66 kV | Contingency Outage | MR-CR-1_Millchester-Cape River 1 66 kV | MR-CR-1_Millchester-Cape River 1 66 kV | MR-CR-1_Millchester-Cape River 1 66 kV | MR-CR-1_Millchester-Cape River 1 66 kV | MR-CR-1_Millchester-Cape River 1 66 kV | MR-CR-1_Millchester-Cape River 1 66 kV | MR-CR-1_Millchester-Cape River 1 66 kV | MR-CR-1_Millchester-Cape River 1 66 kV | MR-CR-1_Millchester-Cape River 1 66 kV | MR-CR-1_Millchester-Cape River 1 66 kV | MR-CR-1_Millchester-Cape River 1 66 kV | MR-CR-1_Millchester-Cape River 1 66 kV | MR-CR-1_Millchester-Cape River 1 66 kV | MR-CR-1_Millchester-Cape River 1 66 kV | MR-CR-1_Millchester-Cape River 1 66 kV
NQ-Townsville Burdekin West | CT-MR-1_Millchester-CHTO No 1 66 kV | % of Rated A | 54% | 54.11% | 69.36% | 97.57% | 54.46% | 68.63% | 60.02% | 63.23% | 73.36% | 60.22% | 63.44% | 73.34% | 60.29% | 63.52% | 73.7%
NQ-Townsville Burdekin West | CT-MR-1_Millchester-CHTO No 1 66 kV | Limiting Line Name | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1
NQ-Townsville Burdekin West | CT-MR-1_Millchester-CHTO No 1 66 kV | Loading (A) | 150.1165 | 168.2954 | 196.986 | 271.2503 | 169.3799 | 194.9004 | 166.8573 | 196.6317 | 208.3374 | 167.4106 | 197.2893 | 208.2848 | 167.6103 | 197.5434 | 209.3055
NQ-Townsville Burdekin West | CT-MR-1_Millchester-CHTO No 1 66 kV | Loading (MVA) | 17.5249 | 19.6485 | 21.7057 | 26.8817 | 19.7244 | 21.5103 | 19.487 | 22.8606 | 22.8264 | 19.5469 | 22.9306 | 22.8127 | 19.5621 | 22.9487 | 22.8979
NQ-Townsville Burdekin West | CT-MR-1_Millchester-CHTO No 1 66 kV | Loading (MW) | 17.3317 | 19.6078 | 15.0479 | 21.2783 | 19.6478 | 14.8398 | 19.4164 | 22.8556 | 15.9725 | 19.4774 | 22.9258 | 15.9641 | 19.4925 | 22.9438 | 16.0754
NQ-Townsville Burdekin West | CT-MR-1_Millchester-CHTO No 1 66 kV | Power Factor | 0.98897 | 0.99793 | 0.69315 | 0.79137 | 0.99612 | 0.68977 | 0.99638 | 0.99978 | 0.69961 | 0.99644 | 0.99979 | 0.69967 | 0.99645 | 0.99979 | 0.70192
NQ-Townsville Burdekin West | CT-MR-1_Millchester-CHTO No 1 66 kV | Rating (A) | 278 | 311 | 284 | 278 | 311 | 284 | 278 | 311 | 284 | 278 | 311 | 284 | 278 | 311 | 284
NQ-Townsville Burdekin West | CT-MR-1_Millchester-CHTO No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Townsville Burdekin West | CT-MR-1_Millchester-CHTO No 1 66 kV | Min Voltage at Constrained Conductor | 67.3947 | 67.3987 | 63.616 | 57.2158 | 67.2259 | 63.7181 | 67.421 | 67.1157 | 63.2553 | 67.4047 | 67.0968 | 63.2332 | 67.3765 | 67.0634 | 63.1598
NQ-Townsville Burdekin West | CT-MR-1_Millchester-CHTO No 1 66 kV | Contingency Outage | MR-CR-1_Millchester-Cape River 1 66 kV | MR-CR-1_Millchester-Cape River 1 66 kV | 7182 Ross - Milchester | 7182 Ross - Milchester | MR-CR-1_Millchester-Cape River 1 66 kV | 7182 Ross - Milchester | MR-CR-1_Millchester-Cape River 1 66 kV | MR-CR-1_Millchester-Cape River 1 66 kV | 7182 Ross - Milchester | MR-CR-1_Millchester-Cape River 1 66 kV | MR-CR-1_Millchester-Cape River 1 66 kV | 7182 Ross - Milchester | MR-CR-1_Millchester-Cape River 1 66 kV | MR-CR-1_Millchester-Cape River 1 66 kV | 7182 Ross - Milchester
NQ-Townsville Burdekin West | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | % of Rated A | 66.36% | 58.23% | 39.69% | 65.43% | 57.43% | 39.21% | 64.47% | 56.59% | 39.12% | 64.3% | 56.45% | 39.03% | 64.68% | 56.79% | 39.22%
NQ-Townsville Burdekin West | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Limiting Line Name | TR_LINE 126322_1 | TR_LINE 126322_1 | TR_LINE 126322_1 | TR_LINE 126322_1 | TR_LINE 126322_1 | TR_LINE 126322_1 | TR_LINE 126322_1 | TR_LINE 126322_1 | TR_LINE 126322_1 | TR_LINE 126322_1 | TR_LINE 126322_1 | TR_LINE 126322_1 | TR_LINE 126322_1 | TR_LINE 126322_1 | TR_LINE 126322_1
NQ-Townsville Burdekin West | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Loading (A) | 299.9375 | 277.1885 | 169.4813 | 295.7489 | 273.3678 | 167.4175 | 291.4124 | 269.3811 | 167.0487 | 290.6141 | 268.6912 | 166.644 | 292.3603 | 270.325 | 167.4894
NQ-Townsville Burdekin West | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Loading (MVA) | 35.3143 | 32.8337 | 20.2519 | 34.8311 | 32.3888 | 20.008 | 34.5493 | 32.1356 | 19.8791 | 34.45 | 32.0469 | 19.8295 | 34.6409 | 32.2237 | 19.9252
NQ-Townsville Burdekin West | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Loading (MW) | 35.2031 | 32.6515 | 19.3337 | 34.7086 | 32.1927 | 19.063 | 34.4088 | 31.9162 | 18.9007 | 34.3075 | 31.8254 | 18.8465 | 34.5041 | 32.0095 | 18.9547
NQ-Townsville Burdekin West | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Power Factor | 0.99679 | 0.99438 | 0.95457 | 0.99642 | 0.99387 | 0.95267 | 0.99587 | 0.9931 | 0.95068 | 0.9958 | 0.99301 | 0.95033 | 0.99599 | 0.99328 | 0.95119
NQ-Townsville Burdekin West | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Rating (A) | 452 | 476 | 427 | 452 | 476 | 427 | 452 | 476 | 427 | 452 | 476 | 427 | 452 | 476 | 427
NQ-Townsville Burdekin West | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Townsville Burdekin West | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Min Voltage at Constrained Conductor | 67.9528 | 68.3681 | 68.9838 | 67.9729 | 68.3848 | 68.9935 | 68.427 | 68.8552 | 68.7004 | 68.4178 | 68.8416 | 68.6953 | 68.3858 | 68.8026 | 68.6786
NQ-Townsville Burdekin West | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Contingency Outage | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV
NQ-Townsville Burdekin West | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | % of Rated A | 57.84% | 51.9% | 37.95% | 57.35% | 51.46% | 37.65% | 56.84% | 50.96% | 37.79% | 57.01% | 51.11% | 37.91% | 57.67% | 51.71% | 38.32%
NQ-Townsville Burdekin West | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Limiting Line Name | TR_LINE 32461_1 | TR_LINE 32461_1 | TR_LINE 32461_1 | TR_LINE 32461_1 | TR_LINE 32461_1 | TR_LINE 32461_1 | TR_LINE 32461_1 | TR_LINE 32461_1 | TR_LINE 32461_1 | TR_LINE 32461_1 | TR_LINE 32461_1 | TR_LINE 32461_1 | TR_LINE 32461_1 | TR_LINE 32461_1 | TR_LINE 32461_1
NQ-Townsville Burdekin West | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Loading (A) | 318.6826 | 302.0608 | 198.8426 | 316.0117 | 299.4833 | 197.3051 | 313.1711 | 296.5943 | 198.0404 | 314.1269 | 297.4807 | 198.6483 | 317.775 | 300.9385 | 200.8156
NQ-Townsville Burdekin West | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Loading (MVA) | 37.3067 | 35.5733 | 23.6679 | 37.0046 | 35.2783 | 23.4882 | 36.9051 | 35.1687 | 23.4345 | 37.0098 | 35.2641 | 23.5037 | 37.4169 | 35.65 | 23.7528
NQ-Townsville Burdekin West | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Loading (MW) | 36.8725 | 35.2269 | 23.6127 | 36.581 | 34.9411 | 23.4356 | 36.4831 | 34.8418 | 23.3806 | 36.5819 | 34.9325 | 23.4483 | 36.9724 | 35.3086 | 23.6932
NQ-Townsville Burdekin West | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Power Factor | 0.98836 | 0.99026 | 0.99767 | 0.98855 | 0.99044 | 0.99776 | 0.98857 | 0.99071 | 0.9977 | 0.98844 | 0.9906 | 0.99764 | 0.98812 | 0.99042 | 0.99749
NQ-Townsville Burdekin West | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Rating (A) | 551 | 582 | 524 | 551 | 582 | 524 | 551 | 582 | 524 | 551 | 582 | 524 | 551 | 582 | 524
NQ-Townsville Burdekin West | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Townsville Burdekin West | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Min Voltage at Constrained Conductor | 67.5781 | 67.985 | 68.716 | 67.5975 | 68.0016 | 68.7259 | 68.0274 | 68.4507 | 68.3139 | 68.0128 | 68.4319 | 68.3061 | 67.9715 | 68.3857 | 68.2849
NQ-Townsville Burdekin West | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Contingency Outage | ST-RP-1_Stuart-Ross Plains 66 kV | ST-RP-1_Stuart-Ross Plains 66 kV | ST-RP-1_Stuart-Ross Plains 66 kV | ST-RP-1_Stuart-Ross Plains 66 kV | ST-RP-1_Stuart-Ross Plains 66 kV | ST-RP-1_Stuart-Ross Plains 66 kV | ST-RP-1_Stuart-Ross Plains 66 kV | ST-RP-1_Stuart-Ross Plains 66 kV | ST-RP-1_Stuart-Ross Plains 66 kV | ST-RP-1_Stuart-Ross Plains 66 kV | ST-RP-1_Stuart-Ross Plains 66 kV | ST-RP-1_Stuart-Ross Plains 66 kV | ST-RP-1_Stuart-Ross Plains 66 kV | ST-RP-1_Stuart-Ross Plains 66 kV | ST-RP-1_Stuart-Ross Plains 66 kV
NQ-Townsville Burdekin West | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | % of Rated A | 52.47% | 42.18% | 20.4% | 52.46% | 42.18% | 20.4% | 52.14% | 41.6% | 20.51% | 52.42% | 41.83% | 20.61% | 53.27% | 42.52% | 20.92%
NQ-Townsville Burdekin West | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Limiting Line Name | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1
NQ-Townsville Burdekin West | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Loading (A) | 131.6895 | 162.3927 | 77.5386 | 131.6702 | 162.3741 | 77.5334 | 130.8751 | 160.1571 | 77.9345 | 131.5834 | 161.044 | 78.33 | 133.7023 | 163.6838 | 79.515
NQ-Townsville Burdekin West | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Loading (MVA) | 15.5803 | 19.1653 | 9.2754 | 15.5803 | 19.1653 | 9.2754 | 15.5798 | 19.1584 | 9.2705 | 15.6616 | 19.2601 | 9.3167 | 15.907 | 19.5654 | 9.4556
NQ-Townsville Burdekin West | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Loading (MW) | 15.579 | 19.1547 | 9.1573 | 15.579 | 19.1547 | 9.1573 | 15.5779 | 19.1511 | 9.1576 | 15.66 | 19.2521 | 9.2057 | 15.9061 | 19.5552 | 9.35
NQ-Townsville Burdekin West | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Power Factor | 0.99992 | 0.99944 | 0.98727 | 0.99992 | 0.99945 | 0.98726 | 0.99988 | 0.99962 | 0.98783 | 0.9999 | 0.99959 | 0.98809 | 0.99994 | 0.99948 | 0.98884
NQ-Townsville Burdekin West | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Rating (A) | 251 | 385 | 380 | 251 | 385 | 380 | 251 | 385 | 380 | 251 | 385 | 380 | 251 | 385 | 380
NQ-Townsville Burdekin West | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Townsville Burdekin West | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Min Voltage at Constrained Conductor | 68.3066 | 68.1379 | 69.0642 | 68.3166 | 68.1454 | 69.0693 | 68.7298 | 69.0639 | 68.677 | 68.7185 | 69.0482 | 68.671 | 68.6892 | 69.0115 | 68.656
NQ-Townsville Burdekin West | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Contingency Outage | ST-RM-1_Stuart-Rasmussen 66 kV | ST-RM-1_Stuart-Rasmussen 66 kV | ST-RM-1_Stuart-Rasmussen 66 kV | ST-RM-1_Stuart-Rasmussen 66 kV | ST-RM-1_Stuart-Rasmussen 66 kV | ST-RM-1_Stuart-Rasmussen 66 kV | ST-RM-1_Stuart-Rasmussen 66 kV | ST-RM-1_Stuart-Rasmussen 66 kV | ST-RM-1_Stuart-Rasmussen 66 kV | ST-RM-1_Stuart-Rasmussen 66 kV | ST-RM-1_Stuart-Rasmussen 66 kV | ST-RM-1_Stuart-Rasmussen 66 kV | ST-RM-1_Stuart-Rasmussen 66 kV | ST-RM-1_Stuart-Rasmussen 66 kV | ST-RM-1_Stuart-Rasmussen 66 kV
NQ-Townsville Burdekin West | EAAY_Clare South - East Ayr 66 kV | % of Rated A | 78.7% | 54.73% | 34.94% | 77.67% | 54.41% | 34.51% | 77.55% | 54.32% | 34.45% | 77.92% | 54.54% | 34.6% | 78.95% | 55.26% | 35.05%
NQ-Townsville Burdekin West | EAAY_Clare South - East Ayr 66 kV | Limiting Line Name | TR_LINE 40742_1 | TR_LINE 40742_1 | TR_LINE 40742_1 | TR_LINE 40742_1 | TR_LINE 40742_1 | TR_LINE 40742_1 | TR_LINE 40742_1 | TR_LINE 40742_1 | TR_LINE 40742_1 | TR_LINE 40742_1 | TR_LINE 40742_1 | TR_LINE 40742_1 | TR_LINE 40742_1 | TR_LINE 40742_1 | TR_LINE 40742_1
NQ-Townsville Burdekin West | EAAY_Clare South - East Ayr 66 kV | Loading (A) | 165.2702 | 172.3888 | 108.3212 | 163.1104 | 171.3855 | 106.9837 | 162.85 | 171.0935 | 106.799 | 163.6244 | 171.7973 | 107.2545 | 165.7985 | 174.0581 | 108.6673
NQ-Townsville Burdekin West | EAAY_Clare South - East Ayr 66 kV | Loading (MVA) | 18.5017 | 19.4819 | 12.425 | 18.3365 | 19.1344 | 12.2799 | 18.3103 | 19.1063 | 12.2599 | 18.3929 | 19.1802 | 12.3105 | 18.6198 | 19.413 | 12.4649
NQ-Townsville Burdekin West | EAAY_Clare South - East Ayr 66 kV | Loading (MW) | 18.0195 | 18.9158 | 12.3753 | 18.1181 | 18.5927 | 12.2359 | 18.0928 | 18.5648 | 12.2163 | 18.1728 | 18.6342 | 12.2659 | 18.3894 | 18.8491 | 12.4154
NQ-Townsville Burdekin West | EAAY_Clare South - East Ayr 66 kV | Power Factor | 0.97394 | 0.97095 | 0.996 | 0.98809 | 0.97169 | 0.99642 | 0.98812 | 0.97166 | 0.99645 | 0.98803 | 0.97153 | 0.99637 | 0.98763 | 0.97095 | 0.99603
NQ-Townsville Burdekin West | EAAY_Clare South - East Ayr 66 kV | Rating (A) | 210 | 315 | 310 | 210 | 315 | 310 | 210 | 315 | 310 | 210 | 315 | 310 | 210 | 315 | 310
NQ-Townsville Burdekin West | EAAY_Clare South - East Ayr 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Townsville Burdekin West | EAAY_Clare South - East Ayr 66 kV | Min Voltage at Constrained Conductor | 64.6225 | 65.2355 | 66.2194 | 64.8944 | 64.4469 | 66.2642 | 64.9052 | 64.4622 | 66.2706 | 64.8895 | 64.4463 | 66.2618 | 64.8283 | 64.3811 | 66.2201
NQ-Townsville Burdekin West | EAAY_Clare South - East Ayr 66 kV | Contingency Outage | MOPA_Clare South - Mona Park 66 kV | MOPA_Clare South - Mona Park 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | MOPA_Clare South - Mona Park 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | MOPA_Clare South - Mona Park 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | MOPA_Clare South - Mona Park 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | MOPA_Clare South - Mona Park 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV
NQ-Townsville Burdekin West | GA-BO-1_Garbutt-Bohle No 1 66 kV | % of Rated A | 72.13% | 86.61% | 49.73% | 72.48% | 87.08% | 49.95% | 72.63% | 87.1% | 50.81% | 73.64% | 88.39% | 51.48% | 75.24% | 90.33% | 52.55%
NQ-Townsville Burdekin West | GA-BO-1_Garbutt-Bohle No 1 66 kV | Limiting Line Name | TR_LINE 32140_1 | TR_LINE 32140_1 | TR_LINE 32140_1 | TR_LINE 32140_1 | TR_LINE 32140_1 | TR_LINE 32140_1 | TR_LINE 32140_1 | TR_LINE 32140_1 | TR_LINE 32140_1 | TR_LINE 32140_1 | TR_LINE 32140_1 | TR_LINE 32140_1 | TR_LINE 32140_1 | TR_LINE 32140_1 | TR_LINE 32140_1
NQ-Townsville Burdekin West | GA-BO-1_Garbutt-Bohle No 1 66 kV | Loading (A) | 397.4625 | 504.0449 | 260.5623 | 399.3781 | 506.7814 | 261.7601 | 400.1759 | 506.92 | 266.2382 | 405.7753 | 514.4408 | 269.778 | 414.5797 | 525.7088 | 275.3491
NQ-Townsville Burdekin West | GA-BO-1_Garbutt-Bohle No 1 66 kV | Loading (MVA) | 46.3537 | 58.3306 | 31.0177 | 46.5798 | 58.6433 | 31.1614 | 46.8016 | 58.9525 | 31.3089 | 47.4334 | 59.7842 | 31.7166 | 48.4099 | 61.0168 | 32.3527
NQ-Townsville Burdekin West | GA-BO-1_Garbutt-Bohle No 1 66 kV | Loading (MW) | 46.2108 | 57.9563 | 31.0143 | 46.4337 | 58.2607 | 31.1576 | 46.6554 | 58.5618 | 31.3027 | 47.2769 | 59.3703 | 31.7089 | 48.2364 | 60.5788 | 32.3421
NQ-Townsville Burdekin West | GA-BO-1_Garbutt-Bohle No 1 66 kV | Power Factor | 0.99692 | 0.99358 | 0.99989 | 0.99686 | 0.99348 | 0.99988 | 0.99687 | 0.99337 | 0.9998 | 0.9967 | 0.99308 | 0.99976 | 0.99642 | 0.99282 | 0.99967
NQ-Townsville Burdekin West | GA-BO-1_Garbutt-Bohle No 1 66 kV | Rating (A) | 551 | 582 | 524 | 551 | 582 | 524 | 551 | 582 | 524 | 551 | 582 | 524 | 551 | 582 | 524
NQ-Townsville Burdekin West | GA-BO-1_Garbutt-Bohle No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Townsville Burdekin West | GA-BO-1_Garbutt-Bohle No 1 66 kV | Min Voltage at Constrained Conductor | 67.3292 | 66.8088 | 68.7266 | 67.3331 | 66.8042 | 68.7289 | 67.5189 | 67.1381 | 67.8928 | 67.4859 | 67.0898 | 67.8744 | 67.4125 | 67.0052 | 67.8347
NQ-Townsville Burdekin West | GA-BO-1_Garbutt-Bohle No 1 66 kV | Contingency Outage | BO-DG-1_Bohle-Dan Gleeson 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV
NQ-Townsville Burdekin West | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | % of Rated A | 76.04% | 75.41% | 44.1% | 75.72% | 75.2% | 43.96% | 75.69% | 74.99% | 44.66% | 75.91% | 75.25% | 44.8% | 76.88% | 76.23% | 45.35%
NQ-Townsville Burdekin West | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Limiting Line Name | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1
NQ-Townsville Burdekin West | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Loading (A) | 262.3417 | 270.7291 | 141.1114 | 261.2371 | 269.9537 | 140.6625 | 261.1456 | 269.2242 | 142.9026 | 261.8949 | 270.1559 | 143.3491 | 265.2198 | 273.6802 | 145.1351
NQ-Townsville Burdekin West | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Loading (MVA) | 31.0519 | 32.0041 | 16.9468 | 30.9274 | 31.917 | 16.8947 | 31.0079 | 32.0166 | 16.9489 | 31.0922 | 32.1203 | 17.0006 | 31.4697 | 32.5185 | 17.2075
NQ-Townsville Burdekin West | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Loading (MW) | 30.4338 | 31.4082 | 16.7237 | 30.3171 | 31.3268 | 16.6738 | 30.3987 | 31.4261 | 16.726 | 30.4815 | 31.5275 | 16.777 | 30.8466 | 31.9131 | 16.9801
NQ-Townsville Burdekin West | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Power Factor | 0.9801 | 0.98138 | 0.98684 | 0.98027 | 0.98151 | 0.98693 | 0.98035 | 0.98156 | 0.98684 | 0.98036 | 0.98154 | 0.98685 | 0.9802 | 0.98139 | 0.98678
NQ-Townsville Burdekin West | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Rating (A) | 345 | 359 | 320 | 345 | 359 | 320 | 345 | 359 | 320 | 345 | 359 | 320 | 345 | 359 | 320
NQ-Townsville Burdekin West | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Townsville Burdekin West | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Min Voltage at Constrained Conductor | 68.2846 | 68.1965 | 69.3117 | 68.2987 | 68.2066 | 69.3192 | 68.5006 | 68.6052 | 68.4506 | 68.4903 | 68.59 | 68.4452 | 68.452 | 68.5451 | 68.4256
NQ-Townsville Burdekin West | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Contingency Outage | 6325_Oonoonba-Stuart 66 kV | 6325_Oonoonba-Stuart 66 kV | 6325_Oonoonba-Stuart 66 kV | 6325_Oonoonba-Stuart 66 kV | 6325_Oonoonba-Stuart 66 kV | 6325_Oonoonba-Stuart 66 kV | 6325_Oonoonba-Stuart 66 kV | 6325_Oonoonba-Stuart 66 kV | 6325_Oonoonba-Stuart 66 kV | 6325_Oonoonba-Stuart 66 kV | 6325_Oonoonba-Stuart 66 kV | 6325_Oonoonba-Stuart 66 kV | 6325_Oonoonba-Stuart 66 kV | 6325_Oonoonba-Stuart 66 kV | 6325_Oonoonba-Stuart 66 kV
NQ-Townsville Burdekin West | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | % of Rated A | 30.05% | 16.61% | 15.25% | 29.65% | 16.39% | 15.05% | 29.57% | 16.31% | 15.22% | 29.77% | 16.42% | 15.32% | 30.19% | 16.65% | 15.53%
NQ-Townsville Burdekin West | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Limiting Line Name | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1
NQ-Townsville Burdekin West | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Loading (A) | 50.7907 | 39.6918 | 35.5356 | 50.1038 | 39.1633 | 35.0659 | 49.9661 | 38.9744 | 35.4635 | 50.3139 | 39.2459 | 35.7031 | 51.0219 | 39.7938 | 36.1866
NQ-Townsville Burdekin West | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Loading (MVA) | 6.0135 | 4.6911 | 4.2641 | 5.9332 | 4.629 | 4.2081 | 5.9331 | 4.6294 | 4.2066 | 5.9733 | 4.6604 | 4.2346 | 6.0537 | 4.7224 | 4.2906
NQ-Townsville Burdekin West | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Loading (MW) | 6.0132 | 4.6883 | 4.2561 | 5.9329 | 4.6258 | 4.1994 | 5.9329 | 4.6259 | 4.1992 | 5.973 | 4.6571 | 4.2275 | 6.0533 | 4.7195 | 4.2842
NQ-Townsville Burdekin West | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Power Factor | 0.99994 | 0.9994 | 0.99813 | 0.99996 | 0.9993 | 0.99794 | 0.99997 | 0.99922 | 0.99823 | 0.99996 | 0.99928 | 0.99832 | 0.99993 | 0.99939 | 0.99849
NQ-Townsville Burdekin West | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Rating (A) | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233
NQ-Townsville Burdekin West | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Townsville Burdekin West | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Min Voltage at Constrained Conductor | 68.3561 | 68.2345 | 69.2778 | 68.3671 | 68.241 | 69.2846 | 68.5548 | 68.5777 | 68.4835 | 68.542 | 68.5589 | 68.4766 | 68.5004 | 68.5142 | 68.4553
NQ-Townsville Burdekin West | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Contingency Outage | BO-DG-1_Bohle-Dan Gleeson 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV
NQ-Townsville Burdekin West | GA-TP-1_Garbutt-Townsville Port 1 66 kV | % of Rated A | 103.6% | 96.51% | 76.57% | 101.5% | 94.91% | 75.7% | 101.9% | 95.34% | 72.51% | 102% | 95.58% | 72.57% | 102.7% | 96.29% | 72.96%
NQ-Townsville Burdekin West | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Limiting Line Name | TR_LINE 161962_1 | TR_LINE 161962_1 | TR_LINE 161962_1 | TR_LINE 161962_1 | TR_LINE 161962_1 | TR_LINE 161962_1 | TR_LINE 161962_1 | TR_LINE 161962_1 | TR_LINE 161962_1 | TR_LINE 161962_1 | TR_LINE 161962_1 | TR_LINE 161962_1 | TR_LINE 161962_1 | TR_LINE 161962_1 | TR_LINE 161962_1
NQ-Townsville Burdekin West | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Loading (A) | 267.3474 | 284.6903 | 208.2592 | 261.8109 | 279.9703 | 205.9044 | 262.8342 | 281.2655 | 197.2164 | 263.1894 | 281.956 | 197.3842 | 264.8638 | 284.0631 | 198.4421
NQ-Townsville Burdekin West | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Loading (MVA) | 31.85 | 33.9063 | 25.0548 | 31.1858 | 33.3394 | 24.7704 | 31.3898 | 33.6589 | 23.5375 | 31.4283 | 33.736 | 23.5559 | 31.6152 | 33.9724 | 23.6771
NQ-Townsville Burdekin West | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Loading (MW) | 29.7002 | 31.989 | 21.3539 | 28.9295 | 31.3457 | 20.9864 | 28.9131 | 31.1251 | 22.8803 | 28.9576 | 31.2188 | 22.8985 | 29.1821 | 31.5101 | 23.0275
NQ-Townsville Burdekin West | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Power Factor | 0.93235 | 0.94331 | 0.85213 | 0.9275 | 0.94005 | 0.84708 | 0.92094 | 0.92455 | 0.97202 | 0.92123 | 0.92522 | 0.97203 | 0.92288 | 0.92735 | 0.97251
NQ-Townsville Burdekin West | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Rating (A) | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272
NQ-Townsville Burdekin West | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Townsville Burdekin West | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Min Voltage at Constrained Conductor | 68.7744 | 68.7529 | 69.4576 | 68.7649 | 68.7436 | 69.4546 | 68.9455 | 69.0843 | 68.8974 | 68.9371 | 69.0728 | 68.8926 | 68.9085 | 69.0406 | 68.878
NQ-Townsville Burdekin West | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Contingency Outage | 6325_Oonoonba-Stuart 66 kV | 6325_Oonoonba-Stuart 66 kV | 6325_Oonoonba-Stuart 66 kV | 6325_Oonoonba-Stuart 66 kV | 6325_Oonoonba-Stuart 66 kV | 6325_Oonoonba-Stuart 66 kV | 6325_Oonoonba-Stuart 66 kV | 6325_Oonoonba-Stuart 66 kV | 6325_Oonoonba-Stuart 66 kV | 6325_Oonoonba-Stuart 66 kV | 6325_Oonoonba-Stuart 66 kV | 6325_Oonoonba-Stuart 66 kV | 6325_Oonoonba-Stuart 66 kV | 6325_Oonoonba-Stuart 66 kV | 6325_Oonoonba-Stuart 66 kV
NQ-Townsville Burdekin West | GARB-12 11kV | % of Rated A | 0.6985% | 0.6981% | 0.6935% | 0.6989% | 0.6984% | 0.6937% | 0.6989% | 0.6952% | 0.6933% | 0.6989% | 0.6952% | 0.6933% | 0.6987% | 0.6947% | 0.693%
NQ-Townsville Burdekin West | GARB-12 11kV | Limiting Line Name | HV_CABLE 14927_1 | HV_CABLE 14927_1 | HV_CABLE 14927_1 | HV_CABLE 14927_1 | HV_CABLE 14927_1 | HV_CABLE 14927_1 | HV_CABLE 14927_1 | HV_CABLE 14927_1 | HV_CABLE 14927_1 | HV_CABLE 14927_1 | HV_CABLE 14927_1 | HV_CABLE 14927_1 | HV_CABLE 14927_1 | HV_CABLE 14927_1 | HV_CABLE 14927_1
NQ-Townsville Burdekin West | GARB-12 11kV | Loading (A) | 2.7942 | 2.7926 | 2.7738 | 2.7957 | 2.7938 | 2.7747 | 2.7956 | 2.781 | 2.7731 | 2.7956 | 2.7807 | 2.7731 | 2.7947 | 2.7789 | 2.7721
NQ-Townsville Burdekin West | GARB-12 11kV | Loading (MVA) | 0.052723 | 0.052663 | 0.051959 | 0.05278 | 0.052709 | 0.051992 | 0.052778 | 0.052227 | 0.051931 | 0.052777 | 0.052217 | 0.051931 | 0.052743 | 0.052149 | 0.051894
NQ-Townsville Burdekin West | GARB-12 11kV | Loading (MW) | 0.0010559 | 0.0010547 | 0.0010406 | 0.001057 | 0.0010556 | 0.0010413 | 0.001057 | 0.001046 | 0.00104 | 0.001057 | 0.0010458 | 0.0010401 | 0.0010563 | 0.0010444 | 0.0010393
NQ-Townsville Burdekin West | GARB-12 11kV | Power Factor | 0.020021 | 0.020021 | 0.020021 | 0.020021 | 0.020021 | 0.020021 | 0.020021 | 0.020021 | 0.020021 | 0.020021 | 0.020021 | 0.020021 | 0.020021 | 0.020021 | 0.020021
NQ-Townsville Burdekin West | GARB-12 11kV | Rating (A) | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400
NQ-Townsville Burdekin West | GARB-12 11kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Townsville Burdekin West | GARB-12 11kV | Min Voltage at Constrained Conductor | 10.894 | 10.8878 | 10.8148 | 10.8999 | 10.8926 | 10.8182 | 10.8997 | 10.8426 | 10.8118 | 10.8996 | 10.8416 | 10.8119 | 10.8961 | 10.8345 | 10.8081
NQ-Townsville Burdekin West | GARB-12 11kV | Contingency Outage | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | PA-RP-1_Peter Arlett-Ross Plains 66 kV | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | PA-RP-1_Peter Arlett-Ross Plains 66 kV | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | BC-IN-1_Black River - Ingham No 1 66 kV | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | BC-IN-1_Black River - Ingham No 1 66 kV | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | GA-HP-1_Garbutt-Hermit Park No 1 66 kV
NQ-Townsville Burdekin West | GI-AY-1_Giru - Ayr 1 66 kV | % of Rated A | 18.97% | 19.72% | 16.26% | 18.48% | 19.53% | 15.84% | 18.48% | 19.52% | 15.84% | 18.48% | 19.53% | 15.84% | 18.96% | 20.03% | 16.26%
NQ-Townsville Burdekin West | GI-AY-1_Giru - Ayr 1 66 kV | Limiting Line Name | TR_LINE 33583_2 | TR_LINE 33583_2 | TR_LINE 33583_2 | TR_LINE 33583_2 | TR_LINE 33583_2 | TR_LINE 33583_2 | TR_LINE 33583_2 | TR_LINE 33583_2 | TR_LINE 33583_2 | TR_LINE 33583_2 | TR_LINE 33583_2 | TR_LINE 33583_2 | TR_LINE 33583_2 | TR_LINE 33583_2 | TR_LINE 33583_2
NQ-Townsville Burdekin West | GI-AY-1_Giru - Ayr 1 66 kV | Loading (A) | 35.8505 | 40.6261 | 30.2419 | 34.9304 | 40.2313 | 29.4703 | 34.9249 | 40.2189 | 29.4677 | 34.9308 | 40.2331 | 29.4705 | 35.8308 | 41.2546 | 30.2353
NQ-Townsville Burdekin West | GI-AY-1_Giru - Ayr 1 66 kV | Loading (MVA) | 4.003 | 4.4676 | 3.4444 | 3.9056 | 4.3703 | 3.3598 | 3.9056 | 4.3702 | 3.3598 | 3.9056 | 4.3703 | 3.3599 | 4.0028 | 4.4741 | 3.4444
NQ-Townsville Burdekin West | GI-AY-1_Giru - Ayr 1 66 kV | Loading (MW) | 3.5746 | 4.0848 | 3.0895 | 3.493 | 3.9986 | 3.0181 | 3.493 | 3.9986 | 3.0181 | 3.4931 | 3.9986 | 3.0181 | 3.5746 | 4.0854 | 3.0895
NQ-Townsville Burdekin West | GI-AY-1_Giru - Ayr 1 66 kV | Power Factor | 0.89297 | 0.91428 | 0.89694 | 0.89435 | 0.91492 | 0.89828 | 0.89436 | 0.91494 | 0.89828 | 0.89435 | 0.91491 | 0.89828 | 0.893 | 0.91311 | 0.89695
NQ-Townsville Burdekin West | GI-AY-1_Giru - Ayr 1 66 kV | Rating (A) | 189 | 206 | 186 | 189 | 206 | 186 | 189 | 206 | 186 | 189 | 206 | 186 | 189 | 206 | 186
NQ-Townsville Burdekin West | GI-AY-1_Giru - Ayr 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Townsville Burdekin West | GI-AY-1_Giru - Ayr 1 66 kV | Min Voltage at Constrained Conductor | 64.465 | 63.4909 | 65.7576 | 64.554 | 62.7174 | 65.8224 | 64.5635 | 62.7348 | 65.828 | 64.5533 | 62.7148 | 65.8221 | 64.4983 | 62.6136 | 65.771
NQ-Townsville Burdekin West | GI-AY-1_Giru - Ayr 1 66 kV | Contingency Outage | ST-GI-1_Stuart-Giru 66 kV To T Only | MOPA_Clare South - Mona Park 66 kV | ST-GI-1_Stuart-Giru 66 kV To T Only | ST-GI-1_Stuart-Giru 66 kV To T Only | MOPA_Clare South - Mona Park 66 kV | ST-GI-1_Stuart-Giru 66 kV To T Only | ST-GI-1_Stuart-Giru 66 kV To T Only | MOPA_Clare South - Mona Park 66 kV | ST-GI-1_Stuart-Giru 66 kV To T Only | ST-GI-1_Stuart-Giru 66 kV To T Only | MOPA_Clare South - Mona Park 66 kV | ST-GI-1_Stuart-Giru 66 kV To T Only | ST-GI-1_Stuart-Giru 66 kV To T Only | MOPA_Clare South - Mona Park 66 kV | ST-GI-1_Stuart-Giru 66 kV To T Only
NQ-Townsville Burdekin West | HP-OO_Hermit park - Oonoonba 66 kV | % of Rated A | 52.64% | 49.54% | 45.44% | 51.94% | 48.95% | 45.12% | 54.31% | 50.66% | 42.28% | 54.27% | 50.67% | 42.22% | 54.58% | 50.92% | 42.35%
NQ-Townsville Burdekin West | HP-OO_Hermit park - Oonoonba 66 kV | Limiting Line Name | TR_LINE 106404_1 | TR_LINE 106404_1 | TR_LINE 106404_1 | TR_LINE 106404_1 | TR_LINE 106404_1 | TR_LINE 106404_1 | TR_LINE 106404_1 | TR_LINE 106404_1 | TR_LINE 106404_1 | TR_LINE 106404_1 | TR_LINE 106404_1 | TR_LINE 106404_1 | TR_LINE 106404_1 | TR_LINE 106404_1 | TR_LINE 106404_1
NQ-Townsville Burdekin West | HP-OO_Hermit park - Oonoonba 66 kV | Loading (A) | 181.6094 | 175.3699 | 141.7768 | 179.2078 | 173.2823 | 140.7777 | 187.3759 | 179.3309 | 131.9102 | 187.2355 | 179.3613 | 131.7172 | 188.2911 | 180.2604 | 132.1319
NQ-Townsville Burdekin West | HP-OO_Hermit park - Oonoonba 66 kV | Loading (MVA) | 21.477 | 20.7039 | 16.9658 | 21.1964 | 20.4595 | 16.8476 | 22.2557 | 21.3171 | 15.6666 | 22.2356 | 21.3166 | 15.6422 | 22.3506 | 21.4111 | 15.6873
NQ-Townsville Burdekin West | HP-OO_Hermit park - Oonoonba 66 kV | Loading (MW) | 18.2177 | 17.0991 | 11.7422 | 17.8603 | 16.774 | 11.5557 | 20.2645 | 17.6639 | 14.4972 | 20.2397 | 17.6545 | 14.4665 | 20.3766 | 17.7887 | 14.514
NQ-Townsville Burdekin West | HP-OO_Hermit park - Oonoonba 66 kV | Power Factor | 0.84796 | 0.8256 | 0.69185 | 0.84233 | 0.81958 | 0.68564 | 0.91031 | 0.82834 | 0.92526 | 0.91002 | 0.82791 | 0.92474 | 0.91146 | 0.83053 | 0.92511
NQ-Townsville Burdekin West | HP-OO_Hermit park - Oonoonba 66 kV | Rating (A) | 345 | 354 | 312 | 345 | 354 | 312 | 345 | 354 | 312 | 345 | 354 | 312 | 345 | 354 | 312
NQ-Townsville Burdekin West | HP-OO_Hermit park - Oonoonba 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Townsville Burdekin West | HP-OO_Hermit park - Oonoonba 66 kV | Min Voltage at Constrained Conductor | 68.276 | 68.1612 | 69.0889 | 68.2876 | 68.168 | 69.0943 | 68.5679 | 68.6299 | 68.564 | 68.5573 | 68.6165 | 68.5576 | 68.5254 | 68.5771 | 68.5392
NQ-Townsville Burdekin West | HP-OO_Hermit park - Oonoonba 66 kV | Contingency Outage | GA-TP-1_Garbutt-Townsville Port 1 66 kV | GA-TP-1_Garbutt-Townsville Port 1 66 kV | GA-TP-1_Garbutt-Townsville Port 1 66 kV | GA-TP-1_Garbutt-Townsville Port 1 66 kV | GA-TP-1_Garbutt-Townsville Port 1 66 kV | GA-TP-1_Garbutt-Townsville Port 1 66 kV | ST-RP-1_Stuart-Ross Plains 66 kV | GA-TP-1_Garbutt-Townsville Port 1 66 kV | GA-TP-1_Garbutt-Townsville Port 1 66 kV | ST-RP-1_Stuart-Ross Plains 66 kV | GA-TP-1_Garbutt-Townsville Port 1 66 kV | GA-TP-1_Garbutt-Townsville Port 1 66 kV | ST-RP-1_Stuart-Ross Plains 66 kV | GA-TP-1_Garbutt-Townsville Port 1 66 kV | GA-TP-1_Garbutt-Townsville Port 1 66 kV
NQ-Townsville Burdekin West | HU-RI-1_Hughenden-Richmond No 1 66 kV | % of Rated A | 15.88% | 14.4% | 10.4% | 15.58% | 14.05% | 10.33% | 25.63% | 21.82% | 12.38% | 25.64% | 21.83% | 12.38% | 25.81% | 21.98% | 12.26%
NQ-Townsville Burdekin West | HU-RI-1_Hughenden-Richmond No 1 66 kV | Limiting Line Name | TR_LINE 163222_1 | TR_LINE 163213_1 | TR_LINE 163213_1 | TR_LINE 163222_1 | TR_LINE 163213_1 | TR_LINE 163213_1 | TR_LINE 32108_1 | TR_LINE 32108_1 | TR_LINE 163213_1 | TR_LINE 32108_1 | TR_LINE 32108_1 | TR_LINE 163213_1 | TR_LINE 32108_1 | TR_LINE 32108_1 | TR_LINE 163213_1
NQ-Townsville Burdekin West | HU-RI-1_Hughenden-Richmond No 1 66 kV | Loading (A) | 45.2494 | 52.2897 | 34.5321 | 44.3967 | 50.9991 | 34.3098 | 73.0554 | 79.8592 | 41.0959 | 73.0773 | 79.8814 | 41.0976 | 73.5713 | 80.4537 | 40.6951
NQ-Townsville Burdekin West | HU-RI-1_Hughenden-Richmond No 1 66 kV | Loading (MVA) | 4.8296 | 5.2432 | 4.0501 | 4.7655 | 5.1525 | 4.0255 | 6.6947 | 7.4891 | 4.5533 | 6.695 | 7.4894 | 4.5528 | 6.6898 | 7.4873 | 4.502
NQ-Townsville Burdekin West | HU-RI-1_Hughenden-Richmond No 1 66 kV | Loading (MW) | 4.5769 | 5.1662 | 2.7131 | 4.4836 | 5.0557 | 2.6536 | 6.6609 | 7.4379 | 4.0201 | 6.661 | 7.438 | 4.0202 | 6.6377 | 7.413 | 4.0031
NQ-Townsville Burdekin West | HU-RI-1_Hughenden-Richmond No 1 66 kV | Power Factor | 0.94769 | 0.98531 | 0.66989 | 0.94083 | 0.98122 | 0.65919 | 0.99494 | 0.99315 | 0.88291 | 0.99493 | 0.99314 | 0.88301 | 0.99221 | 0.99008 | 0.88917
NQ-Townsville Burdekin West | HU-RI-1_Hughenden-Richmond No 1 66 kV | Rating (A) | 285 | 363 | 332 | 285 | 363 | 332 | 285 | 366 | 332 | 285 | 366 | 332 | 285 | 366 | 332
NQ-Townsville Burdekin West | HU-RI-1_Hughenden-Richmond No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Townsville Burdekin West | HU-RI-1_Hughenden-Richmond No 1 66 kV | Min Voltage at Constrained Conductor | 61.3923 | 57.891 | 67.7145 | 61.775 | 58.3295 | 67.739 | 52.9063 | 54.1417 | 63.9685 | 52.8924 | 54.1286 | 63.9587 | 52.4969 | 53.7287 | 63.8712
NQ-Townsville Burdekin West | HU-RI-1_Hughenden-Richmond No 1 66 kV | Contingency Outage | 6382 JACR-HUGH 132kV | 6382 JACR-HUGH 132kV | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | 6382 JACR-HUGH 132kV | 6382 JACR-HUGH 132kV | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | 6382 JACR-HUGH 132kV | 7460 CPRE-JACR 132kV | 6382 JACR-HUGH 132kV | 6382 JACR-HUGH 132kV | 7460 CPRE-JACR 132kV | 6382 JACR-HUGH 132kV | 6382 JACR-HUGH 132kV | 7460 CPRE-JACR 132kV | 6382 JACR-HUGH 132kV
NQ-Townsville Burdekin West | HU-WI-1 Hughenden-Winton No 1 66 kV | % of Rated A | 14.28% | 13.57% | 10.53% | 13.96% | 13.2% | 10.47% | 14.76% | 13.27% | 10.44% | 14.74% | 13.26% | 10.42% | 14.79% | 13.29% | 10.42%
NQ-Townsville Burdekin West | HU-WI-1 Hughenden-Winton No 1 66 kV | Limiting Line Name | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2
NQ-Townsville Burdekin West | HU-WI-1 Hughenden-Winton No 1 66 kV | Loading (A) | 37.4264 | 39.4957 | 27.8106 | 36.5702 | 38.4081 | 27.6377 | 38.6656 | 38.6075 | 27.5566 | 38.6281 | 38.5725 | 27.5202 | 38.7419 | 38.6711 | 27.5171
NQ-Townsville Burdekin West | HU-WI-1 Hughenden-Winton No 1 66 kV | Loading (MVA) | 3.9963 | 3.9603 | 3.2618 | 3.9268 | 3.8804 | 3.2427 | 3.7615 | 3.8681 | 3.2173 | 3.757 | 3.8639 | 3.213 | 3.7521 | 3.8583 | 3.212
NQ-Townsville Burdekin West | HU-WI-1 Hughenden-Winton No 1 66 kV | Loading (MW) | 3.6796 | 3.7766 | 1.9263 | 3.576 | 3.667 | 1.8772 | 3.6016 | 3.6694 | 1.8772 | 3.599 | 3.6671 | 1.8755 | 3.6003 | 3.6683 | 1.8755
NQ-Townsville Burdekin West | HU-WI-1 Hughenden-Winton No 1 66 kV | Power Factor | 0.92074 | 0.95362 | 0.59056 | 0.91067 | 0.94502 | 0.57891 | 0.95749 | 0.94863 | 0.58347 | 0.95794 | 0.94906 | 0.58372 | 0.95957 | 0.95074 | 0.5839
NQ-Townsville Burdekin West | HU-WI-1 Hughenden-Winton No 1 66 kV | Rating (A) | 262 | 291 | 264 | 262 | 291 | 264 | 262 | 291 | 264 | 262 | 291 | 264 | 262 | 291 | 264
NQ-Townsville Burdekin West | HU-WI-1 Hughenden-Winton No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Townsville Burdekin West | HU-WI-1 Hughenden-Winton No 1 66 kV | Min Voltage at Constrained Conductor | 61.6477 | 57.8904 | 67.7145 | 61.9934 | 58.329 | 67.739 | 56.1645 | 57.8443 | 67.4078 | 56.1528 | 57.8334 | 67.4063 | 55.9136 | 57.6024 | 67.393
NQ-Townsville Burdekin West | HU-WI-1 Hughenden-Winton No 1 66 kV | Contingency Outage | 6382 JACR-HUGH 132kV | 6382 JACR-HUGH 132kV | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | 6382 JACR-HUGH 132kV | 6382 JACR-HUGH 132kV | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | 6382 JACR-HUGH 132kV | 7460 CPRE-JACR 132kV | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | 6382 JACR-HUGH 132kV | 7460 CPRE-JACR 132kV | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | 6382 JACR-HUGH 132kV | 7460 CPRE-JACR 132kV | MR-LE-1_Millchester-Mt Leyshon 1 66 kV
NQ-Townsville Burdekin West | HUGH-HU-20 | % of Rated A | 3.044e-08% | 1.483e-05% | 1.765e-05% | 1.711e-05% | 3.917e-08% | 2.696e-06% | 2.911e-06% | 1.673e-05% | 3.693e-08% | 2.911e-06% | 1.674e-05% | 3.852e-07% | 2.911e-06% | 1.71e-05% | 1.256e-05%
NQ-Townsville Burdekin West | HUGH-HU-20 | Limiting Line Name | Link_HUGH_B624_HU-20 TORRENS CK | Link_HUGH_B624_HU-20 TORRENS CK | Link_HUGH_B624_HU-20 TORRENS CK | Link_HUGH_B624_HU-20 TORRENS CK | Link_HUGH_B624_HU-20 TORRENS CK | Link_HUGH_B624_HU-20 TORRENS CK | Link_HUGH_B624_HU-20 TORRENS CK | Link_HUGH_B624_HU-20 TORRENS CK | Link_HUGH_B624_HU-20 TORRENS CK | Link_HUGH_B624_HU-20 TORRENS CK | Link_HUGH_B624_HU-20 TORRENS CK | Link_HUGH_B624_HU-20 TORRENS CK | Link_HUGH_B624_HU-20 TORRENS CK | Link_HUGH_B624_HU-20 TORRENS CK | Link_HUGH_B624_HU-20 TORRENS CK
NQ-Townsville Burdekin West | HUGH-HU-20 | Loading (A) | 1.522e-06 | 0.00074148 | 0.00088246 | 0.00085529 | 1.9584e-06 | 0.00013482 | 0.00014553 | 0.00083648 | 1.8464e-06 | 0.00014555 | 0.00083697 | 1.9262e-05 | 0.00014554 | 0.0008551 | 0.00062795
NQ-Townsville Burdekin West | HUGH-HU-20 | Loading (MVA) | 8.7411e-08 | 4.2324e-05 | 5.0527e-05 | 4.8928e-05 | 1.1163e-07 | 7.693e-06 | 8.3621e-06 | 4.7708e-05 | 1.0619e-07 | 8.3629e-06 | 4.7727e-05 | 1.1057e-06 | 8.3619e-06 | 4.8564e-05 | 3.5984e-05
NQ-Townsville Burdekin West | HUGH-HU-20 | Loading (MW) | 8.7353e-08 | 1.1589e-05 | 2.7305e-05 | 2.0321e-05 | 1.0852e-07 | 4.7619e-07 | 1.0471e-06 | 8.8382e-06 | 1.058e-07 | 1.0461e-06 | 8.8273e-06 | 1.0817e-06 | 1.0442e-06 | 8.594e-06 | 1.5467e-05
NQ-Townsville Burdekin West | HUGH-HU-20 | Power Factor | 0.99933 | 0.27381 | 0.54041 | 0.41532 | 0.97209 | 0.061899 | 0.12522 | 0.18526 | 0.99635 | 0.12509 | 0.18496 | 0.9783 | 0.12488 | 0.17696 | 0.42982
NQ-Townsville Burdekin West | HUGH-HU-20 | Rating (A) | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000
NQ-Townsville Burdekin West | HUGH-HU-20 | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Townsville Burdekin West | HUGH-HU-20 | Min Voltage at Constrained Conductor | 33.1588 | 32.9552 | 33.0575 | 33.0286 | 32.9104 | 32.9436 | 33.1744 | 32.9288 | 33.2029 | 33.1727 | 32.9225 | 33.1402 | 33.1704 | 32.79 | 33.0847
NQ-Townsville Burdekin West | HUGH-HU-20 | Contingency Outage | HU-RI-1_Hughenden-Richmond No 1 66 kV | 6382 JACR-HUGH 132kV | 6382 JACR-HUGH 132kV | 6382 JACR-HUGH 132kV | 6383 CARI-CPRE 66kV | CHTO_Clare South - Charters Towers 66 kV | HU-RI-1_Hughenden-Richmond No 1 66 kV | 7460 CPRE-JACR 132kV | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | HU-RI-1_Hughenden-Richmond No 1 66 kV | 7460 CPRE-JACR 132kV | RI-JC-1_Richmond-Julia Creek No 1 66 kV | HU-RI-1_Hughenden-Richmond No 1 66 kV | 7460 CPRE-JACR 132kV | 6382 JACR-HUGH 132kV
NQ-Townsville Burdekin West | HUGH-HU-40 | % of Rated A | 3.868e-09% | 3.881e-09% | 3.885e-09% | 3.882e-09% | 3.882e-09% | 3.886e-09% | 3.876e-09% | 3.884e-09% | 3.873e-09% | 3.875e-09% | 3.884e-09% | 3.873e-09% | 3.874e-09% | 3.882e-09% | 3.872e-09%
NQ-Townsville Burdekin West | HUGH-HU-40 | Limiting Line Name | Link_HUGH_D624_HU-40 RICHMOND | Link_HUGH_D624_HU-40 RICHMOND | Link_HUGH_D624_HU-40 RICHMOND | Link_HUGH_D624_HU-40 RICHMOND | Link_HUGH_D624_HU-40 RICHMOND | Link_HUGH_D624_HU-40 RICHMOND | Link_HUGH_D624_HU-40 RICHMOND | Link_HUGH_D624_HU-40 RICHMOND | Link_HUGH_D624_HU-40 RICHMOND | Link_HUGH_D624_HU-40 RICHMOND | Link_HUGH_D624_HU-40 RICHMOND | Link_HUGH_D624_HU-40 RICHMOND | Link_HUGH_D624_HU-40 RICHMOND | Link_HUGH_D624_HU-40 RICHMOND | Link_HUGH_D624_HU-40 RICHMOND
NQ-Townsville Burdekin West | HUGH-HU-40 | Loading (A) | 1.9338e-07 | 1.9404e-07 | 1.9424e-07 | 1.9409e-07 | 1.9409e-07 | 1.9432e-07 | 1.9378e-07 | 1.942e-07 | 1.9363e-07 | 1.9377e-07 | 1.9419e-07 | 1.9363e-07 | 1.9369e-07 | 1.9411e-07 | 1.9359e-07
NQ-Townsville Burdekin West | HUGH-HU-40 | Loading (MVA) | 1.1106e-08 | 1.1183e-08 | 1.1205e-08 | 1.1188e-08 | 1.1188e-08 | 1.1214e-08 | 1.1153e-08 | 1.12e-08 | 1.1136e-08 | 1.1152e-08 | 1.12e-08 | 1.1135e-08 | 1.1142e-08 | 1.1191e-08 | 1.1131e-08
NQ-Townsville Burdekin West | HUGH-HU-40 | Loading (MW) | 1.1106e-08 | 1.1183e-08 | 1.1205e-08 | 1.1188e-08 | 1.1188e-08 | 1.1214e-08 | 1.1153e-08 | 1.12e-08 | 1.1136e-08 | 1.1152e-08 | 1.12e-08 | 1.1135e-08 | 1.1142e-08 | 1.1191e-08 | 1.1131e-08
NQ-Townsville Burdekin West | HUGH-HU-40 | Power Factor | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
NQ-Townsville Burdekin West | HUGH-HU-40 | Rating (A) | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000
NQ-Townsville Burdekin West | HUGH-HU-40 | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Townsville Burdekin West | HUGH-HU-40 | Min Voltage at Constrained Conductor | 33.1588 | 33.2727 | 33.3068 | 33.2806 | 33.2814 | 33.3201 | 33.2285 | 33.2992 | 33.2029 | 33.2271 | 33.2988 | 33.2021 | 33.2121 | 33.2846 | 33.1955
NQ-Townsville Burdekin West | HUGH-HU-40 | Contingency Outage | HU-RI-1_Hughenden-Richmond No 1 66 kV | RI-JC-1_Richmond-Julia Creek No 1 66 kV | CR-HU-1_Cape River-Hughenden No 1 66 kV | 7182 Ross - Milchester | RI-JC-1_Richmond-Julia Creek No 1 66 kV | CR-HU-1_Cape River-Hughenden No 1 66 kV | HU-WI-1 Hughenden-Winton No 1 66 kV | HU-WI-1 Hughenden-Winton No 1 66 kV | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | HU-WI-1 Hughenden-Winton No 1 66 kV | HU-WI-1 Hughenden-Winton No 1 66 kV | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | HU-WI-1 Hughenden-Winton No 1 66 kV | HU-WI-1 Hughenden-Winton No 1 66 kV | MR-LE-1_Millchester-Mt Leyshon 1 66 kV
NQ-Townsville Burdekin West | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | % of Rated A | 39.09% | 27.06% | 18.96% | 38.9% | 27.3% | 18.7% | 38.85% | 27.26% | 18.69% | 39.12% | 27.45% | 18.69% | 39.75% | 27.9% | 18.78%
NQ-Townsville Burdekin West | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Limiting Line Name | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1
NQ-Townsville Burdekin West | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Loading (A) | 66.0553 | 64.9532 | 44.3768 | 65.7456 | 65.5319 | 43.7675 | 65.662 | 65.4236 | 43.7349 | 66.1179 | 65.891 | 43.7415 | 67.1713 | 66.9555 | 43.9522
NQ-Townsville Burdekin West | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Loading (MVA) | 7.3039 | 7.2477 | 5.1319 | 7.2835 | 7.2233 | 5.0648 | 7.2755 | 7.2135 | 5.0613 | 7.324 | 7.2627 | 5.0617 | 7.4322 | 7.371 | 5.0838
NQ-Townsville Burdekin West | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Loading (MW) | 6.819 | 6.733 | 1.2876 | 6.8015 | 6.7164 | 1.2151 | 6.7922 | 6.7041 | 1.2064 | 6.8462 | 6.7601 | 1.1859 | 6.9701 | 6.8854 | 1.1757
NQ-Townsville Burdekin West | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Power Factor | 0.93362 | 0.92899 | 0.25083 | 0.93383 | 0.92983 | 0.23984 | 0.93358 | 0.92939 | 0.23828 | 0.93476 | 0.9308 | 0.23422 | 0.93782 | 0.93412 | 0.2312
NQ-Townsville Burdekin West | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Rating (A) | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234
NQ-Townsville Burdekin West | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Townsville Burdekin West | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Min Voltage at Constrained Conductor | 63.8364 | 64.4207 | 66.7672 | 63.9579 | 63.6363 | 66.8114 | 63.9687 | 63.655 | 66.8155 | 63.9516 | 63.6345 | 66.8104 | 63.8786 | 63.5566 | 66.7801
NQ-Townsville Burdekin West | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Contingency Outage | EAAY_Clare South - East Ayr 66 kV | EAAY_Clare South - East Ayr 66 kV | AY-EA-1_Ayr - East Ayr No 1 66 kV | EAAY_Clare South - East Ayr 66 kV | EAAY_Clare South - East Ayr 66 kV | AY-EA-1_Ayr - East Ayr No 1 66 kV | EAAY_Clare South - East Ayr 66 kV | EAAY_Clare South - East Ayr 66 kV | AY-EA-1_Ayr - East Ayr No 1 66 kV | EAAY_Clare South - East Ayr 66 kV | EAAY_Clare South - East Ayr 66 kV | AY-EA-1_Ayr - East Ayr No 1 66 kV | EAAY_Clare South - East Ayr 66 kV | EAAY_Clare South - East Ayr 66 kV | AY-EA-1_Ayr - East Ayr No 1 66 kV
NQ-Townsville Burdekin West | KA-AY-01_Ayr - Kalamia No 1 66 kV | % of Rated A | 12.02% | 13.7% | 9.094% | 11.99% | 13.87% | 9.083% | 11.71% | 13.53% | 8.868% | 11.99% | 13.87% | 9.084% | 12.01% | 13.89% | 9.091%
NQ-Townsville Burdekin West | KA-AY-01_Ayr - Kalamia No 1 66 kV | Limiting Line Name | TR_LINE 32782_1 | TR_LINE 32782_1 | TR_LINE 32782_1 | TR_LINE 32782_1 | TR_LINE 32782_1 | TR_LINE 32782_1 | TR_LINE 32782_1 | TR_LINE 32782_1 | TR_LINE 32782_1 | TR_LINE 32782_1 | TR_LINE 32782_1 | TR_LINE 32782_1 | TR_LINE 32782_1 | TR_LINE 32782_1 | TR_LINE 32782_1
NQ-Townsville Burdekin West | KA-AY-01_Ayr - Kalamia No 1 66 kV | Loading (A) | 23.9102 | 30.5461 | 18.5521 | 23.867 | 30.9263 | 18.53 | 23.3067 | 30.1806 | 18.0905 | 23.8697 | 30.9276 | 18.5312 | 23.8921 | 30.9687 | 18.5462
NQ-Townsville Burdekin West | KA-AY-01_Ayr - Kalamia No 1 66 kV | Loading (MVA) | 2.6245 | 3.3773 | 2.0949 | 2.6244 | 3.3772 | 2.0948 | 2.5634 | 3.2972 | 2.0455 | 2.6244 | 3.3772 | 2.0948 | 2.6244 | 3.3774 | 2.0949
NQ-Townsville Burdekin West | KA-AY-01_Ayr - Kalamia No 1 66 kV | Loading (MW) | 2.3047 | 2.9543 | 1.8443 | 2.3046 | 2.9543 | 1.8443 | 2.2511 | 2.8854 | 1.8014 | 2.3046 | 2.9543 | 1.8443 | 2.3047 | 2.9543 | 1.8443
NQ-Townsville Burdekin West | KA-AY-01_Ayr - Kalamia No 1 66 kV | Power Factor | 0.87812 | 0.87472 | 0.88036 | 0.87816 | 0.87475 | 0.88039 | 0.87813 | 0.87509 | 0.88064 | 0.87816 | 0.87475 | 0.88039 | 0.87814 | 0.87471 | 0.88037
NQ-Townsville Burdekin West | KA-AY-01_Ayr - Kalamia No 1 66 kV | Rating (A) | 199 | 223 | 204 | 199 | 223 | 204 | 199 | 223 | 204 | 199 | 223 | 204 | 199 | 223 | 204
NQ-Townsville Burdekin West | KA-AY-01_Ayr - Kalamia No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Townsville Burdekin West | KA-AY-01_Ayr - Kalamia No 1 66 kV | Min Voltage at Constrained Conductor | 63.3729 | 63.8344 | 65.1943 | 63.4842 | 63.0478 | 65.2701 | 63.5011 | 63.0752 | 65.2815 | 63.4773 | 63.0453 | 65.2659 | 63.4195 | 62.9646 | 65.2145
NQ-Townsville Burdekin West | KA-AY-01_Ayr - Kalamia No 1 66 kV | Contingency Outage | MOPA_Clare South - Mona Park 66 kV | MOPA_Clare South - Mona Park 66 kV | MOPA_Clare South - Mona Park 66 kV | MOPA_Clare South - Mona Park 66 kV | MOPA_Clare South - Mona Park 66 kV | MOPA_Clare South - Mona Park 66 kV | MOPA_Clare South - Mona Park 66 kV | MOPA_Clare South - Mona Park 66 kV | MOPA_Clare South - Mona Park 66 kV | MOPA_Clare South - Mona Park 66 kV | MOPA_Clare South - Mona Park 66 kV | MOPA_Clare South - Mona Park 66 kV | MOPA_Clare South - Mona Park 66 kV | MOPA_Clare South - Mona Park 66 kV | MOPA_Clare South - Mona Park 66 kV
NQ-Townsville Burdekin West | MAFU-07_Max Fulton No 7 11 kV | % of Rated A | 1.175% | 1.18% | 1.176% | 1.174% | 1.179% | 1.176% | 1.177% | 1.181% | 1.182% | 1.177% | 1.181% | 1.182% | 1.176% | 1.18% | 1.181%
NQ-Townsville Burdekin West | MAFU-07_Max Fulton No 7 11 kV | Limiting Line Name | HV_CABLE MF-07A 12159603 | HV_CABLE MF-07A 12159603 | HV_CABLE MF-07A 12159603 | HV_CABLE MF-07A 12159603 | HV_CABLE MF-07A 12159603 | HV_CABLE MF-07A 12159603 | HV_CABLE MF-07A 12159603 | HV_CABLE MF-07A 12159603 | HV_CABLE MF-07A 12159603 | HV_CABLE MF-07A 12159603 | HV_CABLE MF-07A 12159603 | HV_CABLE MF-07A 12159603 | HV_CABLE MF-07A 12159603 | HV_CABLE MF-07A 12159603 | HV_CABLE MF-07A 12159603
NQ-Townsville Burdekin West | MAFU-07_Max Fulton No 7 11 kV | Loading (A) | 3.7008 | 3.7164 | 3.705 | 3.6971 | 3.7127 | 3.703 | 3.7071 | 3.7194 | 3.7224 | 3.7067 | 3.7187 | 3.7221 | 3.7047 | 3.7165 | 3.7211
NQ-Townsville Burdekin West | MAFU-07_Max Fulton No 7 11 kV | Loading (MVA) | 0.07203 | 0.072638 | 0.072193 | 0.071888 | 0.072493 | 0.072118 | 0.072277 | 0.072756 | 0.072872 | 0.07226 | 0.07273 | 0.072861 | 0.072182 | 0.072641 | 0.072821
NQ-Townsville Burdekin West | MAFU-07_Max Fulton No 7 11 kV | Loading (MW) | 0.0014421 | 0.0014543 | 0.0014453 | 0.0014392 | 0.0014514 | 0.0014438 | 0.001447 | 0.0014566 | 0.0014589 | 0.0014467 | 0.0014561 | 0.0014587 | 0.0014451 | 0.0014543 | 0.0014579
NQ-Townsville Burdekin West | MAFU-07_Max Fulton No 7 11 kV | Power Factor | 0.020019 | 0.020019 | 0.020019 | 0.020019 | 0.020019 | 0.020019 | 0.020019 | 0.020019 | 0.020019 | 0.020019 | 0.020019 | 0.020019 | 0.020019 | 0.020019 | 0.020019
NQ-Townsville Burdekin West | MAFU-07_Max Fulton No 7 11 kV | Rating (A) | 315 | 315 | 315 | 315 | 315 | 315 | 315 | 315 | 315 | 315 | 315 | 315 | 315 | 315 | 315
NQ-Townsville Burdekin West | MAFU-07_Max Fulton No 7 11 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Townsville Burdekin West | MAFU-07_Max Fulton No 7 11 kV | Min Voltage at Constrained Conductor | 11.2372 | 11.2846 | 11.2499 | 11.2261 | 11.2733 | 11.244 | 11.2564 | 11.2937 | 11.3027 | 11.2551 | 11.2917 | 11.3018 | 11.2491 | 11.2848 | 11.2988
NQ-Townsville Burdekin West | MAFU-07_Max Fulton No 7 11 kV | Contingency Outage | MF-TP-1_Max Fulton-TOPO No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | ST-TOPO-1_Stuart-Townsville Port 66 kV | MF-TP-1_Max Fulton-TOPO No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | ST-TOPO-1_Stuart-Townsville Port 66 kV | MF-TP-1_Max Fulton-TOPO No 1 66 kV | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | MF-TP-1_Max Fulton-TOPO No 1 66 kV | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | MF-TP-1_Max Fulton-TOPO No 1 66 kV | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | GA-TP-1_Garbutt-Townsville Port 1 66 kV
NQ-Townsville Burdekin West | MF-TP-1_Max Fulton-TOPO No 1 66 kV | % of Rated A | 22.28% | 16.75% | 9.875% | 24.78% | 18.62% | 10.98% | 24.35% | 18.24% | 10.93% | 24.35% | 18.24% | 10.93% | 24.87% | 18.63% | 11.16%
NQ-Townsville Burdekin West | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Limiting Line Name | TR_LINE 31651_1 | TR_LINE 31651_1 | TR_LINE 31651_1 | TR_LINE 31651_1 | TR_LINE 31651_1 | TR_LINE 31651_1 | TR_LINE 31651_1 | TR_LINE 31651_1 | TR_LINE 31651_1 | TR_LINE 31651_1 | TR_LINE 31651_1 | TR_LINE 31651_1 | TR_LINE 31651_1 | TR_LINE 31651_1 | TR_LINE 31651_1
NQ-Townsville Burdekin West | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Loading (A) | 57.4874 | 49.4049 | 26.8604 | 63.9391 | 54.9403 | 29.853 | 62.8131 | 53.7964 | 29.7317 | 62.827 | 53.8114 | 29.7355 | 64.1548 | 54.9502 | 30.3507
NQ-Townsville Burdekin West | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Loading (MVA) | 6.7637 | 5.8128 | 3.2143 | 7.5191 | 6.4612 | 3.5717 | 7.4175 | 6.3737 | 3.5243 | 7.4176 | 6.3737 | 3.5243 | 7.5689 | 6.5035 | 3.5959
NQ-Townsville Burdekin West | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Loading (MW) | 6.6858 | 5.7546 | 3.1998 | 7.4239 | 6.3897 | 3.5524 | 7.3254 | 6.3049 | 3.5053 | 7.3254 | 6.3049 | 3.5053 | 7.473 | 6.432 | 3.5759
NQ-Townsville Burdekin West | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Power Factor | 0.98846 | 0.98996 | 0.99547 | 0.98732 | 0.98891 | 0.99458 | 0.98756 | 0.9892 | 0.99459 | 0.98756 | 0.98919 | 0.99458 | 0.98732 | 0.98897 | 0.99441
NQ-Townsville Burdekin West | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Rating (A) | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272
NQ-Townsville Burdekin West | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Townsville Burdekin West | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Min Voltage at Constrained Conductor | 67.9277 | 67.9287 | 69.0892 | 67.8933 | 67.8977 | 69.0766 | 68.1772 | 68.4022 | 68.4381 | 68.1625 | 68.3835 | 68.4294 | 68.1133 | 68.3306 | 68.4035
NQ-Townsville Burdekin West | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Contingency Outage | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV
NQ-Townsville Burdekin West | MF-TP-2_Max Fulton-TOPO No 2 66 kV | % of Rated A | 24.32% | 19.16% | 15.54% | 26.33% | 20.59% | 16.09% | 26% | 20.33% | 16.21% | 26% | 20.34% | 16.21% | 26.42% | 20.63% | 16.33%
NQ-Townsville Burdekin West | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Limiting Line Name | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1
NQ-Townsville Burdekin West | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Loading (A) | 62.7376 | 56.535 | 42.2708 | 67.9348 | 60.7323 | 43.7633 | 67.0785 | 59.9844 | 44.1018 | 67.0864 | 59.9908 | 44.1008 | 68.1619 | 60.8553 | 44.4105
NQ-Townsville Burdekin West | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Loading (MVA) | 7.3857 | 6.6553 | 5.0887 | 7.9937 | 7.1464 | 5.2678 | 7.9259 | 7.1107 | 5.2722 | 7.9251 | 7.1096 | 5.2717 | 8.0464 | 7.2065 | 5.3077
NQ-Townsville Burdekin West | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Loading (MW) | 6.6913 | 5.7602 | 3.2059 | 7.4294 | 6.3952 | 3.5585 | 7.331 | 6.3106 | 3.5114 | 7.331 | 6.3106 | 3.5114 | 7.4786 | 6.4376 | 3.582
NQ-Townsville Burdekin West | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Power Factor | 0.90599 | 0.86551 | 0.63 | 0.9294 | 0.89489 | 0.67552 | 0.92494 | 0.88747 | 0.66603 | 0.92503 | 0.88762 | 0.66609 | 0.92943 | 0.89331 | 0.67486
NQ-Townsville Burdekin West | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Rating (A) | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272
NQ-Townsville Burdekin West | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Townsville Burdekin West | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Min Voltage at Constrained Conductor | 67.9662 | 67.9652 | 69.5038 | 67.9333 | 67.9356 | 69.4957 | 68.217 | 68.44 | 69.0201 | 68.2023 | 68.4212 | 69.0148 | 68.1534 | 68.3686 | 69.0016
NQ-Townsville Burdekin West | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Contingency Outage | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | ST-TOPO-1_Stuart-Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | ST-TOPO-1_Stuart-Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | GA-TP-1_Garbutt-Townsville Port 1 66 kV
NQ-Townsville Burdekin West | MOPA_Clare South - Mona Park 66 kV | % of Rated A | 96.5% | 67.05% | 47.46% | 95.14% | 66.84% | 46.9% | 95.03% | 66.76% | 46.85% | 95.36% | 66.97% | 46.99% | 96.89% | 68.01% | 47.77%
NQ-Townsville Burdekin West | MOPA_Clare South - Mona Park 66 kV | Limiting Line Name | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1
NQ-Townsville Burdekin West | MOPA_Clare South - Mona Park 66 kV | Loading (A) | 202.6487 | 211.2087 | 147.1311 | 199.792 | 210.5535 | 145.3856 | 199.5635 | 210.2956 | 145.2324 | 200.2629 | 210.9686 | 145.6612 | 203.464 | 214.2363 | 148.0764
NQ-Townsville Burdekin West | MOPA_Clare South - Mona Park 66 kV | Loading (MVA) | 23.7141 | 25.0056 | 17.2826 | 23.3943 | 24.6296 | 17.0806 | 23.3694 | 24.6031 | 17.0632 | 23.4513 | 24.6817 | 17.1138 | 23.8214 | 25.0586 | 17.395
NQ-Townsville Burdekin West | MOPA_Clare South - Mona Park 66 kV | Loading (MW) | 22.5009 | 23.6495 | 16.7822 | 22.4792 | 23.3016 | 16.6002 | 22.4501 | 23.2705 | 16.5795 | 22.5261 | 23.341 | 16.6269 | 22.8569 | 23.671 | 16.8813
NQ-Townsville Burdekin West | MOPA_Clare South - Mona Park 66 kV | Power Factor | 0.94884 | 0.94577 | 0.97104 | 0.96088 | 0.94608 | 0.97188 | 0.96066 | 0.94583 | 0.97165 | 0.96055 | 0.94568 | 0.97155 | 0.95951 | 0.94463 | 0.97047
NQ-Townsville Burdekin West | MOPA_Clare South - Mona Park 66 kV | Rating (A) | 210 | 315 | 310 | 210 | 315 | 310 | 210 | 315 | 310 | 210 | 315 | 310 | 210 | 315 | 310
NQ-Townsville Burdekin West | MOPA_Clare South - Mona Park 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Townsville Burdekin West | MOPA_Clare South - Mona Park 66 kV | Min Voltage at Constrained Conductor | 67.5567 | 68.3484 | 67.8146 | 67.5988 | 67.5302 | 67.8264 | 67.6042 | 67.5403 | 67.8292 | 67.6041 | 67.5398 | 67.8297 | 67.5905 | 67.525 | 67.8199
NQ-Townsville Burdekin West | MOPA_Clare South - Mona Park 66 kV | Contingency Outage | EAAY_Clare South - East Ayr 66 kV | EAAY_Clare South - East Ayr 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | EAAY_Clare South - East Ayr 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | EAAY_Clare South - East Ayr 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | EAAY_Clare South - East Ayr 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | EAAY_Clare South - East Ayr 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV
NQ-Townsville Burdekin West | MP-AY-1 Mona Park - Ayr No 1 66 kV | % of Rated A | 62.75% | 44.16% | 27.38% | 61.99% | 43.89% | 27.06% | 61.84% | 43.77% | 26.99% | 62.18% | 44.01% | 27.13% | 62.89% | 44.51% | 27.42%
NQ-Townsville Burdekin West | MP-AY-1 Mona Park - Ayr No 1 66 kV | Limiting Line Name | TR_LINE 32495_1 | TR_LINE 32495_1 | TR_LINE 32534_1 | TR_LINE 32495_1 | TR_LINE 32495_1 | TR_LINE 32534_1 | TR_LINE 32495_1 | TR_LINE 32495_1 | TR_LINE 32534_1 | TR_LINE 32495_1 | TR_LINE 32495_1 | TR_LINE 32534_1 | TR_LINE 32495_1 | TR_LINE 32495_1 | TR_LINE 32534_1
NQ-Townsville Burdekin West | MP-AY-1 Mona Park - Ayr No 1 66 kV | Loading (A) | 124.8715 | 129.8332 | 79.1194 | 123.3602 | 129.0329 | 78.2032 | 123.0518 | 128.6792 | 77.9922 | 123.7294 | 129.3826 | 78.3942 | 125.1607 | 130.85 | 79.2358
NQ-Townsville Burdekin West | MP-AY-1 Mona Park - Ayr No 1 66 kV | Loading (MVA) | 13.8745 | 14.5055 | 9.1002 | 13.7237 | 14.2402 | 8.9999 | 13.6921 | 14.2628 | 8.9759 | 13.7636 | 14.3382 | 9.0215 | 13.9072 | 14.4856 | 9.1131
NQ-Townsville Burdekin West | MP-AY-1 Mona Park - Ayr No 1 66 kV | Loading (MW) | 13.8058 | 14.2828 | 9.0999 | 13.661 | 14.031 | 8.999 | 13.6318 | 14.1861 | 8.9747 | 13.7016 | 14.2623 | 9.0206 | 13.842 | 14.4087 | 9.1125
NQ-Townsville Burdekin West | MP-AY-1 Mona Park - Ayr No 1 66 kV | Power Factor | 0.99505 | 0.98464 | 0.99997 | 0.99543 | 0.98531 | 0.9999 | 0.99559 | 0.99463 | 0.99986 | 0.9955 | 0.9947 | 0.99989 | 0.99531 | 0.99469 | 0.99994
NQ-Townsville Burdekin West | MP-AY-1 Mona Park - Ayr No 1 66 kV | Rating (A) | 199 | 294 | 289 | 199 | 294 | 289 | 199 | 294 | 289 | 199 | 294 | 289 | 199 | 294 | 289
NQ-Townsville Burdekin West | MP-AY-1 Mona Park - Ayr No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Townsville Burdekin West | MP-AY-1 Mona Park - Ayr No 1 66 kV | Min Voltage at Constrained Conductor | 64.1483 | 64.5029 | 66.4048 | 64.2287 | 63.7159 | 66.4422 | 64.2414 | 63.9922 | 66.4448 | 64.2231 | 63.9809 | 66.4399 | 64.1512 | 63.9137 | 66.4013
NQ-Townsville Burdekin West | MP-AY-1 Mona Park - Ayr No 1 66 kV | Contingency Outage | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | EAAY_Clare South - East Ayr 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | EAAY_Clare South - East Ayr 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV
NQ-Townsville Burdekin West | MR-CR-1_Millchester-Cape River 1 66 kV | % of Rated A | 66.87% | 55.21% | 33.01% | 88.48% | 54.57% | 32.48% | 82.91% | 68.8% | 38.88% | 82.95% | 68.84% | 38.89% | 82.83% | 68.75% | 38.84%
NQ-Townsville Burdekin West | MR-CR-1_Millchester-Cape River 1 66 kV | Limiting Line Name | TR_LINE 165123_1 | TR_LINE 165123_1 | TR_LINE 165123_1 | TR_LINE 165123_1 | TR_LINE 165123_1 | TR_LINE 165123_1 | TR_LINE 165123_1 | TR_LINE 165123_1 | TR_LINE 165123_1 | TR_LINE 165123_1 | TR_LINE 165123_1 | TR_LINE 165123_1 | TR_LINE 165123_1 | TR_LINE 165123_1 | TR_LINE 165123_1
NQ-Townsville Burdekin West | MR-CR-1_Millchester-Cape River 1 66 kV | Loading (A) | 103.6523 | 126.4343 | 74.6089 | 137.1502 | 124.955 | 73.3961 | 128.5172 | 157.5604 | 87.8762 | 128.5798 | 157.6519 | 87.895 | 128.3796 | 157.4477 | 87.7771
NQ-Townsville Burdekin West | MR-CR-1_Millchester-Cape River 1 66 kV | Loading (MVA) | 12.1485 | 14.809 | 8.7628 | 13.6383 | 14.6046 | 8.6233 | 15.0581 | 18.3934 | 10.3112 | 15.0623 | 18.3998 | 10.3121 | 15.0325 | 18.3679 | 10.295
NQ-Townsville Burdekin West | MR-CR-1_Millchester-Cape River 1 66 kV | Loading (MW) | 11.6352 | 14.0938 | 8.4162 | 8.8264 | 13.8455 | 8.2901 | 14.3414 | 17.3862 | 9.8775 | 14.3399 | 17.3859 | 9.876 | 14.3022 | 17.3452 | 9.8558
NQ-Townsville Burdekin West | MR-CR-1_Millchester-Cape River 1 66 kV | Power Factor | 0.95774 | 0.95169 | 0.96044 | 0.64708 | 0.94801 | 0.96135 | 0.95239 | 0.94521 | 0.95793 | 0.95202 | 0.94486 | 0.95771 | 0.95141 | 0.94429 | 0.95735
NQ-Townsville Burdekin West | MR-CR-1_Millchester-Cape River 1 66 kV | Rating (A) | 155 | 229 | 226 | 155 | 229 | 226 | 155 | 229 | 226 | 155 | 229 | 226 | 155 | 229 | 226
NQ-Townsville Burdekin West | MR-CR-1_Millchester-Cape River 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Townsville Burdekin West | MR-CR-1_Millchester-Cape River 1 66 kV | Min Voltage at Constrained Conductor | 67.666 | 67.6215 | 67.8082 | 57.412 | 67.478 | 67.8315 | 67.6445 | 67.3965 | 67.7434 | 67.6303 | 67.3808 | 67.7347 | 67.6017 | 67.3511 | 67.7128
NQ-Townsville Burdekin West | MR-CR-1_Millchester-Cape River 1 66 kV | Contingency Outage | CT-CR-1_Charters Towers-CARI No 1 66 kV | CT-CR-1_Charters Towers-CARI No 1 66 kV | CT-CR-1_Charters Towers-CARI No 1 66 kV | 7182 Ross - Milchester | CT-CR-1_Charters Towers-CARI No 1 66 kV | CT-CR-1_Charters Towers-CARI No 1 66 kV | CT-CR-1_Charters Towers-CARI No 1 66 kV | CT-CR-1_Charters Towers-CARI No 1 66 kV | CT-CR-1_Charters Towers-CARI No 1 66 kV | CT-CR-1_Charters Towers-CARI No 1 66 kV | CT-CR-1_Charters Towers-CARI No 1 66 kV | CT-CR-1_Charters Towers-CARI No 1 66 kV | CT-CR-1_Charters Towers-CARI No 1 66 kV | CT-CR-1_Charters Towers-CARI No 1 66 kV | CT-CR-1_Charters Towers-CARI No 1 66 kV
NQ-Townsville Burdekin West | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | % of Rated A | 38.68% | 31.95% | 38.57% | 46.6% | 31.54% | 37.98% | 38.2% | 31.61% | 38.3% | 38.23% | 31.63% | 38.33% | 38.77% | 32.04% | 38.91%
NQ-Townsville Burdekin West | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Limiting Line Name | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 49923_1
NQ-Townsville Burdekin West | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Loading (A) | 72.7233 | 65.4962 | 71.3536 | 87.6148 | 64.6665 | 70.2599 | 71.8225 | 64.8105 | 70.8538 | 71.8698 | 64.8474 | 70.9083 | 72.8895 | 65.688 | 71.976
NQ-Townsville Burdekin West | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Loading (MVA) | 8.1452 | 7.3117 | 7.5547 | 8.306 | 7.2136 | 7.4498 | 8.0356 | 7.2161 | 7.4603 | 8.0372 | 7.217 | 7.4619 | 8.1485 | 7.3098 | 7.5663
NQ-Townsville Burdekin West | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Loading (MW) | 7.1545 | 6.4561 | 6.642 | 7.1614 | 6.3599 | 6.5414 | 7.063 | 6.3747 | 6.5596 | 7.048 | 6.361 | 6.5457 | 7.1556 | 6.4567 | 6.6462
NQ-Townsville Burdekin West | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Power Factor | 0.86281 | 0.86493 | 0.8647 | 0.85424 | 0.86313 | 0.86303 | 0.86314 | 0.86514 | 0.86474 | 0.86098 | 0.86299 | 0.86258 | 0.86269 | 0.86544 | 0.86427
NQ-Townsville Burdekin West | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Rating (A) | 188 | 205 | 185 | 188 | 205 | 185 | 188 | 205 | 185 | 188 | 205 | 185 | 188 | 205 | 185
NQ-Townsville Burdekin West | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Townsville Burdekin West | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Min Voltage at Constrained Conductor | 63.815 | 63.9919 | 60.1772 | 52.7742 | 63.9995 | 60.3363 | 63.7901 | 63.853 | 59.8504 | 63.7654 | 63.8324 | 59.8201 | 63.6798 | 63.7626 | 59.6907
NQ-Townsville Burdekin West | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Contingency Outage | WO-CT-1_Woodstock-CHTO No 1 66 kV | 6383 CARI-CPRE 66kV | 7182 Ross - Milchester | 7182 Ross - Milchester | 7460 CPRE-JACR 132kV | 7182 Ross - Milchester | 6383 CARI-CPRE 66kV | 7460 CPRE-JACR 132kV | 7182 Ross - Milchester | 6383 CARI-CPRE 66kV | 7460 CPRE-JACR 132kV | 7182 Ross - Milchester | 6383 CARI-CPRE 66kV | 7460 CPRE-JACR 132kV | 7182 Ross - Milchester
NQ-Townsville Burdekin West | PA-RP-1_Peter Arlett-Ross Plains 66 kV | % of Rated A | 77.41% | 61.9% | 49.08% | 77.04% | 61.6% | 48.85% | 76.68% | 64.35% | 52.56% | 77.06% | 64.58% | 52.66% | 77.82% | 64.87% | 52.77%
NQ-Townsville Burdekin West | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Limiting Line Name | TR_LINE 32958_1 | TR_LINE 32958_1 | TR_LINE 32958_1 | TR_LINE 32958_1 | TR_LINE 32958_1 | TR_LINE 32958_1 | TR_LINE 32958_1 | TR_LINE 45760_1 | TR_LINE 45760_1 | TR_LINE 32958_1 | TR_LINE 45760_1 | TR_LINE 45760_1 | TR_LINE 32958_1 | TR_LINE 45760_1 | TR_LINE 45760_1
NQ-Townsville Burdekin West | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Loading (A) | 199.7292 | 182.5934 | 133.4969 | 198.762 | 181.7257 | 132.8762 | 197.8425 | 189.8394 | 142.9755 | 198.8098 | 190.5243 | 143.2344 | 200.7873 | 191.3764 | 143.5397
NQ-Townsville Burdekin West | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Loading (MVA) | 23.3393 | 21.3494 | 15.8329 | 23.2311 | 21.2511 | 15.761 | 23.2216 | 22.6455 | 17.0243 | 23.3298 | 22.7226 | 17.0535 | 23.5469 | 22.8125 | 17.0857
NQ-Townsville Burdekin West | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Loading (MW) | 22.354 | 20.5166 | 15.3487 | 22.2547 | 20.4256 | 15.2808 | 22.2533 | 22.0753 | 17.0151 | 22.3526 | 22.1613 | 17.0444 | 22.5512 | 22.2667 | 17.0768
NQ-Townsville Burdekin West | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Power Factor | 0.95778 | 0.96099 | 0.96942 | 0.95797 | 0.96115 | 0.96953 | 0.9583 | 0.97479 | 0.99946 | 0.95811 | 0.97527 | 0.99946 | 0.95772 | 0.97604 | 0.99948
NQ-Townsville Burdekin West | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Rating (A) | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272
NQ-Townsville Burdekin West | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Townsville Burdekin West | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Min Voltage at Constrained Conductor | 67.422 | 67.4663 | 68.4486 | 67.436 | 67.4764 | 68.4564 | 67.7222 | 68.866 | 68.7406 | 67.7065 | 68.8518 | 68.7339 | 67.6629 | 68.8165 | 68.7171
NQ-Townsville Burdekin West | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Contingency Outage | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | 6325_Oonoonba-Stuart 66 kV | 6325_Oonoonba-Stuart 66 kV | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | 6325_Oonoonba-Stuart 66 kV | 6325_Oonoonba-Stuart 66 kV | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | 6325_Oonoonba-Stuart 66 kV | 6325_Oonoonba-Stuart 66 kV
NQ-Townsville Burdekin West | PEAR-01_Hospital 3 11kV | % of Rated A | 0.3823% | 0.3863% | 0.3869% | 0.3824% | 0.3864% | 0.387% | 0.3848% | 0.3876% | 0.3899% | 0.3847% | 0.3875% | 0.3898% | 0.3843% | 0.3876% | 0.3896%
NQ-Townsville Burdekin West | PEAR-01_Hospital 3 11kV | Limiting Line Name | PEAR-01 FEEDER C | PEAR-01 FEEDER C | PEAR-01 FEEDER C | PEAR-01 FEEDER C | PEAR-01 FEEDER C | PEAR-01 FEEDER C | PEAR-01 FEEDER C | PEAR-01 FEEDER C | PEAR-01 FEEDER C | PEAR-01 FEEDER C | PEAR-01 FEEDER C | PEAR-01 FEEDER C | PEAR-01 FEEDER C | PEAR-01 FEEDER C | PEAR-01 FEEDER C
NQ-Townsville Burdekin West | PEAR-01_Hospital 3 11kV | Loading (A) | 1.8502 | 1.8697 | 1.8726 | 1.8509 | 1.8702 | 1.8729 | 1.8624 | 1.8761 | 1.8871 | 1.8617 | 1.8754 | 1.8867 | 1.8601 | 1.8761 | 1.8859
NQ-Townsville Burdekin West | PEAR-01_Hospital 3 11kV | Loading (MVA) | 0.0348 | 0.035535 | 0.035645 | 0.034825 | 0.035553 | 0.035658 | 0.035259 | 0.035779 | 0.0362 | 0.035233 | 0.035751 | 0.036186 | 0.035173 | 0.035781 | 0.036152
NQ-Townsville Burdekin West | PEAR-01_Hospital 3 11kV | Loading (MW) | 0.00069617 | 0.00071087 | 0.00071307 | 0.00069667 | 0.00071123 | 0.00071332 | 0.00070534 | 0.00071575 | 0.00072418 | 0.00070484 | 0.0007152 | 0.00072389 | 0.00070364 | 0.0007158 | 0.00072322
NQ-Townsville Burdekin West | PEAR-01_Hospital 3 11kV | Power Factor | 0.020005 | 0.020005 | 0.020005 | 0.020005 | 0.020005 | 0.020005 | 0.020005 | 0.020005 | 0.020005 | 0.020005 | 0.020005 | 0.020005 | 0.020005 | 0.020005 | 0.020005
NQ-Townsville Burdekin West | PEAR-01_Hospital 3 11kV | Rating (A) | 484 | 484 | 484 | 484 | 484 | 484 | 484 | 484 | 484 | 484 | 484 | 484 | 484 | 484 | 484
NQ-Townsville Burdekin West | PEAR-01_Hospital 3 11kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Townsville Burdekin West | PEAR-01_Hospital 3 11kV | Min Voltage at Constrained Conductor | 10.859 | 10.9731 | 10.99 | 10.8629 | 10.9759 | 10.992 | 10.9303 | 11.0107 | 11.0754 | 10.9264 | 11.0064 | 11.0731 | 10.9171 | 11.0111 | 11.068
NQ-Townsville Burdekin West | PEAR-01_Hospital 3 11kV | Contingency Outage | BO-DG-1_Bohle-Dan Gleeson 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | 6299_Townsville Port 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | 6299_Townsville Port 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | BC-IN-1_Black River - Ingham No 1 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | BC-IN-1_Black River - Ingham No 1 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV
NQ-Townsville Burdekin West | PEAR-06_Hospital 1 11kV | % of Rated A | 0.5397% | 0.5454% | 0.5462% | 0.5399% | 0.5455% | 0.5463% | 0.5432% | 0.5472% | 0.5504% | 0.543% | 0.547% | 0.5503% | 0.5426% | 0.5472% | 0.5501%
NQ-Townsville Burdekin West | PEAR-06_Hospital 1 11kV | Limiting Line Name | PEAR-06 FEEDER A | PEAR-06 FEEDER A | PEAR-06 FEEDER A | PEAR-06 FEEDER A | PEAR-06 FEEDER A | PEAR-06 FEEDER A | PEAR-06 FEEDER A | PEAR-06 FEEDER A | PEAR-06 FEEDER A | PEAR-06 FEEDER A | PEAR-06 FEEDER A | PEAR-06 FEEDER A | PEAR-06 FEEDER A | PEAR-06 FEEDER A | PEAR-06 FEEDER A
NQ-Townsville Burdekin West | PEAR-06_Hospital 1 11kV | Loading (A) | 2.6121 | 2.6395 | 2.6436 | 2.613 | 2.6402 | 2.6441 | 2.6292 | 2.6485 | 2.6641 | 2.6283 | 2.6475 | 2.6636 | 2.626 | 2.6486 | 2.6623
NQ-Townsville Burdekin West | PEAR-06_Hospital 1 11kV | Loading (MVA) | 0.049129 | 0.050166 | 0.050321 | 0.049164 | 0.050192 | 0.050339 | 0.049776 | 0.05051 | 0.051106 | 0.049741 | 0.050472 | 0.051085 | 0.049656 | 0.050514 | 0.051038
NQ-Townsville Burdekin West | PEAR-06_Hospital 1 11kV | Loading (MW) | 0.0030146 | 0.0030783 | 0.0030878 | 0.0030168 | 0.0030798 | 0.0030889 | 0.0030543 | 0.0030994 | 0.0031359 | 0.0030522 | 0.003097 | 0.0031347 | 0.0030469 | 0.0030996 | 0.0031318
NQ-Townsville Burdekin West | PEAR-06_Hospital 1 11kV | Power Factor | 0.061361 | 0.061361 | 0.061361 | 0.061361 | 0.061361 | 0.061361 | 0.061361 | 0.061361 | 0.061361 | 0.061361 | 0.061361 | 0.061361 | 0.061361 | 0.061361 | 0.061361
NQ-Townsville Burdekin West | PEAR-06_Hospital 1 11kV | Rating (A) | 484 | 484 | 484 | 484 | 484 | 484 | 484 | 484 | 484 | 484 | 484 | 484 | 484 | 484 | 484
NQ-Townsville Burdekin West | PEAR-06_Hospital 1 11kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Townsville Burdekin West | PEAR-06_Hospital 1 11kV | Min Voltage at Constrained Conductor | 10.859 | 10.9731 | 10.99 | 10.8629 | 10.9759 | 10.992 | 10.9303 | 11.0107 | 11.0754 | 10.9264 | 11.0064 | 11.0731 | 10.9171 | 11.0111 | 11.068
NQ-Townsville Burdekin West | PEAR-06_Hospital 1 11kV | Contingency Outage | BO-DG-1_Bohle-Dan Gleeson 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | 6299_Townsville Port 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | 6299_Townsville Port 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | BC-IN-1_Black River - Ingham No 1 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | BC-IN-1_Black River - Ingham No 1 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV
NQ-Townsville Burdekin West | PEAR-12_Hospital 2 11kV | % of Rated A | 0.3773% | 0.3813% | 0.3819% | 0.3775% | 0.3814% | 0.382% | 0.3798% | 0.3826% | 0.3849% | 0.3797% | 0.3825% | 0.3848% | 0.3794% | 0.3826% | 0.3846%
NQ-Townsville Burdekin West | PEAR-12_Hospital 2 11kV | Limiting Line Name | PEAR-12 FEEDER B | PEAR-12 FEEDER B | PEAR-12 FEEDER B | PEAR-12 FEEDER B | PEAR-12 FEEDER B | PEAR-12 FEEDER B | PEAR-12 FEEDER B | PEAR-12 FEEDER B | PEAR-12 FEEDER B | PEAR-12 FEEDER B | PEAR-12 FEEDER B | PEAR-12 FEEDER B | PEAR-12 FEEDER B | PEAR-12 FEEDER B | PEAR-12 FEEDER B
NQ-Townsville Burdekin West | PEAR-12_Hospital 2 11kV | Loading (A) | 1.8264 | 1.8455 | 1.8484 | 1.827 | 1.846 | 1.8487 | 1.8383 | 1.8519 | 1.8627 | 1.8377 | 1.8511 | 1.8624 | 1.8361 | 1.8519 | 1.8615
NQ-Townsville Burdekin West | PEAR-12_Hospital 2 11kV | Loading (MVA) | 0.034351 | 0.035076 | 0.035185 | 0.034375 | 0.035094 | 0.035197 | 0.034803 | 0.035317 | 0.035733 | 0.034779 | 0.03529 | 0.035719 | 0.034719 | 0.035319 | 0.035686
NQ-Townsville Burdekin West | PEAR-12_Hospital 2 11kV | Loading (MW) | 0.00068716 | 0.00070167 | 0.00070384 | 0.00068765 | 0.00070203 | 0.00070409 | 0.00069621 | 0.00070649 | 0.00071481 | 0.00069572 | 0.00070594 | 0.00071452 | 0.00069453 | 0.00070654 | 0.00071387
NQ-Townsville Burdekin West | PEAR-12_Hospital 2 11kV | Power Factor | 0.020004 | 0.020004 | 0.020004 | 0.020004 | 0.020004 | 0.020004 | 0.020004 | 0.020004 | 0.020004 | 0.020004 | 0.020004 | 0.020004 | 0.020004 | 0.020004 | 0.020004
NQ-Townsville Burdekin West | PEAR-12_Hospital 2 11kV | Rating (A) | 484 | 484 | 484 | 484 | 484 | 484 | 484 | 484 | 484 | 484 | 484 | 484 | 484 | 484 | 484
NQ-Townsville Burdekin West | PEAR-12_Hospital 2 11kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Townsville Burdekin West | PEAR-12_Hospital 2 11kV | Min Voltage at Constrained Conductor | 10.859 | 10.9731 | 10.99 | 10.8629 | 10.9759 | 10.992 | 10.9303 | 11.0107 | 11.0754 | 10.9264 | 11.0064 | 11.0731 | 10.9171 | 11.0111 | 11.068
NQ-Townsville Burdekin West | PEAR-12_Hospital 2 11kV | Contingency Outage | BO-DG-1_Bohle-Dan Gleeson 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | 6299_Townsville Port 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | 6299_Townsville Port 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | BC-IN-1_Black River - Ingham No 1 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | BC-IN-1_Black River - Ingham No 1 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV | BO-DG-1_Bohle-Dan Gleeson 66 kV
NQ-Townsville Burdekin West | RI-10_Richmond No 10 33 kV | % of Rated A | 3.776e-09% | 3.785e-09% | 3.785e-09% | 3.781e-09% | 3.778e-09% | 3.789e-09% | 3.764e-09% | 3.765e-09% | 3.768e-09% | 3.764e-09% | 3.765e-09% | 3.767e-09% | 3.764e-09% | 3.764e-09% | 3.764e-09%
NQ-Townsville Burdekin West | RI-10_Richmond No 10 33 kV | Limiting Line Name | Link_RICH_RICH-A624_RI-10 RICHMOND 33KV | Link_RICH_RICH-A624_RI-10 RICHMOND 33KV | Link_RICH_RICH-A624_RI-10 RICHMOND 33KV | Link_RICH_RICH-A624_RI-10 RICHMOND 33KV | Link_RICH_RICH-A624_RI-10 RICHMOND 33KV | Link_RICH_RICH-A624_RI-10 RICHMOND 33KV | Link_RICH_RICH-A624_RI-10 RICHMOND 33KV | Link_RICH_RICH-A624_RI-10 RICHMOND 33KV | Link_RICH_RICH-A624_RI-10 RICHMOND 33KV | Link_RICH_RICH-A624_RI-10 RICHMOND 33KV | Link_RICH_RICH-A624_RI-10 RICHMOND 33KV | Link_RICH_RICH-A624_RI-10 RICHMOND 33KV | Link_RICH_RICH-A624_RI-10 RICHMOND 33KV | Link_RICH_RICH-A624_RI-10 RICHMOND 33KV | Link_RICH_RICH-A624_RI-10 RICHMOND 33KV
NQ-Townsville Burdekin West | RI-10_Richmond No 10 33 kV | Loading (A) | 1.8878e-07 | 1.8923e-07 | 1.8927e-07 | 1.8904e-07 | 1.8891e-07 | 1.8945e-07 | 1.8821e-07 | 1.8824e-07 | 1.8838e-07 | 1.882e-07 | 1.8823e-07 | 1.8837e-07 | 1.8819e-07 | 1.8822e-07 | 1.8822e-07
NQ-Townsville Burdekin West | RI-10_Richmond No 10 33 kV | Loading (MVA) | 1.0584e-08 | 1.0635e-08 | 1.0639e-08 | 1.0614e-08 | 1.0599e-08 | 1.066e-08 | 1.0521e-08 | 1.0525e-08 | 1.054e-08 | 1.052e-08 | 1.0523e-08 | 1.0539e-08 | 1.0518e-08 | 1.0521e-08 | 1.0521e-08
NQ-Townsville Burdekin West | RI-10_Richmond No 10 33 kV | Loading (MW) | 1.0584e-08 | 1.0635e-08 | 1.0639e-08 | 1.0614e-08 | 1.0599e-08 | 1.066e-08 | 1.0521e-08 | 1.0525e-08 | 1.054e-08 | 1.052e-08 | 1.0523e-08 | 1.0539e-08 | 1.0518e-08 | 1.0521e-08 | 1.0521e-08
NQ-Townsville Burdekin West | RI-10_Richmond No 10 33 kV | Power Factor | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
NQ-Townsville Burdekin West | RI-10_Richmond No 10 33 kV | Rating (A) | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000
NQ-Townsville Burdekin West | RI-10_Richmond No 10 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Townsville Burdekin West | RI-10_Richmond No 10 33 kV | Min Voltage at Constrained Conductor | 32.3705 | 32.4482 | 32.4547 | 32.4156 | 32.393 | 32.4859 | 32.2735 | 32.2789 | 32.3019 | 32.2716 | 32.277 | 32.3011 | 32.2691 | 32.2738 | 32.2741
NQ-Townsville Burdekin West | RI-10_Richmond No 10 33 kV | Contingency Outage | HU-WI-1 Hughenden-Winton No 1 66 kV | RI-JC-1_Richmond-Julia Creek No 1 66 kV | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | HU-WI-1 Hughenden-Winton No 1 66 kV | HU-WI-1 Hughenden-Winton No 1 66 kV | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | RI-JC-1_Richmond-Julia Creek No 1 66 kV | RI-JC-1_Richmond-Julia Creek No 1 66 kV | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | RI-JC-1_Richmond-Julia Creek No 1 66 kV | RI-JC-1_Richmond-Julia Creek No 1 66 kV | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | RI-JC-1_Richmond-Julia Creek No 1 66 kV | RI-JC-1_Richmond-Julia Creek No 1 66 kV | MR-LE-1_Millchester-Mt Leyshon 1 66 kV
NQ-Townsville Burdekin West | RI-20_Richmond No 20 33 kV | % of Rated A | 3.776e-09% | 3.785e-09% | 3.785e-09% | 3.781e-09% | 3.778e-09% | 3.789e-09% | 3.764e-09% | 3.765e-09% | 3.768e-09% | 3.764e-09% | 3.765e-09% | 3.767e-09% | 3.764e-09% | 3.764e-09% | 3.764e-09%
NQ-Townsville Burdekin West | RI-20_Richmond No 20 33 kV | Limiting Line Name | Link_RICH_RICH-B624_RI-20 JULIA CREEK 33 | Link_RICH_RICH-B624_RI-20 JULIA CREEK 33 | Link_RICH_RICH-B624_RI-20 JULIA CREEK 33 | Link_RICH_RICH-B624_RI-20 JULIA CREEK 33 | Link_RICH_RICH-B624_RI-20 JULIA CREEK 33 | Link_RICH_RICH-B624_RI-20 JULIA CREEK 33 | Link_RICH_RICH-B624_RI-20 JULIA CREEK 33 | Link_RICH_RICH-B624_RI-20 JULIA CREEK 33 | Link_RICH_RICH-B624_RI-20 JULIA CREEK 33 | Link_RICH_RICH-B624_RI-20 JULIA CREEK 33 | Link_RICH_RICH-B624_RI-20 JULIA CREEK 33 | Link_RICH_RICH-B624_RI-20 JULIA CREEK 33 | Link_RICH_RICH-B624_RI-20 JULIA CREEK 33 | Link_RICH_RICH-B624_RI-20 JULIA CREEK 33 | Link_RICH_RICH-B624_RI-20 JULIA CREEK 33
NQ-Townsville Burdekin West | RI-20_Richmond No 20 33 kV | Loading (A) | 1.8878e-07 | 1.8923e-07 | 1.8927e-07 | 1.8904e-07 | 1.8891e-07 | 1.8945e-07 | 1.8821e-07 | 1.8824e-07 | 1.8838e-07 | 1.882e-07 | 1.8823e-07 | 1.8837e-07 | 1.8819e-07 | 1.8822e-07 | 1.8822e-07
NQ-Townsville Burdekin West | RI-20_Richmond No 20 33 kV | Loading (MVA) | 1.0584e-08 | 1.0635e-08 | 1.0639e-08 | 1.0614e-08 | 1.0599e-08 | 1.066e-08 | 1.0521e-08 | 1.0525e-08 | 1.054e-08 | 1.052e-08 | 1.0523e-08 | 1.0539e-08 | 1.0518e-08 | 1.0521e-08 | 1.0521e-08
NQ-Townsville Burdekin West | RI-20_Richmond No 20 33 kV | Loading (MW) | 1.0584e-08 | 1.0635e-08 | 1.0639e-08 | 1.0614e-08 | 1.0599e-08 | 1.066e-08 | 1.0521e-08 | 1.0525e-08 | 1.054e-08 | 1.052e-08 | 1.0523e-08 | 1.0539e-08 | 1.0518e-08 | 1.0521e-08 | 1.0521e-08
NQ-Townsville Burdekin West | RI-20_Richmond No 20 33 kV | Power Factor | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
NQ-Townsville Burdekin West | RI-20_Richmond No 20 33 kV | Rating (A) | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000
NQ-Townsville Burdekin West | RI-20_Richmond No 20 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Townsville Burdekin West | RI-20_Richmond No 20 33 kV | Min Voltage at Constrained Conductor | 32.3705 | 32.4482 | 32.4547 | 32.4156 | 32.393 | 32.4859 | 32.2735 | 32.2789 | 32.3019 | 32.2716 | 32.277 | 32.3011 | 32.2691 | 32.2738 | 32.2741
NQ-Townsville Burdekin West | RI-20_Richmond No 20 33 kV | Contingency Outage | HU-WI-1 Hughenden-Winton No 1 66 kV | RI-JC-1_Richmond-Julia Creek No 1 66 kV | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | HU-WI-1 Hughenden-Winton No 1 66 kV | HU-WI-1 Hughenden-Winton No 1 66 kV | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | RI-JC-1_Richmond-Julia Creek No 1 66 kV | RI-JC-1_Richmond-Julia Creek No 1 66 kV | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | RI-JC-1_Richmond-Julia Creek No 1 66 kV | RI-JC-1_Richmond-Julia Creek No 1 66 kV | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | RI-JC-1_Richmond-Julia Creek No 1 66 kV | RI-JC-1_Richmond-Julia Creek No 1 66 kV | MR-LE-1_Millchester-Mt Leyshon 1 66 kV
NQ-Townsville Burdekin West | RI-50_Richmond No 50 33 kV | % of Rated A | 3.776e-09% | 3.785e-09% | 3.785e-09% | 3.781e-09% | 3.778e-09% | 3.789e-09% | 3.764e-09% | 3.765e-09% | 3.768e-09% | 3.764e-09% | 3.765e-09% | 3.767e-09% | 3.764e-09% | 3.764e-09% | 3.764e-09%
NQ-Townsville Burdekin West | RI-50_Richmond No 50 33 kV | Limiting Line Name | Link_RICH_RICH E624_RI-50 JULIA CREEK NO | Link_RICH_RICH E624_RI-50 JULIA CREEK NO | Link_RICH_RICH E624_RI-50 JULIA CREEK NO | Link_RICH_RICH E624_RI-50 JULIA CREEK NO | Link_RICH_RICH E624_RI-50 JULIA CREEK NO | Link_RICH_RICH E624_RI-50 JULIA CREEK NO | Link_RICH_RICH E624_RI-50 JULIA CREEK NO | Link_RICH_RICH E624_RI-50 JULIA CREEK NO | Link_RICH_RICH E624_RI-50 JULIA CREEK NO | Link_RICH_RICH E624_RI-50 JULIA CREEK NO | Link_RICH_RICH E624_RI-50 JULIA CREEK NO | Link_RICH_RICH E624_RI-50 JULIA CREEK NO | Link_RICH_RICH E624_RI-50 JULIA CREEK NO | Link_RICH_RICH E624_RI-50 JULIA CREEK NO | Link_RICH_RICH E624_RI-50 JULIA CREEK NO
NQ-Townsville Burdekin West | RI-50_Richmond No 50 33 kV | Loading (A) | 1.8878e-07 | 1.8923e-07 | 1.8927e-07 | 1.8904e-07 | 1.8891e-07 | 1.8945e-07 | 1.8821e-07 | 1.8824e-07 | 1.8838e-07 | 1.882e-07 | 1.8823e-07 | 1.8837e-07 | 1.8819e-07 | 1.8822e-07 | 1.8822e-07
NQ-Townsville Burdekin West | RI-50_Richmond No 50 33 kV | Loading (MVA) | 1.0584e-08 | 1.0635e-08 | 1.0639e-08 | 1.0614e-08 | 1.0599e-08 | 1.066e-08 | 1.0521e-08 | 1.0525e-08 | 1.054e-08 | 1.052e-08 | 1.0523e-08 | 1.0539e-08 | 1.0518e-08 | 1.0521e-08 | 1.0521e-08
NQ-Townsville Burdekin West | RI-50_Richmond No 50 33 kV | Loading (MW) | 1.0584e-08 | 1.0635e-08 | 1.0639e-08 | 1.0614e-08 | 1.0599e-08 | 1.066e-08 | 1.0521e-08 | 1.0525e-08 | 1.054e-08 | 1.052e-08 | 1.0523e-08 | 1.0539e-08 | 1.0518e-08 | 1.0521e-08 | 1.0521e-08
NQ-Townsville Burdekin West | RI-50_Richmond No 50 33 kV | Power Factor | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
NQ-Townsville Burdekin West | RI-50_Richmond No 50 33 kV | Rating (A) | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000
NQ-Townsville Burdekin West | RI-50_Richmond No 50 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Townsville Burdekin West | RI-50_Richmond No 50 33 kV | Min Voltage at Constrained Conductor | 32.3705 | 32.4482 | 32.4547 | 32.4156 | 32.393 | 32.4859 | 32.2735 | 32.2789 | 32.3019 | 32.2716 | 32.277 | 32.3011 | 32.2691 | 32.2738 | 32.2741
NQ-Townsville Burdekin West | RI-50_Richmond No 50 33 kV | Contingency Outage | HU-WI-1 Hughenden-Winton No 1 66 kV | RI-JC-1_Richmond-Julia Creek No 1 66 kV | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | HU-WI-1 Hughenden-Winton No 1 66 kV | HU-WI-1 Hughenden-Winton No 1 66 kV | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | RI-JC-1_Richmond-Julia Creek No 1 66 kV | RI-JC-1_Richmond-Julia Creek No 1 66 kV | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | RI-JC-1_Richmond-Julia Creek No 1 66 kV | RI-JC-1_Richmond-Julia Creek No 1 66 kV | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | RI-JC-1_Richmond-Julia Creek No 1 66 kV | RI-JC-1_Richmond-Julia Creek No 1 66 kV | MR-LE-1_Millchester-Mt Leyshon 1 66 kV
NQ-Townsville Burdekin West | RI-JC-1_Richmond-Julia Creek No 1 66 kV | % of Rated A | 6.863% | 7.126% | 4.39% | 6.84% | 7.072% | 4.392% | 11.28% | 11.14% | 4.89% | 11.28% | 11.14% | 4.89% | 11.45% | 11.31% | 4.777%
NQ-Townsville Burdekin West | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Limiting Line Name | TR_LINE 32331_1 | TR_LINE 32331_1 | TR_LINE 32331_1 | TR_LINE 32331_1 | TR_LINE 32331_1 | TR_LINE 32331_1 | TR_LINE 162594_1 | TR_LINE 162594_1 | TR_LINE 32331_1 | TR_LINE 162594_1 | TR_LINE 162594_1 | TR_LINE 32331_1 | TR_LINE 162594_1 | TR_LINE 162594_1 | TR_LINE 32331_1
NQ-Townsville Burdekin West | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Loading (A) | 24.3648 | 27.6476 | 18.4376 | 24.2817 | 27.4393 | 18.4466 | 40.0404 | 43.221 | 20.5379 | 40.0535 | 43.2342 | 20.5378 | 40.6403 | 43.8839 | 20.064
NQ-Townsville Burdekin West | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Loading (MVA) | 2.5664 | 2.6967 | 2.1837 | 2.5757 | 2.7028 | 2.1865 | 3.4411 | 3.7829 | 2.3964 | 3.4412 | 3.7829 | 2.3963 | 3.4502 | 3.7935 | 2.3391
NQ-Townsville Burdekin West | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Loading (MW) | 2.3681 | 2.6215 | 1.2531 | 2.3672 | 2.6196 | 1.2531 | 3.3336 | 3.6615 | 1.8147 | 3.3336 | 3.6615 | 1.8147 | 3.3069 | 3.6322 | 1.7991
NQ-Townsville Burdekin West | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Power Factor | 0.92274 | 0.97212 | 0.57384 | 0.91904 | 0.96919 | 0.57309 | 0.96873 | 0.9679 | 0.75728 | 0.96872 | 0.96789 | 0.7573 | 0.95843 | 0.95746 | 0.76916
NQ-Townsville Burdekin West | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Rating (A) | 355 | 388 | 420 | 355 | 388 | 420 | 355 | 388 | 420 | 355 | 388 | 420 | 355 | 388 | 420
NQ-Townsville Burdekin West | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Townsville Burdekin West | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Min Voltage at Constrained Conductor | 60.8139 | 56.3135 | 68.3799 | 61.2438 | 56.8704 | 68.4357 | 49.6185 | 50.5321 | 67.3653 | 49.6029 | 50.5173 | 67.3636 | 49.0148 | 49.9087 | 67.3078
NQ-Townsville Burdekin West | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Contingency Outage | 6382 JACR-HUGH 132kV | 6382 JACR-HUGH 132kV | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | 6382 JACR-HUGH 132kV | 6382 JACR-HUGH 132kV | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | 6382 JACR-HUGH 132kV | 7460 CPRE-JACR 132kV | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | 6382 JACR-HUGH 132kV | 7460 CPRE-JACR 132kV | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | 6382 JACR-HUGH 132kV | 7460 CPRE-JACR 132kV | MR-LE-1_Millchester-Mt Leyshon 1 66 kV
NQ-Townsville Burdekin West | ST-GI-1_Stuart-Giru 66 kV | % of Rated A | 12.19% | 13.59% | 11.99% | 12.19% | 13.59% | 11.98% | 12.14% | 13.48% | 12% | 12.14% | 13.49% | 12% | 12.14% | 13.49% | 12.01%
NQ-Townsville Burdekin West | ST-GI-1_Stuart-Giru 66 kV | Limiting Line Name | TR_LINE 31680_2 | TR_LINE 31680_2 | TR_LINE 31680_2 | TR_LINE 31680_2 | TR_LINE 31680_2 | TR_LINE 31680_2 | TR_LINE 31680_2 | TR_LINE 31680_2 | TR_LINE 31680_2 | TR_LINE 31680_2 | TR_LINE 31680_2 | TR_LINE 31680_2 | TR_LINE 31680_2 | TR_LINE 31680_2 | TR_LINE 31680_2
NQ-Townsville Burdekin West | ST-GI-1_Stuart-Giru 66 kV | Loading (A) | 11.949 | 14.5386 | 11.5056 | 11.9484 | 14.5386 | 11.5054 | 11.8941 | 14.4285 | 11.523 | 11.8959 | 14.4312 | 11.5241 | 11.9006 | 14.4373 | 11.5268
NQ-Townsville Burdekin West | ST-GI-1_Stuart-Giru 66 kV | Loading (MVA) | 1.3995 | 1.6962 | 1.3588 | 1.3995 | 1.6962 | 1.3588 | 1.3994 | 1.6961 | 1.3587 | 1.3994 | 1.6961 | 1.3587 | 1.3994 | 1.6961 | 1.3587
NQ-Townsville Burdekin West | ST-GI-1_Stuart-Giru 66 kV | Loading (MW) | 1.3945 | 1.6898 | 1.354 | 1.3945 | 1.6898 | 1.354 | 1.3944 | 1.6897 | 1.3539 | 1.3944 | 1.6897 | 1.3539 | 1.3944 | 1.6897 | 1.3539
NQ-Townsville Burdekin West | ST-GI-1_Stuart-Giru 66 kV | Power Factor | 0.99484 | 0.99428 | 0.9949 | 0.99484 | 0.99428 | 0.9949 | 0.99486 | 0.99433 | 0.99494 | 0.99486 | 0.99432 | 0.99494 | 0.99486 | 0.99432 | 0.99494
NQ-Townsville Burdekin West | ST-GI-1_Stuart-Giru 66 kV | Rating (A) | 98 | 107 | 96 | 98 | 107 | 96 | 98 | 107 | 96 | 98 | 107 | 96 | 98 | 107 | 96
NQ-Townsville Burdekin West | ST-GI-1_Stuart-Giru 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Townsville Burdekin West | ST-GI-1_Stuart-Giru 66 kV | Min Voltage at Constrained Conductor | 67.6191 | 67.3597 | 68.1858 | 67.6224 | 67.3599 | 68.1875 | 67.9284 | 67.8676 | 68.0783 | 67.9183 | 67.8552 | 68.0718 | 67.8916 | 67.8269 | 68.0563
NQ-Townsville Burdekin West | ST-GI-1_Stuart-Giru 66 kV | Contingency Outage | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | GA-HP-1_Garbutt-Hermit Park No 1 66 kV
NQ-Townsville Burdekin West | ST-GI-1_Stuart-Giru 66 kV To T Only | % of Rated A | 1.867% | 1.488% | 1.581% | 1.883% | 1.48% | 1.583% | 1.87% | 1.48% | 1.583% | 1.87% | 1.48% | 1.583% | 1.868% | 1.478% | 1.582%
NQ-Townsville Burdekin West | ST-GI-1_Stuart-Giru 66 kV To T Only | Limiting Line Name | TR_LINE 195987_1 | TR_LINE 195987_1 | TR_LINE 195987_1 | TR_LINE 195987_1 | TR_LINE 195987_1 | TR_LINE 195987_1 | TR_LINE 195987_1 | TR_LINE 195987_1 | TR_LINE 195987_1 | TR_LINE 195987_1 | TR_LINE 195987_1 | TR_LINE 195987_1 | TR_LINE 195987_1 | TR_LINE 195987_1 | TR_LINE 195987_1
NQ-Townsville Burdekin West | ST-GI-1_Stuart-Giru 66 kV To T Only | Loading (A) | 2.464 | 2.4848 | 2.5141 | 2.4861 | 2.471 | 2.5166 | 2.468 | 2.4717 | 2.5166 | 2.4678 | 2.4712 | 2.5166 | 2.4652 | 2.4684 | 2.5146
NQ-Townsville Burdekin West | ST-GI-1_Stuart-Giru 66 kV To T Only | Loading (MVA) | 0.27484 | 0.27951 | 0.28614 | 0.27981 | 0.27642 | 0.28671 | 0.27573 | 0.27656 | 0.28671 | 0.2757 | 0.27645 | 0.2867 | 0.27512 | 0.27582 | 0.28626
NQ-Townsville Burdekin West | ST-GI-1_Stuart-Giru 66 kV To T Only | Loading (MW) | 7.1647e-05 | 7.2864e-05 | 7.4594e-05 | 7.2942e-05 | 7.2059e-05 | 7.4741e-05 | 7.188e-05 | 7.2097e-05 | 7.4741e-05 | 7.1873e-05 | 7.2068e-05 | 7.474e-05 | 7.1721e-05 | 7.1903e-05 | 7.4625e-05
NQ-Townsville Burdekin West | ST-GI-1_Stuart-Giru 66 kV To T Only | Power Factor | 0.00024573 | 0.00024573 | 0.00024573 | 0.00024573 | 0.00024573 | 0.00024573 | 0.00024573 | 0.00024573 | 0.00024573 | 0.00024573 | 0.00024573 | 0.00024573 | 0.00024573 | 0.00024573 | 0.00024573
NQ-Townsville Burdekin West | ST-GI-1_Stuart-Giru 66 kV To T Only | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
NQ-Townsville Burdekin West | ST-GI-1_Stuart-Giru 66 kV To T Only | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Townsville Burdekin West | ST-GI-1_Stuart-Giru 66 kV To T Only | Min Voltage at Constrained Conductor | 64.3995 | 64.9441 | 65.7107 | 64.979 | 64.5843 | 65.7754 | 64.504 | 64.6013 | 65.7752 | 64.5008 | 64.5885 | 65.7746 | 64.4327 | 64.5146 | 65.7241
NQ-Townsville Burdekin West | ST-GI-1_Stuart-Giru 66 kV To T Only | Contingency Outage | KA-AY-01_Ayr - Kalamia No 1 66 kV | KA-AY-01_Ayr - Kalamia No 1 66 kV | KA-AY-01_Ayr - Kalamia No 1 66 kV | 7182 Ross - Milchester | CT-MR-1_Millchester-CHTO No 1 66 kV | KA-AY-01_Ayr - Kalamia No 1 66 kV | KA-AY-01_Ayr - Kalamia No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | KA-AY-01_Ayr - Kalamia No 1 66 kV | KA-AY-01_Ayr - Kalamia No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | KA-AY-01_Ayr - Kalamia No 1 66 kV | KA-AY-01_Ayr - Kalamia No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | KA-AY-01_Ayr - Kalamia No 1 66 kV
NQ-Townsville Burdekin West | ST-RM-1_Stuart-Rasmussen 66 kV | % of Rated A | 28.33% | 29.08% | 20.97% | 28.19% | 28.95% | 20.9% | 29.47% | 30.36% | 22.09% | 29.55% | 30.45% | 22.12% | 29.76% | 30.69% | 22.23%
NQ-Townsville Burdekin West | ST-RM-1_Stuart-Rasmussen 66 kV | Limiting Line Name | TR_LINE 32428_1 | TR_LINE 32428_1 | TR_LINE 32428_1 | TR_LINE 32428_1 | TR_LINE 32428_1 | TR_LINE 32428_1 | TR_LINE 32428_1 | TR_LINE 32428_1 | TR_LINE 32428_1 | TR_LINE 32428_1 | TR_LINE 32428_1 | TR_LINE 32428_1 | TR_LINE 32428_1 | TR_LINE 32428_1 | TR_LINE 32428_1
NQ-Townsville Burdekin West | ST-RM-1_Stuart-Rasmussen 66 kV | Loading (A) | 156.107 | 169.2329 | 109.8737 | 155.3371 | 168.4811 | 109.5104 | 162.4072 | 176.6959 | 115.7376 | 162.7938 | 177.2116 | 115.9121 | 163.9946 | 178.6131 | 116.4973
NQ-Townsville Burdekin West | ST-RM-1_Stuart-Rasmussen 66 kV | Loading (MVA) | 18.6042 | 20.184 | 13.1649 | 18.5125 | 20.0936 | 13.1214 | 19.4301 | 21.1612 | 13.8323 | 19.4739 | 21.2196 | 13.8519 | 19.6114 | 21.3798 | 13.9193
NQ-Townsville Burdekin West | ST-RM-1_Stuart-Rasmussen 66 kV | Loading (MW) | 18.531 | 19.9274 | 12.752 | 18.4355 | 19.8291 | 12.7028 | 19.2305 | 20.7086 | 13.6352 | 19.2767 | 20.7735 | 13.6555 | 19.4223 | 20.9506 | 13.726
NQ-Townsville Burdekin West | ST-RM-1_Stuart-Rasmussen 66 kV | Power Factor | 0.99489 | 0.98459 | 0.96864 | 0.99465 | 0.98413 | 0.9681 | 0.98759 | 0.97474 | 0.98551 | 0.98774 | 0.97511 | 0.98557 | 0.98822 | 0.97608 | 0.98584
NQ-Townsville Burdekin West | ST-RM-1_Stuart-Rasmussen 66 kV | Rating (A) | 551 | 582 | 524 | 551 | 582 | 524 | 551 | 582 | 524 | 551 | 582 | 524 | 551 | 582 | 524
NQ-Townsville Burdekin West | ST-RM-1_Stuart-Rasmussen 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Townsville Burdekin West | ST-RM-1_Stuart-Rasmussen 66 kV | Min Voltage at Constrained Conductor | 68.3403 | 68.4949 | 69.0468 | 68.3472 | 68.499 | 69.0503 | 68.6916 | 68.8624 | 68.7551 | 68.68 | 68.8471 | 68.7484 | 68.6495 | 68.8106 | 68.7319
NQ-Townsville Burdekin West | ST-RM-1_Stuart-Rasmussen 66 kV | Contingency Outage | ST-RP-1_Stuart-Ross Plains 66 kV | ST-RP-1_Stuart-Ross Plains 66 kV | ST-RP-1_Stuart-Ross Plains 66 kV | ST-RP-1_Stuart-Ross Plains 66 kV | ST-RP-1_Stuart-Ross Plains 66 kV | ST-RP-1_Stuart-Ross Plains 66 kV | ST-RP-1_Stuart-Ross Plains 66 kV | ST-RP-1_Stuart-Ross Plains 66 kV | ST-RP-1_Stuart-Ross Plains 66 kV | ST-RP-1_Stuart-Ross Plains 66 kV | ST-RP-1_Stuart-Ross Plains 66 kV | ST-RP-1_Stuart-Ross Plains 66 kV | ST-RP-1_Stuart-Ross Plains 66 kV | ST-RP-1_Stuart-Ross Plains 66 kV | ST-RP-1_Stuart-Ross Plains 66 kV
NQ-Townsville Burdekin West | ST-RP-1_Stuart-Ross Plains 66 kV | % of Rated A | 46.99% | 41.64% | 30.42% | 46.6% | 41.29% | 30.27% | 46.27% | 42.51% | 32.04% | 46.41% | 42.61% | 32.08% | 46.95% | 42.95% | 32.26%
NQ-Townsville Burdekin West | ST-RP-1_Stuart-Ross Plains 66 kV | Limiting Line Name | TR_LINE 32392_1 | TR_LINE 32392_1 | TR_LINE 32425_1 | TR_LINE 32392_1 | TR_LINE 32392_1 | TR_LINE 32425_1 | TR_LINE 32392_1 | TR_LINE 32425_1 | TR_LINE 32425_1 | TR_LINE 32392_1 | TR_LINE 32425_1 | TR_LINE 32425_1 | TR_LINE 32392_1 | TR_LINE 32425_1 | TR_LINE 32425_1
NQ-Townsville Burdekin West | ST-RP-1_Stuart-Ross Plains 66 kV | Loading (A) | 319.0468 | 303.9385 | 201.7044 | 316.4106 | 301.3861 | 200.7115 | 314.1506 | 310.3416 | 212.4381 | 315.1178 | 311.0706 | 212.6998 | 318.7817 | 313.5612 | 213.9039
NQ-Townsville Burdekin West | ST-RP-1_Stuart-Ross Plains 66 kV | Loading (MVA) | 37.3979 | 35.6377 | 24.1276 | 37.0958 | 35.343 | 24.0092 | 36.9858 | 37.1359 | 25.3725 | 37.0918 | 37.2171 | 25.4015 | 37.5006 | 37.5012 | 25.5404
NQ-Townsville Burdekin West | ST-RP-1_Stuart-Ross Plains 66 kV | Loading (MW) | 36.9337 | 35.2717 | 23.6663 | 36.6422 | 34.9861 | 23.5367 | 36.5442 | 36.763 | 25.2496 | 36.644 | 36.8503 | 25.2792 | 37.0354 | 37.1541 | 25.4221
NQ-Townsville Burdekin West | ST-RP-1_Stuart-Ross Plains 66 kV | Power Factor | 0.98759 | 0.98973 | 0.98087 | 0.98777 | 0.9899 | 0.9803 | 0.98806 | 0.98994 | 0.99515 | 0.98793 | 0.99012 | 0.99518 | 0.98759 | 0.99072 | 0.99536
NQ-Townsville Burdekin West | ST-RP-1_Stuart-Ross Plains 66 kV | Rating (A) | 679 | 730 | 663 | 679 | 730 | 663 | 679 | 730 | 663 | 679 | 730 | 663 | 679 | 730 | 663
NQ-Townsville Burdekin West | ST-RP-1_Stuart-Ross Plains 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Townsville Burdekin West | ST-RP-1_Stuart-Ross Plains 66 kV | Min Voltage at Constrained Conductor | 67.6687 | 67.6897 | 69.0613 | 67.6814 | 67.6987 | 69.0624 | 67.9663 | 69.0849 | 68.9542 | 67.9519 | 69.0737 | 68.9481 | 67.911 | 69.0481 | 68.9349
NQ-Townsville Burdekin West | ST-RP-1_Stuart-Ross Plains 66 kV | Contingency Outage | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | 6325_Oonoonba-Stuart 66 kV | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | 6325_Oonoonba-Stuart 66 kV | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | 6325_Oonoonba-Stuart 66 kV | 6325_Oonoonba-Stuart 66 kV | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | 6325_Oonoonba-Stuart 66 kV | 6325_Oonoonba-Stuart 66 kV | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | 6325_Oonoonba-Stuart 66 kV | 6325_Oonoonba-Stuart 66 kV
NQ-Townsville Burdekin West | ST-TOPO-1_Stuart-Townsville Port 66 kV | % of Rated A | 79.41% | 60.92% | 47.95% | 80.73% | 61.8% | 48.38% | 82.1% | 62.9% | 49.24% | 82.29% | 63.08% | 49.33% | 83.21% | 63.78% | 49.75%
NQ-Townsville Burdekin West | ST-TOPO-1_Stuart-Townsville Port 66 kV | Limiting Line Name | TR_LINE 31745_2 | TR_LINE 31664_1 | TR_LINE 31664_1 | TR_LINE 31745_2 | TR_LINE 31664_1 | TR_LINE 31664_1 | TR_LINE 31745_2 | TR_LINE 31664_1 | TR_LINE 31664_1 | TR_LINE 31745_2 | TR_LINE 31664_1 | TR_LINE 31664_1 | TR_LINE 31745_2 | TR_LINE 31664_1 | TR_LINE 31664_1
NQ-Townsville Burdekin West | ST-TOPO-1_Stuart-Townsville Port 66 kV | Loading (A) | 199.3195 | 191.2834 | 135.2216 | 202.6286 | 194.0515 | 136.4389 | 206.0726 | 197.5121 | 138.8434 | 206.5408 | 198.0837 | 139.1082 | 208.845 | 200.2622 | 140.2959
NQ-Townsville Burdekin West | ST-TOPO-1_Stuart-Townsville Port 66 kV | Loading (MVA) | 23.4731 | 22.6968 | 16.2047 | 23.8532 | 23.0234 | 16.3505 | 24.3605 | 23.6118 | 16.5682 | 24.4107 | 23.6754 | 16.5981 | 24.6662 | 23.9239 | 16.7357
NQ-Townsville Burdekin West | ST-TOPO-1_Stuart-Townsville Port 66 kV | Loading (MW) | 22.8008 | 22.0541 | 14.564 | 23.2129 | 22.4094 | 14.7414 | 23.745 | 22.9987 | 16.19 | 23.7994 | 23.0691 | 16.2218 | 24.0751 | 23.3417 | 16.3687
NQ-Townsville Burdekin West | ST-TOPO-1_Stuart-Townsville Port 66 kV | Power Factor | 0.97133 | 0.97167 | 0.89873 | 0.97313 | 0.97332 | 0.90157 | 0.97471 | 0.97402 | 0.97717 | 0.97493 | 0.97438 | 0.97732 | 0.97601 | 0.97565 | 0.97806
NQ-Townsville Burdekin West | ST-TOPO-1_Stuart-Townsville Port 66 kV | Rating (A) | 251 | 314 | 282 | 251 | 314 | 282 | 251 | 314 | 282 | 251 | 314 | 282 | 251 | 314 | 282
NQ-Townsville Burdekin West | ST-TOPO-1_Stuart-Townsville Port 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Townsville Burdekin West | ST-TOPO-1_Stuart-Townsville Port 66 kV | Min Voltage at Constrained Conductor | 67.9911 | 68.5036 | 69.188 | 67.9636 | 68.4981 | 69.1875 | 68.249 | 69.0178 | 68.8935 | 68.2347 | 69.004 | 68.8866 | 68.188 | 68.9698 | 68.8698
NQ-Townsville Burdekin West | ST-TOPO-1_Stuart-Townsville Port 66 kV | Contingency Outage | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV
NQ-Townsville Burdekin West | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | % of Rated A | 66.56% | 63.81% | 48.12% | 66.49% | 63.81% | 48.09% | 61.93% | 59.17% | 44.91% | 62.23% | 59.49% | 45.12% | 63.02% | 60.26% | 45.65%
NQ-Townsville Burdekin West | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Limiting Line Name | TR_LINE 157896_1 | TR_LINE 157896_1 | TR_LINE 157896_1 | TR_LINE 157896_1 | TR_LINE 157896_1 | TR_LINE 157896_1 | TR_LINE 157896_1 | TR_LINE 157896_1 | TR_LINE 157896_1 | TR_LINE 157896_1 | TR_LINE 157896_1 | TR_LINE 157896_1 | TR_LINE 157896_1 | TR_LINE 157896_1 | TR_LINE 157896_1
NQ-Townsville Burdekin West | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Loading (A) | 612.994 | 640.6469 | 441.7595 | 612.3596 | 640.6405 | 441.5047 | 570.4173 | 594.1088 | 412.2344 | 573.1586 | 597.3005 | 414.2201 | 580.3893 | 604.981 | 419.0449
NQ-Townsville Burdekin West | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Loading (MVA) | 72.7042 | 75.8697 | 52.8698 | 72.6333 | 75.869 | 52.8345 | 68.0311 | 70.9928 | 49.1684 | 68.3456 | 71.3581 | 49.3994 | 69.175 | 72.2386 | 49.9624
NQ-Townsville Burdekin West | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Loading (MW) | 72.6425 | 75.8429 | 52.2153 | 72.5686 | 75.8414 | 52.1926 | 67.6092 | 70.3377 | 48.8935 | 67.939 | 70.7268 | 49.1343 | 68.8058 | 71.6584 | 49.7165
NQ-Townsville Burdekin West | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Power Factor | 0.99913 | 0.99963 | 0.98756 | 0.99909 | 0.99962 | 0.9878 | 0.99375 | 0.9907 | 0.99437 | 0.994 | 0.99109 | 0.9946 | 0.99461 | 0.9919 | 0.99504
NQ-Townsville Burdekin West | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Rating (A) | 921 | 1003.9999 | 918 | 921 | 1003.9999 | 918 | 921 | 1003.9999 | 918 | 921 | 1003.9999 | 918 | 921 | 1003.9999 | 918
NQ-Townsville Burdekin West | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Townsville Burdekin West | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Min Voltage at Constrained Conductor | 68.4718 | 68.368 | 69.0968 | 68.4758 | 68.368 | 69.0905 | 68.8558 | 68.9889 | 68.8605 | 68.8432 | 68.9732 | 68.8524 | 68.8103 | 68.9376 | 68.8352
NQ-Townsville Burdekin West | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Contingency Outage | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV
NQ-Townsville Burdekin West | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | % of Rated A | 67.19% | 64.42% | 48.58% | 67.12% | 64.42% | 48.56% | 62.53% | 59.74% | 45.34% | 62.83% | 60.06% | 45.56% | 63.62% | 60.83% | 46.09%
NQ-Townsville Burdekin West | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Limiting Line Name | TR_LINE 157898_1 | TR_LINE 157898_1 | TR_LINE 157898_1 | TR_LINE 157898_1 | TR_LINE 157898_1 | TR_LINE 157898_1 | TR_LINE 157898_1 | TR_LINE 157898_1 | TR_LINE 157898_1 | TR_LINE 157898_1 | TR_LINE 157898_1 | TR_LINE 157898_1 | TR_LINE 157898_1 | TR_LINE 157898_1 | TR_LINE 157898_1
NQ-Townsville Burdekin West | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Loading (A) | 618.8502 | 646.76 | 446.0032 | 618.2132 | 646.7538 | 445.7459 | 575.8848 | 599.8054 | 416.1946 | 578.6519 | 603.027 | 418.1991 | 585.9505 | 610.7795 | 423.0706
NQ-Townsville Burdekin West | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Loading (MVA) | 73.4263 | 76.6244 | 53.3893 | 73.3547 | 76.6237 | 53.3537 | 68.7045 | 71.6959 | 49.6517 | 69.0223 | 72.065 | 49.8851 | 69.8602 | 72.9546 | 50.4537
NQ-Townsville Burdekin West | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Loading (MW) | 73.3755 | 76.6048 | 52.7614 | 73.3013 | 76.6035 | 52.7382 | 68.3086 | 71.0728 | 49.3946 | 68.6413 | 71.4653 | 49.6375 | 69.5157 | 72.4052 | 50.2251
NQ-Townsville Burdekin West | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Power Factor | 0.99929 | 0.99973 | 0.98818 | 0.99925 | 0.99972 | 0.98841 | 0.99419 | 0.99124 | 0.99479 | 0.99443 | 0.99161 | 0.995 | 0.99502 | 0.99241 | 0.99544
NQ-Townsville Burdekin West | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Rating (A) | 921 | 1003.9999 | 918 | 921 | 1003.9999 | 918 | 921 | 1003.9999 | 918 | 921 | 1003.9999 | 918 | 921 | 1003.9999 | 918
NQ-Townsville Burdekin West | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Townsville Burdekin West | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Min Voltage at Constrained Conductor | 68.4972 | 68.3952 | 69.1118 | 68.501 | 68.3952 | 69.1055 | 68.8771 | 69.0103 | 68.8756 | 68.8647 | 68.9948 | 68.8676 | 68.8322 | 68.9597 | 68.8505
NQ-Townsville Burdekin West | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Contingency Outage | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV
NQ-Townsville Burdekin West | ST-WO-1_Stuart-Woodstock South 1 66 kV | % of Rated A | 63.89% | 53.78% | 103% | 173.4% | 53.16% | 101.8% | 67.92% | 57.76% | 108.9% | 68.03% | 57.85% | 109% | 68.05% | 57.86% | 109.4%
NQ-Townsville Burdekin West | ST-WO-1_Stuart-Woodstock South 1 66 kV | Limiting Line Name | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1
NQ-Townsville Burdekin West | ST-WO-1_Stuart-Woodstock South 1 66 kV | Loading (A) | 84.3289 | 89.8201 | 163.7133 | 228.8297 | 88.7789 | 161.8199 | 89.6553 | 96.4642 | 173.1483 | 89.7947 | 96.6042 | 173.2316 | 89.822 | 96.6286 | 173.9216
NQ-Townsville Burdekin West | ST-WO-1_Stuart-Woodstock South 1 66 kV | Loading (MVA) | 9.782 | 10.4014 | 19.0374 | 25.5736 | 10.2837 | 18.829 | 10.4344 | 11.233 | 20.0345 | 10.4483 | 11.2463 | 20.0409 | 10.4471 | 11.2436 | 20.1102
NQ-Townsville Burdekin West | ST-WO-1_Stuart-Woodstock South 1 66 kV | Loading (MW) | 9.5212 | 10.0541 | 16.8532 | 24.2552 | 9.9444 | 16.6458 | 10.1233 | 10.8422 | 17.727 | 10.1395 | 10.8585 | 17.7382 | 10.1416 | 10.8601 | 17.8171
NQ-Townsville Burdekin West | ST-WO-1_Stuart-Woodstock South 1 66 kV | Power Factor | 0.97333 | 0.96634 | 0.87975 | 0.9426 | 0.96677 | 0.87861 | 0.96997 | 0.96468 | 0.87875 | 0.97023 | 0.96499 | 0.87903 | 0.97054 | 0.96536 | 0.87989
NQ-Townsville Burdekin West | ST-WO-1_Stuart-Woodstock South 1 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
NQ-Townsville Burdekin West | ST-WO-1_Stuart-Woodstock South 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Townsville Burdekin West | ST-WO-1_Stuart-Woodstock South 1 66 kV | Min Voltage at Constrained Conductor | 66.6707 | 66.5517 | 66.7956 | 63.8327 | 66.5733 | 66.8441 | 66.8805 | 66.9042 | 66.4441 | 66.8643 | 66.885 | 66.4326 | 66.8356 | 66.8516 | 66.3942
NQ-Townsville Burdekin West | ST-WO-1_Stuart-Woodstock South 1 66 kV | Contingency Outage | CT-MR-1_Millchester-CHTO No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | 7182 Ross - Milchester | 7182 Ross - Milchester | CT-MR-1_Millchester-CHTO No 1 66 kV | 7182 Ross - Milchester | CT-MR-1_Millchester-CHTO No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | 7182 Ross - Milchester | CT-MR-1_Millchester-CHTO No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | 7182 Ross - Milchester | CT-MR-1_Millchester-CHTO No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | 7182 Ross - Milchester
NQ-Townsville Burdekin West | TOPO-08_Townsville Port No 8 11 kV | % of Rated A | 0.3232% | 0.324% | 0.3274% | 0.3233% | 0.324% | 0.3273% | 0.3241% | 0.3246% | 0.3251% | 0.324% | 0.3245% | 0.325% | 0.3239% | 0.3243% | 0.3249%
NQ-Townsville Burdekin West | TOPO-08_Townsville Port No 8 11 kV | Limiting Line Name | HV_CABLE TOPO-08A 12159494 | HV_CABLE TOPO-08A 12159494 | HV_CABLE TOPO-08A 12159494 | HV_CABLE TOPO-08A 12159494 | HV_CABLE TOPO-08A 12159494 | HV_CABLE TOPO-08A 12159494 | HV_CABLE TOPO-08A 12159494 | HV_CABLE TOPO-08A 12159494 | HV_CABLE TOPO-08A 12159494 | HV_CABLE TOPO-08A 12159494 | HV_CABLE TOPO-08A 12159494 | HV_CABLE TOPO-08A 12159494 | HV_CABLE TOPO-08A 12159494 | HV_CABLE TOPO-08A 12159494 | HV_CABLE TOPO-08A 12159494
NQ-Townsville Burdekin West | TOPO-08_Townsville Port No 8 11 kV | Loading (A) | 1.81 | 1.8143 | 1.8332 | 1.8102 | 1.8142 | 1.8331 | 1.8151 | 1.8176 | 1.8205 | 1.8147 | 1.817 | 1.8202 | 1.8138 | 1.8159 | 1.8197
NQ-Townsville Burdekin West | TOPO-08_Townsville Port No 8 11 kV | Loading (MVA) | 0.033883 | 0.034045 | 0.034755 | 0.03389 | 0.03404 | 0.034753 | 0.034074 | 0.034165 | 0.034276 | 0.034057 | 0.034145 | 0.034265 | 0.034026 | 0.034105 | 0.034247
NQ-Townsville Burdekin West | TOPO-08_Townsville Port No 8 11 kV | Loading (MW) | 0.00067785 | 0.00068108 | 0.00069529 | 0.00067798 | 0.00068098 | 0.00069525 | 0.00068166 | 0.0006835 | 0.00068571 | 0.00068133 | 0.00068308 | 0.00068549 | 0.0006807 | 0.00068229 | 0.00068512
NQ-Townsville Burdekin West | TOPO-08_Townsville Port No 8 11 kV | Power Factor | 0.020001 | 0.020001 | 0.020001 | 0.020001 | 0.020001 | 0.020001 | 0.020001 | 0.020001 | 0.020001 | 0.020001 | 0.020001 | 0.020001 | 0.020001 | 0.020001 | 0.020001
NQ-Townsville Burdekin West | TOPO-08_Townsville Port No 8 11 kV | Rating (A) | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560
NQ-Townsville Burdekin West | TOPO-08_Townsville Port No 8 11 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Townsville Burdekin West | TOPO-08_Townsville Port No 8 11 kV | Min Voltage at Constrained Conductor | 10.8078 | 10.8335 | 10.9459 | 10.8089 | 10.8328 | 10.9457 | 10.8381 | 10.8527 | 10.8703 | 10.8356 | 10.8495 | 10.8686 | 10.8305 | 10.8431 | 10.8656
NQ-Townsville Burdekin West | TOPO-08_Townsville Port No 8 11 kV | Contingency Outage | MF-TP-1_Max Fulton-TOPO No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | ST-TOPO-1_Stuart-Townsville Port 66 kV | MF-TP-1_Max Fulton-TOPO No 1 66 kV | GA-BO-1_Garbutt-Bohle No 1 66 kV | ST-TOPO-1_Stuart-Townsville Port 66 kV | MF-TP-1_Max Fulton-TOPO No 1 66 kV | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | MF-TP-1_Max Fulton-TOPO No 1 66 kV | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | MF-TP-1_Max Fulton-TOPO No 1 66 kV | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | GA-TP-1_Garbutt-Townsville Port 1 66 kV
NQ-Townsville Burdekin West | TP-NS-1_Townsville Port-NESM No 1 66 kV | % of Rated A | 19.79% | 13.51% | 13.1% | 19.53% | 13.33% | 12.93% | 19.45% | 13.24% | 13.04% | 19.59% | 13.33% | 13.13% | 19.86% | 13.52% | 13.31%
NQ-Townsville Burdekin West | TP-NS-1_Townsville Port-NESM No 1 66 kV | Limiting Line Name | TR_LINE 31649_1 | TR_LINE 56322_1 | TR_LINE 56322_1 | TR_LINE 31649_1 | TR_LINE 56322_1 | TR_LINE 56322_1 | TR_LINE 31649_1 | TR_LINE 56322_1 | TR_LINE 56322_1 | TR_LINE 31649_1 | TR_LINE 56322_1 | TR_LINE 56322_1 | TR_LINE 31649_1 | TR_LINE 56322_1 | TR_LINE 56322_1
NQ-Townsville Burdekin West | TP-NS-1_Townsville Port-NESM No 1 66 kV | Loading (A) | 51.0513 | 39.8401 | 35.6217 | 50.3921 | 39.3293 | 35.1601 | 50.1826 | 39.0461 | 35.4768 | 50.5329 | 39.3177 | 35.717 | 51.2484 | 39.8696 | 36.2019
NQ-Townsville Burdekin West | TP-NS-1_Townsville Port-NESM No 1 66 kV | Loading (MVA) | 6.0077 | 4.689 | 4.2633 | 5.9275 | 4.6271 | 4.2074 | 5.9275 | 4.6278 | 4.2061 | 5.9676 | 4.6587 | 4.234 | 6.0477 | 4.7205 | 4.2899
NQ-Townsville Burdekin West | TP-NS-1_Townsville Port-NESM No 1 66 kV | Loading (MW) | 6.0074 | 4.6858 | 4.2544 | 5.9273 | 4.6234 | 4.1978 | 5.9274 | 4.6237 | 4.1976 | 5.9674 | 4.6548 | 4.2259 | 6.0474 | 4.717 | 4.2824
NQ-Townsville Burdekin West | TP-NS-1_Townsville Port-NESM No 1 66 kV | Power Factor | 0.99995 | 0.9993 | 0.99791 | 0.99997 | 0.9992 | 0.99771 | 0.99998 | 0.9991 | 0.99799 | 0.99997 | 0.99916 | 0.99808 | 0.99995 | 0.99926 | 0.99827
NQ-Townsville Burdekin West | TP-NS-1_Townsville Port-NESM No 1 66 kV | Rating (A) | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272 | 258 | 295 | 272
NQ-Townsville Burdekin West | TP-NS-1_Townsville Port-NESM No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Townsville Burdekin West | TP-NS-1_Townsville Port-NESM No 1 66 kV | Min Voltage at Constrained Conductor | 67.9411 | 67.9439 | 69.0917 | 67.9116 | 67.917 | 69.0813 | 68.1948 | 68.4209 | 68.4425 | 68.1799 | 68.402 | 68.4337 | 68.1312 | 68.3496 | 68.4079
NQ-Townsville Burdekin West | TP-NS-1_Townsville Port-NESM No 1 66 kV | Contingency Outage | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV | 6299_Townsville Port 66 kV
NQ-Townsville Burdekin West | WO-CT-1_Woodstock-CHTO No 1 66 kV | % of Rated A | 40.31% | 39.95% | 91.36% | 120.7% | 39.41% | 90.23% | 43.27% | 43.48% | 96.96% | 43.35% | 43.56% | 97.01% | 43.37% | 43.57% | 97.42%
NQ-Townsville Burdekin West | WO-CT-1_Woodstock-CHTO No 1 66 kV | Limiting Line Name | TR_LINE 46566_1 | TR_LINE 46566_1 | TR_LINE 46566_1 | TR_LINE 46566_1 | TR_LINE 46566_1 | TR_LINE 46566_1 | TR_LINE 46566_1 | TR_LINE 46566_1 | TR_LINE 46566_1 | TR_LINE 46566_1 | TR_LINE 46566_1 | TR_LINE 46566_1 | TR_LINE 46566_1 | TR_LINE 46566_1 | TR_LINE 46566_1
NQ-Townsville Burdekin West | WO-CT-1_Woodstock-CHTO No 1 66 kV | Loading (A) | 72.1521 | 75.5101 | 153.4795 | 215.9659 | 74.4759 | 151.5879 | 77.4576 | 82.1853 | 162.8939 | 77.5971 | 82.323 | 162.9771 | 77.6237 | 82.3437 | 163.6666
NQ-Townsville Burdekin West | WO-CT-1_Woodstock-CHTO No 1 66 kV | Loading (MVA) | 7.9279 | 8.2981 | 16.9994 | 21.6502 | 8.1908 | 16.8161 | 8.5223 | 9.0515 | 17.9283 | 8.5338 | 9.062 | 17.9317 | 8.5317 | 9.058 | 17.9878
NQ-Townsville Burdekin West | WO-CT-1_Woodstock-CHTO No 1 66 kV | Loading (MW) | 7.5857 | 7.7967 | 13.0497 | 17.4059 | 7.7057 | 12.9105 | 8.0915 | 8.4576 | 13.5713 | 8.1052 | 8.4713 | 13.5794 | 8.1068 | 8.4725 | 13.6318
NQ-Townsville Burdekin West | WO-CT-1_Woodstock-CHTO No 1 66 kV | Power Factor | 0.95683 | 0.93958 | 0.76463 | 0.79908 | 0.94078 | 0.76479 | 0.94944 | 0.93423 | 0.75358 | 0.94976 | 0.93466 | 0.75388 | 0.95019 | 0.9352 | 0.75441
NQ-Townsville Burdekin West | WO-CT-1_Woodstock-CHTO No 1 66 kV | Rating (A) | 179 | 189 | 168 | 179 | 189 | 168 | 179 | 189 | 168 | 179 | 189 | 168 | 179 | 189 | 168
NQ-Townsville Burdekin West | WO-CT-1_Woodstock-CHTO No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Townsville Burdekin West | WO-CT-1_Woodstock-CHTO No 1 66 kV | Min Voltage at Constrained Conductor | 63.3511 | 63.3646 | 63.9027 | 57.7858 | 63.4148 | 64.0029 | 63.4339 | 63.4997 | 63.503 | 63.4048 | 63.4665 | 63.4823 | 63.3667 | 63.4223 | 63.4119
NQ-Townsville Burdekin West | WO-CT-1_Woodstock-CHTO No 1 66 kV | Contingency Outage | CT-MR-1_Millchester-CHTO No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | 7182 Ross - Milchester | 7182 Ross - Milchester | CT-MR-1_Millchester-CHTO No 1 66 kV | 7182 Ross - Milchester | CT-MR-1_Millchester-CHTO No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | 7182 Ross - Milchester | CT-MR-1_Millchester-CHTO No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | 7182 Ross - Milchester | CT-MR-1_Millchester-CHTO No 1 66 kV | CT-MR-1_Millchester-CHTO No 1 66 kV | 7182 Ross - Milchester
SW-Bulli Creek Waggamba | 7235_Bulli Creek - Waggamba 132 kV | % of Rated A | 10.72% | 13.07% | 9.506% | 10.72% | 13.07% | 9.506% | 11.28% | 13.88% | 9.887% | 11.28% | 13.88% | 9.887% | 11.28% | 13.89% | 9.888%
SW-Bulli Creek Waggamba | 7235_Bulli Creek - Waggamba 132 kV | Limiting Line Name | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1
SW-Bulli Creek Waggamba | 7235_Bulli Creek - Waggamba 132 kV | Loading (A) | 69.6558 | 86.1534 | 54.6606 | 69.6554 | 86.1535 | 54.6605 | 73.3095 | 91.4921 | 56.8512 | 73.3139 | 91.4972 | 56.8521 | 73.345 | 91.5047 | 56.8535
SW-Bulli Creek Waggamba | 7235_Bulli Creek - Waggamba 132 kV | Loading (MVA) | 16.8317 | 20.7968 | 13.2397 | 16.8318 | 20.7968 | 13.2397 | 17.7095 | 21.7845 | 13.7681 | 17.7092 | 21.7843 | 13.7679 | 17.707 | 21.7841 | 13.7677
SW-Bulli Creek Waggamba | 7235_Bulli Creek - Waggamba 132 kV | Loading (MW) | 16.0653 | 20.3618 | 11.9259 | 16.0653 | 20.3618 | 11.9259 | 17.0457 | 21.4645 | 12.5629 | 17.0458 | 21.4645 | 12.5629 | 17.0459 | 21.4645 | 12.563
SW-Bulli Creek Waggamba | 7235_Bulli Creek - Waggamba 132 kV | Power Factor | 0.95446 | 0.97908 | 0.90077 | 0.95446 | 0.97908 | 0.90076 | 0.96252 | 0.98531 | 0.91247 | 0.96254 | 0.98532 | 0.91248 | 0.96267 | 0.98533 | 0.9125
SW-Bulli Creek Waggamba | 7235_Bulli Creek - Waggamba 132 kV | Rating (A) | 650 | 659 | 575 | 650 | 659 | 575 | 650 | 659 | 575 | 650 | 659 | 575 | 650 | 659 | 575
SW-Bulli Creek Waggamba | 7235_Bulli Creek - Waggamba 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Bulli Creek Waggamba | 7235_Bulli Creek - Waggamba 132 kV | Min Voltage at Constrained Conductor | 139.5118 | 139.3671 | 139.844 | 139.513 | 139.3668 | 139.8443 | 139.4717 | 137.4665 | 139.8215 | 139.4608 | 137.4578 | 139.8177 | 139.3841 | 137.4451 | 139.8114
SW-Bulli Creek Waggamba | 7235_Bulli Creek - Waggamba 132 kV | Contingency Outage | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | 7234_Middle Ridge-Torrington 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F4132_Shirley Road 33 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV
SW-Chinchilla Western Network | 3196_Tara 33 kV | % of Rated A | 14.8% | 12.59% | 9.209% | 14.79% | 12.59% | 9.21% | 14.79% | 12.59% | 9.21% | 14.79% | 12.59% | 9.209% | 14.8% | 12.59% | 9.209%
SW-Chinchilla Western Network | 3196_Tara 33 kV | Limiting Line Name | TR_LINE 27355_1 | TR_LINE 24024_1 | TR_LINE 24024_1 | TR_LINE 27355_1 | TR_LINE 24024_1 | TR_LINE 24024_1 | TR_LINE 27355_1 | TR_LINE 24024_1 | TR_LINE 24024_1 | TR_LINE 27355_1 | TR_LINE 24024_1 | TR_LINE 24024_1 | TR_LINE 27355_1 | TR_LINE 24024_1 | TR_LINE 24024_1
SW-Chinchilla Western Network | 3196_Tara 33 kV | Loading (A) | 13.7641 | 14.6091 | 10.6828 | 13.7578 | 14.6037 | 10.683 | 13.7569 | 14.6005 | 10.6831 | 13.7572 | 14.6011 | 10.683 | 13.7632 | 14.6094 | 10.6826
SW-Chinchilla Western Network | 3196_Tara 33 kV | Loading (MVA) | 0.77749 | 0.82801 | 0.61776 | 0.77776 | 0.82822 | 0.61786 | 0.77781 | 0.82827 | 0.61789 | 0.77779 | 0.82825 | 0.61784 | 0.77754 | 0.82799 | 0.61766
SW-Chinchilla Western Network | 3196_Tara 33 kV | Loading (MW) | 0.7307 | 0.78739 | 0.48622 | 0.7307 | 0.78738 | 0.48622 | 0.7307 | 0.78738 | 0.48622 | 0.7307 | 0.78738 | 0.48622 | 0.7307 | 0.78739 | 0.48622
SW-Chinchilla Western Network | 3196_Tara 33 kV | Power Factor | 0.93982 | 0.95094 | 0.78707 | 0.9395 | 0.95069 | 0.78694 | 0.93944 | 0.95063 | 0.78691 | 0.93946 | 0.95066 | 0.78697 | 0.93976 | 0.95096 | 0.78719
SW-Chinchilla Western Network | 3196_Tara 33 kV | Rating (A) | 93 | 116 | 116 | 93 | 116 | 116 | 93 | 116 | 116 | 93 | 116 | 116 | 93 | 116 | 116
SW-Chinchilla Western Network | 3196_Tara 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Chinchilla Western Network | 3196_Tara 33 kV | Min Voltage at Constrained Conductor | 32.6118 | 32.7225 | 33.3867 | 32.6378 | 32.7432 | 33.3915 | 32.642 | 32.7525 | 33.3927 | 32.6405 | 32.75 | 33.3903 | 32.616 | 32.7214 | 33.382
SW-Chinchilla Western Network | 3196_Tara 33 kV | Contingency Outage | F5540_7244 Tangkam-Dalby 110 kV | F5545_7245 Tangkam-Dalby 110 kV | 3153_Cecil Plains Road 33 kV | F5540_7244 Tangkam-Dalby 110 kV | F5545_7245 Tangkam-Dalby 110 kV | 3153_Cecil Plains Road 33 kV | F5540_7244 Tangkam-Dalby 110 kV | F5545_7245 Tangkam-Dalby 110 kV | 3153_Cecil Plains Road 33 kV | F5540_7244 Tangkam-Dalby 110 kV | F5545_7245 Tangkam-Dalby 110 kV | 3153_Cecil Plains Road 33 kV | F5545_7245 Tangkam-Dalby 110 kV | F5545_7245 Tangkam-Dalby 110 kV | 3153_Cecil Plains Road 33 kV
SW-Chinchilla Western Network | 3203_Miles 33 kV | % of Rated A | 81.63% | 83% | 38.46% | 80.69% | 81.99% | 38.11% | 79.76% | 81.03% | 37.72% | 79.76% | 81.03% | 37.72% | 81.63% | 83% | 38.46%
SW-Chinchilla Western Network | 3203_Miles 33 kV | Limiting Line Name | TR_CABLE 8720_1 | TR_CABLE 8720_1 | HV_CABLE 219934_1 | TR_CABLE 8720_1 | TR_CABLE 8720_1 | HV_CABLE 219934_1 | TR_CABLE 8720_1 | TR_CABLE 8720_1 | HV_CABLE 219934_1 | TR_CABLE 8720_1 | TR_CABLE 8720_1 | HV_CABLE 219934_1 | TR_CABLE 8720_1 | TR_CABLE 8720_1 | HV_CABLE 219934_1
SW-Chinchilla Western Network | 3203_Miles 33 kV | Loading (A) | 147.744 | 150.2296 | 69.6151 | 146.0441 | 148.4041 | 68.9746 | 144.3727 | 146.667 | 68.2709 | 144.3727 | 146.667 | 68.2709 | 147.744 | 150.2295 | 69.6151
SW-Chinchilla Western Network | 3203_Miles 33 kV | Loading (MVA) | 8.4269 | 8.5693 | 4.0618 | 8.3325 | 8.4679 | 4.0248 | 8.2402 | 8.372 | 3.984 | 8.2402 | 8.372 | 3.984 | 8.4269 | 8.5693 | 4.0618
SW-Chinchilla Western Network | 3203_Miles 33 kV | Loading (MW) | 8.3641 | 8.5169 | 4.0597 | 8.2703 | 8.4163 | 4.0222 | 8.18 | 8.3221 | 3.9811 | 8.18 | 8.3221 | 3.9811 | 8.3641 | 8.5169 | 4.0597
SW-Chinchilla Western Network | 3203_Miles 33 kV | Power Factor | 0.9925 | 0.99385 | 0.99949 | 0.99249 | 0.99386 | 0.99936 | 0.99264 | 0.99399 | 0.99927 | 0.99264 | 0.99399 | 0.99927 | 0.9925 | 0.99385 | 0.99949
SW-Chinchilla Western Network | 3203_Miles 33 kV | Rating (A) | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181
SW-Chinchilla Western Network | 3203_Miles 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Chinchilla Western Network | 3203_Miles 33 kV | Min Voltage at Constrained Conductor | 32.9305 | 32.9327 | 33.6857 | 32.9406 | 32.9436 | 33.6887 | 32.9529 | 32.9561 | 33.6909 | 32.9529 | 32.9561 | 33.6909 | 32.9305 | 32.9327 | 33.6857
SW-Chinchilla Western Network | 3203_Miles 33 kV | Contingency Outage | F083C_Chinchilla 33 kV | F083C_Chinchilla 33 kV | F083C_Chinchilla 33 kV | F083C_Chinchilla 33 kV | F083C_Chinchilla 33 kV | F083C_Chinchilla 33 kV | F083C_Chinchilla 33 kV | F083C_Chinchilla 33 kV | F083C_Chinchilla 33 kV | F083C_Chinchilla 33 kV | F083C_Chinchilla 33 kV | F083C_Chinchilla 33 kV | F083C_Chinchilla 33 kV | F083C_Chinchilla 33 kV | F083C_Chinchilla 33 kV
SW-Chinchilla Western Network | F001R_Yuleba 33 kV | % of Rated A | 14.11% | 10.65% | 7.416% | 14.1% | 10.65% | 7.415% | 14.16% | 10.69% | 7.422% | 14.16% | 10.69% | 7.422% | 14.17% | 10.69% | 7.423%
SW-Chinchilla Western Network | F001R_Yuleba 33 kV | Limiting Line Name | TR_LINE 28050_1 | TR_LINE 28050_1 | TR_LINE 28050_1 | TR_LINE 28050_1 | TR_LINE 28050_1 | TR_LINE 28050_1 | TR_LINE 28050_1 | TR_LINE 28050_1 | TR_LINE 28050_1 | TR_LINE 28050_1 | TR_LINE 28050_1 | TR_LINE 28050_1 | TR_LINE 28050_1 | TR_LINE 28050_1 | TR_LINE 28050_1
SW-Chinchilla Western Network | F001R_Yuleba 33 kV | Loading (A) | 13.1197 | 12.8887 | 8.6025 | 13.1172 | 12.8838 | 8.6012 | 13.1693 | 12.9336 | 8.61 | 13.1693 | 12.9336 | 8.61 | 13.1737 | 12.9374 | 8.6107
SW-Chinchilla Western Network | F001R_Yuleba 33 kV | Loading (MVA) | 0.73292 | 0.72073 | 0.48213 | 0.73314 | 0.7208 | 0.48214 | 0.73327 | 0.72093 | 0.48211 | 0.73327 | 0.72093 | 0.48211 | 0.73331 | 0.72095 | 0.48211
SW-Chinchilla Western Network | F001R_Yuleba 33 kV | Loading (MW) | 0.71043 | 0.71003 | 0.48182 | 0.71022 | 0.7098 | 0.48183 | 0.71036 | 0.70995 | 0.48179 | 0.71036 | 0.70995 | 0.48179 | 0.71035 | 0.70994 | 0.48178
SW-Chinchilla Western Network | F001R_Yuleba 33 kV | Power Factor | 0.96932 | 0.98516 | 0.99936 | 0.96874 | 0.98475 | 0.99936 | 0.96875 | 0.98476 | 0.99933 | 0.96875 | 0.98476 | 0.99933 | 0.9687 | 0.98473 | 0.99932
SW-Chinchilla Western Network | F001R_Yuleba 33 kV | Rating (A) | 93 | 121 | 116 | 93 | 121 | 116 | 93 | 121 | 116 | 93 | 121 | 116 | 93 | 121 | 116
SW-Chinchilla Western Network | F001R_Yuleba 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Chinchilla Western Network | F001R_Yuleba 33 kV | Min Voltage at Constrained Conductor | 32.2529 | 32.2849 | 32.358 | 32.2691 | 32.3003 | 32.3631 | 32.1472 | 32.1822 | 32.3282 | 32.1472 | 32.1822 | 32.3282 | 32.1378 | 32.1734 | 32.3257
SW-Chinchilla Western Network | F001R_Yuleba 33 kV | Contingency Outage | 7374_Roma Power Station 132 kV | 7374_Roma Power Station 132 kV | F217R_St George 66 kV | 7374_Roma Power Station 132 kV | 7374_Roma Power Station 132 kV | F217R_St George 66 kV | 7374_Roma Power Station 132 kV | 7374_Roma Power Station 132 kV | F217R_St George 66 kV | 7374_Roma Power Station 132 kV | 7374_Roma Power Station 132 kV | F217R_St George 66 kV | 7374_Roma Power Station 132 kV | 7374_Roma Power Station 132 kV | F217R_St George 66 kV
SW-Chinchilla Western Network | F022R_Brucedale 33 kV | % of Rated A | 10.34% | 8.37% | 5.909% | 10.34% | 8.366% | 5.908% | 10.38% | 8.398% | 5.92% | 10.38% | 8.398% | 5.92% | 10.39% | 8.4% | 5.92%
SW-Chinchilla Western Network | F022R_Brucedale 33 kV | Limiting Line Name | TR_LINE 22816_1 | TR_LINE 22816_1 | TR_LINE 25050_1 | TR_LINE 22816_1 | TR_LINE 22816_1 | TR_LINE 25050_1 | TR_LINE 22816_1 | TR_LINE 22816_1 | TR_LINE 25050_1 | TR_LINE 22816_1 | TR_LINE 22816_1 | TR_LINE 25050_1 | TR_LINE 22816_1 | TR_LINE 22816_1 | TR_LINE 25050_1
SW-Chinchilla Western Network | F022R_Brucedale 33 kV | Loading (A) | 9.62 | 10.1275 | 6.8542 | 9.6147 | 10.1224 | 6.8534 | 9.6549 | 10.1616 | 6.8674 | 9.6549 | 10.1616 | 6.8674 | 9.662 | 10.1645 | 6.8677
SW-Chinchilla Western Network | F022R_Brucedale 33 kV | Loading (MVA) | 0.5373 | 0.5663 | 0.38416 | 0.53727 | 0.56628 | 0.38418 | 0.53748 | 0.56639 | 0.38454 | 0.53748 | 0.56639 | 0.38454 | 0.53772 | 0.56639 | 0.38453
SW-Chinchilla Western Network | F022R_Brucedale 33 kV | Loading (MW) | 0.53615 | 0.56622 | 0.37558 | 0.53614 | 0.56621 | 0.37558 | 0.5362 | 0.56628 | 0.3756 | 0.5362 | 0.56628 | 0.3756 | 0.53624 | 0.56628 | 0.3756
SW-Chinchilla Western Network | F022R_Brucedale 33 kV | Power Factor | 0.99765 | 0.99982 | 0.97768 | 0.99768 | 0.99983 | 0.97763 | 0.9974 | 0.99975 | 0.97675 | 0.9974 | 0.99975 | 0.97675 | 0.99704 | 0.99974 | 0.97678
SW-Chinchilla Western Network | F022R_Brucedale 33 kV | Rating (A) | 93 | 121 | 116 | 93 | 121 | 116 | 93 | 121 | 116 | 93 | 121 | 116 | 93 | 121 | 116
SW-Chinchilla Western Network | F022R_Brucedale 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Chinchilla Western Network | F022R_Brucedale 33 kV | Min Voltage at Constrained Conductor | 32.2464 | 32.2781 | 32.3583 | 32.2626 | 32.2936 | 32.3634 | 32.1407 | 32.1754 | 32.3285 | 32.1407 | 32.1754 | 32.3285 | 32.1312 | 32.1666 | 32.326
SW-Chinchilla Western Network | F022R_Brucedale 33 kV | Contingency Outage | 7374_Roma Power Station 132 kV | 7374_Roma Power Station 132 kV | F217R_St George 66 kV | 7374_Roma Power Station 132 kV | 7374_Roma Power Station 132 kV | F217R_St George 66 kV | 7374_Roma Power Station 132 kV | 7374_Roma Power Station 132 kV | F217R_St George 66 kV | 7374_Roma Power Station 132 kV | 7374_Roma Power Station 132 kV | F217R_St George 66 kV | 7374_Roma Power Station 132 kV | 7374_Roma Power Station 132 kV | F217R_St George 66 kV
SW-Chinchilla Western Network | F049R_Roma North 33 kV | % of Rated A | 53.87% | 46.1% | 22.8% | 53.87% | 46.1% | 22.8% | 53.87% | 46.1% | 22.8% | 53.87% | 46.1% | 22.8% | 53.87% | 46.1% | 22.8%
SW-Chinchilla Western Network | F049R_Roma North 33 kV | Limiting Line Name | TR_LINE 22900_1 | TR_LINE 22900_1 | TR_LINE 22900_1 | TR_LINE 22900_1 | TR_LINE 22900_1 | TR_LINE 22900_1 | TR_LINE 22900_1 | TR_LINE 22900_1 | TR_LINE 22900_1 | TR_LINE 22900_1 | TR_LINE 22900_1 | TR_LINE 22900_1 | TR_LINE 22900_1 | TR_LINE 22900_1 | TR_LINE 22900_1
SW-Chinchilla Western Network | F049R_Roma North 33 kV | Loading (A) | 50.1031 | 55.8213 | 26.5116 | 50.1031 | 55.8213 | 26.5116 | 50.1031 | 55.8213 | 26.5116 | 50.1031 | 55.8213 | 26.5116 | 50.1031 | 55.8213 | 26.5116
SW-Chinchilla Western Network | F049R_Roma North 33 kV | Loading (MVA) | 2.7993 | 3.1212 | 1.4878 | 2.7993 | 3.1212 | 1.4878 | 2.7993 | 3.1212 | 1.4878 | 2.7993 | 3.1212 | 1.4878 | 2.7993 | 3.1212 | 1.4878
SW-Chinchilla Western Network | F049R_Roma North 33 kV | Loading (MW) | 2.6693 | 2.9812 | 1.4696 | 2.6693 | 2.9812 | 1.4696 | 2.6693 | 2.9812 | 1.4696 | 2.6693 | 2.9812 | 1.4696 | 2.6693 | 2.9812 | 1.4696
SW-Chinchilla Western Network | F049R_Roma North 33 kV | Power Factor | 0.95355 | 0.95516 | 0.98773 | 0.95355 | 0.95516 | 0.98773 | 0.95355 | 0.95516 | 0.98773 | 0.95355 | 0.95516 | 0.98773 | 0.95355 | 0.95516 | 0.98773
SW-Chinchilla Western Network | F049R_Roma North 33 kV | Rating (A) | 93 | 121 | 116 | 93 | 121 | 116 | 93 | 121 | 116 | 93 | 121 | 116 | 93 | 121 | 116
SW-Chinchilla Western Network | F049R_Roma North 33 kV | Time | 16:30:00 | 19:00 | 5:30 | 16:30:00 | 19:00 | 5:30 | 16:30:00 | 19:00 | 5:30 | 16:30:00 | 19:00 | 5:30 | 16:30:00 | 19:00 | 5:30
SW-Chinchilla Western Network | F049R_Roma North 33 kV | Min Voltage at Constrained Conductor | 32.2 | 32.2 | 32.4 | 32.2 | 32.2 | 32.4 | 32.2 | 32.2 | 32.4 | 32.2 | 32.2 | 32.4 | 32.2 | 32.2 | 32.4
SW-Chinchilla Western Network | F049R_Roma North 33 kV | Contingency Outage | F079S_St George Meatworks 33 kV | F079S_St George Meatworks 33 kV | F079S_St George Meatworks 33 kV | F079S_St George Meatworks 33 kV | F079S_St George Meatworks 33 kV | F079S_St George Meatworks 33 kV | F079S_St George Meatworks 33 kV | F079S_St George Meatworks 33 kV | F079S_St George Meatworks 33 kV | F079S_St George Meatworks 33 kV | F079S_St George Meatworks 33 kV | F079S_St George Meatworks 33 kV | F079S_St George Meatworks 33 kV | F079S_St George Meatworks 33 kV | F079S_St George Meatworks 33 kV
SW-Chinchilla Western Network | F060T_Tara 33 kV | % of Rated A | 14.7% | 11.97% | 9.188% | 14.7% | 11.97% | 9.188% | 14.7% | 11.97% | 9.188% | 14.7% | 11.97% | 9.188% | 14.72% | 11.97% | 9.187%
SW-Chinchilla Western Network | F060T_Tara 33 kV | Limiting Line Name | TR_LINE 23982_1 | TR_LINE 23982_1 | TR_LINE 23982_1 | TR_LINE 23982_1 | TR_LINE 23982_1 | TR_LINE 23982_1 | TR_LINE 23982_1 | TR_LINE 23982_1 | TR_LINE 23982_1 | TR_LINE 23982_1 | TR_LINE 23982_1 | TR_LINE 23982_1 | TR_LINE 23982_1 | TR_LINE 23982_1 | TR_LINE 23982_1
SW-Chinchilla Western Network | F060T_Tara 33 kV | Loading (A) | 13.6739 | 14.6088 | 10.7494 | 13.6676 | 14.6034 | 10.7496 | 13.6667 | 14.6002 | 10.7497 | 13.667 | 14.6008 | 10.7496 | 13.6924 | 14.6091 | 10.7492
SW-Chinchilla Western Network | F060T_Tara 33 kV | Loading (MVA) | 0.7774 | 0.82821 | 0.61799 | 0.77767 | 0.82842 | 0.61809 | 0.77771 | 0.82848 | 0.61812 | 0.7777 | 0.82845 | 0.61807 | 0.77643 | 0.8282 | 0.61789
SW-Chinchilla Western Network | F060T_Tara 33 kV | Loading (MW) | 0.7306 | 0.78734 | 0.48619 | 0.7306 | 0.78733 | 0.4862 | 0.7306 | 0.78733 | 0.4862 | 0.7306 | 0.78733 | 0.4862 | 0.73062 | 0.78734 | 0.48619
SW-Chinchilla Western Network | F060T_Tara 33 kV | Power Factor | 0.9398 | 0.95065 | 0.78673 | 0.93948 | 0.95039 | 0.78661 | 0.93942 | 0.95033 | 0.78657 | 0.93944 | 0.95036 | 0.78664 | 0.94101 | 0.95066 | 0.78686
SW-Chinchilla Western Network | F060T_Tara 33 kV | Rating (A) | 93 | 122 | 117 | 93 | 122 | 117 | 93 | 122 | 117 | 93 | 122 | 117 | 93 | 122 | 117
SW-Chinchilla Western Network | F060T_Tara 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Chinchilla Western Network | F060T_Tara 33 kV | Min Voltage at Constrained Conductor | 32.8233 | 32.7305 | 33.192 | 32.8495 | 32.7511 | 33.1967 | 32.8537 | 32.7605 | 33.198 | 32.8522 | 32.758 | 33.1955 | 32.7379 | 32.7294 | 33.1873
SW-Chinchilla Western Network | F060T_Tara 33 kV | Contingency Outage | F5540_7244 Tangkam-Dalby 110 kV | F5545_7245 Tangkam-Dalby 110 kV | 3153_Cecil Plains Road 33 kV | F5540_7244 Tangkam-Dalby 110 kV | F5545_7245 Tangkam-Dalby 110 kV | 3153_Cecil Plains Road 33 kV | F5540_7244 Tangkam-Dalby 110 kV | F5545_7245 Tangkam-Dalby 110 kV | 3153_Cecil Plains Road 33 kV | F5540_7244 Tangkam-Dalby 110 kV | F5545_7245 Tangkam-Dalby 110 kV | 3153_Cecil Plains Road 33 kV | F5540_7244 Tangkam-Dalby 110 kV | F5545_7245 Tangkam-Dalby 110 kV | 3153_Cecil Plains Road 33 kV
SW-Chinchilla Western Network | F067C_Kogan 33 kV | % of Rated A | 39.42% | 26.45% | 26.74% | 39.4% | 26.45% | 26.73% | 38.9% | 26.45% | 26.73% | 38.91% | 26.45% | 26.73% | 39.4% | 26.45% | 26.73%
SW-Chinchilla Western Network | F067C_Kogan 33 kV | Limiting Line Name | TR_LINE 27340_1 | TR_LINE 28354_1 | TR_LINE 27340_1 | TR_LINE 27340_1 | TR_LINE 28354_1 | TR_LINE 27340_1 | TR_LINE 27340_1 | TR_LINE 28354_1 | TR_LINE 27340_1 | TR_LINE 27340_1 | TR_LINE 28354_1 | TR_LINE 27340_1 | TR_LINE 27340_1 | TR_LINE 28354_1 | TR_LINE 27340_1
SW-Chinchilla Western Network | F067C_Kogan 33 kV | Loading (A) | 36.6648 | 32.2707 | 31.2836 | 36.6434 | 32.2707 | 31.278 | 36.1812 | 32.2693 | 31.2761 | 36.1877 | 32.2693 | 31.2778 | 36.6459 | 32.2745 | 31.2778
SW-Chinchilla Western Network | F067C_Kogan 33 kV | Loading (MVA) | 2.0587 | 1.8381 | 1.7588 | 2.0586 | 1.8381 | 1.7587 | 2.0331 | 1.8381 | 1.7587 | 2.0331 | 1.8381 | 1.7587 | 2.0586 | 1.8382 | 1.7587
SW-Chinchilla Western Network | F067C_Kogan 33 kV | Loading (MW) | 1.6786 | 1.5325 | 1.4343 | 1.6786 | 1.5325 | 1.4343 | 1.6668 | 1.5325 | 1.4343 | 1.6668 | 1.5325 | 1.4343 | 1.6786 | 1.5325 | 1.4343
SW-Chinchilla Western Network | F067C_Kogan 33 kV | Power Factor | 0.81188 | 0.83357 | 0.8115 | 0.81191 | 0.83357 | 0.81152 | 0.81631 | 0.83357 | 0.81152 | 0.8163 | 0.83357 | 0.81152 | 0.81191 | 0.83356 | 0.81152
SW-Chinchilla Western Network | F067C_Kogan 33 kV | Rating (A) | 93 | 122 | 117 | 93 | 122 | 117 | 93 | 122 | 117 | 93 | 122 | 117 | 93 | 122 | 117
SW-Chinchilla Western Network | F067C_Kogan 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Chinchilla Western Network | F067C_Kogan 33 kV | Min Voltage at Constrained Conductor | 32.3205 | 32.8828 | 32.4173 | 32.3379 | 32.8828 | 32.4225 | 32.3489 | 32.884 | 32.4243 | 32.3436 | 32.884 | 32.4227 | 32.3358 | 32.8796 | 32.4227
SW-Chinchilla Western Network | F067C_Kogan 33 kV | Contingency Outage | F071C RYWUNG | F083C_Chinchilla 33 kV | F069C_Brigalow 33 kV | F071C RYWUNG | F083C_Chinchilla 33 kV | F069C_Brigalow 33 kV | F071C RYWUNG | F083C_Chinchilla 33 kV | F069C_Brigalow 33 kV | F071C RYWUNG | F083C_Chinchilla 33 kV | F069C_Brigalow 33 kV | F071C RYWUNG | F083C_Chinchilla 33 kV | F069C_Brigalow 33 kV
SW-Chinchilla Western Network | F069C_Brigalow 33 kV | % of Rated A | 24.07% | 20.53% | 10.46% | 24.05% | 20.53% | 10.46% | 24.05% | 20.53% | 10.45% | 24.05% | 20.53% | 10.45% | 26.55% | 22.67% | 11.47%
SW-Chinchilla Western Network | F069C_Brigalow 33 kV | Limiting Line Name | TR_LINE 28423_1 | TR_LINE 28423_1 | TR_LINE 28423_1 | TR_LINE 28423_1 | TR_LINE 28423_1 | TR_LINE 28423_1 | TR_LINE 28423_1 | TR_LINE 28423_1 | TR_LINE 28423_1 | TR_LINE 28423_1 | TR_LINE 28423_1 | TR_LINE 28423_1 | TR_LINE 28423_1 | TR_LINE 28423_1 | TR_LINE 28423_1
SW-Chinchilla Western Network | F069C_Brigalow 33 kV | Loading (A) | 14.6803 | 15.8101 | 7.6336 | 14.6724 | 15.8101 | 7.6326 | 14.6682 | 15.8088 | 7.6318 | 14.6706 | 15.8088 | 7.6321 | 16.1933 | 17.454 | 8.3729
SW-Chinchilla Western Network | F069C_Brigalow 33 kV | Loading (MVA) | 0.83795 | 0.90439 | 0.4382 | 0.83794 | 0.90439 | 0.4382 | 0.83793 | 0.90438 | 0.4382 | 0.83793 | 0.90438 | 0.4382 | 0.92349 | 0.99686 | 0.48038
SW-Chinchilla Western Network | F069C_Brigalow 33 kV | Loading (MW) | 0.83784 | 0.904 | 0.43388 | 0.83783 | 0.904 | 0.43388 | 0.83782 | 0.904 | 0.43388 | 0.83782 | 0.904 | 0.43388 | 0.92298 | 0.99583 | 0.47736
SW-Chinchilla Western Network | F069C_Brigalow 33 kV | Power Factor | 0.99986 | 0.99957 | 0.99015 | 0.99987 | 0.99957 | 0.99014 | 0.99987 | 0.99957 | 0.99013 | 0.99987 | 0.99957 | 0.99013 | 0.99944 | 0.99897 | 0.99372
SW-Chinchilla Western Network | F069C_Brigalow 33 kV | Rating (A) | 61 | 77 | 73 | 61 | 77 | 73 | 61 | 77 | 73 | 61 | 77 | 73 | 61 | 77 | 73
SW-Chinchilla Western Network | F069C_Brigalow 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Chinchilla Western Network | F069C_Brigalow 33 kV | Min Voltage at Constrained Conductor | 32.9537 | 33.0246 | 33.1411 | 32.9707 | 33.0246 | 33.1462 | 32.9797 | 33.0271 | 33.1499 | 32.9746 | 33.0271 | 33.1483 | 32.9242 | 32.9728 | 33.1235
SW-Chinchilla Western Network | F069C_Brigalow 33 kV | Contingency Outage | F071C RYWUNG | F083C_Chinchilla 33 kV | F073C_Fairymeadow 33 kV | F071C RYWUNG | F083C_Chinchilla 33 kV | F073C_Fairymeadow 33 kV | F071C RYWUNG | F083C_Chinchilla 33 kV | F073C_Fairymeadow 33 kV | F071C RYWUNG | F083C_Chinchilla 33 kV | F073C_Fairymeadow 33 kV | F071C RYWUNG | F083C_Chinchilla 33 kV | F073C_Fairymeadow 33 kV
SW-Chinchilla Western Network | F071C RYWUNG | % of Rated A | 3.154% | 3.149% | 3.17% | 3.156% | 3.151% | 3.171% | 3.157% | 3.151% | 3.171% | 3.157% | 3.151% | 3.171% | 3.156% | 3.15% | 3.171%
SW-Chinchilla Western Network | F071C RYWUNG | Limiting Line Name | TR_LINE 199202_1 | TR_LINE 199202_1 | TR_LINE 199202_1 | TR_LINE 199202_1 | TR_LINE 199202_1 | TR_LINE 199202_1 | TR_LINE 199202_1 | TR_LINE 199202_1 | TR_LINE 199202_1 | TR_LINE 199202_1 | TR_LINE 199202_1 | TR_LINE 199202_1 | TR_LINE 199202_1 | TR_LINE 199202_1 | TR_LINE 199202_1
SW-Chinchilla Western Network | F071C RYWUNG | Loading (A) | 2.7759 | 2.7713 | 2.7897 | 2.7775 | 2.7726 | 2.7902 | 2.7783 | 2.7731 | 2.7905 | 2.7778 | 2.7727 | 2.7904 | 2.7775 | 2.7723 | 2.7902
SW-Chinchilla Western Network | F071C RYWUNG | Loading (MVA) | 0.16057 | 0.16094 | 0.16139 | 0.16075 | 0.16109 | 0.16145 | 0.16084 | 0.16114 | 0.16148 | 0.16079 | 0.16109 | 0.16146 | 0.16074 | 0.16105 | 0.16144
SW-Chinchilla Western Network | F071C RYWUNG | Loading (MW) | 0.009942 | 0.014999 | 0.0093356 | 0.0099438 | 0.015001 | 0.0093361 | 0.0099446 | 0.015001 | 0.0093364 | 0.0099441 | 0.015001 | 0.0093363 | 0.0099437 | 0.015 | 0.0093361
SW-Chinchilla Western Network | F071C RYWUNG | Power Factor | 0.061918 | 0.093198 | 0.057844 | 0.061857 | 0.093122 | 0.057827 | 0.06183 | 0.093092 | 0.057818 | 0.061847 | 0.093119 | 0.057823 | 0.06186 | 0.093142 | 0.057828
SW-Chinchilla Western Network | F071C RYWUNG | Rating (A) | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88
SW-Chinchilla Western Network | F071C RYWUNG | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Chinchilla Western Network | F071C RYWUNG | Min Voltage at Constrained Conductor | 33.3959 | 33.5283 | 33.401 | 33.4151 | 33.5434 | 33.4068 | 33.4235 | 33.5493 | 33.4098 | 33.4183 | 33.544 | 33.4082 | 33.4141 | 33.5395 | 33.4063
SW-Chinchilla Western Network | F071C RYWUNG | Contingency Outage | F067C_Kogan 33 kV | F067C_Kogan 33 kV | F067C_Kogan 33 kV | F067C_Kogan 33 kV | F067C_Kogan 33 kV | F067C_Kogan 33 kV | F067C_Kogan 33 kV | F067C_Kogan 33 kV | F067C_Kogan 33 kV | F067C_Kogan 33 kV | F067C_Kogan 33 kV | F067C_Kogan 33 kV | F067C_Kogan 33 kV | F067C_Kogan 33 kV | F067C_Kogan 33 kV
SW-Chinchilla Western Network | F073C_Fairymeadow 33 kV | % of Rated A | 4.092% | 4.525% | 2.398% | 4.086% | 4.525% | 2.398% | 4.085% | 4.525% | 2.398% | 4.086% | 4.525% | 2.398% | 4.086% | 4.526% | 2.398%
SW-Chinchilla Western Network | F073C_Fairymeadow 33 kV | Limiting Line Name | TR_LINE 174241_1 | TR_CABLE 124_1 | TR_LINE 174241_1 | TR_LINE 174241_1 | TR_CABLE 124_1 | TR_LINE 174241_1 | TR_LINE 174241_1 | TR_CABLE 124_1 | TR_LINE 174241_1 | TR_LINE 174241_1 | TR_CABLE 124_1 | TR_LINE 174241_1 | TR_LINE 174241_1 | TR_CABLE 124_1 | TR_LINE 174241_1
SW-Chinchilla Western Network | F073C_Fairymeadow 33 kV | Loading (A) | 3.8058 | 4.5254 | 2.7818 | 3.8 | 4.5254 | 2.7818 | 3.7994 | 4.5253 | 2.7817 | 3.7998 | 4.5253 | 2.7818 | 3.8002 | 4.5258 | 2.7818
SW-Chinchilla Western Network | F073C_Fairymeadow 33 kV | Loading (MVA) | 0.21973 | 0.25784 | 0.16051 | 0.21951 | 0.25784 | 0.16053 | 0.21952 | 0.25784 | 0.16054 | 0.21951 | 0.25784 | 0.16053 | 0.2195 | 0.25784 | 0.16053
SW-Chinchilla Western Network | F073C_Fairymeadow 33 kV | Loading (MW) | 0.21508 | 0.23977 | 0.14145 | 0.21503 | 0.23977 | 0.14145 | 0.21503 | 0.23977 | 0.14145 | 0.21503 | 0.23977 | 0.14145 | 0.21503 | 0.23977 | 0.14145
SW-Chinchilla Western Network | F073C_Fairymeadow 33 kV | Power Factor | 0.97881 | 0.92881 | 0.88121 | 0.97961 | 0.92881 | 0.8811 | 0.97956 | 0.92881 | 0.88107 | 0.9796 | 0.92881 | 0.8811 | 0.97963 | 0.92881 | 0.8811
SW-Chinchilla Western Network | F073C_Fairymeadow 33 kV | Rating (A) | 93 | 100 | 116 | 93 | 100 | 116 | 93 | 100 | 116 | 93 | 100 | 116 | 93 | 100 | 116
SW-Chinchilla Western Network | F073C_Fairymeadow 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Chinchilla Western Network | F073C_Fairymeadow 33 kV | Min Voltage at Constrained Conductor | 33.3333 | 32.8954 | 33.3131 | 33.3498 | 32.8954 | 33.3181 | 33.3569 | 32.8966 | 33.3199 | 33.3519 | 32.8966 | 33.3183 | 33.3478 | 32.8923 | 33.3183
SW-Chinchilla Western Network | F073C_Fairymeadow 33 kV | Contingency Outage | F071C RYWUNG | F083C_Chinchilla 33 kV | F069C_Brigalow 33 kV | F071C RYWUNG | F083C_Chinchilla 33 kV | F069C_Brigalow 33 kV | F071C RYWUNG | F083C_Chinchilla 33 kV | F069C_Brigalow 33 kV | F071C RYWUNG | F083C_Chinchilla 33 kV | F069C_Brigalow 33 kV | F071C RYWUNG | F083C_Chinchilla 33 kV | F069C_Brigalow 33 kV
SW-Chinchilla Western Network | F074C_Miles-Condamine 33 kV | % of Rated A | 15.47% | 11.89% | 6.784% | 15.46% | 11.29% | 6.525% | 15.45% | 11.29% | 6.524% | 15.45% | 11.29% | 6.524% | 15.47% | 11.89% | 6.784%
SW-Chinchilla Western Network | F074C_Miles-Condamine 33 kV | Limiting Line Name | TR_LINE 138809_5 | TR_LINE 195522_1 | TR_LINE 42883_1 | TR_LINE 138809_5 | TR_LINE 195522_1 | TR_LINE 42883_1 | TR_LINE 138809_5 | TR_LINE 195522_1 | TR_LINE 42883_1 | TR_LINE 138809_5 | TR_LINE 195522_1 | TR_LINE 42883_1 | TR_LINE 138809_5 | TR_LINE 195522_1 | TR_LINE 42883_1
SW-Chinchilla Western Network | F074C_Miles-Condamine 33 kV | Loading (A) | 22.1227 | 35.0746 | 17.8417 | 22.1053 | 33.3113 | 17.1598 | 22.0968 | 33.2982 | 17.1582 | 22.0968 | 33.2982 | 17.1582 | 22.1227 | 35.0747 | 17.8417
SW-Chinchilla Western Network | F074C_Miles-Condamine 33 kV | Loading (MVA) | 1.2499 | 1.9992 | 1.0155 | 1.25 | 1.8993 | 0.98288 | 1.25 | 1.8993 | 0.98292 | 1.25 | 1.8993 | 0.98292 | 1.2499 | 1.9992 | 1.0155
SW-Chinchilla Western Network | F074C_Miles-Condamine 33 kV | Loading (MW) | 1.2476 | 1.9976 | 0.97547 | 1.2476 | 1.8971 | 0.93864 | 1.2476 | 1.8971 | 0.93864 | 1.2476 | 1.8971 | 0.93864 | 1.2476 | 1.9976 | 0.97547
SW-Chinchilla Western Network | F074C_Miles-Condamine 33 kV | Power Factor | 0.99813 | 0.99918 | 0.96061 | 0.99809 | 0.99881 | 0.95499 | 0.9981 | 0.9988 | 0.95494 | 0.9981 | 0.9988 | 0.95494 | 0.99813 | 0.99918 | 0.96061
SW-Chinchilla Western Network | F074C_Miles-Condamine 33 kV | Rating (A) | 143 | 295 | 263 | 143 | 295 | 263 | 143 | 295 | 263 | 143 | 295 | 263 | 143 | 295 | 263
SW-Chinchilla Western Network | F074C_Miles-Condamine 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Chinchilla Western Network | F074C_Miles-Condamine 33 kV | Min Voltage at Constrained Conductor | 32.607 | 32.908 | 32.859 | 32.6331 | 32.9189 | 33.0686 | 32.6455 | 32.9316 | 33.0731 | 32.6455 | 32.9317 | 33.0731 | 32.6069 | 32.908 | 32.859
SW-Chinchilla Western Network | F074C_Miles-Condamine 33 kV | Contingency Outage | F076C_Dulacca 33 kV | F076C_Dulacca 33 kV | F076C_Dulacca 33 kV | F076C_Dulacca 33 kV | F076C_Dulacca 33 kV | F076C_Dulacca 33 kV | F076C_Dulacca 33 kV | F076C_Dulacca 33 kV | F076C_Dulacca 33 kV | F076C_Dulacca 33 kV | F076C_Dulacca 33 kV | F076C_Dulacca 33 kV | F076C_Dulacca 33 kV | F076C_Dulacca 33 kV | F076C_Dulacca 33 kV
SW-Chinchilla Western Network | F075S_St George Town 33 kV | % of Rated A | 53.55% | 52.04% | 23.8% | 53.56% | 52.04% | 23.81% | 53.54% | 52.02% | 23.8% | 53.54% | 52.02% | 23.8% | 53.54% | 52.02% | 23.8%
SW-Chinchilla Western Network | F075S_St George Town 33 kV | Limiting Line Name | TR_CABLE 16563_1 | TR_CABLE 16563_1 | TR_LINE 25567_1 | TR_CABLE 16563_1 | TR_CABLE 16563_1 | TR_LINE 25567_1 | TR_CABLE 16563_1 | TR_CABLE 16563_1 | TR_LINE 25567_1 | TR_CABLE 16563_1 | TR_CABLE 16563_1 | TR_LINE 25567_1 | TR_CABLE 16563_1 | TR_CABLE 16563_1 | TR_LINE 25567_1
SW-Chinchilla Western Network | F075S_St George Town 33 kV | Loading (A) | 87.8298 | 85.3434 | 39.04 | 87.8339 | 85.3473 | 39.0405 | 87.8046 | 85.3196 | 39.037 | 87.8046 | 85.3196 | 39.037 | 87.8024 | 85.3175 | 39.0368
SW-Chinchilla Western Network | F075S_St George Town 33 kV | Loading (MVA) | 5.0219 | 4.8796 | 2.2135 | 5.0219 | 4.8796 | 2.2135 | 5.0218 | 4.8795 | 2.2135 | 5.0218 | 4.8795 | 2.2135 | 5.0218 | 4.8795 | 2.2135
SW-Chinchilla Western Network | F075S_St George Town 33 kV | Loading (MW) | 4.8272 | 4.6926 | 2.1466 | 4.8272 | 4.6926 | 2.1466 | 4.8272 | 4.6926 | 2.1466 | 4.8272 | 4.6926 | 2.1466 | 4.8272 | 4.6926 | 2.1466
SW-Chinchilla Western Network | F075S_St George Town 33 kV | Power Factor | 0.96118 | 0.96163 | 0.96944 | 0.96118 | 0.96163 | 0.96944 | 0.96119 | 0.96164 | 0.96944 | 0.96119 | 0.96164 | 0.96944 | 0.96119 | 0.96164 | 0.96944
SW-Chinchilla Western Network | F075S_St George Town 33 kV | Rating (A) | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164
SW-Chinchilla Western Network | F075S_St George Town 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Chinchilla Western Network | F075S_St George Town 33 kV | Min Voltage at Constrained Conductor | 33.0116 | 33.0105 | 32.6726 | 33.0102 | 33.0091 | 32.6722 | 33.0204 | 33.019 | 32.6751 | 33.0204 | 33.019 | 32.6751 | 33.0212 | 33.0198 | 32.6753
SW-Chinchilla Western Network | F075S_St George Town 33 kV | Contingency Outage | F077S_Main Camp 33 kV | F079S_St George Meatworks 33 kV | F081S_Noondoo 33 kV | F077S_Main Camp 33 kV | F079S_St George Meatworks 33 kV | F081S_Noondoo 33 kV | F077S_Main Camp 33 kV | F079S_St George Meatworks 33 kV | F081S_Noondoo 33 kV | F077S_Main Camp 33 kV | F079S_St George Meatworks 33 kV | F081S_Noondoo 33 kV | F077S_Main Camp 33 kV | F079S_St George Meatworks 33 kV | F081S_Noondoo 33 kV
SW-Chinchilla Western Network | F076C_Dulacca 33 kV | % of Rated A | 2.492% | 1.918% | 1.906% | 2.493% | 1.919% | 1.906% | 2.493% | 1.919% | 1.907% | 2.493% | 1.919% | 1.907% | 2.492% | 1.918% | 1.906%
SW-Chinchilla Western Network | F076C_Dulacca 33 kV | Limiting Line Name | TR_LINE 27218_1 | TR_LINE 27218_1 | TR_LINE 27218_1 | TR_LINE 27218_1 | TR_LINE 27218_1 | TR_LINE 27218_1 | TR_LINE 27218_1 | TR_LINE 27218_1 | TR_LINE 27218_1 | TR_LINE 27218_1 | TR_LINE 27218_1 | TR_LINE 27218_1 | TR_LINE 27218_1 | TR_LINE 27218_1 | TR_LINE 27218_1
SW-Chinchilla Western Network | F076C_Dulacca 33 kV | Loading (A) | 2.8908 | 3.0696 | 2.9737 | 2.8915 | 3.0702 | 2.9741 | 2.8925 | 3.0709 | 2.9745 | 2.8925 | 3.0709 | 2.9745 | 2.8908 | 3.0696 | 2.9737
SW-Chinchilla Western Network | F076C_Dulacca 33 kV | Loading (MVA) | 0.16695 | 0.17714 | 0.17335 | 0.16704 | 0.17723 | 0.17339 | 0.16715 | 0.17733 | 0.17344 | 0.16715 | 0.17733 | 0.17344 | 0.16695 | 0.17714 | 0.17335
SW-Chinchilla Western Network | F076C_Dulacca 33 kV | Loading (MW) | 0.08435 | 0.1098 | 0.065258 | 0.084351 | 0.10981 | 0.065258 | 0.084352 | 0.10981 | 0.065259 | 0.084352 | 0.10981 | 0.065259 | 0.08435 | 0.1098 | 0.065258
SW-Chinchilla Western Network | F076C_Dulacca 33 kV | Power Factor | 0.50524 | 0.61987 | 0.37646 | 0.50499 | 0.61957 | 0.37636 | 0.50466 | 0.6192 | 0.37626 | 0.50466 | 0.6192 | 0.37626 | 0.50525 | 0.61987 | 0.37646
SW-Chinchilla Western Network | F076C_Dulacca 33 kV | Rating (A) | 116 | 160 | 156 | 116 | 160 | 156 | 116 | 160 | 156 | 116 | 160 | 156 | 116 | 160 | 156
SW-Chinchilla Western Network | F076C_Dulacca 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Chinchilla Western Network | F076C_Dulacca 33 kV | Min Voltage at Constrained Conductor | 33.3429 | 33.318 | 33.6557 | 33.3519 | 33.3278 | 33.6602 | 33.3633 | 33.3399 | 33.6647 | 33.3633 | 33.3399 | 33.6647 | 33.3428 | 33.3179 | 33.6557
SW-Chinchilla Western Network | F076C_Dulacca 33 kV | Contingency Outage | F077C_Wandoan 33 kV | F077C_Wandoan 33 kV | F077C_Wandoan 33 kV | F077C_Wandoan 33 kV | F077C_Wandoan 33 kV | F077C_Wandoan 33 kV | F077C_Wandoan 33 kV | F077C_Wandoan 33 kV | F077C_Wandoan 33 kV | F077C_Wandoan 33 kV | F077C_Wandoan 33 kV | F077C_Wandoan 33 kV | F077C_Wandoan 33 kV | F077C_Wandoan 33 kV | F077C_Wandoan 33 kV
SW-Chinchilla Western Network | F077C_Wandoan 33 kV | % of Rated A | 34.4% | 20.7% | 10.23% | 34.39% | 20.69% | 10.17% | 34.37% | 20.68% | 10.16% | 34.37% | 20.68% | 10.16% | 34.4% | 20.7% | 10.23%
SW-Chinchilla Western Network | F077C_Wandoan 33 kV | Limiting Line Name | TR_LINE 23394_1 | TR_LINE 23394_1 | TR_LINE 155280_1 | TR_LINE 23394_1 | TR_LINE 23394_1 | TR_LINE 155280_1 | TR_LINE 23394_1 | TR_LINE 23394_1 | TR_LINE 155280_1 | TR_LINE 23394_1 | TR_LINE 23394_1 | TR_LINE 155280_1 | TR_LINE 23394_1 | TR_LINE 23394_1 | TR_LINE 155280_1
SW-Chinchilla Western Network | F077C_Wandoan 33 kV | Loading (A) | 59.513 | 57.5346 | 28.4513 | 59.4923 | 57.5129 | 28.2594 | 59.4666 | 57.4922 | 28.2561 | 59.4665 | 57.4922 | 28.2561 | 59.5132 | 57.5347 | 28.4513
SW-Chinchilla Western Network | F077C_Wandoan 33 kV | Loading (MVA) | 3.3245 | 3.218 | 1.6125 | 3.3244 | 3.2179 | 1.6119 | 3.3243 | 3.218 | 1.6119 | 3.3243 | 3.218 | 1.6119 | 3.3245 | 3.218 | 1.6125
SW-Chinchilla Western Network | F077C_Wandoan 33 kV | Loading (MW) | 3.2625 | 3.1684 | 1.6026 | 3.2625 | 3.1683 | 1.6024 | 3.2624 | 3.1683 | 1.6024 | 3.2624 | 3.1683 | 1.6024 | 3.2625 | 3.1684 | 1.6026
SW-Chinchilla Western Network | F077C_Wandoan 33 kV | Power Factor | 0.98135 | 0.98457 | 0.99176 | 0.98137 | 0.98458 | 0.99197 | 0.98139 | 0.98454 | 0.99196 | 0.98139 | 0.98454 | 0.99196 | 0.98135 | 0.98457 | 0.99176
SW-Chinchilla Western Network | F077C_Wandoan 33 kV | Rating (A) | 173 | 278 | 278 | 173 | 278 | 278 | 173 | 278 | 278 | 173 | 278 | 278 | 173 | 278 | 278
SW-Chinchilla Western Network | F077C_Wandoan 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Chinchilla Western Network | F077C_Wandoan 33 kV | Min Voltage at Constrained Conductor | 32.2504 | 32.2908 | 32.6885 | 32.2606 | 32.3019 | 32.9 | 32.2733 | 32.3148 | 32.9045 | 32.2733 | 32.3148 | 32.9045 | 32.2503 | 32.2908 | 32.6885
SW-Chinchilla Western Network | F077C_Wandoan 33 kV | Contingency Outage | F076C_Dulacca 33 kV | F076C_Dulacca 33 kV | F076C_Dulacca 33 kV | F076C_Dulacca 33 kV | F076C_Dulacca 33 kV | F076C_Dulacca 33 kV | F076C_Dulacca 33 kV | F076C_Dulacca 33 kV | F076C_Dulacca 33 kV | F076C_Dulacca 33 kV | F076C_Dulacca 33 kV | F076C_Dulacca 33 kV | F076C_Dulacca 33 kV | F076C_Dulacca 33 kV | F076C_Dulacca 33 kV
SW-Chinchilla Western Network | F077S_Main Camp 33 kV | % of Rated A | 62.34% | 47.69% | 34.62% | 62.34% | 47.69% | 34.63% | 62.32% | 47.67% | 34.62% | 62.32% | 47.67% | 34.62% | 62.32% | 47.67% | 34.62%
SW-Chinchilla Western Network | F077S_Main Camp 33 kV | Limiting Line Name | TR_CABLE 16560_1 | TR_CABLE 16560_1 | TR_CABLE 137_1 | TR_CABLE 16560_1 | TR_CABLE 16560_1 | TR_CABLE 137_1 | TR_CABLE 16560_1 | TR_CABLE 16560_1 | TR_CABLE 137_1 | TR_CABLE 16560_1 | TR_CABLE 16560_1 | TR_CABLE 137_1 | TR_CABLE 16560_1 | TR_CABLE 16560_1 | TR_CABLE 137_1
SW-Chinchilla Western Network | F077S_Main Camp 33 kV | Loading (A) | 62.3369 | 47.6878 | 34.6249 | 62.3401 | 47.6901 | 34.6253 | 62.3171 | 47.6734 | 34.6222 | 62.3171 | 47.6734 | 34.6222 | 62.3154 | 47.6722 | 34.622
SW-Chinchilla Western Network | F077S_Main Camp 33 kV | Loading (MVA) | 3.5539 | 2.7163 | 1.9404 | 3.554 | 2.7163 | 1.9404 | 3.5537 | 2.7161 | 1.9404 | 3.5537 | 2.7161 | 1.9404 | 3.5537 | 2.7161 | 1.9404
SW-Chinchilla Western Network | F077S_Main Camp 33 kV | Loading (MW) | 3.2339 | 2.5492 | 1.6252 | 3.234 | 2.5492 | 1.6252 | 3.2339 | 2.5491 | 1.6252 | 3.2339 | 2.5491 | 1.6252 | 3.2339 | 2.5491 | 1.6252
SW-Chinchilla Western Network | F077S_Main Camp 33 kV | Power Factor | 0.9099 | 0.93839 | 0.83748 | 0.9099 | 0.93839 | 0.83748 | 0.90995 | 0.93844 | 0.83748 | 0.90995 | 0.93844 | 0.83748 | 0.90996 | 0.93845 | 0.83748
SW-Chinchilla Western Network | F077S_Main Camp 33 kV | Rating (A) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
SW-Chinchilla Western Network | F077S_Main Camp 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Chinchilla Western Network | F077S_Main Camp 33 kV | Min Voltage at Constrained Conductor | 32.9156 | 32.8858 | 32.3556 | 32.9143 | 32.8845 | 32.3551 | 32.924 | 32.8939 | 32.358 | 32.924 | 32.8939 | 32.358 | 32.9248 | 32.8946 | 32.3582
SW-Chinchilla Western Network | F077S_Main Camp 33 kV | Contingency Outage | F075S_St George Town 33 kV | F075S_St George Town 33 kV | F081S_Noondoo 33 kV | F075S_St George Town 33 kV | F075S_St George Town 33 kV | F081S_Noondoo 33 kV | F075S_St George Town 33 kV | F075S_St George Town 33 kV | F081S_Noondoo 33 kV | F075S_St George Town 33 kV | F075S_St George Town 33 kV | F081S_Noondoo 33 kV | F075S_St George Town 33 kV | F075S_St George Town 33 kV | F081S_Noondoo 33 kV
SW-Chinchilla Western Network | F078S_Beardmore Dam 33 kV | % of Rated A | 4.271% | 7.193% | 2.948% | 4.272% | 7.193% | 2.948% | 4.27% | 7.191% | 2.948% | 4.27% | 7.191% | 2.948% | 4.27% | 7.191% | 2.948%
SW-Chinchilla Western Network | F078S_Beardmore Dam 33 kV | Limiting Line Name | TR_CABLE 4960_1 | TR_CABLE 4960_1 | TR_CABLE 4960_1 | TR_CABLE 4960_1 | TR_CABLE 4960_1 | TR_CABLE 4960_1 | TR_CABLE 4960_1 | TR_CABLE 4960_1 | TR_CABLE 4960_1 | TR_CABLE 4960_1 | TR_CABLE 4960_1 | TR_CABLE 4960_1 | TR_CABLE 4960_1 | TR_CABLE 4960_1 | TR_CABLE 4960_1
SW-Chinchilla Western Network | F078S_Beardmore Dam 33 kV | Loading (A) | 4.2714 | 7.1928 | 2.9484 | 4.2715 | 7.1931 | 2.9484 | 4.2703 | 7.1911 | 2.9482 | 4.2703 | 7.1911 | 2.9482 | 4.2702 | 7.1909 | 2.9482
SW-Chinchilla Western Network | F078S_Beardmore Dam 33 kV | Loading (MVA) | 0.24257 | 0.40756 | 0.16702 | 0.24256 | 0.40756 | 0.16702 | 0.24257 | 0.40757 | 0.16702 | 0.24257 | 0.40757 | 0.16702 | 0.24257 | 0.40757 | 0.16702
SW-Chinchilla Western Network | F078S_Beardmore Dam 33 kV | Loading (MW) | 0.21987 | 0.37252 | 0.14973 | 0.21987 | 0.37252 | 0.14973 | 0.21987 | 0.37252 | 0.14973 | 0.21987 | 0.37252 | 0.14973 | 0.21987 | 0.37252 | 0.14973
SW-Chinchilla Western Network | F078S_Beardmore Dam 33 kV | Power Factor | 0.90625 | 0.9139 | 0.89618 | 0.90626 | 0.9139 | 0.89619 | 0.90624 | 0.9139 | 0.89618 | 0.90624 | 0.9139 | 0.89618 | 0.90624 | 0.9139 | 0.89618
SW-Chinchilla Western Network | F078S_Beardmore Dam 33 kV | Rating (A) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
SW-Chinchilla Western Network | F078S_Beardmore Dam 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Chinchilla Western Network | F078S_Beardmore Dam 33 kV | Min Voltage at Constrained Conductor | 32.7869 | 32.7141 | 32.706 | 32.7855 | 32.7128 | 32.7055 | 32.7953 | 32.7223 | 32.7084 | 32.7953 | 32.7223 | 32.7084 | 32.7961 | 32.723 | 32.7086
SW-Chinchilla Western Network | F078S_Beardmore Dam 33 kV | Contingency Outage | F075S_St George Town 33 kV | F075S_St George Town 33 kV | F081S_Noondoo 33 kV | F075S_St George Town 33 kV | F075S_St George Town 33 kV | F081S_Noondoo 33 kV | F075S_St George Town 33 kV | F075S_St George Town 33 kV | F081S_Noondoo 33 kV | F075S_St George Town 33 kV | F075S_St George Town 33 kV | F081S_Noondoo 33 kV | F075S_St George Town 33 kV | F075S_St George Town 33 kV | F081S_Noondoo 33 kV
SW-Chinchilla Western Network | F079S_St George Meatworks 33 kV | % of Rated A | 44.51% | 45.34% | 35.34% | 44.51% | 45.35% | 35.34% | 44.5% | 45.33% | 35.34% | 44.5% | 45.33% | 35.34% | 44.5% | 45.33% | 35.34%
SW-Chinchilla Western Network | F079S_St George Meatworks 33 kV | Limiting Line Name | TR_CABLE 16561_1 | TR_CABLE 16561_1 | TR_CABLE 16561_1 | TR_CABLE 16561_1 | TR_CABLE 16561_1 | TR_CABLE 16561_1 | TR_CABLE 16561_1 | TR_CABLE 16561_1 | TR_CABLE 16561_1 | TR_CABLE 16561_1 | TR_CABLE 16561_1 | TR_CABLE 16561_1 | TR_CABLE 16561_1 | TR_CABLE 16561_1 | TR_CABLE 16561_1
SW-Chinchilla Western Network | F079S_St George Meatworks 33 kV | Loading (A) | 44.5098 | 45.3443 | 35.3435 | 44.5114 | 45.3459 | 35.3439 | 44.4997 | 45.3343 | 35.3416 | 44.4997 | 45.3343 | 35.3416 | 44.4988 | 45.3334 | 35.3414
SW-Chinchilla Western Network | F079S_St George Meatworks 33 kV | Loading (MVA) | 2.5376 | 2.5828 | 2.0076 | 2.5376 | 2.5828 | 2.0075 | 2.5377 | 2.5829 | 2.0076 | 2.5377 | 2.5829 | 2.0076 | 2.5377 | 2.5829 | 2.0076
SW-Chinchilla Western Network | F079S_St George Meatworks 33 kV | Loading (MW) | 2.5372 | 2.5827 | 1.9936 | 2.5372 | 2.5826 | 1.9936 | 2.5372 | 2.5827 | 1.9936 | 2.5372 | 2.5827 | 1.9936 | 2.5373 | 2.5827 | 1.9936
SW-Chinchilla Western Network | F079S_St George Meatworks 33 kV | Power Factor | 0.99984 | 0.99993 | 0.99303 | 0.99984 | 0.99993 | 0.99303 | 0.99983 | 0.99993 | 0.99302 | 0.99983 | 0.99993 | 0.99302 | 0.99983 | 0.99993 | 0.99302
SW-Chinchilla Western Network | F079S_St George Meatworks 33 kV | Rating (A) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
SW-Chinchilla Western Network | F079S_St George Meatworks 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Chinchilla Western Network | F079S_St George Meatworks 33 kV | Min Voltage at Constrained Conductor | 32.9159 | 32.8859 | 32.7941 | 32.9145 | 32.8846 | 32.7936 | 32.9243 | 32.894 | 32.7965 | 32.9243 | 32.894 | 32.7965 | 32.925 | 32.8947 | 32.7967
SW-Chinchilla Western Network | F079S_St George Meatworks 33 kV | Contingency Outage | F075S_St George Town 33 kV | F075S_St George Town 33 kV | F081S_Noondoo 33 kV | F075S_St George Town 33 kV | F075S_St George Town 33 kV | F081S_Noondoo 33 kV | F075S_St George Town 33 kV | F075S_St George Town 33 kV | F081S_Noondoo 33 kV | F075S_St George Town 33 kV | F075S_St George Town 33 kV | F081S_Noondoo 33 kV | F075S_St George Town 33 kV | F075S_St George Town 33 kV | F081S_Noondoo 33 kV
SW-Chinchilla Western Network | F081S_Noondoo 33 kV | % of Rated A | 41.31% | 43.2% | 38.57% | 41.32% | 43.2% | 38.57% | 41.3% | 43.18% | 38.56% | 41.3% | 43.18% | 38.56% | 41.3% | 43.18% | 38.56%
SW-Chinchilla Western Network | F081S_Noondoo 33 kV | Limiting Line Name | TR_CABLE 16562_1 | TR_CABLE 16562_1 | TR_CABLE 16562_1 | TR_CABLE 16562_1 | TR_CABLE 16562_1 | TR_CABLE 16562_1 | TR_CABLE 16562_1 | TR_CABLE 16562_1 | TR_CABLE 16562_1 | TR_CABLE 16562_1 | TR_CABLE 16562_1 | TR_CABLE 16562_1 | TR_CABLE 16562_1 | TR_CABLE 16562_1 | TR_CABLE 16562_1
SW-Chinchilla Western Network | F081S_Noondoo 33 kV | Loading (A) | 41.3132 | 43.1967 | 38.5673 | 41.3151 | 43.2049 | 38.5678 | 41.2971 | 43.1839 | 38.5629 | 41.2971 | 43.1839 | 38.5629 | 41.296 | 43.1829 | 38.5626
SW-Chinchilla Western Network | F081S_Noondoo 33 kV | Loading (MVA) | 2.3553 | 2.4605 | 2.1908 | 2.3554 | 2.4609 | 2.1908 | 2.355 | 2.4604 | 2.1907 | 2.355 | 2.4604 | 2.1907 | 2.355 | 2.4603 | 2.1907
SW-Chinchilla Western Network | F081S_Noondoo 33 kV | Loading (MW) | 2.3531 | 2.4575 | 2.1907 | 2.3531 | 2.4579 | 2.1907 | 2.3528 | 2.4575 | 2.1906 | 2.3528 | 2.4575 | 2.1906 | 2.3528 | 2.4575 | 2.1906
SW-Chinchilla Western Network | F081S_Noondoo 33 kV | Power Factor | 0.99894 | 0.9987 | 0.99995 | 0.99894 | 0.9987 | 0.99995 | 0.99895 | 0.99874 | 0.99995 | 0.99895 | 0.99874 | 0.99995 | 0.99895 | 0.99874 | 0.99995
SW-Chinchilla Western Network | F081S_Noondoo 33 kV | Rating (A) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
SW-Chinchilla Western Network | F081S_Noondoo 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Chinchilla Western Network | F081S_Noondoo 33 kV | Min Voltage at Constrained Conductor | 32.9158 | 32.8858 | 32.796 | 32.9145 | 32.8845 | 32.7956 | 32.9242 | 32.8939 | 32.7984 | 32.9242 | 32.8939 | 32.7984 | 32.9249 | 32.8946 | 32.7986
SW-Chinchilla Western Network | F081S_Noondoo 33 kV | Contingency Outage | F075S_St George Town 33 kV | F075S_St George Town 33 kV | F075S_St George Town 33 kV | F075S_St George Town 33 kV | F075S_St George Town 33 kV | F075S_St George Town 33 kV | F075S_St George Town 33 kV | F075S_St George Town 33 kV | F075S_St George Town 33 kV | F075S_St George Town 33 kV | F075S_St George Town 33 kV | F075S_St George Town 33 kV | F075S_St George Town 33 kV | F075S_St George Town 33 kV | F075S_St George Town 33 kV
SW-Chinchilla Western Network | F083C_Chinchilla 33 kV | % of Rated A | 62.72% | 51.01% | 25.44% | 61.13% | 49.72% | 24.81% | 60.58% | 49.33% | 24.6% | 61.08% | 49.84% | 24.8% | 61.09% | 49.85% | 24.8%
SW-Chinchilla Western Network | F083C_Chinchilla 33 kV | Limiting Line Name | TR_LINE 195206_1 | TR_LINE 195206_1 | TR_LINE 195206_1 | TR_LINE 195206_1 | TR_LINE 195206_1 | TR_LINE 195206_1 | TR_LINE 195206_1 | TR_LINE 195206_1 | TR_LINE 195206_1 | TR_LINE 195206_1 | TR_LINE 195206_1 | TR_LINE 195206_1 | TR_LINE 195206_1 | TR_LINE 195206_1 | TR_LINE 195206_1
SW-Chinchilla Western Network | F083C_Chinchilla 33 kV | Loading (A) | 209.4732 | 171.8895 | 74.2776 | 204.1625 | 167.5536 | 72.4441 | 202.3382 | 166.2413 | 71.8243 | 204.012 | 167.9629 | 72.4217 | 204.0386 | 167.9859 | 72.4259
SW-Chinchilla Western Network | F083C_Chinchilla 33 kV | Loading (MVA) | 12.0905 | 9.9594 | 4.2834 | 11.7901 | 9.7121 | 4.1783 | 11.6873 | 9.6375 | 4.1429 | 11.7821 | 9.7358 | 4.1771 | 11.7822 | 9.7358 | 4.1771
SW-Chinchilla Western Network | F083C_Chinchilla 33 kV | Loading (MW) | 11.6712 | 9.6456 | 4.1715 | 11.3853 | 9.4088 | 4.0697 | 11.2879 | 9.3376 | 4.0354 | 11.379 | 9.4319 | 4.0689 | 11.379 | 9.4319 | 4.0689
SW-Chinchilla Western Network | F083C_Chinchilla 33 kV | Power Factor | 0.96532 | 0.96849 | 0.9739 | 0.96567 | 0.96878 | 0.97401 | 0.96583 | 0.96888 | 0.97407 | 0.96578 | 0.96879 | 0.9741 | 0.96578 | 0.96879 | 0.9741
SW-Chinchilla Western Network | F083C_Chinchilla 33 kV | Rating (A) | 334 | 337 | 292 | 334 | 337 | 292 | 334 | 337 | 292 | 334 | 337 | 292 | 334 | 337 | 292
SW-Chinchilla Western Network | F083C_Chinchilla 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Chinchilla Western Network | F083C_Chinchilla 33 kV | Min Voltage at Constrained Conductor | 33.3053 | 33.4369 | 33.2883 | 33.3229 | 33.4508 | 33.2936 | 33.3303 | 33.4562 | 33.2964 | 33.325 | 33.4508 | 33.2947 | 33.321 | 33.4462 | 33.2928
SW-Chinchilla Western Network | F083C_Chinchilla 33 kV | Contingency Outage | F071C RYWUNG | F071C RYWUNG | F071C RYWUNG | F071C RYWUNG | F071C RYWUNG | F071C RYWUNG | F071C RYWUNG | F071C RYWUNG | F071C RYWUNG | F071C RYWUNG | F071C RYWUNG | F071C RYWUNG | F071C RYWUNG | F071C RYWUNG | F071C RYWUNG
SW-Chinchilla Western Network | F083S_Dirrabandi Town 33 kV | % of Rated A | 11.78% | 10.76% | 7.675% | 11.78% | 10.76% | 7.675% | 11.78% | 10.76% | 7.675% | 11.78% | 10.76% | 7.675% | 11.78% | 10.76% | 7.675%
SW-Chinchilla Western Network | F083S_Dirrabandi Town 33 kV | Limiting Line Name | TR_LINE 44480_1 | TR_LINE 44480_1 | TR_LINE 44480_1 | TR_LINE 44480_1 | TR_LINE 44480_1 | TR_LINE 44480_1 | TR_LINE 44480_1 | TR_LINE 44480_1 | TR_LINE 44480_1 | TR_LINE 44480_1 | TR_LINE 44480_1 | TR_LINE 44480_1 | TR_LINE 44480_1 | TR_LINE 44480_1 | TR_LINE 44480_1
SW-Chinchilla Western Network | F083S_Dirrabandi Town 33 kV | Loading (A) | 8.6007 | 9.7884 | 6.6007 | 8.601 | 9.7889 | 6.6007 | 8.5987 | 9.789 | 6.6006 | 8.5987 | 9.789 | 6.6006 | 8.5985 | 9.7888 | 6.6006
SW-Chinchilla Western Network | F083S_Dirrabandi Town 33 kV | Loading (MVA) | 0.47641 | 0.54094 | 0.36593 | 0.4764 | 0.54094 | 0.36593 | 0.47644 | 0.54114 | 0.36596 | 0.47644 | 0.54114 | 0.36596 | 0.47644 | 0.54114 | 0.36596
SW-Chinchilla Western Network | F083S_Dirrabandi Town 33 kV | Loading (MW) | 0.47115 | 0.53594 | 0.32877 | 0.47115 | 0.53594 | 0.32877 | 0.47116 | 0.53595 | 0.32878 | 0.47116 | 0.53595 | 0.32878 | 0.47116 | 0.53595 | 0.32878
SW-Chinchilla Western Network | F083S_Dirrabandi Town 33 kV | Power Factor | 0.98898 | 0.99075 | 0.89846 | 0.98898 | 0.99076 | 0.89847 | 0.98892 | 0.99042 | 0.8984 | 0.98892 | 0.99042 | 0.8984 | 0.98891 | 0.99041 | 0.8984
SW-Chinchilla Western Network | F083S_Dirrabandi Town 33 kV | Rating (A) | 73 | 91 | 86 | 73 | 91 | 86 | 73 | 91 | 86 | 73 | 91 | 86 | 73 | 91 | 86
SW-Chinchilla Western Network | F083S_Dirrabandi Town 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Chinchilla Western Network | F083S_Dirrabandi Town 33 kV | Min Voltage at Constrained Conductor | 31.9635 | 31.8867 | 31.9971 | 31.9621 | 31.885 | 31.9966 | 31.9727 | 31.8964 | 31.9997 | 31.9727 | 31.8964 | 31.9997 | 31.9735 | 31.8972 | 31.9999
SW-Chinchilla Western Network | F083S_Dirrabandi Town 33 kV | Contingency Outage | F075S_St George Town 33 kV | F075S_St George Town 33 kV | F075S_St George Town 33 kV | F075S_St George Town 33 kV | F075S_St George Town 33 kV | F075S_St George Town 33 kV | F075S_St George Town 33 kV | F075S_St George Town 33 kV | F075S_St George Town 33 kV | F075S_St George Town 33 kV | F075S_St George Town 33 kV | F075S_St George Town 33 kV | F075S_St George Town 33 kV | F075S_St George Town 33 kV | F075S_St George Town 33 kV
SW-Chinchilla Western Network | F106R_Roma East 33 kV | % of Rated A | 69.7% | 67.68% | 31.13% | 68.91% | 66.91% | 30.8% | 79.78% | 77.49% | 35.43% | 79.78% | 77.49% | 35.43% | 80.57% | 78.26% | 35.76%
SW-Chinchilla Western Network | F106R_Roma East 33 kV | Limiting Line Name | TR_LINE 44567_2 | TR_LINE 44567_2 | TR_LINE 44567_2 | TR_LINE 44567_2 | TR_LINE 44567_2 | TR_LINE 44567_2 | TR_LINE 44567_2 | TR_LINE 44567_2 | TR_LINE 44567_2 | TR_LINE 44567_2 | TR_LINE 44567_2 | TR_LINE 44567_2 | TR_LINE 44567_2 | TR_LINE 44567_2 | TR_LINE 44567_2
SW-Chinchilla Western Network | F106R_Roma East 33 kV | Loading (A) | 178.4355 | 172.5786 | 68.1777 | 176.4147 | 170.6301 | 67.45 | 204.229 | 197.6004 | 77.5877 | 204.229 | 197.6004 | 77.5877 | 206.2506 | 199.5509 | 78.3144
SW-Chinchilla Western Network | F106R_Roma East 33 kV | Loading (MVA) | 9.8176 | 9.5099 | 3.7996 | 9.7131 | 9.4087 | 3.7599 | 11.1734 | 10.829 | 4.3166 | 11.1734 | 10.829 | 4.3166 | 11.2785 | 10.9309 | 4.3564
SW-Chinchilla Western Network | F106R_Roma East 33 kV | Loading (MW) | 9.4288 | 9.1389 | 3.6835 | 9.3303 | 9.0434 | 3.6452 | 10.7089 | 10.3811 | 4.1814 | 10.7089 | 10.3811 | 4.1814 | 10.8075 | 10.4768 | 4.2197
SW-Chinchilla Western Network | F106R_Roma East 33 kV | Power Factor | 0.9604 | 0.96099 | 0.96943 | 0.96059 | 0.96117 | 0.96948 | 0.95843 | 0.95864 | 0.96867 | 0.95843 | 0.95864 | 0.96867 | 0.95824 | 0.95845 | 0.96861
SW-Chinchilla Western Network | F106R_Roma East 33 kV | Rating (A) | 256 | 255 | 219 | 256 | 255 | 219 | 256 | 255 | 219 | 256 | 255 | 219 | 256 | 255 | 219
SW-Chinchilla Western Network | F106R_Roma East 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Chinchilla Western Network | F106R_Roma East 33 kV | Min Voltage at Constrained Conductor | 31.7363 | 31.786 | 32.1663 | 31.7586 | 31.8074 | 32.1735 | 31.5527 | 31.6073 | 32.1093 | 31.5527 | 31.6073 | 32.1093 | 31.5371 | 31.5925 | 32.1047
SW-Chinchilla Western Network | F106R_Roma East 33 kV | Contingency Outage | 7374_Roma Power Station 132 kV | 7374_Roma Power Station 132 kV | F217R_St George 66 kV | 7374_Roma Power Station 132 kV | 7374_Roma Power Station 132 kV | F217R_St George 66 kV | 7374_Roma Power Station 132 kV | 7374_Roma Power Station 132 kV | F217R_St George 66 kV | 7374_Roma Power Station 132 kV | 7374_Roma Power Station 132 kV | F217R_St George 66 kV | 7374_Roma Power Station 132 kV | 7374_Roma Power Station 132 kV | F217R_St George 66 kV
SW-Chinchilla Western Network | F127R_Roma West 33 kV | % of Rated A | 68.53% | 51.42% | 22.6% | 66.91% | 50.21% | 22.09% | 67.18% | 50.41% | 22.12% | 67.18% | 50.41% | 22.12% | 67.21% | 50.42% | 22.12%
SW-Chinchilla Western Network | F127R_Roma West 33 kV | Limiting Line Name | TR_LINE 27140_1 | TR_LINE 27140_1 | TR_LINE 27140_1 | TR_LINE 27140_1 | TR_LINE 27140_1 | TR_LINE 27140_1 | TR_LINE 27140_1 | TR_LINE 27140_1 | TR_LINE 27140_1 | TR_LINE 27140_1 | TR_LINE 27140_1 | TR_LINE 27140_1 | TR_LINE 27140_1 | TR_LINE 27140_1 | TR_LINE 27140_1
SW-Chinchilla Western Network | F127R_Roma West 33 kV | Loading (A) | 79.4899 | 82.2718 | 35.2622 | 77.6186 | 80.3343 | 34.4614 | 77.9339 | 80.6512 | 34.4998 | 77.9339 | 80.6512 | 34.4998 | 77.9585 | 80.6749 | 34.5025
SW-Chinchilla Western Network | F127R_Roma West 33 kV | Loading (MVA) | 4.3602 | 4.5144 | 1.9608 | 4.2617 | 4.4123 | 1.917 | 4.2622 | 4.4128 | 1.917 | 4.2622 | 4.4128 | 1.917 | 4.2623 | 4.4129 | 1.917
SW-Chinchilla Western Network | F127R_Roma West 33 kV | Loading (MW) | 4.2199 | 4.3673 | 1.909 | 4.1257 | 4.2698 | 1.8665 | 4.1258 | 4.2699 | 1.8665 | 4.1258 | 4.2699 | 1.8665 | 4.1258 | 4.27 | 1.8665
SW-Chinchilla Western Network | F127R_Roma West 33 kV | Power Factor | 0.96782 | 0.96743 | 0.97355 | 0.96809 | 0.96771 | 0.97366 | 0.968 | 0.96763 | 0.97365 | 0.968 | 0.96763 | 0.97365 | 0.968 | 0.96762 | 0.97365
SW-Chinchilla Western Network | F127R_Roma West 33 kV | Rating (A) | 116 | 160 | 156 | 116 | 160 | 156 | 116 | 160 | 156 | 116 | 160 | 156 | 116 | 160 | 156
SW-Chinchilla Western Network | F127R_Roma West 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Chinchilla Western Network | F127R_Roma West 33 kV | Min Voltage at Constrained Conductor | 31.6684 | 31.6791 | 32.1045 | 31.6988 | 31.7094 | 32.1155 | 31.5745 | 31.5887 | 32.0803 | 31.5745 | 31.5887 | 32.0803 | 31.5649 | 31.5797 | 32.0778
SW-Chinchilla Western Network | F127R_Roma West 33 kV | Contingency Outage | 7374_Roma Power Station 132 kV | 7374_Roma Power Station 132 kV | F217R_St George 66 kV | 7374_Roma Power Station 132 kV | 7374_Roma Power Station 132 kV | F217R_St George 66 kV | 7374_Roma Power Station 132 kV | 7374_Roma Power Station 132 kV | F217R_St George 66 kV | 7374_Roma Power Station 132 kV | 7374_Roma Power Station 132 kV | F217R_St George 66 kV | 7374_Roma Power Station 132 kV | 7374_Roma Power Station 132 kV | F217R_St George 66 kV
SW-Chinchilla Western Network | F187R_Mungallala 33 kV | % of Rated A | 0.0007618% | 0.0007593% | 0.0009045% | 0.000762% | 0.0007595% | 0.0009046% | 0.0007636% | 0.0007622% | 0.0009103% | 0.0007636% | 0.0007622% | 0.0009103% | 0.0007633% | 0.000762% | 0.0009103%
SW-Chinchilla Western Network | F187R_Mungallala 33 kV | Limiting Line Name | TR_LINE 12064483_1 | TR_LINE 12064483_1 | TR_LINE 12064483_1 | TR_LINE 12064483_1 | TR_LINE 12064483_1 | TR_LINE 12064483_1 | TR_LINE 12064483_1 | TR_LINE 12064483_1 | TR_LINE 12064483_1 | TR_LINE 12064483_1 | TR_LINE 12064483_1 | TR_LINE 12064483_1 | TR_LINE 12064483_1 | TR_LINE 12064483_1 | TR_LINE 12064483_1
SW-Chinchilla Western Network | F187R_Mungallala 33 kV | Loading (A) | 0.0019501 | 0.0019361 | 0.0019809 | 0.0019508 | 0.0019367 | 0.0019811 | 0.0019548 | 0.0019437 | 0.0019937 | 0.0019548 | 0.0019437 | 0.0019937 | 0.0019542 | 0.001943 | 0.0019937
SW-Chinchilla Western Network | F187R_Mungallala 33 kV | Loading (MVA) | 0.00010674 | 0.00010521 | 0.00011014 | 0.00010681 | 0.00010528 | 0.00011016 | 0.00010725 | 0.00010603 | 0.00011156 | 0.00010725 | 0.00010603 | 0.00011156 | 0.00010718 | 0.00010596 | 0.00011156
SW-Chinchilla Western Network | F187R_Mungallala 33 kV | Loading (MW) | 1.0086e-08 | 9.9456e-09 | 1.0405e-08 | 1.0092e-08 | 9.9445e-09 | 1.0408e-08 | 1.0135e-08 | 1.0029e-08 | 1.0546e-08 | 1.0138e-08 | 1.002e-08 | 1.0545e-08 | 1.0133e-08 | 1.0011e-08 | 1.0547e-08
SW-Chinchilla Western Network | F187R_Mungallala 33 kV | Power Factor | 9.4492e-05 | 9.4524e-05 | 9.4469e-05 | 9.449e-05 | 9.4454e-05 | 9.4472e-05 | 9.4497e-05 | 9.4585e-05 | 9.4534e-05 | 9.4517e-05 | 9.4496e-05 | 9.4522e-05 | 9.4517e-05 | 9.4468e-05 | 9.4539e-05
SW-Chinchilla Western Network | F187R_Mungallala 33 kV | Rating (A) | 256 | 255 | 219 | 256 | 255 | 219 | 256 | 255 | 219 | 256 | 255 | 219 | 256 | 255 | 219
SW-Chinchilla Western Network | F187R_Mungallala 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Chinchilla Western Network | F187R_Mungallala 33 kV | Min Voltage at Constrained Conductor | 31.601 | 31.3741 | 32.1001 | 31.6112 | 31.3839 | 32.1028 | 31.6768 | 31.496 | 32.3063 | 31.6768 | 31.496 | 32.3063 | 31.6662 | 31.4856 | 32.3063
SW-Chinchilla Western Network | F187R_Mungallala 33 kV | Contingency Outage | F127R_Roma West 33 kV | F127R_Roma West 33 kV | F106R_Roma East 33 kV | F127R_Roma West 33 kV | F127R_Roma West 33 kV | F106R_Roma East 33 kV | F127R_Roma West 33 kV | F127R_Roma West 33 kV | F106R_Roma East 33 kV | F127R_Roma West 33 kV | F127R_Roma West 33 kV | F106R_Roma East 33 kV | F127R_Roma West 33 kV | F127R_Roma West 33 kV | F106R_Roma East 33 kV
SW-Chinchilla Western Network | F217R_St George 66 kV | % of Rated A | 33.19% | 30.87% | 24.17% | 33.16% | 30.84% | 24.17% | 33.36% | 31.02% | 23.99% | 33.36% | 31.02% | 23.99% | 33.37% | 31.03% | 23.99%
SW-Chinchilla Western Network | F217R_St George 66 kV | Limiting Line Name | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1
SW-Chinchilla Western Network | F217R_St George 66 kV | Loading (A) | 148.3572 | 140.1355 | 95.7243 | 148.2406 | 140.0291 | 95.7087 | 149.0973 | 140.8341 | 94.9895 | 149.0973 | 140.8341 | 94.9895 | 149.1629 | 140.8939 | 94.9895
SW-Chinchilla Western Network | F217R_St George 66 kV | Loading (MVA) | 16.6495 | 15.7376 | 10.7092 | 16.6412 | 15.7301 | 10.7079 | 16.7014 | 15.7877 | 10.6486 | 16.7014 | 15.7877 | 10.6486 | 16.706 | 15.792 | 10.6486
SW-Chinchilla Western Network | F217R_St George 66 kV | Loading (MW) | 15.293 | 14.3615 | 9.1266 | 15.2892 | 14.3586 | 9.1263 | 15.3157 | 14.3817 | 9.113 | 15.3157 | 14.3817 | 9.113 | 15.3177 | 14.3834 | 9.113
SW-Chinchilla Western Network | F217R_St George 66 kV | Power Factor | 0.91849 | 0.91252 | 0.85222 | 0.91872 | 0.91278 | 0.85229 | 0.91699 | 0.91091 | 0.85579 | 0.91699 | 0.91091 | 0.85579 | 0.91686 | 0.91077 | 0.85579
SW-Chinchilla Western Network | F217R_St George 66 kV | Rating (A) | 447 | 454 | 396 | 447 | 454 | 396 | 447 | 454 | 396 | 447 | 454 | 396 | 447 | 454 | 396
SW-Chinchilla Western Network | F217R_St George 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Chinchilla Western Network | F217R_St George 66 kV | Min Voltage at Constrained Conductor | 64.793 | 64.8379 | 64.5911 | 64.8118 | 64.856 | 64.5938 | 64.6724 | 64.7215 | 64.7225 | 64.6724 | 64.7215 | 64.7225 | 64.6618 | 64.7115 | 64.7225
SW-Chinchilla Western Network | F217R_St George 66 kV | Contingency Outage | 7374_Roma Power Station 132 kV | 7374_Roma Power Station 132 kV | F127R_Roma West 33 kV | 7374_Roma Power Station 132 kV | 7374_Roma Power Station 132 kV | F127R_Roma West 33 kV | 7374_Roma Power Station 132 kV | 7374_Roma Power Station 132 kV | F106R_Roma East 33 kV | 7374_Roma Power Station 132 kV | 7374_Roma Power Station 132 kV | F106R_Roma East 33 kV | 7374_Roma Power Station 132 kV | 7374_Roma Power Station 132 kV | F106R_Roma East 33 kV
SW-Toowoomba Dalby Warwick | 3153_Cecil Plains Road 33 kV | % of Rated A | 59.73% | 56.31% | 46.93% | 59.66% | 56.29% | 46.93% | 60.43% | 56.28% | 46.92% | 60.43% | 56.28% | 46.93% | 60.4% | 56.33% | 46.94%
SW-Toowoomba Dalby Warwick | 3153_Cecil Plains Road 33 kV | Limiting Line Name | TR_LINE 183124_2 | TR_CABLE 5205_1 | TR_CABLE 5205_1 | TR_LINE 183124_2 | TR_CABLE 5205_1 | TR_CABLE 5205_1 | TR_LINE 183124_2 | TR_CABLE 5205_1 | TR_CABLE 5205_1 | TR_LINE 183124_2 | TR_CABLE 5205_1 | TR_CABLE 5205_1 | TR_LINE 183124_2 | TR_CABLE 5205_1 | TR_CABLE 5205_1
SW-Toowoomba Dalby Warwick | 3153_Cecil Plains Road 33 kV | Loading (A) | 55.5451 | 56.3126 | 46.9309 | 55.4824 | 56.288 | 46.9254 | 56.2014 | 56.2764 | 46.9228 | 56.2009 | 56.2844 | 46.9258 | 56.1725 | 56.3257 | 46.9398
SW-Toowoomba Dalby Warwick | 3153_Cecil Plains Road 33 kV | Loading (MVA) | 3.2273 | 3.2419 | 2.7259 | 3.227 | 3.2418 | 2.7259 | 3.2304 | 3.2417 | 2.7259 | 3.2304 | 3.2418 | 2.7259 | 3.2303 | 3.242 | 2.7259
SW-Toowoomba Dalby Warwick | 3153_Cecil Plains Road 33 kV | Loading (MW) | 3.0562 | 3.0802 | 2.6077 | 3.0562 | 3.0802 | 2.6077 | 3.0568 | 3.0802 | 2.6077 | 3.0568 | 3.0802 | 2.6077 | 3.0568 | 3.0802 | 2.6077
SW-Toowoomba Dalby Warwick | 3153_Cecil Plains Road 33 kV | Power Factor | 0.94698 | 0.94994 | 0.95645 | 0.94705 | 0.94997 | 0.95646 | 0.94625 | 0.94998 | 0.95646 | 0.94625 | 0.94997 | 0.95646 | 0.94628 | 0.94993 | 0.95644
SW-Toowoomba Dalby Warwick | 3153_Cecil Plains Road 33 kV | Rating (A) | 93 | 100 | 100 | 93 | 100 | 100 | 93 | 100 | 100 | 93 | 100 | 100 | 93 | 100 | 100
SW-Toowoomba Dalby Warwick | 3153_Cecil Plains Road 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Toowoomba Dalby Warwick | 3153_Cecil Plains Road 33 kV | Min Voltage at Constrained Conductor | 33.5434 | 33.238 | 33.5346 | 33.5782 | 33.2514 | 33.5382 | 33.1836 | 33.2577 | 33.5399 | 33.1838 | 33.2534 | 33.5379 | 33.1992 | 33.2309 | 33.5287
SW-Toowoomba Dalby Warwick | 3153_Cecil Plains Road 33 kV | Contingency Outage | F5545_7245 Tangkam-Dalby 110 kV | 7314_Dalby East 110 kV | F097D_Jandowae 33 kV | F5545_7245 Tangkam-Dalby 110 kV | 7314_Dalby East 110 kV | F097D_Jandowae 33 kV | F5540_7244 Tangkam-Dalby 110 kV | 7314_Dalby East 110 kV | F097D_Jandowae 33 kV | F5540_7244 Tangkam-Dalby 110 kV | 7314_Dalby East 110 kV | F097D_Jandowae 33 kV | F4132_Shirley Road 33 kV | 7314_Dalby East 110 kV | F097D_Jandowae 33 kV
SW-Toowoomba Dalby Warwick | 3154_Central Dalby 1 33 kV | % of Rated A | 50.72% | 45.63% | 21.33% | 50.14% | 45.15% | 21.08% | 49.88% | 44.92% | 20.99% | 49.7% | 44.79% | 20.92% | 50.8% | 45.18% | 21.08%
SW-Toowoomba Dalby Warwick | 3154_Central Dalby 1 33 kV | Limiting Line Name | TR_CABLE 4402_1 | TR_CABLE 4402_1 | TR_LINE 121841_1 | TR_CABLE 4402_1 | TR_CABLE 4402_1 | TR_LINE 121841_1 | TR_CABLE 4402_1 | TR_CABLE 4402_1 | TR_LINE 121841_1 | TR_CABLE 4402_1 | TR_CABLE 4402_1 | TR_LINE 121841_1 | TR_CABLE 4402_1 | TR_CABLE 4402_1 | TR_LINE 121841_1
SW-Toowoomba Dalby Warwick | 3154_Central Dalby 1 33 kV | Loading (A) | 228.2486 | 205.3182 | 87.4701 | 225.6351 | 203.1915 | 86.4143 | 224.4773 | 202.1274 | 86.0694 | 223.6437 | 201.5483 | 85.7575 | 228.5954 | 203.3303 | 86.4412
SW-Toowoomba Dalby Warwick | 3154_Central Dalby 1 33 kV | Loading (MVA) | 13.0214 | 11.6228 | 5.1097 | 12.8831 | 11.5096 | 5.0495 | 12.8217 | 11.4529 | 5.0298 | 12.7735 | 11.4191 | 5.0114 | 12.8852 | 11.5101 | 5.0496
SW-Toowoomba Dalby Warwick | 3154_Central Dalby 1 33 kV | Loading (MW) | 12.531 | 11.2122 | 4.999 | 12.402 | 11.1064 | 4.942 | 12.3448 | 11.0532 | 4.9229 | 12.2985 | 11.0207 | 4.905 | 12.4024 | 11.1065 | 4.942
SW-Toowoomba Dalby Warwick | 3154_Central Dalby 1 33 kV | Power Factor | 0.96212 | 0.96446 | 0.97835 | 0.96243 | 0.96475 | 0.9787 | 0.96258 | 0.96489 | 0.97874 | 0.96259 | 0.96489 | 0.97877 | 0.96231 | 0.96472 | 0.97869
SW-Toowoomba Dalby Warwick | 3154_Central Dalby 1 33 kV | Rating (A) | 450 | 450 | 410 | 450 | 450 | 410 | 450 | 450 | 410 | 450 | 450 | 410 | 450 | 450 | 410
SW-Toowoomba Dalby Warwick | 3154_Central Dalby 1 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Toowoomba Dalby Warwick | 3154_Central Dalby 1 33 kV | Min Voltage at Constrained Conductor | 32.9374 | 32.683 | 33.7261 | 32.965 | 32.7036 | 33.7365 | 32.977 | 32.7136 | 33.7392 | 32.9756 | 32.711 | 33.7381 | 32.5433 | 32.6825 | 33.7265
SW-Toowoomba Dalby Warwick | 3154_Central Dalby 1 33 kV | Contingency Outage | F008D_Central Dalby 2 33 kV | F008D_Central Dalby 2 33 kV | F008D_Central Dalby 2 33 kV | F008D_Central Dalby 2 33 kV | F008D_Central Dalby 2 33 kV | F008D_Central Dalby 2 33 kV | F008D_Central Dalby 2 33 kV | F008D_Central Dalby 2 33 kV | F008D_Central Dalby 2 33 kV | F008D_Central Dalby 2 33 kV | F008D_Central Dalby 2 33 kV | F008D_Central Dalby 2 33 kV | F008D_Central Dalby 2 33 kV | F008D_Central Dalby 2 33 kV | F008D_Central Dalby 2 33 kV
SW-Toowoomba Dalby Warwick | 3178_Wilkie Creek 33 kV | % of Rated A | 4.164% | 4.15% | 4.19% | 4.165% | 4.146% | 4.19% | 4.166% | 4.146% | 4.191% | 4.165% | 4.145% | 4.19% | 4.177% | 4.148% | 4.189%
SW-Toowoomba Dalby Warwick | 3178_Wilkie Creek 33 kV | Limiting Line Name | TR_CABLE 3771_1 | TR_CABLE 3771_1 | TR_CABLE 3771_1 | TR_CABLE 3771_1 | TR_CABLE 3771_1 | TR_CABLE 3771_1 | TR_CABLE 3771_1 | TR_CABLE 3771_1 | TR_CABLE 3771_1 | TR_CABLE 3771_1 | TR_CABLE 3771_1 | TR_CABLE 3771_1 | TR_CABLE 3771_1 | TR_CABLE 3771_1 | TR_CABLE 3771_1
SW-Toowoomba Dalby Warwick | 3178_Wilkie Creek 33 kV | Loading (A) | 3.8724 | 3.8593 | 3.8965 | 3.8739 | 3.8554 | 3.8971 | 3.8746 | 3.8559 | 3.8972 | 3.8739 | 3.8553 | 3.897 | 3.8847 | 3.858 | 3.896
SW-Toowoomba Dalby Warwick | 3178_Wilkie Creek 33 kV | Loading (MVA) | 0.22341 | 0.22344 | 0.22542 | 0.22358 | 0.223 | 0.22549 | 0.22366 | 0.22306 | 0.2255 | 0.22358 | 0.22298 | 0.22547 | 0.22481 | 0.22329 | 0.22536
SW-Toowoomba Dalby Warwick | 3178_Wilkie Creek 33 kV | Loading (MW) | 0.0097114 | 0.015375 | 0.0071233 | 0.0097126 | 0.015372 | 0.0071237 | 0.0097131 | 0.015372 | 0.0071238 | 0.0097126 | 0.015372 | 0.0071236 | 0.0097212 | 0.015374 | 0.0071228
SW-Toowoomba Dalby Warwick | 3178_Wilkie Creek 33 kV | Power Factor | 0.043469 | 0.068812 | 0.0316 | 0.043441 | 0.068934 | 0.031593 | 0.043429 | 0.068917 | 0.031591 | 0.043441 | 0.068938 | 0.031594 | 0.043241 | 0.068853 | 0.031606
SW-Toowoomba Dalby Warwick | 3178_Wilkie Creek 33 kV | Rating (A) | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93
SW-Toowoomba Dalby Warwick | 3178_Wilkie Creek 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Toowoomba Dalby Warwick | 3178_Wilkie Creek 33 kV | Min Voltage at Constrained Conductor | 33.3092 | 33.4261 | 33.401 | 33.3217 | 33.3938 | 33.4057 | 33.3272 | 33.3982 | 33.407 | 33.3216 | 33.3928 | 33.4045 | 33.4125 | 33.4152 | 33.3963
SW-Toowoomba Dalby Warwick | 3178_Wilkie Creek 33 kV | Contingency Outage | 3153_Cecil Plains Road 33 kV | 3153_Cecil Plains Road 33 kV | 3153_Cecil Plains Road 33 kV | 3153_Cecil Plains Road 33 kV | F099D_Warra 33 kV | 3153_Cecil Plains Road 33 kV | 3153_Cecil Plains Road 33 kV | F099D_Warra 33 kV | 3153_Cecil Plains Road 33 kV | 3153_Cecil Plains Road 33 kV | F099D_Warra 33 kV | 3153_Cecil Plains Road 33 kV | 3153_Cecil Plains Road 33 kV | 3153_Cecil Plains Road 33 kV | 3153_Cecil Plains Road 33 kV
SW-Toowoomba Dalby Warwick | 3282_Killarney 33kV | % of Rated A | 24.67% | 20.38% | 11.08% | 24.68% | 20.42% | 11.08% | 24.66% | 20.4% | 11.08% | 24.7% | 20.43% | 11.08% | 24.85% | 20.51% | 11.1%
SW-Toowoomba Dalby Warwick | 3282_Killarney 33kV | Limiting Line Name | TR_LINE 23129_2 | TR_LINE 23129_2 | TR_LINE 23129_2 | TR_LINE 23129_2 | TR_LINE 23129_2 | TR_LINE 23129_2 | TR_LINE 23129_2 | TR_LINE 23129_2 | TR_LINE 23129_2 | TR_LINE 23129_2 | TR_LINE 23129_2 | TR_LINE 23129_2 | TR_LINE 23129_2 | TR_LINE 23129_2 | TR_LINE 23129_2
SW-Toowoomba Dalby Warwick | 3282_Killarney 33kV | Loading (A) | 28.621 | 32.6157 | 17.2839 | 28.6345 | 32.678 | 17.2891 | 28.6108 | 32.6465 | 17.2846 | 28.6484 | 32.6905 | 17.2905 | 28.8244 | 32.809 | 17.3092
SW-Toowoomba Dalby Warwick | 3282_Killarney 33kV | Loading (MVA) | 1.5914 | 1.8007 | 1.0085 | 1.5915 | 1.8007 | 1.0085 | 1.5914 | 1.8007 | 1.0085 | 1.5915 | 1.8007 | 1.0085 | 1.5914 | 1.8008 | 1.0086
SW-Toowoomba Dalby Warwick | 3282_Killarney 33kV | Loading (MW) | 1.5455 | 1.7477 | 0.98103 | 1.5455 | 1.7477 | 0.98103 | 1.5455 | 1.7477 | 0.98103 | 1.5456 | 1.7477 | 0.98103 | 1.5455 | 1.7478 | 0.98103
SW-Toowoomba Dalby Warwick | 3282_Killarney 33kV | Power Factor | 0.97091 | 0.9704 | 0.97245 | 0.9709 | 0.97038 | 0.97244 | 0.97091 | 0.97039 | 0.97244 | 0.9709 | 0.97038 | 0.97244 | 0.97094 | 0.97034 | 0.97244
SW-Toowoomba Dalby Warwick | 3282_Killarney 33kV | Rating (A) | 116 | 160 | 156 | 116 | 160 | 156 | 116 | 160 | 156 | 116 | 160 | 156 | 116 | 160 | 156
SW-Toowoomba Dalby Warwick | 3282_Killarney 33kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Toowoomba Dalby Warwick | 3282_Killarney 33kV | Min Voltage at Constrained Conductor | 32.0958 | 31.8633 | 33.6894 | 32.0809 | 31.8033 | 33.6792 | 32.1071 | 31.8337 | 33.688 | 32.0654 | 31.7913 | 33.6767 | 31.8682 | 31.6779 | 33.6404
SW-Toowoomba Dalby Warwick | 3282_Killarney 33kV | Contingency Outage | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV
SW-Toowoomba Dalby Warwick | 3283_Allora 33kV | % of Rated A | 47% | 55.36% | 24.18% | 47.02% | 55.48% | 24.19% | 46.98% | 55.42% | 24.18% | 47.05% | 55.51% | 24.19% | 48.43% | 57.02% | 24.73%
SW-Toowoomba Dalby Warwick | 3283_Allora 33kV | Limiting Line Name | TR_LINE ALLORA-pole2134509_a | TR_LINE 23956_1 | TR_LINE 23956_1 | TR_LINE ALLORA-pole2134509_a | TR_LINE 23956_1 | TR_LINE 23956_1 | TR_LINE ALLORA-pole2134509_a | TR_LINE 23956_1 | TR_LINE 23956_1 | TR_LINE ALLORA-pole2134509_a | TR_LINE 23956_1 | TR_LINE 23956_1 | TR_LINE ALLORA-pole2134509_a | TR_LINE 23956_1 | TR_LINE 23956_1
SW-Toowoomba Dalby Warwick | 3283_Allora 33kV | Loading (A) | 77.5472 | 93.5639 | 34.3357 | 77.5874 | 93.7671 | 34.3465 | 77.5169 | 93.6643 | 34.3371 | 77.6289 | 93.8079 | 34.3492 | 79.9126 | 96.3639 | 35.1216
SW-Toowoomba Dalby Warwick | 3283_Allora 33kV | Loading (MVA) | 4.1622 | 4.939 | 1.9836 | 4.1623 | 4.9395 | 1.9837 | 4.1621 | 4.9393 | 1.9836 | 4.1623 | 4.9396 | 1.9837 | 4.2495 | 5.0441 | 2.0248
SW-Toowoomba Dalby Warwick | 3283_Allora 33kV | Loading (MW) | 3.957 | 4.6982 | 1.9076 | 3.957 | 4.6984 | 1.9076 | 3.9569 | 4.6983 | 1.9076 | 3.957 | 4.6984 | 1.9076 | 4.0385 | 4.7955 | 1.9467
SW-Toowoomba Dalby Warwick | 3283_Allora 33kV | Power Factor | 0.95069 | 0.95125 | 0.96162 | 0.95068 | 0.95119 | 0.96162 | 0.9507 | 0.95122 | 0.96162 | 0.95067 | 0.95118 | 0.96162 | 0.95035 | 0.95072 | 0.96137
SW-Toowoomba Dalby Warwick | 3283_Allora 33kV | Rating (A) | 165 | 169 | 142 | 165 | 169 | 142 | 165 | 169 | 142 | 165 | 169 | 142 | 165 | 169 | 142
SW-Toowoomba Dalby Warwick | 3283_Allora 33kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Toowoomba Dalby Warwick | 3283_Allora 33kV | Min Voltage at Constrained Conductor | 30.9871 | 30.4546 | 33.3484 | 30.9716 | 30.3913 | 33.3382 | 30.9988 | 30.4233 | 33.3471 | 30.9555 | 30.3786 | 33.3356 | 30.7007 | 30.1977 | 33.2786
SW-Toowoomba Dalby Warwick | 3283_Allora 33kV | Contingency Outage | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV
SW-Toowoomba Dalby Warwick | 3900_Peranga 33 kV | % of Rated A | 20.62% | 24.53% | 18.31% | 20.62% | 24.53% | 18.31% | 19.07% | 22.73% | 16.9% | 20.63% | 24.53% | 18.31% | 20.58% | 24.54% | 18.31%
SW-Toowoomba Dalby Warwick | 3900_Peranga 33 kV | Limiting Line Name | TR_CABLE 9120_1 | TR_CABLE 9120_1 | TR_CABLE 9120_1 | TR_CABLE 9120_1 | TR_CABLE 9120_1 | TR_CABLE 9120_1 | TR_CABLE 9120_1 | TR_CABLE 9120_1 | TR_CABLE 9120_1 | TR_CABLE 9120_1 | TR_CABLE 9120_1 | TR_CABLE 9120_1 | TR_CABLE 9120_1 | TR_CABLE 9120_1 | TR_CABLE 9120_1
SW-Toowoomba Dalby Warwick | 3900_Peranga 33 kV | Loading (A) | 20.6225 | 24.5292 | 18.306 | 20.6211 | 24.5288 | 18.3055 | 19.0672 | 22.725 | 16.8976 | 20.6264 | 24.5329 | 18.307 | 20.5821 | 24.5416 | 18.31
SW-Toowoomba Dalby Warwick | 3900_Peranga 33 kV | Loading (MVA) | 1.2092 | 1.4391 | 1.0732 | 1.2092 | 1.4391 | 1.0732 | 1.1181 | 1.3333 | 0.99063 | 1.2092 | 1.4391 | 1.0732 | 1.2089 | 1.4392 | 1.0732
SW-Toowoomba Dalby Warwick | 3900_Peranga 33 kV | Loading (MW) | 1.1783 | 1.3918 | 1.0513 | 1.1783 | 1.3918 | 1.0513 | 1.0736 | 1.2679 | 0.95786 | 1.1783 | 1.3919 | 1.0513 | 1.1782 | 1.3919 | 1.0513
SW-Toowoomba Dalby Warwick | 3900_Peranga 33 kV | Power Factor | 0.97429 | 0.96703 | 0.97939 | 0.9743 | 0.96703 | 0.97939 | 0.9601 | 0.95084 | 0.96674 | 0.97428 | 0.96701 | 0.97938 | 0.97445 | 0.96698 | 0.97937
SW-Toowoomba Dalby Warwick | 3900_Peranga 33 kV | Rating (A) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
SW-Toowoomba Dalby Warwick | 3900_Peranga 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Toowoomba Dalby Warwick | 3900_Peranga 33 kV | Min Voltage at Constrained Conductor | 33.8532 | 33.8729 | 33.8474 | 33.8553 | 33.8734 | 33.8482 | 33.855 | 33.8729 | 33.8472 | 33.8476 | 33.8683 | 33.8457 | 33.9122 | 33.8578 | 33.8407
SW-Toowoomba Dalby Warwick | 3900_Peranga 33 kV | Contingency Outage | F5545_7245 Tangkam-Dalby 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | 7314_Dalby East 110 kV | F5545_7245 Tangkam-Dalby 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | 7314_Dalby East 110 kV | F5540_7244 Tangkam-Dalby 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | 7314_Dalby East 110 kV | 7234_Middle Ridge-Torrington 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | 7314_Dalby East 110 kV | F4132_Shirley Road 33 kV | 7234_Middle Ridge-Torrington 110 kV | 7314_Dalby East 110 kV
SW-Toowoomba Dalby Warwick | 7233_Middle Ridge-Torrington 110 kV | % of Rated A | 46.75% | 38.19% | 23.77% | 46.5% | 38% | 23.66% | 46.36% | 37.89% | 23.58% | 50.09% | 40.42% | 25.17% | 53.91% | 43.37% | 27.03%
SW-Toowoomba Dalby Warwick | 7233_Middle Ridge-Torrington 110 kV | Limiting Line Name | TR_LINE 27024_2 | TR_LINE 27024_2 | TR_LINE 27024_2 | TR_LINE 27024_2 | TR_LINE 27024_2 | TR_LINE 27024_2 | TR_LINE 27024_2 | TR_LINE 27024_2 | TR_LINE 27024_2 | TR_LINE 27024_2 | TR_LINE 27024_2 | TR_LINE 27024_2 | TR_LINE 27024_2 | TR_LINE 27024_2 | TR_LINE 27024_2
SW-Toowoomba Dalby Warwick | 7233_Middle Ridge-Torrington 110 kV | Loading (A) | 410.5011 | 368.1581 | 203.0238 | 408.2743 | 366.2887 | 202.0278 | 407.057 | 365.212 | 201.4119 | 439.7491 | 389.6012 | 214.9249 | 473.3392 | 418.0614 | 230.8614
SW-Toowoomba Dalby Warwick | 7233_Middle Ridge-Torrington 110 kV | Loading (MVA) | 80.9823 | 72.8176 | 40.6299 | 80.5509 | 72.4515 | 40.4321 | 80.3199 | 72.2426 | 40.31 | 86.59 | 76.9469 | 42.9835 | 93.6093 | 82.3543 | 46.1163
SW-Toowoomba Dalby Warwick | 7233_Middle Ridge-Torrington 110 kV | Loading (MW) | 74.9945 | 68.2522 | 39.5963 | 74.6202 | 67.947 | 39.4146 | 74.4299 | 67.7647 | 39.3017 | 79.1945 | 71.496 | 41.6875 | 82.9424 | 74.4624 | 44.1513
SW-Toowoomba Dalby Warwick | 7233_Middle Ridge-Torrington 110 kV | Power Factor | 0.92606 | 0.9373 | 0.97456 | 0.92637 | 0.93783 | 0.97484 | 0.92667 | 0.93802 | 0.97499 | 0.91459 | 0.92916 | 0.96985 | 0.88605 | 0.90417 | 0.95739
SW-Toowoomba Dalby Warwick | 7233_Middle Ridge-Torrington 110 kV | Rating (A) | 878 | 964 | 854 | 878 | 964 | 854 | 878 | 964 | 854 | 878 | 964 | 854 | 878 | 964 | 854
SW-Toowoomba Dalby Warwick | 7233_Middle Ridge-Torrington 110 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Toowoomba Dalby Warwick | 7233_Middle Ridge-Torrington 110 kV | Min Voltage at Constrained Conductor | 112.8156 | 113.2929 | 115.2655 | 112.8355 | 113.3066 | 115.2732 | 112.8536 | 113.3172 | 115.2789 | 112.4597 | 113.027 | 115.1472 | 112.7316 | 112.5478 | 114.943
SW-Toowoomba Dalby Warwick | 7233_Middle Ridge-Torrington 110 kV | Contingency Outage | 7234_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV
SW-Toowoomba Dalby Warwick | 7234_Middle Ridge-Torrington 110 kV | % of Rated A | 46.65% | 38.14% | 23.76% | 46.36% | 37.94% | 23.64% | 46.23% | 37.83% | 23.57% | 49.9% | 40.31% | 25.15% | 54.08% | 43.32% | 27.06%
SW-Toowoomba Dalby Warwick | 7234_Middle Ridge-Torrington 110 kV | Limiting Line Name | TR_LINE 27022_2 | TR_LINE 27022_2 | TR_LINE 27022_2 | TR_LINE 27022_2 | TR_LINE 27022_2 | TR_LINE 27022_2 | TR_LINE 27022_2 | TR_LINE 27022_2 | TR_LINE 27022_2 | TR_LINE 27022_2 | TR_LINE 27022_2 | TR_LINE 27022_2 | TR_LINE 27022_2 | TR_LINE 27022_2 | TR_LINE 27022_2
SW-Toowoomba Dalby Warwick | 7234_Middle Ridge-Torrington 110 kV | Loading (A) | 409.5539 | 367.6407 | 202.8882 | 407.0666 | 365.781 | 201.8837 | 405.888 | 364.6692 | 201.2693 | 438.0876 | 388.6225 | 214.7389 | 474.795 | 417.6028 | 231.0656
SW-Toowoomba Dalby Warwick | 7234_Middle Ridge-Torrington 110 kV | Loading (MVA) | 80.811 | 72.7246 | 40.6055 | 80.3314 | 72.3602 | 40.4061 | 80.1074 | 72.1449 | 40.2843 | 86.2879 | 76.7683 | 42.9496 | 93.9126 | 82.2831 | 46.1613
SW-Toowoomba Dalby Warwick | 7234_Middle Ridge-Torrington 110 kV | Loading (MW) | 74.9964 | 68.2628 | 39.5981 | 74.6093 | 67.9577 | 39.4161 | 74.4198 | 67.7742 | 39.3032 | 79.1739 | 71.4834 | 41.6881 | 83.4257 | 74.6374 | 44.2499
SW-Toowoomba Dalby Warwick | 7234_Middle Ridge-Torrington 110 kV | Power Factor | 0.92805 | 0.93865 | 0.97519 | 0.92877 | 0.93916 | 0.9755 | 0.929 | 0.93942 | 0.97564 | 0.91755 | 0.93116 | 0.97063 | 0.88833 | 0.90708 | 0.95859
SW-Toowoomba Dalby Warwick | 7234_Middle Ridge-Torrington 110 kV | Rating (A) | 878 | 964 | 854 | 878 | 964 | 854 | 878 | 964 | 854 | 878 | 964 | 854 | 878 | 964 | 854
SW-Toowoomba Dalby Warwick | 7234_Middle Ridge-Torrington 110 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Toowoomba Dalby Warwick | 7234_Middle Ridge-Torrington 110 kV | Min Voltage at Constrained Conductor | 112.8524 | 113.3174 | 115.2753 | 112.8793 | 113.3308 | 115.2834 | 112.8963 | 113.3425 | 115.2889 | 112.5145 | 113.0632 | 115.1588 | 112.7587 | 112.5901 | 114.9558
SW-Toowoomba Dalby Warwick | 7234_Middle Ridge-Torrington 110 kV | Contingency Outage | 7233_Middle Ridge-Torrington 110 kV | 7233_Middle Ridge-Torrington 110 kV | 7233_Middle Ridge-Torrington 110 kV | 7233_Middle Ridge-Torrington 110 kV | 7233_Middle Ridge-Torrington 110 kV | 7233_Middle Ridge-Torrington 110 kV | 7233_Middle Ridge-Torrington 110 kV | 7233_Middle Ridge-Torrington 110 kV | 7233_Middle Ridge-Torrington 110 kV | 7233_Middle Ridge-Torrington 110 kV | 7233_Middle Ridge-Torrington 110 kV | 7233_Middle Ridge-Torrington 110 kV | 7233_Middle Ridge-Torrington 110 kV | 7233_Middle Ridge-Torrington 110 kV | 7233_Middle Ridge-Torrington 110 kV
SW-Toowoomba Dalby Warwick | 728_Middle Ridge-South Toowoomba 110 kV | % of Rated A | 42.2% | 37.33% | 23.2% | 41.96% | 37.26% | 23.16% | 41.86% | 37.27% | 23.14% | 41.86% | 37.32% | 23.32% | 41.85% | 37.6% | 23.4%
SW-Toowoomba Dalby Warwick | 728_Middle Ridge-South Toowoomba 110 kV | Limiting Line Name | TR_LINE 33947_1 | TR_LINE 33947_1 | TR_LINE 33947_1 | TR_LINE 33947_1 | TR_LINE 33947_1 | TR_LINE 33947_1 | TR_LINE 33947_1 | TR_LINE 33947_1 | TR_LINE 33947_1 | TR_LINE 33947_1 | TR_LINE 33947_1 | TR_LINE 33947_1 | TR_LINE 33947_1 | TR_LINE 33947_1 | TR_LINE 33947_1
SW-Toowoomba Dalby Warwick | 728_Middle Ridge-South Toowoomba 110 kV | Loading (A) | 434.2553 | 396.4317 | 221.1105 | 431.7666 | 395.7302 | 220.6804 | 430.6898 | 395.7651 | 220.5232 | 430.7869 | 396.3311 | 222.2422 | 430.6606 | 399.3195 | 223.0033
SW-Toowoomba Dalby Warwick | 728_Middle Ridge-South Toowoomba 110 kV | Loading (MVA) | 86.6814 | 79.2101 | 44.4888 | 86.1886 | 79.0691 | 44.4026 | 85.9795 | 79.0777 | 44.3715 | 85.9446 | 79.1484 | 44.7108 | 86.4758 | 79.6875 | 44.8483
SW-Toowoomba Dalby Warwick | 728_Middle Ridge-South Toowoomba 110 kV | Loading (MW) | 86.1556 | 78.2467 | 35.703 | 85.6331 | 78.0951 | 35.5565 | 85.4071 | 78.114 | 35.5053 | 85.3803 | 78.1951 | 35.5133 | 85.9623 | 78.7915 | 35.7524
SW-Toowoomba Dalby Warwick | 728_Middle Ridge-South Toowoomba 110 kV | Power Factor | 0.9936 | 0.98742 | 0.80219 | 0.99321 | 0.98727 | 0.80045 | 0.99299 | 0.9874 | 0.79986 | 0.99309 | 0.98754 | 0.79397 | 0.99374 | 0.98835 | 0.79686
SW-Toowoomba Dalby Warwick | 728_Middle Ridge-South Toowoomba 110 kV | Rating (A) | 1029 | 1062 | 953 | 1029 | 1062 | 953 | 1029 | 1062 | 953 | 1029 | 1062 | 953 | 1029 | 1062 | 953
SW-Toowoomba Dalby Warwick | 728_Middle Ridge-South Toowoomba 110 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Toowoomba Dalby Warwick | 728_Middle Ridge-South Toowoomba 110 kV | Min Voltage at Constrained Conductor | 115.2184 | 115.3531 | 116.1637 | 115.2253 | 115.3522 | 116.1647 | 115.2339 | 115.3543 | 116.1663 | 115.1609 | 115.2921 | 116.1469 | 115.9045 | 115.2067 | 116.1062
SW-Toowoomba Dalby Warwick | 728_Middle Ridge-South Toowoomba 110 kV | Contingency Outage | 730_Middle Ridge-South Toowoomba 110 kV | 730_Middle Ridge-South Toowoomba 110 kV | 730_Middle Ridge-South Toowoomba 110 kV | 730_Middle Ridge-South Toowoomba 110 kV | 730_Middle Ridge-South Toowoomba 110 kV | 730_Middle Ridge-South Toowoomba 110 kV | 730_Middle Ridge-South Toowoomba 110 kV | 730_Middle Ridge-South Toowoomba 110 kV | 730_Middle Ridge-South Toowoomba 110 kV | 730_Middle Ridge-South Toowoomba 110 kV | 730_Middle Ridge-South Toowoomba 110 kV | 730_Middle Ridge-South Toowoomba 110 kV | 730_Middle Ridge-South Toowoomba 110 kV | 730_Middle Ridge-South Toowoomba 110 kV | 730_Middle Ridge-South Toowoomba 110 kV
SW-Toowoomba Dalby Warwick | 730_Middle Ridge-South Toowoomba 110 kV | % of Rated A | 42.2% | 37.33% | 23.2% | 41.96% | 37.26% | 23.16% | 41.86% | 37.27% | 23.14% | 41.87% | 37.32% | 23.32% | 41.85% | 37.6% | 23.4%
SW-Toowoomba Dalby Warwick | 730_Middle Ridge-South Toowoomba 110 kV | Limiting Line Name | TR_LINE 33960_1 | TR_LINE 33960_1 | TR_LINE 33960_1 | TR_LINE 33960_1 | TR_LINE 33960_1 | TR_LINE 33960_1 | TR_LINE 33960_1 | TR_LINE 33960_1 | TR_LINE 33960_1 | TR_LINE 33960_1 | TR_LINE 33960_1 | TR_LINE 33960_1 | TR_LINE 33960_1 | TR_LINE 33960_1 | TR_LINE 33960_1
SW-Toowoomba Dalby Warwick | 730_Middle Ridge-South Toowoomba 110 kV | Loading (A) | 434.2643 | 396.4437 | 221.1152 | 431.7756 | 395.7421 | 220.685 | 430.699 | 395.7769 | 220.5279 | 430.7961 | 396.3431 | 222.2469 | 430.6698 | 399.3315 | 223.0081
SW-Toowoomba Dalby Warwick | 730_Middle Ridge-South Toowoomba 110 kV | Loading (MVA) | 86.6833 | 79.2127 | 44.4897 | 86.1906 | 79.0716 | 44.4035 | 85.9814 | 79.0802 | 44.3725 | 85.9466 | 79.1509 | 44.7118 | 86.4778 | 79.6901 | 44.8493
SW-Toowoomba Dalby Warwick | 730_Middle Ridge-South Toowoomba 110 kV | Loading (MW) | 86.1565 | 78.2477 | 35.7031 | 85.634 | 78.096 | 35.5566 | 85.408 | 78.1149 | 35.5054 | 85.3812 | 78.196 | 35.5135 | 85.9632 | 78.7924 | 35.7525
SW-Toowoomba Dalby Warwick | 730_Middle Ridge-South Toowoomba 110 kV | Power Factor | 0.99358 | 0.9874 | 0.80218 | 0.9932 | 0.98725 | 0.80044 | 0.99298 | 0.98738 | 0.79985 | 0.99307 | 0.98752 | 0.79395 | 0.99372 | 0.98833 | 0.79684
SW-Toowoomba Dalby Warwick | 730_Middle Ridge-South Toowoomba 110 kV | Rating (A) | 1029 | 1062 | 953 | 1029 | 1062 | 953 | 1029 | 1062 | 953 | 1029 | 1062 | 953 | 1029 | 1062 | 953
SW-Toowoomba Dalby Warwick | 730_Middle Ridge-South Toowoomba 110 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Toowoomba Dalby Warwick | 730_Middle Ridge-South Toowoomba 110 kV | Min Voltage at Constrained Conductor | 115.2185 | 115.3534 | 116.1637 | 115.2255 | 115.3524 | 116.1647 | 115.2341 | 115.3545 | 116.1663 | 115.1611 | 115.2923 | 116.147 | 115.9046 | 115.207 | 116.1062
SW-Toowoomba Dalby Warwick | 730_Middle Ridge-South Toowoomba 110 kV | Contingency Outage | 728_Middle Ridge-South Toowoomba 110 kV | 728_Middle Ridge-South Toowoomba 110 kV | 728_Middle Ridge-South Toowoomba 110 kV | 728_Middle Ridge-South Toowoomba 110 kV | 728_Middle Ridge-South Toowoomba 110 kV | 728_Middle Ridge-South Toowoomba 110 kV | 728_Middle Ridge-South Toowoomba 110 kV | 728_Middle Ridge-South Toowoomba 110 kV | 728_Middle Ridge-South Toowoomba 110 kV | 728_Middle Ridge-South Toowoomba 110 kV | 728_Middle Ridge-South Toowoomba 110 kV | 728_Middle Ridge-South Toowoomba 110 kV | 728_Middle Ridge-South Toowoomba 110 kV | 728_Middle Ridge-South Toowoomba 110 kV | 728_Middle Ridge-South Toowoomba 110 kV
SW-Toowoomba Dalby Warwick | 7314_Dalby East 110 kV | % of Rated A | 4.527% | 4.291% | 4.874% | 4.528% | 4.292% | 4.875% | 4.529% | 4.293% | 4.875% | 4.528% | 4.292% | 4.875% | 4.535% | 4.29% | 4.873%
SW-Toowoomba Dalby Warwick | 7314_Dalby East 110 kV | Limiting Line Name | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1
SW-Toowoomba Dalby Warwick | 7314_Dalby East 110 kV | Loading (A) | 12.5385 | 12.6589 | 12.8186 | 12.5435 | 12.6624 | 12.8206 | 12.5457 | 12.6641 | 12.8211 | 12.5435 | 12.662 | 12.8201 | 12.5632 | 12.6546 | 12.8167
SW-Toowoomba Dalby Warwick | 7314_Dalby East 110 kV | Loading (MVA) | 2.435 | 2.4641 | 2.5304 | 2.4369 | 2.4655 | 2.5312 | 2.4377 | 2.4661 | 2.5314 | 2.4369 | 2.4653 | 2.531 | 2.4443 | 2.4625 | 2.5297
SW-Toowoomba Dalby Warwick | 7314_Dalby East 110 kV | Loading (MW) | 0.82575 | 0.87481 | 0.54725 | 0.82576 | 0.87481 | 0.54725 | 0.82576 | 0.87481 | 0.54726 | 0.82576 | 0.87481 | 0.54725 | 0.82577 | 0.8748 | 0.54725
SW-Toowoomba Dalby Warwick | 7314_Dalby East 110 kV | Power Factor | 0.33911 | 0.35502 | 0.21627 | 0.33885 | 0.35482 | 0.21621 | 0.33874 | 0.35473 | 0.21619 | 0.33886 | 0.35485 | 0.21622 | 0.33783 | 0.35525 | 0.21633
SW-Toowoomba Dalby Warwick | 7314_Dalby East 110 kV | Rating (A) | 277 | 295 | 263 | 277 | 295 | 263 | 277 | 295 | 263 | 277 | 295 | 263 | 277 | 295 | 263
SW-Toowoomba Dalby Warwick | 7314_Dalby East 110 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Toowoomba Dalby Warwick | 7314_Dalby East 110 kV | Min Voltage at Constrained Conductor | 112.1236 | 112.3848 | 113.9702 | 112.1655 | 112.4151 | 113.9863 | 112.184 | 112.4296 | 113.9905 | 112.165 | 112.4115 | 113.9822 | 112.3315 | 112.3484 | 113.9544
SW-Toowoomba Dalby Warwick | 7314_Dalby East 110 kV | Contingency Outage | 3153_Cecil Plains Road 33 kV | F099D_Warra 33 kV | 3153_Cecil Plains Road 33 kV | 3153_Cecil Plains Road 33 kV | F099D_Warra 33 kV | 3153_Cecil Plains Road 33 kV | 3153_Cecil Plains Road 33 kV | F099D_Warra 33 kV | 3153_Cecil Plains Road 33 kV | 3153_Cecil Plains Road 33 kV | F099D_Warra 33 kV | 3153_Cecil Plains Road 33 kV | F099D_Warra 33 kV | F099D_Warra 33 kV | 3153_Cecil Plains Road 33 kV
SW-Toowoomba Dalby Warwick | 7448_South Toowoomba-TWCE 110 kV | % of Rated A | 15.99% | 10.52% | 7.968% | 15.68% | 10.39% | 7.929% | 15.44% | 10.29% | 7.901% | 15.29% | 10.23% | 7.881% | 15.13% | 10.2% | 7.87%
SW-Toowoomba Dalby Warwick | 7448_South Toowoomba-TWCE 110 kV | Limiting Line Name | TR_CABLE 14006_1 | TR_CABLE 13760_1 | TR_CABLE 13760_1 | TR_CABLE 14006_1 | TR_CABLE 13760_1 | TR_CABLE 13760_1 | TR_CABLE 14006_1 | TR_CABLE 13760_1 | TR_CABLE 13760_1 | TR_CABLE 14006_1 | TR_CABLE 13760_1 | TR_CABLE 13760_1 | TR_CABLE 14006_1 | TR_CABLE 13760_1 | TR_CABLE 13760_1
SW-Toowoomba Dalby Warwick | 7448_South Toowoomba-TWCE 110 kV | Loading (A) | 67.1746 | 44.1796 | 33.4674 | 65.8396 | 43.6265 | 33.303 | 64.8363 | 43.2149 | 33.1825 | 64.2312 | 42.949 | 33.1017 | 63.5649 | 42.8215 | 33.0561
SW-Toowoomba Dalby Warwick | 7448_South Toowoomba-TWCE 110 kV | Loading (MVA) | 13.3964 | 8.8231 | 6.7557 | 13.131 | 8.7121 | 6.7227 | 12.932 | 8.6302 | 6.6984 | 12.8001 | 8.5723 | 6.6816 | 12.738 | 8.5404 | 6.6699
SW-Toowoomba Dalby Warwick | 7448_South Toowoomba-TWCE 110 kV | Loading (MW) | 12.8286 | 7.863 | 4.2875 | 12.5807 | 7.7132 | 4.207 | 12.3948 | 7.6009 | 4.1467 | 12.2709 | 7.5259 | 4.1064 | 12.2095 | 7.4883 | 4.0862
SW-Toowoomba Dalby Warwick | 7448_South Toowoomba-TWCE 110 kV | Power Factor | 0.95566 | 0.89118 | 0.63465 | 0.9561 | 0.88534 | 0.6258 | 0.95643 | 0.88073 | 0.61905 | 0.9566 | 0.87793 | 0.61459 | 0.95643 | 0.8768 | 0.61263
SW-Toowoomba Dalby Warwick | 7448_South Toowoomba-TWCE 110 kV | Rating (A) | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420
SW-Toowoomba Dalby Warwick | 7448_South Toowoomba-TWCE 110 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Toowoomba Dalby Warwick | 7448_South Toowoomba-TWCE 110 kV | Min Voltage at Constrained Conductor | 115.1388 | 115.3022 | 116.5437 | 115.1459 | 115.2947 | 116.5458 | 115.1564 | 115.2995 | 116.5477 | 115.0555 | 115.2351 | 116.538 | 115.6972 | 115.148 | 116.4958
SW-Toowoomba Dalby Warwick | 7448_South Toowoomba-TWCE 110 kV | Contingency Outage | 7234_Middle Ridge-Torrington 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | 730_Middle Ridge-South Toowoomba 110 kV | 7234_Middle Ridge-Torrington 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | 730_Middle Ridge-South Toowoomba 110 kV | 7234_Middle Ridge-Torrington 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | 730_Middle Ridge-South Toowoomba 110 kV | 7234_Middle Ridge-Torrington 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | 730_Middle Ridge-South Toowoomba 110 kV | F4132_Shirley Road 33 kV | 7234_Middle Ridge-Torrington 110 kV | 730_Middle Ridge-South Toowoomba 110 kV
SW-Toowoomba Dalby Warwick | 7449 South Toowoomba-TWCE 110 kV | % of Rated A | 9.397% | 7.794% | 7.288% | 9.301% | 7.759% | 7.283% | 9.23% | 7.734% | 7.279% | 9.183% | 7.717% | 7.276% | 9.157% | 7.708% | 7.272%
SW-Toowoomba Dalby Warwick | 7449 South Toowoomba-TWCE 110 kV | Limiting Line Name | TR_CABLE 13761_1 | TR_CABLE 13761_1 | TR_CABLE 13761_1 | TR_CABLE 13761_1 | TR_CABLE 13761_1 | TR_CABLE 13761_1 | TR_CABLE 13761_1 | TR_CABLE 13761_1 | TR_CABLE 13761_1 | TR_CABLE 13761_1 | TR_CABLE 13761_1 | TR_CABLE 13761_1 | TR_CABLE 13761_1 | TR_CABLE 13761_1 | TR_CABLE 13761_1
SW-Toowoomba Dalby Warwick | 7449 South Toowoomba-TWCE 110 kV | Loading (A) | 39.4682 | 32.733 | 30.6099 | 39.0645 | 32.589 | 30.5871 | 38.7659 | 32.484 | 30.5711 | 38.5691 | 32.4122 | 30.558 | 38.4599 | 32.3746 | 30.5425
SW-Toowoomba Dalby Warwick | 7449 South Toowoomba-TWCE 110 kV | Loading (MVA) | 7.8724 | 6.5562 | 6.1789 | 7.7923 | 6.5272 | 6.1744 | 7.7334 | 6.5063 | 6.1713 | 7.6874 | 6.491 | 6.1681 | 7.754 | 6.4823 | 6.1628
SW-Toowoomba Dalby Warwick | 7449 South Toowoomba-TWCE 110 kV | Loading (MW) | 6.5177 | 3.991 | 2.2058 | 6.394 | 3.9163 | 2.1656 | 6.3013 | 3.8602 | 2.1354 | 6.2392 | 3.8228 | 2.1153 | 6.2111 | 3.804 | 2.1051
SW-Toowoomba Dalby Warwick | 7449 South Toowoomba-TWCE 110 kV | Power Factor | 0.82793 | 0.60874 | 0.35699 | 0.82056 | 0.59999 | 0.35073 | 0.81481 | 0.5933 | 0.34603 | 0.81162 | 0.58894 | 0.34294 | 0.80102 | 0.58684 | 0.34159
SW-Toowoomba Dalby Warwick | 7449 South Toowoomba-TWCE 110 kV | Rating (A) | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420 | 420
SW-Toowoomba Dalby Warwick | 7449 South Toowoomba-TWCE 110 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Toowoomba Dalby Warwick | 7449 South Toowoomba-TWCE 110 kV | Min Voltage at Constrained Conductor | 115.1585 | 115.6397 | 116.5437 | 115.1651 | 115.6372 | 116.5458 | 115.1753 | 115.6391 | 116.5477 | 115.0742 | 115.6219 | 116.538 | 116.4007 | 115.6009 | 116.4958
SW-Toowoomba Dalby Warwick | 7449 South Toowoomba-TWCE 110 kV | Contingency Outage | 7234_Middle Ridge-Torrington 110 kV | F4132_Shirley Road 33 kV | 730_Middle Ridge-South Toowoomba 110 kV | 7234_Middle Ridge-Torrington 110 kV | F4132_Shirley Road 33 kV | 730_Middle Ridge-South Toowoomba 110 kV | 7234_Middle Ridge-Torrington 110 kV | F4132_Shirley Road 33 kV | 730_Middle Ridge-South Toowoomba 110 kV | 7234_Middle Ridge-Torrington 110 kV | F3820_Boundary Road 33 kV | 730_Middle Ridge-South Toowoomba 110 kV | F3820_Boundary Road 33 kV | F3820_Boundary Road 33 kV | 730_Middle Ridge-South Toowoomba 110 kV
SW-Toowoomba Dalby Warwick | 790_Warwick-Stanthorpe 110 kV | % of Rated A | 42.64% | 36.02% | 20.55% | 43.92% | 37.29% | 21% | 43.9% | 37.26% | 20.99% | 43.95% | 37.3% | 21% | 44.31% | 38.04% | 21.23%
SW-Toowoomba Dalby Warwick | 790_Warwick-Stanthorpe 110 kV | Limiting Line Name | TR_LINE 198182_1 | TR_LINE 198182_1 | TR_LINE 198182_1 | TR_LINE 198182_1 | TR_LINE 198182_1 | TR_LINE 198182_1 | TR_LINE 198182_1 | TR_LINE 198182_1 | TR_LINE 198182_1 | TR_LINE 198182_1 | TR_LINE 198182_1 | TR_LINE 198182_1 | TR_LINE 198182_1 | TR_LINE 198182_1 | TR_LINE 198182_1
SW-Toowoomba Dalby Warwick | 790_Warwick-Stanthorpe 110 kV | Loading (A) | 54.1517 | 64.8379 | 35.9553 | 55.7846 | 67.1182 | 36.7417 | 55.7471 | 67.0612 | 36.738 | 55.8107 | 67.1457 | 36.7431 | 56.2785 | 68.4705 | 37.1556
SW-Toowoomba Dalby Warwick | 790_Warwick-Stanthorpe 110 kV | Loading (MVA) | 10.0292 | 11.7783 | 7.1868 | 10.3168 | 12.1565 | 7.3381 | 10.3172 | 12.1563 | 7.3391 | 10.3165 | 12.1566 | 7.3378 | 10.4646 | 12.3475 | 7.4108
SW-Toowoomba Dalby Warwick | 790_Warwick-Stanthorpe 110 kV | Loading (MW) | 9.9798 | 11.7748 | 6.5406 | 10.2788 | 12.1559 | 6.7331 | 10.2787 | 12.1556 | 6.7331 | 10.2788 | 12.156 | 6.7331 | 10.4274 | 12.3475 | 6.8294
SW-Toowoomba Dalby Warwick | 790_Warwick-Stanthorpe 110 kV | Power Factor | 0.99508 | 0.99971 | 0.91009 | 0.99632 | 0.99995 | 0.91755 | 0.99626 | 0.99994 | 0.91743 | 0.99635 | 0.99995 | 0.91759 | 0.99644 | 1 | 0.92155
SW-Toowoomba Dalby Warwick | 790_Warwick-Stanthorpe 110 kV | Rating (A) | 127 | 180 | 175 | 127 | 180 | 175 | 127 | 180 | 175 | 127 | 180 | 175 | 127 | 180 | 175
SW-Toowoomba Dalby Warwick | 790_Warwick-Stanthorpe 110 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Toowoomba Dalby Warwick | 790_Warwick-Stanthorpe 110 kV | Min Voltage at Constrained Conductor | 106.9264 | 104.8765 | 115.4004 | 106.7723 | 104.5663 | 115.3084 | 106.8488 | 104.6538 | 115.3355 | 106.7195 | 104.5243 | 115.2988 | 107.3519 | 104.1121 | 115.1532
SW-Toowoomba Dalby Warwick | 790_Warwick-Stanthorpe 110 kV | Contingency Outage | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV
SW-Toowoomba Dalby Warwick | F008D_Central Dalby 2 33 kV | % of Rated A | 46.66% | 41.98% | 18.64% | 46.12% | 41.54% | 18.42% | 45.89% | 41.33% | 18.34% | 45.72% | 41.21% | 18.28% | 46.73% | 41.57% | 18.42%
SW-Toowoomba Dalby Warwick | F008D_Central Dalby 2 33 kV | Limiting Line Name | TR_CABLE 4401_1 | TR_CABLE 4401_1 | TR_LINE 92498_1 | TR_CABLE 4401_1 | TR_CABLE 4401_1 | TR_LINE 92498_1 | TR_CABLE 4401_1 | TR_CABLE 4401_1 | TR_LINE 92498_1 | TR_CABLE 4401_1 | TR_CABLE 4401_1 | TR_LINE 92498_1 | TR_CABLE 4401_1 | TR_CABLE 4401_1 | TR_LINE 92498_1
SW-Toowoomba Dalby Warwick | F008D_Central Dalby 2 33 kV | Loading (A) | 233.278 | 209.8809 | 89.4815 | 230.6173 | 207.7114 | 88.4022 | 229.4374 | 206.6255 | 88.0496 | 228.5866 | 206.0347 | 87.7308 | 233.6289 | 207.8541 | 88.4297
SW-Toowoomba Dalby Warwick | F008D_Central Dalby 2 33 kV | Loading (MVA) | 13.3359 | 11.9033 | 5.2567 | 13.1945 | 11.7875 | 5.1943 | 13.1316 | 11.7293 | 5.1739 | 13.0822 | 11.6948 | 5.1548 | 13.1965 | 11.788 | 5.1944
SW-Toowoomba Dalby Warwick | F008D_Central Dalby 2 33 kV | Loading (MW) | 12.6807 | 11.3503 | 5.0921 | 12.5508 | 11.2437 | 5.0342 | 12.4932 | 11.1901 | 5.0146 | 12.4463 | 11.1571 | 4.9964 | 12.5509 | 11.2437 | 5.0342
SW-Toowoomba Dalby Warwick | F008D_Central Dalby 2 33 kV | Power Factor | 0.95058 | 0.95327 | 0.9687 | 0.95093 | 0.9536 | 0.96917 | 0.9511 | 0.95376 | 0.96923 | 0.95111 | 0.95376 | 0.96928 | 0.9508 | 0.95356 | 0.96915
SW-Toowoomba Dalby Warwick | F008D_Central Dalby 2 33 kV | Rating (A) | 500 | 500 | 480 | 500 | 500 | 480 | 500 | 500 | 480 | 500 | 500 | 480 | 500 | 500 | 480
SW-Toowoomba Dalby Warwick | F008D_Central Dalby 2 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Toowoomba Dalby Warwick | F008D_Central Dalby 2 33 kV | Min Voltage at Constrained Conductor | 33.0056 | 32.7442 | 33.7523 | 33.0323 | 32.7642 | 33.7624 | 33.0439 | 32.7739 | 33.765 | 33.0422 | 32.7711 | 33.7638 | 32.6115 | 32.7432 | 33.7524
SW-Toowoomba Dalby Warwick | F008D_Central Dalby 2 33 kV | Contingency Outage | 3154_Central Dalby 1 33 kV | 3154_Central Dalby 1 33 kV | 3154_Central Dalby 1 33 kV | 3154_Central Dalby 1 33 kV | 3154_Central Dalby 1 33 kV | 3154_Central Dalby 1 33 kV | 3154_Central Dalby 1 33 kV | 3154_Central Dalby 1 33 kV | 3154_Central Dalby 1 33 kV | 3154_Central Dalby 1 33 kV | 3154_Central Dalby 1 33 kV | 3154_Central Dalby 1 33 kV | 3154_Central Dalby 1 33 kV | 3154_Central Dalby 1 33 kV | 3154_Central Dalby 1 33 kV
SW-Toowoomba Dalby Warwick | F019D_West Dalby No 1 33 kV | % of Rated A | 48.17% | 39.24% | 20.93% | 47.57% | 38.8% | 20.54% | 47.36% | 38.62% | 20.54% | 47.13% | 38.48% | 20.36% | 48.19% | 38.83% | 20.55%
SW-Toowoomba Dalby Warwick | F019D_West Dalby No 1 33 kV | Limiting Line Name | TR_LINE 58890_1 | TR_LINE 58890_1 | TR_LINE 58890_1 | TR_LINE 58890_1 | TR_LINE 58890_1 | TR_LINE 58890_1 | TR_LINE 58890_1 | TR_LINE 58890_1 | TR_LINE 58890_1 | TR_LINE 58890_1 | TR_LINE 58890_1 | TR_LINE 58890_1 | TR_LINE 58890_1 | TR_LINE 58890_1 | TR_LINE 58890_1
SW-Toowoomba Dalby Warwick | F019D_West Dalby No 1 33 kV | Loading (A) | 180.6509 | 160.5062 | 77.0223 | 178.3815 | 158.7011 | 75.5834 | 177.5891 | 157.9753 | 75.5792 | 176.7213 | 157.3699 | 74.9378 | 180.73 | 158.8094 | 75.6076
SW-Toowoomba Dalby Warwick | F019D_West Dalby No 1 33 kV | Loading (MVA) | 10.4597 | 9.2079 | 4.5212 | 10.3349 | 9.1087 | 4.4378 | 10.2918 | 9.069 | 4.4378 | 10.2406 | 9.0332 | 4.4 | 10.3412 | 9.1092 | 4.438
SW-Toowoomba Dalby Warwick | F019D_West Dalby No 1 33 kV | Loading (MW) | 9.8551 | 8.717 | 4.3481 | 9.7433 | 8.6276 | 4.2721 | 9.7042 | 8.5913 | 4.2721 | 9.6569 | 8.5581 | 4.236 | 9.7454 | 8.6277 | 4.2721
SW-Toowoomba Dalby Warwick | F019D_West Dalby No 1 33 kV | Power Factor | 0.94219 | 0.94669 | 0.96172 | 0.94275 | 0.94718 | 0.96265 | 0.94291 | 0.94733 | 0.96266 | 0.94301 | 0.9474 | 0.96274 | 0.94239 | 0.94714 | 0.96263
SW-Toowoomba Dalby Warwick | F019D_West Dalby No 1 33 kV | Rating (A) | 375 | 409 | 368 | 375 | 409 | 368 | 375 | 409 | 368 | 375 | 409 | 368 | 375 | 409 | 368
SW-Toowoomba Dalby Warwick | F019D_West Dalby No 1 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Toowoomba Dalby Warwick | F019D_West Dalby No 1 33 kV | Min Voltage at Constrained Conductor | 33.304 | 33.0132 | 33.8493 | 33.3274 | 33.0303 | 33.859 | 33.337 | 33.0381 | 33.8607 | 33.3346 | 33.0348 | 33.8598 | 32.9107 | 33.0095 | 33.849
SW-Toowoomba Dalby Warwick | F019D_West Dalby No 1 33 kV | Contingency Outage | F008D_Central Dalby 2 33 kV | F008D_Central Dalby 2 33 kV | F039D_West Dalby No 2 33 kV | F008D_Central Dalby 2 33 kV | F008D_Central Dalby 2 33 kV | F039D_West Dalby No 2 33 kV | F008D_Central Dalby 2 33 kV | F008D_Central Dalby 2 33 kV | F039D_West Dalby No 2 33 kV | F008D_Central Dalby 2 33 kV | F008D_Central Dalby 2 33 kV | F039D_West Dalby No 2 33 kV | F008D_Central Dalby 2 33 kV | F008D_Central Dalby 2 33 kV | F039D_West Dalby No 2 33 kV
SW-Toowoomba Dalby Warwick | F039D_West Dalby No 2 33 kV | % of Rated A | 53.1% | 43.78% | 27.19% | 52.08% | 43.04% | 26.68% | 52.07% | 43.02% | 26.68% | 51.47% | 42.6% | 26.46% | 52.79% | 43.07% | 26.69%
SW-Toowoomba Dalby Warwick | F039D_West Dalby No 2 33 kV | Limiting Line Name | TR_CABLE 139_1 | TR_CABLE 139_1 | TR_CABLE 139_1 | TR_CABLE 139_1 | TR_CABLE 139_1 | TR_CABLE 139_1 | TR_CABLE 139_1 | TR_CABLE 139_1 | TR_CABLE 139_1 | TR_CABLE 139_1 | TR_CABLE 139_1 | TR_CABLE 139_1 | TR_CABLE 139_1 | TR_CABLE 139_1 | TR_CABLE 139_1
SW-Toowoomba Dalby Warwick | F039D_West Dalby No 2 33 kV | Loading (A) | 150.8019 | 124.3285 | 77.2191 | 147.9168 | 122.2261 | 75.7803 | 147.8868 | 122.1893 | 75.7743 | 146.167 | 120.9816 | 75.134 | 149.9217 | 122.3105 | 75.8046
SW-Toowoomba Dalby Warwick | F039D_West Dalby No 2 33 kV | Loading (MVA) | 8.5969 | 7.0367 | 4.5063 | 8.4401 | 6.9223 | 4.4239 | 8.44 | 6.9222 | 4.4239 | 8.3419 | 6.8535 | 4.3864 | 8.4446 | 6.9226 | 4.424
SW-Toowoomba Dalby Warwick | F039D_West Dalby No 2 33 kV | Loading (MW) | 8.1573 | 6.7117 | 4.3329 | 8.014 | 6.6067 | 4.2574 | 8.014 | 6.6067 | 4.2574 | 7.9212 | 6.5413 | 4.2216 | 8.0145 | 6.6067 | 4.2574
SW-Toowoomba Dalby Warwick | F039D_West Dalby No 2 33 kV | Power Factor | 0.94876 | 0.95372 | 0.96138 | 0.94942 | 0.9543 | 0.96224 | 0.94943 | 0.95431 | 0.96225 | 0.94947 | 0.95435 | 0.9623 | 0.94896 | 0.95426 | 0.96222
SW-Toowoomba Dalby Warwick | F039D_West Dalby No 2 33 kV | Rating (A) | 284 | 284 | 284 | 284 | 284 | 284 | 284 | 284 | 284 | 284 | 284 | 284 | 284 | 284 | 284
SW-Toowoomba Dalby Warwick | F039D_West Dalby No 2 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Toowoomba Dalby Warwick | F039D_West Dalby No 2 33 kV | Min Voltage at Constrained Conductor | 32.9134 | 32.6765 | 33.6929 | 32.9433 | 32.6986 | 33.7045 | 32.9496 | 32.7078 | 33.707 | 32.9498 | 32.7063 | 33.7065 | 32.5205 | 32.6774 | 33.6945
SW-Toowoomba Dalby Warwick | F039D_West Dalby No 2 33 kV | Contingency Outage | F019D_West Dalby No 1 33 kV | F019D_West Dalby No 1 33 kV | F019D_West Dalby No 1 33 kV | F019D_West Dalby No 1 33 kV | F019D_West Dalby No 1 33 kV | F019D_West Dalby No 1 33 kV | F019D_West Dalby No 1 33 kV | F019D_West Dalby No 1 33 kV | F019D_West Dalby No 1 33 kV | F019D_West Dalby No 1 33 kV | F019D_West Dalby No 1 33 kV | F019D_West Dalby No 1 33 kV | F019D_West Dalby No 1 33 kV | F019D_West Dalby No 1 33 kV | F019D_West Dalby No 1 33 kV
SW-Toowoomba Dalby Warwick | F095D_Kaimkillenbun 33 kV | % of Rated A | 19.57% | 22.11% | 11.08% | 19.55% | 22.11% | 11.07% | 19.79% | 22.1% | 11.07% | 19.79% | 22.1% | 11.07% | 19.77% | 22.11% | 11.05%
SW-Toowoomba Dalby Warwick | F095D_Kaimkillenbun 33 kV | Limiting Line Name | TR_LINE 81370_2 | TR_CABLE 5206_1 | TR_CABLE 5206_1 | TR_LINE 81370_2 | TR_CABLE 5206_1 | TR_CABLE 5206_1 | TR_LINE 81370_2 | TR_CABLE 5206_1 | TR_CABLE 5206_1 | TR_LINE 81370_2 | TR_CABLE 5206_1 | TR_CABLE 5206_1 | TR_LINE 81370_2 | TR_CABLE 5206_1 | TR_CABLE 5206_1
SW-Toowoomba Dalby Warwick | F095D_Kaimkillenbun 33 kV | Loading (A) | 18.2045 | 22.1146 | 11.0754 | 18.1853 | 22.1053 | 11.0744 | 18.4073 | 22.1009 | 11.074 | 18.4072 | 22.1039 | 11.0745 | 18.39 | 22.112 | 11.0505
SW-Toowoomba Dalby Warwick | F095D_Kaimkillenbun 33 kV | Loading (MVA) | 1.0578 | 1.2732 | 0.64331 | 1.0577 | 1.2732 | 0.64333 | 1.0581 | 1.2731 | 0.64333 | 1.0581 | 1.2731 | 0.64333 | 1.0576 | 1.2728 | 0.64176
SW-Toowoomba Dalby Warwick | F095D_Kaimkillenbun 33 kV | Loading (MW) | 1.0574 | 1.2732 | 0.62347 | 1.0574 | 1.2732 | 0.62347 | 1.0579 | 1.2731 | 0.62347 | 1.0579 | 1.2731 | 0.62347 | 1.0575 | 1.2727 | 0.62317
SW-Toowoomba Dalby Warwick | F095D_Kaimkillenbun 33 kV | Power Factor | 0.99966 | 0.99981 | 0.96916 | 0.99964 | 0.99982 | 0.96913 | 0.99979 | 0.99982 | 0.96912 | 0.99979 | 0.99982 | 0.96913 | 0.9999 | 0.99968 | 0.97104
SW-Toowoomba Dalby Warwick | F095D_Kaimkillenbun 33 kV | Rating (A) | 93 | 100 | 100 | 93 | 100 | 100 | 93 | 100 | 100 | 93 | 100 | 100 | 93 | 100 | 100
SW-Toowoomba Dalby Warwick | F095D_Kaimkillenbun 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Toowoomba Dalby Warwick | F095D_Kaimkillenbun 33 kV | Min Voltage at Constrained Conductor | 33.5435 | 33.2387 | 33.5352 | 33.5783 | 33.2521 | 33.5389 | 33.1837 | 33.2584 | 33.5406 | 33.1839 | 33.254 | 33.5386 | 33.1993 | 33.2316 | 33.5293
SW-Toowoomba Dalby Warwick | F095D_Kaimkillenbun 33 kV | Contingency Outage | F5545_7245 Tangkam-Dalby 110 kV | 7314_Dalby East 110 kV | F097D_Jandowae 33 kV | F5545_7245 Tangkam-Dalby 110 kV | 7314_Dalby East 110 kV | F097D_Jandowae 33 kV | F5540_7244 Tangkam-Dalby 110 kV | 7314_Dalby East 110 kV | F097D_Jandowae 33 kV | F5540_7244 Tangkam-Dalby 110 kV | 7314_Dalby East 110 kV | F097D_Jandowae 33 kV | F4132_Shirley Road 33 kV | 7314_Dalby East 110 kV | F097D_Jandowae 33 kV
SW-Toowoomba Dalby Warwick | F097D_Jandowae 33 kV | % of Rated A | 18.5% | 11.84% | 9.029% | 17.77% | 11.46% | 8.708% | 17.88% | 11.45% | 8.707% | 17.88% | 11.46% | 8.707% | 18.04% | 11.47% | 8.71%
SW-Toowoomba Dalby Warwick | F097D_Jandowae 33 kV | Limiting Line Name | TR_LINE 76815_3 | TR_LINE 76815_3 | TR_LINE 76815_3 | TR_LINE 76815_3 | TR_LINE 76815_3 | TR_LINE 102880_1 | TR_LINE 76815_3 | TR_LINE 76815_3 | TR_LINE 102880_1 | TR_LINE 76815_3 | TR_LINE 76815_3 | TR_LINE 102880_1 | TR_LINE 76815_3 | TR_LINE 76815_3 | TR_LINE 102880_1
SW-Toowoomba Dalby Warwick | F097D_Jandowae 33 kV | Loading (A) | 26.4586 | 25.1022 | 18.8701 | 25.4148 | 24.2921 | 21.5949 | 25.5637 | 24.2845 | 21.5933 | 25.5613 | 24.2857 | 21.5941 | 25.7956 | 24.3097 | 21.6019
SW-Toowoomba Dalby Warwick | F097D_Jandowae 33 kV | Loading (MVA) | 1.5052 | 1.418 | 1.0905 | 1.4472 | 1.3732 | 1.2498 | 1.4483 | 1.3732 | 1.2497 | 1.4483 | 1.3732 | 1.2498 | 1.45 | 1.3733 | 1.2498
SW-Toowoomba Dalby Warwick | F097D_Jandowae 33 kV | Loading (MW) | 1.4322 | 1.3657 | 1.0509 | 1.3818 | 1.3262 | 1.1949 | 1.3819 | 1.3262 | 1.1949 | 1.3819 | 1.3262 | 1.1949 | 1.3821 | 1.3262 | 1.1949
SW-Toowoomba Dalby Warwick | F097D_Jandowae 33 kV | Power Factor | 0.95068 | 0.96239 | 0.96313 | 0.95399 | 0.96499 | 0.95613 | 0.95336 | 0.96501 | 0.95614 | 0.95336 | 0.96501 | 0.95614 | 0.95236 | 0.96492 | 0.9561
SW-Toowoomba Dalby Warwick | F097D_Jandowae 33 kV | Rating (A) | 143 | 212 | 209 | 143 | 212 | 248 | 143 | 212 | 248 | 143 | 212 | 248 | 143 | 212 | 248
SW-Toowoomba Dalby Warwick | F097D_Jandowae 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Toowoomba Dalby Warwick | F097D_Jandowae 33 kV | Min Voltage at Constrained Conductor | 32.8441 | 32.6132 | 33.3635 | 32.8772 | 32.6377 | 33.4129 | 32.7099 | 32.647 | 33.415 | 32.7127 | 32.6455 | 33.4139 | 32.4531 | 32.6165 | 33.4031
SW-Toowoomba Dalby Warwick | F097D_Jandowae 33 kV | Contingency Outage | F019D_West Dalby No 1 33 kV | F019D_West Dalby No 1 33 kV | F099D_Warra 33 kV | F019D_West Dalby No 1 33 kV | F019D_West Dalby No 1 33 kV | F099D_Warra 33 kV | F5540_7244 Tangkam-Dalby 110 kV | F019D_West Dalby No 1 33 kV | F099D_Warra 33 kV | F5540_7244 Tangkam-Dalby 110 kV | F019D_West Dalby No 1 33 kV | F099D_Warra 33 kV | F019D_West Dalby No 1 33 kV | F019D_West Dalby No 1 33 kV | F099D_Warra 33 kV
SW-Toowoomba Dalby Warwick | F099D_Warra 33 kV | % of Rated A | 22.15% | 20.83% | 15.79% | 22.13% | 20.81% | 15.79% | 22.23% | 20.81% | 15.79% | 22.22% | 20.81% | 15.79% | 22.43% | 20.83% | 15.79%
SW-Toowoomba Dalby Warwick | F099D_Warra 33 kV | Limiting Line Name | TR_LINE 25305_1 | TR_LINE 25305_1 | TR_LINE 25305_1 | TR_LINE 25305_1 | TR_LINE 25305_1 | TR_LINE 25305_1 | TR_LINE 25305_1 | TR_LINE 25305_1 | TR_LINE 25305_1 | TR_LINE 25305_1 | TR_LINE 25305_1 | TR_LINE 25305_1 | TR_LINE 25305_1 | TR_LINE 25305_1 | TR_LINE 25305_1
SW-Toowoomba Dalby Warwick | F099D_Warra 33 kV | Loading (A) | 36.5435 | 36.8652 | 24.789 | 36.5067 | 36.8377 | 24.7848 | 36.6736 | 36.8262 | 24.7831 | 36.6702 | 36.8281 | 24.784 | 37.0036 | 36.864 | 24.7828
SW-Toowoomba Dalby Warwick | F099D_Warra 33 kV | Loading (MVA) | 2.0821 | 2.0853 | 1.4336 | 2.0819 | 2.0851 | 1.4335 | 2.0808 | 2.0851 | 1.4335 | 2.0808 | 2.0851 | 1.4335 | 2.0831 | 2.0853 | 1.433
SW-Toowoomba Dalby Warwick | F099D_Warra 33 kV | Loading (MW) | 1.9588 | 1.9718 | 1.3789 | 1.9587 | 1.9718 | 1.3789 | 1.9589 | 1.9718 | 1.3789 | 1.9589 | 1.9718 | 1.3789 | 1.9589 | 1.9718 | 1.3789
SW-Toowoomba Dalby Warwick | F099D_Warra 33 kV | Power Factor | 0.94067 | 0.94547 | 0.9617 | 0.94076 | 0.94553 | 0.96172 | 0.9413 | 0.94556 | 0.96173 | 0.94131 | 0.94555 | 0.96172 | 0.9403 | 0.94547 | 0.96208
SW-Toowoomba Dalby Warwick | F099D_Warra 33 kV | Rating (A) | 165 | 177 | 157 | 165 | 177 | 157 | 165 | 177 | 157 | 165 | 177 | 157 | 165 | 177 | 157
SW-Toowoomba Dalby Warwick | F099D_Warra 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Toowoomba Dalby Warwick | F099D_Warra 33 kV | Min Voltage at Constrained Conductor | 32.8877 | 32.6506 | 33.3862 | 32.9176 | 32.6727 | 33.3912 | 32.7507 | 32.6819 | 33.3934 | 32.7535 | 32.6804 | 33.3923 | 32.4944 | 32.6516 | 33.3817
SW-Toowoomba Dalby Warwick | F099D_Warra 33 kV | Contingency Outage | F019D_West Dalby No 1 33 kV | F019D_West Dalby No 1 33 kV | F097D_Jandowae 33 kV | F019D_West Dalby No 1 33 kV | F019D_West Dalby No 1 33 kV | F097D_Jandowae 33 kV | F5540_7244 Tangkam-Dalby 110 kV | F019D_West Dalby No 1 33 kV | F097D_Jandowae 33 kV | F5540_7244 Tangkam-Dalby 110 kV | F019D_West Dalby No 1 33 kV | F097D_Jandowae 33 kV | F019D_West Dalby No 1 33 kV | F019D_West Dalby No 1 33 kV | F097D_Jandowae 33 kV
SW-Toowoomba Dalby Warwick | F2060_Sladevale 1 33kV | % of Rated A | 11.71% | 13.98% | 6.821% | 11.72% | 14.01% | 6.821% | 11.71% | 13.99% | 6.821% | 11.72% | 14.01% | 6.821% | 12.03% | 14.37% | 6.875%
SW-Toowoomba Dalby Warwick | F2060_Sladevale 1 33kV | Limiting Line Name | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1
SW-Toowoomba Dalby Warwick | F2060_Sladevale 1 33kV | Loading (A) | 74.3777 | 88.7659 | 43.3137 | 74.409 | 88.9412 | 43.3123 | 74.354 | 88.8524 | 43.3135 | 74.4415 | 88.9764 | 43.3104 | 76.3857 | 91.2725 | 43.6593
SW-Toowoomba Dalby Warwick | F2060_Sladevale 1 33kV | Loading (MVA) | 4.2579 | 5.0668 | 2.6313 | 4.2578 | 5.0679 | 2.6308 | 4.258 | 5.0673 | 2.6313 | 4.2578 | 5.0681 | 2.6302 | 4.3434 | 5.1813 | 2.6496
SW-Toowoomba Dalby Warwick | F2060_Sladevale 1 33kV | Loading (MW) | 4.2035 | 5.0558 | 1.9532 | 4.2038 | 5.0575 | 1.9532 | 4.2033 | 5.0567 | 1.9532 | 4.2041 | 5.0579 | 1.9533 | 4.3004 | 5.1748 | 1.9943
SW-Toowoomba Dalby Warwick | F2060_Sladevale 1 33kV | Power Factor | 0.98722 | 0.99783 | 0.7423 | 0.9873 | 0.99795 | 0.74244 | 0.98716 | 0.99789 | 0.74231 | 0.98739 | 0.99797 | 0.74264 | 0.99009 | 0.99876 | 0.75268
SW-Toowoomba Dalby Warwick | F2060_Sladevale 1 33kV | Rating (A) | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635
SW-Toowoomba Dalby Warwick | F2060_Sladevale 1 33kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Toowoomba Dalby Warwick | F2060_Sladevale 1 33kV | Min Voltage at Constrained Conductor | 33.0515 | 32.9553 | 35.074 | 33.0371 | 32.8976 | 35.0686 | 33.0624 | 32.9268 | 35.0735 | 33.0222 | 32.886 | 35.0614 | 32.8292 | 32.7744 | 35.0385
SW-Toowoomba Dalby Warwick | F2060_Sladevale 1 33kV | Contingency Outage | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5560_735(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5560_735(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5560_735(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5560_735(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5560_735(Middle Ridge-Warwick) 110 kV
SW-Toowoomba Dalby Warwick | F2325_Broxburn 33 kV | % of Rated A | 46.43% | 43.21% | 28.03% | 49.32% | 45.62% | 29.44% | 49.32% | 45.62% | 29.44% | 49.36% | 45.65% | 29.45% | 49.66% | 46.25% | 29.59%
SW-Toowoomba Dalby Warwick | F2325_Broxburn 33 kV | Limiting Line Name | TR_LINE 174733_1 | TR_LINE 126800_1 | TR_LINE 126800_1 | TR_LINE 174733_1 | TR_LINE 174733_1 | TR_LINE 126800_1 | TR_LINE 174733_1 | TR_LINE 174733_1 | TR_LINE 126800_1 | TR_LINE 174733_1 | TR_LINE 174733_1 | TR_LINE 126800_1 | TR_LINE 174733_1 | TR_LINE 174733_1 | TR_LINE 126800_1
SW-Toowoomba Dalby Warwick | F2325_Broxburn 33 kV | Loading (A) | 155.0854 | 169.3843 | 95.3027 | 164.7436 | 153.733 | 100.1008 | 164.729 | 153.728 | 100.0992 | 164.8612 | 153.8426 | 100.1279 | 165.873 | 155.8571 | 100.6036
SW-Toowoomba Dalby Warwick | F2325_Broxburn 33 kV | Loading (MVA) | 8.4229 | 9.7389 | 5.4529 | 8.9113 | 8.3629 | 5.7259 | 8.9113 | 8.3629 | 5.7259 | 8.9116 | 8.3631 | 5.726 | 9.0076 | 8.4551 | 5.7785
SW-Toowoomba Dalby Warwick | F2325_Broxburn 33 kV | Loading (MW) | 7.9283 | 8.9821 | 5.1001 | 8.3786 | 7.8732 | 5.3525 | 8.3786 | 7.8732 | 5.3525 | 8.3786 | 7.8731 | 5.3526 | 8.4687 | 7.9578 | 5.4022
SW-Toowoomba Dalby Warwick | F2325_Broxburn 33 kV | Power Factor | 0.94127 | 0.92229 | 0.93529 | 0.94022 | 0.94144 | 0.9348 | 0.94022 | 0.94144 | 0.9348 | 0.94019 | 0.94142 | 0.93478 | 0.94017 | 0.94118 | 0.93488
SW-Toowoomba Dalby Warwick | F2325_Broxburn 33 kV | Rating (A) | 334 | 392 | 340 | 334 | 337 | 340 | 334 | 337 | 340 | 334 | 337 | 340 | 334 | 337 | 340
SW-Toowoomba Dalby Warwick | F2325_Broxburn 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Toowoomba Dalby Warwick | F2325_Broxburn 33 kV | Min Voltage at Constrained Conductor | 31.3514 | 33.1741 | 33.0238 | 31.2244 | 31.4019 | 33.014 | 31.2271 | 31.4029 | 33.0144 | 31.2029 | 31.3802 | 33.0057 | 31.3468 | 31.3155 | 33.1508
SW-Toowoomba Dalby Warwick | F2325_Broxburn 33 kV | Contingency Outage | F5555_734(Middle Ridge-Yarranlea) 110 kV | F2460_Cecil Plains 33 kV | F2460_Cecil Plains 33 kV | F2460_Cecil Plains 33 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F2460_Cecil Plains 33 kV | F2460_Cecil Plains 33 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F2460_Cecil Plains 33 kV | F2460_Cecil Plains 33 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F2460_Cecil Plains 33 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F2460_Cecil Plains 33 kV | 7449 South Toowoomba-TWCE 110 kV
SW-Toowoomba Dalby Warwick | F2450_Carrington Road 33 kV | % of Rated A | 12.38% | 8.767% | 5.586% | 12.38% | 8.763% | 5.585% | 12.38% | 8.761% | 5.584% | 12.35% | 8.759% | 5.561% | 12.65% | 8.985% | 5.715%
SW-Toowoomba Dalby Warwick | F2450_Carrington Road 33 kV | Limiting Line Name | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1
SW-Toowoomba Dalby Warwick | F2450_Carrington Road 33 kV | Loading (A) | 41.7296 | 29.5445 | 18.8239 | 41.7195 | 29.5316 | 18.8202 | 41.7248 | 29.5233 | 18.8178 | 41.6125 | 29.5177 | 18.7423 | 42.6257 | 30.2795 | 19.258
SW-Toowoomba Dalby Warwick | F2450_Carrington Road 33 kV | Loading (MVA) | 2.4185 | 1.7159 | 1.0957 | 2.4185 | 1.7159 | 1.0957 | 2.4185 | 1.7159 | 1.0957 | 2.4184 | 1.7159 | 1.0957 | 2.4829 | 1.7612 | 1.1245
SW-Toowoomba Dalby Warwick | F2450_Carrington Road 33 kV | Loading (MW) | 2.1746 | 1.5464 | 0.98946 | 2.1746 | 1.5464 | 0.98947 | 2.1746 | 1.5464 | 0.98947 | 2.1746 | 1.5464 | 0.98951 | 2.2317 | 1.587 | 1.0155
SW-Toowoomba Dalby Warwick | F2450_Carrington Road 33 kV | Power Factor | 0.89906 | 0.90114 | 0.90293 | 0.89907 | 0.90114 | 0.90293 | 0.89906 | 0.90115 | 0.90293 | 0.8991 | 0.90115 | 0.90296 | 0.89874 | 0.90101 | 0.90294
SW-Toowoomba Dalby Warwick | F2450_Carrington Road 33 kV | Rating (A) | 337 | 337 | 337 | 337 | 337 | 337 | 337 | 337 | 337 | 337 | 337 | 337 | 337 | 337 | 337
SW-Toowoomba Dalby Warwick | F2450_Carrington Road 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Toowoomba Dalby Warwick | F2450_Carrington Road 33 kV | Min Voltage at Constrained Conductor | 33.4615 | 33.5315 | 33.6056 | 33.4695 | 33.546 | 33.6123 | 33.4653 | 33.5553 | 33.6165 | 33.5544 | 33.5618 | 33.7527 | 33.6301 | 33.5808 | 33.713
SW-Toowoomba Dalby Warwick | F2450_Carrington Road 33 kV | Contingency Outage | F3980_Purrawunda 33 kV | 7233_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV | 7233_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | 7233_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F3820_Boundary Road 33 kV | 7234_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV
SW-Toowoomba Dalby Warwick | F2460_Cecil Plains 33 kV | % of Rated A | 30.53% | 19.8% | 18.91% | 29.89% | 19.47% | 18.72% | 29.89% | 19.47% | 18.72% | 29.88% | 19.46% | 18.71% | 30.54% | 19.78% | 18.9%
SW-Toowoomba Dalby Warwick | F2460_Cecil Plains 33 kV | Limiting Line Name | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1
SW-Toowoomba Dalby Warwick | F2460_Cecil Plains 33 kV | Loading (A) | 43.6536 | 41.7786 | 39.3394 | 42.7453 | 41.0776 | 38.9293 | 42.7465 | 41.0781 | 38.9297 | 42.735 | 41.0655 | 38.9218 | 43.6652 | 41.7268 | 39.3053
SW-Toowoomba Dalby Warwick | F2460_Cecil Plains 33 kV | Loading (MVA) | 2.5609 | 2.4496 | 2.3022 | 2.5074 | 2.4083 | 2.2789 | 2.5077 | 2.4084 | 2.2789 | 2.5052 | 2.4061 | 2.2778 | 2.5637 | 2.4398 | 2.2971
SW-Toowoomba Dalby Warwick | F2460_Cecil Plains 33 kV | Loading (MW) | 1.6078 | 1.3957 | 1.0728 | 1.5077 | 1.309 | 1.0064 | 1.5077 | 1.309 | 1.0064 | 1.5077 | 1.309 | 1.0064 | 1.6078 | 1.3956 | 1.0728
SW-Toowoomba Dalby Warwick | F2460_Cecil Plains 33 kV | Power Factor | 0.62697 | 0.56902 | 0.46507 | 0.60053 | 0.54279 | 0.44057 | 0.60047 | 0.54277 | 0.44056 | 0.60105 | 0.54327 | 0.44078 | 0.62629 | 0.5713 | 0.46609
SW-Toowoomba Dalby Warwick | F2460_Cecil Plains 33 kV | Rating (A) | 143 | 211 | 208 | 143 | 211 | 208 | 143 | 211 | 208 | 143 | 211 | 208 | 143 | 211 | 208
SW-Toowoomba Dalby Warwick | F2460_Cecil Plains 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Toowoomba Dalby Warwick | F2460_Cecil Plains 33 kV | Min Voltage at Constrained Conductor | 33.8701 | 33.852 | 33.7868 | 33.8671 | 33.8483 | 33.7975 | 33.8696 | 33.8492 | 33.798 | 33.8457 | 33.8286 | 33.788 | 33.8982 | 33.7582 | 33.7416
SW-Toowoomba Dalby Warwick | F2460_Cecil Plains 33 kV | Contingency Outage | F3530_Millmerran 33 kV | F3830_Norwin 33 kV | F3530_Millmerran 33 kV | F3530_Millmerran 33 kV | F3830_Norwin 33 kV | F3530_Millmerran 33 kV | F3530_Millmerran 33 kV | F3830_Norwin 33 kV | F3530_Millmerran 33 kV | F3530_Millmerran 33 kV | F3830_Norwin 33 kV | F3530_Millmerran 33 kV | F3830_Norwin 33 kV | F3820_Boundary Road 33 kV | F3530_Millmerran 33 kV
SW-Toowoomba Dalby Warwick | F2520_Clifton 33 kV | % of Rated A | 42.06% | 55.8% | 28.74% | 47.67% | 64.74% | 31.05% | 50.79% | 69.47% | 32.31% | 50.85% | 69.59% | 32.26% | 51.11% | 69.66% | 32.26%
SW-Toowoomba Dalby Warwick | F2520_Clifton 33 kV | Limiting Line Name | TR_LINE 188412_1 | TR_LINE 188412_1 | TR_LINE 188412_1 | TR_LINE 188412_1 | TR_LINE 188412_1 | TR_LINE 188412_1 | TR_LINE 188412_1 | TR_LINE 188412_1 | TR_LINE 188412_1 | TR_LINE 188412_1 | TR_LINE 188412_1 | TR_LINE 188412_1 | TR_LINE 188412_1 | TR_LINE 188412_1 | TR_LINE 188412_1
SW-Toowoomba Dalby Warwick | F2520_Clifton 33 kV | Loading (A) | 51.312 | 68.0702 | 35.0622 | 58.1586 | 78.9853 | 37.8838 | 61.9644 | 84.7492 | 39.4232 | 62.032 | 84.9022 | 39.3547 | 62.3601 | 84.9886 | 39.3575
SW-Toowoomba Dalby Warwick | F2520_Clifton 33 kV | Loading (MVA) | 2.9697 | 3.8437 | 2.0998 | 3.349 | 4.4254 | 2.2352 | 3.5596 | 4.7277 | 2.3226 | 3.5579 | 4.7266 | 2.3414 | 3.55 | 4.726 | 2.3405
SW-Toowoomba Dalby Warwick | F2520_Clifton 33 kV | Loading (MW) | 2.6785 | 3.6849 | 1.5096 | 3.1314 | 4.3161 | 1.7613 | 3.3594 | 4.6344 | 1.8874 | 3.3596 | 4.635 | 1.8873 | 3.3605 | 4.6353 | 1.8873
SW-Toowoomba Dalby Warwick | F2520_Clifton 33 kV | Power Factor | 0.90183 | 0.95851 | 0.71892 | 0.93489 | 0.97513 | 0.78798 | 0.94361 | 0.9801 | 0.81264 | 0.94411 | 0.98044 | 0.80607 | 0.94646 | 0.98062 | 0.80635
SW-Toowoomba Dalby Warwick | F2520_Clifton 33 kV | Rating (A) | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122
SW-Toowoomba Dalby Warwick | F2520_Clifton 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Toowoomba Dalby Warwick | F2520_Clifton 33 kV | Min Voltage at Constrained Conductor | 33.4033 | 32.5808 | 34.5754 | 33.2312 | 32.3218 | 34.0604 | 33.1497 | 32.1785 | 34.0097 | 33.0977 | 32.1132 | 34.3447 | 32.8497 | 32.0765 | 34.3302
SW-Toowoomba Dalby Warwick | F2520_Clifton 33 kV | Contingency Outage | F3255_Jennings Street 33 kV | F3255_Jennings Street 33 kV | F3867_Pampas 33 kV | F3255_Jennings Street 33 kV | F3255_Jennings Street 33 kV | 728_Middle Ridge-South Toowoomba 110 kV | F3255_Jennings Street 33 kV | F3255_Jennings Street 33 kV | 728_Middle Ridge-South Toowoomba 110 kV | F3255_Jennings Street 33 kV | F3255_Jennings Street 33 kV | 7449 South Toowoomba-TWCE 110 kV | F3255_Jennings Street 33 kV | F3255_Jennings Street 33 kV | 7449 South Toowoomba-TWCE 110 kV
SW-Toowoomba Dalby Warwick | F2777_East Stanthorpe 33 kV | % of Rated A | 1.601% | 1.18% | 1.259% | 1.601% | 1.186% | 1.259% | 1.602% | 1.181% | 1.259% | 1.6% | 1.185% | 1.258% | 1.606% | 1.185% | 1.258%
SW-Toowoomba Dalby Warwick | F2777_East Stanthorpe 33 kV | Limiting Line Name | TR_LINE 140241_1 | TR_LINE 140241_1 | TR_LINE 140241_1 | TR_LINE 140241_1 | TR_LINE 140241_1 | TR_LINE 140241_1 | TR_LINE 140241_1 | TR_LINE 140241_1 | TR_LINE 140241_1 | TR_LINE 140241_1 | TR_LINE 140241_1 | TR_LINE 140241_1 | TR_LINE 140241_1 | TR_LINE 140241_1 | TR_LINE 140241_1
SW-Toowoomba Dalby Warwick | F2777_East Stanthorpe 33 kV | Loading (A) | 2.4657 | 2.4541 | 2.5301 | 2.4657 | 2.4662 | 2.5297 | 2.4665 | 2.4557 | 2.5301 | 2.4645 | 2.4652 | 2.5292 | 2.474 | 2.4646 | 2.5276
SW-Toowoomba Dalby Warwick | F2777_East Stanthorpe 33 kV | Loading (MVA) | 0.14548 | 0.14412 | 0.15361 | 0.14548 | 0.14554 | 0.15357 | 0.14558 | 0.1443 | 0.15362 | 0.14534 | 0.14542 | 0.15351 | 0.14635 | 0.14514 | 0.15331
SW-Toowoomba Dalby Warwick | F2777_East Stanthorpe 33 kV | Loading (MW) | 6.9281e-05 | 6.8632e-05 | 7.2733e-05 | 6.928e-05 | 6.9308e-05 | 7.2713e-05 | 6.9327e-05 | 6.8717e-05 | 7.2735e-05 | 6.9214e-05 | 6.9253e-05 | 7.2684e-05 | 6.9798e-05 | 6.9327e-05 | 7.2591e-05
SW-Toowoomba Dalby Warwick | F2777_East Stanthorpe 33 kV | Power Factor | 0.00047418 | 0.00047418 | 0.00047145 | 0.00047418 | 0.00047418 | 0.00047145 | 0.00047418 | 0.00047418 | 0.00047145 | 0.00047418 | 0.00047418 | 0.00047145 | 0.00047489 | 0.00047562 | 0.00047145
SW-Toowoomba Dalby Warwick | F2777_East Stanthorpe 33 kV | Rating (A) | 154 | 208 | 201 | 154 | 208 | 201 | 154 | 208 | 201 | 154 | 208 | 201 | 154 | 208 | 201
SW-Toowoomba Dalby Warwick | F2777_East Stanthorpe 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Toowoomba Dalby Warwick | F2777_East Stanthorpe 33 kV | Min Voltage at Constrained Conductor | 34.065 | 33.905 | 35.0535 | 34.0648 | 34.0717 | 35.0488 | 34.0765 | 33.9262 | 35.054 | 34.0487 | 34.0581 | 35.0419 | 34.1538 | 33.9994 | 35.0194
SW-Toowoomba Dalby Warwick | F2777_East Stanthorpe 33 kV | Contingency Outage | F3970_Pozieres 33 kV | F4245_Stanthorpe 33 kV | F5560_735(Middle Ridge-Warwick) 110 kV | F3970_Pozieres 33 kV | 3283_Allora 33kV | F5560_735(Middle Ridge-Warwick) 110 kV | F3970_Pozieres 33 kV | F4245_Stanthorpe 33 kV | F5560_735(Middle Ridge-Warwick) 110 kV | F3970_Pozieres 33 kV | 3283_Allora 33kV | F5560_735(Middle Ridge-Warwick) 110 kV | F4605_West Warwick 33 kV | 3283_Allora 33kV | F5560_735(Middle Ridge-Warwick) 110 kV
SW-Toowoomba Dalby Warwick | F2780_East Warwick No 1 33 kV | % of Rated A | 53.97% | 53.01% | 33.1% | 53.41% | 52.46% | 32.84% | 53.11% | 52.17% | 32.71% | 53.15% | 52.2% | 32.71% | 53.6% | 52.48% | 32.85%
SW-Toowoomba Dalby Warwick | F2780_East Warwick No 1 33 kV | Limiting Line Name | TR_LINE 23896_1 | TR_LINE 23896_1 | TR_LINE 23896_1 | TR_LINE 23896_1 | TR_LINE 23896_1 | TR_LINE 23896_1 | TR_LINE 23896_1 | TR_LINE 23896_1 | TR_LINE 23896_1 | TR_LINE 23896_1 | TR_LINE 23896_1 | TR_LINE 23896_1 | TR_LINE 23896_1 | TR_LINE 23896_1 | TR_LINE 23896_1
SW-Toowoomba Dalby Warwick | F2780_East Warwick No 1 33 kV | Loading (A) | 286.0404 | 287.8175 | 157.8894 | 283.0699 | 284.8566 | 156.6413 | 281.5003 | 283.2868 | 156.0099 | 281.7006 | 283.4633 | 156.03 | 284.0791 | 284.9648 | 156.6937
SW-Toowoomba Dalby Warwick | F2780_East Warwick No 1 33 kV | Loading (MVA) | 16.8251 | 16.8518 | 9.4686 | 16.6494 | 16.675 | 9.393 | 16.5625 | 16.5876 | 9.3561 | 16.5605 | 16.5859 | 9.3543 | 16.607 | 16.6419 | 9.3884
SW-Toowoomba Dalby Warwick | F2780_East Warwick No 1 33 kV | Loading (MW) | 16.4931 | 16.5339 | 8.2664 | 16.3066 | 16.3469 | 8.1733 | 16.2132 | 16.2533 | 8.1268 | 16.2134 | 16.2534 | 8.1268 | 16.3084 | 16.3479 | 8.1733
SW-Toowoomba Dalby Warwick | F2780_East Warwick No 1 33 kV | Power Factor | 0.98019 | 0.98106 | 0.87295 | 0.97933 | 0.98024 | 0.87007 | 0.97883 | 0.97977 | 0.86852 | 0.97896 | 0.97988 | 0.86869 | 0.98195 | 0.98226 | 0.8705
SW-Toowoomba Dalby Warwick | F2780_East Warwick No 1 33 kV | Rating (A) | 530 | 543 | 477 | 530 | 543 | 477 | 530 | 543 | 477 | 530 | 543 | 477 | 530 | 543 | 477
SW-Toowoomba Dalby Warwick | F2780_East Warwick No 1 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Toowoomba Dalby Warwick | F2780_East Warwick No 1 33 kV | Min Voltage at Constrained Conductor | 33.9577 | 33.8014 | 34.6232 | 33.9557 | 33.7945 | 34.6203 | 33.9669 | 33.8037 | 34.624 | 33.9386 | 33.7792 | 34.6128 | 33.7487 | 33.7144 | 34.5918
SW-Toowoomba Dalby Warwick | F2780_East Warwick No 1 33 kV | Contingency Outage | F2785_East Warwick No 2 33 kV | F2785_East Warwick No 2 33 kV | F2785_East Warwick No 2 33 kV | F2785_East Warwick No 2 33 kV | F2785_East Warwick No 2 33 kV | F2785_East Warwick No 2 33 kV | F2785_East Warwick No 2 33 kV | F2785_East Warwick No 2 33 kV | F2785_East Warwick No 2 33 kV | F2785_East Warwick No 2 33 kV | F2785_East Warwick No 2 33 kV | F2785_East Warwick No 2 33 kV | F2785_East Warwick No 2 33 kV | F2785_East Warwick No 2 33 kV | F2785_East Warwick No 2 33 kV
SW-Toowoomba Dalby Warwick | F2785_East Warwick No 2 33 kV | % of Rated A | 53.97% | 53% | 33.1% | 53.41% | 52.46% | 32.83% | 53.11% | 52.17% | 32.7% | 53.15% | 52.2% | 32.71% | 53.6% | 52.48% | 32.85%
SW-Toowoomba Dalby Warwick | F2785_East Warwick No 2 33 kV | Limiting Line Name | TR_LINE 23891_1 | TR_LINE 23891_1 | TR_LINE 23891_1 | TR_LINE 23891_1 | TR_LINE 23891_1 | TR_LINE 23891_1 | TR_LINE 23891_1 | TR_LINE 23891_1 | TR_LINE 23891_1 | TR_LINE 23891_1 | TR_LINE 23891_1 | TR_LINE 23891_1 | TR_LINE 23891_1 | TR_LINE 23891_1 | TR_LINE 23891_1
SW-Toowoomba Dalby Warwick | F2785_East Warwick No 2 33 kV | Loading (A) | 286.0362 | 287.8137 | 157.8688 | 283.0653 | 284.8524 | 156.6205 | 281.4956 | 283.2824 | 155.989 | 281.6959 | 283.459 | 156.0091 | 284.0754 | 284.9613 | 156.6729
SW-Toowoomba Dalby Warwick | F2785_East Warwick No 2 33 kV | Loading (MVA) | 16.8247 | 16.8514 | 9.4673 | 16.649 | 16.6746 | 9.3917 | 16.5621 | 16.5872 | 9.3548 | 16.5601 | 16.5855 | 9.353 | 16.6066 | 16.6415 | 9.3871
SW-Toowoomba Dalby Warwick | F2785_East Warwick No 2 33 kV | Loading (MW) | 16.4935 | 16.5342 | 8.2664 | 16.3069 | 16.3472 | 8.1734 | 16.2135 | 16.2536 | 8.1268 | 16.2137 | 16.2538 | 8.1268 | 16.3087 | 16.3482 | 8.1734
SW-Toowoomba Dalby Warwick | F2785_East Warwick No 2 33 kV | Power Factor | 0.98022 | 0.98109 | 0.87306 | 0.97936 | 0.98028 | 0.87018 | 0.97886 | 0.9798 | 0.86864 | 0.979 | 0.97991 | 0.8688 | 0.98198 | 0.98229 | 0.87061
SW-Toowoomba Dalby Warwick | F2785_East Warwick No 2 33 kV | Rating (A) | 530 | 543 | 477 | 530 | 543 | 477 | 530 | 543 | 477 | 530 | 543 | 477 | 530 | 543 | 477
SW-Toowoomba Dalby Warwick | F2785_East Warwick No 2 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Toowoomba Dalby Warwick | F2785_East Warwick No 2 33 kV | Min Voltage at Constrained Conductor | 33.9569 | 33.8006 | 34.623 | 33.955 | 33.7938 | 34.62 | 33.9662 | 33.803 | 34.6237 | 33.9378 | 33.7784 | 34.6126 | 33.7479 | 33.7136 | 34.5916
SW-Toowoomba Dalby Warwick | F2785_East Warwick No 2 33 kV | Contingency Outage | F2780_East Warwick No 1 33 kV | F2780_East Warwick No 1 33 kV | F2780_East Warwick No 1 33 kV | F2780_East Warwick No 1 33 kV | F2780_East Warwick No 1 33 kV | F2780_East Warwick No 1 33 kV | F2780_East Warwick No 1 33 kV | F2780_East Warwick No 1 33 kV | F2780_East Warwick No 1 33 kV | F2780_East Warwick No 1 33 kV | F2780_East Warwick No 1 33 kV | F2780_East Warwick No 1 33 kV | F2780_East Warwick No 1 33 kV | F2780_East Warwick No 1 33 kV | F2780_East Warwick No 1 33 kV
SW-Toowoomba Dalby Warwick | F3040 Hampton Street | % of Rated A | 0.3084% | 0.3088% | 0.3091% | 0.3084% | 0.3089% | 0.3091% | 0.3084% | 0.3089% | 0.3091% | 0.3084% | 0.3088% | 0.3093% | 0.3068% | 0.3085% | 0.3092%
SW-Toowoomba Dalby Warwick | F3040 Hampton Street | Limiting Line Name | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1
SW-Toowoomba Dalby Warwick | F3040 Hampton Street | Loading (A) | 1.5418 | 1.5441 | 1.5454 | 1.5419 | 1.5444 | 1.5454 | 1.542 | 1.5446 | 1.5454 | 1.542 | 1.5438 | 1.5464 | 1.5338 | 1.5426 | 1.5458
SW-Toowoomba Dalby Warwick | F3040 Hampton Street | Loading (MVA) | 0.093119 | 0.093403 | 0.093552 | 0.093131 | 0.093437 | 0.093554 | 0.093148 | 0.093462 | 0.093555 | 0.09315 | 0.093362 | 0.093676 | 0.092155 | 0.093215 | 0.093601
SW-Toowoomba Dalby Warwick | F3040 Hampton Street | Loading (MW) | 0.0013123 | 0.0013163 | 0.0013184 | 0.0013125 | 0.0013168 | 0.0013185 | 0.0013127 | 0.0013172 | 0.0013185 | 0.0013128 | 0.0013158 | 0.0013202 | 0.0012987 | 0.0013137 | 0.0013191
SW-Toowoomba Dalby Warwick | F3040 Hampton Street | Power Factor | 0.011534 | 0.011534 | 0.011534 | 0.011534 | 0.011534 | 0.011534 | 0.011534 | 0.011534 | 0.011534 | 0.011534 | 0.011534 | 0.011534 | 0.011534 | 0.011534 | 0.011534
SW-Toowoomba Dalby Warwick | F3040 Hampton Street | Rating (A) | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500
SW-Toowoomba Dalby Warwick | F3040 Hampton Street | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Toowoomba Dalby Warwick | F3040 Hampton Street | Min Voltage at Constrained Conductor | 34.8701 | 34.9233 | 34.9511 | 34.8723 | 34.9296 | 34.9515 | 34.8757 | 34.9344 | 34.9518 | 34.876 | 34.9157 | 34.9744 | 34.6893 | 34.8881 | 34.9604
SW-Toowoomba Dalby Warwick | F3040 Hampton Street | Contingency Outage | F3820_Boundary Road 33 kV | F2520_Clifton 33 kV | F3867_Pampas 33 kV | F3820_Boundary Road 33 kV | F2520_Clifton 33 kV | F3867_Pampas 33 kV | F3820_Boundary Road 33 kV | F2520_Clifton 33 kV | F3867_Pampas 33 kV | F3820_Boundary Road 33 kV | F2520_Clifton 33 kV | 730_Middle Ridge-South Toowoomba 110 kV | F3820_Boundary Road 33 kV | F3820_Boundary Road 33 kV | 730_Middle Ridge-South Toowoomba 110 kV
SW-Toowoomba Dalby Warwick | F3095_Highfields 33 kV | % of Rated A | 48.75% | 37.99% | 19.93% | 48.75% | 37.99% | 19.93% | 48.73% | 37.97% | 19.92% | 48.09% | 38% | 19.93% | 21.7% | 17.75% | 10.09%
SW-Toowoomba Dalby Warwick | F3095_Highfields 33 kV | Limiting Line Name | TR_LINE 194642_1 | TR_LINE 194642_1 | TR_LINE 194642_1 | TR_LINE 194642_1 | TR_LINE 194642_1 | TR_LINE 194642_1 | TR_LINE 194642_1 | TR_LINE 194642_1 | TR_LINE 194642_1 | TR_LINE 194642_1 | TR_LINE 194642_1 | TR_LINE 194642_1 | TR_LINE 194642_1 | TR_LINE 194642_1 | TR_LINE 194642_1
SW-Toowoomba Dalby Warwick | F3095_Highfields 33 kV | Loading (A) | 82.3875 | 91.1698 | 46.6412 | 82.3836 | 91.1768 | 46.6409 | 82.346 | 91.136 | 46.6241 | 81.2676 | 91.1963 | 46.638 | 36.6739 | 42.591 | 23.6188
SW-Toowoomba Dalby Warwick | F3095_Highfields 33 kV | Loading (MVA) | 4.763 | 5.2675 | 2.7386 | 4.763 | 5.2675 | 2.7386 | 4.7614 | 5.2657 | 2.7377 | 4.757 | 5.266 | 2.7377 | 2.1256 | 2.4801 | 1.3882
SW-Toowoomba Dalby Warwick | F3095_Highfields 33 kV | Loading (MW) | 4.52 | 5.0106 | 2.5864 | 4.52 | 5.0106 | 2.5864 | 4.5216 | 5.0125 | 2.5872 | 4.5191 | 5.0126 | 2.5873 | 2.0239 | 2.3749 | 1.2871
SW-Toowoomba Dalby Warwick | F3095_Highfields 33 kV | Power Factor | 0.94899 | 0.95123 | 0.94432 | 0.94899 | 0.95122 | 0.94432 | 0.94963 | 0.95191 | 0.94493 | 0.95 | 0.95188 | 0.94492 | 0.95199 | 0.95745 | 0.92694
SW-Toowoomba Dalby Warwick | F3095_Highfields 33 kV | Rating (A) | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234
SW-Toowoomba Dalby Warwick | F3095_Highfields 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Toowoomba Dalby Warwick | F3095_Highfields 33 kV | Min Voltage at Constrained Conductor | 33.3513 | 33.3273 | 33.8903 | 33.3527 | 33.3249 | 33.8906 | 33.3571 | 33.3285 | 33.8918 | 33.7693 | 33.3083 | 33.8824 | 33.4589 | 33.6122 | 33.9343
SW-Toowoomba Dalby Warwick | F3095_Highfields 33 kV | Contingency Outage | 7234_Middle Ridge-Torrington 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | 7449 South Toowoomba-TWCE 110 kV | 7234_Middle Ridge-Torrington 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | 7449 South Toowoomba-TWCE 110 kV | 7234_Middle Ridge-Torrington 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | 7449 South Toowoomba-TWCE 110 kV | 7234_Middle Ridge-Torrington 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | 7449 South Toowoomba-TWCE 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F4132_Shirley Road 33 kV
SW-Toowoomba Dalby Warwick | F3253_Jellicoe Street 33 kV | % of Rated A | 0.9559% | 0.6813% | 0.5921% | 0.9561% | 0.6815% | 0.5922% | 0.952% | 0.6815% | 0.5922% | 0.9499% | 0.6769% | 0.5898% | 0.9491% | 0.6769% | 0.587%
SW-Toowoomba Dalby Warwick | F3253_Jellicoe Street 33 kV | Limiting Line Name | TR_LINE 23977_2 | TR_LINE 23977_2 | TR_LINE 23977_2 | TR_LINE 23977_2 | TR_LINE 23977_2 | TR_LINE 23977_2 | TR_LINE 23977_2 | TR_LINE 23977_2 | TR_LINE 23977_2 | TR_LINE 23977_2 | TR_LINE 23977_2 | TR_LINE 23977_2 | TR_LINE 23977_2 | TR_LINE 23977_2 | TR_LINE 23977_2
SW-Toowoomba Dalby Warwick | F3253_Jellicoe Street 33 kV | Loading (A) | 2.1126 | 2.1255 | 2.1374 | 2.113 | 2.1262 | 2.1378 | 2.1039 | 2.1264 | 2.1379 | 2.0992 | 2.1118 | 2.1292 | 2.0975 | 2.1121 | 2.119
SW-Toowoomba Dalby Warwick | F3253_Jellicoe Street 33 kV | Loading (MVA) | 0.1226 | 0.12411 | 0.1255 | 0.12265 | 0.12419 | 0.12555 | 0.1216 | 0.12422 | 0.12557 | 0.12106 | 0.12252 | 0.12454 | 0.12087 | 0.12255 | 0.12335
SW-Toowoomba Dalby Warwick | F3253_Jellicoe Street 33 kV | Loading (MW) | 0.0021718 | 0.0021986 | 0.0022232 | 0.0021727 | 0.0021999 | 0.002224 | 0.002154 | 0.0022004 | 0.0022243 | 0.0021445 | 0.0021703 | 0.0022062 | 0.0021411 | 0.0021708 | 0.002185
SW-Toowoomba Dalby Warwick | F3253_Jellicoe Street 33 kV | Power Factor | 0.017714 | 0.017714 | 0.017714 | 0.017714 | 0.017714 | 0.017714 | 0.017714 | 0.017714 | 0.017714 | 0.017714 | 0.017714 | 0.017714 | 0.017714 | 0.017714 | 0.017714
SW-Toowoomba Dalby Warwick | F3253_Jellicoe Street 33 kV | Rating (A) | 221 | 312 | 361 | 221 | 312 | 361 | 221 | 312 | 361 | 221 | 312 | 361 | 221 | 312 | 361
SW-Toowoomba Dalby Warwick | F3253_Jellicoe Street 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Toowoomba Dalby Warwick | F3253_Jellicoe Street 33 kV | Min Voltage at Constrained Conductor | 33.507 | 33.7127 | 33.9006 | 33.5136 | 33.7229 | 33.9071 | 33.369 | 33.7267 | 33.9092 | 33.2951 | 33.495 | 33.7711 | 33.2688 | 33.4992 | 33.6083
SW-Toowoomba Dalby Warwick | F3253_Jellicoe Street 33 kV | Contingency Outage | 7234_Middle Ridge-Torrington 110 kV | F4132_Shirley Road 33 kV | F4132_Shirley Road 33 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F4132_Shirley Road 33 kV | F4132_Shirley Road 33 kV | F4132_Shirley Road 33 kV | F4132_Shirley Road 33 kV | F4132_Shirley Road 33 kV | F2450_Carrington Road 33 kV | F4132_Shirley Road 33 kV | F4132_Shirley Road 33 kV | F4132_Shirley Road 33 kV | F3910_Perseverence Creek 1 33 kV | F4132_Shirley Road 33 kV
SW-Toowoomba Dalby Warwick | F3255_Jennings Street 33 kV | % of Rated A | 68.2% | 59.7% | 28.21% | 67.53% | 59.14% | 27.96% | 67.2% | 58.86% | 27.84% | 67.26% | 58.91% | 27.85% | 68.45% | 59.53% | 28.11%
SW-Toowoomba Dalby Warwick | F3255_Jennings Street 33 kV | Limiting Line Name | TR_CABLE 7923_1 | TR_CABLE 7923_1 | TR_CABLE 7923_1 | TR_CABLE 7923_1 | TR_CABLE 7923_1 | TR_CABLE 7923_1 | TR_CABLE 7923_1 | TR_CABLE 7923_1 | TR_CABLE 7923_1 | TR_CABLE 7923_1 | TR_CABLE 7923_1 | TR_CABLE 7923_1 | TR_CABLE 7923_1 | TR_CABLE 7923_1 | TR_CABLE 7923_1
SW-Toowoomba Dalby Warwick | F3255_Jennings Street 33 kV | Loading (A) | 420.7647 | 368.3286 | 174.0781 | 416.6822 | 364.9005 | 172.534 | 414.6133 | 363.1801 | 171.7624 | 414.9668 | 363.4459 | 171.8138 | 422.3338 | 367.2884 | 173.4283
SW-Toowoomba Dalby Warwick | F3255_Jennings Street 33 kV | Loading (MVA) | 24.8274 | 21.8406 | 10.4558 | 24.5952 | 21.6401 | 10.364 | 24.479 | 21.5399 | 10.3181 | 24.4821 | 21.5418 | 10.3183 | 24.7433 | 21.7454 | 10.4103
SW-Toowoomba Dalby Warwick | F3255_Jennings Street 33 kV | Loading (MW) | 23.3924 | 20.7262 | 10.1645 | 23.1898 | 20.5471 | 10.0772 | 23.0884 | 20.4575 | 10.0335 | 23.0889 | 20.4578 | 10.0335 | 23.2953 | 20.6373 | 10.1209
SW-Toowoomba Dalby Warwick | F3255_Jennings Street 33 kV | Power Factor | 0.94196 | 0.94875 | 0.97198 | 0.94262 | 0.94927 | 0.97217 | 0.94295 | 0.94953 | 0.97226 | 0.94285 | 0.94946 | 0.97225 | 0.94123 | 0.94883 | 0.97205
SW-Toowoomba Dalby Warwick | F3255_Jennings Street 33 kV | Rating (A) | 617 | 617 | 617 | 617 | 617 | 617 | 617 | 617 | 617 | 617 | 617 | 617 | 617 | 617 | 617
SW-Toowoomba Dalby Warwick | F3255_Jennings Street 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Toowoomba Dalby Warwick | F3255_Jennings Street 33 kV | Min Voltage at Constrained Conductor | 34.0668 | 34.2349 | 34.6778 | 34.0788 | 34.2392 | 34.681 | 34.0871 | 34.2421 | 34.6826 | 34.0623 | 34.2202 | 34.6727 | 33.8252 | 34.1821 | 34.6562
SW-Toowoomba Dalby Warwick | F3255_Jennings Street 33 kV | Contingency Outage | F4015_Ramsay Street 33 kV | F4015_Ramsay Street 33 kV | F4015_Ramsay Street 33 kV | F4015_Ramsay Street 33 kV | F4015_Ramsay Street 33 kV | F4015_Ramsay Street 33 kV | F4015_Ramsay Street 33 kV | F4015_Ramsay Street 33 kV | F4015_Ramsay Street 33 kV | F4015_Ramsay Street 33 kV | F4015_Ramsay Street 33 kV | F4015_Ramsay Street 33 kV | F4015_Ramsay Street 33 kV | F4015_Ramsay Street 33 kV | F4015_Ramsay Street 33 kV
SW-Toowoomba Dalby Warwick | F3315_Sladevale 2 33kV | % of Rated A | 7.14% | 7.343% | 6.917% | 7.14% | 7.359% | 6.916% | 7.141% | 7.345% | 6.917% | 7.138% | 7.358% | 6.915% | 7.151% | 7.353% | 6.911%
SW-Toowoomba Dalby Warwick | F3315_Sladevale 2 33kV | Limiting Line Name | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1
SW-Toowoomba Dalby Warwick | F3315_Sladevale 2 33kV | Loading (A) | 45.3377 | 46.6311 | 43.9226 | 45.3364 | 46.7293 | 43.9165 | 45.3447 | 46.6422 | 43.922 | 45.3235 | 46.7207 | 43.9083 | 45.4061 | 46.6897 | 43.8832
SW-Toowoomba Dalby Warwick | F3315_Sladevale 2 33kV | Loading (MVA) | 2.683 | 2.7463 | 2.6707 | 2.6828 | 2.7654 | 2.6699 | 2.6841 | 2.7485 | 2.6706 | 2.6807 | 2.7638 | 2.6689 | 2.694 | 2.7574 | 2.6657
SW-Toowoomba Dalby Warwick | F3315_Sladevale 2 33kV | Loading (MW) | 1.5911 | 1.8053 | 1.0019 | 1.5911 | 1.8048 | 1.0019 | 1.591 | 1.8053 | 1.0019 | 1.5911 | 1.8048 | 1.0019 | 1.5908 | 1.805 | 1.0019
SW-Toowoomba Dalby Warwick | F3315_Sladevale 2 33kV | Power Factor | 0.59302 | 0.65736 | 0.37513 | 0.59307 | 0.65263 | 0.37524 | 0.59276 | 0.65682 | 0.37514 | 0.59354 | 0.65304 | 0.37539 | 0.59051 | 0.6546 | 0.37585
SW-Toowoomba Dalby Warwick | F3315_Sladevale 2 33kV | Rating (A) | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635 | 635
SW-Toowoomba Dalby Warwick | F3315_Sladevale 2 33kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Toowoomba Dalby Warwick | F3315_Sladevale 2 33kV | Min Voltage at Constrained Conductor | 34.1661 | 34.003 | 35.1055 | 34.1644 | 34.1675 | 35.1002 | 34.1753 | 34.0218 | 35.105 | 34.1475 | 34.1533 | 35.0929 | 34.2552 | 34.0977 | 35.0708
SW-Toowoomba Dalby Warwick | F3315_Sladevale 2 33kV | Contingency Outage | F3970_Pozieres 33 kV | F4245_Stanthorpe 33 kV | F5560_735(Middle Ridge-Warwick) 110 kV | F3970_Pozieres 33 kV | 3283_Allora 33kV | F5560_735(Middle Ridge-Warwick) 110 kV | F3970_Pozieres 33 kV | F4245_Stanthorpe 33 kV | F5560_735(Middle Ridge-Warwick) 110 kV | F3970_Pozieres 33 kV | 3283_Allora 33kV | F5560_735(Middle Ridge-Warwick) 110 kV | F4605_West Warwick 33 kV | 3283_Allora 33kV | F5560_735(Middle Ridge-Warwick) 110 kV
SW-Toowoomba Dalby Warwick | F3530_Millmerran 33 kV | % of Rated A | 44.48% | 33.4% | 15.25% | 43.24% | 32.44% | 14.83% | 43.24% | 32.44% | 14.83% | 43.24% | 32.44% | 14.73% | 44.71% | 33.29% | 15.14%
SW-Toowoomba Dalby Warwick | F3530_Millmerran 33 kV | Limiting Line Name | TR_LINE 23295_1 | TR_LINE 23295_1 | TR_LINE 23295_1 | TR_LINE 23295_1 | TR_LINE 23295_1 | TR_LINE 23295_1 | TR_LINE 23295_1 | TR_LINE 23295_1 | TR_LINE 23295_1 | TR_LINE 23295_1 | TR_LINE 23295_1 | TR_LINE 23295_1 | TR_LINE 23295_1 | TR_LINE 23295_1 | TR_LINE 23295_1
SW-Toowoomba Dalby Warwick | F3530_Millmerran 33 kV | Loading (A) | 56.4916 | 60.1182 | 26.6788 | 54.9184 | 58.3912 | 25.9464 | 54.9134 | 58.3895 | 25.946 | 54.9103 | 58.3932 | 25.7701 | 56.7764 | 59.9222 | 26.4957
SW-Toowoomba Dalby Warwick | F3530_Millmerran 33 kV | Loading (MVA) | 3.2706 | 3.4786 | 1.5308 | 3.1783 | 3.3799 | 1.4885 | 3.1782 | 3.3799 | 1.4885 | 3.1782 | 3.3799 | 1.4881 | 3.2714 | 3.4775 | 1.5304
SW-Toowoomba Dalby Warwick | F3530_Millmerran 33 kV | Loading (MW) | 3.2365 | 3.4398 | 1.5257 | 3.1463 | 3.3436 | 1.4839 | 3.1462 | 3.3436 | 1.4839 | 3.1462 | 3.3436 | 1.4836 | 3.2373 | 3.4391 | 1.5254
SW-Toowoomba Dalby Warwick | F3530_Millmerran 33 kV | Power Factor | 0.9893 | 0.98887 | 0.99193 | 0.98945 | 0.98925 | 0.99199 | 0.98945 | 0.98925 | 0.99199 | 0.98945 | 0.98925 | 0.99202 | 0.98938 | 0.98895 | 0.99196
SW-Toowoomba Dalby Warwick | F3530_Millmerran 33 kV | Rating (A) | 127 | 180 | 175 | 127 | 180 | 175 | 127 | 180 | 175 | 127 | 180 | 175 | 127 | 180 | 175
SW-Toowoomba Dalby Warwick | F3530_Millmerran 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Toowoomba Dalby Warwick | F3530_Millmerran 33 kV | Min Voltage at Constrained Conductor | 32.4818 | 32.3849 | 32.8391 | 32.5025 | 32.4341 | 32.8506 | 32.5054 | 32.435 | 32.8511 | 32.5072 | 32.433 | 33.074 | 32.3153 | 32.4893 | 33.0646
SW-Toowoomba Dalby Warwick | F3530_Millmerran 33 kV | Contingency Outage | F3820_Boundary Road 33 kV | F3910_Perseverence Creek 1 33 kV | F2460_Cecil Plains 33 kV | F3820_Boundary Road 33 kV | F3820_Boundary Road 33 kV | F2460_Cecil Plains 33 kV | F3820_Boundary Road 33 kV | F3820_Boundary Road 33 kV | F2460_Cecil Plains 33 kV | F3820_Boundary Road 33 kV | F3820_Boundary Road 33 kV | F2450_Carrington Road 33 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F2460_Cecil Plains 33 kV | F3820_Boundary Road 33 kV
SW-Toowoomba Dalby Warwick | F3815 North Street No 1 33 kV | % of Rated A | 1.315% | 0.9872% | 1.038% | 1.315% | 0.9872% | 1.038% | 1.315% | 0.9872% | 1.038% | 1.328% | 0.9867% | 1.037% | 1.318% | 0.9865% | 1.037%
SW-Toowoomba Dalby Warwick | F3815 North Street No 1 33 kV | Limiting Line Name | TR_LINE 181524_1 | TR_LINE 181524_1 | TR_LINE 181524_1 | TR_LINE 181524_1 | TR_LINE 181524_1 | TR_LINE 181524_1 | TR_LINE 181524_1 | TR_LINE 181524_1 | TR_LINE 181524_1 | TR_LINE 181524_1 | TR_LINE 181524_1 | TR_LINE 181524_1 | TR_LINE 181524_1 | TR_LINE 181524_1 | TR_LINE 181524_1
SW-Toowoomba Dalby Warwick | F3815 North Street No 1 33 kV | Loading (A) | 2.3272 | 2.3298 | 2.3451 | 2.3273 | 2.3298 | 2.3451 | 2.3275 | 2.3298 | 2.3451 | 2.3501 | 2.3285 | 2.3445 | 2.3328 | 2.3281 | 2.3439
SW-Toowoomba Dalby Warwick | F3815 North Street No 1 33 kV | Loading (MVA) | 0.1371 | 0.13741 | 0.13921 | 0.13711 | 0.13741 | 0.13922 | 0.13713 | 0.13741 | 0.13922 | 0.13982 | 0.13726 | 0.13915 | 0.13776 | 0.13721 | 0.13908
SW-Toowoomba Dalby Warwick | F3815 North Street No 1 33 kV | Loading (MW) | 0.00043772 | 0.00043871 | 0.00044447 | 0.00043776 | 0.00043869 | 0.00044448 | 0.00043782 | 0.00043871 | 0.00044449 | 0.00044639 | 0.00043823 | 0.00044425 | 0.00043982 | 0.00043807 | 0.00044403
SW-Toowoomba Dalby Warwick | F3815 North Street No 1 33 kV | Power Factor | 0.0031927 | 0.0031927 | 0.0031927 | 0.0031927 | 0.0031927 | 0.0031927 | 0.0031927 | 0.0031927 | 0.0031927 | 0.0031927 | 0.0031927 | 0.0031927 | 0.0031927 | 0.0031927 | 0.0031927
SW-Toowoomba Dalby Warwick | F3815 North Street No 1 33 kV | Rating (A) | 177 | 236 | 226 | 177 | 236 | 226 | 177 | 236 | 226 | 177 | 236 | 226 | 177 | 236 | 226
SW-Toowoomba Dalby Warwick | F3815 North Street No 1 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Toowoomba Dalby Warwick | F3815 North Street No 1 33 kV | Min Voltage at Constrained Conductor | 34.0133 | 34.0516 | 34.2744 | 34.0149 | 34.051 | 34.2747 | 34.0171 | 34.0517 | 34.2752 | 34.3485 | 34.0329 | 34.2659 | 34.0945 | 34.0269 | 34.2575
SW-Toowoomba Dalby Warwick | F3815 North Street No 1 33 kV | Contingency Outage | F3910_Perseverence Creek 1 33 kV | F3910_Perseverence Creek 1 33 kV | F3910_Perseverence Creek 1 33 kV | F3910_Perseverence Creek 1 33 kV | F3910_Perseverence Creek 1 33 kV | F3910_Perseverence Creek 1 33 kV | F3910_Perseverence Creek 1 33 kV | F3910_Perseverence Creek 1 33 kV | F3910_Perseverence Creek 1 33 kV | F3820_Boundary Road 33 kV | F3910_Perseverence Creek 1 33 kV | F3910_Perseverence Creek 1 33 kV | F4132_Shirley Road 33 kV | F3910_Perseverence Creek 1 33 kV | F3910_Perseverence Creek 1 33 kV
SW-Toowoomba Dalby Warwick | F3820_Boundary Road 33 kV | % of Rated A | 44.27% | 33.44% | 21.63% | 43.71% | 33.01% | 21.38% | 43.71% | 33% | 21.38% | 55.77% | 42.31% | 27.07% | 69.03% | 52.21% | 33.53%
SW-Toowoomba Dalby Warwick | F3820_Boundary Road 33 kV | Limiting Line Name | TR_CABLE 73_1 | TR_CABLE 73_1 | TR_CABLE 172_1 | TR_CABLE 73_1 | TR_CABLE 73_1 | TR_CABLE 172_1 | TR_CABLE 73_1 | TR_CABLE 73_1 | TR_CABLE 172_1 | TR_CABLE 73_1 | TR_CABLE 73_1 | TR_CABLE 73_1 | TR_CABLE 73_1 | TR_CABLE 73_1 | TR_CABLE 73_1
SW-Toowoomba Dalby Warwick | F3820_Boundary Road 33 kV | Loading (A) | 305.4683 | 230.7016 | 152.7232 | 301.6278 | 227.7848 | 150.928 | 301.5693 | 227.7152 | 150.9081 | 384.8143 | 291.9697 | 186.79 | 476.3316 | 360.2256 | 231.3871
SW-Toowoomba Dalby Warwick | F3820_Boundary Road 33 kV | Loading (MVA) | 17.7984 | 13.4406 | 8.8402 | 17.5798 | 13.2764 | 8.7389 | 17.5794 | 13.276 | 8.7388 | 22.4616 | 17.0474 | 11.0102 | 27.8659 | 21.0155 | 13.5369
SW-Toowoomba Dalby Warwick | F3820_Boundary Road 33 kV | Loading (MW) | 16.2846 | 12.4843 | 8.1637 | 16.0936 | 12.3385 | 8.0695 | 16.0935 | 12.3385 | 8.0695 | 20.3137 | 15.5577 | 10.2253 | 24.9256 | 19.0698 | 12.5208
SW-Toowoomba Dalby Warwick | F3820_Boundary Road 33 kV | Power Factor | 0.9146 | 0.92856 | 0.92339 | 0.91512 | 0.92907 | 0.92332 | 0.91514 | 0.92909 | 0.92332 | 0.90397 | 0.91228 | 0.92845 | 0.894 | 0.90703 | 0.92465
SW-Toowoomba Dalby Warwick | F3820_Boundary Road 33 kV | Rating (A) | 690 | 690 | 706 | 690 | 690 | 706 | 690 | 690 | 706 | 690 | 690 | 690 | 690 | 690 | 690
SW-Toowoomba Dalby Warwick | F3820_Boundary Road 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Toowoomba Dalby Warwick | F3820_Boundary Road 33 kV | Min Voltage at Constrained Conductor | 33.6399 | 33.6362 | 33.4192 | 33.6497 | 33.6508 | 33.4291 | 33.6555 | 33.6601 | 33.4333 | 33.7 | 33.7101 | 34.0314 | 33.7756 | 33.6826 | 33.7769
SW-Toowoomba Dalby Warwick | F3820_Boundary Road 33 kV | Contingency Outage | F3253_Jellicoe Street 33 kV | 7233_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV | F3253_Jellicoe Street 33 kV | 7233_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV | F3253_Jellicoe Street 33 kV | 7233_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV | F3253_Jellicoe Street 33 kV | F3253_Jellicoe Street 33 kV | 7234_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV
SW-Toowoomba Dalby Warwick | F3830_Norwin 33 kV | % of Rated A | 16.01% | 17.21% | 34.62% | 15.48% | 16.65% | 33.45% | 15.48% | 16.65% | 33.45% | 15.49% | 16.66% | 33.46% | 15.94% | 17.26% | 34.47%
SW-Toowoomba Dalby Warwick | F3830_Norwin 33 kV | Limiting Line Name | TR_CABLE 175_1 | TR_CABLE 175_1 | TR_CABLE 175_1 | TR_CABLE 175_1 | TR_CABLE 175_1 | TR_CABLE 175_1 | TR_CABLE 175_1 | TR_CABLE 175_1 | TR_CABLE 175_1 | TR_CABLE 175_1 | TR_CABLE 175_1 | TR_CABLE 175_1 | TR_CABLE 175_1 | TR_CABLE 175_1 | TR_CABLE 175_1
SW-Toowoomba Dalby Warwick | F3830_Norwin 33 kV | Loading (A) | 18.569 | 19.9616 | 40.1579 | 17.9604 | 19.3189 | 38.7984 | 17.959 | 19.3182 | 38.7977 | 17.9718 | 19.3312 | 38.8092 | 18.495 | 20.0201 | 39.9904
SW-Toowoomba Dalby Warwick | F3830_Norwin 33 kV | Loading (MVA) | 1.0466 | 1.1257 | 2.2044 | 1.0126 | 1.0891 | 2.1323 | 1.0126 | 1.0891 | 2.1323 | 1.0126 | 1.0891 | 2.1323 | 1.0465 | 1.1257 | 2.2047
SW-Toowoomba Dalby Warwick | F3830_Norwin 33 kV | Loading (MW) | 0.8454 | 0.90891 | 1.7701 | 0.81812 | 0.87958 | 1.713 | 0.81812 | 0.87958 | 1.713 | 0.81812 | 0.87958 | 1.713 | 0.84539 | 0.90892 | 1.7702
SW-Toowoomba Dalby Warwick | F3830_Norwin 33 kV | Power Factor | 0.80764 | 0.80731 | 0.80294 | 0.80779 | 0.80746 | 0.80326 | 0.80779 | 0.80747 | 0.80326 | 0.80778 | 0.80746 | 0.80326 | 0.80768 | 0.80729 | 0.80282
SW-Toowoomba Dalby Warwick | F3830_Norwin 33 kV | Rating (A) | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116
SW-Toowoomba Dalby Warwick | F3830_Norwin 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Toowoomba Dalby Warwick | F3830_Norwin 33 kV | Min Voltage at Constrained Conductor | 32.5408 | 32.5581 | 31.6923 | 32.5515 | 32.5494 | 31.7306 | 32.5541 | 32.5504 | 31.7311 | 32.5311 | 32.5287 | 31.722 | 32.6688 | 32.4643 | 31.8304
SW-Toowoomba Dalby Warwick | F3830_Norwin 33 kV | Contingency Outage | F5555_734(Middle Ridge-Yarranlea) 110 kV | F2460_Cecil Plains 33 kV | F2460_Cecil Plains 33 kV | F2460_Cecil Plains 33 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F2460_Cecil Plains 33 kV | F2460_Cecil Plains 33 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F2460_Cecil Plains 33 kV | F2460_Cecil Plains 33 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F2460_Cecil Plains 33 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F2460_Cecil Plains 33 kV | 7448_South Toowoomba-TWCE 110 kV
SW-Toowoomba Dalby Warwick | F3855 Omaras Road 33 kV | % of Rated A | 16.54% | 15.64% | 17.37% | 16.53% | 15.63% | 17.36% | 16.54% | 15.63% | 17.36% | 16.49% | 15.63% | 17.29% | 16.45% | 15.62% | 17.31%
SW-Toowoomba Dalby Warwick | F3855 Omaras Road 33 kV | Limiting Line Name | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1
SW-Toowoomba Dalby Warwick | F3855 Omaras Road 33 kV | Loading (A) | 38.531 | 36.4411 | 40.4685 | 38.5219 | 36.4252 | 40.4604 | 38.5267 | 36.4151 | 40.4553 | 38.4244 | 36.4081 | 40.2912 | 38.3328 | 36.384 | 40.3365
SW-Toowoomba Dalby Warwick | F3855 Omaras Road 33 kV | Loading (MVA) | 2.2337 | 2.1145 | 2.3492 | 2.2337 | 2.1145 | 2.3492 | 2.2337 | 2.1145 | 2.3492 | 2.2337 | 2.1145 | 2.3493 | 2.2337 | 2.1145 | 2.3493
SW-Toowoomba Dalby Warwick | F3855 Omaras Road 33 kV | Loading (MW) | 1.9795 | 1.8738 | 2.0818 | 1.9795 | 1.8738 | 2.0818 | 1.9795 | 1.8738 | 2.0818 | 1.9795 | 1.8738 | 2.0818 | 1.9795 | 1.8738 | 2.0818
SW-Toowoomba Dalby Warwick | F3855 Omaras Road 33 kV | Power Factor | 0.886 | 0.886 | 0.886 | 0.886 | 0.886 | 0.886 | 0.886 | 0.886 | 0.886 | 0.886 | 0.886 | 0.886 | 0.886 | 0.886 | 0.886
SW-Toowoomba Dalby Warwick | F3855 Omaras Road 33 kV | Rating (A) | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233 | 233
SW-Toowoomba Dalby Warwick | F3855 Omaras Road 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Toowoomba Dalby Warwick | F3855 Omaras Road 33 kV | Min Voltage at Constrained Conductor | 33.4706 | 33.5008 | 33.5159 | 33.4785 | 33.5154 | 33.5227 | 33.4744 | 33.5248 | 33.5269 | 33.5634 | 33.5312 | 33.6635 | 33.6437 | 33.5534 | 33.6256
SW-Toowoomba Dalby Warwick | F3855 Omaras Road 33 kV | Contingency Outage | F3980_Purrawunda 33 kV | 7233_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV | 7233_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | 7233_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F3820_Boundary Road 33 kV | 7234_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV
SW-Toowoomba Dalby Warwick | F3867_Pampas 33 kV | % of Rated A | 57.94% | 59.23% | 40.84% | 57.37% | 58.65% | 40.59% | 57.37% | 58.65% | 40.59% | 57.39% | 58.68% | 40.58% | 57.72% | 59.4% | 40.64%
SW-Toowoomba Dalby Warwick | F3867_Pampas 33 kV | Limiting Line Name | TR_CABLE 106_1 | TR_CABLE 106_1 | TR_LINE 23248_1 | TR_CABLE 106_1 | TR_CABLE 106_1 | TR_LINE 23248_1 | TR_CABLE 106_1 | TR_CABLE 106_1 | TR_LINE 23248_1 | TR_CABLE 106_1 | TR_CABLE 106_1 | TR_LINE 23248_1 | TR_CABLE 106_1 | TR_CABLE 106_1 | TR_LINE 23248_1
SW-Toowoomba Dalby Warwick | F3867_Pampas 33 kV | Loading (A) | 173.8057 | 177.6789 | 120.0659 | 172.1198 | 175.9625 | 119.3302 | 172.104 | 175.9564 | 119.3282 | 172.185 | 176.0327 | 119.3148 | 173.1657 | 178.1917 | 119.4813
SW-Toowoomba Dalby Warwick | F3867_Pampas 33 kV | Loading (MVA) | 9.4278 | 9.645 | 6.6059 | 9.336 | 9.5472 | 6.5649 | 9.336 | 9.5472 | 6.5649 | 9.3336 | 9.5448 | 6.5625 | 9.4308 | 9.6431 | 6.6018
SW-Toowoomba Dalby Warwick | F3867_Pampas 33 kV | Loading (MW) | 8.6098 | 8.8218 | 5.9621 | 8.5194 | 8.7257 | 5.9202 | 8.5194 | 8.7256 | 5.9202 | 8.5192 | 8.7255 | 5.9196 | 8.6116 | 8.8221 | 5.9612
SW-Toowoomba Dalby Warwick | F3867_Pampas 33 kV | Power Factor | 0.91313 | 0.91455 | 0.90254 | 0.91244 | 0.91385 | 0.90181 | 0.91244 | 0.91386 | 0.90181 | 0.91265 | 0.91406 | 0.90204 | 0.91304 | 0.91477 | 0.90296
SW-Toowoomba Dalby Warwick | F3867_Pampas 33 kV | Rating (A) | 300 | 300 | 294 | 300 | 300 | 294 | 300 | 300 | 294 | 300 | 300 | 294 | 300 | 300 | 294
SW-Toowoomba Dalby Warwick | F3867_Pampas 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Toowoomba Dalby Warwick | F3867_Pampas 33 kV | Min Voltage at Constrained Conductor | 31.3174 | 31.3404 | 31.7645 | 31.3163 | 31.3253 | 31.7617 | 31.319 | 31.3263 | 31.7622 | 31.2964 | 31.305 | 31.7542 | 31.4432 | 31.244 | 31.9001
SW-Toowoomba Dalby Warwick | F3867_Pampas 33 kV | Contingency Outage | F5550_733(Middle Ridge-Yarranlea) 110 kV | F2460_Cecil Plains 33 kV | F2460_Cecil Plains 33 kV | F2460_Cecil Plains 33 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F2460_Cecil Plains 33 kV | F2460_Cecil Plains 33 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F2460_Cecil Plains 33 kV | F2460_Cecil Plains 33 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F2460_Cecil Plains 33 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F2460_Cecil Plains 33 kV | 7449 South Toowoomba-TWCE 110 kV
SW-Toowoomba Dalby Warwick | F3910_Perseverence Creek 1 33 kV | % of Rated A | 42.69% | 32.47% | 19.81% | 42.69% | 32.47% | 19.81% | 42.68% | 32.46% | 19.81% | 42.12% | 32.48% | 19.81% | 42.12% | 32.48% | 19.81%
SW-Toowoomba Dalby Warwick | F3910_Perseverence Creek 1 33 kV | Limiting Line Name | TR_LINE 187299_1 | TR_LINE 187299_1 | TR_LINE 187299_1 | TR_LINE 187299_1 | TR_LINE 187299_1 | TR_LINE 187299_1 | TR_LINE 187299_1 | TR_LINE 187299_1 | TR_LINE 187299_1 | TR_LINE 187299_1 | TR_LINE 187299_1 | TR_LINE 187299_1 | TR_LINE 187299_1 | TR_LINE 187299_1 | TR_LINE 187299_1
SW-Toowoomba Dalby Warwick | F3910_Perseverence Creek 1 33 kV | Loading (A) | 72.1534 | 77.916 | 46.3534 | 72.15 | 77.9221 | 46.3531 | 72.1291 | 77.9004 | 46.3451 | 71.1769 | 77.9525 | 46.359 | 71.1769 | 77.9525 | 46.359
SW-Toowoomba Dalby Warwick | F3910_Perseverence Creek 1 33 kV | Loading (MVA) | 4.0497 | 4.3615 | 2.6686 | 4.0497 | 4.3615 | 2.6686 | 4.0491 | 4.3607 | 2.6682 | 4.0481 | 4.3608 | 2.6683 | 4.0481 | 4.3608 | 2.6683
SW-Toowoomba Dalby Warwick | F3910_Perseverence Creek 1 33 kV | Loading (MW) | 3.924 | 4.2334 | 2.5618 | 3.924 | 4.2334 | 2.5618 | 3.924 | 4.2334 | 2.5619 | 3.9235 | 4.2335 | 2.5619 | 3.9235 | 4.2335 | 2.5619
SW-Toowoomba Dalby Warwick | F3910_Perseverence Creek 1 33 kV | Power Factor | 0.96895 | 0.97063 | 0.96 | 0.96895 | 0.97063 | 0.96 | 0.9691 | 0.9708 | 0.96014 | 0.96923 | 0.97079 | 0.96013 | 0.96923 | 0.97079 | 0.96013
SW-Toowoomba Dalby Warwick | F3910_Perseverence Creek 1 33 kV | Rating (A) | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234 | 169 | 240 | 234
SW-Toowoomba Dalby Warwick | F3910_Perseverence Creek 1 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Toowoomba Dalby Warwick | F3910_Perseverence Creek 1 33 kV | Min Voltage at Constrained Conductor | 32.4042 | 32.3179 | 33.2383 | 32.4057 | 32.3155 | 33.2386 | 32.4099 | 32.3189 | 33.2397 | 32.8355 | 32.298 | 33.2301 | 32.8355 | 32.298 | 33.2301
SW-Toowoomba Dalby Warwick | F3910_Perseverence Creek 1 33 kV | Contingency Outage | 7234_Middle Ridge-Torrington 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | 7449 South Toowoomba-TWCE 110 kV | 7234_Middle Ridge-Torrington 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | 7449 South Toowoomba-TWCE 110 kV | 7234_Middle Ridge-Torrington 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | 7449 South Toowoomba-TWCE 110 kV | 7234_Middle Ridge-Torrington 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | 7449 South Toowoomba-TWCE 110 kV | 7234_Middle Ridge-Torrington 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | 7449 South Toowoomba-TWCE 110 kV
SW-Toowoomba Dalby Warwick | F3970_Pozieres 33 kV | % of Rated A | 34.24% | 21.83% | 15.02% | 34.3% | 21.9% | 15.03% | 34.27% | 21.88% | 15.03% | 34.3% | 21.91% | 15.03% | 34.1% | 22.01% | 15.06%
SW-Toowoomba Dalby Warwick | F3970_Pozieres 33 kV | Limiting Line Name | TR_LINE 24233_1 | TR_LINE 23973_2 | TR_LINE 23973_2 | TR_LINE 24233_1 | TR_LINE 23973_2 | TR_LINE 23973_2 | TR_LINE 24233_1 | TR_LINE 23973_2 | TR_LINE 23973_2 | TR_LINE 24233_1 | TR_LINE 23973_2 | TR_LINE 23973_2 | TR_LINE 24233_1 | TR_LINE 23973_2 | TR_LINE 23973_2
SW-Toowoomba Dalby Warwick | F3970_Pozieres 33 kV | Loading (A) | 48.9575 | 45.397 | 30.1881 | 49.0433 | 45.5569 | 30.2164 | 49.0047 | 45.5153 | 30.2088 | 49.0548 | 45.5771 | 30.2191 | 48.759 | 45.7821 | 30.2612
SW-Toowoomba Dalby Warwick | F3970_Pozieres 33 kV | Loading (MVA) | 2.7639 | 2.5356 | 1.8738 | 2.7641 | 2.536 | 1.8739 | 2.764 | 2.5359 | 1.8739 | 2.7633 | 2.5361 | 1.8739 | 2.7637 | 2.5366 | 1.874
SW-Toowoomba Dalby Warwick | F3970_Pozieres 33 kV | Loading (MW) | 2.4473 | 2.2544 | 1.677 | 2.4473 | 2.2546 | 1.677 | 2.4473 | 2.2545 | 1.677 | 2.4473 | 2.2546 | 1.677 | 2.4473 | 2.2547 | 1.677
SW-Toowoomba Dalby Warwick | F3970_Pozieres 33 kV | Power Factor | 0.88544 | 0.88903 | 0.8948 | 0.88541 | 0.88893 | 0.89478 | 0.88543 | 0.88896 | 0.89478 | 0.88563 | 0.88892 | 0.89477 | 0.88551 | 0.88879 | 0.89473
SW-Toowoomba Dalby Warwick | F3970_Pozieres 33 kV | Rating (A) | 143 | 208 | 201 | 143 | 208 | 201 | 143 | 208 | 201 | 143 | 208 | 201 | 143 | 208 | 201
SW-Toowoomba Dalby Warwick | F3970_Pozieres 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Toowoomba Dalby Warwick | F3970_Pozieres 33 kV | Min Voltage at Constrained Conductor | 32.5945 | 32.2426 | 35.8374 | 32.5387 | 32.1346 | 35.8052 | 32.5636 | 32.1629 | 35.8138 | 32.522 | 32.121 | 35.8021 | 32.7242 | 31.9838 | 35.7542
SW-Toowoomba Dalby Warwick | F3970_Pozieres 33 kV | Contingency Outage | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV
SW-Toowoomba Dalby Warwick | F3980_Purrawunda 33 kV | % of Rated A | 44.65% | 50.84% | 39.76% | 44.65% | 50.83% | 39.76% | 44.05% | 50.08% | 39.26% | 44.58% | 50.81% | 39.67% | 44.51% | 50.78% | 39.69%
SW-Toowoomba Dalby Warwick | F3980_Purrawunda 33 kV | Limiting Line Name | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1
SW-Toowoomba Dalby Warwick | F3980_Purrawunda 33 kV | Loading (A) | 94.2135 | 107.2805 | 83.9002 | 94.213 | 107.2443 | 83.8912 | 92.9392 | 105.6594 | 82.8311 | 94.0566 | 107.2052 | 83.7051 | 93.9104 | 107.1502 | 83.7547
SW-Toowoomba Dalby Warwick | F3980_Purrawunda 33 kV | Loading (MVA) | 5.4882 | 6.2519 | 4.894 | 5.4882 | 6.2525 | 4.8945 | 5.4133 | 6.1618 | 4.8332 | 5.4928 | 6.2532 | 4.9039 | 5.4973 | 6.2541 | 4.9014
SW-Toowoomba Dalby Warwick | F3980_Purrawunda 33 kV | Loading (MW) | 5.2289 | 6.0807 | 4.5419 | 5.2289 | 6.0806 | 4.5418 | 5.1414 | 5.978 | 4.4661 | 5.2283 | 6.0804 | 4.5412 | 5.2278 | 6.0802 | 4.5414
SW-Toowoomba Dalby Warwick | F3980_Purrawunda 33 kV | Power Factor | 0.95276 | 0.97262 | 0.92804 | 0.95276 | 0.9725 | 0.92795 | 0.94976 | 0.97016 | 0.92404 | 0.95185 | 0.97238 | 0.92603 | 0.95098 | 0.9722 | 0.92655
SW-Toowoomba Dalby Warwick | F3980_Purrawunda 33 kV | Rating (A) | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211 | 211
SW-Toowoomba Dalby Warwick | F3980_Purrawunda 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Toowoomba Dalby Warwick | F3980_Purrawunda 33 kV | Min Voltage at Constrained Conductor | 33.631 | 33.6447 | 33.677 | 33.6313 | 33.6592 | 33.6837 | 33.6272 | 33.6685 | 33.6879 | 33.7158 | 33.6749 | 33.8238 | 33.7956 | 33.697 | 33.7861
SW-Toowoomba Dalby Warwick | F3980_Purrawunda 33 kV | Contingency Outage | F5560_735(Middle Ridge-Warwick) 110 kV | 7233_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV | 7233_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | 7233_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F3820_Boundary Road 33 kV | 7234_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV
SW-Toowoomba Dalby Warwick | F4005_Racecourse 33 kV | % of Rated A | 43.57% | 35.39% | 19.34% | 43.07% | 34.99% | 19.13% | 42.58% | 34.6% | 18.92% | 42.23% | 34.71% | 18.95% | 42.45% | 34.66% | 19.11%
SW-Toowoomba Dalby Warwick | F4005_Racecourse 33 kV | Limiting Line Name | TR_CABLE 65_1 | TR_CABLE 65_1 | TR_CABLE 65_1 | TR_CABLE 65_1 | TR_CABLE 65_1 | TR_CABLE 65_1 | TR_CABLE 65_1 | TR_CABLE 65_1 | TR_CABLE 65_1 | TR_CABLE 65_1 | TR_CABLE 65_1 | TR_CABLE 65_1 | TR_CABLE 65_1 | TR_CABLE 65_1 | TR_CABLE 65_1
SW-Toowoomba Dalby Warwick | F4005_Racecourse 33 kV | Loading (A) | 307.5927 | 249.861 | 136.5645 | 304.0745 | 247.0557 | 135.0574 | 300.5974 | 244.2622 | 133.556 | 298.1134 | 245.0797 | 133.7957 | 299.6641 | 244.7062 | 134.8852
SW-Toowoomba Dalby Warwick | F4005_Racecourse 33 kV | Loading (MVA) | 17.7334 | 14.5106 | 8.0286 | 17.5381 | 14.3515 | 7.9412 | 17.343 | 14.1924 | 7.8538 | 17.3455 | 14.1937 | 7.854 | 17.4427 | 14.2705 | 7.898
SW-Toowoomba Dalby Warwick | F4005_Racecourse 33 kV | Loading (MW) | 17.1646 | 14.0786 | 7.8268 | 16.9785 | 13.926 | 7.7421 | 16.7923 | 13.7734 | 7.6574 | 16.7927 | 13.7736 | 7.6574 | 16.8857 | 13.8494 | 7.6998
SW-Toowoomba Dalby Warwick | F4005_Racecourse 33 kV | Power Factor | 0.9678 | 0.97012 | 0.97477 | 0.96796 | 0.97024 | 0.97483 | 0.96812 | 0.97037 | 0.9749 | 0.96801 | 0.9703 | 0.97488 | 0.96794 | 0.97038 | 0.97482
SW-Toowoomba Dalby Warwick | F4005_Racecourse 33 kV | Rating (A) | 706 | 706 | 706 | 706 | 706 | 706 | 706 | 706 | 706 | 706 | 706 | 706 | 706 | 706 | 706
SW-Toowoomba Dalby Warwick | F4005_Racecourse 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Toowoomba Dalby Warwick | F4005_Racecourse 33 kV | Min Voltage at Constrained Conductor | 33.2855 | 33.5294 | 33.9424 | 33.2999 | 33.5383 | 33.9475 | 33.3103 | 33.5459 | 33.9513 | 33.5926 | 33.4369 | 33.8913 | 33.6061 | 33.6692 | 33.8058
SW-Toowoomba Dalby Warwick | F4005_Racecourse 33 kV | Contingency Outage | F4685_Wyalla Street 33 kV | F4685_Wyalla Street 33 kV | F4685_Wyalla Street 33 kV | F4685_Wyalla Street 33 kV | F4685_Wyalla Street 33 kV | F4685_Wyalla Street 33 kV | F4685_Wyalla Street 33 kV | F4685_Wyalla Street 33 kV | F4685_Wyalla Street 33 kV | F4685_Wyalla Street 33 kV | F4685_Wyalla Street 33 kV | F4685_Wyalla Street 33 kV | F4685_Wyalla Street 33 kV | F4685_Wyalla Street 33 kV | F4685_Wyalla Street 33 kV
SW-Toowoomba Dalby Warwick | F4015_Ramsay Street 33 kV | % of Rated A | 70.38% | 61.57% | 29.05% | 69.69% | 60.99% | 28.79% | 69.34% | 60.7% | 28.66% | 69.4% | 60.75% | 28.67% | 70.64% | 61.39% | 28.94%
SW-Toowoomba Dalby Warwick | F4015_Ramsay Street 33 kV | Limiting Line Name | TR_CABLE 7922_1 | TR_CABLE 7922_1 | TR_CABLE 7922_1 | TR_CABLE 7922_1 | TR_CABLE 7922_1 | TR_CABLE 7922_1 | TR_CABLE 7922_1 | TR_CABLE 7922_1 | TR_CABLE 7922_1 | TR_CABLE 7922_1 | TR_CABLE 7922_1 | TR_CABLE 7922_1 | TR_CABLE 7922_1 | TR_CABLE 7922_1 | TR_CABLE 7922_1
SW-Toowoomba Dalby Warwick | F4015_Ramsay Street 33 kV | Loading (A) | 422.2655 | 369.4107 | 174.2759 | 418.145 | 365.9577 | 172.728 | 416.0571 | 364.2249 | 171.9545 | 416.4155 | 364.4936 | 172.0062 | 423.8659 | 368.3656 | 173.6247
SW-Toowoomba Dalby Warwick | F4015_Ramsay Street 33 kV | Loading (MVA) | 24.8535 | 21.8583 | 10.4582 | 24.6205 | 21.6573 | 10.3664 | 24.5039 | 21.5568 | 10.3204 | 24.507 | 21.5588 | 10.3206 | 24.77 | 21.763 | 10.4127
SW-Toowoomba Dalby Warwick | F4015_Ramsay Street 33 kV | Loading (MW) | 23.3954 | 20.7283 | 10.1648 | 23.1927 | 20.5491 | 10.0775 | 23.0913 | 20.4596 | 10.0338 | 23.0917 | 20.4598 | 10.0338 | 23.2984 | 20.6394 | 10.1212
SW-Toowoomba Dalby Warwick | F4015_Ramsay Street 33 kV | Power Factor | 0.9411 | 0.9481 | 0.9718 | 0.94178 | 0.94863 | 0.97199 | 0.94213 | 0.9489 | 0.97208 | 0.94202 | 0.94882 | 0.97207 | 0.94036 | 0.94817 | 0.97187
SW-Toowoomba Dalby Warwick | F4015_Ramsay Street 33 kV | Rating (A) | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600
SW-Toowoomba Dalby Warwick | F4015_Ramsay Street 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Toowoomba Dalby Warwick | F4015_Ramsay Street 33 kV | Min Voltage at Constrained Conductor | 33.9815 | 34.1623 | 34.6465 | 33.9945 | 34.1674 | 34.65 | 34.0033 | 34.1707 | 34.6517 | 33.9784 | 34.1487 | 34.6418 | 33.7393 | 34.1097 | 34.625
SW-Toowoomba Dalby Warwick | F4015_Ramsay Street 33 kV | Contingency Outage | F3255_Jennings Street 33 kV | F3255_Jennings Street 33 kV | F3255_Jennings Street 33 kV | F3255_Jennings Street 33 kV | F3255_Jennings Street 33 kV | F3255_Jennings Street 33 kV | F3255_Jennings Street 33 kV | F3255_Jennings Street 33 kV | F3255_Jennings Street 33 kV | F3255_Jennings Street 33 kV | F3255_Jennings Street 33 kV | F3255_Jennings Street 33 kV | F3255_Jennings Street 33 kV | F3255_Jennings Street 33 kV | F3255_Jennings Street 33 kV
SW-Toowoomba Dalby Warwick | F4132_Shirley Road 33 kV | % of Rated A | 56.08% | 42.49% | 14.65% | 56.06% | 42.47% | 14.65% | 56.07% | 42.46% | 14.64% | 56.22% | 42.72% | 14.68% | 63.63% | 46.82% | 18%
SW-Toowoomba Dalby Warwick | F4132_Shirley Road 33 kV | Limiting Line Name | TR_LINE 108727_1 | TR_CABLE 239_1 | TR_CABLE 239_1 | TR_LINE 108727_1 | TR_CABLE 239_1 | TR_CABLE 239_1 | TR_LINE 108727_1 | TR_CABLE 239_1 | TR_CABLE 239_1 | TR_LINE 108727_1 | TR_CABLE 239_1 | TR_CABLE 239_1 | TR_LINE 108727_1 | TR_CABLE 239_1 | TR_CABLE 239_1
SW-Toowoomba Dalby Warwick | F4132_Shirley Road 33 kV | Loading (A) | 235.5247 | 286.8224 | 98.8858 | 235.4511 | 286.6822 | 98.8651 | 235.4957 | 286.5924 | 98.8522 | 236.1399 | 288.3914 | 99.0986 | 267.2467 | 316.0275 | 121.4928
SW-Toowoomba Dalby Warwick | F4132_Shirley Road 33 kV | Loading (MVA) | 13.4185 | 16.6202 | 5.759 | 13.4183 | 16.6193 | 5.759 | 13.4184 | 16.6188 | 5.7589 | 13.4912 | 16.7256 | 5.7966 | 15.2356 | 18.5074 | 7.1017
SW-Toowoomba Dalby Warwick | F4132_Shirley Road 33 kV | Loading (MW) | 13.0291 | 15.9573 | 5.6836 | 13.029 | 15.957 | 5.6836 | 13.0291 | 15.9568 | 5.6836 | 13.1039 | 16.0562 | 5.7215 | 14.5518 | 17.4715 | 7.0306
SW-Toowoomba Dalby Warwick | F4132_Shirley Road 33 kV | Power Factor | 0.97098 | 0.95996 | 0.98677 | 0.97099 | 0.95999 | 0.98678 | 0.97099 | 0.96001 | 0.98678 | 0.97129 | 0.95982 | 0.9869 | 0.95512 | 0.94386 | 0.98986
SW-Toowoomba Dalby Warwick | F4132_Shirley Road 33 kV | Rating (A) | 420 | 675 | 675 | 420 | 675 | 675 | 420 | 675 | 675 | 420 | 675 | 675 | 420 | 675 | 675
SW-Toowoomba Dalby Warwick | F4132_Shirley Road 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Toowoomba Dalby Warwick | F4132_Shirley Road 33 kV | Min Voltage at Constrained Conductor | 32.8928 | 33.4551 | 33.6244 | 32.9026 | 33.4697 | 33.6312 | 32.8967 | 33.4791 | 33.6354 | 32.9849 | 33.4841 | 33.7712 | 32.914 | 33.8112 | 33.7481
SW-Toowoomba Dalby Warwick | F4132_Shirley Road 33 kV | Contingency Outage | F3980_Purrawunda 33 kV | 7233_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV | F3980_Purrawunda 33 kV | 7233_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | 7233_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV | 7234_Middle Ridge-Torrington 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F3820_Boundary Road 33 kV | F3820_Boundary Road 33 kV | F3820_Boundary Road 33 kV | F3820_Boundary Road 33 kV
SW-Toowoomba Dalby Warwick | F4245_Stanthorpe 33 kV | % of Rated A | 46.46% | 58.12% | 33.79% | 48.06% | 60.44% | 34.44% | 48.03% | 60.4% | 34.44% | 48.07% | 60.46% | 34.44% | 48.64% | 61.78% | 34.79%
SW-Toowoomba Dalby Warwick | F4245_Stanthorpe 33 kV | Limiting Line Name | TR_CABLE 107_1 | TR_CABLE 107_1 | TR_LINE 23344_1 | TR_CABLE 107_1 | TR_CABLE 107_1 | TR_LINE 23344_1 | TR_CABLE 107_1 | TR_CABLE 107_1 | TR_LINE 23344_1 | TR_CABLE 107_1 | TR_CABLE 107_1 | TR_LINE 23344_1 | TR_CABLE 107_1 | TR_CABLE 107_1 | TR_LINE 23344_1
SW-Toowoomba Dalby Warwick | F4245_Stanthorpe 33 kV | Loading (A) | 135.6738 | 169.7209 | 98.6734 | 140.3224 | 176.4933 | 100.5691 | 140.2516 | 176.361 | 100.5681 | 140.3711 | 176.5569 | 100.5695 | 142.0203 | 180.396 | 101.5846
SW-Toowoomba Dalby Warwick | F4245_Stanthorpe 33 kV | Loading (MVA) | 7.8273 | 9.5671 | 6.3336 | 8.0794 | 9.9115 | 6.2936 | 8.0813 | 9.9127 | 6.295 | 8.0781 | 9.9109 | 6.2931 | 8.2208 | 10.0813 | 6.3482
SW-Toowoomba Dalby Warwick | F4245_Stanthorpe 33 kV | Loading (MW) | 7.4309 | 9.4082 | 4.8492 | 7.7258 | 9.7819 | 5.0416 | 7.7258 | 9.7819 | 5.0416 | 7.7258 | 9.7819 | 5.0416 | 7.8735 | 9.969 | 5.1378
SW-Toowoomba Dalby Warwick | F4245_Stanthorpe 33 kV | Power Factor | 0.94936 | 0.98338 | 0.76553 | 0.95623 | 0.98693 | 0.80097 | 0.95601 | 0.9868 | 0.80079 | 0.95639 | 0.98699 | 0.80103 | 0.95776 | 0.98886 | 0.80922
SW-Toowoomba Dalby Warwick | F4245_Stanthorpe 33 kV | Rating (A) | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292
SW-Toowoomba Dalby Warwick | F4245_Stanthorpe 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Toowoomba Dalby Warwick | F4245_Stanthorpe 33 kV | Min Voltage at Constrained Conductor | 33.3077 | 32.5441 | 37.0586 | 33.2418 | 32.4217 | 36.1303 | 33.2663 | 32.4499 | 36.1389 | 33.2249 | 32.4081 | 36.1273 | 33.4189 | 32.2636 | 36.0799
SW-Toowoomba Dalby Warwick | F4245_Stanthorpe 33 kV | Contingency Outage | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5560_735(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV
SW-Toowoomba Dalby Warwick | F4470 Vacy Street | % of Rated A | 0.453% | 0.4537% | 0.454% | 0.453% | 0.4538% | 0.4541% | 0.4531% | 0.4538% | 0.4541% | 0.4531% | 0.4536% | 0.4543% | 0.4506% | 0.4532% | 0.4542%
SW-Toowoomba Dalby Warwick | F4470 Vacy Street | Limiting Line Name | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2
SW-Toowoomba Dalby Warwick | F4470 Vacy Street | Loading (A) | 2.265 | 2.2684 | 2.2702 | 2.2651 | 2.2688 | 2.2703 | 2.2653 | 2.2691 | 2.2703 | 2.2654 | 2.2679 | 2.2717 | 2.2532 | 2.2661 | 2.2708
SW-Toowoomba Dalby Warwick | F4470 Vacy Street | Loading (MVA) | 0.1368 | 0.13721 | 0.13743 | 0.13681 | 0.13726 | 0.13744 | 0.13684 | 0.1373 | 0.13744 | 0.13684 | 0.13715 | 0.13762 | 0.13538 | 0.13694 | 0.13751
SW-Toowoomba Dalby Warwick | F4470 Vacy Street | Loading (MW) | 0.002378 | 0.0023852 | 0.002389 | 0.0023783 | 0.0023861 | 0.0023891 | 0.0023787 | 0.0023868 | 0.0023891 | 0.0023788 | 0.0023842 | 0.0023922 | 0.0023534 | 0.0023804 | 0.0023903
SW-Toowoomba Dalby Warwick | F4470 Vacy Street | Power Factor | 0.0077605 | 0.0077605 | 0.0077605 | 0.0077605 | 0.0077605 | 0.0077605 | 0.0077605 | 0.0077605 | 0.0077605 | 0.0077605 | 0.0077605 | 0.0077605 | 0.0077605 | 0.0077605 | 0.0077605
SW-Toowoomba Dalby Warwick | F4470 Vacy Street | Rating (A) | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500
SW-Toowoomba Dalby Warwick | F4470 Vacy Street | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Toowoomba Dalby Warwick | F4470 Vacy Street | Min Voltage at Constrained Conductor | 34.8701 | 34.9233 | 34.9511 | 34.8723 | 34.9296 | 34.9515 | 34.8757 | 34.9344 | 34.9518 | 34.876 | 34.9157 | 34.9744 | 34.6893 | 34.8881 | 34.9604
SW-Toowoomba Dalby Warwick | F4470 Vacy Street | Contingency Outage | F3820_Boundary Road 33 kV | F2520_Clifton 33 kV | F3867_Pampas 33 kV | F3820_Boundary Road 33 kV | F2520_Clifton 33 kV | F3867_Pampas 33 kV | F3820_Boundary Road 33 kV | F2520_Clifton 33 kV | F3867_Pampas 33 kV | F3820_Boundary Road 33 kV | F2520_Clifton 33 kV | 730_Middle Ridge-South Toowoomba 110 kV | F3820_Boundary Road 33 kV | F3820_Boundary Road 33 kV | 730_Middle Ridge-South Toowoomba 110 kV
SW-Toowoomba Dalby Warwick | F4605_West Warwick 33 kV | % of Rated A | 40.29% | 45.01% | 21.6% | 40.31% | 45.1% | 21.61% | 39.89% | 44.61% | 21.4% | 40.33% | 45.11% | 21.61% | 40.97% | 45.71% | 21.84%
SW-Toowoomba Dalby Warwick | F4605_West Warwick 33 kV | Limiting Line Name | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1
SW-Toowoomba Dalby Warwick | F4605_West Warwick 33 kV | Loading (A) | 156.7362 | 176.447 | 73.4463 | 156.8084 | 176.776 | 73.4683 | 155.1586 | 174.8853 | 72.7453 | 156.8831 | 176.842 | 73.4738 | 159.3824 | 179.2017 | 74.2574
SW-Toowoomba Dalby Warwick | F4605_West Warwick 33 kV | Loading (MVA) | 8.9766 | 10.0819 | 4.353 | 8.9768 | 10.0831 | 4.353 | 8.8891 | 9.9841 | 4.3113 | 8.9771 | 10.0834 | 4.353 | 9.0677 | 10.1843 | 4.3949
SW-Toowoomba Dalby Warwick | F4605_West Warwick 33 kV | Loading (MW) | 8.7206 | 9.7713 | 4.2709 | 8.7207 | 9.7718 | 4.2709 | 8.6373 | 9.6781 | 4.2304 | 8.7208 | 9.7719 | 4.2709 | 8.8053 | 9.8663 | 4.3115
SW-Toowoomba Dalby Warwick | F4605_West Warwick 33 kV | Power Factor | 0.97148 | 0.9692 | 0.98115 | 0.97147 | 0.96913 | 0.98114 | 0.97167 | 0.96936 | 0.98125 | 0.97145 | 0.96911 | 0.98114 | 0.97106 | 0.96877 | 0.98102
SW-Toowoomba Dalby Warwick | F4605_West Warwick 33 kV | Rating (A) | 389 | 392 | 340 | 389 | 392 | 340 | 389 | 392 | 340 | 389 | 392 | 340 | 389 | 392 | 340
SW-Toowoomba Dalby Warwick | F4605_West Warwick 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Toowoomba Dalby Warwick | F4605_West Warwick 33 kV | Min Voltage at Constrained Conductor | 33.0592 | 32.981 | 34.2155 | 33.0449 | 32.9237 | 34.2056 | 33.0701 | 32.9528 | 34.2142 | 33.03 | 32.9122 | 34.2031 | 32.84 | 32.8038 | 34.1677
SW-Toowoomba Dalby Warwick | F4605_West Warwick 33 kV | Contingency Outage | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV
SW-Toowoomba Dalby Warwick | F4685_Wyalla Street 33 kV | % of Rated A | 44.65% | 36.26% | 19.8% | 44.14% | 35.85% | 19.59% | 43.63% | 35.44% | 19.37% | 43.27% | 35.55% | 19.4% | 43.49% | 35.51% | 19.56%
SW-Toowoomba Dalby Warwick | F4685_Wyalla Street 33 kV | Limiting Line Name | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 71_1
SW-Toowoomba Dalby Warwick | F4685_Wyalla Street 33 kV | Loading (A) | 308.0696 | 250.1614 | 136.6463 | 304.5392 | 247.3488 | 135.1372 | 301.0503 | 244.548 | 133.634 | 298.5557 | 245.2758 | 133.8742 | 300.111 | 244.9921 | 134.9651
SW-Toowoomba Dalby Warwick | F4685_Wyalla Street 33 kV | Loading (MVA) | 17.7343 | 14.511 | 8.0287 | 17.539 | 14.3519 | 7.9413 | 17.3439 | 14.1929 | 7.8539 | 17.3463 | 14.1893 | 7.8541 | 17.4435 | 14.2709 | 7.898
SW-Toowoomba Dalby Warwick | F4685_Wyalla Street 33 kV | Loading (MW) | 17.1653 | 14.079 | 7.827 | 16.9791 | 13.9264 | 7.7423 | 16.793 | 13.7738 | 7.6575 | 16.7933 | 13.7732 | 7.6576 | 16.8863 | 13.8499 | 7.7
SW-Toowoomba Dalby Warwick | F4685_Wyalla Street 33 kV | Power Factor | 0.96776 | 0.97009 | 0.97477 | 0.96792 | 0.97022 | 0.97483 | 0.96808 | 0.97034 | 0.97489 | 0.96797 | 0.97054 | 0.97487 | 0.9679 | 0.97036 | 0.97481
SW-Toowoomba Dalby Warwick | F4685_Wyalla Street 33 kV | Rating (A) | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690 | 690
SW-Toowoomba Dalby Warwick | F4685_Wyalla Street 33 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Toowoomba Dalby Warwick | F4685_Wyalla Street 33 kV | Min Voltage at Constrained Conductor | 33.2356 | 33.4902 | 33.9224 | 33.2507 | 33.4996 | 33.9277 | 33.2619 | 33.5077 | 33.9318 | 33.5445 | 33.4 | 33.8717 | 33.5577 | 33.631 | 33.7861
SW-Toowoomba Dalby Warwick | F4685_Wyalla Street 33 kV | Contingency Outage | F4005_Racecourse 33 kV | F4005_Racecourse 33 kV | F4005_Racecourse 33 kV | F4005_Racecourse 33 kV | F4005_Racecourse 33 kV | F4005_Racecourse 33 kV | F4005_Racecourse 33 kV | F4005_Racecourse 33 kV | F4005_Racecourse 33 kV | F4005_Racecourse 33 kV | F4005_Racecourse 33 kV | F4005_Racecourse 33 kV | F4005_Racecourse 33 kV | F4005_Racecourse 33 kV | F4005_Racecourse 33 kV
SW-Toowoomba Dalby Warwick | F5540_7244 Tangkam-Dalby 110 kV | % of Rated A | 57.12% | 50.89% | 28.38% | 56.53% | 50.44% | 28.15% | 56.29% | 50.23% | 28.08% | 56.09% | 50.09% | 28.01% | 56.38% | 50.48% | 28.15%
SW-Toowoomba Dalby Warwick | F5540_7244 Tangkam-Dalby 110 kV | Limiting Line Name | TR_LINE 140812_1 | TR_LINE 140812_1 | TR_LINE 24297_1 | TR_LINE 140812_1 | TR_LINE 140812_1 | TR_LINE 24297_1 | TR_LINE 140812_1 | TR_LINE 140812_1 | TR_LINE 24297_1 | TR_LINE 140812_1 | TR_LINE 140812_1 | TR_LINE 24297_1 | TR_LINE 140812_1 | TR_LINE 140812_1 | TR_LINE 24297_1
SW-Toowoomba Dalby Warwick | F5540_7244 Tangkam-Dalby 110 kV | Loading (A) | 150.8083 | 136.9051 | 66.6896 | 149.2355 | 135.6752 | 66.1515 | 148.6092 | 135.119 | 65.9894 | 148.0722 | 134.755 | 65.8156 | 148.8391 | 135.7817 | 66.164
SW-Toowoomba Dalby Warwick | F5540_7244 Tangkam-Dalby 110 kV | Loading (MVA) | 28.2303 | 25.8206 | 13.227 | 27.9592 | 25.6044 | 13.1205 | 27.8515 | 25.5066 | 13.0884 | 27.7499 | 25.436 | 13.0525 | 27.9667 | 25.6078 | 13.1194
SW-Toowoomba Dalby Warwick | F5540_7244 Tangkam-Dalby 110 kV | Loading (MW) | 27.4515 | 25.2575 | 13.1692 | 27.2076 | 25.06 | 13.0565 | 27.1101 | 24.9697 | 13.0231 | 27.0156 | 24.9033 | 12.9856 | 27.2071 | 25.06 | 13.0564
SW-Toowoomba Dalby Warwick | F5540_7244 Tangkam-Dalby 110 kV | Power Factor | 0.97241 | 0.97818 | 0.99563 | 0.97311 | 0.97873 | 0.99513 | 0.97337 | 0.97894 | 0.99501 | 0.97353 | 0.97905 | 0.99488 | 0.97283 | 0.9786 | 0.9952
SW-Toowoomba Dalby Warwick | F5540_7244 Tangkam-Dalby 110 kV | Rating (A) | 264 | 269 | 235 | 264 | 269 | 235 | 264 | 269 | 235 | 264 | 269 | 235 | 264 | 269 | 235
SW-Toowoomba Dalby Warwick | F5540_7244 Tangkam-Dalby 110 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Toowoomba Dalby Warwick | F5540_7244 Tangkam-Dalby 110 kV | Min Voltage at Constrained Conductor | 108.0644 | 108.8794 | 113.9927 | 108.1547 | 108.9466 | 114.0025 | 108.1923 | 108.9773 | 114.0051 | 108.1886 | 108.9693 | 113.9949 | 108.4721 | 108.8757 | 113.9709
SW-Toowoomba Dalby Warwick | F5540_7244 Tangkam-Dalby 110 kV | Contingency Outage | F5545_7245 Tangkam-Dalby 110 kV | F5545_7245 Tangkam-Dalby 110 kV | F5545_7245 Tangkam-Dalby 110 kV | F5545_7245 Tangkam-Dalby 110 kV | F5545_7245 Tangkam-Dalby 110 kV | F5545_7245 Tangkam-Dalby 110 kV | F5545_7245 Tangkam-Dalby 110 kV | F5545_7245 Tangkam-Dalby 110 kV | F5545_7245 Tangkam-Dalby 110 kV | F5545_7245 Tangkam-Dalby 110 kV | F5545_7245 Tangkam-Dalby 110 kV | F5545_7245 Tangkam-Dalby 110 kV | F5545_7245 Tangkam-Dalby 110 kV | F5545_7245 Tangkam-Dalby 110 kV | F5545_7245 Tangkam-Dalby 110 kV
SW-Toowoomba Dalby Warwick | F5545_7245 Tangkam-Dalby 110 kV | % of Rated A | 118.3% | 75.73% | 38.05% | 117% | 75.05% | 37.75% | 116.7% | 74.74% | 37.65% | 116.3% | 74.54% | 37.56% | 116.8% | 75.11% | 37.75%
SW-Toowoomba Dalby Warwick | F5545_7245 Tangkam-Dalby 110 kV | Limiting Line Name | TR_LINE 215532_1 | TR_LINE 215532_1 | TR_LINE 140801_1 | TR_LINE 215532_1 | TR_LINE 215532_1 | TR_LINE 140801_1 | TR_LINE 215532_1 | TR_LINE 215532_1 | TR_LINE 140801_1 | TR_LINE 215532_1 | TR_LINE 215532_1 | TR_LINE 140801_1 | TR_LINE 215532_1 | TR_LINE 215532_1 | TR_LINE 140801_1
SW-Toowoomba Dalby Warwick | F5545_7245 Tangkam-Dalby 110 kV | Loading (A) | 150.1918 | 136.3095 | 66.594 | 148.6346 | 135.0914 | 66.0568 | 148.1882 | 134.5369 | 65.8952 | 147.6535 | 134.176 | 65.7217 | 148.2941 | 135.1975 | 66.0695
SW-Toowoomba Dalby Warwick | F5545_7245 Tangkam-Dalby 110 kV | Loading (MVA) | 28.2582 | 25.8269 | 13.208 | 27.9865 | 25.6104 | 13.1016 | 27.9059 | 25.512 | 13.0696 | 27.8037 | 25.4413 | 13.0338 | 28.0025 | 25.614 | 13.1006
SW-Toowoomba Dalby Warwick | F5545_7245 Tangkam-Dalby 110 kV | Loading (MW) | 27.479 | 25.2785 | 13.1511 | 27.2345 | 25.0807 | 13.0388 | 27.1456 | 24.9902 | 13.0054 | 27.0508 | 24.9236 | 12.968 | 27.2402 | 25.0807 | 13.0385
SW-Toowoomba Dalby Warwick | F5545_7245 Tangkam-Dalby 110 kV | Power Factor | 0.9724 | 0.97873 | 0.99569 | 0.9731 | 0.97928 | 0.9952 | 0.97273 | 0.97951 | 0.99508 | 0.97289 | 0.97961 | 0.99495 | 0.97275 | 0.97914 | 0.99526
SW-Toowoomba Dalby Warwick | F5545_7245 Tangkam-Dalby 110 kV | Rating (A) | 127 | 180 | 175 | 127 | 180 | 175 | 127 | 180 | 175 | 127 | 180 | 175 | 127 | 180 | 175
SW-Toowoomba Dalby Warwick | F5545_7245 Tangkam-Dalby 110 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Toowoomba Dalby Warwick | F5545_7245 Tangkam-Dalby 110 kV | Min Voltage at Constrained Conductor | 108.5872 | 109.3576 | 114.1928 | 108.6704 | 109.4194 | 114.1995 | 108.684 | 109.4482 | 114.2013 | 108.6784 | 109.4387 | 114.1902 | 108.9826 | 109.3489 | 114.1682
SW-Toowoomba Dalby Warwick | F5545_7245 Tangkam-Dalby 110 kV | Contingency Outage | F5540_7244 Tangkam-Dalby 110 kV | F5540_7244 Tangkam-Dalby 110 kV | F5540_7244 Tangkam-Dalby 110 kV | F5540_7244 Tangkam-Dalby 110 kV | F5540_7244 Tangkam-Dalby 110 kV | F5540_7244 Tangkam-Dalby 110 kV | F5540_7244 Tangkam-Dalby 110 kV | F5540_7244 Tangkam-Dalby 110 kV | F5540_7244 Tangkam-Dalby 110 kV | F5540_7244 Tangkam-Dalby 110 kV | F5540_7244 Tangkam-Dalby 110 kV | F5540_7244 Tangkam-Dalby 110 kV | F5540_7244 Tangkam-Dalby 110 kV | F5540_7244 Tangkam-Dalby 110 kV | F5540_7244 Tangkam-Dalby 110 kV
SW-Toowoomba Dalby Warwick | F5550_733(Middle Ridge-Yarranlea) 110 kV | % of Rated A | 41.52% | 40.88% | 31.13% | 42.02% | 41.47% | 31.33% | 42.01% | 41.47% | 31.33% | 42.05% | 41.5% | 31.34% | 42.58% | 42.1% | 31.78%
SW-Toowoomba Dalby Warwick | F5550_733(Middle Ridge-Yarranlea) 110 kV | Limiting Line Name | TR_LINE 224268_1 | TR_LINE 224268_1 | TR_LINE 224268_1 | TR_LINE 224268_1 | TR_LINE 224268_1 | TR_LINE 224268_1 | TR_LINE 224268_1 | TR_LINE 224268_1 | TR_LINE 224268_1 | TR_LINE 224268_1 | TR_LINE 224268_1 | TR_LINE 224268_1 | TR_LINE 224268_1 | TR_LINE 224268_1 | TR_LINE 224268_1
SW-Toowoomba Dalby Warwick | F5550_733(Middle Ridge-Yarranlea) 110 kV | Loading (A) | 119.1673 | 116.9037 | 76.8932 | 120.5895 | 118.6078 | 77.3762 | 120.5768 | 118.6037 | 77.3748 | 120.6971 | 118.6823 | 77.4133 | 122.2145 | 120.3968 | 78.5055
SW-Toowoomba Dalby Warwick | F5550_733(Middle Ridge-Yarranlea) 110 kV | Loading (MVA) | 22.7329 | 22.3451 | 15.0538 | 22.9928 | 22.6525 | 15.1454 | 22.9922 | 22.6523 | 15.1454 | 22.9986 | 22.6539 | 15.1485 | 23.428 | 22.95 | 15.3531
SW-Toowoomba Dalby Warwick | F5550_733(Middle Ridge-Yarranlea) 110 kV | Loading (MW) | 20.9406 | 20.5889 | 14.2031 | 21.1869 | 20.8335 | 14.2838 | 21.1867 | 20.8334 | 14.2838 | 21.1883 | 20.8341 | 14.2844 | 21.5353 | 21.1294 | 14.5008
SW-Toowoomba Dalby Warwick | F5550_733(Middle Ridge-Yarranlea) 110 kV | Power Factor | 0.92113 | 0.92137 | 0.94344 | 0.92142 | 0.91967 | 0.94307 | 0.92144 | 0.91967 | 0.94307 | 0.92126 | 0.91964 | 0.94291 | 0.91918 | 0.92064 | 0.94444
SW-Toowoomba Dalby Warwick | F5550_733(Middle Ridge-Yarranlea) 110 kV | Rating (A) | 287 | 286 | 247 | 287 | 286 | 247 | 287 | 286 | 247 | 287 | 286 | 247 | 287 | 286 | 247
SW-Toowoomba Dalby Warwick | F5550_733(Middle Ridge-Yarranlea) 110 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Toowoomba Dalby Warwick | F5550_733(Middle Ridge-Yarranlea) 110 kV | Min Voltage at Constrained Conductor | 110.1333 | 110.3513 | 113.0313 | 110.0788 | 110.2617 | 113.0093 | 110.0872 | 110.2644 | 113.0109 | 110.008 | 110.1992 | 112.9779 | 110.6708 | 110.0496 | 112.9108
SW-Toowoomba Dalby Warwick | F5550_733(Middle Ridge-Yarranlea) 110 kV | Contingency Outage | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV | F5555_734(Middle Ridge-Yarranlea) 110 kV
SW-Toowoomba Dalby Warwick | F5555_734(Middle Ridge-Yarranlea) 110 kV | % of Rated A | 41.52% | 40.86% | 31.13% | 42.01% | 41.46% | 31.32% | 42% | 41.46% | 31.32% | 42.04% | 41.49% | 31.34% | 42.57% | 42.09% | 31.78%
SW-Toowoomba Dalby Warwick | F5555_734(Middle Ridge-Yarranlea) 110 kV | Limiting Line Name | TR_LINE 25640_1 | TR_LINE 25640_1 | TR_LINE 25640_1 | TR_LINE 25640_1 | TR_LINE 25640_1 | TR_LINE 25640_1 | TR_LINE 25640_1 | TR_LINE 25640_1 | TR_LINE 25640_1 | TR_LINE 25640_1 | TR_LINE 25640_1 | TR_LINE 25640_1 | TR_LINE 25640_1 | TR_LINE 25640_1 | TR_LINE 25640_1
SW-Toowoomba Dalby Warwick | F5555_734(Middle Ridge-Yarranlea) 110 kV | Loading (A) | 119.1544 | 116.8705 | 76.8824 | 120.5552 | 118.5729 | 77.3652 | 120.5425 | 118.5688 | 77.3637 | 120.6627 | 118.6477 | 77.4022 | 122.1772 | 120.3844 | 78.4967
SW-Toowoomba Dalby Warwick | F5555_734(Middle Ridge-Yarranlea) 110 kV | Loading (MVA) | 22.7417 | 22.3493 | 15.051 | 22.9988 | 22.6571 | 15.1426 | 22.9981 | 22.6569 | 15.1425 | 23.0045 | 22.6586 | 15.1457 | 23.4338 | 22.9595 | 15.3507
SW-Toowoomba Dalby Warwick | F5555_734(Middle Ridge-Yarranlea) 110 kV | Loading (MW) | 20.962 | 20.6088 | 14.2117 | 21.2082 | 20.854 | 14.2926 | 21.2081 | 20.8539 | 14.2926 | 21.2097 | 20.8546 | 14.2931 | 21.557 | 21.1514 | 14.51
SW-Toowoomba Dalby Warwick | F5555_734(Middle Ridge-Yarranlea) 110 kV | Power Factor | 0.92126 | 0.92162 | 0.94357 | 0.92168 | 0.91992 | 0.9432 | 0.9217 | 0.91993 | 0.9432 | 0.92151 | 0.91989 | 0.94304 | 0.91944 | 0.92077 | 0.94456
SW-Toowoomba Dalby Warwick | F5555_734(Middle Ridge-Yarranlea) 110 kV | Rating (A) | 287 | 286 | 247 | 287 | 286 | 247 | 287 | 286 | 247 | 287 | 286 | 247 | 287 | 286 | 247
SW-Toowoomba Dalby Warwick | F5555_734(Middle Ridge-Yarranlea) 110 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Toowoomba Dalby Warwick | F5555_734(Middle Ridge-Yarranlea) 110 kV | Min Voltage at Constrained Conductor | 110.1243 | 110.3444 | 113.0262 | 110.0717 | 110.2548 | 113.0042 | 110.0801 | 110.2575 | 113.0058 | 110.0009 | 110.1922 | 112.9728 | 110.6638 | 110.0405 | 112.9054
SW-Toowoomba Dalby Warwick | F5555_734(Middle Ridge-Yarranlea) 110 kV | Contingency Outage | F5550_733(Middle Ridge-Yarranlea) 110 kV | F5550_733(Middle Ridge-Yarranlea) 110 kV | F5550_733(Middle Ridge-Yarranlea) 110 kV | F5550_733(Middle Ridge-Yarranlea) 110 kV | F5550_733(Middle Ridge-Yarranlea) 110 kV | F5550_733(Middle Ridge-Yarranlea) 110 kV | F5550_733(Middle Ridge-Yarranlea) 110 kV | F5550_733(Middle Ridge-Yarranlea) 110 kV | F5550_733(Middle Ridge-Yarranlea) 110 kV | F5550_733(Middle Ridge-Yarranlea) 110 kV | F5550_733(Middle Ridge-Yarranlea) 110 kV | F5550_733(Middle Ridge-Yarranlea) 110 kV | F5550_733(Middle Ridge-Yarranlea) 110 kV | F5550_733(Middle Ridge-Yarranlea) 110 kV | F5550_733(Middle Ridge-Yarranlea) 110 kV
SW-Toowoomba Dalby Warwick | F5560_735(Middle Ridge-Warwick) 110 kV | % of Rated A | 86.41% | 76.52% | 45.35% | 86.67% | 76.93% | 45.45% | 86.28% | 76.58% | 45.35% | 86.52% | 76.81% | 45.4% | 86.8% | 77.83% | 45.66%
SW-Toowoomba Dalby Warwick | F5560_735(Middle Ridge-Warwick) 110 kV | Limiting Line Name | TR_LINE 94897_1 | TR_LINE 94897_1 | TR_LINE 25701_1 | TR_LINE 94897_1 | TR_LINE 94897_1 | TR_LINE 25701_1 | TR_LINE 94897_1 | TR_LINE 94897_1 | TR_LINE 25701_1 | TR_LINE 94897_1 | TR_LINE 94897_1 | TR_LINE 25701_1 | TR_LINE 94897_1 | TR_LINE 94897_1 | TR_LINE 25701_1
SW-Toowoomba Dalby Warwick | F5560_735(Middle Ridge-Warwick) 110 kV | Loading (A) | 222.0614 | 244.8791 | 133.3416 | 222.7325 | 246.1877 | 133.637 | 221.7448 | 245.0585 | 133.329 | 222.3593 | 245.7907 | 133.4674 | 223.086 | 249.0475 | 134.2335
SW-Toowoomba Dalby Warwick | F5560_735(Middle Ridge-Warwick) 110 kV | Loading (MVA) | 44.2813 | 48.8687 | 26.8054 | 44.4165 | 49.1262 | 26.8646 | 44.2215 | 48.9032 | 26.8033 | 44.3157 | 49.022 | 26.8261 | 44.749 | 49.6343 | 26.9697
SW-Toowoomba Dalby Warwick | F5560_735(Middle Ridge-Warwick) 110 kV | Loading (MW) | 44.1662 | 48.8673 | 23.1201 | 44.3104 | 49.1262 | 23.2283 | 44.1056 | 48.9031 | 23.1364 | 44.208 | 49.022 | 23.1792 | 44.656 | 49.6315 | 23.4183
SW-Toowoomba Dalby Warwick | F5560_735(Middle Ridge-Warwick) 110 kV | Power Factor | 0.99727 | 0.99995 | 0.86252 | 0.99748 | 1 | 0.86465 | 0.99724 | 0.99999 | 0.86319 | 0.99744 | 1 | 0.86405 | 0.9978 | 0.99994 | 0.86832
SW-Toowoomba Dalby Warwick | F5560_735(Middle Ridge-Warwick) 110 kV | Rating (A) | 257 | 320 | 294 | 257 | 320 | 294 | 257 | 320 | 294 | 257 | 320 | 294 | 257 | 320 | 294
SW-Toowoomba Dalby Warwick | F5560_735(Middle Ridge-Warwick) 110 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Toowoomba Dalby Warwick | F5560_735(Middle Ridge-Warwick) 110 kV | Min Voltage at Constrained Conductor | 114.8257 | 114.8531 | 115.7429 | 114.8271 | 114.8387 | 115.7075 | 114.8351 | 114.8473 | 115.7338 | 114.7594 | 114.7808 | 115.6982 | 115.5029 | 114.6867 | 115.5843
SW-Toowoomba Dalby Warwick | F5560_735(Middle Ridge-Warwick) 110 kV | Contingency Outage | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV | F5565_736(Middle Ridge-Warwick) 110 kV
SW-Toowoomba Dalby Warwick | F5565_736(Middle Ridge-Warwick) 110 kV | % of Rated A | 27.87% | 29.8% | 19.5% | 27.94% | 29.94% | 19.54% | 27.83% | 29.81% | 19.5% | 27.9% | 29.89% | 19.52% | 27.97% | 30.23% | 19.62%
SW-Toowoomba Dalby Warwick | F5565_736(Middle Ridge-Warwick) 110 kV | Limiting Line Name | TR_LINE 141691_1 | TR_LINE 141691_1 | TR_LINE 141691_1 | TR_LINE 141691_1 | TR_LINE 141691_1 | TR_LINE 141691_1 | TR_LINE 141691_1 | TR_LINE 141691_1 | TR_LINE 141691_1 | TR_LINE 141691_1 | TR_LINE 141691_1 | TR_LINE 141691_1 | TR_LINE 141691_1 | TR_LINE 141691_1 | TR_LINE 141691_1
SW-Toowoomba Dalby Warwick | F5565_736(Middle Ridge-Warwick) 110 kV | Loading (A) | 212.6474 | 232.1441 | 133.598 | 213.2105 | 233.2016 | 133.866 | 212.3483 | 232.2456 | 133.5787 | 212.8643 | 232.8472 | 133.7057 | 213.4211 | 235.5259 | 134.4114
SW-Toowoomba Dalby Warwick | F5565_736(Middle Ridge-Warwick) 110 kV | Loading (MVA) | 42.3966 | 46.2873 | 26.932 | 42.5092 | 46.4944 | 26.9857 | 42.3417 | 46.3069 | 26.9285 | 42.4166 | 46.4003 | 26.9469 | 42.7993 | 46.8923 | 27.0808
SW-Toowoomba Dalby Warwick | F5565_736(Middle Ridge-Warwick) 110 kV | Loading (MW) | 41.9799 | 46.1692 | 22.4491 | 42.1078 | 46.3897 | 22.5536 | 41.9239 | 46.1935 | 22.4652 | 42.0129 | 46.2944 | 22.5064 | 42.4438 | 46.8222 | 22.7363
SW-Toowoomba Dalby Warwick | F5565_736(Middle Ridge-Warwick) 110 kV | Power Factor | 0.99007 | 0.99738 | 0.83355 | 0.99046 | 0.99768 | 0.83576 | 0.99003 | 0.99748 | 0.83425 | 0.99038 | 0.99765 | 0.83522 | 0.99161 | 0.99844 | 0.83957
SW-Toowoomba Dalby Warwick | F5565_736(Middle Ridge-Warwick) 110 kV | Rating (A) | 763 | 779 | 685 | 763 | 779 | 685 | 763 | 779 | 685 | 763 | 779 | 685 | 763 | 779 | 685
SW-Toowoomba Dalby Warwick | F5565_736(Middle Ridge-Warwick) 110 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
SW-Toowoomba Dalby Warwick | F5565_736(Middle Ridge-Warwick) 110 kV | Min Voltage at Constrained Conductor | 115.087 | 115.0734 | 116.3879 | 115.087 | 115.0627 | 116.3866 | 115.0999 | 115.0714 | 116.3896 | 115.0233 | 115.0048 | 116.3584 | 115.7558 | 114.8981 | 116.3226
SW-Toowoomba Dalby Warwick | F5565_736(Middle Ridge-Warwick) 110 kV | Contingency Outage | F5560_735(Middle Ridge-Warwick) 110 kV | F5560_735(Middle Ridge-Warwick) 110 kV | F5560_735(Middle Ridge-Warwick) 110 kV | F5560_735(Middle Ridge-Warwick) 110 kV | F5560_735(Middle Ridge-Warwick) 110 kV | F5560_735(Middle Ridge-Warwick) 110 kV | F5560_735(Middle Ridge-Warwick) 110 kV | F5560_735(Middle Ridge-Warwick) 110 kV | F5560_735(Middle Ridge-Warwick) 110 kV | F5560_735(Middle Ridge-Warwick) 110 kV | F5560_735(Middle Ridge-Warwick) 110 kV | F5560_735(Middle Ridge-Warwick) 110 kV | F5560_735(Middle Ridge-Warwick) 110 kV | F5560_735(Middle Ridge-Warwick) 110 kV | F5560_735(Middle Ridge-Warwick) 110 kV
WB-Korenan | 6112_Agnes Water 66 kV | % of Rated A | 13.64% | 9.701% | 4.773% | 13.39% | 9.52% | 4.69% | 13.4% | 9.521% | 4.736% | 13.65% | 9.818% | 4.821% | 13.65% | 9.723% | 4.821%
WB-Korenan | 6112_Agnes Water 66 kV | Limiting Line Name | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1
WB-Korenan | 6112_Agnes Water 66 kV | Loading (A) | 38.7338 | 46.7575 | 23.0542 | 38.0277 | 45.8874 | 22.6537 | 38.0425 | 45.8914 | 22.8758 | 38.7581 | 47.323 | 23.2844 | 38.7653 | 46.8629 | 23.2868
WB-Korenan | 6112_Agnes Water 66 kV | Loading (MVA) | 4.5128 | 5.4344 | 2.6821 | 4.4302 | 5.334 | 2.6354 | 4.4301 | 5.334 | 2.632 | 4.5127 | 5.4343 | 2.6787 | 4.5127 | 5.4344 | 2.6787
WB-Korenan | 6112_Agnes Water 66 kV | Loading (MW) | 4.4978 | 5.4291 | 2.6224 | 4.4141 | 5.3279 | 2.5736 | 4.4141 | 5.3279 | 2.5737 | 4.4979 | 5.4298 | 2.6224 | 4.4979 | 5.4291 | 2.6224
WB-Korenan | 6112_Agnes Water 66 kV | Power Factor | 0.99669 | 0.99901 | 0.97771 | 0.99637 | 0.99885 | 0.97656 | 0.99639 | 0.99885 | 0.97787 | 0.99671 | 0.99917 | 0.979 | 0.99671 | 0.99902 | 0.97901
WB-Korenan | 6112_Agnes Water 66 kV | Rating (A) | 284 | 482 | 483 | 284 | 482 | 483 | 284 | 482 | 483 | 284 | 482 | 483 | 284 | 482 | 483
WB-Korenan | 6112_Agnes Water 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB-Korenan | 6112_Agnes Water 66 kV | Min Voltage at Constrained Conductor | 67.2644 | 67.1015 | 67.1694 | 67.2593 | 67.1104 | 67.1643 | 67.2325 | 67.1046 | 66.4267 | 67.2212 | 66.2973 | 66.4194 | 67.2085 | 66.9499 | 66.4117
WB-Korenan | 6112_Agnes Water 66 kV | Contingency Outage | 7315_Aramara 132 kV | 7315_Aramara 132 kV | M027_ISIS - Childers 66 kV | 7315_Aramara 132 kV | 7316_Aramara 132 kV | 786_Gin Gin - Bundaberg 132 kV | 7315_Aramara 132 kV | 7315_Aramara 132 kV | 7187_Gin Gin - Bundaberg 132 kV | 7315_Aramara 132 kV | 7187_Gin Gin - Bundaberg 132 kV | 7187_Gin Gin - Bundaberg 132 kV | 7315_Aramara 132 kV | M024_Gayndah - Mundubbera 66 kV | 7187_Gin Gin - Bundaberg 132 kV
WB-Korenan | 7188_Gin Gin - Korenan QR 132 kV | % of Rated A | 7.071% | 7.139% | 5.34% | 6.996% | 7.053% | 5.305% | 6.997% | 7.054% | 5.293% | 7.073% | 7.131% | 5.329% | 7.073% | 7.14% | 5.329%
WB-Korenan | 7188_Gin Gin - Korenan QR 132 kV | Limiting Line Name | TR_LINE 88330_1 | TR_LINE 88330_1 | TR_LINE 88330_1 | TR_LINE 88330_1 | TR_LINE 88330_1 | TR_LINE 88330_1 | TR_LINE 88330_1 | TR_LINE 88330_1 | TR_LINE 88330_1 | TR_LINE 88330_1 | TR_LINE 88330_1 | TR_LINE 88330_1 | TR_LINE 88330_1 | TR_LINE 88330_1 | TR_LINE 88330_1
WB-Korenan | 7188_Gin Gin - Korenan QR 132 kV | Loading (A) | 26.7291 | 30.1279 | 20.6132 | 26.4455 | 29.7651 | 20.4755 | 26.4494 | 29.7665 | 20.4322 | 26.7358 | 30.0934 | 20.5686 | 26.7378 | 30.1299 | 20.5686
WB-Korenan | 7188_Gin Gin - Korenan QR 132 kV | Loading (MVA) | 6.3939 | 7.2003 | 4.9303 | 6.3248 | 7.1134 | 4.8979 | 6.3233 | 7.1131 | 4.9166 | 6.3915 | 7.1933 | 4.9494 | 6.3907 | 7.1999 | 4.9493
WB-Korenan | 7188_Gin Gin - Korenan QR 132 kV | Loading (MW) | 5.6824 | 6.6609 | 3.7211 | 5.598 | 6.5587 | 3.6721 | 5.598 | 6.5588 | 3.6721 | 5.6824 | 6.6616 | 3.7211 | 5.6825 | 6.6609 | 3.7211
WB-Korenan | 7188_Gin Gin - Korenan QR 132 kV | Power Factor | 0.88872 | 0.92509 | 0.75474 | 0.88508 | 0.92203 | 0.74973 | 0.8853 | 0.92206 | 0.74688 | 0.88907 | 0.92609 | 0.75182 | 0.88917 | 0.92515 | 0.75184
WB-Korenan | 7188_Gin Gin - Korenan QR 132 kV | Rating (A) | 378 | 422 | 386 | 378 | 422 | 386 | 378 | 422 | 386 | 378 | 422 | 386 | 378 | 422 | 386
WB-Korenan | 7188_Gin Gin - Korenan QR 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB-Korenan | 7188_Gin Gin - Korenan QR 132 kV | Min Voltage at Constrained Conductor | 137.8827 | 137.6407 | 138.0798 | 137.8653 | 137.6495 | 138.1013 | 137.8107 | 137.6376 | 138.9244 | 137.7948 | 137.6611 | 138.9179 | 137.7688 | 137.6239 | 138.9148
WB-Korenan | 7188_Gin Gin - Korenan QR 132 kV | Contingency Outage | 7315_Aramara 132 kV | 7315_Aramara 132 kV | M041_West Bundaberg-Meadowvale 66 kV | 7315_Aramara 132 kV | 7316_Aramara 132 kV | M041_West Bundaberg-Meadowvale 66 kV | 7315_Aramara 132 kV | 7315_Aramara 132 kV | 786_Gin Gin - Bundaberg 132 kV | 7315_Aramara 132 kV | 7187_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 7315_Aramara 132 kV | 7187_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV
WB-Wide Bay | 6205_East Bundaberg-BUCE 66 kV | % of Rated A | 94.69% | 98.27% | 63.07% | 94.82% | 98.26% | 63.13% | 94.93% | 98.33% | 62.96% | 95.52% | 98.5% | 63.3% | 96.57% | 99.66% | 63.88%
WB-Wide Bay | 6205_East Bundaberg-BUCE 66 kV | Limiting Line Name | TR_LINE 176527_1 | TR_LINE 176527_1 | TR_LINE 176527_1 | TR_LINE 176527_1 | TR_LINE 176527_1 | TR_LINE 176527_1 | TR_LINE 176527_1 | TR_LINE 176527_1 | TR_LINE 176527_1 | TR_LINE 176527_1 | TR_LINE 176527_1 | TR_LINE 176527_1 | TR_LINE 176527_1 | TR_LINE 176527_1 | TR_LINE 176527_1
WB-Wide Bay | 6205_East Bundaberg-BUCE 66 kV | Loading (A) | 375.9227 | 428.4448 | 224.5346 | 376.4329 | 428.421 | 224.7499 | 376.8686 | 428.7259 | 224.1384 | 379.2279 | 429.4606 | 225.3653 | 383.3909 | 434.5251 | 227.4021
WB-Wide Bay | 6205_East Bundaberg-BUCE 66 kV | Loading (MVA) | 42.6921 | 48.4769 | 25.7298 | 42.5839 | 48.3173 | 25.6918 | 42.6574 | 48.4154 | 25.7267 | 42.9107 | 48.7121 | 25.864 | 43.3396 | 49.206 | 26.0857
WB-Wide Bay | 6205_East Bundaberg-BUCE 66 kV | Loading (MW) | 42.4857 | 48.3901 | 24.6374 | 42.3122 | 48.2039 | 24.5519 | 42.4031 | 48.3004 | 24.5967 | 42.6652 | 48.5939 | 24.7487 | 43.0921 | 49.1002 | 24.9945
WB-Wide Bay | 6205_East Bundaberg-BUCE 66 kV | Power Factor | 0.99511 | 0.99817 | 0.95744 | 0.99355 | 0.9976 | 0.95553 | 0.99397 | 0.99758 | 0.95597 | 0.99421 | 0.99752 | 0.95678 | 0.99422 | 0.9978 | 0.95807
WB-Wide Bay | 6205_East Bundaberg-BUCE 66 kV | Rating (A) | 397 | 436 | 356 | 397 | 436 | 356 | 397 | 436 | 356 | 397 | 436 | 356 | 397 | 436 | 356
WB-Wide Bay | 6205_East Bundaberg-BUCE 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB-Wide Bay | 6205_East Bundaberg-BUCE 66 kV | Min Voltage at Constrained Conductor | 65.5447 | 65.2973 | 66.1513 | 65.2905 | 65.0862 | 65.9904 | 65.3274 | 65.1719 | 66.2604 | 65.3063 | 65.4594 | 66.2512 | 65.2425 | 65.3518 | 66.2203
WB-Wide Bay | 6205_East Bundaberg-BUCE 66 kV | Contingency Outage | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV
WB-Wide Bay | 6302_Bundaberg Central - WEBU 66 kV | % of Rated A | 126.9% | 119.3% | 86.72% | 126.6% | 119.1% | 86.57% | 126.5% | 119% | 86.28% | 127.1% | 119.1% | 86.6% | 128.5% | 120.5% | 87.32%
WB-Wide Bay | 6302_Bundaberg Central - WEBU 66 kV | Limiting Line Name | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1
WB-Wide Bay | 6302_Bundaberg Central - WEBU 66 kV | Loading (A) | 503.6732 | 520.3092 | 308.7306 | 502.6988 | 519.3253 | 308.1959 | 502.2789 | 519.0528 | 307.1629 | 504.6191 | 519.2007 | 308.301 | 510.3179 | 525.2012 | 310.8451
WB-Wide Bay | 6302_Bundaberg Central - WEBU 66 kV | Loading (MVA) | 57.6777 | 59.38 | 35.4495 | 57.3308 | 59.0679 | 35.2993 | 57.3167 | 59.1124 | 35.3236 | 57.5698 | 59.3904 | 35.451 | 58.1719 | 59.9917 | 35.7302
WB-Wide Bay | 6302_Bundaberg Central - WEBU 66 kV | Loading (MW) | 57.1418 | 58.8268 | 32.5498 | 56.6992 | 58.4525 | 32.3177 | 56.7002 | 58.4864 | 32.3124 | 56.968 | 58.7803 | 32.4662 | 57.5869 | 59.4257 | 32.8129
WB-Wide Bay | 6302_Bundaberg Central - WEBU 66 kV | Power Factor | 0.98835 | 0.98822 | 0.91406 | 0.98641 | 0.98697 | 0.91132 | 0.9867 | 0.98679 | 0.91056 | 0.98703 | 0.98716 | 0.91162 | 0.98744 | 0.98806 | 0.91419
WB-Wide Bay | 6302_Bundaberg Central - WEBU 66 kV | Rating (A) | 397 | 436 | 356 | 397 | 436 | 356 | 397 | 436 | 356 | 397 | 436 | 356 | 397 | 436 | 356
WB-Wide Bay | 6302_Bundaberg Central - WEBU 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB-Wide Bay | 6302_Bundaberg Central - WEBU 66 kV | Min Voltage at Constrained Conductor | 65.5911 | 65.3495 | 66.1653 | 65.3356 | 65.1375 | 66.004 | 65.3728 | 65.2231 | 66.274 | 65.3521 | 65.5107 | 66.265 | 65.2889 | 65.4042 | 66.2346
WB-Wide Bay | 6302_Bundaberg Central - WEBU 66 kV | Contingency Outage | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV | M036_Bundaberg-South Bundaberg 66 kV
WB-Wide Bay | 6366_Gootchie 66 kV | % of Rated A | 55.14% | 40.87% | 14.65% | 54.92% | 45.41% | 29.42% | 59.01% | 49.27% | 29.05% | 63.26% | 53.15% | 28.8% | 64% | 53.82% | 28.65%
WB-Wide Bay | 6366_Gootchie 66 kV | Limiting Line Name | TR_LINE 42255_1 | TR_LINE 42255_1 | TR_LINE 7245_1 | TR_LINE 139374_1 | TR_LINE 139374_1 | TR_LINE 7245_1 | TR_LINE 139374_1 | TR_LINE 139374_1 | TR_LINE 7245_1 | TR_LINE 139374_1 | TR_LINE 139374_1 | TR_LINE 7245_1 | TR_LINE 139374_1 | TR_LINE 139374_1 | TR_LINE 7245_1
WB-Wide Bay | 6366_Gootchie 66 kV | Loading (A) | 72.7801 | 68.2493 | 23.2965 | 72.4907 | 75.8344 | 46.7712 | 77.8952 | 82.2728 | 46.1906 | 83.5047 | 88.762 | 45.794 | 84.4803 | 89.8817 | 45.5502
WB-Wide Bay | 6366_Gootchie 66 kV | Loading (MVA) | 8.0643 | 7.5735 | 2.7223 | 8.0907 | 8.4389 | 5.4897 | 8.655 | 9.1054 | 5.4499 | 9.2318 | 9.7661 | 5.4004 | 9.3293 | 9.8768 | 5.3697
WB-Wide Bay | 6366_Gootchie 66 kV | Loading (MW) | 7.8806 | 7.412 | 2.7118 | 7.8619 | 8.1858 | 3.5586 | 8.3907 | 8.8063 | 3.8142 | 8.9299 | 9.4203 | 3.7471 | 9.0203 | 9.5232 | 3.7063
WB-Wide Bay | 6366_Gootchie 66 kV | Power Factor | 0.9772 | 0.97866 | 0.99617 | 0.97166 | 0.96995 | 0.64823 | 0.96942 | 0.96711 | 0.69987 | 0.96726 | 0.96457 | 0.69386 | 0.96684 | 0.96417 | 0.69022
WB-Wide Bay | 6366_Gootchie 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
WB-Wide Bay | 6366_Gootchie 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB-Wide Bay | 6366_Gootchie 66 kV | Min Voltage at Constrained Conductor | 63.9659 | 64.0615 | 66.851 | 64.4199 | 64.2284 | 67.7657 | 64.1287 | 63.8747 | 68.0569 | 63.8051 | 63.4975 | 68.0362 | 63.734 | 63.4169 | 68.0204
WB-Wide Bay | 6366_Gootchie 66 kV | Contingency Outage | 7187_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | M018_Maryborough-Maryborough City 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV
WB-Wide Bay | 7187_Gin Gin - Bundaberg 132 kV | % of Rated A | 85.47% | 80.62% | 63.4% | 84.18% | 79.53% | 63.08% | 88.22% | 83.35% | 68.33% | 88.45% | 83.95% | 68.44% | 88.86% | 84.46% | 68.64%
WB-Wide Bay | 7187_Gin Gin - Bundaberg 132 kV | Limiting Line Name | TR_LINE 6941_1 | TR_LINE 6941_1 | TR_LINE 6941_1 | TR_LINE 6941_1 | TR_LINE 6941_1 | TR_LINE 6941_1 | TR_LINE 6941_c | TR_LINE 6941_c | TR_LINE 6941_c | TR_LINE 6941_c | TR_LINE 6941_c | TR_LINE 6941_c | TR_LINE 6941_c | TR_LINE 6941_c | TR_LINE 6941_c
WB-Wide Bay | 7187_Gin Gin - Bundaberg 132 kV | Loading (A) | 580.3165 | 589.3313 | 420.3704 | 571.5975 | 581.3858 | 418.199 | 598.98 | 609.3067 | 453.0478 | 600.6076 | 613.7081 | 453.7337 | 603.3769 | 617.3761 | 455.0539
WB-Wide Bay | 7187_Gin Gin - Bundaberg 132 kV | Loading (MVA) | 138.8862 | 140.9331 | 100.151 | 136.7829 | 139.0253 | 99.6165 | 138.8646 | 141.152 | 105.8753 | 139.2255 | 142.6281 | 106.0306 | 139.8294 | 143.4351 | 106.3235
WB-Wide Bay | 7187_Gin Gin - Bundaberg 132 kV | Loading (MW) | 138.8411 | 140.9212 | 97.7357 | 136.7503 | 139.0175 | 97.321 | 137.6677 | 140.2232 | 100.3216 | 138.0733 | 141.8725 | 100.5019 | 138.7863 | 142.7768 | 100.8767
WB-Wide Bay | 7187_Gin Gin - Bundaberg 132 kV | Power Factor | 0.99968 | 0.99992 | 0.97588 | 0.99976 | 0.99994 | 0.97696 | 0.98247 | 0.98522 | 0.93564 | 0.98292 | 0.98714 | 0.93594 | 0.98405 | 0.98819 | 0.93681
WB-Wide Bay | 7187_Gin Gin - Bundaberg 132 kV | Rating (A) | 679 | 731 | 663 | 679 | 731 | 663 | 679 | 731 | 663 | 679 | 731 | 663 | 679 | 731 | 663
WB-Wide Bay | 7187_Gin Gin - Bundaberg 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB-Wide Bay | 7187_Gin Gin - Bundaberg 132 kV | Min Voltage at Constrained Conductor | 138.1762 | 138.0679 | 137.5507 | 138.1596 | 138.0603 | 137.5269 | 133.061 | 132.8077 | 134.8124 | 133.0212 | 133.1285 | 134.809 | 132.9265 | 133.0192 | 134.7993
WB-Wide Bay | 7187_Gin Gin - Bundaberg 132 kV | Contingency Outage | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV
WB-Wide Bay | 7190_Woolooga-Mungar 132 kV | % of Rated A | 2.54% | 2.418% | 2.676% | 2.54% | 2.417% | 2.676% | 2.54% | 2.417% | 2.676% | 2.54% | 2.417% | 2.676% | 2.54% | 2.417% | 2.676%
WB-Wide Bay | 7190_Woolooga-Mungar 132 kV | Limiting Line Name | TR_LINE 6802_2 | TR_LINE 6802_2 | TR_LINE 6802_2 | TR_LINE 6802_2 | TR_LINE 6802_2 | TR_LINE 6802_2 | TR_LINE 6802_2 | TR_LINE 6802_2 | TR_LINE 6802_2 | TR_LINE 6802_2 | TR_LINE 6802_2 | TR_LINE 6802_2 | TR_LINE 6802_2 | TR_LINE 6802_2 | TR_LINE 6802_2
WB-Wide Bay | 7190_Woolooga-Mungar 132 kV | Loading (A) | 14.3267 | 14.5055 | 14.5063 | 14.3259 | 14.5046 | 14.5061 | 14.3259 | 14.5046 | 14.5061 | 14.3259 | 14.5046 | 14.5061 | 14.3259 | 14.5046 | 14.5061
WB-Wide Bay | 7190_Woolooga-Mungar 132 kV | Loading (MVA) | 3.4395 | 3.4824 | 3.4825 | 3.4391 | 3.482 | 3.4824 | 3.4391 | 3.482 | 3.4824 | 3.4391 | 3.482 | 3.4824 | 3.4391 | 3.482 | 3.4824
WB-Wide Bay | 7190_Woolooga-Mungar 132 kV | Loading (MW) | 0.73913 | 0.48275 | 0.48101 | 0.73905 | 0.48269 | 0.48099 | 0.73905 | 0.48269 | 0.48099 | 0.73905 | 0.48269 | 0.48099 | 0.73905 | 0.48269 | 0.48099
WB-Wide Bay | 7190_Woolooga-Mungar 132 kV | Power Factor | 0.2149 | 0.13863 | 0.13812 | 0.2149 | 0.13863 | 0.13812 | 0.2149 | 0.13863 | 0.13812 | 0.2149 | 0.13863 | 0.13812 | 0.2149 | 0.13863 | 0.13812
WB-Wide Bay | 7190_Woolooga-Mungar 132 kV | Rating (A) | 564 | 600 | 542 | 564 | 600 | 542 | 564 | 600 | 542 | 564 | 600 | 542 | 564 | 600 | 542
WB-Wide Bay | 7190_Woolooga-Mungar 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB-Wide Bay | 7190_Woolooga-Mungar 132 kV | Min Voltage at Constrained Conductor | 138.6077 | 138.6086 | 138.602 | 138.6 | 138.6 | 138.6 | 138.6 | 138.6 | 138.6 | 138.6 | 138.6 | 138.6 | 138.6 | 138.6 | 138.6
WB-Wide Bay | 7190_Woolooga-Mungar 132 kV | Contingency Outage | M027_ISIS - Childers 66 kV | M027_ISIS - Childers 66 kV | M027_ISIS - Childers 66 kV | M029_Bundaberg - Farnsfield 66 kV | M033_Wallaville 66 kV | M027_ISIS - Childers 66 kV | M029_Bundaberg - Farnsfield 66 kV | M033_Wallaville 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV | M029_Bundaberg - Farnsfield 66 kV | M003_Kingaroy- Yarraman 66 kV | 7215_Bundaberg - ISIS No 1 132 kV | M029_Bundaberg - Farnsfield 66 kV | M003_Kingaroy- Yarraman 66 kV | 7329_Maryborough 132 kV
WB-Wide Bay | 7204_Bundaberg - Clayton 132 kV | % of Rated A | 0.9504% | 0.6258% | 0.9914% | 0.9508% | 0.6259% | 0.989% | 0.9599% | 0.6307% | 0.9994% | 0.9602% | 0.6298% | 0.9995% | 0.9608% | 0.6302% | 0.9997%
WB-Wide Bay | 7204_Bundaberg - Clayton 132 kV | Limiting Line Name | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1
WB-Wide Bay | 7204_Bundaberg - Clayton 132 kV | Loading (A) | 8.4206 | 6.1393 | 8.3179 | 8.4241 | 6.1403 | 8.2974 | 8.5048 | 6.1868 | 8.3854 | 8.5071 | 6.1787 | 8.3858 | 8.5126 | 6.1824 | 8.3872
WB-Wide Bay | 7204_Bundaberg - Clayton 132 kV | Loading (MVA) | 1.9642 | 1.428 | 1.9756 | 1.9639 | 1.4278 | 1.9775 | 1.9576 | 1.4209 | 1.97 | 1.9574 | 1.4221 | 1.9699 | 1.957 | 1.4215 | 1.9698
WB-Wide Bay | 7204_Bundaberg - Clayton 132 kV | Loading (MW) | 1.6522 | 1.1306 | 1.6542 | 1.6522 | 1.1306 | 1.6542 | 1.6522 | 1.1306 | 1.6542 | 1.6522 | 1.1306 | 1.6542 | 1.6522 | 1.1306 | 1.6542
WB-Wide Bay | 7204_Bundaberg - Clayton 132 kV | Power Factor | 0.84106 | 0.79173 | 0.83727 | 0.84118 | 0.79181 | 0.83643 | 0.84391 | 0.79568 | 0.83964 | 0.84399 | 0.79502 | 0.83966 | 0.84417 | 0.79532 | 0.8397
WB-Wide Bay | 7204_Bundaberg - Clayton 132 kV | Rating (A) | 886 | 981 | 839 | 886 | 981 | 839 | 886 | 981 | 839 | 886 | 981 | 839 | 886 | 981 | 839
WB-Wide Bay | 7204_Bundaberg - Clayton 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB-Wide Bay | 7204_Bundaberg - Clayton 132 kV | Min Voltage at Constrained Conductor | 134.6733 | 134.2879 | 137.1268 | 134.5999 | 134.2509 | 137.5997 | 132.8893 | 132.5961 | 135.6352 | 132.842 | 132.8805 | 135.6255 | 132.7281 | 132.7495 | 135.5962
WB-Wide Bay | 7204_Bundaberg - Clayton 132 kV | Contingency Outage | 7187_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | M027_ISIS - Childers 66 kV | 7187_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 7187_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV
WB-Wide Bay | 7215_Bundaberg - ISIS No 1 132 kV | % of Rated A | 86.75% | 54.48% | 49.86% | 87.07% | 54.63% | 50.74% | 96.32% | 60.44% | 56.62% | 96.55% | 60.69% | 56.7% | 96.36% | 60.58% | 56.67%
WB-Wide Bay | 7215_Bundaberg - ISIS No 1 132 kV | Limiting Line Name | TR_LINE 6780_2 | TR_LINE 6780_2 | TR_LINE 6780_2 | TR_LINE 6780_2 | TR_LINE 6780_2 | TR_LINE 6780_2 | TR_LINE 6780_2 | TR_LINE 6780_2 | TR_LINE 6780_2 | TR_LINE 6780_2 | TR_LINE 6780_2 | TR_LINE 6780_2 | TR_LINE 6780_2 | TR_LINE 6780_2 | TR_LINE 6780_2
WB-Wide Bay | 7215_Bundaberg - ISIS No 1 132 kV | Loading (A) | 215.1361 | 215.7576 | 195.9366 | 215.9263 | 216.337 | 199.4002 | 238.8807 | 239.337 | 222.5054 | 239.4524 | 240.3126 | 222.8239 | 238.9685 | 239.9091 | 222.7103
WB-Wide Bay | 7215_Bundaberg - ISIS No 1 132 kV | Loading (MVA) | 50.772 | 50.8101 | 46.8022 | 50.9023 | 50.91 | 47.5959 | 55.6022 | 55.6314 | 52.606 | 55.7275 | 56.1065 | 52.6785 | 55.5797 | 55.9803 | 52.643
WB-Wide Bay | 7215_Bundaberg - ISIS No 1 132 kV | Loading (MW) | 47.793 | 47.9313 | 44.569 | 47.2269 | 47.3897 | 44.9542 | 49.9984 | 50.4197 | 48.6598 | 50.1594 | 51.8878 | 48.7279 | 50.0871 | 51.7958 | 48.6713
WB-Wide Bay | 7215_Bundaberg - ISIS No 1 132 kV | Power Factor | 0.93866 | 0.9406 | 0.95228 | 0.92457 | 0.92761 | 0.94438 | 0.89094 | 0.89824 | 0.9208 | 0.89175 | 0.91764 | 0.92077 | 0.89294 | 0.91814 | 0.92031
WB-Wide Bay | 7215_Bundaberg - ISIS No 1 132 kV | Rating (A) | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393
WB-Wide Bay | 7215_Bundaberg - ISIS No 1 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB-Wide Bay | 7215_Bundaberg - ISIS No 1 132 kV | Min Voltage at Constrained Conductor | 136.2544 | 135.9638 | 137.8274 | 136.1041 | 135.8664 | 137.8108 | 134.3849 | 134.1991 | 136.5005 | 134.366 | 134.7956 | 136.4932 | 134.2811 | 134.7186 | 136.4708
WB-Wide Bay | 7215_Bundaberg - ISIS No 1 132 kV | Contingency Outage | 7328_Bundaberg - ISIS No 2 132 kV | 7328_Bundaberg - ISIS No 2 132 kV | 7328_Bundaberg - ISIS No 2 132 kV | 7328_Bundaberg - ISIS No 2 132 kV | 7328_Bundaberg - ISIS No 2 132 kV | 7328_Bundaberg - ISIS No 2 132 kV | 7328_Bundaberg - ISIS No 2 132 kV | 7328_Bundaberg - ISIS No 2 132 kV | 7328_Bundaberg - ISIS No 2 132 kV | 7328_Bundaberg - ISIS No 2 132 kV | 7328_Bundaberg - ISIS No 2 132 kV | 7328_Bundaberg - ISIS No 2 132 kV | 7328_Bundaberg - ISIS No 2 132 kV | 7328_Bundaberg - ISIS No 2 132 kV | 7328_Bundaberg - ISIS No 2 132 kV
WB-Wide Bay | 7315_Aramara 132 kV | % of Rated A | 40.9% | 37.97% | 14.32% | 39.06% | 36.23% | 14.28% | 40.14% | 37.32% | 13.66% | 40.4% | 36.85% | 13.8% | 40.87% | 37.33% | 14%
WB-Wide Bay | 7315_Aramara 132 kV | Limiting Line Name | TR_LINE 86019_1 | TR_LINE 86019_1 | TR_LINE 88000_1 | TR_LINE 86019_1 | TR_LINE 86019_1 | TR_LINE 88000_1 | TR_LINE 86019_1 | TR_LINE 86019_1 | TR_LINE 86019_1 | TR_LINE 86019_1 | TR_LINE 86019_1 | TR_LINE 86019_1 | TR_LINE 86019_1 | TR_LINE 86019_1 | TR_LINE 86019_1
WB-Wide Bay | 7315_Aramara 132 kV | Loading (A) | 446.6728 | 457.554 | 158.5203 | 426.5553 | 436.6088 | 158.0993 | 438.3198 | 449.673 | 151.2628 | 441.1684 | 444.0991 | 152.7499 | 446.2794 | 449.8242 | 155.0057
WB-Wide Bay | 7315_Aramara 132 kV | Loading (MVA) | 105.2565 | 107.673 | 37.9444 | 100.6807 | 102.9555 | 37.8612 | 102.7457 | 105.3089 | 35.9542 | 103.3795 | 104.1962 | 36.3036 | 104.4907 | 105.4375 | 36.8384
WB-Wide Bay | 7315_Aramara 132 kV | Loading (MW) | 100.1768 | 102.3982 | 37.8944 | 95.6618 | 97.8686 | 37.7348 | 95.3207 | 97.8943 | 35.7605 | 95.9137 | 97.4391 | 36.1037 | 96.8413 | 98.4644 | 36.6449
WB-Wide Bay | 7315_Aramara 132 kV | Power Factor | 0.95174 | 0.95101 | 0.99868 | 0.95015 | 0.95059 | 0.99666 | 0.92773 | 0.92959 | 0.9946 | 0.92778 | 0.93515 | 0.99448 | 0.92679 | 0.93387 | 0.99474
WB-Wide Bay | 7315_Aramara 132 kV | Rating (A) | 1092 | 1205 | 1107 | 1092 | 1205 | 1107 | 1092 | 1205 | 1107 | 1092 | 1205 | 1107 | 1092 | 1205 | 1107
WB-Wide Bay | 7315_Aramara 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB-Wide Bay | 7315_Aramara 132 kV | Min Voltage at Constrained Conductor | 136.0386 | 135.8518 | 138.1966 | 136.2623 | 136.1322 | 138.2614 | 135.3229 | 135.1965 | 137.2325 | 135.2784 | 135.4475 | 137.2172 | 135.1662 | 135.3164 | 137.2121
WB-Wide Bay | 7315_Aramara 132 kV | Contingency Outage | 7316_Aramara 132 kV | 7316_Aramara 132 kV | 7316_Aramara 132 kV | 7316_Aramara 132 kV | 7316_Aramara 132 kV | 7316_Aramara 132 kV | 7316_Aramara 132 kV | 7316_Aramara 132 kV | 7316_Aramara 132 kV | 7316_Aramara 132 kV | 7316_Aramara 132 kV | 7316_Aramara 132 kV | 7316_Aramara 132 kV | 7316_Aramara 132 kV | 7316_Aramara 132 kV
WB-Wide Bay | 7316_Aramara 132 kV | % of Rated A | 40.9% | 37.97% | 14.32% | 39.06% | 36.23% | 14.28% | 40.14% | 37.32% | 13.66% | 40.4% | 36.85% | 13.8% | 40.87% | 37.33% | 14%
WB-Wide Bay | 7316_Aramara 132 kV | Limiting Line Name | TR_LINE 88015_1 | TR_LINE 88015_1 | TR_LINE 88004_1 | TR_LINE 88015_1 | TR_LINE 88015_1 | TR_LINE 88004_1 | TR_LINE 88015_1 | TR_LINE 88015_1 | TR_LINE 88015_1 | TR_LINE 88015_1 | TR_LINE 88015_1 | TR_LINE 88015_1 | TR_LINE 88015_1 | TR_LINE 88015_1 | TR_LINE 88015_1
WB-Wide Bay | 7316_Aramara 132 kV | Loading (A) | 446.6635 | 457.5446 | 158.5161 | 426.5451 | 436.5935 | 158.0949 | 438.3088 | 449.6617 | 151.2586 | 441.1573 | 444.088 | 152.7456 | 446.2682 | 449.8129 | 155.0014
WB-Wide Bay | 7316_Aramara 132 kV | Loading (MVA) | 105.254 | 107.6705 | 37.9434 | 100.678 | 102.952 | 37.8601 | 102.7429 | 105.306 | 35.9532 | 103.3767 | 104.1933 | 36.3026 | 104.4878 | 105.4346 | 36.8374
WB-Wide Bay | 7316_Aramara 132 kV | Loading (MW) | 100.1742 | 102.3956 | 37.8934 | 95.6591 | 97.8657 | 37.7337 | 95.318 | 97.8915 | 35.7594 | 95.911 | 97.4362 | 36.1027 | 96.8386 | 98.4616 | 36.6438
WB-Wide Bay | 7316_Aramara 132 kV | Power Factor | 0.95174 | 0.95101 | 0.99868 | 0.95015 | 0.9506 | 0.99666 | 0.92773 | 0.92959 | 0.9946 | 0.92778 | 0.93515 | 0.99448 | 0.92679 | 0.93386 | 0.99474
WB-Wide Bay | 7316_Aramara 132 kV | Rating (A) | 1092 | 1205 | 1107 | 1092 | 1205 | 1107 | 1092 | 1205 | 1107 | 1092 | 1205 | 1107 | 1092 | 1205 | 1107
WB-Wide Bay | 7316_Aramara 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB-Wide Bay | 7316_Aramara 132 kV | Min Voltage at Constrained Conductor | 136.0381 | 135.8514 | 138.1966 | 136.2619 | 136.1322 | 138.2615 | 135.3225 | 135.1961 | 137.2324 | 135.278 | 135.4471 | 137.2172 | 135.1658 | 135.316 | 137.212
WB-Wide Bay | 7316_Aramara 132 kV | Contingency Outage | 7315_Aramara 132 kV | 7315_Aramara 132 kV | 7315_Aramara 132 kV | 7315_Aramara 132 kV | 7315_Aramara 132 kV | 7315_Aramara 132 kV | 7315_Aramara 132 kV | 7315_Aramara 132 kV | 7315_Aramara 132 kV | 7315_Aramara 132 kV | 7315_Aramara 132 kV | 7315_Aramara 132 kV | 7315_Aramara 132 kV | 7315_Aramara 132 kV | 7315_Aramara 132 kV
WB-Wide Bay | 7328_Bundaberg - ISIS No 2 132 kV | % of Rated A | 86.69% | 54.45% | 49.82% | 87.01% | 54.59% | 50.7% | 96.25% | 60.4% | 56.58% | 96.48% | 60.64% | 56.66% | 96.29% | 60.54% | 56.63%
WB-Wide Bay | 7328_Bundaberg - ISIS No 2 132 kV | Limiting Line Name | TR_LINE 98484_1 | TR_LINE 98484_1 | TR_LINE 98484_1 | TR_LINE 98484_1 | TR_LINE 98484_1 | TR_LINE 98484_1 | TR_LINE 98484_1 | TR_LINE 98484_1 | TR_LINE 98484_1 | TR_LINE 98484_1 | TR_LINE 98484_1 | TR_LINE 98484_1 | TR_LINE 98484_1 | TR_LINE 98484_1 | TR_LINE 98484_1
WB-Wide Bay | 7328_Bundaberg - ISIS No 2 132 kV | Loading (A) | 214.9845 | 215.605 | 195.8008 | 215.7745 | 216.1843 | 199.2618 | 238.7107 | 239.166 | 222.3484 | 239.2819 | 240.1403 | 222.6678 | 238.7982 | 239.737 | 222.5543
WB-Wide Bay | 7328_Bundaberg - ISIS No 2 132 kV | Loading (MVA) | 50.736 | 50.774 | 46.7698 | 50.866 | 50.8737 | 47.5627 | 55.5616 | 55.5907 | 52.5683 | 55.6867 | 56.0656 | 52.6411 | 55.539 | 55.9395 | 52.6056
WB-Wide Bay | 7328_Bundaberg - ISIS No 2 132 kV | Loading (MW) | 47.7599 | 47.8981 | 44.5382 | 47.1943 | 47.3568 | 44.9231 | 49.9642 | 50.3852 | 48.6267 | 50.1251 | 51.8521 | 48.6947 | 50.0529 | 51.7602 | 48.6381
WB-Wide Bay | 7328_Bundaberg - ISIS No 2 132 kV | Power Factor | 0.94119 | 0.94321 | 0.95229 | 0.92763 | 0.93069 | 0.94449 | 0.89881 | 0.90592 | 0.92479 | 0.89967 | 0.92446 | 0.9248 | 0.90077 | 0.92491 | 0.92435
WB-Wide Bay | 7328_Bundaberg - ISIS No 2 132 kV | Rating (A) | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393
WB-Wide Bay | 7328_Bundaberg - ISIS No 2 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB-Wide Bay | 7328_Bundaberg - ISIS No 2 132 kV | Min Voltage at Constrained Conductor | 136.2538 | 135.9634 | 137.9042 | 136.1028 | 135.8653 | 137.8105 | 134.3823 | 134.1969 | 136.499 | 134.3635 | 134.7941 | 136.4918 | 134.2786 | 134.7171 | 136.4694
WB-Wide Bay | 7328_Bundaberg - ISIS No 2 132 kV | Contingency Outage | 7215_Bundaberg - ISIS No 1 132 kV | 7215_Bundaberg - ISIS No 1 132 kV | 7215_Bundaberg - ISIS No 1 132 kV | 7215_Bundaberg - ISIS No 1 132 kV | 7215_Bundaberg - ISIS No 1 132 kV | 7215_Bundaberg - ISIS No 1 132 kV | 7215_Bundaberg - ISIS No 1 132 kV | 7215_Bundaberg - ISIS No 1 132 kV | 7215_Bundaberg - ISIS No 1 132 kV | 7215_Bundaberg - ISIS No 1 132 kV | 7215_Bundaberg - ISIS No 1 132 kV | 7215_Bundaberg - ISIS No 1 132 kV | 7215_Bundaberg - ISIS No 1 132 kV | 7215_Bundaberg - ISIS No 1 132 kV | 7215_Bundaberg - ISIS No 1 132 kV
WB-Wide Bay | 7329_Maryborough 132 kV | % of Rated A | 84.33% | 77.99% | 45.1% | 77.11% | 70.71% | 43.93% | 78.38% | 71.96% | 44.77% | 78.93% | 72.52% | 45.01% | 79.63% | 73.18% | 45.4%
WB-Wide Bay | 7329_Maryborough 132 kV | Limiting Line Name | TR_LINE 156753_1 | TR_LINE 156753_1 | TR_LINE 120325_1 | TR_LINE 156753_1 | TR_LINE 156753_1 | TR_LINE 120325_1 | TR_LINE 156753_1 | TR_LINE 156753_1 | TR_LINE 120325_1 | TR_LINE 156753_1 | TR_LINE 156753_1 | TR_LINE 120325_1 | TR_LINE 156753_1 | TR_LINE 156753_1 | TR_LINE 120325_1
WB-Wide Bay | 7329_Maryborough 132 kV | Loading (A) | 475.6412 | 467.9202 | 244.466 | 434.9123 | 424.2341 | 238.1104 | 442.0361 | 431.7662 | 242.6641 | 445.1615 | 435.1479 | 243.9554 | 449.1078 | 439.0647 | 246.0513
WB-Wide Bay | 7329_Maryborough 132 kV | Loading (MVA) | 112.0133 | 110.0878 | 58.4161 | 102.6611 | 100.1194 | 56.9508 | 103.6559 | 101.1894 | 57.7268 | 104.3429 | 102.121 | 58.0282 | 105.179 | 102.9722 | 58.5252
WB-Wide Bay | 7329_Maryborough 132 kV | Loading (MW) | 110.8894 | 109.044 | 57.861 | 101.8005 | 99.44 | 55.9337 | 102.7503 | 100.4194 | 56.7752 | 103.3745 | 101.2746 | 57.12 | 104.131 | 102.103 | 57.5754
WB-Wide Bay | 7329_Maryborough 132 kV | Power Factor | 0.98997 | 0.99052 | 0.99025 | 0.99162 | 0.99321 | 0.98184 | 0.99126 | 0.99239 | 0.98318 | 0.99072 | 0.99171 | 0.98401 | 0.99004 | 0.99156 | 0.98341
WB-Wide Bay | 7329_Maryborough 132 kV | Rating (A) | 564 | 600 | 542 | 564 | 600 | 542 | 564 | 600 | 542 | 564 | 600 | 542 | 564 | 600 | 542
WB-Wide Bay | 7329_Maryborough 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB-Wide Bay | 7329_Maryborough 132 kV | Min Voltage at Constrained Conductor | 131.9521 | 131.9149 | 137.7918 | 132.7063 | 132.8481 | 137.97 | 131.7292 | 131.7951 | 137.2161 | 131.6162 | 131.9174 | 137.1978 | 131.435 | 131.7865 | 137.196
WB-Wide Bay | 7329_Maryborough 132 kV | Contingency Outage | 7330_Maryborough 132 kV | 7330_Maryborough 132 kV | 7330_Maryborough 132 kV | 7330_Maryborough 132 kV | 7330_Maryborough 132 kV | 7330_Maryborough 132 kV | 7330_Maryborough 132 kV | 7330_Maryborough 132 kV | 7330_Maryborough 132 kV | 7330_Maryborough 132 kV | 7330_Maryborough 132 kV | 7330_Maryborough 132 kV | 7330_Maryborough 132 kV | 7330_Maryborough 132 kV | 7330_Maryborough 132 kV
WB-Wide Bay | 7330_Maryborough 132 kV | % of Rated A | 84.34% | 77.99% | 45.1% | 77.11% | 70.71% | 43.93% | 78.37% | 71.96% | 44.77% | 78.93% | 72.52% | 45.01% | 79.63% | 73.18% | 45.4%
WB-Wide Bay | 7330_Maryborough 132 kV | Limiting Line Name | TR_LINE 156755_1 | TR_LINE 156755_1 | TR_LINE 7684_1 | TR_LINE 156755_1 | TR_LINE 156755_1 | TR_LINE 7684_1 | TR_LINE 156755_1 | TR_LINE 156755_1 | TR_LINE 7684_1 | TR_LINE 156755_1 | TR_LINE 156755_1 | TR_LINE 7684_1 | TR_LINE 156755_1 | TR_LINE 156755_1 | TR_LINE 7684_1
WB-Wide Bay | 7330_Maryborough 132 kV | Loading (A) | 475.6506 | 467.9292 | 244.4659 | 434.9088 | 424.2303 | 238.105 | 442.0325 | 431.7623 | 242.6586 | 445.158 | 435.1442 | 243.9499 | 449.1045 | 439.0611 | 246.0458
WB-Wide Bay | 7330_Maryborough 132 kV | Loading (MVA) | 112.0151 | 110.0895 | 58.4159 | 102.66 | 100.1183 | 56.9495 | 103.6549 | 101.1882 | 57.7253 | 104.3418 | 102.1199 | 58.0268 | 105.1779 | 102.9711 | 58.5238
WB-Wide Bay | 7330_Maryborough 132 kV | Loading (MW) | 110.8906 | 109.0452 | 57.8608 | 101.799 | 99.4385 | 55.9324 | 102.7488 | 100.4179 | 56.7739 | 103.3729 | 101.2731 | 57.1186 | 104.1295 | 102.1015 | 57.574
WB-Wide Bay | 7330_Maryborough 132 kV | Power Factor | 0.98996 | 0.99051 | 0.99025 | 0.99161 | 0.99321 | 0.98184 | 0.99126 | 0.99239 | 0.98318 | 0.99071 | 0.99171 | 0.98401 | 0.99003 | 0.99155 | 0.98341
WB-Wide Bay | 7330_Maryborough 132 kV | Rating (A) | 564 | 600 | 542 | 564 | 600 | 542 | 564 | 600 | 542 | 564 | 600 | 542 | 564 | 600 | 542
WB-Wide Bay | 7330_Maryborough 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB-Wide Bay | 7330_Maryborough 132 kV | Min Voltage at Constrained Conductor | 131.9498 | 131.9126 | 137.7921 | 132.7045 | 132.8464 | 137.9703 | 131.7273 | 131.7932 | 137.2164 | 131.6143 | 131.9155 | 137.1981 | 131.433 | 131.7846 | 137.1963
WB-Wide Bay | 7330_Maryborough 132 kV | Contingency Outage | 7329_Maryborough 132 kV | 7329_Maryborough 132 kV | 7329_Maryborough 132 kV | 7329_Maryborough 132 kV | 7329_Maryborough 132 kV | 7329_Maryborough 132 kV | 7329_Maryborough 132 kV | 7329_Maryborough 132 kV | 7329_Maryborough 132 kV | 7329_Maryborough 132 kV | 7329_Maryborough 132 kV | 7329_Maryborough 132 kV | 7329_Maryborough 132 kV | 7329_Maryborough 132 kV | 7329_Maryborough 132 kV
WB-Wide Bay | 764_Woolooga-Kilkivan No 1 132 kV | % of Rated A | 13.19% | 8.647% | 4.27% | 24.44% | 15.76% | 6.922% | 24.91% | 16.12% | 7.053% | 25.58% | 16.61% | 7.238% | 25.85% | 16.8% | 7.316%
WB-Wide Bay | 764_Woolooga-Kilkivan No 1 132 kV | Limiting Line Name | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1
WB-Wide Bay | 764_Woolooga-Kilkivan No 1 132 kV | Loading (A) | 32.7161 | 34.244 | 16.7821 | 60.6065 | 62.4277 | 27.2034 | 61.7724 | 63.8542 | 27.7189 | 63.4423 | 65.7591 | 28.4458 | 64.1188 | 66.5238 | 28.7527
WB-Wide Bay | 764_Woolooga-Kilkivan No 1 132 kV | Loading (MVA) | 7.84 | 8.2051 | 4.0288 | 14.4967 | 14.93 | 6.5291 | 14.7741 | 15.2691 | 6.6475 | 15.1712 | 15.7219 | 6.8214 | 15.3321 | 15.9037 | 6.8949
WB-Wide Bay | 764_Woolooga-Kilkivan No 1 132 kV | Loading (MW) | 7.5372 | 7.8628 | 3.9535 | 13.9466 | 14.3321 | 6.505 | 14.1935 | 14.6306 | 6.6243 | 14.5445 | 15.0274 | 6.7922 | 14.6879 | 15.189 | 6.8634
WB-Wide Bay | 764_Woolooga-Kilkivan No 1 132 kV | Power Factor | 0.96025 | 0.9571 | 0.9813 | 0.95992 | 0.95776 | 0.9961 | 0.95853 | 0.95593 | 0.99553 | 0.95646 | 0.95351 | 0.99471 | 0.95573 | 0.95272 | 0.99441
WB-Wide Bay | 764_Woolooga-Kilkivan No 1 132 kV | Rating (A) | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393
WB-Wide Bay | 764_Woolooga-Kilkivan No 1 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB-Wide Bay | 764_Woolooga-Kilkivan No 1 132 kV | Min Voltage at Constrained Conductor | 138.3541 | 138.3368 | 138.5324 | 138.0989 | 138.0768 | 138.4651 | 138.0847 | 138.0591 | 138.4594 | 138.0642 | 138.0353 | 138.4515 | 138.0561 | 138.0262 | 138.4484
WB-Wide Bay | 764_Woolooga-Kilkivan No 1 132 kV | Contingency Outage | M027_ISIS - Childers 66 kV | M027_ISIS - Childers 66 kV | M027_ISIS - Childers 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV
WB-Wide Bay | 765_Woolooga-Kilkivan No 2 132 kV | % of Rated A | 13.19% | 8.647% | 4.27% | 24.44% | 15.76% | 6.922% | 24.91% | 16.12% | 7.053% | 25.58% | 16.61% | 7.238% | 25.85% | 16.8% | 7.316%
WB-Wide Bay | 765_Woolooga-Kilkivan No 2 132 kV | Limiting Line Name | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1
WB-Wide Bay | 765_Woolooga-Kilkivan No 2 132 kV | Loading (A) | 32.714 | 34.2418 | 16.781 | 60.6061 | 62.4274 | 27.2033 | 61.772 | 63.8538 | 27.7187 | 63.4419 | 65.7587 | 28.4456 | 64.1184 | 66.5234 | 28.7526
WB-Wide Bay | 765_Woolooga-Kilkivan No 2 132 kV | Loading (MVA) | 7.8395 | 8.2045 | 4.0286 | 14.4966 | 14.9299 | 6.5291 | 14.774 | 15.269 | 6.6475 | 15.1711 | 15.7218 | 6.8214 | 15.332 | 15.9036 | 6.8949
WB-Wide Bay | 765_Woolooga-Kilkivan No 2 132 kV | Loading (MW) | 7.5367 | 7.8623 | 3.9532 | 13.9465 | 14.332 | 6.505 | 14.1934 | 14.6305 | 6.6243 | 14.5444 | 15.0273 | 6.7922 | 14.6878 | 15.1889 | 6.8633
WB-Wide Bay | 765_Woolooga-Kilkivan No 2 132 kV | Power Factor | 0.96025 | 0.9571 | 0.9813 | 0.95992 | 0.95776 | 0.9961 | 0.95853 | 0.95593 | 0.99553 | 0.95646 | 0.95351 | 0.99471 | 0.95573 | 0.95272 | 0.99441
WB-Wide Bay | 765_Woolooga-Kilkivan No 2 132 kV | Rating (A) | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393
WB-Wide Bay | 765_Woolooga-Kilkivan No 2 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB-Wide Bay | 765_Woolooga-Kilkivan No 2 132 kV | Min Voltage at Constrained Conductor | 138.3541 | 138.3368 | 138.5324 | 138.0988 | 138.0768 | 138.4651 | 138.0847 | 138.0591 | 138.4594 | 138.0642 | 138.0353 | 138.4515 | 138.0561 | 138.0261 | 138.4484
WB-Wide Bay | 765_Woolooga-Kilkivan No 2 132 kV | Contingency Outage | M027_ISIS - Childers 66 kV | M027_ISIS - Childers 66 kV | M027_ISIS - Childers 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV
WB-Wide Bay | 784_ISIS 132 kV | % of Rated A | 40.13% | 27.57% | 18.71% | 42.78% | 29.71% | 19.23% | 55.1% | 37.03% | 25.41% | 54.83% | 34.17% | 25.32% | 55.03% | 34.5% | 25.4%
WB-Wide Bay | 784_ISIS 132 kV | Limiting Line Name | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1
WB-Wide Bay | 784_ISIS 132 kV | Loading (A) | 99.5246 | 109.1835 | 73.5339 | 106.1022 | 117.6712 | 75.5908 | 136.6385 | 146.6561 | 99.8681 | 135.9679 | 135.3021 | 99.4919 | 136.479 | 136.6255 | 99.8415
WB-Wide Bay | 784_ISIS 132 kV | Loading (MVA) | 23.4058 | 25.595 | 17.5412 | 24.9544 | 27.5966 | 18.03 | 31.8125 | 34.0482 | 23.6307 | 31.6508 | 31.5158 | 23.5409 | 31.7514 | 31.7929 | 23.6197
WB-Wide Bay | 784_ISIS 132 kV | Loading (MW) | 1.086 | 4.9165 | 13.6112 | 3.0428 | 7.372 | 13.0054 | 2.4323 | 7.0635 | 15.5157 | 2.4587 | 5.7894 | 15.4888 | 2.6961 | 6.0855 | 15.3599
WB-Wide Bay | 784_ISIS 132 kV | Power Factor | 0.045689 | 0.1913 | 0.77596 | 0.12117 | 0.26629 | 0.72132 | 0.075468 | 0.20639 | 0.65659 | 0.076699 | 0.18272 | 0.65795 | 0.083925 | 0.19042 | 0.6503
WB-Wide Bay | 784_ISIS 132 kV | Rating (A) | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393
WB-Wide Bay | 784_ISIS 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB-Wide Bay | 784_ISIS 132 kV | Min Voltage at Constrained Conductor | 135.7787 | 135.3437 | 137.7247 | 135.7883 | 135.4019 | 137.7101 | 134.4199 | 134.0398 | 136.6121 | 134.3964 | 134.4815 | 136.6076 | 134.3186 | 134.3502 | 136.585
WB-Wide Bay | 784_ISIS 132 kV | Contingency Outage | 785_ISIS 132 kV | 785_ISIS 132 kV | 785_ISIS 132 kV | 785_ISIS 132 kV | 785_ISIS 132 kV | 785_ISIS 132 kV | 785_ISIS 132 kV | 785_ISIS 132 kV | 785_ISIS 132 kV | 785_ISIS 132 kV | 785_ISIS 132 kV | 785_ISIS 132 kV | 785_ISIS 132 kV | 785_ISIS 132 kV | 785_ISIS 132 kV
WB-Wide Bay | 785_ISIS 132 kV | % of Rated A | 40.27% | 27.66% | 18.78% | 42.93% | 29.81% | 19.31% | 55.32% | 37.19% | 25.51% | 55.05% | 34.3% | 25.42% | 55.25% | 34.64% | 25.51%
WB-Wide Bay | 785_ISIS 132 kV | Limiting Line Name | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1
WB-Wide Bay | 785_ISIS 132 kV | Loading (A) | 99.8735 | 109.5503 | 73.8161 | 106.4734 | 118.0661 | 75.8844 | 137.1884 | 147.2536 | 100.2659 | 136.5149 | 135.8365 | 99.888 | 137.0272 | 137.1639 | 100.2397
WB-Wide Bay | 785_ISIS 132 kV | Loading (MVA) | 23.486 | 25.679 | 17.6076 | 25.0398 | 27.6871 | 18.099 | 31.9368 | 34.1826 | 23.7231 | 31.7744 | 31.6367 | 23.633 | 31.8752 | 31.9146 | 23.7122
WB-Wide Bay | 785_ISIS 132 kV | Loading (MW) | 1.0531 | 4.8915 | 13.6669 | 3.0143 | 7.3523 | 13.0599 | 2.3868 | 7.0289 | 15.5826 | 2.4137 | 5.7564 | 15.5556 | 2.6516 | 6.0528 | 15.4263
WB-Wide Bay | 785_ISIS 132 kV | Power Factor | 0.044813 | 0.19046 | 0.77619 | 0.12035 | 0.26552 | 0.72158 | 0.074697 | 0.20559 | 0.65685 | 0.075926 | 0.18192 | 0.65821 | 0.083148 | 0.18962 | 0.65056
WB-Wide Bay | 785_ISIS 132 kV | Rating (A) | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393 | 248 | 396 | 393
WB-Wide Bay | 785_ISIS 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB-Wide Bay | 785_ISIS 132 kV | Min Voltage at Constrained Conductor | 135.7683 | 135.3331 | 137.7171 | 135.7779 | 135.3914 | 137.7023 | 134.4043 | 134.0228 | 136.6024 | 134.3808 | 134.4663 | 136.598 | 134.303 | 134.335 | 136.5753
WB-Wide Bay | 785_ISIS 132 kV | Contingency Outage | 784_ISIS 132 kV | 784_ISIS 132 kV | 784_ISIS 132 kV | 784_ISIS 132 kV | 784_ISIS 132 kV | 784_ISIS 132 kV | 784_ISIS 132 kV | 784_ISIS 132 kV | 784_ISIS 132 kV | 784_ISIS 132 kV | 784_ISIS 132 kV | 784_ISIS 132 kV | 784_ISIS 132 kV | 784_ISIS 132 kV | 784_ISIS 132 kV
WB-Wide Bay | 786_Gin Gin - Bundaberg 132 kV | % of Rated A | 205.2% | 122.6% | 87.25% | 202.1% | 120.9% | 86.8% | 203.7% | 122.1% | 87.09% | 204.1% | 122.2% | 87.24% | 205.2% | 123% | 87.54%
WB-Wide Bay | 786_Gin Gin - Bundaberg 132 kV | Limiting Line Name | TR_LINE 112963_1 | TR_LINE 112963_1 | TR_LINE 112963_1 | TR_LINE 112963_1 | TR_LINE 112963_1 | TR_LINE 112963_1 | TR_LINE 112963_1 | TR_LINE 112963_1 | TR_LINE 112963_1 | TR_LINE 112963_1 | TR_LINE 112963_1 | TR_LINE 112963_1 | TR_LINE 112963_1 | TR_LINE 112963_1 | TR_LINE 112963_1
WB-Wide Bay | 786_Gin Gin - Bundaberg 132 kV | Loading (A) | 580.5946 | 589.6366 | 420.564 | 571.8703 | 581.5811 | 418.3905 | 576.3361 | 587.4869 | 419.7768 | 577.6781 | 587.8714 | 420.4878 | 580.8094 | 591.3961 | 421.931
WB-Wide Bay | 786_Gin Gin - Bundaberg 132 kV | Loading (MVA) | 138.9562 | 141.0172 | 100.1991 | 136.8515 | 139.0807 | 99.6641 | 139.5612 | 142.1434 | 100.1087 | 139.8784 | 140.5198 | 100.2733 | 140.5953 | 141.3206 | 100.606
WB-Wide Bay | 786_Gin Gin - Bundaberg 132 kV | Loading (MW) | 138.9089 | 141.0019 | 97.7697 | 136.8171 | 139.0707 | 97.3547 | 139.5528 | 142.1077 | 97.8484 | 139.8693 | 140.5184 | 98.0317 | 140.5768 | 141.3206 | 98.4164
WB-Wide Bay | 786_Gin Gin - Bundaberg 132 kV | Power Factor | 0.9989 | 0.99935 | 0.97271 | 0.99908 | 0.99946 | 0.97388 | 0.99994 | 0.99975 | 0.9745 | 0.99994 | 0.99967 | 0.97473 | 0.99987 | 0.99979 | 0.97534
WB-Wide Bay | 786_Gin Gin - Bundaberg 132 kV | Rating (A) | 283 | 481 | 482 | 283 | 481 | 482 | 283 | 481 | 482 | 283 | 481 | 482 | 283 | 481 | 482
WB-Wide Bay | 786_Gin Gin - Bundaberg 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB-Wide Bay | 786_Gin Gin - Bundaberg 132 kV | Min Voltage at Constrained Conductor | 137.444 | 137.2937 | 137.4913 | 137.4256 | 137.2849 | 137.4555 | 138.9529 | 138.7881 | 137.6057 | 138.942 | 137.1876 | 137.5962 | 138.8827 | 137.1242 | 137.5733
WB-Wide Bay | 786_Gin Gin - Bundaberg 132 kV | Contingency Outage | 7187_Gin Gin - Bundaberg 132 kV | 7187_Gin Gin - Bundaberg 132 kV | 7187_Gin Gin - Bundaberg 132 kV | 7187_Gin Gin - Bundaberg 132 kV | 7187_Gin Gin - Bundaberg 132 kV | 7187_Gin Gin - Bundaberg 132 kV | 7187_Gin Gin - Bundaberg 132 kV | 7187_Gin Gin - Bundaberg 132 kV | 7187_Gin Gin - Bundaberg 132 kV | 7187_Gin Gin - Bundaberg 132 kV | 7187_Gin Gin - Bundaberg 132 kV | 7187_Gin Gin - Bundaberg 132 kV | 7187_Gin Gin - Bundaberg 132 kV | 7187_Gin Gin - Bundaberg 132 kV | 7187_Gin Gin - Bundaberg 132 kV
WB-Wide Bay | M001_Tarong-Kingaroy East 66 kV | % of Rated A | 65.51% | 56.51% | 30.62% | 65.26% | 56.06% | 30.64% | 64.87% | 55.75% | 30.47% | 64.87% | 55.75% | 30.47% | 65.42% | 56.18% | 30.72%
WB-Wide Bay | M001_Tarong-Kingaroy East 66 kV | Limiting Line Name | TR_LINE 7253_1 | TR_LINE 7253_1 | TR_LINE 7253_1 | TR_LINE 7253_1 | TR_LINE 7253_1 | TR_LINE 7253_1 | TR_LINE 7253_1 | TR_LINE 7253_1 | TR_LINE 7253_1 | TR_LINE 7253_1 | TR_LINE 7253_1 | TR_LINE 7253_1 | TR_LINE 7253_1 | TR_LINE 7253_1 | TR_LINE 7253_1
WB-Wide Bay | M001_Tarong-Kingaroy East 66 kV | Loading (A) | 359.0152 | 327.1982 | 159.5085 | 357.6285 | 324.6019 | 159.6377 | 355.5004 | 322.7715 | 158.7456 | 355.5037 | 322.7771 | 158.7462 | 358.5234 | 325.2555 | 160.0604
WB-Wide Bay | M001_Tarong-Kingaroy East 66 kV | Loading (MVA) | 42.5623 | 38.3528 | 18.8076 | 42.4022 | 38.0555 | 18.8222 | 42.1563 | 37.8456 | 18.7189 | 42.1564 | 37.8457 | 18.7189 | 42.5045 | 38.129 | 18.8725
WB-Wide Bay | M001_Tarong-Kingaroy East 66 kV | Loading (MW) | 40.1726 | 36.4323 | 18.4104 | 40.0376 | 36.1736 | 18.4213 | 39.8237 | 35.9881 | 18.3243 | 39.8237 | 35.9881 | 18.3243 | 40.1244 | 36.236 | 18.4686
WB-Wide Bay | M001_Tarong-Kingaroy East 66 kV | Power Factor | 0.94385 | 0.94993 | 0.97888 | 0.94423 | 0.95055 | 0.9787 | 0.94467 | 0.95092 | 0.97892 | 0.94467 | 0.95092 | 0.97892 | 0.944 | 0.95035 | 0.9786
WB-Wide Bay | M001_Tarong-Kingaroy East 66 kV | Rating (A) | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521
WB-Wide Bay | M001_Tarong-Kingaroy East 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB-Wide Bay | M001_Tarong-Kingaroy East 66 kV | Min Voltage at Constrained Conductor | 64.4295 | 64.1118 | 66.7405 | 64.4584 | 64.163 | 66.7356 | 64.5 | 64.1976 | 66.7541 | 64.4994 | 64.1965 | 66.7538 | 64.4384 | 64.1471 | 66.7315
WB-Wide Bay | M001_Tarong-Kingaroy East 66 kV | Contingency Outage | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV
WB-Wide Bay | M002_Tarong-Kingaroy West 66 kV | % of Rated A | 65.51% | 56.51% | 30.62% | 65.26% | 56.06% | 30.64% | 64.87% | 55.74% | 30.47% | 64.87% | 55.74% | 30.47% | 65.42% | 56.17% | 30.72%
WB-Wide Bay | M002_Tarong-Kingaroy West 66 kV | Limiting Line Name | TR_LINE 7252_1 | TR_LINE 7252_1 | TR_LINE 7252_1 | TR_LINE 7252_1 | TR_LINE 7252_1 | TR_LINE 7252_1 | TR_LINE 7252_1 | TR_LINE 7252_1 | TR_LINE 7252_1 | TR_LINE 7252_1 | TR_LINE 7252_1 | TR_LINE 7252_1 | TR_LINE 7252_1 | TR_LINE 7252_1 | TR_LINE 7252_1
WB-Wide Bay | M002_Tarong-Kingaroy West 66 kV | Loading (A) | 358.9958 | 327.1828 | 159.5063 | 357.6093 | 324.5869 | 159.6355 | 355.4816 | 322.7567 | 158.7435 | 355.4849 | 322.7624 | 158.7441 | 358.5041 | 325.2404 | 160.0582
WB-Wide Bay | M002_Tarong-Kingaroy West 66 kV | Loading (MVA) | 40.0696 | 36.3379 | 18.4397 | 39.9327 | 36.0783 | 18.4532 | 39.7206 | 35.8942 | 18.3552 | 39.7206 | 35.8942 | 18.3552 | 40.0202 | 36.142 | 18.501
WB-Wide Bay | M002_Tarong-Kingaroy West 66 kV | Loading (MW) | 38.689 | 35.2001 | 18.1179 | 38.5654 | 34.9609 | 18.1284 | 38.369 | 34.789 | 18.0347 | 38.369 | 34.7891 | 18.0347 | 38.6449 | 35.0185 | 18.1741
WB-Wide Bay | M002_Tarong-Kingaroy West 66 kV | Power Factor | 0.96555 | 0.96869 | 0.98255 | 0.96576 | 0.96903 | 0.9824 | 0.96597 | 0.96921 | 0.98254 | 0.96597 | 0.96921 | 0.98254 | 0.96563 | 0.96891 | 0.98233
WB-Wide Bay | M002_Tarong-Kingaroy West 66 kV | Rating (A) | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521
WB-Wide Bay | M002_Tarong-Kingaroy West 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB-Wide Bay | M002_Tarong-Kingaroy West 66 kV | Min Voltage at Constrained Conductor | 64.4327 | 64.1145 | 66.7414 | 64.4615 | 64.1657 | 66.7365 | 64.5031 | 64.2003 | 66.7549 | 64.5025 | 64.1992 | 66.7547 | 64.4416 | 64.1498 | 66.7323
WB-Wide Bay | M002_Tarong-Kingaroy West 66 kV | Contingency Outage | M001_Tarong-Kingaroy East 66 kV | M001_Tarong-Kingaroy East 66 kV | M001_Tarong-Kingaroy East 66 kV | M001_Tarong-Kingaroy East 66 kV | M001_Tarong-Kingaroy East 66 kV | M001_Tarong-Kingaroy East 66 kV | M001_Tarong-Kingaroy East 66 kV | M001_Tarong-Kingaroy East 66 kV | M001_Tarong-Kingaroy East 66 kV | M001_Tarong-Kingaroy East 66 kV | M001_Tarong-Kingaroy East 66 kV | M001_Tarong-Kingaroy East 66 kV | M001_Tarong-Kingaroy East 66 kV | M001_Tarong-Kingaroy East 66 kV | M001_Tarong-Kingaroy East 66 kV
WB-Wide Bay | M003_Kingaroy- Yarraman 66 kV | % of Rated A | 70.67% | 59.19% | 21.5% | 69.98% | 58.59% | 21.31% | 69.93% | 58.55% | 21.3% | 69.93% | 58.55% | 21.3% | 70.65% | 59.15% | 21.5%
WB-Wide Bay | M003_Kingaroy- Yarraman 66 kV | Limiting Line Name | TR_LINE 7742_1 | TR_LINE 7742_1 | TR_LINE 7742_1 | TR_LINE 7742_1 | TR_LINE 7742_1 | TR_LINE 7742_1 | TR_LINE 7742_1 | TR_LINE 7742_1 | TR_LINE 7742_1 | TR_LINE 7742_1 | TR_LINE 7742_1 | TR_LINE 7742_1 | TR_LINE 7742_1 | TR_LINE 7742_1 | TR_LINE 7742_1
WB-Wide Bay | M003_Kingaroy- Yarraman 66 kV | Loading (A) | 93.2782 | 98.8461 | 34.1813 | 92.3776 | 97.8423 | 33.8788 | 92.3103 | 97.7824 | 33.8689 | 92.3112 | 97.7841 | 33.8691 | 93.2638 | 98.784 | 34.1862
WB-Wide Bay | M003_Kingaroy- Yarraman 66 kV | Loading (MVA) | 10.0772 | 10.602 | 3.91 | 9.9878 | 10.507 | 3.8755 | 9.9875 | 10.5067 | 3.8754 | 9.9875 | 10.5067 | 3.8754 | 10.0771 | 10.6017 | 3.91
WB-Wide Bay | M003_Kingaroy- Yarraman 66 kV | Loading (MW) | 9.8868 | 10.3936 | 3.884 | 9.8001 | 10.3017 | 3.85 | 9.8 | 10.3016 | 3.85 | 9.8 | 10.3016 | 3.85 | 9.8867 | 10.3935 | 3.884
WB-Wide Bay | M003_Kingaroy- Yarraman 66 kV | Power Factor | 0.98111 | 0.98034 | 0.99335 | 0.98121 | 0.98046 | 0.99343 | 0.98123 | 0.98048 | 0.99344 | 0.98123 | 0.98048 | 0.99344 | 0.98111 | 0.98036 | 0.99335
WB-Wide Bay | M003_Kingaroy- Yarraman 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
WB-Wide Bay | M003_Kingaroy- Yarraman 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB-Wide Bay | M003_Kingaroy- Yarraman 66 kV | Min Voltage at Constrained Conductor | 62.371 | 61.923 | 66.042 | 62.4207 | 61.9976 | 66.0438 | 62.4639 | 62.0337 | 66.0626 | 62.4633 | 62.0326 | 66.0623 | 62.3802 | 61.9599 | 66.0328
WB-Wide Bay | M003_Kingaroy- Yarraman 66 kV | Contingency Outage | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV
WB-Wide Bay | M004_Murgon-Kingaroy 66 kV | % of Rated A | 7.607% | 6.241% | 3.93% | 7.592% | 6.218% | 3.972% | 7.594% | 6.221% | 3.972% | 7.599% | 6.227% | 3.972% | 7.951% | 6.557% | 4.047%
WB-Wide Bay | M004_Murgon-Kingaroy 66 kV | Limiting Line Name | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1
WB-Wide Bay | M004_Murgon-Kingaroy 66 kV | Loading (A) | 12.8564 | 14.9158 | 9.1568 | 12.8313 | 14.861 | 9.2537 | 12.8342 | 14.8679 | 9.2543 | 12.8415 | 14.882 | 9.2537 | 13.4369 | 15.671 | 9.4289
WB-Wide Bay | M004_Murgon-Kingaroy 66 kV | Loading (MVA) | 1.4702 | 1.7 | 1.055 | 1.4734 | 1.7024 | 1.097 | 1.473 | 1.702 | 1.0972 | 1.472 | 1.7011 | 1.097 | 1.539 | 1.7897 | 1.1174
WB-Wide Bay | M004_Murgon-Kingaroy 66 kV | Loading (MW) | 1.3279 | 1.6081 | 0.69255 | 1.3276 | 1.6079 | 0.6923 | 1.3276 | 1.6079 | 0.6923 | 1.3276 | 1.608 | 0.6923 | 1.4121 | 1.7103 | 0.7359
WB-Wide Bay | M004_Murgon-Kingaroy 66 kV | Power Factor | 0.90322 | 0.94592 | 0.65642 | 0.90099 | 0.94449 | 0.6311 | 0.90127 | 0.94476 | 0.63097 | 0.90194 | 0.9453 | 0.6311 | 0.91751 | 0.95566 | 0.65855
WB-Wide Bay | M004_Murgon-Kingaroy 66 kV | Rating (A) | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233
WB-Wide Bay | M004_Murgon-Kingaroy 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB-Wide Bay | M004_Murgon-Kingaroy 66 kV | Min Voltage at Constrained Conductor | 66.0216 | 65.8021 | 66.5216 | 66.2981 | 66.1376 | 68.4412 | 66.2637 | 66.0901 | 68.4512 | 66.1795 | 65.9931 | 68.4412 | 66.1278 | 65.9351 | 68.4238
WB-Wide Bay | M004_Murgon-Kingaroy 66 kV | Contingency Outage | M027_ISIS - Childers 66 kV | M027_ISIS - Childers 66 kV | M027_ISIS - Childers 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | 6366_Gootchie 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | 6366_Gootchie 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | 6366_Gootchie 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | 6366_Gootchie 66 kV
WB-Wide Bay | M005 KINGAROY-BOONDOOMA | % of Rated A | 21.31% | 8.794% | 10.28% | 23.84% | 9.829% | 11.51% | 23.83% | 9.823% | 11.5% | 23.83% | 9.824% | 11.5% | 24.49% | 10.09% | 11.81%
WB-Wide Bay | M005 KINGAROY-BOONDOOMA | Limiting Line Name | TR_LINE 65620_1 | TR_LINE 65620_1 | TR_LINE 65620_1 | TR_LINE 65620_1 | TR_LINE 65620_1 | TR_LINE 65620_1 | TR_LINE 65620_1 | TR_LINE 65620_1 | TR_LINE 65620_1 | TR_LINE 65620_1 | TR_LINE 65620_1 | TR_LINE 65620_1 | TR_LINE 65620_1 | TR_LINE 65620_1 | TR_LINE 65620_1
WB-Wide Bay | M005 KINGAROY-BOONDOOMA | Loading (A) | 28.5576 | 15.9173 | 17.9955 | 31.9517 | 17.7901 | 20.1342 | 31.9303 | 17.7803 | 20.1284 | 31.9306 | 17.7806 | 20.1285 | 32.8169 | 18.2672 | 20.6705
WB-Wide Bay | M005 KINGAROY-BOONDOOMA | Loading (MVA) | 3.1648 | 1.7585 | 2.0741 | 3.5408 | 1.9665 | 2.3197 | 3.5407 | 1.9665 | 2.3197 | 3.5407 | 1.9665 | 2.3197 | 3.6349 | 2.0185 | 2.3811
WB-Wide Bay | M005 KINGAROY-BOONDOOMA | Loading (MW) | 2.9869 | 1.6638 | 1.961 | 3.3394 | 1.8599 | 2.1923 | 3.3394 | 1.8599 | 2.1923 | 3.3394 | 1.8599 | 2.1923 | 3.4276 | 1.9089 | 2.2501
WB-Wide Bay | M005 KINGAROY-BOONDOOMA | Power Factor | 0.94343 | 0.94592 | 0.94529 | 0.94275 | 0.94555 | 0.94484 | 0.94275 | 0.94556 | 0.94484 | 0.94275 | 0.94556 | 0.94484 | 0.94257 | 0.94546 | 0.94472
WB-Wide Bay | M005 KINGAROY-BOONDOOMA | Rating (A) | 134 | 181 | 175 | 134 | 181 | 175 | 134 | 181 | 175 | 134 | 181 | 175 | 134 | 181 | 175
WB-Wide Bay | M005 KINGAROY-BOONDOOMA | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB-Wide Bay | M005 KINGAROY-BOONDOOMA | Min Voltage at Constrained Conductor | 63.9827 | 63.7844 | 66.5425 | 63.9795 | 63.8193 | 66.5167 | 64.0216 | 63.8542 | 66.5353 | 64.021 | 63.8531 | 66.5351 | 63.9491 | 63.797 | 66.5072
WB-Wide Bay | M005 KINGAROY-BOONDOOMA | Contingency Outage | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV
WB-Wide Bay | M007_Proston 66 kV | % of Rated A | 11.98% | 11.37% | 5.416% | 11.93% | 11.31% | 5.362% | 11.93% | 11.32% | 5.36% | 11.95% | 11.34% | 5.36% | 12.73% | 12.08% | 5.615%
WB-Wide Bay | M007_Proston 66 kV | Limiting Line Name | TR_LINE 7270_1 | TR_LINE 7270_1 | TR_LINE 7264_1 | TR_LINE 7270_1 | TR_LINE 7270_1 | TR_LINE 7264_1 | TR_LINE 7270_1 | TR_LINE 7270_1 | TR_LINE 7264_1 | TR_LINE 7270_1 | TR_LINE 7270_1 | TR_LINE 7264_1 | TR_LINE 7270_1 | TR_LINE 7270_1 | TR_LINE 7264_1
WB-Wide Bay | M007_Proston 66 kV | Loading (A) | 11.8614 | 14.4375 | 6.5529 | 11.8081 | 14.3657 | 6.4885 | 11.8146 | 14.3767 | 6.4856 | 11.8303 | 14.3992 | 6.486 | 12.6003 | 15.3353 | 6.7937
WB-Wide Bay | M007_Proston 66 kV | Loading (MVA) | 1.3429 | 1.6251 | 0.75507 | 1.3426 | 1.6255 | 0.76183 | 1.3426 | 1.6255 | 0.76218 | 1.3427 | 1.6256 | 0.76212 | 1.4279 | 1.7282 | 0.79812
WB-Wide Bay | M007_Proston 66 kV | Loading (MW) | 1.3274 | 1.6074 | 0.69226 | 1.327 | 1.6072 | 0.6921 | 1.3271 | 1.6073 | 0.69209 | 1.3271 | 1.6074 | 0.69209 | 1.4115 | 1.7096 | 0.7357
WB-Wide Bay | M007_Proston 66 kV | Power Factor | 0.97894 | 0.97746 | 0.91681 | 0.97901 | 0.97726 | 0.90848 | 0.979 | 0.97724 | 0.90804 | 0.97898 | 0.97721 | 0.90811 | 0.97846 | 0.97687 | 0.92179
WB-Wide Bay | M007_Proston 66 kV | Rating (A) | 99 | 127 | 121 | 99 | 127 | 121 | 99 | 127 | 121 | 99 | 127 | 121 | 99 | 127 | 121
WB-Wide Bay | M007_Proston 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB-Wide Bay | M007_Proston 66 kV | Min Voltage at Constrained Conductor | 65.3656 | 64.9873 | 66.525 | 65.6457 | 65.3273 | 67.7863 | 65.6108 | 65.279 | 67.8485 | 65.5256 | 65.1805 | 67.8385 | 65.4264 | 65.0649 | 67.8249
WB-Wide Bay | M007_Proston 66 kV | Contingency Outage | M027_ISIS - Childers 66 kV | M027_ISIS - Childers 66 kV | M027_ISIS - Childers 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M020_Maryborough-Torquay 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M020_Maryborough-Torquay 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV
WB-Wide Bay | M008_Kilkivan-Murgon No 1 66 kV | % of Rated A | 38.41% | 28.84% | 14.55% | 39.15% | 29.36% | 14.61% | 38.95% | 29.21% | 14.51% | 39.23% | 29.43% | 14.6% | 39.7% | 29.81% | 14.76%
WB-Wide Bay | M008_Kilkivan-Murgon No 1 66 kV | Limiting Line Name | TR_LINE 7214_1 | TR_LINE 7214_1 | TR_LINE 7214_1 | TR_LINE 7214_1 | TR_LINE 7214_1 | TR_LINE 7214_1 | TR_LINE 7214_1 | TR_LINE 7214_1 | TR_LINE 7214_1 | TR_LINE 7214_1 | TR_LINE 7214_1 | TR_LINE 7214_1 | TR_LINE 7214_1 | TR_LINE 7214_1 | TR_LINE 7214_1
WB-Wide Bay | M008_Kilkivan-Murgon No 1 66 kV | Loading (A) | 69.5269 | 72.679 | 35.6359 | 70.8688 | 73.9875 | 35.7941 | 70.4928 | 73.6168 | 35.5495 | 71.0046 | 74.1612 | 35.7656 | 71.8562 | 75.116 | 36.1696
WB-Wide Bay | M008_Kilkivan-Murgon No 1 66 kV | Loading (MVA) | 8.1428 | 8.4956 | 4.1505 | 8.3391 | 8.6969 | 4.2473 | 8.2892 | 8.6458 | 4.2217 | 8.341 | 8.6995 | 4.2471 | 8.4379 | 8.8077 | 4.295
WB-Wide Bay | M008_Kilkivan-Murgon No 1 66 kV | Loading (MW) | 7.941 | 8.2717 | 4.1369 | 8.1266 | 8.4621 | 4.2345 | 8.0798 | 8.4141 | 4.2097 | 8.1273 | 8.463 | 4.2344 | 8.2181 | 8.5645 | 4.2813
WB-Wide Bay | M008_Kilkivan-Murgon No 1 66 kV | Power Factor | 0.97489 | 0.97335 | 0.99639 | 0.97421 | 0.97271 | 0.99665 | 0.97442 | 0.97291 | 0.99682 | 0.97406 | 0.97253 | 0.99669 | 0.97365 | 0.97211 | 0.99647
WB-Wide Bay | M008_Kilkivan-Murgon No 1 66 kV | Rating (A) | 181 | 252 | 245 | 181 | 252 | 245 | 181 | 252 | 245 | 181 | 252 | 245 | 181 | 252 | 245
WB-Wide Bay | M008_Kilkivan-Murgon No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB-Wide Bay | M008_Kilkivan-Murgon No 1 66 kV | Min Voltage at Constrained Conductor | 67.5904 | 67.4564 | 67.2413 | 67.9079 | 67.8324 | 68.5061 | 67.862 | 67.7735 | 68.561 | 67.7933 | 67.693 | 68.5574 | 67.7664 | 67.6627 | 68.5558
WB-Wide Bay | M008_Kilkivan-Murgon No 1 66 kV | Contingency Outage | M027_ISIS - Childers 66 kV | M027_ISIS - Childers 66 kV | M027_ISIS - Childers 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M020_Maryborough-Torquay 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M020_Maryborough-Torquay 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV
WB-Wide Bay | M009_Kilkivan-Murgon No 2 66 kV | % of Rated A | 36.93% | 27.36% | 14.02% | 37.77% | 27.95% | 14.12% | 37.54% | 27.79% | 14.01% | 37.84% | 28.01% | 14.11% | 38.36% | 28.42% | 14.29%
WB-Wide Bay | M009_Kilkivan-Murgon No 2 66 kV | Limiting Line Name | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1
WB-Wide Bay | M009_Kilkivan-Murgon No 2 66 kV | Loading (A) | 62.4122 | 65.3975 | 32.6586 | 63.8329 | 66.7944 | 32.8984 | 63.4414 | 66.4063 | 32.6476 | 63.955 | 66.951 | 32.8717 | 64.8202 | 67.9203 | 33.2886
WB-Wide Bay | M009_Kilkivan-Murgon No 2 66 kV | Loading (MVA) | 7.1935 | 7.5257 | 3.7629 | 7.3923 | 7.7297 | 3.8624 | 7.3418 | 7.6779 | 3.8364 | 7.3941 | 7.7321 | 3.8622 | 7.492 | 7.8416 | 3.9104
WB-Wide Bay | M009_Kilkivan-Murgon No 2 66 kV | Loading (MW) | 7.0647 | 7.3785 | 3.752 | 7.2541 | 7.5727 | 3.8512 | 7.2064 | 7.5238 | 3.8259 | 7.2548 | 7.5737 | 3.8511 | 7.3474 | 7.6771 | 3.8988
WB-Wide Bay | M009_Kilkivan-Murgon No 2 66 kV | Power Factor | 0.97094 | 0.97003 | 0.9873 | 0.97037 | 0.96947 | 0.98741 | 0.97054 | 0.96963 | 0.98762 | 0.97027 | 0.96934 | 0.98745 | 0.97001 | 0.9691 | 0.98722
WB-Wide Bay | M009_Kilkivan-Murgon No 2 66 kV | Rating (A) | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233 | 169 | 239 | 233
WB-Wide Bay | M009_Kilkivan-Murgon No 2 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB-Wide Bay | M009_Kilkivan-Murgon No 2 66 kV | Min Voltage at Constrained Conductor | 66.0219 | 65.8028 | 66.5216 | 66.2984 | 66.1383 | 67.7825 | 66.264 | 66.0907 | 67.8446 | 66.1799 | 65.9937 | 67.8347 | 66.1282 | 65.9358 | 67.8217
WB-Wide Bay | M009_Kilkivan-Murgon No 2 66 kV | Contingency Outage | M027_ISIS - Childers 66 kV | M027_ISIS - Childers 66 kV | M027_ISIS - Childers 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M020_Maryborough-Torquay 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M020_Maryborough-Torquay 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV
WB-Wide Bay | M010_Maryborough - Owanyilla 66 kV | % of Rated A | 44.06% | 28.84% | 11.32% | 27.65% | 18.36% | 15.8% | 29.31% | 18.74% | 16.37% | 30.66% | 20% | 16.69% | 30.71% | 20.05% | 16.68%
WB-Wide Bay | M010_Maryborough - Owanyilla 66 kV | Limiting Line Name | TR_LINE 199621_1 | TR_LINE 199621_1 | TR_LINE 7259_1 | TR_LINE 199623_1 | TR_LINE 199621_1 | TR_LINE 7259_1 | TR_LINE 199623_1 | TR_LINE 199621_1 | TR_LINE 7259_1 | TR_LINE 199621_1 | TR_LINE 199621_1 | TR_LINE 7259_1 | TR_LINE 199621_1 | TR_LINE 199621_1 | TR_LINE 7259_1
WB-Wide Bay | M010_Maryborough - Owanyilla 66 kV | Loading (A) | 109.7169 | 110.1873 | 41.8806 | 68.8602 | 70.1441 | 58.4566 | 72.9813 | 71.5905 | 60.5827 | 76.3406 | 76.3963 | 61.7539 | 76.4586 | 76.5831 | 61.7344
WB-Wide Bay | M010_Maryborough - Owanyilla 66 kV | Loading (MVA) | 12.7167 | 12.7605 | 4.9102 | 8.0738 | 8.2847 | 6.8449 | 8.5929 | 8.393 | 7.1378 | 8.9812 | 8.9643 | 7.274 | 8.9884 | 8.9786 | 7.2693
WB-Wide Bay | M010_Maryborough - Owanyilla 66 kV | Loading (MW) | 12.386 | 12.4286 | 4.9074 | 8.0435 | 8.2828 | 5.7226 | 8.5908 | 8.3927 | 6.2924 | 8.9812 | 8.9569 | 6.4943 | 8.9883 | 8.9694 | 6.4981
WB-Wide Bay | M010_Maryborough - Owanyilla 66 kV | Power Factor | 0.97399 | 0.97399 | 0.99941 | 0.99624 | 0.99976 | 0.83604 | 0.99976 | 0.99996 | 0.88157 | 1 | 0.99916 | 0.89281 | 0.99999 | 0.99897 | 0.89391
WB-Wide Bay | M010_Maryborough - Owanyilla 66 kV | Rating (A) | 249 | 382 | 370 | 249 | 382 | 370 | 249 | 382 | 370 | 249 | 382 | 370 | 249 | 382 | 370
WB-Wide Bay | M010_Maryborough - Owanyilla 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB-Wide Bay | M010_Maryborough - Owanyilla 66 kV | Min Voltage at Constrained Conductor | 66.9119 | 66.8556 | 67.6873 | 67.689 | 68.1872 | 67.6038 | 67.9715 | 67.6828 | 68.0222 | 67.9194 | 67.7429 | 68.0048 | 67.8687 | 67.6854 | 67.9826
WB-Wide Bay | M010_Maryborough - Owanyilla 66 kV | Contingency Outage | 7187_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | M018_Maryborough-Maryborough City 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV
WB-Wide Bay | M011_Kilkivan-Maryborough 66 kV | % of Rated A | 29.82% | 22.15% | 6.152% | 82.75% | 66.14% | 26.01% | 86.88% | 70.03% | 27.59% | 91.19% | 73.97% | 29.17% | 91.95% | 74.66% | 29.43%
WB-Wide Bay | M011_Kilkivan-Maryborough 66 kV | Limiting Line Name | TR_LINE 33838_1 | TR_LINE 33838_1 | TR_LINE 33838_1 | TR_LINE 42252_1 | TR_LINE 42252_1 | TR_LINE 42252_1 | TR_LINE 42252_1 | TR_LINE 42252_1 | TR_LINE 42252_1 | TR_LINE 42252_1 | TR_LINE 42252_1 | TR_LINE 42252_1 | TR_LINE 42252_1 | TR_LINE 42252_1 | TR_LINE 42252_1
WB-Wide Bay | M011_Kilkivan-Maryborough 66 kV | Loading (A) | 39.3632 | 36.9918 | 9.7823 | 109.2241 | 110.4571 | 41.361 | 114.6823 | 116.9563 | 43.875 | 120.3749 | 123.5324 | 46.3746 | 121.3733 | 124.6761 | 46.793
WB-Wide Bay | M011_Kilkivan-Maryborough 66 kV | Loading (MVA) | 4.2929 | 4.0446 | 1.1293 | 12.5447 | 12.6681 | 4.9083 | 13.1443 | 13.3793 | 5.2022 | 13.7627 | 14.0907 | 5.4933 | 13.8678 | 14.2107 | 5.5416
WB-Wide Bay | M011_Kilkivan-Maryborough 66 kV | Loading (MW) | 4.1285 | 3.8931 | 1.0965 | 12.1874 | 12.2946 | 4.8756 | 12.7464 | 12.953 | 5.159 | 13.3196 | 13.6087 | 5.439 | 13.4162 | 13.7191 | 5.4856
WB-Wide Bay | M011_Kilkivan-Maryborough 66 kV | Power Factor | 0.9617 | 0.96254 | 0.97094 | 0.97152 | 0.97052 | 0.99331 | 0.96973 | 0.96814 | 0.99167 | 0.96781 | 0.96579 | 0.99009 | 0.96744 | 0.96541 | 0.98988
WB-Wide Bay | M011_Kilkivan-Maryborough 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
WB-Wide Bay | M011_Kilkivan-Maryborough 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB-Wide Bay | M011_Kilkivan-Maryborough 66 kV | Min Voltage at Constrained Conductor | 62.965 | 63.1262 | 66.6515 | 66.3039 | 66.2087 | 68.5134 | 66.1663 | 66.0396 | 68.4545 | 66.0023 | 65.8482 | 68.3891 | 65.9593 | 65.7996 | 68.3733
WB-Wide Bay | M011_Kilkivan-Maryborough 66 kV | Contingency Outage | 7187_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | M018_Maryborough-Maryborough City 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV
WB-Wide Bay | M012_Maryborough-Rocky St 66 kV | % of Rated A | 46.15% | 43.73% | 29.06% | 47.2% | 44.5% | 29.84% | 48.78% | 45.91% | 30.49% | 48.8% | 45.87% | 30.49% | 49.36% | 46.38% | 30.74%
WB-Wide Bay | M012_Maryborough-Rocky St 66 kV | Limiting Line Name | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1
WB-Wide Bay | M012_Maryborough-Rocky St 66 kV | Loading (A) | 252.8942 | 253.1781 | 151.4075 | 258.6311 | 257.6535 | 155.4833 | 267.2922 | 265.8392 | 158.8494 | 267.4212 | 265.5693 | 158.8638 | 270.4703 | 268.5388 | 160.1744
WB-Wide Bay | M012_Maryborough-Rocky St 66 kV | Loading (MVA) | 29.6958 | 29.7673 | 17.7519 | 30.488 | 30.4197 | 18.2955 | 31.2811 | 31.1654 | 18.8056 | 31.2782 | 31.1715 | 18.8035 | 31.5985 | 31.4871 | 18.962
WB-Wide Bay | M012_Maryborough-Rocky St 66 kV | Loading (MW) | 28.9542 | 29.039 | 15.5088 | 29.654 | 29.6372 | 15.9535 | 30.5323 | 30.4221 | 16.4876 | 30.5326 | 30.4217 | 16.4876 | 30.8803 | 30.7642 | 16.6768
WB-Wide Bay | M012_Maryborough-Rocky St 66 kV | Power Factor | 0.97255 | 0.97309 | 0.87148 | 0.96999 | 0.97172 | 0.86969 | 0.97343 | 0.97355 | 0.8744 | 0.97353 | 0.97334 | 0.87449 | 0.97466 | 0.97445 | 0.87712
WB-Wide Bay | M012_Maryborough-Rocky St 66 kV | Rating (A) | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521
WB-Wide Bay | M012_Maryborough-Rocky St 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB-Wide Bay | M012_Maryborough-Rocky St 66 kV | Min Voltage at Constrained Conductor | 67.6815 | 67.7662 | 67.6918 | 67.9533 | 68.0522 | 67.9358 | 67.4434 | 67.5616 | 68.3503 | 67.4041 | 67.6448 | 68.3365 | 67.3203 | 67.5677 | 68.3488
WB-Wide Bay | M012_Maryborough-Rocky St 66 kV | Contingency Outage | M018_Maryborough-Maryborough City 66 kV | M018_Maryborough-Maryborough City 66 kV | M018_Maryborough-Maryborough City 66 kV | M018_Maryborough-Maryborough City 66 kV | M018_Maryborough-Maryborough City 66 kV | M018_Maryborough-Maryborough City 66 kV | M018_Maryborough-Maryborough City 66 kV | M018_Maryborough-Maryborough City 66 kV | M018_Maryborough-Maryborough City 66 kV | M018_Maryborough-Maryborough City 66 kV | M018_Maryborough-Maryborough City 66 kV | M018_Maryborough-Maryborough City 66 kV | M018_Maryborough-Maryborough City 66 kV | M018_Maryborough-Maryborough City 66 kV | M018_Maryborough-Maryborough City 66 kV
WB-Wide Bay | M014_Torquay-Pialba 66 kV | % of Rated A | 16.22% | 9.108% | 9.758% | 15.79% | 8.894% | 9.587% | 15.49% | 8.797% | 9.45% | 15.39% | 8.761% | 9.423% | 15.3% | 8.645% | 9.667%
WB-Wide Bay | M014_Torquay-Pialba 66 kV | Limiting Line Name | TR_LINE 7168_1 | TR_LINE 7168_1 | TR_LINE 7168_1 | TR_LINE 7168_1 | TR_LINE 7168_1 | TR_LINE 7168_1 | TR_LINE 7168_1 | TR_LINE 7168_1 | TR_LINE 7168_1 | TR_LINE 7168_1 | TR_LINE 7168_1 | TR_LINE 7168_1 | TR_LINE 7168_1 | TR_LINE 7168_1 | TR_LINE 7168_1
WB-Wide Bay | M014_Torquay-Pialba 66 kV | Loading (A) | 98.5949 | 61.2045 | 53.7665 | 95.9834 | 59.7668 | 52.8261 | 94.1721 | 59.1165 | 52.0717 | 93.5962 | 58.8758 | 51.9229 | 93.0415 | 58.0949 | 53.2638
WB-Wide Bay | M014_Torquay-Pialba 66 kV | Loading (MVA) | 11.1955 | 6.9717 | 6.2584 | 10.8794 | 6.7795 | 6.1102 | 10.6714 | 6.6915 | 6.0615 | 10.6337 | 6.6646 | 6.0417 | 10.5542 | 6.5923 | 6.2032
WB-Wide Bay | M014_Torquay-Pialba 66 kV | Loading (MW) | 10.3899 | 4.5843 | 4.4903 | 10.0561 | 4.3553 | 4.3256 | 9.7994 | 4.1415 | 4.1938 | 9.7412 | 4.0693 | 4.1597 | 9.6796 | 3.9629 | 4.1122
WB-Wide Bay | M014_Torquay-Pialba 66 kV | Power Factor | 0.92804 | 0.65757 | 0.71749 | 0.92432 | 0.64242 | 0.70793 | 0.91829 | 0.61892 | 0.69187 | 0.91607 | 0.61058 | 0.68849 | 0.91713 | 0.60114 | 0.66292
WB-Wide Bay | M014_Torquay-Pialba 66 kV | Rating (A) | 608 | 672 | 551 | 608 | 672 | 551 | 608 | 672 | 551 | 608 | 672 | 551 | 608 | 672 | 551
WB-Wide Bay | M014_Torquay-Pialba 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB-Wide Bay | M014_Torquay-Pialba 66 kV | Min Voltage at Constrained Conductor | 65.5587 | 65.7647 | 67.2032 | 65.441 | 65.4902 | 66.7796 | 65.424 | 65.3509 | 67.2075 | 65.5942 | 65.3547 | 67.1798 | 65.4922 | 65.5147 | 67.2389
WB-Wide Bay | M014_Torquay-Pialba 66 kV | Contingency Outage | 7187_Gin Gin - Bundaberg 132 kV | 7315_Aramara 132 kV | M018_Maryborough-Maryborough City 66 kV | 7329_Maryborough 132 kV | 7329_Maryborough 132 kV | 7329_Maryborough 132 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 7187_Gin Gin - Bundaberg 132 kV | M012_Maryborough-Rocky St 66 kV | 786_Gin Gin - Bundaberg 132 kV | 7187_Gin Gin - Bundaberg 132 kV | M012_Maryborough-Rocky St 66 kV | 7187_Gin Gin - Bundaberg 132 kV | 7329_Maryborough 132 kV
WB-Wide Bay | M015_Maryborough-Howard No 1 66 kV | % of Rated A | 1.887% | 1.483% | 1.567% | 1.879% | 1.489% | 1.561% | 1.88% | 1.478% | 1.566% | 1.879% | 1.48% | 1.566% | 1.878% | 1.479% | 1.566%
WB-Wide Bay | M015_Maryborough-Howard No 1 66 kV | Limiting Line Name | TR_LINE 112139_1 | TR_LINE 112139_1 | TR_LINE 112139_1 | TR_LINE 112139_1 | TR_LINE 112139_1 | TR_LINE 112139_1 | TR_LINE 112139_1 | TR_LINE 112139_1 | TR_LINE 112139_1 | TR_LINE 112139_1 | TR_LINE 112139_1 | TR_LINE 112139_1 | TR_LINE 112139_1 | TR_LINE 112139_1 | TR_LINE 112139_1
WB-Wide Bay | M015_Maryborough-Howard No 1 66 kV | Loading (A) | 2.491 | 2.4769 | 2.4921 | 2.48 | 2.4872 | 2.4816 | 2.4816 | 2.4688 | 2.4906 | 2.4809 | 2.4714 | 2.4901 | 2.4791 | 2.4693 | 2.4906
WB-Wide Bay | M015_Maryborough-Howard No 1 66 kV | Loading (MVA) | 0.29493 | 0.29161 | 0.2952 | 0.29235 | 0.29405 | 0.29272 | 0.29273 | 0.28971 | 0.29486 | 0.29256 | 0.29032 | 0.29474 | 0.29214 | 0.28983 | 0.29485
WB-Wide Bay | M015_Maryborough-Howard No 1 66 kV | Loading (MW) | 5.3351e-05 | 5.275e-05 | 5.34e-05 | 5.2884e-05 | 5.3191e-05 | 5.2951e-05 | 5.2952e-05 | 5.2406e-05 | 5.3337e-05 | 5.2921e-05 | 5.2515e-05 | 5.3316e-05 | 5.2845e-05 | 5.2428e-05 | 5.3335e-05
WB-Wide Bay | M015_Maryborough-Howard No 1 66 kV | Power Factor | 0.00017813 | 0.00017813 | 0.00017813 | 0.00017813 | 0.00017813 | 0.00017813 | 0.00017813 | 0.00017813 | 0.00017813 | 0.00017813 | 0.00017813 | 0.00017813 | 0.00017813 | 0.00017813 | 0.00017813
WB-Wide Bay | M015_Maryborough-Howard No 1 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
WB-Wide Bay | M015_Maryborough-Howard No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB-Wide Bay | M015_Maryborough-Howard No 1 66 kV | Min Voltage at Constrained Conductor | 68.3592 | 67.9735 | 68.3907 | 68.0596 | 68.2567 | 68.1026 | 68.1032 | 67.7515 | 68.3506 | 68.0832 | 67.822 | 68.3367 | 68.0347 | 67.7655 | 68.3491
WB-Wide Bay | M015_Maryborough-Howard No 1 66 kV | Contingency Outage | M020_Maryborough-Torquay 66 kV | M010_Maryborough - Owanyilla 66 kV | M010_Maryborough - Owanyilla 66 kV | M018_Maryborough-Maryborough City 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV | M020_Maryborough-Torquay 66 kV | M020_Maryborough-Torquay 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV | M018_Maryborough-Maryborough City 66 kV | M020_Maryborough-Torquay 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV | M018_Maryborough-Maryborough City 66 kV | M020_Maryborough-Torquay 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV | M018_Maryborough-Maryborough City 66 kV
WB-Wide Bay | M017_Rocky St - Maryborough City 66 kV | % of Rated A | 30.38% | 30.19% | 17.24% | 29.81% | 29.59% | 17.13% | 29.91% | 29.68% | 17.01% | 29.93% | 29.65% | 17.01% | 30.23% | 29.96% | 17.14%
WB-Wide Bay | M017_Rocky St - Maryborough City 66 kV | Limiting Line Name | TR_LINE 39141_1 | TR_LINE 39141_1 | TR_LINE 39141_1 | TR_LINE 39141_1 | TR_LINE 39141_1 | TR_LINE 39141_1 | TR_LINE 39141_1 | TR_LINE 39141_1 | TR_LINE 39141_1 | TR_LINE 39141_1 | TR_LINE 39141_1 | TR_LINE 39141_1 | TR_LINE 39141_1 | TR_LINE 39141_1 | TR_LINE 39141_1
WB-Wide Bay | M017_Rocky St - Maryborough City 66 kV | Loading (A) | 166.4817 | 174.7883 | 89.8057 | 163.3685 | 171.3023 | 89.2422 | 163.8811 | 171.8339 | 88.6089 | 163.993 | 171.661 | 88.6235 | 165.6873 | 173.492 | 89.2849
WB-Wide Bay | M017_Rocky St - Maryborough City 66 kV | Loading (MVA) | 19.2786 | 20.2034 | 10.6067 | 18.9976 | 19.9115 | 10.4439 | 18.9197 | 19.8275 | 10.4356 | 18.9181 | 19.8295 | 10.4341 | 19.0921 | 20.0133 | 10.5131
WB-Wide Bay | M017_Rocky St - Maryborough City 66 kV | Loading (MW) | 19.0347 | 20.0044 | 9.5751 | 18.758 | 19.7133 | 9.4364 | 18.6658 | 19.6163 | 9.3898 | 18.6659 | 19.6161 | 9.3898 | 18.8509 | 19.8105 | 9.4825
WB-Wide Bay | M017_Rocky St - Maryborough City 66 kV | Power Factor | 0.98735 | 0.99015 | 0.90274 | 0.98738 | 0.99004 | 0.90353 | 0.98658 | 0.98934 | 0.89979 | 0.98667 | 0.98923 | 0.89992 | 0.98736 | 0.98986 | 0.90197
WB-Wide Bay | M017_Rocky St - Maryborough City 66 kV | Rating (A) | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521
WB-Wide Bay | M017_Rocky St - Maryborough City 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB-Wide Bay | M017_Rocky St - Maryborough City 66 kV | Min Voltage at Constrained Conductor | 66.8565 | 66.7338 | 68.1894 | 67.1377 | 67.1082 | 67.5665 | 66.653 | 66.6182 | 67.9954 | 66.6019 | 66.6922 | 67.9742 | 66.5273 | 66.5998 | 67.9817
WB-Wide Bay | M017_Rocky St - Maryborough City 66 kV | Contingency Outage | M012_Maryborough-Rocky St 66 kV | M012_Maryborough-Rocky St 66 kV | M012_Maryborough-Rocky St 66 kV | M012_Maryborough-Rocky St 66 kV | M012_Maryborough-Rocky St 66 kV | M012_Maryborough-Rocky St 66 kV | M012_Maryborough-Rocky St 66 kV | M012_Maryborough-Rocky St 66 kV | M012_Maryborough-Rocky St 66 kV | M012_Maryborough-Rocky St 66 kV | M012_Maryborough-Rocky St 66 kV | M012_Maryborough-Rocky St 66 kV | M012_Maryborough-Rocky St 66 kV | M012_Maryborough-Rocky St 66 kV | M012_Maryborough-Rocky St 66 kV
WB-Wide Bay | M018_Maryborough-Maryborough City 66 kV | % of Rated A | 54.02% | 52.8% | 33.71% | 54.84% | 53.32% | 34.66% | 56.59% | 54.86% | 35.33% | 56.72% | 54.91% | 35.4% | 57.33% | 55.48% | 35.68%
WB-Wide Bay | M018_Maryborough-Maryborough City 66 kV | Limiting Line Name | TR_LINE 122162_1 | TR_LINE 122162_1 | TR_LINE 122162_1 | TR_LINE 122162_1 | TR_LINE 122162_1 | TR_LINE 122162_1 | TR_LINE 122162_1 | TR_LINE 122162_1 | TR_LINE 122162_1 | TR_LINE 122162_1 | TR_LINE 122162_1 | TR_LINE 122162_1 | TR_LINE 122162_1 | TR_LINE 122162_1 | TR_LINE 122162_1
WB-Wide Bay | M018_Maryborough-Maryborough City 66 kV | Loading (A) | 296.0417 | 305.7248 | 175.6126 | 300.5343 | 308.7041 | 180.602 | 310.0918 | 317.616 | 184.0522 | 310.8252 | 317.9086 | 184.4178 | 314.1859 | 321.2249 | 185.8844
WB-Wide Bay | M018_Maryborough-Maryborough City 66 kV | Loading (MVA) | 34.5062 | 35.6034 | 20.7565 | 35.1719 | 36.1434 | 21.1524 | 36.0425 | 36.9291 | 21.6944 | 36.1027 | 37.0051 | 21.7316 | 36.4552 | 37.3459 | 21.9081
WB-Wide Bay | M018_Maryborough-Maryborough City 66 kV | Loading (MW) | 34.3918 | 35.557 | 19.8179 | 35.0277 | 36.0739 | 20.21 | 35.9139 | 36.8689 | 20.7442 | 35.9802 | 36.9469 | 20.7968 | 36.3319 | 37.294 | 20.9869
WB-Wide Bay | M018_Maryborough-Maryborough City 66 kV | Power Factor | 0.99565 | 0.998 | 0.95321 | 0.99473 | 0.99723 | 0.95376 | 0.99528 | 0.99755 | 0.95449 | 0.99548 | 0.99762 | 0.95527 | 0.99547 | 0.99783 | 0.95624
WB-Wide Bay | M018_Maryborough-Maryborough City 66 kV | Rating (A) | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521
WB-Wide Bay | M018_Maryborough-Maryborough City 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB-Wide Bay | M018_Maryborough-Maryborough City 66 kV | Min Voltage at Constrained Conductor | 67.0316 | 66.9347 | 68.2056 | 67.3091 | 67.3034 | 67.5839 | 66.8337 | 66.822 | 68.0142 | 66.7845 | 66.897 | 67.9942 | 66.7118 | 66.8091 | 68.0033
WB-Wide Bay | M018_Maryborough-Maryborough City 66 kV | Contingency Outage | M012_Maryborough-Rocky St 66 kV | M012_Maryborough-Rocky St 66 kV | M012_Maryborough-Rocky St 66 kV | M012_Maryborough-Rocky St 66 kV | M012_Maryborough-Rocky St 66 kV | M012_Maryborough-Rocky St 66 kV | M012_Maryborough-Rocky St 66 kV | M012_Maryborough-Rocky St 66 kV | M012_Maryborough-Rocky St 66 kV | M012_Maryborough-Rocky St 66 kV | M012_Maryborough-Rocky St 66 kV | M012_Maryborough-Rocky St 66 kV | M012_Maryborough-Rocky St 66 kV | M012_Maryborough-Rocky St 66 kV | M012_Maryborough-Rocky St 66 kV
WB-Wide Bay | M020_Maryborough-Torquay 66 kV | % of Rated A | 47.03% | 42.88% | 27.98% | 46.42% | 42.28% | 27.76% | 46.06% | 42.09% | 27.39% | 46.07% | 42.25% | 27.49% | 46.48% | 42.5% | 27.71%
WB-Wide Bay | M020_Maryborough-Torquay 66 kV | Limiting Line Name | TR_LINE 7933_2 | TR_LINE 7933_2 | TR_LINE 112154_1 | TR_LINE 7933_2 | TR_LINE 7933_2 | TR_LINE 112154_1 | TR_LINE 7933_2 | TR_LINE 7933_2 | TR_LINE 112154_1 | TR_LINE 7933_2 | TR_LINE 7933_2 | TR_LINE 112154_1 | TR_LINE 7933_2 | TR_LINE 7933_2 | TR_LINE 112154_1
WB-Wide Bay | M020_Maryborough-Torquay 66 kV | Loading (A) | 285.9595 | 288.1828 | 154.1969 | 282.2102 | 284.1298 | 152.96 | 280.0163 | 282.8642 | 150.9235 | 280.0912 | 283.8935 | 151.4505 | 282.6267 | 285.6276 | 152.7087
WB-Wide Bay | M020_Maryborough-Torquay 66 kV | Loading (MVA) | 32.472 | 32.6582 | 18.0141 | 31.9888 | 32.2306 | 17.7567 | 31.7318 | 32.0188 | 17.6302 | 31.8229 | 32.1372 | 17.685 | 32.061 | 32.4126 | 17.8216
WB-Wide Bay | M020_Maryborough-Torquay 66 kV | Loading (MW) | 32.4716 | 32.6514 | 17.9224 | 31.9884 | 32.2259 | 17.6657 | 31.7317 | 32.0144 | 17.5317 | 31.8228 | 32.1323 | 17.5884 | 32.0604 | 32.4059 | 17.7295
WB-Wide Bay | M020_Maryborough-Torquay 66 kV | Power Factor | 0.99999 | 0.99979 | 0.99491 | 0.99999 | 0.99986 | 0.99487 | 1 | 0.99986 | 0.99441 | 1 | 0.99985 | 0.99454 | 0.99998 | 0.99979 | 0.99483
WB-Wide Bay | M020_Maryborough-Torquay 66 kV | Rating (A) | 608 | 672 | 551 | 608 | 672 | 551 | 608 | 672 | 551 | 608 | 672 | 551 | 608 | 672 | 551
WB-Wide Bay | M020_Maryborough-Torquay 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB-Wide Bay | M020_Maryborough-Torquay 66 kV | Min Voltage at Constrained Conductor | 65.5587 | 65.4258 | 67.4486 | 65.441 | 65.4902 | 67.0227 | 65.424 | 65.3509 | 67.4431 | 65.5942 | 65.3547 | 67.4174 | 65.4922 | 65.5147 | 67.3782
WB-Wide Bay | M020_Maryborough-Torquay 66 kV | Contingency Outage | 7187_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | M018_Maryborough-Maryborough City 66 kV | 7329_Maryborough 132 kV | 7329_Maryborough 132 kV | 7329_Maryborough 132 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 7187_Gin Gin - Bundaberg 132 kV | M012_Maryborough-Rocky St 66 kV | 786_Gin Gin - Bundaberg 132 kV | 7187_Gin Gin - Bundaberg 132 kV | M012_Maryborough-Rocky St 66 kV | 7187_Gin Gin - Bundaberg 132 kV | 7187_Gin Gin - Bundaberg 132 kV
WB-Wide Bay | M022_Howard - ISIS 66 kV | % of Rated A | 10.43% | 12.82% | 6.354% | 13.95% | 17.22% | 8.431% | 17.7% | 21.84% | 10.6% | 17.7% | 21.89% | 10.6% | 17.84% | 22% | 10.68%
WB-Wide Bay | M022_Howard - ISIS 66 kV | Limiting Line Name | TR_LINE 118970_1 | TR_LINE 118970_1 | TR_LINE 118970_1 | TR_LINE 118970_1 | TR_LINE 118970_1 | TR_LINE 118970_1 | TR_LINE 118970_1 | TR_LINE 118970_1 | TR_LINE 118970_1 | TR_LINE 118970_1 | TR_LINE 118970_1 | TR_LINE 118970_1 | TR_LINE 118970_1 | TR_LINE 118970_1 | TR_LINE 118970_1
WB-Wide Bay | M022_Howard - ISIS 66 kV | Loading (A) | 57.1784 | 74.199 | 33.1065 | 76.4571 | 99.6886 | 43.9265 | 97.0045 | 126.4691 | 55.2469 | 97.0148 | 126.7662 | 55.2438 | 97.7573 | 127.399 | 55.6449
WB-Wide Bay | M022_Howard - ISIS 66 kV | Loading (MVA) | 6.5951 | 8.5488 | 3.8193 | 8.822 | 11.4665 | 5.087 | 11.1619 | 14.5452 | 6.4038 | 11.162 | 14.5485 | 6.4038 | 11.2413 | 14.6497 | 6.4478
WB-Wide Bay | M022_Howard - ISIS 66 kV | Loading (MW) | 6.512 | 8.4092 | 3.7791 | 8.673 | 11.2083 | 5.0282 | 10.9187 | 14.1207 | 6.3225 | 10.9187 | 14.1216 | 6.3225 | 10.9939 | 14.2182 | 6.3657
WB-Wide Bay | M022_Howard - ISIS 66 kV | Power Factor | 0.9841 | 0.98113 | 0.98757 | 0.98073 | 0.97668 | 0.98592 | 0.97723 | 0.97082 | 0.98414 | 0.97722 | 0.97066 | 0.98414 | 0.97706 | 0.97055 | 0.98407
WB-Wide Bay | M022_Howard - ISIS 66 kV | Rating (A) | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521
WB-Wide Bay | M022_Howard - ISIS 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB-Wide Bay | M022_Howard - ISIS 66 kV | Min Voltage at Constrained Conductor | 66.5932 | 66.4002 | 66.606 | 66.4792 | 66.0698 | 66.8606 | 66.1174 | 65.8403 | 66.9217 | 66.1107 | 65.6962 | 66.9254 | 66.068 | 65.8216 | 66.9004
WB-Wide Bay | M022_Howard - ISIS 66 kV | Contingency Outage | 7315_Aramara 132 kV | 785_ISIS 132 kV | M027_ISIS - Childers 66 kV | 7315_Aramara 132 kV | 786_Gin Gin - Bundaberg 132 kV | 785_ISIS 132 kV | 6302_Bundaberg Central - WEBU 66 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 6302_Bundaberg Central - WEBU 66 kV | M039_Bundaberg-West Bundaberg No 1 66 kV | 786_Gin Gin - Bundaberg 132 kV | M039_Bundaberg-West Bundaberg No 1 66 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV
WB-Wide Bay | M023_6242 (Pialba-Point Vernon) 66 kV | % of Rated A | 27.14% | 18.38% | 16.25% | 26.42% | 17.92% | 15.93% | 26.17% | 17.79% | 15.74% | 26.1% | 17.78% | 15.74% | 26.27% | 17.83% | 15.81%
WB-Wide Bay | M023_6242 (Pialba-Point Vernon) 66 kV | Limiting Line Name | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1
WB-Wide Bay | M023_6242 (Pialba-Point Vernon) 66 kV | Loading (A) | 164.1878 | 122.7895 | 88.9029 | 159.8208 | 119.7023 | 87.1217 | 158.3066 | 118.8073 | 86.0932 | 157.9349 | 118.7997 | 86.1133 | 158.926 | 119.114 | 86.4949
WB-Wide Bay | M023_6242 (Pialba-Point Vernon) 66 kV | Loading (MVA) | 18.6478 | 13.9388 | 10.3615 | 18.1202 | 13.6025 | 10.0902 | 17.9453 | 13.4731 | 10.0353 | 17.9502 | 13.4733 | 10.0336 | 18.0345 | 13.5421 | 10.0716
WB-Wide Bay | M023_6242 (Pialba-Point Vernon) 66 kV | Loading (MW) | 18.3652 | 13.4451 | 9.4678 | 17.8203 | 13.0464 | 9.1877 | 17.6386 | 12.9137 | 9.094 | 17.6382 | 12.9137 | 9.094 | 17.7293 | 12.9799 | 9.1408
WB-Wide Bay | M023_6242 (Pialba-Point Vernon) 66 kV | Power Factor | 0.98484 | 0.96457 | 0.91374 | 0.98344 | 0.95911 | 0.91055 | 0.9829 | 0.95847 | 0.9062 | 0.98261 | 0.95845 | 0.90636 | 0.98307 | 0.95848 | 0.90758
WB-Wide Bay | M023_6242 (Pialba-Point Vernon) 66 kV | Rating (A) | 605 | 668 | 547 | 605 | 668 | 547 | 605 | 668 | 547 | 605 | 668 | 547 | 605 | 668 | 547
WB-Wide Bay | M023_6242 (Pialba-Point Vernon) 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB-Wide Bay | M023_6242 (Pialba-Point Vernon) 66 kV | Min Voltage at Constrained Conductor | 65.572 | 65.5393 | 67.2896 | 65.4577 | 65.6075 | 66.8671 | 65.446 | 65.473 | 67.2979 | 65.6181 | 65.4783 | 67.2707 | 65.515 | 65.6388 | 67.2275
WB-Wide Bay | M023_6242 (Pialba-Point Vernon) 66 kV | Contingency Outage | 7187_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | M018_Maryborough-Maryborough City 66 kV | 7329_Maryborough 132 kV | 7329_Maryborough 132 kV | 7329_Maryborough 132 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 7187_Gin Gin - Bundaberg 132 kV | M012_Maryborough-Rocky St 66 kV | 786_Gin Gin - Bundaberg 132 kV | 7187_Gin Gin - Bundaberg 132 kV | M012_Maryborough-Rocky St 66 kV | 7187_Gin Gin - Bundaberg 132 kV | 7187_Gin Gin - Bundaberg 132 kV
WB-Wide Bay | M024_Gayndah - Mundubbera 66 kV | % of Rated A | 58.37% | 49.2% | 26.89% | 51.17% | 40.8% | 24.96% | 50.61% | 40.31% | 24.77% | 50.61% | 40.23% | 24.77% | 51.02% | 40.73% | 24.83%
WB-Wide Bay | M024_Gayndah - Mundubbera 66 kV | Limiting Line Name | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1
WB-Wide Bay | M024_Gayndah - Mundubbera 66 kV | Loading (A) | 77.0485 | 87.0837 | 45.7158 | 67.548 | 72.2171 | 42.425 | 66.8048 | 71.357 | 42.1172 | 66.8107 | 71.2015 | 42.1165 | 67.348 | 72.0958 | 42.2113
WB-Wide Bay | M024_Gayndah - Mundubbera 66 kV | Loading (MVA) | 7.6849 | 8.2524 | 4.3103 | 7.7122 | 8.2542 | 4.8557 | 7.6358 | 8.1576 | 4.8326 | 7.6356 | 8.1411 | 4.8328 | 7.6892 | 8.2307 | 4.8406
WB-Wide Bay | M024_Gayndah - Mundubbera 66 kV | Loading (MW) | 7.4759 | 8.124 | 3.9163 | 7.4153 | 8.012 | 4.0764 | 7.3264 | 7.9043 | 4.0323 | 7.3265 | 7.9035 | 4.0323 | 7.4084 | 8.0054 | 4.0724
WB-Wide Bay | M024_Gayndah - Mundubbera 66 kV | Power Factor | 0.97253 | 0.98247 | 0.90859 | 0.96149 | 0.97066 | 0.8395 | 0.95949 | 0.96894 | 0.83441 | 0.95952 | 0.97081 | 0.83437 | 0.96348 | 0.97263 | 0.8413
WB-Wide Bay | M024_Gayndah - Mundubbera 66 kV | Rating (A) | 132 | 177 | 170 | 132 | 177 | 170 | 132 | 177 | 170 | 132 | 177 | 170 | 132 | 177 | 170
WB-Wide Bay | M024_Gayndah - Mundubbera 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB-Wide Bay | M024_Gayndah - Mundubbera 66 kV | Min Voltage at Constrained Conductor | 56.3877 | 53.2499 | 53.9396 | 64.9297 | 64.872 | 65.777 | 65.0246 | 64.9115 | 65.9551 | 65.0168 | 64.9105 | 65.9591 | 64.9181 | 64.7823 | 65.9017
WB-Wide Bay | M024_Gayndah - Mundubbera 66 kV | Contingency Outage | M049_ISIS - Gayndah 66 kV | M049_ISIS - Gayndah 66 kV | M027_ISIS - Childers 66 kV | 7188_Gin Gin - Korenan QR 132 kV | 785_ISIS 132 kV | 785_ISIS 132 kV | 6302_Bundaberg Central - WEBU 66 kV | 785_ISIS 132 kV | 786_Gin Gin - Bundaberg 132 kV | 6302_Bundaberg Central - WEBU 66 kV | M049_ISIS - Gayndah 66 kV | 786_Gin Gin - Bundaberg 132 kV | M012_Maryborough-Rocky St 66 kV | M049_ISIS - Gayndah 66 kV | 786_Gin Gin - Bundaberg 132 kV
WB-Wide Bay | M025_Eidsvold 66 kV | % of Rated A | 14.69% | 14.72% | 6.094% | 12.67% | 11.91% | 5.256% | 11.93% | 11.22% | 4.978% | 11.93% | 11.23% | 4.978% | 12.67% | 11.93% | 5.247%
WB-Wide Bay | M025_Eidsvold 66 kV | Limiting Line Name | TR_LINE 7673_1 | TR_LINE 7673_1 | TR_LINE 77926_1 | TR_LINE 7673_1 | TR_LINE 7673_1 | TR_LINE 77926_1 | TR_LINE 7673_1 | TR_LINE 7673_1 | TR_LINE 77926_1 | TR_LINE 7673_1 | TR_LINE 7673_1 | TR_LINE 77926_1 | TR_LINE 7673_1 | TR_LINE 7673_1 | TR_LINE 77926_1
WB-Wide Bay | M025_Eidsvold 66 kV | Loading (A) | 15.7179 | 20.3096 | 8.0445 | 13.5531 | 16.4355 | 6.9374 | 12.7656 | 15.4901 | 6.5707 | 12.7672 | 15.491 | 6.5704 | 13.5561 | 16.4602 | 6.926
WB-Wide Bay | M025_Eidsvold 66 kV | Loading (MVA) | 1.5147 | 1.8394 | 0.74997 | 1.5094 | 1.8253 | 0.78949 | 1.4245 | 1.7223 | 0.74982 | 1.4245 | 1.7223 | 0.74983 | 1.5094 | 1.8254 | 0.78968
WB-Wide Bay | M025_Eidsvold 66 kV | Loading (MW) | 1.4966 | 1.8118 | 0.73779 | 1.4936 | 1.8043 | 0.76829 | 1.41 | 1.7032 | 0.7254 | 1.41 | 1.7032 | 0.7254 | 1.4936 | 1.8044 | 0.76833
WB-Wide Bay | M025_Eidsvold 66 kV | Power Factor | 0.98617 | 0.9824 | 0.98376 | 0.98811 | 0.9868 | 0.97315 | 0.98852 | 0.9873 | 0.96743 | 0.98852 | 0.9873 | 0.96742 | 0.98811 | 0.98678 | 0.97296
WB-Wide Bay | M025_Eidsvold 66 kV | Rating (A) | 107 | 138 | 132 | 107 | 138 | 132 | 107 | 138 | 132 | 107 | 138 | 132 | 107 | 138 | 132
WB-Wide Bay | M025_Eidsvold 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB-Wide Bay | M025_Eidsvold 66 kV | Min Voltage at Constrained Conductor | 55.6382 | 52.2898 | 53.8214 | 64.2984 | 64.119 | 65.7009 | 64.4237 | 64.1948 | 65.8821 | 64.4158 | 64.1911 | 65.8862 | 64.2845 | 64.0254 | 65.825
WB-Wide Bay | M025_Eidsvold 66 kV | Contingency Outage | M049_ISIS - Gayndah 66 kV | M049_ISIS - Gayndah 66 kV | M027_ISIS - Childers 66 kV | 7188_Gin Gin - Korenan QR 132 kV | 785_ISIS 132 kV | 785_ISIS 132 kV | 6302_Bundaberg Central - WEBU 66 kV | 785_ISIS 132 kV | 786_Gin Gin - Bundaberg 132 kV | 6302_Bundaberg Central - WEBU 66 kV | M049_ISIS - Gayndah 66 kV | 786_Gin Gin - Bundaberg 132 kV | M012_Maryborough-Rocky St 66 kV | M049_ISIS - Gayndah 66 kV | 786_Gin Gin - Bundaberg 132 kV
WB-Wide Bay | M026_ISIS - Bundaberg 66 kV | % of Rated A | 15.06% | 20.2% | 7.856% | 15.04% | 20.22% | 7.817% | 15.07% | 20.19% | 7.797% | 15.71% | 21.09% | 8.122% | 15.72% | 21.05% | 8.125%
WB-Wide Bay | M026_ISIS - Bundaberg 66 kV | Limiting Line Name | TR_CABLE 3770_1 | TR_CABLE 3770_1 | TR_CABLE 3770_1 | TR_CABLE 3770_1 | TR_CABLE 3770_1 | TR_CABLE 3770_1 | TR_CABLE 3770_1 | TR_CABLE 3770_1 | TR_CABLE 3770_1 | TR_CABLE 3770_1 | TR_CABLE 3770_1 | TR_CABLE 3770_1 | TR_CABLE 3770_1 | TR_CABLE 3770_1 | TR_CABLE 3770_1
WB-Wide Bay | M026_ISIS - Bundaberg 66 kV | Loading (A) | 15.0641 | 20.2024 | 7.8562 | 15.0434 | 20.2168 | 7.8171 | 15.0739 | 20.1899 | 7.7965 | 15.7103 | 21.0889 | 8.1222 | 15.7184 | 21.0459 | 8.1247
WB-Wide Bay | M026_ISIS - Bundaberg 66 kV | Loading (MVA) | 1.7447 | 2.3357 | 0.90876 | 1.7447 | 2.3357 | 0.90913 | 1.7447 | 2.3357 | 0.90911 | 1.8178 | 2.4339 | 0.94704 | 1.8179 | 2.4338 | 0.94705
WB-Wide Bay | M026_ISIS - Bundaberg 66 kV | Loading (MW) | 1.7228 | 2.3029 | 0.8994 | 1.7228 | 2.3029 | 0.89966 | 1.7228 | 2.3029 | 0.89966 | 1.7947 | 2.399 | 0.93714 | 1.7947 | 2.399 | 0.93714
WB-Wide Bay | M026_ISIS - Bundaberg 66 kV | Power Factor | 0.9872 | 0.98574 | 0.9892 | 0.98721 | 0.98573 | 0.98908 | 0.9872 | 0.98575 | 0.98909 | 0.98702 | 0.98547 | 0.98905 | 0.98701 | 0.9855 | 0.98905
WB-Wide Bay | M026_ISIS - Bundaberg 66 kV | Rating (A) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
WB-Wide Bay | M026_ISIS - Bundaberg 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB-Wide Bay | M026_ISIS - Bundaberg 66 kV | Min Voltage at Constrained Conductor | 66.8678 | 66.7506 | 66.7851 | 66.9591 | 66.7037 | 67.146 | 66.8247 | 66.7913 | 67.3217 | 66.8054 | 66.6329 | 67.3191 | 66.7711 | 66.7666 | 67.2981
WB-Wide Bay | M026_ISIS - Bundaberg 66 kV | Contingency Outage | 7315_Aramara 132 kV | 785_ISIS 132 kV | M027_ISIS - Childers 66 kV | 7315_Aramara 132 kV | 786_Gin Gin - Bundaberg 132 kV | 785_ISIS 132 kV | 6302_Bundaberg Central - WEBU 66 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 6302_Bundaberg Central - WEBU 66 kV | M039_Bundaberg-West Bundaberg No 1 66 kV | 786_Gin Gin - Bundaberg 132 kV | M039_Bundaberg-West Bundaberg No 1 66 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV
WB-Wide Bay | M026b_FORMER_ISIS - Bundaberg 66kV | % of Rated A | 0.2436% | 0.2227% | 0.2741% | 0.2435% | 0.2227% | 0.2747% | 0.2436% | 0.2226% | 0.2745% | 0.2436% | 0.2227% | 0.2744% | 0.2435% | 0.2228% | 0.2744%
WB-Wide Bay | M026b_FORMER_ISIS - Bundaberg 66kV | Limiting Line Name | TR_LINE 12084300_1 | TR_LINE 12084300_1 | TR_LINE 12084300_1 | TR_LINE 12084300_1 | TR_LINE 12084300_1 | TR_LINE 12084300_1 | TR_LINE 12084300_1 | TR_LINE 12084300_1 | TR_LINE 12084300_1 | TR_LINE 12084300_1 | TR_LINE 12084300_1 | TR_LINE 12084300_1 | TR_LINE 12084300_1 | TR_LINE 12084300_1 | TR_LINE 12084300_1
WB-Wide Bay | M026b_FORMER_ISIS - Bundaberg 66kV | Loading (A) | 1.0695 | 1.0691 | 1.0662 | 1.069 | 1.0687 | 1.0685 | 1.0694 | 1.0686 | 1.0677 | 1.0692 | 1.0691 | 1.0676 | 1.0691 | 1.0695 | 1.0674
WB-Wide Bay | M026b_FORMER_ISIS - Bundaberg 66kV | Loading (MVA) | 0.12347 | 0.12338 | 0.1227 | 0.12336 | 0.12329 | 0.12323 | 0.12344 | 0.12325 | 0.12305 | 0.1234 | 0.12339 | 0.12303 | 0.12338 | 0.12347 | 0.12298
WB-Wide Bay | M026b_FORMER_ISIS - Bundaberg 66kV | Loading (MW) | 1.9374e-06 | 1.9358e-06 | 1.9252e-06 | 1.9356e-06 | 1.9345e-06 | 1.9336e-06 | 1.9369e-06 | 1.9339e-06 | 1.9307e-06 | 1.9362e-06 | 1.936e-06 | 1.9305e-06 | 1.9358e-06 | 1.9372e-06 | 1.9296e-06
WB-Wide Bay | M026b_FORMER_ISIS - Bundaberg 66kV | Power Factor | 1.569e-05 | 1.569e-05 | 1.569e-05 | 1.569e-05 | 1.569e-05 | 1.569e-05 | 1.569e-05 | 1.569e-05 | 1.569e-05 | 1.569e-05 | 1.569e-05 | 1.569e-05 | 1.569e-05 | 1.569e-05 | 1.569e-05
WB-Wide Bay | M026b_FORMER_ISIS - Bundaberg 66kV | Rating (A) | 439 | 480 | 389 | 439 | 480 | 389 | 439 | 480 | 389 | 439 | 480 | 389 | 439 | 480 | 389
WB-Wide Bay | M026b_FORMER_ISIS - Bundaberg 66kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB-Wide Bay | M026b_FORMER_ISIS - Bundaberg 66kV | Min Voltage at Constrained Conductor | 66.6547 | 66.6285 | 66.4457 | 66.625 | 66.6057 | 66.5899 | 66.6462 | 66.5954 | 66.54 | 66.6349 | 66.6311 | 66.5358 | 66.628 | 66.6523 | 66.5206
WB-Wide Bay | M026b_FORMER_ISIS - Bundaberg 66kV | Contingency Outage | M029_Bundaberg - Farnsfield 66 kV | M010_Maryborough - Owanyilla 66 kV | SOBU-BARG-1_SOBU-Bargara-1 66 kV | M047_Mount Rawdon Tee 66 kV | M042_Meadowvale-Gooburrum 66 kV | M041_West Bundaberg-Meadowvale 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV | M042_Meadowvale-Gooburrum 66 kV | SOBU-BARG-1_SOBU-Bargara-1 66 kV | T014_Maryborough-Pialba Tee Howard 66 kV | M025_Eidsvold 66 kV | SOBU-BARG-1_SOBU-Bargara-1 66 kV | M027_ISIS - Childers 66 kV | 6315_ISCM - ISCI 66 kV | SOBU-BARG-1_SOBU-Bargara-1 66 kV
WB-Wide Bay | M027_ISIS - Childers 66 kV | % of Rated A | 139.1% | 147.8% | 86.54% | 74.55% | 77.58% | 55.31% | 74.31% | 77.05% | 54.88% | 74.72% | 77.64% | 55.18% | 74.91% | 77.71% | 55.14%
WB-Wide Bay | M027_ISIS - Childers 66 kV | Limiting Line Name | TR_LINE 172006_1 | TR_LINE 172006_1 | TR_LINE 183684_1 | TR_LINE 172006_1 | TR_LINE 172006_1 | TR_LINE 183684_1 | TR_LINE 172006_1 | TR_LINE 172006_1 | TR_LINE 183684_1 | TR_LINE 172006_1 | TR_LINE 172006_1 | TR_LINE 183684_1 | TR_LINE 172006_1 | TR_LINE 172006_1 | TR_LINE 183684_1
WB-Wide Bay | M027_ISIS - Childers 66 kV | Loading (A) | 358.7537 | 391.7236 | 202.4989 | 192.3295 | 205.5783 | 129.4332 | 191.709 | 204.1948 | 128.4245 | 192.7691 | 205.7577 | 129.1181 | 193.2558 | 205.9257 | 129.0363
WB-Wide Bay | M027_ISIS - Childers 66 kV | Loading (MVA) | 40.9408 | 44.2779 | 23.543 | 22.0596 | 23.4934 | 15.0155 | 21.9416 | 23.3651 | 14.9373 | 22.0622 | 23.4946 | 15.0197 | 22.1025 | 23.5563 | 15.0046
WB-Wide Bay | M027_ISIS - Childers 66 kV | Loading (MW) | 40.544 | 43.6107 | 23.387 | 21.9189 | 23.28 | 14.9963 | 21.7749 | 23.1222 | 14.9219 | 21.9196 | 23.2803 | 14.996 | 21.9355 | 23.3018 | 14.9875
WB-Wide Bay | M027_ISIS - Childers 66 kV | Power Factor | 0.99031 | 0.98493 | 0.99272 | 0.99362 | 0.99092 | 0.99862 | 0.9924 | 0.98961 | 0.99888 | 0.99353 | 0.99088 | 0.99832 | 0.99244 | 0.9892 | 0.99878
WB-Wide Bay | M027_ISIS - Childers 66 kV | Rating (A) | 258 | 265 | 234 | 258 | 265 | 234 | 258 | 265 | 234 | 258 | 265 | 234 | 258 | 265 | 234
WB-Wide Bay | M027_ISIS - Childers 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB-Wide Bay | M027_ISIS - Childers 66 kV | Min Voltage at Constrained Conductor | 65.6249 | 64.967 | 66.7315 | 66.0848 | 65.8321 | 66.7075 | 65.9435 | 65.9166 | 66.8829 | 65.9412 | 65.7779 | 66.892 | 65.8942 | 65.8959 | 66.8648
WB-Wide Bay | M027_ISIS - Childers 66 kV | Contingency Outage | M049_ISIS - Gayndah 66 kV | M049_ISIS - Gayndah 66 kV | M049_ISIS - Gayndah 66 kV | 7315_Aramara 132 kV | 786_Gin Gin - Bundaberg 132 kV | 785_ISIS 132 kV | 6302_Bundaberg Central - WEBU 66 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 6302_Bundaberg Central - WEBU 66 kV | M039_Bundaberg-West Bundaberg No 1 66 kV | 786_Gin Gin - Bundaberg 132 kV | M039_Bundaberg-West Bundaberg No 1 66 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV
WB-Wide Bay | M028_Childers - Gayndah 66 kV | % of Rated A | 162.5% | 129.6% | 115.3% | 3.139e-08% | 3.605e-08% | 1.14e-08% | 3.127e-08% | 3.578e-08% | 1.117e-08% | 3.148e-08% | 3.609e-08% | 1.151e-08% | 3.173e-08% | 3.635e-08% | 1.14e-08%
WB-Wide Bay | M028_Childers - Gayndah 66 kV | Limiting Line Name | TR_LINE 33780_2 | TR_LINE 33780_2 | TR_LINE 33780_1 | 3-Phase Link 66kV_M028 GAYNDAH_Term(1) | 3-Phase Link 66kV_M028 GAYNDAH_Term(1) | 3-Phase Link 66kV_M028 GAYNDAH_Term(1) | 3-Phase Link 66kV_M028 GAYNDAH_Term(1) | 3-Phase Link 66kV_M028 GAYNDAH_Term(1) | 3-Phase Link 66kV_M028 GAYNDAH_Term(1) | 3-Phase Link 66kV_M028 GAYNDAH_Term(1) | 3-Phase Link 66kV_M028 GAYNDAH_Term(1) | 3-Phase Link 66kV_M028 GAYNDAH_Term(1) | 3-Phase Link 66kV_M028 GAYNDAH_Term(1) | 3-Phase Link 66kV_M028 GAYNDAH_Term(1) | 3-Phase Link 66kV_M028 GAYNDAH_Term(1)
WB-Wide Bay | M028_Childers - Gayndah 66 kV | Loading (A) | 214.4391 | 216.3846 | 183.2935 | 1.5696e-06 | 1.8026e-06 | 5.7002e-07 | 1.5634e-06 | 1.7892e-06 | 5.5875e-07 | 1.5739e-06 | 1.8045e-06 | 5.7561e-07 | 1.5866e-06 | 1.8177e-06 | 5.7015e-07
WB-Wide Bay | M028_Childers - Gayndah 66 kV | Loading (MVA) | 20.0996 | 21.0029 | 17.0232 | 1.7966e-07 | 2.0554e-07 | 6.5781e-08 | 1.7857e-07 | 2.0428e-07 | 6.465e-08 | 1.7976e-07 | 2.0559e-07 | 6.6611e-08 | 1.8108e-07 | 2.0746e-07 | 6.5952e-08
WB-Wide Bay | M028_Childers - Gayndah 66 kV | Loading (MW) | 19.2838 | 19.7614 | 17.0206 | 1.772e-07 | 2.0114e-07 | 5.7353e-08 | 1.7566e-07 | 1.9938e-07 | 5.6493e-08 | 1.7725e-07 | 2.0116e-07 | 5.7298e-08 | 1.7823e-07 | 2.0227e-07 | 5.744e-08
WB-Wide Bay | M028_Childers - Gayndah 66 kV | Power Factor | 0.95935 | 0.94081 | 0.99281 | 0.98631 | 0.97859 | 0.87188 | 0.98373 | 0.97604 | 0.87383 | 0.98604 | 0.97847 | 0.86019 | 0.98427 | 0.975 | 0.87094
WB-Wide Bay | M028_Childers - Gayndah 66 kV | Rating (A) | 132 | 167 | 159 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000 | 5000
WB-Wide Bay | M028_Childers - Gayndah 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB-Wide Bay | M028_Childers - Gayndah 66 kV | Min Voltage at Constrained Conductor | 54.1073 | 56.0316 | 45.9183 | 66.0848 | 65.8321 | 66.6268 | 65.9435 | 65.9166 | 66.8024 | 65.9412 | 65.7779 | 66.812 | 65.8942 | 65.8959 | 66.7841
WB-Wide Bay | M028_Childers - Gayndah 66 kV | Contingency Outage | M027_ISIS - Childers 66 kV | M027_ISIS - Childers 66 kV | M027_ISIS - Childers 66 kV | 7315_Aramara 132 kV | 786_Gin Gin - Bundaberg 132 kV | 785_ISIS 132 kV | 6302_Bundaberg Central - WEBU 66 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 6302_Bundaberg Central - WEBU 66 kV | M039_Bundaberg-West Bundaberg No 1 66 kV | 786_Gin Gin - Bundaberg 132 kV | M039_Bundaberg-West Bundaberg No 1 66 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV
WB-Wide Bay | M029_Bundaberg - Farnsfield 66 kV | % of Rated A | 3.822% | 3.186% | 9.105% | 3.833% | 3.193% | 9.077% | 3.758% | 3.13% | 8.915% | 3.834% | 3.185% | 9.093% | 3.839% | 3.189% | 9.095%
WB-Wide Bay | M029_Bundaberg - Farnsfield 66 kV | Limiting Line Name | TR_LINE 8235_1 | TR_LINE 8235_1 | TR_LINE 8235_1 | TR_LINE 8235_1 | TR_LINE 8235_1 | TR_LINE 8235_1 | TR_LINE 8235_1 | TR_LINE 8235_1 | TR_LINE 8235_1 | TR_LINE 8235_1 | TR_LINE 8235_1 | TR_LINE 8235_1 | TR_LINE 8235_1 | TR_LINE 8235_1 | TR_LINE 8235_1
WB-Wide Bay | M029_Bundaberg - Farnsfield 66 kV | Loading (A) | 7.3759 | 8.7285 | 24.3115 | 7.3972 | 8.7485 | 24.2368 | 7.2537 | 8.5754 | 23.8018 | 7.3998 | 8.7267 | 24.2791 | 7.4089 | 8.7373 | 24.2845
WB-Wide Bay | M029_Bundaberg - Farnsfield 66 kV | Loading (MVA) | 0.83965 | 0.98977 | 2.7591 | 0.83967 | 0.98979 | 2.7588 | 0.82345 | 0.97066 | 2.7051 | 0.83967 | 0.98977 | 2.759 | 0.83968 | 0.98978 | 2.759
WB-Wide Bay | M029_Bundaberg - Farnsfield 66 kV | Loading (MW) | 0.72699 | 0.85637 | 2.3691 | 0.72699 | 0.85638 | 2.369 | 0.713 | 0.8399 | 2.3234 | 0.72699 | 0.85637 | 2.3691 | 0.72699 | 0.85638 | 2.3691
WB-Wide Bay | M029_Bundaberg - Farnsfield 66 kV | Power Factor | 0.86572 | 0.8651 | 0.85829 | 0.8657 | 0.86508 | 0.85836 | 0.86576 | 0.86516 | 0.85854 | 0.8657 | 0.8651 | 0.85832 | 0.86569 | 0.86509 | 0.85832
WB-Wide Bay | M029_Bundaberg - Farnsfield 66 kV | Rating (A) | 193 | 274 | 267 | 193 | 274 | 267 | 193 | 274 | 267 | 193 | 274 | 267 | 193 | 274 | 267
WB-Wide Bay | M029_Bundaberg - Farnsfield 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB-Wide Bay | M029_Bundaberg - Farnsfield 66 kV | Min Voltage at Constrained Conductor | 65.7238 | 65.4691 | 65.5221 | 65.5361 | 65.3209 | 65.7186 | 65.542 | 65.3508 | 65.6177 | 65.5132 | 65.4822 | 65.607 | 65.4334 | 65.4039 | 65.593
WB-Wide Bay | M029_Bundaberg - Farnsfield 66 kV | Contingency Outage | M049_ISIS - Gayndah 66 kV | 786_Gin Gin - Bundaberg 132 kV | M041_West Bundaberg-Meadowvale 66 kV | 7187_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 7187_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | M041_West Bundaberg-Meadowvale 66 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | M041_West Bundaberg-Meadowvale 66 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | M041_West Bundaberg-Meadowvale 66 kV
WB-Wide Bay | M030_Farnsfield - Childers 66 kV | % of Rated A | 37.26% | 38.44% | 12.8% | 36.51% | 33.59% | 12.76% | 36.6% | 33.54% | 12.8% | 36.6% | 33.63% | 13.02% | 37.09% | 34.04% | 13.03%
WB-Wide Bay | M030_Farnsfield - Childers 66 kV | Limiting Line Name | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1
WB-Wide Bay | M030_Farnsfield - Childers 66 kV | Loading (A) | 49.1881 | 64.1869 | 20.3501 | 48.1946 | 56.1006 | 20.293 | 48.3135 | 56.0146 | 20.3524 | 48.3154 | 56.156 | 20.6939 | 48.9572 | 56.8467 | 20.7224
WB-Wide Bay | M030_Farnsfield - Childers 66 kV | Loading (MVA) | 5.5727 | 5.5416 | 2.3844 | 5.4988 | 6.3702 | 2.3745 | 5.5004 | 6.3688 | 2.3909 | 5.5004 | 6.3712 | 2.4168 | 5.5697 | 6.4607 | 2.4192
WB-Wide Bay | M030_Farnsfield - Childers 66 kV | Loading (MW) | 5.5356 | 2.7012 | 1.5774 | 5.4631 | 6.2733 | 1.5569 | 5.4633 | 6.2732 | 1.557 | 5.4633 | 6.2734 | 1.5571 | 5.5353 | 6.3564 | 1.5775
WB-Wide Bay | M030_Farnsfield - Childers 66 kV | Power Factor | 0.99281 | 0.48527 | 0.66154 | 0.99296 | 0.98414 | 0.6557 | 0.99269 | 0.98435 | 0.6512 | 0.99268 | 0.984 | 0.64428 | 0.99331 | 0.98321 | 0.65209
WB-Wide Bay | M030_Farnsfield - Childers 66 kV | Rating (A) | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159 | 132 | 167 | 159
WB-Wide Bay | M030_Farnsfield - Childers 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB-Wide Bay | M030_Farnsfield - Childers 66 kV | Min Voltage at Constrained Conductor | 65.3231 | 49.846 | 67.648 | 65.7897 | 65.4605 | 67.5553 | 65.6468 | 65.5462 | 67.8252 | 65.6445 | 65.4056 | 67.4277 | 65.5955 | 65.517 | 67.4021
WB-Wide Bay | M030_Farnsfield - Childers 66 kV | Contingency Outage | M049_ISIS - Gayndah 66 kV | M027_ISIS - Childers 66 kV | M018_Maryborough-Maryborough City 66 kV | 7315_Aramara 132 kV | 786_Gin Gin - Bundaberg 132 kV | 6315_ISCM - ISCI 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 786_Gin Gin - Bundaberg 132 kV | 6315_ISCM - ISCI 66 kV | 6302_Bundaberg Central - WEBU 66 kV | M039_Bundaberg-West Bundaberg No 1 66 kV | M047_Mount Rawdon Tee 66 kV | M039_Bundaberg-West Bundaberg No 1 66 kV | 786_Gin Gin - Bundaberg 132 kV | M047_Mount Rawdon Tee 66 kV
WB-Wide Bay | M032_Bundaberg-South Kolan No 1 66 kV | % of Rated A | 62.12% | 52.15% | 27.01% | 62.3% | 52.27% | 26.98% | 61.65% | 51.72% | 26.79% | 62.32% | 52.14% | 27% | 63.05% | 52.73% | 27.2%
WB-Wide Bay | M032_Bundaberg-South Kolan No 1 66 kV | Limiting Line Name | TR_LINE 138990_1 | TR_LINE 138990_1 | TR_LINE 138990_1 | TR_LINE 138990_1 | TR_LINE 138990_1 | TR_LINE 138990_1 | TR_LINE 138990_1 | TR_LINE 138990_1 | TR_LINE 138990_1 | TR_LINE 138990_1 | TR_LINE 138990_1 | TR_LINE 138990_1 | TR_LINE 138990_1 | TR_LINE 138990_1 | TR_LINE 138990_1
WB-Wide Bay | M032_Bundaberg-South Kolan No 1 66 kV | Loading (A) | 81.9948 | 92.299 | 45.9191 | 82.2322 | 92.5181 | 45.859 | 81.3745 | 91.5457 | 45.5435 | 82.2612 | 92.2806 | 45.893 | 83.2212 | 93.3314 | 46.2472
WB-Wide Bay | M032_Bundaberg-South Kolan No 1 66 kV | Loading (MVA) | 9.3098 | 10.4268 | 5.2266 | 9.3098 | 10.4275 | 5.2354 | 9.2138 | 10.323 | 5.1911 | 9.3098 | 10.4268 | 5.2304 | 9.4061 | 10.5317 | 5.2695
WB-Wide Bay | M032_Bundaberg-South Kolan No 1 66 kV | Loading (MW) | 9.2977 | 10.4235 | 4.7436 | 9.2988 | 10.4248 | 4.7435 | 9.2012 | 10.3193 | 4.6946 | 9.299 | 10.4236 | 4.7436 | 9.3972 | 10.5294 | 4.7926
WB-Wide Bay | M032_Bundaberg-South Kolan No 1 66 kV | Power Factor | 0.9987 | 0.99969 | 0.90759 | 0.99882 | 0.99973 | 0.90604 | 0.99863 | 0.99964 | 0.90435 | 0.99884 | 0.99969 | 0.90692 | 0.99906 | 0.99979 | 0.9095
WB-Wide Bay | M032_Bundaberg-South Kolan No 1 66 kV | Rating (A) | 132 | 177 | 170 | 132 | 177 | 170 | 132 | 177 | 170 | 132 | 177 | 170 | 132 | 177 | 170
WB-Wide Bay | M032_Bundaberg-South Kolan No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB-Wide Bay | M032_Bundaberg-South Kolan No 1 66 kV | Min Voltage at Constrained Conductor | 65.5528 | 65.2214 | 65.7153 | 65.3634 | 65.0717 | 65.912 | 65.3712 | 65.1037 | 65.8072 | 65.3404 | 65.2345 | 65.8003 | 65.2549 | 65.1488 | 65.7837
WB-Wide Bay | M032_Bundaberg-South Kolan No 1 66 kV | Contingency Outage | M049_ISIS - Gayndah 66 kV | 786_Gin Gin - Bundaberg 132 kV | M041_West Bundaberg-Meadowvale 66 kV | 7187_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 7187_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | M041_West Bundaberg-Meadowvale 66 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | M041_West Bundaberg-Meadowvale 66 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | M041_West Bundaberg-Meadowvale 66 kV
WB-Wide Bay | M033_Wallaville 66 kV | % of Rated A | 26.15% | 28.58% | 17.87% | 26.21% | 28.64% | 17.85% | 25.9% | 28.29% | 17.72% | 26.22% | 28.57% | 17.86% | 26.57% | 28.94% | 18%
WB-Wide Bay | M033_Wallaville 66 kV | Limiting Line Name | TR_LINE 214482_2 | TR_LINE 214482_2 | TR_LINE 214482_2 | TR_LINE 214482_2 | TR_LINE 214482_2 | TR_LINE 214482_2 | TR_LINE 214482_2 | TR_LINE 214482_2 | TR_LINE 214482_2 | TR_LINE 214482_2 | TR_LINE 214482_2 | TR_LINE 214482_2 | TR_LINE 214482_2 | TR_LINE 214482_2 | TR_LINE 214482_2
WB-Wide Bay | M033_Wallaville 66 kV | Loading (A) | 67.4566 | 75.724 | 41.8054 | 67.6343 | 75.8901 | 41.7638 | 66.8092 | 74.9603 | 41.456 | 67.656 | 75.7096 | 41.7873 | 68.5595 | 76.7002 | 42.1227
WB-Wide Bay | M033_Wallaville 66 kV | Loading (MVA) | 7.5711 | 8.4403 | 4.7418 | 7.5684 | 8.4387 | 4.7514 | 7.4782 | 8.341 | 4.7092 | 7.5681 | 8.4405 | 4.7459 | 7.6575 | 8.5377 | 4.7824
WB-Wide Bay | M033_Wallaville 66 kV | Loading (MW) | 7.4894 | 8.3793 | 4.1537 | 7.4899 | 8.3799 | 4.1537 | 7.3945 | 8.2774 | 4.1052 | 7.4899 | 8.3793 | 4.1537 | 7.5855 | 8.482 | 4.2021
WB-Wide Bay | M033_Wallaville 66 kV | Power Factor | 0.9892 | 0.99278 | 0.87598 | 0.98962 | 0.99303 | 0.87419 | 0.98881 | 0.99237 | 0.87175 | 0.98967 | 0.99275 | 0.87521 | 0.9906 | 0.99348 | 0.87866
WB-Wide Bay | M033_Wallaville 66 kV | Rating (A) | 258 | 265 | 234 | 258 | 265 | 234 | 258 | 265 | 234 | 258 | 265 | 234 | 258 | 265 | 234
WB-Wide Bay | M033_Wallaville 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB-Wide Bay | M033_Wallaville 66 kV | Min Voltage at Constrained Conductor | 64.7928 | 64.344 | 65.4837 | 64.5993 | 64.1906 | 65.6828 | 64.6179 | 64.2351 | 65.5818 | 64.5757 | 64.3573 | 65.5697 | 64.4775 | 64.2579 | 65.5479
WB-Wide Bay | M033_Wallaville 66 kV | Contingency Outage | M049_ISIS - Gayndah 66 kV | 786_Gin Gin - Bundaberg 132 kV | M041_West Bundaberg-Meadowvale 66 kV | 7187_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 7187_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | M041_West Bundaberg-Meadowvale 66 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | M041_West Bundaberg-Meadowvale 66 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | M041_West Bundaberg-Meadowvale 66 kV
WB-Wide Bay | M034_Monduran Dam 66 kV | % of Rated A | 9.639% | 9.138% | 4.957% | 9.67% | 9.161% | 4.942% | 9.666% | 9.153% | 4.95% | 9.674% | 9.136% | 4.951% | 9.69% | 9.152% | 4.953%
WB-Wide Bay | M034_Monduran Dam 66 kV | Limiting Line Name | TR_LINE 209283_1 | TR_LINE 209283_1 | TR_LINE 209283_1 | TR_LINE 209283_1 | TR_LINE 209283_1 | TR_LINE 209283_1 | TR_LINE 209283_1 | TR_LINE 209283_1 | TR_LINE 209283_1 | TR_LINE 209283_1 | TR_LINE 209283_1 | TR_LINE 209283_1 | TR_LINE 209283_1 | TR_LINE 209283_1 | TR_LINE 209283_1
WB-Wide Bay | M034_Monduran Dam 66 kV | Loading (A) | 12.724 | 16.1745 | 8.4274 | 12.7643 | 16.2152 | 8.4017 | 12.7588 | 16.2011 | 8.4142 | 12.7692 | 16.171 | 8.4163 | 12.7914 | 16.1995 | 8.4196
WB-Wide Bay | M034_Monduran Dam 66 kV | Loading (MVA) | 1.4131 | 1.7801 | 0.95179 | 1.4132 | 1.7802 | 0.95183 | 1.4132 | 1.7802 | 0.95181 | 1.4132 | 1.7801 | 0.95181 | 1.4133 | 1.7802 | 0.95181
WB-Wide Bay | M034_Monduran Dam 66 kV | Loading (MW) | 1.1797 | 1.6101 | 0.91134 | 1.1796 | 1.6101 | 0.91139 | 1.1797 | 1.6101 | 0.91137 | 1.1796 | 1.6101 | 0.91136 | 1.1796 | 1.6101 | 0.91136
WB-Wide Bay | M034_Monduran Dam 66 kV | Power Factor | 0.832 | 0.90075 | 0.9556 | 0.83188 | 0.90068 | 0.95564 | 0.8319 | 0.90071 | 0.95562 | 0.83187 | 0.90076 | 0.95562 | 0.83181 | 0.90071 | 0.95561
WB-Wide Bay | M034_Monduran Dam 66 kV | Rating (A) | 132 | 177 | 170 | 132 | 177 | 170 | 132 | 177 | 170 | 132 | 177 | 170 | 132 | 177 | 170
WB-Wide Bay | M034_Monduran Dam 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB-Wide Bay | M034_Monduran Dam 66 kV | Min Voltage at Constrained Conductor | 64.1186 | 63.5412 | 65.2065 | 63.9215 | 63.3845 | 65.4077 | 63.9483 | 63.4385 | 65.3094 | 63.8976 | 63.5548 | 65.2935 | 63.7896 | 63.4448 | 65.2676
WB-Wide Bay | M034_Monduran Dam 66 kV | Contingency Outage | M049_ISIS - Gayndah 66 kV | 786_Gin Gin - Bundaberg 132 kV | M041_West Bundaberg-Meadowvale 66 kV | 7187_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 7187_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | M041_West Bundaberg-Meadowvale 66 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | M041_West Bundaberg-Meadowvale 66 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | M041_West Bundaberg-Meadowvale 66 kV
WB-Wide Bay | M035_Bundaberg-South Kolan No 2 66 kV | % of Rated A | 9.617% | 11.49% | 5.912% | 9.646% | 11.52% | 5.899% | 9.569% | 11.43% | 5.87% | 9.65% | 11.49% | 5.907% | 9.788% | 11.66% | 5.973%
WB-Wide Bay | M035_Bundaberg-South Kolan No 2 66 kV | Limiting Line Name | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1
WB-Wide Bay | M035_Bundaberg-South Kolan No 2 66 kV | Loading (A) | 52.6987 | 66.5244 | 30.8038 | 52.8599 | 66.6905 | 30.7333 | 52.436 | 66.1976 | 30.581 | 52.8795 | 66.511 | 30.7732 | 53.639 | 67.5083 | 31.1206
WB-Wide Bay | M035_Bundaberg-South Kolan No 2 66 kV | Loading (MVA) | 5.9928 | 7.5272 | 3.5074 | 5.9937 | 7.5287 | 3.5098 | 5.9464 | 7.4766 | 3.4868 | 5.9938 | 7.5271 | 3.5084 | 6.0717 | 7.6301 | 3.5472
WB-Wide Bay | M035_Bundaberg-South Kolan No 2 66 kV | Loading (MW) | 5.9924 | 7.5104 | 3.414 | 5.9931 | 7.5112 | 3.4138 | 5.946 | 7.4603 | 3.3903 | 5.9932 | 7.5104 | 3.4139 | 6.0707 | 7.611 | 3.4565
WB-Wide Bay | M035_Bundaberg-South Kolan No 2 66 kV | Power Factor | 0.99967 | 0.99713 | 0.97338 | 0.99962 | 0.99703 | 0.97267 | 0.99968 | 0.99717 | 0.97234 | 0.99961 | 0.99713 | 0.97307 | 0.99948 | 0.99683 | 0.97444
WB-Wide Bay | M035_Bundaberg-South Kolan No 2 66 kV | Rating (A) | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521 | 548 | 579 | 521
WB-Wide Bay | M035_Bundaberg-South Kolan No 2 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB-Wide Bay | M035_Bundaberg-South Kolan No 2 66 kV | Min Voltage at Constrained Conductor | 65.5596 | 65.2263 | 65.7117 | 65.3704 | 65.0767 | 65.9083 | 65.3778 | 65.1084 | 65.8034 | 65.3474 | 65.2395 | 65.7967 | 65.262 | 65.1539 | 65.7801
WB-Wide Bay | M035_Bundaberg-South Kolan No 2 66 kV | Contingency Outage | M049_ISIS - Gayndah 66 kV | 786_Gin Gin - Bundaberg 132 kV | M041_West Bundaberg-Meadowvale 66 kV | 7187_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 7187_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | M041_West Bundaberg-Meadowvale 66 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | M041_West Bundaberg-Meadowvale 66 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | M041_West Bundaberg-Meadowvale 66 kV
WB-Wide Bay | M036_Bundaberg-South Bundaberg 66 kV | % of Rated A | 116.8% | 109.9% | 79.85% | 116.3% | 109.6% | 79.67% | 116.2% | 109.5% | 79.4% | 116.8% | 109.6% | 79.7% | 118.1% | 110.9% | 80.36%
WB-Wide Bay | M036_Bundaberg-South Bundaberg 66 kV | Limiting Line Name | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1
WB-Wide Bay | M036_Bundaberg-South Bundaberg 66 kV | Loading (A) | 512.6452 | 527.5809 | 310.5973 | 510.7046 | 525.9281 | 309.925 | 510.2652 | 525.6184 | 308.8769 | 512.7167 | 525.9365 | 310.0349 | 518.6691 | 532.1561 | 312.6114
WB-Wide Bay | M036_Bundaberg-South Bundaberg 66 kV | Loading (MVA) | 58.9444 | 60.4799 | 35.5876 | 58.5266 | 60.1634 | 35.4458 | 58.5308 | 60.1858 | 35.4687 | 58.7972 | 60.462 | 35.5981 | 59.4347 | 61.102 | 35.8828
WB-Wide Bay | M036_Bundaberg-South Bundaberg 66 kV | Loading (MW) | 58.7013 | 60.2045 | 33.1181 | 58.2384 | 59.8151 | 32.8824 | 58.2336 | 59.8465 | 32.8731 | 58.5125 | 60.1386 | 33.0295 | 59.1704 | 60.815 | 33.3849
WB-Wide Bay | M036_Bundaberg-South Bundaberg 66 kV | Power Factor | 0.98728 | 0.98611 | 0.9143 | 0.98587 | 0.98396 | 0.91105 | 0.98563 | 0.98424 | 0.91025 | 0.98597 | 0.98478 | 0.9113 | 0.98651 | 0.98576 | 0.91396
WB-Wide Bay | M036_Bundaberg-South Bundaberg 66 kV | Rating (A) | 439 | 480 | 389 | 439 | 480 | 389 | 439 | 480 | 389 | 439 | 480 | 389 | 439 | 480 | 389
WB-Wide Bay | M036_Bundaberg-South Bundaberg 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB-Wide Bay | M036_Bundaberg-South Bundaberg 66 kV | Min Voltage at Constrained Conductor | 64.2903 | 64.0587 | 65.6868 | 64.1182 | 63.9855 | 65.5915 | 64.1884 | 64.0431 | 65.8663 | 64.1516 | 64.2909 | 65.8499 | 64.0601 | 64.155 | 65.805
WB-Wide Bay | M036_Bundaberg-South Bundaberg 66 kV | Contingency Outage | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV
WB-Wide Bay | M037_South - East Bundaberg 66 kV | % of Rated A | 128.6% | 86.85% | 68.08% | 128% | 86.77% | 68.08% | 127.9% | 86.7% | 67.83% | 128.3% | 86.51% | 67.96% | 129.9% | 87.46% | 68.42%
WB-Wide Bay | M037_South - East Bundaberg 66 kV | Limiting Line Name | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1
WB-Wide Bay | M037_South - East Bundaberg 66 kV | Loading (A) | 290.6316 | 270.0983 | 175.6439 | 289.2497 | 269.8702 | 175.6349 | 289.0716 | 269.6379 | 174.9928 | 289.9703 | 269.0439 | 175.3256 | 293.5563 | 271.9865 | 176.5295
WB-Wide Bay | M037_South - East Bundaberg 66 kV | Loading (MVA) | 32.3249 | 29.9498 | 19.9994 | 32.0887 | 29.8952 | 19.9706 | 32.1046 | 29.8956 | 19.9809 | 32.1855 | 29.9442 | 20.0138 | 32.5357 | 30.2059 | 20.1369
WB-Wide Bay | M037_South - East Bundaberg 66 kV | Loading (MW) | 31.4565 | 28.5736 | 16.7264 | 31.1056 | 28.297 | 16.5517 | 31.1052 | 28.3317 | 16.5486 | 31.1966 | 28.4267 | 16.5957 | 31.5619 | 28.7508 | 16.788
WB-Wide Bay | M037_South - East Bundaberg 66 kV | Power Factor | 0.97005 | 0.95029 | 0.83249 | 0.96606 | 0.94247 | 0.82485 | 0.96555 | 0.94367 | 0.82432 | 0.96596 | 0.9454 | 0.82531 | 0.96674 | 0.94795 | 0.82979
WB-Wide Bay | M037_South - East Bundaberg 66 kV | Rating (A) | 226 | 311 | 258 | 226 | 311 | 258 | 226 | 311 | 258 | 226 | 311 | 258 | 226 | 311 | 258
WB-Wide Bay | M037_South - East Bundaberg 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB-Wide Bay | M037_South - East Bundaberg 66 kV | Min Voltage at Constrained Conductor | 63.8832 | 63.7738 | 65.7392 | 63.7349 | 63.7327 | 65.6477 | 63.8082 | 63.7857 | 65.9225 | 63.7679 | 64.0273 | 65.9058 | 63.6671 | 63.8779 | 65.859
WB-Wide Bay | M037_South - East Bundaberg 66 kV | Contingency Outage | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV | 6302_Bundaberg Central - WEBU 66 kV
WB-Wide Bay | M039_Bundaberg-West Bundaberg No 1 66 kV | % of Rated A | 67.91% | 58.89% | 43.09% | 66.58% | 57.75% | 41.68% | 66.18% | 57.45% | 41.38% | 66.15% | 57.21% | 41.37% | 66.73% | 57.73% | 41.65%
WB-Wide Bay | M039_Bundaberg-West Bundaberg No 1 66 kV | Limiting Line Name | TR_LINE 200241_1 | TR_LINE 200241_1 | TR_LINE 200241_1 | TR_LINE 7876_1 | TR_LINE 7853_1 | TR_LINE 200241_1 | TR_LINE 7876_1 | TR_LINE 200241_1 | TR_LINE 200241_1 | TR_LINE 7876_1 | TR_LINE 200241_1 | TR_LINE 200241_1 | TR_LINE 7876_1 | TR_LINE 7853_1 | TR_LINE 200241_1
WB-Wide Bay | M039_Bundaberg-West Bundaberg No 1 66 kV | Loading (A) | 547.3547 | 531.7694 | 321.0247 | 536.6167 | 521.4908 | 310.5101 | 533.3796 | 518.7473 | 308.2943 | 533.1341 | 516.6006 | 308.1984 | 537.8127 | 521.3432 | 310.2834
WB-Wide Bay | M039_Bundaberg-West Bundaberg No 1 66 kV | Loading (MVA) | 63.0401 | 61.0622 | 36.8153 | 61.3901 | 59.7128 | 35.5415 | 61.06 | 59.5023 | 35.4304 | 61.0206 | 59.4967 | 35.4164 | 61.4901 | 59.9348 | 35.6458
WB-Wide Bay | M039_Bundaberg-West Bundaberg No 1 66 kV | Loading (MW) | 63.0182 | 61.0198 | 35.3217 | 61.3864 | 59.7128 | 34.5403 | 61.0582 | 59.5022 | 34.3674 | 61.019 | 59.4967 | 34.3499 | 61.4862 | 59.9347 | 34.6122
WB-Wide Bay | M039_Bundaberg-West Bundaberg No 1 66 kV | Power Factor | 0.99964 | 0.99928 | 0.95935 | 0.99994 | 1 | 0.97175 | 0.99997 | 1 | 0.96992 | 0.99997 | 1 | 0.96981 | 0.99994 | 1 | 0.97093
WB-Wide Bay | M039_Bundaberg-West Bundaberg No 1 66 kV | Rating (A) | 806 | 903 | 745 | 806 | 903 | 745 | 806 | 903 | 745 | 806 | 903 | 745 | 806 | 903 | 745
WB-Wide Bay | M039_Bundaberg-West Bundaberg No 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB-Wide Bay | M039_Bundaberg-West Bundaberg No 1 66 kV | Min Voltage at Constrained Conductor | 66.4863 | 66.2884 | 66.2103 | 66.0175 | 66.0859 | 66.0845 | 66.0617 | 66.2152 | 66.3513 | 66.0495 | 66.4842 | 66.3457 | 65.9778 | 66.3503 | 66.3269
WB-Wide Bay | M039_Bundaberg-West Bundaberg No 1 66 kV | Contingency Outage | M040_Bundaberg-West Bundaberg No 2 66 kV | M040_Bundaberg-West Bundaberg No 2 66 kV | M040_Bundaberg-West Bundaberg No 2 66 kV | M040_Bundaberg-West Bundaberg No 2 66 kV | M040_Bundaberg-West Bundaberg No 2 66 kV | M040_Bundaberg-West Bundaberg No 2 66 kV | M040_Bundaberg-West Bundaberg No 2 66 kV | M040_Bundaberg-West Bundaberg No 2 66 kV | M040_Bundaberg-West Bundaberg No 2 66 kV | M040_Bundaberg-West Bundaberg No 2 66 kV | M040_Bundaberg-West Bundaberg No 2 66 kV | M040_Bundaberg-West Bundaberg No 2 66 kV | M040_Bundaberg-West Bundaberg No 2 66 kV | M040_Bundaberg-West Bundaberg No 2 66 kV | M040_Bundaberg-West Bundaberg No 2 66 kV
WB-Wide Bay | M040_Bundaberg-West Bundaberg No 2 66 kV | % of Rated A | 67.47% | 58.5% | 42.79% | 66.15% | 57.37% | 41.39% | 65.74% | 57.07% | 41.1% | 65.71% | 56.83% | 41.08% | 66.29% | 57.36% | 41.36%
WB-Wide Bay | M040_Bundaberg-West Bundaberg No 2 66 kV | Limiting Line Name | TR_LINE 169764_1 | TR_LINE 169764_1 | TR_LINE 169764_1 | TR_LINE 7295_1 | TR_LINE 169764_1 | TR_LINE 169764_1 | TR_LINE 169764_1 | TR_LINE 169764_1 | TR_LINE 169764_1 | TR_LINE 169764_1 | TR_LINE 169764_1 | TR_LINE 169764_1 | TR_LINE 7295_1 | TR_LINE 169764_1 | TR_LINE 169764_1
WB-Wide Bay | M040_Bundaberg-West Bundaberg No 2 66 kV | Loading (A) | 543.7759 | 528.2784 | 318.8085 | 533.1368 | 518.0842 | 308.3698 | 529.9034 | 515.3333 | 306.1672 | 529.6591 | 513.2092 | 306.072 | 534.3105 | 517.9266 | 308.1432
WB-Wide Bay | M040_Bundaberg-West Bundaberg No 2 66 kV | Loading (MVA) | 62.6177 | 60.652 | 36.5675 | 60.9553 | 59.3657 | 35.2952 | 60.8704 | 59.1042 | 35.1848 | 60.8306 | 59.0985 | 35.1709 | 61.0544 | 59.5862 | 35.3988
WB-Wide Bay | M040_Bundaberg-West Bundaberg No 2 66 kV | Loading (MW) | 62.6008 | 60.6165 | 35.1009 | 60.9504 | 59.3639 | 34.3206 | 60.852 | 59.1035 | 34.1493 | 60.8129 | 59.0981 | 34.132 | 61.0494 | 59.5843 | 34.3923
WB-Wide Bay | M040_Bundaberg-West Bundaberg No 2 66 kV | Power Factor | 0.99924 | 0.99878 | 0.95765 | 0.99992 | 0.99997 | 0.97041 | 0.9997 | 0.99995 | 0.96856 | 0.99971 | 0.99994 | 0.96845 | 0.99992 | 0.99997 | 0.96957
WB-Wide Bay | M040_Bundaberg-West Bundaberg No 2 66 kV | Rating (A) | 806 | 903 | 745 | 806 | 903 | 745 | 806 | 903 | 745 | 806 | 903 | 745 | 806 | 903 | 745
WB-Wide Bay | M040_Bundaberg-West Bundaberg No 2 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB-Wide Bay | M040_Bundaberg-West Bundaberg No 2 66 kV | Min Voltage at Constrained Conductor | 66.2637 | 66.0834 | 66.2077 | 65.6765 | 65.9147 | 66.082 | 66.0562 | 65.9791 | 66.3492 | 66.044 | 66.2488 | 66.3437 | 65.6376 | 66.1804 | 66.3248
WB-Wide Bay | M040_Bundaberg-West Bundaberg No 2 66 kV | Contingency Outage | M039_Bundaberg-West Bundaberg No 1 66 kV | M039_Bundaberg-West Bundaberg No 1 66 kV | M039_Bundaberg-West Bundaberg No 1 66 kV | M039_Bundaberg-West Bundaberg No 1 66 kV | M039_Bundaberg-West Bundaberg No 1 66 kV | M039_Bundaberg-West Bundaberg No 1 66 kV | M039_Bundaberg-West Bundaberg No 1 66 kV | M039_Bundaberg-West Bundaberg No 1 66 kV | M039_Bundaberg-West Bundaberg No 1 66 kV | M039_Bundaberg-West Bundaberg No 1 66 kV | M039_Bundaberg-West Bundaberg No 1 66 kV | M039_Bundaberg-West Bundaberg No 1 66 kV | M039_Bundaberg-West Bundaberg No 1 66 kV | M039_Bundaberg-West Bundaberg No 1 66 kV | M039_Bundaberg-West Bundaberg No 1 66 kV
WB-Wide Bay | M041_West Bundaberg-Meadowvale 66 kV | % of Rated A | 50.06% | 42.27% | 25.98% | 49.54% | 41.79% | 25.63% | 49.53% | 41.77% | 25.76% | 49.55% | 41.69% | 25.77% | 50.31% | 42.35% | 26.1%
WB-Wide Bay | M041_West Bundaberg-Meadowvale 66 kV | Limiting Line Name | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1
WB-Wide Bay | M041_West Bundaberg-Meadowvale 66 kV | Loading (A) | 113.1452 | 131.4704 | 67.0344 | 111.9639 | 129.9615 | 66.1191 | 111.9488 | 129.8986 | 66.4717 | 111.9905 | 129.6517 | 66.4761 | 113.7085 | 131.699 | 67.343
WB-Wide Bay | M041_West Bundaberg-Meadowvale 66 kV | Loading (MVA) | 12.6226 | 14.582 | 7.5575 | 12.4442 | 14.3724 | 7.4654 | 12.4444 | 14.3728 | 7.4985 | 12.4438 | 14.3753 | 7.4983 | 12.6148 | 14.5799 | 7.592
WB-Wide Bay | M041_West Bundaberg-Meadowvale 66 kV | Loading (MW) | 11.4001 | 13.2372 | 6.4066 | 11.2356 | 13.0433 | 6.3115 | 11.2356 | 13.043 | 6.3115 | 11.2357 | 13.0424 | 6.3116 | 11.4012 | 13.2378 | 6.4062
WB-Wide Bay | M041_West Bundaberg-Meadowvale 66 kV | Power Factor | 0.90306 | 0.90778 | 0.84647 | 0.90278 | 0.90752 | 0.84421 | 0.90276 | 0.90747 | 0.84047 | 0.90282 | 0.90728 | 0.8405 | 0.90373 | 0.90795 | 0.84257
WB-Wide Bay | M041_West Bundaberg-Meadowvale 66 kV | Rating (A) | 226 | 311 | 258 | 226 | 311 | 258 | 226 | 311 | 258 | 226 | 311 | 258 | 226 | 311 | 258
WB-Wide Bay | M041_West Bundaberg-Meadowvale 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB-Wide Bay | M041_West Bundaberg-Meadowvale 66 kV | Min Voltage at Constrained Conductor | 64.2649 | 63.8474 | 65.0911 | 64.0268 | 63.6627 | 65.1879 | 64.0367 | 63.6959 | 65.1298 | 64.0095 | 63.8292 | 65.1233 | 63.9037 | 63.7261 | 65.0883
WB-Wide Bay | M041_West Bundaberg-Meadowvale 66 kV | Contingency Outage | M049_ISIS - Gayndah 66 kV | 786_Gin Gin - Bundaberg 132 kV | M027_ISIS - Childers 66 kV | 7187_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 6302_Bundaberg Central - WEBU 66 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV
WB-Wide Bay | M042_Meadowvale-Gooburrum 66 kV | % of Rated A | 34.68% | 33.19% | 20.34% | 34.13% | 32.63% | 19.91% | 34.12% | 32.62% | 19.93% | 34.14% | 32.54% | 19.93% | 34.88% | 33.26% | 20.34%
WB-Wide Bay | M042_Meadowvale-Gooburrum 66 kV | Limiting Line Name | TR_LINE 7778_1 | TR_LINE 7778_1 | TR_LINE 7778_1 | TR_LINE 7778_1 | TR_LINE 7778_1 | TR_LINE 7778_1 | TR_LINE 7778_1 | TR_LINE 7778_1 | TR_LINE 7778_1 | TR_LINE 7778_1 | TR_LINE 7778_1 | TR_LINE 7778_1 | TR_LINE 7778_1 | TR_LINE 7778_1 | TR_LINE 7778_1
WB-Wide Bay | M042_Meadowvale-Gooburrum 66 kV | Loading (A) | 38.4909 | 48.4614 | 24.2083 | 37.8793 | 47.6467 | 23.6943 | 37.8731 | 47.619 | 23.716 | 37.89 | 47.5129 | 23.7185 | 38.72 | 48.56 | 24.2039
WB-Wide Bay | M042_Meadowvale-Gooburrum 66 kV | Loading (MVA) | 4.2342 | 5.2968 | 2.7089 | 4.1514 | 5.1928 | 2.6558 | 4.1514 | 5.1925 | 2.6558 | 4.1515 | 5.1918 | 2.6558 | 4.2356 | 5.2975 | 2.7083
WB-Wide Bay | M042_Meadowvale-Gooburrum 66 kV | Loading (MW) | 3.9139 | 4.8757 | 2.5077 | 3.8382 | 4.7812 | 2.459 | 3.8382 | 4.781 | 2.459 | 3.8382 | 4.7808 | 2.459 | 3.9143 | 4.8759 | 2.5075
WB-Wide Bay | M042_Meadowvale-Gooburrum 66 kV | Power Factor | 0.91811 | 0.91557 | 0.92169 | 0.91824 | 0.91576 | 0.92195 | 0.91824 | 0.91577 | 0.92194 | 0.91823 | 0.91583 | 0.92194 | 0.91798 | 0.91552 | 0.9218
WB-Wide Bay | M042_Meadowvale-Gooburrum 66 kV | Rating (A) | 111 | 146 | 119 | 111 | 146 | 119 | 111 | 146 | 119 | 111 | 146 | 119 | 111 | 146 | 119
WB-Wide Bay | M042_Meadowvale-Gooburrum 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB-Wide Bay | M042_Meadowvale-Gooburrum 66 kV | Min Voltage at Constrained Conductor | 63.4886 | 62.8682 | 64.6052 | 63.2629 | 62.7001 | 64.7124 | 63.2729 | 62.7339 | 64.654 | 63.2454 | 62.8693 | 64.6474 | 63.1227 | 62.7449 | 64.6025
WB-Wide Bay | M042_Meadowvale-Gooburrum 66 kV | Contingency Outage | M049_ISIS - Gayndah 66 kV | 786_Gin Gin - Bundaberg 132 kV | M027_ISIS - Childers 66 kV | 7187_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 6302_Bundaberg Central - WEBU 66 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV
WB-Wide Bay | M046_Tarong-Caboonbah 66 kV | % of Rated A | 16.86% | 10.32% | 6.175% | 16.86% | 10.32% | 6.175% | 16.86% | 10.32% | 6.174% | 16.86% | 10.32% | 6.174% | 16.86% | 10.32% | 6.175%
WB-Wide Bay | M046_Tarong-Caboonbah 66 kV | Limiting Line Name | TR_LINE 9243_1 | TR_LINE 9243_1 | TR_LINE 168863_1 | TR_LINE 9243_1 | TR_LINE 9243_1 | TR_LINE 168863_1 | TR_LINE 9243_1 | TR_LINE 9243_1 | TR_LINE 168863_1 | TR_LINE 9243_1 | TR_LINE 9243_1 | TR_LINE 168863_1 | TR_LINE 9243_1 | TR_LINE 9243_1 | TR_LINE 168863_1
WB-Wide Bay | M046_Tarong-Caboonbah 66 kV | Loading (A) | 41.9749 | 39.4142 | 22.847 | 41.9729 | 39.4098 | 22.8474 | 41.9705 | 39.4069 | 22.8453 | 41.9709 | 39.4076 | 22.8454 | 41.9759 | 39.4125 | 22.8465
WB-Wide Bay | M046_Tarong-Caboonbah 66 kV | Loading (MVA) | 4.9224 | 4.6248 | 2.6996 | 4.9223 | 4.6247 | 2.6996 | 4.9223 | 4.6247 | 2.6995 | 4.9223 | 4.6247 | 2.6995 | 4.9224 | 4.6248 | 2.6996
WB-Wide Bay | M046_Tarong-Caboonbah 66 kV | Loading (MW) | 4.5128 | 4.2545 | 2.5668 | 4.5128 | 4.2545 | 2.5668 | 4.5128 | 4.2544 | 2.5668 | 4.5128 | 4.2544 | 2.5668 | 4.5128 | 4.2545 | 2.5668
WB-Wide Bay | M046_Tarong-Caboonbah 66 kV | Power Factor | 0.91679 | 0.91992 | 0.95082 | 0.9168 | 0.91993 | 0.95082 | 0.9168 | 0.91994 | 0.95083 | 0.9168 | 0.91994 | 0.95083 | 0.91679 | 0.91992 | 0.95082
WB-Wide Bay | M046_Tarong-Caboonbah 66 kV | Rating (A) | 249 | 382 | 370 | 249 | 382 | 370 | 249 | 382 | 370 | 249 | 382 | 370 | 249 | 382 | 370
WB-Wide Bay | M046_Tarong-Caboonbah 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB-Wide Bay | M046_Tarong-Caboonbah 66 kV | Min Voltage at Constrained Conductor | 67.7054 | 67.7455 | 68.2189 | 67.7082 | 67.7521 | 68.218 | 67.7114 | 67.7564 | 68.2233 | 67.7109 | 67.7554 | 68.2231 | 67.7038 | 67.7481 | 68.2202
WB-Wide Bay | M046_Tarong-Caboonbah 66 kV | Contingency Outage | 7187_Gin Gin - Bundaberg 132 kV | M001_Tarong-Kingaroy East 66 kV | M001_Tarong-Kingaroy East 66 kV | 7187_Gin Gin - Bundaberg 132 kV | M001_Tarong-Kingaroy East 66 kV | M001_Tarong-Kingaroy East 66 kV | 7187_Gin Gin - Bundaberg 132 kV | M001_Tarong-Kingaroy East 66 kV | M001_Tarong-Kingaroy East 66 kV | 7187_Gin Gin - Bundaberg 132 kV | M001_Tarong-Kingaroy East 66 kV | M001_Tarong-Kingaroy East 66 kV | 7187_Gin Gin - Bundaberg 132 kV | M001_Tarong-Kingaroy East 66 kV | M001_Tarong-Kingaroy East 66 kV
WB-Wide Bay | M049_ISIS - Gayndah 66 kV | % of Rated A | 107.8% | 102.3% | 92.47% | 30.55% | 29.7% | 22.96% | 30.82% | 29.86% | 23.02% | 30.83% | 29.93% | 23.02% | 30.95% | 29.99% | 23.07%
WB-Wide Bay | M049_ISIS - Gayndah 66 kV | Limiting Line Name | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2
WB-Wide Bay | M049_ISIS - Gayndah 66 kV | Loading (A) | 430.1282 | 424.4653 | 342.1529 | 121.8791 | 123.2555 | 84.9688 | 122.9897 | 123.9084 | 85.1824 | 123.0037 | 124.2131 | 85.1777 | 123.4732 | 124.4453 | 85.3685
WB-Wide Bay | M049_ISIS - Gayndah 66 kV | Loading (MVA) | 49.9999 | 49.518 | 39.4071 | 14.1748 | 14.3026 | 9.8925 | 14.2753 | 14.3969 | 9.9432 | 14.2755 | 14.4021 | 9.9432 | 14.3255 | 14.4576 | 9.9624
WB-Wide Bay | M049_ISIS - Gayndah 66 kV | Loading (MW) | 49.2362 | 49.1852 | 38.1382 | 14.1745 | 14.3026 | 9.7827 | 14.2753 | 14.3969 | 9.833 | 14.2755 | 14.4021 | 9.8329 | 14.3254 | 14.4574 | 9.8562
WB-Wide Bay | M049_ISIS - Gayndah 66 kV | Power Factor | 0.98472 | 0.99328 | 0.9678 | 0.99982 | 0.9999 | 0.98889 | 0.99988 | 0.99992 | 0.98891 | 0.99988 | 0.99993 | 0.98891 | 0.99993 | 0.99996 | 0.98934
WB-Wide Bay | M049_ISIS - Gayndah 66 kV | Rating (A) | 399 | 415 | 370 | 399 | 415 | 370 | 399 | 415 | 370 | 399 | 415 | 370 | 399 | 415 | 370
WB-Wide Bay | M049_ISIS - Gayndah 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB-Wide Bay | M049_ISIS - Gayndah 66 kV | Min Voltage at Constrained Conductor | 59.2367 | 60.1878 | 59.5219 | 65.2412 | 65.0516 | 66.1936 | 65.0772 | 65.1229 | 66.3658 | 65.0702 | 64.9731 | 66.3696 | 65.0292 | 65.0931 | 66.3391
WB-Wide Bay | M049_ISIS - Gayndah 66 kV | Contingency Outage | M027_ISIS - Childers 66 kV | M027_ISIS - Childers 66 kV | M027_ISIS - Childers 66 kV | 7315_Aramara 132 kV | 786_Gin Gin - Bundaberg 132 kV | 785_ISIS 132 kV | 6302_Bundaberg Central - WEBU 66 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV | 6302_Bundaberg Central - WEBU 66 kV | M039_Bundaberg-West Bundaberg No 1 66 kV | 786_Gin Gin - Bundaberg 132 kV | M012_Maryborough-Rocky St 66 kV | 786_Gin Gin - Bundaberg 132 kV | 786_Gin Gin - Bundaberg 132 kV
WB-Wide Bay | M051_Tarong Tie 66 kV | % of Rated A | 35.25% | 28.64% | 10.48% | 35.22% | 28.6% | 10.48% | 35.19% | 28.58% | 10.47% | 35.19% | 28.58% | 10.47% | 35.24% | 28.62% | 10.48%
WB-Wide Bay | M051_Tarong Tie 66 kV | Limiting Line Name | TR_LINE 7733_1 | TR_LINE 7733_1 | TR_LINE 7733_1 | TR_LINE 7733_1 | TR_LINE 7733_1 | TR_LINE 7733_1 | TR_LINE 7733_1 | TR_LINE 7733_1 | TR_LINE 7733_1 | TR_LINE 7733_1 | TR_LINE 7733_1 | TR_LINE 7733_1 | TR_LINE 7733_1 | TR_LINE 7733_1 | TR_LINE 7733_1
WB-Wide Bay | M051_Tarong Tie 66 kV | Loading (A) | 37.7138 | 39.5219 | 13.8296 | 37.6815 | 39.4706 | 13.8292 | 37.6535 | 39.4459 | 13.8251 | 37.6539 | 39.4466 | 13.8252 | 37.7078 | 39.4965 | 13.8315
WB-Wide Bay | M051_Tarong Tie 66 kV | Loading (MVA) | 4.0089 | 4.1684 | 1.573 | 4.0088 | 4.1681 | 1.573 | 4.0086 | 4.168 | 1.573 | 4.0086 | 4.168 | 1.573 | 4.0089 | 4.1682 | 1.573
WB-Wide Bay | M051_Tarong Tie 66 kV | Loading (MW) | 3.9036 | 4.0567 | 1.5403 | 3.9035 | 4.0566 | 1.5403 | 3.9034 | 4.0566 | 1.5403 | 3.9034 | 4.0566 | 1.5403 | 3.9035 | 4.0567 | 1.5403
WB-Wide Bay | M051_Tarong Tie 66 kV | Power Factor | 0.97112 | 0.97078 | 0.97794 | 0.97114 | 0.97081 | 0.97794 | 0.97116 | 0.97083 | 0.97795 | 0.97116 | 0.97083 | 0.97795 | 0.97113 | 0.9708 | 0.97794
WB-Wide Bay | M051_Tarong Tie 66 kV | Rating (A) | 107 | 138 | 132 | 107 | 138 | 132 | 107 | 138 | 132 | 107 | 138 | 132 | 107 | 138 | 132
WB-Wide Bay | M051_Tarong Tie 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB-Wide Bay | M051_Tarong Tie 66 kV | Min Voltage at Constrained Conductor | 61.303 | 60.8021 | 65.6697 | 61.3537 | 60.8783 | 65.6715 | 61.3978 | 60.9151 | 65.6904 | 61.3972 | 60.914 | 65.6901 | 61.3124 | 60.8397 | 65.6604
WB-Wide Bay | M051_Tarong Tie 66 kV | Contingency Outage | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV | M002_Tarong-Kingaroy West 66 kV
WB-Wide Bay | SOBU-BARG-1_SOBU-Bargara-1 66 kV | % of Rated A | 21.79% | 19.54% | 10.47% | 21.85% | 19.61% | 10.48% | 21.82% | 19.58% | 10.46% | 21.99% | 19.63% | 10.54% | 22.34% | 19.95% | 10.7%
WB-Wide Bay | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Limiting Line Name | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1
WB-Wide Bay | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Loading (A) | 89.3234 | 123.6992 | 56.4577 | 89.5681 | 124.1039 | 56.4704 | 89.4681 | 123.9289 | 56.395 | 90.1665 | 124.2537 | 56.8096 | 91.5922 | 126.3095 | 57.6482
WB-Wide Bay | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Loading (MVA) | 9.9134 | 13.6538 | 6.4004 | 9.9137 | 13.6547 | 6.4004 | 9.9136 | 13.6543 | 6.4004 | 9.985 | 13.7516 | 6.4463 | 10.1278 | 13.9492 | 6.5381
WB-Wide Bay | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Loading (MW) | 9.8257 | 13.509 | 6.3539 | 9.8258 | 13.5092 | 6.3539 | 9.8258 | 13.5091 | 6.3538 | 9.8961 | 13.6055 | 6.3993 | 10.0368 | 13.7991 | 6.4902
WB-Wide Bay | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Power Factor | 0.99109 | 0.98939 | 0.99259 | 0.99107 | 0.98934 | 0.99259 | 0.99108 | 0.98936 | 0.99259 | 0.99104 | 0.98938 | 0.99257 | 0.99096 | 0.98925 | 0.99253
WB-Wide Bay | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Rating (A) | 410 | 633 | 539 | 410 | 633 | 539 | 410 | 633 | 539 | 410 | 633 | 539 | 410 | 633 | 539
WB-Wide Bay | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB-Wide Bay | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Min Voltage at Constrained Conductor | 64.066 | 63.7055 | 65.4524 | 63.8931 | 63.5014 | 65.4377 | 63.9637 | 63.5895 | 65.5245 | 63.9249 | 63.8752 | 65.5127 | 63.8293 | 63.7375 | 65.4792
WB-Wide Bay | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Contingency Outage | 6302_Bundaberg Central - WEBU 66 kV | M036_Bundaberg-South Bundaberg 66 kV | M041_West Bundaberg-Meadowvale 66 kV | 6302_Bundaberg Central - WEBU 66 kV | M036_Bundaberg-South Bundaberg 66 kV | 6205_East Bundaberg-BUCE 66 kV | 6302_Bundaberg Central - WEBU 66 kV | M036_Bundaberg-South Bundaberg 66 kV | 786_Gin Gin - Bundaberg 132 kV | 6302_Bundaberg Central - WEBU 66 kV | M036_Bundaberg-South Bundaberg 66 kV | 786_Gin Gin - Bundaberg 132 kV | 6302_Bundaberg Central - WEBU 66 kV | M036_Bundaberg-South Bundaberg 66 kV | 786_Gin Gin - Bundaberg 132 kV
WB-Wide Bay | T014_Maryborough-Pialba Tee Howard 66 kV | % of Rated A | 51.47% | 38.14% | 30.13% | 50.85% | 37.21% | 29.49% | 49.87% | 36.95% | 29.26% | 49.89% | 36.91% | 29.27% | 50.06% | 37.02% | 29.56%
WB-Wide Bay | T014_Maryborough-Pialba Tee Howard 66 kV | Limiting Line Name | TR_LINE 224569_1 | TR_LINE 224569_1 | TR_LINE 224569_1 | TR_LINE 224569_1 | TR_LINE 224569_1 | TR_LINE 224569_1 | TR_LINE 224569_1 | TR_LINE 224569_1 | TR_LINE 224569_1 | TR_LINE 224569_1 | TR_LINE 224569_1 | TR_LINE 224569_1 | TR_LINE 224569_1 | TR_LINE 224569_1 | TR_LINE 224569_1
WB-Wide Bay | T014_Maryborough-Pialba Tee Howard 66 kV | Loading (A) | 311.416 | 254.7779 | 164.8091 | 307.6383 | 248.5483 | 161.2833 | 301.7138 | 246.8537 | 160.0759 | 301.8066 | 246.5601 | 160.1014 | 302.8414 | 247.293 | 161.6882
WB-Wide Bay | T014_Maryborough-Pialba Tee Howard 66 kV | Loading (MVA) | 36.3133 | 29.6883 | 19.4197 | 35.5642 | 29.1327 | 19.0864 | 35.0965 | 28.7257 | 18.8306 | 35.0961 | 28.7285 | 18.8296 | 35.1812 | 28.7944 | 19.0416
WB-Wide Bay | T014_Maryborough-Pialba Tee Howard 66 kV | Loading (MW) | 36.2049 | 29.4297 | 18.5424 | 35.4563 | 28.8438 | 18.1568 | 34.963 | 28.4388 | 17.909 | 34.9632 | 28.4383 | 17.909 | 35.0561 | 28.5069 | 17.9675
WB-Wide Bay | T014_Maryborough-Pialba Tee Howard 66 kV | Power Factor | 0.99666 | 0.99083 | 0.95433 | 0.99661 | 0.98961 | 0.95082 | 0.99581 | 0.98953 | 0.95058 | 0.99583 | 0.98942 | 0.95063 | 0.99607 | 0.98954 | 0.94306
WB-Wide Bay | T014_Maryborough-Pialba Tee Howard 66 kV | Rating (A) | 605 | 668 | 547 | 605 | 668 | 547 | 605 | 668 | 547 | 605 | 668 | 547 | 605 | 668 | 547
WB-Wide Bay | T014_Maryborough-Pialba Tee Howard 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
WB-Wide Bay | T014_Maryborough-Pialba Tee Howard 66 kV | Min Voltage at Constrained Conductor | 67.2265 | 67.2126 | 68.02 | 66.6486 | 67.6123 | 68.3164 | 67.0691 | 67.1255 | 67.9095 | 67.0477 | 67.2123 | 67.895 | 66.9793 | 67.1663 | 67.99
WB-Wide Bay | T014_Maryborough-Pialba Tee Howard 66 kV | Contingency Outage | M020_Maryborough-Torquay 66 kV | M020_Maryborough-Torquay 66 kV | M020_Maryborough-Torquay 66 kV | M020_Maryborough-Torquay 66 kV | M020_Maryborough-Torquay 66 kV | M020_Maryborough-Torquay 66 kV | M020_Maryborough-Torquay 66 kV | M020_Maryborough-Torquay 66 kV | M020_Maryborough-Torquay 66 kV | M020_Maryborough-Torquay 66 kV | M020_Maryborough-Torquay 66 kV | M020_Maryborough-Torquay 66 kV | M020_Maryborough-Torquay 66 kV | M020_Maryborough-Torquay 66 kV | M020_Maryborough-Torquay 66 kV
NQ-Mount Isa | 7018_Mica Creek C - Chumvale 220 kV | % of Rated A | 23.04% | 19.71% | 20.7% | 23.04% | 19.71% | 20.7% | 22.97% | 19.65% | 20.67% | 22.97% | 19.65% | 20.67% | 23.15% | 19.8% | 20.81%
NQ-Mount Isa | 7018_Mica Creek C - Chumvale 220 kV | Limiting Line Name | TR_LINE 174437_1 | TR_LINE 174437_1 | TR_LINE 174437_1 | TR_LINE 174437_1 | TR_LINE 174437_1 | TR_LINE 174437_1 | TR_LINE 174437_1 | TR_LINE 174437_1 | TR_LINE 174437_1 | TR_LINE 174437_1 | TR_LINE 174437_1 | TR_LINE 174437_1 | TR_LINE 174437_1 | TR_LINE 174437_1 | TR_LINE 174437_1
NQ-Mount Isa | 7018_Mica Creek C - Chumvale 220 kV | Loading (A) | 196.9974 | 183.3082 | 180.4776 | 196.9896 | 183.3008 | 180.4745 | 196.4185 | 182.7127 | 180.2188 | 196.421 | 182.7152 | 180.2198 | 197.9646 | 184.1274 | 181.4465
NQ-Mount Isa | 7018_Mica Creek C - Chumvale 220 kV | Loading (MVA) | 74.461 | 70.0592 | 69.055 | 74.4606 | 70.0589 | 69.0549 | 74.2672 | 69.8549 | 68.9653 | 74.2673 | 69.855 | 68.9654 | 74.4334 | 70.0138 | 69.071
NQ-Mount Isa | 7018_Mica Creek C - Chumvale 220 kV | Loading (MW) | 72.2666 | 68.3548 | 67.2237 | 72.2665 | 68.3548 | 67.2237 | 72.0808 | 68.1582 | 67.1365 | 72.0808 | 68.1582 | 67.1365 | 72.1824 | 68.2604 | 67.1869
NQ-Mount Isa | 7018_Mica Creek C - Chumvale 220 kV | Power Factor | 0.96941 | 0.97464 | 0.97246 | 0.96941 | 0.97464 | 0.97247 | 0.96944 | 0.97468 | 0.97247 | 0.96944 | 0.97468 | 0.97247 | 0.96862 | 0.97391 | 0.9717
NQ-Mount Isa | 7018_Mica Creek C - Chumvale 220 kV | Rating (A) | 855 | 930 | 872 | 855 | 930 | 872 | 855 | 930 | 872 | 855 | 930 | 872 | 855 | 930 | 872
NQ-Mount Isa | 7018_Mica Creek C - Chumvale 220 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Mount Isa | 7018_Mica Creek C - Chumvale 220 kV | Min Voltage at Constrained Conductor | 218.2266 | 220.6596 | 220.908 | 218.234 | 220.6673 | 220.9112 | 218.3002 | 220.733 | 220.9377 | 218.2977 | 220.7305 | 220.9367 | 217.0798 | 219.5354 | 219.7791
NQ-Mount Isa | 7018_Mica Creek C - Chumvale 220 kV | Contingency Outage | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV
NQ-Mount Isa | CH-CC-1_Chumvale-Cloncurry 66 kV | % of Rated A | 35.54% | 33.53% | 15.74% | 35.54% | 33.53% | 15.74% | 34.51% | 32.65% | 15.32% | 34.51% | 32.65% | 15.32% | 35.21% | 33.23% | 15.55%
NQ-Mount Isa | CH-CC-1_Chumvale-Cloncurry 66 kV | Limiting Line Name | TR_LINE 181845_1 | TR_LINE 181845_1 | TR_LINE 181845_1 | TR_LINE 181845_1 | TR_LINE 181845_1 | TR_LINE 181845_1 | TR_LINE 181845_1 | TR_LINE 181845_1 | TR_LINE 181845_1 | TR_LINE 181845_1 | TR_LINE 181845_1 | TR_LINE 181845_1 | TR_LINE 181845_1 | TR_LINE 181845_1 | TR_LINE 181845_1
NQ-Mount Isa | CH-CC-1_Chumvale-Cloncurry 66 kV | Loading (A) | 57.9344 | 61.0229 | 27.0732 | 57.9328 | 61.0207 | 27.073 | 56.249 | 59.4177 | 26.344 | 56.2495 | 59.4183 | 26.3441 | 57.3856 | 60.4717 | 26.7493
NQ-Mount Isa | CH-CC-1_Chumvale-Cloncurry 66 kV | Loading (MVA) | 6.5402 | 6.9235 | 3.0816 | 6.5402 | 6.9235 | 3.0816 | 6.3533 | 6.726 | 2.9942 | 6.3533 | 6.726 | 2.9942 | 6.4524 | 6.8262 | 3.0415
NQ-Mount Isa | CH-CC-1_Chumvale-Cloncurry 66 kV | Loading (MW) | 6.4608 | 6.8402 | 3.0562 | 6.4608 | 6.8402 | 3.0562 | 6.2776 | 6.6463 | 2.9698 | 6.2776 | 6.6463 | 2.9698 | 6.3733 | 6.7434 | 3.0163
NQ-Mount Isa | CH-CC-1_Chumvale-Cloncurry 66 kV | Power Factor | 0.98773 | 0.98786 | 0.99152 | 0.98773 | 0.98786 | 0.99152 | 0.98795 | 0.98804 | 0.99164 | 0.98795 | 0.98804 | 0.99164 | 0.98761 | 0.98776 | 0.99146
NQ-Mount Isa | CH-CC-1_Chumvale-Cloncurry 66 kV | Rating (A) | 163 | 182 | 172 | 163 | 182 | 172 | 163 | 182 | 172 | 163 | 182 | 172 | 163 | 182 | 172
NQ-Mount Isa | CH-CC-1_Chumvale-Cloncurry 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Mount Isa | CH-CC-1_Chumvale-Cloncurry 66 kV | Min Voltage at Constrained Conductor | 65.1518 | 65.4773 | 65.7158 | 65.1535 | 65.4796 | 65.7165 | 65.188 | 65.3287 | 65.62 | 65.1874 | 65.3281 | 65.6199 | 64.8922 | 65.1458 | 65.6479
NQ-Mount Isa | CH-CC-1_Chumvale-Cloncurry 66 kV | Contingency Outage | MI-GP-1_Mica Creek C-Gunpowder 1 220 kV | MICC-MICB No 2 132 kV | 7431_Ernest Henry 220 kV | MI-GP-1_Mica Creek C-Gunpowder 1 220 kV | MICC-MICB No 2 132 kV | 7431_Ernest Henry 220 kV | MI-GP-1_Mica Creek C-Gunpowder 1 220 kV | GP-CM-1_Gunpowder-Century No 1 220 kV | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | MI-GP-1_Mica Creek C-Gunpowder 1 220 kV | GP-CM-1_Gunpowder-Century No 1 220 kV | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | MI-GP-1_Mica Creek C-Gunpowder 1 220 kV | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV
NQ-Mount Isa | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | % of Rated A | 14.39% | 8.786% | 8.642% | 14.4% | 8.787% | 8.642% | 14.4% | 8.788% | 8.642% | 14.4% | 8.787% | 8.642% | 14.34% | 8.752% | 8.485%
NQ-Mount Isa | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Limiting Line Name | TR_LINE 234732_1 | TR_LINE 234732_1 | TR_LINE 234732_1 | TR_LINE 234732_1 | TR_LINE 234732_1 | TR_LINE 234732_1 | TR_LINE 234732_1 | TR_LINE 234732_1 | TR_LINE 234732_1 | TR_LINE 234732_1 | TR_LINE 234732_1 | TR_LINE 234732_1 | TR_LINE 234732_1 | TR_LINE 234732_1 | TR_LINE 234732_1
NQ-Mount Isa | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Loading (A) | 11.9472 | 11.9494 | 12.1848 | 11.9482 | 11.9504 | 12.1853 | 11.9489 | 11.9512 | 12.1856 | 11.9486 | 11.9508 | 12.1854 | 11.8999 | 11.9023 | 11.9645
NQ-Mount Isa | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Loading (MVA) | 1.4346 | 1.4351 | 1.4904 | 1.4348 | 1.4353 | 1.4905 | 1.435 | 1.4355 | 1.4905 | 1.4349 | 1.4354 | 1.4905 | 1.4236 | 1.4242 | 1.4386
NQ-Mount Isa | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Loading (MW) | 0.092924 | 0.092927 | 0.093239 | 0.092925 | 0.092928 | 0.09324 | 0.092926 | 0.092929 | 0.09324 | 0.092926 | 0.092929 | 0.09324 | 0.092864 | 0.092867 | 0.092946
NQ-Mount Isa | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Power Factor | 0.064774 | 0.064753 | 0.062561 | 0.064764 | 0.064743 | 0.062557 | 0.064758 | 0.064736 | 0.062554 | 0.064761 | 0.064739 | 0.062556 | 0.06523 | 0.065207 | 0.064608
NQ-Mount Isa | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Rating (A) | 83 | 136 | 141 | 83 | 136 | 141 | 83 | 136 | 141 | 83 | 136 | 141 | 83 | 136 | 141
NQ-Mount Isa | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Mount Isa | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Min Voltage at Constrained Conductor | 69.3268 | 69.3383 | 70.6172 | 69.3322 | 69.3441 | 70.6198 | 69.3359 | 69.3482 | 70.6214 | 69.3341 | 69.3463 | 70.6205 | 69.0708 | 69.0838 | 69.4206
NQ-Mount Isa | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Contingency Outage | 7431_Ernest Henry 220 kV | 7432_Dugald River 220 kV | 7431_Ernest Henry 220 kV | 7431_Ernest Henry 220 kV | 7432_Dugald River 220 kV | 7431_Ernest Henry 220 kV | 7431_Ernest Henry 220 kV | 7432_Dugald River 220 kV | 7431_Ernest Henry 220 kV | 7431_Ernest Henry 220 kV | 7432_Dugald River 220 kV | 7431_Ernest Henry 220 kV | 7431_Ernest Henry 220 kV | 7432_Dugald River 220 kV | 7431_Ernest Henry 220 kV
NQ-Mount Isa | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | % of Rated A | 17.59% | 14.44% | 7.428% | 17.43% | 14.3% | 7.36% | 17.37% | 14.26% | 7.337% | 17.43% | 14.3% | 7.36% | 17.71% | 14.54% | 7.479%
NQ-Mount Isa | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Limiting Line Name | TR_LINE 32596_1 | TR_LINE 32596_1 | TR_LINE 210013_1 | TR_LINE 32596_1 | TR_LINE 32596_1 | TR_LINE 210013_1 | TR_LINE 32596_1 | TR_LINE 32596_1 | TR_LINE 210013_1 | TR_LINE 32596_1 | TR_LINE 32596_1 | TR_LINE 210013_1 | TR_LINE 32596_1 | TR_LINE 32596_1 | TR_LINE 210013_1
NQ-Mount Isa | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Loading (A) | 67.5408 | 70.8805 | 34.3161 | 66.9213 | 70.23 | 34.0019 | 66.7112 | 70.0095 | 33.8964 | 66.9177 | 70.2263 | 34.0012 | 68.008 | 71.3693 | 34.5521
NQ-Mount Isa | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Loading (MVA) | 15.7688 | 16.5782 | 8.0466 | 15.6248 | 16.4267 | 7.973 | 15.5767 | 16.3762 | 7.9485 | 15.6248 | 16.4267 | 7.973 | 15.8174 | 16.6294 | 8.0715
NQ-Mount Isa | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Loading (MW) | 15.6208 | 16.4196 | 8.0262 | 15.4787 | 16.2702 | 7.9531 | 15.4313 | 16.2204 | 7.9288 | 15.4787 | 16.2702 | 7.9531 | 15.6683 | 16.4696 | 8.0506
NQ-Mount Isa | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Power Factor | 0.99061 | 0.99043 | 0.99744 | 0.99065 | 0.99047 | 0.99749 | 0.99066 | 0.99048 | 0.9975 | 0.99065 | 0.99047 | 0.99749 | 0.99057 | 0.99039 | 0.99739
NQ-Mount Isa | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Rating (A) | 384 | 491 | 462 | 384 | 491 | 462 | 384 | 491 | 462 | 384 | 491 | 462 | 384 | 491 | 462
NQ-Mount Isa | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Mount Isa | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Min Voltage at Constrained Conductor | 134.7947 | 135.0363 | 135.3802 | 134.7997 | 135.0416 | 135.3818 | 134.8085 | 135.0504 | 135.3851 | 134.8069 | 135.0486 | 135.3846 | 134.2814 | 134.5251 | 134.8714
NQ-Mount Isa | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Contingency Outage | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV
NQ-Mount Isa | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | % of Rated A | 24.16% | 20.51% | 10.34% | 23.93% | 20.32% | 10.25% | 23.86% | 20.26% | 10.22% | 23.93% | 20.32% | 10.25% | 24.32% | 20.65% | 10.41%
NQ-Mount Isa | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Limiting Line Name | TR_LINE 174420_1 | TR_LINE 174420_1 | TR_LINE 174422_1 | TR_LINE 174420_1 | TR_LINE 174420_1 | TR_LINE 174422_1 | TR_LINE 174420_1 | TR_LINE 174420_1 | TR_LINE 174422_1 | TR_LINE 174420_1 | TR_LINE 174420_1 | TR_LINE 174422_1 | TR_LINE 174420_1 | TR_LINE 174420_1 | TR_LINE 174422_1
NQ-Mount Isa | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Loading (A) | 67.3947 | 70.7586 | 34.7465 | 66.7767 | 70.1094 | 34.4393 | 66.5681 | 69.8895 | 34.3362 | 66.7741 | 70.1058 | 34.4386 | 67.8558 | 71.2393 | 34.9756
NQ-Mount Isa | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Loading (MVA) | 15.7684 | 16.5779 | 8.1478 | 15.6243 | 16.4264 | 8.0758 | 15.5763 | 16.3758 | 8.0518 | 15.6243 | 16.4263 | 8.0758 | 15.817 | 16.6289 | 8.1707
NQ-Mount Isa | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Loading (MW) | 15.6207 | 16.4197 | 8.1216 | 15.4786 | 16.2702 | 8.0486 | 15.4312 | 16.2203 | 8.0243 | 15.4786 | 16.2701 | 8.0486 | 15.6682 | 16.4695 | 8.146
NQ-Mount Isa | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Power Factor | 0.99063 | 0.99044 | 0.99679 | 0.99066 | 0.99048 | 0.99663 | 0.99067 | 0.99049 | 0.99657 | 0.99066 | 0.99048 | 0.99663 | 0.99059 | 0.9904 | 0.99698
NQ-Mount Isa | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Rating (A) | 279 | 345 | 336 | 279 | 345 | 336 | 279 | 345 | 336 | 279 | 345 | 336 | 279 | 345 | 336
NQ-Mount Isa | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Mount Isa | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Min Voltage at Constrained Conductor | 135.0827 | 135.2665 | 135.3706 | 135.0875 | 135.2716 | 135.3723 | 135.0943 | 135.2788 | 135.3758 | 135.0927 | 135.2771 | 135.3752 | 134.5784 | 134.7668 | 134.8617
NQ-Mount Isa | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Contingency Outage | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | MICC-MICB No 2 132 kV | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | MICC-MICB No 2 132 kV | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | MICC-MICB No 2 132 kV | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | MICC-MICB No 2 132 kV | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | MICC-MICB No 2 132 kV
NQ-Mount Isa | MICC-MICB No 1 132 kV | % of Rated A | 93.67% | 64.74% | 63.92% | 93.67% | 64.74% | 63.92% | 93.49% | 64.61% | 63.86% | 93.49% | 64.61% | 63.86% | 94.06% | 64.97% | 64.18%
NQ-Mount Isa | MICC-MICB No 1 132 kV | Limiting Line Name | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1
NQ-Mount Isa | MICC-MICB No 1 132 kV | Loading (A) | 488.9668 | 465.4883 | 460.2164 | 488.9513 | 465.4744 | 460.2107 | 488.0344 | 464.5474 | 459.8029 | 488.0396 | 464.552 | 459.8048 | 490.9965 | 467.1502 | 462.1044
NQ-Mount Isa | MICC-MICB No 1 132 kV | Loading (MVA) | 114.3074 | 109.0218 | 107.9221 | 114.3065 | 109.0212 | 107.9219 | 114.0991 | 108.8107 | 107.8289 | 114.0994 | 108.8109 | 107.829 | 114.3465 | 108.9985 | 107.9576
NQ-Mount Isa | MICC-MICB No 1 132 kV | Loading (MW) | 113.5989 | 108.8238 | 107.7259 | 113.5988 | 108.8237 | 107.7258 | 113.4078 | 108.6222 | 107.6365 | 113.4079 | 108.6222 | 107.6365 | 113.5281 | 108.7411 | 107.7012
NQ-Mount Isa | MICC-MICB No 1 132 kV | Power Factor | 0.9938 | 0.99818 | 0.99818 | 0.99381 | 0.99819 | 0.99818 | 0.99394 | 0.99827 | 0.99822 | 0.99394 | 0.99827 | 0.99822 | 0.99284 | 0.99764 | 0.99762
NQ-Mount Isa | MICC-MICB No 1 132 kV | Rating (A) | 522 | 719 | 720 | 522 | 719 | 720 | 522 | 719 | 720 | 522 | 719 | 720 | 522 | 719 | 720
NQ-Mount Isa | MICC-MICB No 1 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Mount Isa | MICC-MICB No 1 132 kV | Min Voltage at Constrained Conductor | 134.9541 | 135.2089 | 135.3786 | 134.9573 | 135.2123 | 135.38 | 134.9656 | 135.2206 | 135.3833 | 134.9645 | 135.2195 | 135.3829 | 134.4416 | 134.6987 | 134.8693
NQ-Mount Isa | MICC-MICB No 1 132 kV | Contingency Outage | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV | MICC-MICB No 2 132 kV
NQ-Mount Isa | MICC-MICB No 2 132 kV | % of Rated A | 93.66% | 64.74% | 63.92% | 93.66% | 64.74% | 63.91% | 93.48% | 64.61% | 63.86% | 93.49% | 64.61% | 63.86% | 94.05% | 64.97% | 64.18%
NQ-Mount Isa | MICC-MICB No 2 132 kV | Limiting Line Name | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1
NQ-Mount Isa | MICC-MICB No 2 132 kV | Loading (A) | 488.9198 | 465.4621 | 460.1909 | 488.9043 | 465.4481 | 460.1852 | 487.9881 | 464.5217 | 459.7775 | 487.9932 | 464.5263 | 459.7794 | 490.9456 | 467.1212 | 462.076
NQ-Mount Isa | MICC-MICB No 2 132 kV | Loading (MVA) | 114.2988 | 109.0174 | 107.9179 | 114.2979 | 109.0169 | 107.9177 | 114.0906 | 108.8065 | 107.8247 | 114.0909 | 108.8066 | 107.8248 | 114.3371 | 108.9936 | 107.9528
NQ-Mount Isa | MICC-MICB No 2 132 kV | Loading (MW) | 113.5975 | 108.8226 | 107.7247 | 113.5973 | 108.8225 | 107.7247 | 113.4064 | 108.621 | 107.6354 | 113.4064 | 108.6211 | 107.6354 | 113.5266 | 108.7399 | 107.7
NQ-Mount Isa | MICC-MICB No 2 132 kV | Power Factor | 0.99386 | 0.99821 | 0.99821 | 0.99387 | 0.99822 | 0.99821 | 0.994 | 0.9983 | 0.99824 | 0.994 | 0.99829 | 0.99824 | 0.99291 | 0.99767 | 0.99766
NQ-Mount Isa | MICC-MICB No 2 132 kV | Rating (A) | 522 | 719 | 720 | 522 | 719 | 720 | 522 | 719 | 720 | 522 | 719 | 720 | 522 | 719 | 720
NQ-Mount Isa | MICC-MICB No 2 132 kV | Time | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00 | 16:30:00 | 19:00:00 | 05:30:00
NQ-Mount Isa | MICC-MICB No 2 132 kV | Min Voltage at Constrained Conductor | 134.9581 | 135.2122 | 135.3817 | 134.9614 | 135.2156 | 135.3831 | 134.9696 | 135.2238 | 135.3865 | 134.9685 | 135.2227 | 135.386 | 134.4458 | 134.7021 | 134.8726
NQ-Mount Isa | MICC-MICB No 2 132 kV | Contingency Outage | MICC-MICB No 1 132 kV | MICC-MICB No 1 132 kV | MICC-MICB No 1 132 kV | MICC-MICB No 1 132 kV | MICC-MICB No 1 132 kV | MICC-MICB No 1 132 kV | MICC-MICB No 1 132 kV | MICC-MICB No 1 132 kV | MICC-MICB No 1 132 kV | MICC-MICB No 1 132 kV | MICC-MICB No 1 132 kV | MICC-MICB No 1 132 kV | MICC-MICB No 1 132 kV | MICC-MICB No 1 132 kV | MICC-MICB No 1 132 kV