## Disclaimer
Substations Forecast
(Ergon Energy Distribution Annual Planning Report 2020)
This workbook forms part of the Ergon Energy Distribution Annual Planning Report 2020 (DAPR) and should be read in conjunction with the report document.
Readers are encouraged to take into account the details and content portrayed in the ‘Introduction & Notes’ section of this workbook when reviewing the associated data.
Disclaimer
Ergon Energy’s Distribution Annual Planning Report (DAPR) is prepared and made available solely for information purposes. While care was taken in the preparation of the information in the DAPR, and it is provided in good faith, Ergon Energy accepts no responsibility or liability (including without limitation, liability to any person by reason of negligence or negligent mis-statement) for any loss or damage that may be incurred by any person acting in reliance on this information or assumptions drawn from it, except to the extent that liability under any applicable Queensland or Commonwealth of Australia statute cannot be excluded.
It contains assumptions regarding, among other things, economic growth and load forecasts which may or may not prove to be correct. The forecasts included in the DAPR involve subjective judgements and analysis which are subject to significant uncertainties and contingencies, many of which are out of the control of Ergon Energy. Ergon Energy makes no representation or warranty as to the accuracy, reliability, completeness or suitability for any particular purpose of the information in this document. All information should be independently investigated, reviewed, analysed and verified, and must not be relied upon in connection with any investment proposal or decision. The information contained in the DAPR is subject to annual review. Ergon Energy is obligated to publish future editions by 31st December, in accordance with the National Electricity Rules.
All financials presented in the DAPR or within this document are correct at the time of writing and represent the existing organisational accounting treatment, which may be subject to change. Energy Queensland is finalising the alignment of its Cost Allocation Methodology between Ergon Energy and Energex, potentially impacting the treatment of some Capital and Operational Project costs.
Forecasted data is subject to ongoing variation due to COVID 19 impacts.

## Introduction & Notes
Substations Forecast (Ergon Energy Distribution Annual Planning Report 2020)
This workbook provides 5 year forecast capacity and loading information for each Ergon Energy owned Substation in the Ergon Energy network.
This workbook forms part of the Ergon Energy Distribution Annual Planning Report 2020 (DAPR) and should be read in conjunction with the report document.
Forecasted data is subject to ongoing variation due to COVID 19 impacts.
Zone Substations
A zone substation refers to an Ergon Energy owned substation that converts energy from transmission or subtransmission voltages to distribution voltages.
Bulk Supply Substations and Transmission Connection Points
A Bulk Supply Substation refers to an Ergon Energy owned substations that converts energy from transmission voltage levels to sub-transmission voltage levels.
Some Ergon Owned Bulk Supply Substations contain asset boundaries with the Transmission Network Service Provider and therefore are also the Transmission Connection Point. Demand forecasts for other TCPs are reported in a separate workbook.
Load Forecasts
The summer and winter load forecasts are provided in the row named 10 PoE Load.
(Note: The 50 PoE Load is used to address Safety Net requirements.)
"Hours PA > 95% Peak Load" gives the hours per year that load is above 95% of the peak load.
· 'zero' values occur for small substations with no metering installed to provide this data
· 'N/A' values occur for new substation which does not yet have history on this data to be able to determine future forecasts.
The peak load given is a compensated load, which is the load with reactive compensation in service.
Capacity
Substation capacity is based on transformer ratings only.
NCC (Normal Cyclic Capacity) Rating is the total capacity of the substation with all transformers in service. Where the NCC rating is not available the manufacturer's transformer profile is used.
ECC (Emergency Cyclic Capacity) Rating is the firm delivery capacities with the largest transformer out of service.
Transfer Capability
The load transfer capabilities of each substation are broken up into the following categories:
· Auto Trans Avail: Transfers conducted automatically by a distribution management system
· Remote Trans Avail: Transfers conducted by a Network Operator located in one of the Operational Control Centres
· Manual Trans Avail: Transfers which require manual switching by a field crew
· Mobile Plant Avail: Supply which can be restored by the use of a mobile substation, HV injection generation or distributed low voltage generation.
The transfer capabilities align with the various time requirements to have certain load levels restored under Ergon Energy’s Safety Net requirements.
Load Shedding
The load shedding rows are defined as follows:
· Shed (30min): Loads to large customers which can be disconnected by remote operation of switchgear
· Shed (4Hour): Loads to large customers which need manual switching by field crews to disconnect them from the network.
Security
The load at risk assessments (LARn and LARc) are assessments of the potential load at risk in a substation. If there are values in the LARn or LARc columns the “Meets Security Standard” row will change to “No” for those columns.
The LARn is calculated by comparing the 10 PoE with the NCC rating. If the 10 PoE load is greater than the NCC rating then there is potentially load at risk under normal operating conditions for the substation.
If there is a value of LARc then Ergon Energy may potentially fail to meet its obligations in the occurrence of a Safety Net event. The LARc value is determined as follows: The Raw LAR is arrived at by comparing the 50 PoE load with the ECC rating. If the 50 PoE load is the greater than the ECC rating then contingencies need to be in place to meet Ergon Energy’s Safety Net obligations. The transfer capabilities, mobile plant capacities and load shed allowances are then taken from the Raw LAR value to give the LARc value.
For the implementation of Safety Net Ergon Energy operates two Substation categories
· Regional Centres are towns/cities with a population of more than 6000 people
· Rural/Remote is used for substations servicing all other areas of the state.
The time required to restore certain load levels for each category is less for the Regional Centre category.
Under Ergon Energy’s Safety Net large customers are exempt from reporting. While all efforts are made to restore supply to them, load shedding can be used to disconnect these customers from the network if required in a contingency event.
Embedded Generation
The embedded generation reported for the substation is the nameplate rating of embedded generation connected to the low voltage side of the substation.

## INDEX
|  | NCC Rating (MVA) | [16 empty] | <-- Dropdown List of Variable Selection
|  | SUMMER |  |  |  |  | WINTER
Substation List | Substation Type | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2020 | 2021 | 2022 | 2023 | 2024 | Sub Brief | Substation | Summer Range Dates | Winter Range Dates | Summer NCC Rating (MVA) Range Results | Winter NCC Rating (MVA) Range Results | Title
Agnes Water (66/22kV) | Zone Substation | 48 | 48 | 48 | 48 | 48 | 55.6 | 55.6 | 55.6 | 55.6 | 55.6 | Agnes Water | AGWA | AGWA!$J$25:$T$25 | AGWA!$U$25:$AQ$25 | AGWA!$J$26:$T$26 | AGWA!$U$26:$AQ$26 | NCC Rating (MVA)
Aitkenvale (66/11kV) | Zone Substation | 61.6 | 61.6 | 61.6 | 61.6 | 61.6 | 64.7 | 64.7 | 64.7 | 64.7 | 64.7 | Aitkenvale | AITK | AITK!$J$25:$T$25 | AITK!$U$25:$AQ$25 | AITK!$J$26:$T$26 | AITK!$U$26:$AQ$26 | Contracted non-network (MVA)
Alan Sherriff (132/11kV) | Zone Substation | 70 | 70 | 70 | 70 | 70 | 73.5 | 73.5 | 73.5 | 73.5 | 73.5 | Alan Sherriff | ALSH | ALSH!$J$25:$T$25 | ALSH!$U$25:$AQ$25 | ALSH!$J$26:$T$26 | ALSH!$U$26:$AQ$26 | 10 PoE Load (MVA)
Alfred Street (33/11kV) | Zone Substation | 90.7 | 90.7 | 90.7 | 90.7 | 90.7 | 93.7 | 93.7 | 93.7 | 93.7 | 93.7 | Alfred Street | ALST | ALST!$J$25:$T$25 | ALST!$U$25:$AQ$25 | ALST!$J$26:$T$26 | ALST!$U$26:$AQ$26 | LARn (MVA)
Alligator Creek BSP (132/33kV) | Bulk Supply | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | Alligator Creek BSP | T065 | 'T065'!$I$23:$S$23 | 'T065'!$T$23:$AQ$23 | 'T065'!$I$24:$S$24 | 'T065'!$T$24:$AQ$24 | LARn (MW)
Allora (33/11kV) | Zone Substation | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.9 | 7.9 | 7.9 | 7.9 | 7.9 | Allora | ALLO | ALLO!$J$25:$T$25 | ALLO!$U$25:$AQ$25 | ALLO!$J$26:$T$26 | ALLO!$U$26:$AQ$26 | Power Factor at Peak Load
Atherton (66/22kV) | Zone Substation | 88.1 | 88.1 | 88.1 | 88.1 | 88.1 | 97.4 | 97.4 | 97.4 | 97.4 | 97.4 | Atherton | ATHE | ATHE!$J$25:$T$25 | ATHE!$U$25:$AQ$25 | ATHE!$J$26:$T$26 | ATHE!$U$26:$AQ$26 | ECC Rating (MVA)
Awoonga (66/11kV) | Zone Substation | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 25.7 | 25.7 | 25.7 | 25.7 | 25.7 | Awoonga | AWOO | AWOO!$J$25:$T$25 | AWOO!$U$25:$AQ$25 | AWOO!$J$26:$T$26 | AWOO!$U$26:$AQ$26 | 50 PoE Load (MVA)
Ayr (66/11kV) | Zone Substation | 23.9 | 23.9 | 23.9 | 23.9 | 23.9 | 25.4 | 25.4 | 25.4 | 25.4 | 25.4 | Ayr | AYRZ | AYRZ!$J$25:$T$25 | AYRZ!$U$25:$AQ$25 | AYRZ!$J$26:$T$26 | AYRZ!$U$26:$AQ$26 | 50 PoE Load > 95% (MVA)
Balberra (33/11kV) | Zone Substation | 7 | 7 | 7 | 7 | 7 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | Balberra | BALB | BALB!$J$25:$T$25 | BALB!$U$25:$AQ$25 | BALB!$J$26:$T$26 | BALB!$U$26:$AQ$26 | Hours PA > 95% Peak Load
Bambaroo (66/11kV) | Zone Substation | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | Bambaroo | BAMB | BAMB!$J$25:$T$25 | BAMB!$U$25:$AQ$25 | BAMB!$J$26:$T$26 | BAMB!$U$26:$AQ$26 | Raw LAR (MVA)
Barcaldine (66/22kV) | Zone Substation | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | Barcaldine | BARR | BARR!$J$25:$T$25 | BARR!$U$25:$AQ$25 | BARR!$J$26:$T$26 | BARR!$U$26:$AQ$26 | Auto Trans Avail (MVA)
Barcaldine BSP (132/66kV) | Bulk Supply | 26.6 | 26.6 | 26.6 | 26.6 | 26.6 | 26.6 | 26.6 | 26.6 | 26.6 | 26.6 | Barcaldine BSP | T072 | 'T072'!$I$23:$S$23 | 'T072'!$T$23:$AQ$23 | 'T072'!$I$24:$S$24 | 'T072'!$T$24:$AQ$24 | Remote Trans Avail (MVA)
Bargara (66/11kV) | Zone Substation | 69.9 | 69.9 | 69.9 | 69.9 | 69.9 | 74.8 | 74.8 | 74.8 | 74.8 | 74.8 | Bargara | BARG | BARG!$J$25:$T$25 | BARG!$U$25:$AQ$25 | BARG!$J$26:$T$26 | BARG!$U$26:$AQ$26 | Manual Trans Avail (MVA)
Barratta (66/11kV) | Zone Substation | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | Barratta | BARR | BARR!$J$25:$T$25 | BARR!$U$25:$AQ$25 | BARR!$J$26:$T$26 | BARR!$U$26:$AQ$26 | Mobile Plant Avail (MVA)
Bedford Weir (66/22kV) | Zone Substation | 20.9 | 20.9 | 20.9 | 20.9 | 20.9 | 23.3 | 23.3 | 23.3 | 23.3 | 23.3 | Bedford Weir | BEWE | BEWE!$J$25:$T$25 | BEWE!$U$25:$AQ$25 | BEWE!$J$26:$T$26 | BEWE!$U$26:$AQ$26 | Shed(30min)
Belgian Gardens (66/11kV) | Zone Substation | 73.9 | 73.9 | 73.9 | 73.9 | 73.9 | 76.6 | 76.6 | 76.6 | 76.6 | 76.6 | Belgian Gardens | BEGA | BEGA!$J$25:$T$25 | BEGA!$U$25:$AQ$25 | BEGA!$J$26:$T$26 | BEGA!$U$26:$AQ$26 | Shed(4Hour)
Berserker (66/11kV) | Zone Substation | 78.5 | 78.5 | 78.5 | 78.5 | 78.5 | 88 | 88 | 88 | 88 | 88 | Berserker | BERS | BERS!$J$25:$T$25 | BERS!$U$25:$AQ$25 | BERS!$J$26:$T$26 | BERS!$U$26:$AQ$26 | LARc (MVA)
Biloela (66/11kV) | Zone Substation | 47.3 | 47.3 | 47.3 | 47.3 | 47.3 | 55 | 55 | 55 | 55 | 55 | Biloela | BILO | BILO!$J$25:$T$25 | BILO!$U$25:$AQ$25 | BILO!$J$26:$T$26 | BILO!$U$26:$AQ$26 | LARc (MW)
Bingegang (66/22kV) | Zone Substation | 11 | 11 | 11 | 11 | 11 | 12 | 12 | 12 | 12 | 12 | Bingegang | BING | BING!$J$25:$T$25 | BING!$U$25:$AQ$25 | BING!$J$26:$T$26 | BING!$U$26:$AQ$26 | Substation Category
Black River (66/11kV) | Zone Substation | 56 | 56 | 56 | 56 | 56 | 59.1 | 59.1 | 59.1 | 59.1 | 59.1 | Black River | BLRI | BLRI!$J$25:$T$25 | BLRI!$U$25:$AQ$25 | BLRI!$J$26:$T$26 | BLRI!$U$26:$AQ$26 | Meets Security Standard
Blackall (66/22kV) | Zone Substation | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 16.5 | 16.5 | 16.5 | 16.5 | 16.5 | Blackall | BLAK | BLAK!$J$25:$T$25 | BLAK!$U$25:$AQ$25 | BLAK!$J$26:$T$26 | BLAK!$U$26:$AQ$26
Blackwater (11/22kV) | Zone Substation | 20 | 20 | 20 | 20 | 20 | 22 | 22 | 22 | 22 | 22 | Blackwater | BLAC | BLAC!$J$25:$T$25 | BLAC!$U$25:$AQ$25 | BLAC!$J$26:$T$26 | BLAC!$U$26:$AQ$26
Bluewater (66/11kV) | Zone Substation | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | Bluewater | BLUE | BLUE!$J$25:$T$25 | BLUE!$U$25:$AQ$25 | BLUE!$J$26:$T$26 | BLUE!$U$26:$AQ$26
Boat Creek BSP (132/66kV) | Bulk Supply | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 162 | 162 | 162 | 162 | 162 | Boat Creek BSP | T130 | 'T130'!$I$23:$S$23 | 'T130'!$T$23:$AQ$23 | 'T130'!$I$24:$S$24 | 'T130'!$T$24:$AQ$24
Bohle (66/11kV) | Zone Substation | 52.7 | 52.7 | 52.7 | 52.7 | 52.7 | 55.3 | 55.3 | 55.3 | 55.3 | 55.3 | Bohle | BOHL | BOHL!$J$25:$T$25 | BOHL!$U$25:$AQ$25 | BOHL!$J$26:$T$26 | BOHL!$U$26:$AQ$26
Boondooma Dam (66/11kV) | Zone Substation | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | Boondooma Dam | BODA | BODA!$J$25:$T$25 | BODA!$U$25:$AQ$25 | BODA!$J$26:$T$26 | BODA!$U$26:$AQ$26
Bowen (66/11kV) | Zone Substation | 39.8 | 39.8 | 39.8 | 39.8 | 39.8 | 44.4 | 44.4 | 44.4 | 44.4 | 44.4 | Bowen | BOWE | BOWE!$J$25:$T$25 | BOWE!$U$25:$AQ$25 | BOWE!$J$26:$T$26 | BOWE!$U$26:$AQ$26
Boyne Residential (66/11kV) | Zone Substation | 26 | 26 | 26 | 26 | 26 | 29.9 | 29.9 | 29.9 | 29.9 | 29.9 | Boyne Residential | BORE | BORE!$J$25:$T$25 | BORE!$U$25:$AQ$25 | BORE!$J$26:$T$26 | BORE!$U$26:$AQ$26
Broadlea BSP (132/66kV) | Bulk Supply | 223.1 | 223.1 | 223.1 | 223.1 | 223.1 | 241.4 | 241.4 | 241.4 | 241.4 | 241.4 | Broadlea BSP | T198 | 'T198'!$I$23:$S$23 | 'T198'!$T$23:$AQ$23 | 'T198'!$I$24:$S$24 | 'T198'!$T$24:$AQ$24
Broxburn (33/11kV) | Zone Substation | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | Broxburn | BROX | BROX!$J$25:$T$25 | BROX!$U$25:$AQ$25 | BROX!$J$26:$T$26 | BROX!$U$26:$AQ$26
Bullyard (66/11kV) | Zone Substation | 14.2 | 14.2 | 14.2 | 14.2 | 14.2 | 15 | 15 | 15 | 15 | 15 | Bullyard | BULL | BULL!$J$25:$T$25 | BULL!$U$25:$AQ$25 | BULL!$J$26:$T$26 | BULL!$U$26:$AQ$26
Bundaberg BSP (132/66kV) | Bulk Supply | 226.4 | 226.4 | 226.4 | 226.4 | 226.4 | 250.8 | 250.8 | 250.8 | 250.8 | 250.8 | Bundaberg BSP | BUND | BUND!$I$23:$S$23 | BUND!$T$23:$AQ$23 | BUND!$I$24:$S$24 | BUND!$T$24:$AQ$24
Bundaberg Central (66/11kV) | Zone Substation | 80.3 | 80.3 | 80.3 | 80.3 | 80.3 | 87.4 | 87.4 | 87.4 | 87.4 | 87.4 | Bundaberg Central | BUCE | BUCE!$J$25:$T$25 | BUCE!$U$25:$AQ$25 | BUCE!$J$26:$T$26 | BUCE!$U$26:$AQ$26
Cairns City (132/22kV) | Zone Substation | 182.3 | 182.3 | 182.3 | 182.3 | 182.3 | 187.9 | 187.9 | 187.9 | 187.9 | 187.9 | Cairns City | CACI | CACI!$J$25:$T$25 | CACI!$U$25:$AQ$25 | CACI!$J$26:$T$26 | CACI!$U$26:$AQ$26
Cairns North (132/22kV) | Zone Substation | 142.8 | 142.8 | 142.8 | 142.8 | 142.8 | 147.1 | 147.1 | 147.1 | 147.1 | 147.1 | Cairns North | CANO | CANO!$J$25:$T$25 | CANO!$U$25:$AQ$25 | CANO!$J$26:$T$26 | CANO!$U$26:$AQ$26
Calen (66/11kV) | Zone Substation | 11 | 11 | 11 | 11 | 11 | 12 | 12 | 12 | 12 | 12 | Calen | CALE | CALE!$J$25:$T$25 | CALE!$U$25:$AQ$25 | CALE!$J$26:$T$26 | CALE!$U$26:$AQ$26
Calliope (66/11kV) | Zone Substation | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 29.9 | 29.9 | 29.9 | 29.9 | 29.9 | Calliope | CALL | CALL!$J$25:$T$25 | CALL!$U$25:$AQ$25 | CALL!$J$26:$T$26 | CALL!$U$26:$AQ$26
Canning Street (66/11kV) | Zone Substation | 46.3 | 46.3 | 46.3 | 46.3 | 46.3 | 54.2 | 54.2 | 54.2 | 54.2 | 54.2 | Canning Street | CAST | CAST!$J$25:$T$25 | CAST!$U$25:$AQ$25 | CAST!$J$26:$T$26 | CAST!$U$26:$AQ$26
Cannonvale (66/11kV) | Zone Substation | 34.9 | 34.9 | 34.9 | 34.9 | 34.9 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | Cannonvale | CANN | CANN!$J$25:$T$25 | CANN!$U$25:$AQ$25 | CANN!$J$26:$T$26 | CANN!$U$26:$AQ$26
Cape Ferguson (66/11kV) | Zone Substation | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | Cape Ferguson | CAFE | CAFE!$J$25:$T$25 | CAFE!$U$25:$AQ$25 | CAFE!$J$26:$T$26 | CAFE!$U$26:$AQ$26
Cape River (66/11kV) | Zone Substation | 1 | 1 | 1 | 1 | 1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | Cape River | CARI | CARI!$J$25:$T$25 | CARI!$U$25:$AQ$25 | CARI!$J$26:$T$26 | CARI!$U$26:$AQ$26
Cape Upstart (66/11kV) | Zone Substation |  | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | Cape Upstart | CAUP | CAUP!$I$22:$Q$22 | CAUP!$R$22:$AQ$22 | CAUP!$I$23:$Q$23 | CAUP!$R$23:$AQ$23
Carmila (33/11kV) | Zone Substation | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | Carmila | CARM | CARM!$J$25:$T$25 | CARM!$U$25:$AQ$25 | CARM!$J$26:$T$26 | CARM!$U$26:$AQ$26
Cawdor Skid B (33/11kV) | Zone Substation | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 33/11kV | CAWD | CAWD!$J$25:$T$25 | CAWD!$U$25:$AQ$25 | CAWD!$J$26:$T$26 | CAWD!$U$26:$AQ$26
Cecil Plains (33/11kV) | Zone Substation | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | Cecil Plains | CEPL | CEPL!$J$25:$T$25 | CEPL!$U$25:$AQ$25 | CEPL!$J$26:$T$26 | CEPL!$U$26:$AQ$26
Charleville (66/22/11kV) | Zone Substation | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | Charleville | CHAR | CHAR!$J$25:$T$25 | CHAR!$U$25:$AQ$25 | CHAR!$J$26:$T$26 | CHAR!$U$26:$AQ$26
Charlton Skid K (33/11kV) | Zone Substation | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 33/11kV | CHAL | CHAL!$J$25:$T$25 | CHAL!$U$25:$AQ$25 | CHAL!$J$26:$T$26 | CHAL!$U$26:$AQ$26
Charters Towers (66/11kV) | Zone Substation | 13.7 | 13.7 | 13.7 | 13.7 | 13.7 | 15 | 15 | 15 | 15 | 15 | Charters Towers | CHTW | CHTW!$J$25:$T$25 | CHTW!$U$25:$AQ$25 | CHTW!$J$26:$T$26 | CHTW!$U$26:$AQ$26
Childers (66/11kV) | Zone Substation | 20.9 | 20.9 | 20.9 | 20.9 | 20.9 | 22.4 | 22.4 | 22.4 | 22.4 | 22.4 | Childers | CHIL | CHIL!$J$25:$T$25 | CHIL!$U$25:$AQ$25 | CHIL!$J$26:$T$26 | CHIL!$U$26:$AQ$26
Chillagoe (66/22kV) | Zone Substation | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | 9.2 | 9.2 | 9.2 | 9.2 | 9.2 | Chillagoe | CHIA | CHIA!$J$25:$T$25 | CHIA!$U$25:$AQ$25 | CHIA!$J$26:$T$26 | CHIA!$U$26:$AQ$26
Chinchilla BSP (132/33kV) | Bulk Supply | 66 | 66 | 66 | 66 | 66 | 78.9 | 78.9 | 78.9 | 78.9 | 78.9 | Chinchilla BSP | CHIN | CHIN!$I$23:$S$23 | CHIN!$T$23:$AQ$23 | CHIN!$I$24:$S$24 | CHIN!$T$24:$AQ$24
Chinchilla Skid E (33/11kV) | Zone Substation | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 33/11kV | SKIE | SKIE!$J$25:$T$25 | SKIE!$U$25:$AQ$25 | SKIE!$J$26:$T$26 | SKIE!$U$26:$AQ$26
Chinchilla Town (33/11kV) | Zone Substation | 21 | 21 | 21 | 21 | 21 | 23 | 23 | 23 | 23 | 23 | Chinchilla Town | CHTO | CHTO!$J$25:$T$25 | CHTO!$U$25:$AQ$25 | CHTO!$J$26:$T$26 | CHTO!$U$26:$AQ$26
Chumvale BSP (220/66kV) | Bulk Supply | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | Chumvale BSP | CHUM | CHUM!$I$23:$S$23 | CHUM!$T$23:$AQ$23 | CHUM!$I$24:$S$24 | CHUM!$T$24:$AQ$24
Clare South (66/11kV) | Zone Substation | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | Clare South | CLSO | CLSO!$J$25:$T$25 | CLSO!$U$25:$AQ$25 | CLSO!$J$26:$T$26 | CLSO!$U$26:$AQ$26
Clermont (66/22kV) | Zone Substation | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | Clermont | CLER | CLER!$J$25:$T$25 | CLER!$U$25:$AQ$25 | CLER!$J$26:$T$26 | CLER!$U$26:$AQ$26
Clermont BSP (132/66kV) | Bulk Supply | 80.9 | 80.9 | 80.9 | 80.9 | 80.9 | 86.9 | 86.9 | 86.9 | 86.9 | 86.9 | Clermont BSP | CLBS | CLBS!$I$23:$S$23 | CLBS!$T$23:$AQ$23 | CLBS!$I$24:$S$24 | CLBS!$T$24:$AQ$24
Clifton (33/11kV) | Zone Substation | 8 | 8 | 8 | 8 | 8 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | Clifton | CLIF | CLIF!$J$25:$T$25 | CLIF!$U$25:$AQ$25 | CLIF!$J$26:$T$26 | CLIF!$U$26:$AQ$26
Clinton (66/11kV) | Zone Substation | 70.4 | 70.4 | 70.4 | 70.4 | 70.4 | 74.8 | 74.8 | 74.8 | 74.8 | 74.8 | Clinton | CLIN | CLIN!$J$25:$T$25 | CLIN!$U$25:$AQ$25 | CLIN!$J$26:$T$26 | CLIN!$U$26:$AQ$26
Cloncurry (66/11kV) | Zone Substation | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | Cloncurry | CLON | CLON!$J$25:$T$25 | CLON!$U$25:$AQ$25 | CLON!$J$26:$T$26 | CLON!$U$26:$AQ$26
Columboola BSP (132/33kV) | Bulk Supply | 40.2 | 40.2 | 40.2 | 40.2 | 40.2 | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | Columboola BSP | COLU | COLU!$I$23:$S$23 | COLU!$T$23:$AQ$23 | COLU!$I$24:$S$24 | COLU!$T$24:$AQ$24
Comet (66/22kV) | Zone Substation | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | Comet | COME | COME!$J$25:$T$25 | COME!$U$25:$AQ$25 | COME!$J$26:$T$26 | COME!$U$26:$AQ$26
Cooktown (66/22kV) | Zone Substation | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | Cooktown | COOK | COOK!$J$25:$T$25 | COOK!$U$25:$AQ$25 | COOK!$J$26:$T$26 | COOK!$U$26:$AQ$26
Coominglah (66/22kV) | Zone Substation | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 3 | 3 | 3 | 3 | 3 | Coominglah | COOM | COOM!$J$25:$T$25 | COOM!$U$25:$AQ$25 | COOM!$J$26:$T$26 | COOM!$U$26:$AQ$26
Craiglie (132/22kV) | Zone Substation | 47.1 | 47.1 | 47.1 | 47.1 | 47.1 | 53.4 | 53.4 | 53.4 | 53.4 | 53.4 | Craiglie | CRAI | CRAI!$J$25:$T$25 | CRAI!$U$25:$AQ$25 | CRAI!$J$26:$T$26 | CRAI!$U$26:$AQ$26
Cranbrook (66/11kV) | Zone Substation | 55.6 | 55.6 | 55.6 | 55.6 | 55.6 | 57.9 | 57.9 | 57.9 | 57.9 | 57.9 | Cranbrook | CRAN | CRAN!$J$25:$T$25 | CRAN!$U$25:$AQ$25 | CRAN!$J$26:$T$26 | CRAN!$U$26:$AQ$26
Crediton (66/11kV) | Zone Substation | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | Crediton | CRED | CRED!$J$25:$T$25 | CRED!$U$25:$AQ$25 | CRED!$J$26:$T$26 | CRED!$U$26:$AQ$26
Crows Nest (33/11kV) | Zone Substation | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 9.4 | 9.4 | 9.4 | 9.4 | 9.4 | Crows Nest | CRNE | CRNE!$J$25:$T$25 | CRNE!$U$25:$AQ$25 | CRNE!$J$26:$T$26 | CRNE!$U$26:$AQ$26
Croydon (66/22kV) | Zone Substation | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | Croydon | CROY | CROY!$J$25:$T$25 | CROY!$U$25:$AQ$25 | CROY!$J$26:$T$26 | CROY!$U$26:$AQ$26
Cunnamulla (66/22kV) | Zone Substation | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | Cunnamulla | CUNN | CUNN!$J$25:$T$25 | CUNN!$U$25:$AQ$25 | CUNN!$J$26:$T$26 | CUNN!$U$26:$AQ$26
Daandine BSP (110/33kV) | Bulk Supply | 37.3 | 37.3 | 37.3 | 37.3 | 37.3 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | Daandine BSP | T188 | 'T188'!$I$23:$S$23 | 'T188'!$T$23:$AQ$23 | 'T188'!$I$24:$S$24 | 'T188'!$T$24:$AQ$24
Dalby Central (33/11kV) | Zone Substation | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 50.9 | 50.9 | 50.9 | 50.9 | 50.9 | Dalby Central | DACE | DACE!$J$25:$T$25 | DACE!$U$25:$AQ$25 | DACE!$J$26:$T$26 | DACE!$U$26:$AQ$26
Dalby East BSP (110/33kV) | Bulk Supply | 130.3 | 130.3 | 130.3 | 130.3 | 130.3 | 149.7 | 149.7 | 149.7 | 149.7 | 149.7 | Dalby East BSP | T002 | 'T002'!$I$23:$S$23 | 'T002'!$T$23:$AQ$23 | 'T002'!$I$24:$S$24 | 'T002'!$T$24:$AQ$24
Dan Gleeson (66/11kV) | Zone Substation | 42.6 | 42.6 | 42.6 | 42.6 | 42.6 | 39.8 | 39.8 | 39.8 | 39.8 | 39.8 | Dan Gleeson | DAGL | DAGL!$J$25:$T$25 | DAGL!$U$25:$AQ$25 | DAGL!$J$26:$T$26 | DAGL!$U$26:$AQ$26
Degilbo (66/11kV) | Zone Substation | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.9 | 5.9 | 5.9 | 5.9 | 5.9 | Degilbo | DEGI | DEGI!$J$25:$T$25 | DEGI!$U$25:$AQ$25 | DEGI!$J$26:$T$26 | DEGI!$U$26:$AQ$26
Dimbulah (66/22kV) | Zone Substation | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 25.9 | 25.9 | 25.9 | 25.9 | 25.9 | Dimbulah | DIMB | DIMB!$J$25:$T$25 | DIMB!$U$25:$AQ$25 | DIMB!$J$26:$T$26 | DIMB!$U$26:$AQ$26
Disraeli (66/11kV) | Zone Substation | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | Disraeli | DISR | DISR!$J$25:$T$25 | DISR!$U$25:$AQ$25 | DISR!$J$26:$T$26 | DISR!$U$26:$AQ$26
Duchess Road (132/66kV) | Zone Substation | 79.6 | 79.6 | 79.6 | 79.6 | 79.6 | 84.4 | 84.4 | 84.4 | 84.4 | 84.4 | Duchess Road | DURO | DURO!$J$25:$T$25 | DURO!$U$25:$AQ$25 | DURO!$J$26:$T$26 | DURO!$U$26:$AQ$26
Dysart (66/22kV) | Zone Substation | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | Dysart | DYSA | DYSA!$J$25:$T$25 | DYSA!$U$25:$AQ$25 | DYSA!$J$26:$T$26 | DYSA!$U$26:$AQ$26
East Ayr (66/11kV) | Zone Substation | 64.9 | 64.9 | 64.9 | 64.9 | 64.9 | 69.9 | 69.9 | 69.9 | 69.9 | 69.9 | East Ayr | EAAY | EAAY!$J$25:$T$25 | EAAY!$U$25:$AQ$25 | EAAY!$J$26:$T$26 | EAAY!$U$26:$AQ$26
East Bundaberg (66/11kV) | Zone Substation | 34.7 | 34.7 | 34.7 | 34.7 | 34.7 | 40.8 | 40.8 | 40.8 | 40.8 | 40.8 | East Bundaberg | EABU | EABU!$J$25:$T$25 | EABU!$U$25:$AQ$25 | EABU!$J$26:$T$26 | EABU!$U$26:$AQ$26
East Toowoomba (33/11kV) | Zone Substation | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 66.1 | 66.1 | 66.1 | 66.1 | 66.1 | East Toowoomba | EATO | EATO!$J$25:$T$25 | EATO!$U$25:$AQ$25 | EATO!$J$26:$T$26 | EATO!$U$26:$AQ$26
Edmonton (132/22kV) | Zone Substation | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | Edmonton | EDMO | EDMO!$J$25:$T$25 | EDMO!$U$25:$AQ$25 | EDMO!$J$26:$T$26 | EDMO!$U$26:$AQ$26
Eidsvold (66/11kV) | Zone Substation | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | Eidsvold | EIDS | EIDS!$J$25:$T$25 | EIDS!$U$25:$AQ$25 | EIDS!$J$26:$T$26 | EIDS!$U$26:$AQ$26
Ellwoods Road (66/11kV) | Zone Substation | 10 | 10 | 10 | 10 | 10 | 11 | 11 | 11 | 11 | 11 | Ellwoods Road | ELRO | ELRO!$J$25:$T$25 | ELRO!$U$25:$AQ$25 | ELRO!$J$26:$T$26 | ELRO!$U$26:$AQ$26
Emerald (66/22kV) | Zone Substation | 69.6 | 69.6 | 69.6 | 69.6 | 69.6 | 81.1 | 81.1 | 81.1 | 81.1 | 81.1 | Emerald | EMER | EMER!$J$25:$T$25 | EMER!$U$25:$AQ$25 | EMER!$J$26:$T$26 | EMER!$U$26:$AQ$26
Eton (33/11kV) | Zone Substation | 14.1 | 14.1 | 14.1 | 14.1 | 14.1 | 15 | 15 | 15 | 15 | 15 | Eton | ETON | ETON!$J$25:$T$25 | ETON!$U$25:$AQ$25 | ETON!$J$26:$T$26 | ETON!$U$26:$AQ$26
Eungella Dam (66/11kV) | Zone Substation | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | Eungella Dam | EUDA | EUDA!$J$25:$T$25 | EUDA!$U$25:$AQ$25 | EUDA!$J$26:$T$26 | EUDA!$U$26:$AQ$26
Evelyn (66/22kV) | Zone Substation | 9.4 | 9.4 | 9.4 | 9.4 | 9.4 | 9.4 | 9.4 | 9.4 | 9.4 | 9.4 | Evelyn | EVEL | EVEL!$J$25:$T$25 | EVEL!$U$25:$AQ$25 | EVEL!$J$26:$T$26 | EVEL!$U$26:$AQ$26
Farleigh (33/11kV) | Zone Substation | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | Farleigh | FARL | FARL!$J$25:$T$25 | FARL!$U$25:$AQ$25 | FARL!$J$26:$T$26 | FARL!$U$26:$AQ$26
Farnsfield (66/11kV) | Zone Substation | 28.9 | 28.9 | 28.9 | 28.9 | 28.9 | 37.4 | 37.4 | 37.4 | 37.4 | 37.4 | Farnsfield | FARN | FARN!$J$25:$T$25 | FARN!$U$25:$AQ$25 | FARN!$J$26:$T$26 | FARN!$U$26:$AQ$26
Frenchville (66/11kV) | Zone Substation | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | Frenchville | FREN | FREN!$J$25:$T$25 | FREN!$U$25:$AQ$25 | FREN!$J$26:$T$26 | FREN!$U$26:$AQ$26
Friend Street (66/11kV) | Zone Substation | 47.4 | 47.4 | 47.4 | 47.4 | 47.4 | 53.3 | 53.3 | 53.3 | 53.3 | 53.3 | Friend Street | GLFS | GLFS!$J$25:$T$25 | GLFS!$U$25:$AQ$25 | GLFS!$J$26:$T$26 | GLFS!$U$26:$AQ$26
Garbutt (66/11kV) | Zone Substation | 53.8 | 53.8 | 53.8 | 53.8 | 53.8 | 54 | 54 | 54 | 54 | 54 | Garbutt | GARB | GARB!$J$25:$T$25 | GARB!$U$25:$AQ$25 | GARB!$J$26:$T$26 | GARB!$U$26:$AQ$26
Gayndah (66/11kV) | Zone Substation | 24.6 | 24.6 | 24.6 | 24.6 | 24.6 | 27.1 | 27.1 | 27.1 | 27.1 | 27.1 | Gayndah | GAYN | GAYN!$J$25:$T$25 | GAYN!$U$25:$AQ$25 | GAYN!$J$26:$T$26 | GAYN!$U$26:$AQ$26
Georgetown (66/22kV) | Zone Substation | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 6 | 6 | 6 | 6 | 6 | Georgetown | GEOR | GEOR!$J$25:$T$25 | GEOR!$U$25:$AQ$25 | GEOR!$J$26:$T$26 | GEOR!$U$26:$AQ$26
Georgetown BSP (132/66kV) | Bulk Supply | 16.7 | 16.7 | 16.7 | 16.7 | 16.7 | 18 | 18 | 18 | 18 | 18 | Georgetown BSP | GEOR1 | GEOR1!$I$23:$S$23 | GEOR1!$T$23:$AQ$23 | GEOR1!$I$24:$S$24 | GEOR1!$T$24:$AQ$24
Giru (66/11kV) | Zone Substation | 9.5 | 9.5 | 9.5 | 9.5 | 9.5 | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | Giru | GIRU | GIRU!$J$25:$T$25 | GIRU!$U$25:$AQ$25 | GIRU!$J$26:$T$26 | GIRU!$U$26:$AQ$26
Givelda (66/11kV) | Zone Substation | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 29.6 | 29.6 | 29.6 | 29.6 | 29.6 | Givelda | GIVE | GIVE!$J$25:$T$25 | GIVE!$U$25:$AQ$25 | GIVE!$J$26:$T$26 | GIVE!$U$26:$AQ$26
Gladstone North BSP (132/66kV) | Bulk Supply | 184 | 184 | 184 | 184 | 184 | 208.8 | 208.8 | 208.8 | 208.8 | 208.8 | Gladstone North BSP | GLNO | GLNO!$I$23:$S$23 | GLNO!$T$23:$AQ$23 | GLNO!$I$24:$S$24 | GLNO!$T$24:$AQ$24
Gladstone South (66/11kV) | Zone Substation | 54.7 | 54.7 | 54.7 | 54.7 | 54.7 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | Gladstone South | GLSO | GLSO!$J$25:$T$25 | GLSO!$U$25:$AQ$25 | GLSO!$J$26:$T$26 | GLSO!$U$26:$AQ$26
Glenden (66/11kV) | Zone Substation | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 16.7 | 16.7 | 16.7 | 16.7 | 16.7 | Glenden | GLEN | GLEN!$J$25:$T$25 | GLEN!$U$25:$AQ$25 | GLEN!$J$26:$T$26 | GLEN!$U$26:$AQ$26
Glenelg (66/33kV) | Zone Substation | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | Glenelg | GLEE | GLEE!$J$25:$T$25 | GLEE!$U$25:$AQ$25 | GLEE!$J$26:$T$26 | GLEE!$U$26:$AQ$26
Glenella 11kV (66/11kV) | Zone Substation | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 83.8 | 83.8 | 83.8 | 83.8 | 83.8 | Glenella 11kV | GLEL | GLEL!$J$25:$T$25 | GLEL!$U$25:$AQ$25 | GLEL!$J$26:$T$26 | GLEL!$U$26:$AQ$26
Gooburrum (66/11kV) | Zone Substation | 14.3 | 14.3 | 14.3 | 14.3 | 14.3 | 15 | 15 | 15 | 15 | 15 | Gooburrum | GOOB | GOOB!$J$25:$T$25 | GOOB!$U$25:$AQ$25 | GOOB!$J$26:$T$26 | GOOB!$U$26:$AQ$26
Gootchie (66/11kV) | Zone Substation | 5 | 5 | 5 | 5 | 5 | 5.8 | 5.8 | 5.8 | 5.8 | 5.8 | Gootchie | GOOT | GOOT!$J$25:$T$25 | GOOT!$U$25:$AQ$25 | GOOT!$J$26:$T$26 | GOOT!$U$26:$AQ$26
Gracemere (66/11kV) | Zone Substation |  |  | 11 | 11 | 11 |  |  | 11 | 11 | 11 | Gracemere | Gracem | Gracem!$I$22:$Q$22 | Gracem!$R$22:$AQ$22 | Gracem!$I$23:$Q$23 | Gracem!$R$23:$AQ$23
Granite Creek (66/22kV) | Zone Substation | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | 3.8 | Granite Creek | GRCR | GRCR!$J$25:$T$25 | GRCR!$U$25:$AQ$25 | GRCR!$J$26:$T$26 | GRCR!$U$26:$AQ$26
Granite Creek BSP (132/66kV) | Bulk Supply | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | Granite Creek BSP | T166 | 'T166'!$I$23:$S$23 | 'T166'!$T$23:$AQ$23 | 'T166'!$I$24:$S$24 | 'T166'!$T$24:$AQ$24
Greenvale (66/11kV) | Zone Substation | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | Greenvale | GREN | GREN!$J$25:$T$25 | GREN!$U$25:$AQ$25 | GREN!$J$26:$T$26 | GREN!$U$26:$AQ$26
Gumlu (66/11kV) | Zone Substation | 1.7 | 1.7 | 1.7 | 1.7 | 1.7 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | Gumlu | GUML | GUML!$J$25:$T$25 | GUML!$U$25:$AQ$25 | GUML!$J$26:$T$26 | GUML!$U$26:$AQ$26
Guthalungra (66/11kV) | Zone Substation | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | Guthalungra | GUTH | GUTH!$J$25:$T$25 | GUTH!$U$25:$AQ$25 | GUTH!$J$26:$T$26 | GUTH!$U$26:$AQ$26
Haughton (66/11kV) | Zone Substation | 6.2 | 6.2 | 6.2 | 6.2 | 6.2 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | Haughton | HAPU | HAPU!$J$25:$T$25 | HAPU!$U$25:$AQ$25 | HAPU!$J$26:$T$26 | HAPU!$U$26:$AQ$26
Helenvale (66/22kV) | Zone Substation | 5.7 | 5.7 | 5.7 | 5.7 | 5.7 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | Helenvale | HELE | HELE!$J$25:$T$25 | HELE!$U$25:$AQ$25 | HELE!$J$26:$T$26 | HELE!$U$26:$AQ$26
Hermit Park (66/11kV) | Zone Substation | 56.6 | 56.6 | 56.6 | 56.6 | 56.6 | 58.6 | 58.6 | 58.6 | 58.6 | 58.6 | Hermit Park | HEPA | HEPA!$J$25:$T$25 | HEPA!$U$25:$AQ$25 | HEPA!$J$26:$T$26 | HEPA!$U$26:$AQ$26
Highfields (33/11kV) | Zone Substation | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | Highfields | HIGH | HIGH!$J$25:$T$25 | HIGH!$U$25:$AQ$25 | HIGH!$J$26:$T$26 | HIGH!$U$26:$AQ$26
Hillsborough (66/11kV) | Zone Substation | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | Hillsborough | HILL | HILL!$J$25:$T$25 | HILL!$U$25:$AQ$25 | HILL!$J$26:$T$26 | HILL!$U$26:$AQ$26
Home Hill (66/11kV) | Zone Substation | 59.3 | 59.3 | 59.3 | 59.3 | 59.3 | 65.1 | 65.1 | 65.1 | 65.1 | 65.1 | Home Hill | HOHI | HOHI!$J$25:$T$25 | HOHI!$U$25:$AQ$25 | HOHI!$J$26:$T$26 | HOHI!$U$26:$AQ$26
Howard (66/11kV) | Zone Substation | 16.1 | 16.1 | 16.1 | 16.1 | 16.1 | 16.1 | 16.1 | 16.1 | 16.1 | 16.1 | Howard | HOWA | HOWA!$J$25:$T$25 | HOWA!$U$25:$AQ$25 | HOWA!$J$26:$T$26 | HOWA!$U$26:$AQ$26
Hughenden (66/33kV) | Zone Substation | 20 | 20 | 20 | 20 | 20 | 22.9 | 22.9 | 22.9 | 22.9 | 22.9 | Hughenden | HUGH | HUGH!$J$25:$T$25 | HUGH!$U$25:$AQ$25 | HUGH!$J$26:$T$26 | HUGH!$U$26:$AQ$26
Ilbilbie (33/11kV) | Zone Substation | 1.2 | 1.2 | 1.2 | 1.2 | 1.2 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | Ilbilbie | ILBI | ILBI!$J$25:$T$25 | ILBI!$U$25:$AQ$25 | ILBI!$J$26:$T$26 | ILBI!$U$26:$AQ$26
Ingham (66/11kV) | Zone Substation | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 28.1 | 28.1 | 28.1 | 28.1 | 28.1 | Ingham | INGH | INGH!$J$25:$T$25 | INGH!$U$25:$AQ$25 | INGH!$J$26:$T$26 | INGH!$U$26:$AQ$26
Isis BSP (132/66kV) | Bulk Supply | 134 | 134 | 134 | 134 | 134 | 145 | 145 | 145 | 145 | 145 | Isis BSP | ISIS | ISIS!$I$23:$S$23 | ISIS!$T$23:$AQ$23 | ISIS!$I$24:$S$24 | ISIS!$T$24:$AQ$24
Jandowae (33/11kV) | Zone Substation | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | Jandowae | JAND | JAND!$J$25:$T$25 | JAND!$U$25:$AQ$25 | JAND!$J$26:$T$26 | JAND!$U$26:$AQ$26
Jarvisfield (66/11kV) | Zone Substation | 12.1 | 12.1 | 12.1 | 12.1 | 12.1 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | Jarvisfield | JARV | JARV!$J$25:$T$25 | JARV!$U$25:$AQ$25 | JARV!$J$26:$T$26 | JARV!$U$26:$AQ$26
Jubilee Pocket (66/11kV) | Zone Substation | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 43.4 | 43.4 | 43.4 | 43.4 | 43.4 | Jubilee Pocket | JUPO | JUPO!$J$25:$T$25 | JUPO!$U$25:$AQ$25 | JUPO!$J$26:$T$26 | JUPO!$U$26:$AQ$26
Julia Creek (66/33kV) | Zone Substation | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | Julia Creek | JUCR | JUCR!$J$25:$T$25 | JUCR!$U$25:$AQ$25 | JUCR!$J$26:$T$26 | JUCR!$U$26:$AQ$26
Kaimkillenbun (33/11kV) | Zone Substation | [10 empty] | Kaimkillenbun | KAIM | KAIM!$J$25:$T$25 | KAIM!$U$25:$AQ$25 | KAIM!$J$26:$T$26 | KAIM!$U$26:$AQ$26 | bar: SUMMER 2020/21 to WINTER 2024
Kalamia (66/11kV) | Zone Substation | 13 | 13 | 13 | 13 | 13 | 14.2 | 14.2 | 14.2 | 14.2 | 14.2 | Kalamia | KALA | KALA!$J$25:$T$25 | KALA!$U$25:$AQ$25 | KALA!$J$26:$T$26 | KALA!$U$26:$AQ$26
Kearneys Spring (110/11kV) | Zone Substation | 79.1 | 79.1 | 79.1 | 79.1 | 79.1 | 89.8 | 89.8 | 89.8 | 89.8 | 89.8 | Kearneys Spring | KESP | KESP!$J$25:$T$25 | KESP!$U$25:$AQ$25 | KESP!$J$26:$T$26 | KESP!$U$26:$AQ$26
Kelsey Creek East (66/11kV) | Zone Substation | 36.8 | 36.8 | 36.8 | 36.8 | 36.8 | 38.4 | 38.4 | 38.4 | 38.4 | 38.4 | Kelsey Creek East | KECE | KECE!$J$25:$T$25 | KECE!$U$25:$AQ$25 | KECE!$J$26:$T$26 | KECE!$U$26:$AQ$26
Kidston (132/6.6kV) | Zone Substation | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 44.9 | 44.9 | 44.9 | 44.9 | 44.9 | Kidston | KIDS | KIDS!$J$25:$T$25 | KIDS!$U$25:$AQ$25 | KIDS!$J$26:$T$26 | KIDS!$U$26:$AQ$26
Kilkivan BSP (132/66kV) | Bulk Supply | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | Kilkivan BSP | KILK | KILK!$I$23:$S$23 | KILK!$T$23:$AQ$23 | KILK!$I$24:$S$24 | KILK!$T$24:$AQ$24
Kilkivan Town (66/11kV) | Zone Substation | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | Kilkivan Town | KITO | KITO!$J$25:$T$25 | KITO!$U$25:$AQ$25 | KITO!$J$26:$T$26 | KITO!$U$26:$AQ$26
Killarney (33/11kV) | Zone Substation | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 8.9 | 8.9 | 8.9 | 8.9 | 8.9 | Killarney | KILL | KILL!$J$25:$T$25 | KILL!$U$25:$AQ$25 | KILL!$J$26:$T$26 | KILL!$U$26:$AQ$26
Kingaroy (66/11kV) | Zone Substation | 57.4 | 57.4 | 57.4 | 57.4 | 57.4 | 64.7 | 64.7 | 64.7 | 64.7 | 64.7 | Kingaroy | KING | KING!$J$25:$T$25 | KING!$U$25:$AQ$25 | KING!$J$26:$T$26 | KING!$U$26:$AQ$26
Kirknie (66/11kV) | Zone Substation | 9.7 | 9.7 | 9.7 | 9.7 | 9.7 | 10.9 | 10.9 | 10.9 | 10.9 | 10.9 | Kirknie | KIRK | KIRK!$J$25:$T$25 | KIRK!$U$25:$AQ$25 | KIRK!$J$26:$T$26 | KIRK!$U$26:$AQ$26
Kogan Creek (33/11kV) | Zone Substation | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | Kogan Creek | KOCR | KOCR!$J$25:$T$25 | KOCR!$U$25:$AQ$25 | KOCR!$J$26:$T$26 | KOCR!$U$26:$AQ$26
Koumala (33/11kV) | Zone Substation | 7 | 7 | 7 | 7 | 7 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | Koumala | KOUM | KOUM!$J$25:$T$25 | KOUM!$U$25:$AQ$25 | KOUM!$J$26:$T$26 | KOUM!$U$26:$AQ$26
Laguna Quays (66/11kV) | Zone Substation | 17.6 | 17.6 | 17.6 | 17.6 | 17.6 | 19 | 19 | 19 | 19 | 19 | Laguna Quays | LAQU | LAQU!$J$25:$T$25 | LAQU!$U$25:$AQ$25 | LAQU!$J$26:$T$26 | LAQU!$U$26:$AQ$26
Lakeland (66/22kV) | Zone Substation | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | Lakeland | LAKE | LAKE!$J$25:$T$25 | LAKE!$U$25:$AQ$25 | LAKE!$J$26:$T$26 | LAKE!$U$26:$AQ$26
Lakeland BSP (132/66kV) | Bulk Supply | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 55.8 | 55.8 | 55.8 | 55.8 | 55.8 | Lakeland BSP | T159 | 'T159'!$I$23:$S$23 | 'T159'!$T$23:$AQ$23 | 'T159'!$I$24:$S$24 | 'T159'!$T$24:$AQ$24
Lakes Creek (66/11kV) | Zone Substation | 45.9 | 45.9 | 45.9 | 45.9 | 45.9 | 50.9 | 50.9 | 50.9 | 50.9 | 50.9 | Lakes Creek | LACR | LACR!$J$25:$T$25 | LACR!$U$25:$AQ$25 | LACR!$J$26:$T$26 | LACR!$U$26:$AQ$26
Landing Road Skid D (66/11kV) | Zone Substation | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 66/11kV | LARO | LARO!$J$25:$T$25 | LARO!$U$25:$AQ$25 | LARO!$J$26:$T$26 | LARO!$U$26:$AQ$26
Lannercost (66/11kV) | Zone Substation | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.7 | 8.7 | 8.7 | 8.7 | 8.7 | Lannercost | LANN | LANN!$J$25:$T$25 | LANN!$U$25:$AQ$25 | LANN!$J$26:$T$26 | LANN!$U$26:$AQ$26
Littlemore (66/11kV) | Zone Substation | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | 2.2 | Littlemore | LITT | LITT!$J$25:$T$25 | LITT!$U$25:$AQ$25 | LITT!$J$26:$T$26 | LITT!$U$26:$AQ$26
Longreach (66/22kV) | Zone Substation | 24.4 | 24.4 | 24.4 | 24.4 | 24.4 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | Longreach | LONG | LONG!$J$25:$T$25 | LONG!$U$25:$AQ$25 | LONG!$J$26:$T$26 | LONG!$U$26:$AQ$26
Louisa Creek (33/11kV) | Zone Substation | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.8 | 7.8 | 7.8 | 7.8 | 7.8 | Louisa Creek | LOCR | LOCR!$J$25:$T$25 | LOCR!$U$25:$AQ$25 | LOCR!$J$26:$T$26 | LOCR!$U$26:$AQ$26
Louisa Creek BSP (132/33kV) | Bulk Supply | 175.8 | 175.8 | 175.8 | 175.8 | 175.8 | 185.2 | 185.2 | 185.2 | 185.2 | 185.2 | Louisa Creek BSP | T176 | 'T176'!$I$23:$S$23 | 'T176'!$T$23:$AQ$23 | 'T176'!$I$24:$S$24 | 'T176'!$T$24:$AQ$24
Lucinda (66/11kV) | Zone Substation | 5.9 | 5.9 | 5.9 | 5.9 | 5.9 | 6 | 6 | 6 | 6 | 6 | Lucinda | LUCI | LUCI!$J$25:$T$25 | LUCI!$U$25:$AQ$25 | LUCI!$J$26:$T$26 | LUCI!$U$26:$AQ$26
Lyndley Lane (33/22kV) | Zone Substation | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | Lyndley Lane | LYLA | LYLA!$J$25:$T$25 | LYLA!$U$25:$AQ$25 | LYLA!$J$26:$T$26 | LYLA!$U$26:$AQ$26
Macknade (66/11kV) | Zone Substation | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | Macknade | MACN | MACN!$J$25:$T$25 | MACN!$U$25:$AQ$25 | MACN!$J$26:$T$26 | MACN!$U$26:$AQ$26
Malchi (66/11kV) | Zone Substation | 23.8 | 23.8 | 23.8 | 23.8 | 23.8 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | Malchi | MALC | MALC!$J$25:$T$25 | MALC!$U$25:$AQ$25 | MALC!$J$26:$T$26 | MALC!$U$26:$AQ$26
Mareeba (66/22kV) | Zone Substation | 51.2 | 51.2 | 51.2 | 51.2 | 51.2 | 63.6 | 63.6 | 63.6 | 63.6 | 63.6 | Mareeba | MARE | MARE!$J$25:$T$25 | MARE!$U$25:$AQ$25 | MARE!$J$26:$T$26 | MARE!$U$26:$AQ$26
Marian South (66/11kV) | Zone Substation | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | Marian South | MASO | MASO!$J$25:$T$25 | MASO!$U$25:$AQ$25 | MASO!$J$26:$T$26 | MASO!$U$26:$AQ$26
Maryborough BSP (132/66kV) | Bulk Supply | 356.1 | 356.1 | 356.1 | 356.1 | 356.1 | 403.7 | 403.7 | 403.7 | 403.7 | 403.7 | Maryborough BSP | MARY | MARY!$I$23:$S$23 | MARY!$T$23:$AQ$23 | MARY!$I$24:$S$24 | MARY!$T$24:$AQ$24
Maryborough City (66/11kV) | Zone Substation | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 42.7 | 42.7 | 42.7 | 42.7 | 42.7 | Maryborough City | MACI | MACI!$J$25:$T$25 | MACI!$U$25:$AQ$25 | MACI!$J$26:$T$26 | MACI!$U$26:$AQ$26
Max Fulton (66/11kV) | Zone Substation | 76.3 | 76.3 | 76.3 | 76.3 | 76.3 | 77.7 | 77.7 | 77.7 | 77.7 | 77.7 | Max Fulton | MAFU | MAFU!$J$25:$T$25 | MAFU!$U$25:$AQ$25 | MAFU!$J$26:$T$26 | MAFU!$U$26:$AQ$26
McKinley Creek (66/11kV) | Zone Substation | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | McKinley Creek | MCCR | MCCR!$J$25:$T$25 | MCCR!$U$25:$AQ$25 | MCCR!$J$26:$T$26 | MCCR!$U$26:$AQ$26
Meadowvale (66/11kV) | Zone Substation | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 17.3 | 17.3 | 17.3 | 17.3 | 17.3 | Meadowvale | MEAD | MEAD!$J$25:$T$25 | MEAD!$U$25:$AQ$25 | MEAD!$J$26:$T$26 | MEAD!$U$26:$AQ$26
Meandarra (33/22kV) | Zone Substation | 1 | 1 | 1 | 1 | 1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | Meandarra | MEAN | MEAN!$J$25:$T$25 | MEAN!$U$25:$AQ$25 | MEAN!$J$26:$T$26 | MEAN!$U$26:$AQ$26
Merinda (66/11kV) | Zone Substation | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | Merinda | MERI | MERI!$J$25:$T$25 | MERI!$U$25:$AQ$25 | MERI!$J$26:$T$26 | MERI!$U$26:$AQ$26
Meringandan (33/11kV) | Zone Substation | 16.9 | 16.9 | 16.9 | 16.9 | 16.9 | 18.5 | 18.5 | 18.5 | 18.5 | 18.5 | Meringandan | MERN | MERN!$J$25:$T$25 | MERN!$U$25:$AQ$25 | MERN!$J$26:$T$26 | MERN!$U$26:$AQ$26
Middlemount (66/22kV) | Zone Substation | 15.3 | 15.3 | 15.3 | 15.3 | 15.3 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | Middlemount | MIDD | MIDD!$J$25:$T$25 | MIDD!$U$25:$AQ$25 | MIDD!$J$26:$T$26 | MIDD!$U$26:$AQ$26
Miles (33/11kV) | Zone Substation | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 9.4 | 9.4 | 9.4 | 9.4 | 9.4 | Miles | MILE | MILE!$J$25:$T$25 | MILE!$U$25:$AQ$25 | MILE!$J$26:$T$26 | MILE!$U$26:$AQ$26
Miles-Condamine (33/22kV) | Zone Substation | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | Miles-Condamine | MICO | MICO!$J$25:$T$25 | MICO!$U$25:$AQ$25 | MICO!$J$26:$T$26 | MICO!$U$26:$AQ$26
Millaroo (66/11kV) | Zone Substation | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | Millaroo | MILL | MILL!$J$25:$T$25 | MILL!$U$25:$AQ$25 | MILL!$J$26:$T$26 | MILL!$U$26:$AQ$26
Millchester (66/11kV) | Zone Substation | 10.6 | 10.6 | 10.6 | 10.6 | 10.6 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | Millchester | MILC | MILC!$J$25:$T$25 | MILC!$U$25:$AQ$25 | MILC!$J$26:$T$26 | MILC!$U$26:$AQ$26
Millchester BSP (132/66kV) | Bulk Supply | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | Millchester BSP | T095 | 'T095'!$I$23:$S$23 | 'T095'!$T$23:$AQ$23 | 'T095'!$I$24:$S$24 | 'T095'!$T$24:$AQ$24
Millmerran (33/11kV) | Zone Substation | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | Millmerran | MILM | MILM!$J$25:$T$25 | MILM!$U$25:$AQ$25 | MILM!$J$26:$T$26 | MILM!$U$26:$AQ$26
Mingela (66/11kV) | Zone Substation | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | Mingela | MING | MING!$J$25:$T$25 | MING!$U$25:$AQ$25 | MING!$J$26:$T$26 | MING!$U$26:$AQ$26
Mirani (66/11kV) | Zone Substation | 6.1 | 6.1 | 6.1 | 6.1 | 6.1 | 7 | 7 | 7 | 7 | 7 | Mirani | MIRA | MIRA!$J$25:$T$25 | MIRA!$U$25:$AQ$25 | MIRA!$J$26:$T$26 | MIRA!$U$26:$AQ$26
Miriam Vale (66/22kV) | Zone Substation | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9.4 | 9.4 | 9.4 | 9.4 | 9.4 | Miriam Vale | MIVA | MIVA!$J$25:$T$25 | MIVA!$U$25:$AQ$25 | MIVA!$J$26:$T$26 | MIVA!$U$26:$AQ$26
Mitchell (33/11kV) | Zone Substation | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | Mitchell | MITC | MITC!$J$25:$T$25 | MITC!$U$25:$AQ$25 | MITC!$J$26:$T$26 | MITC!$U$26:$AQ$26
Mona Park (66/11kV) | Zone Substation | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 8 | 8 | 8 | 8 | 8 | Mona Park | MOPA | MOPA!$J$25:$T$25 | MOPA!$U$25:$AQ$25 | MOPA!$J$26:$T$26 | MOPA!$U$26:$AQ$26
Monduran Dam (66/11kV) | Zone Substation | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | Monduran Dam | MODA | MODA!$J$25:$T$25 | MODA!$U$25:$AQ$25 | MODA!$J$26:$T$26 | MODA!$U$26:$AQ$26
Monto (66/11kV) | Zone Substation | 14 | 14 | 14 | 14 | 14 | 16.7 | 16.7 | 16.7 | 16.7 | 16.7 | Monto | MONT | MONT!$J$25:$T$25 | MONT!$U$25:$AQ$25 | MONT!$J$26:$T$26 | MONT!$U$26:$AQ$26
Moorvale (66/11kV) | Zone Substation | 10.5 | 10.5 | 10.5 | 10.5 | 10.5 | 11 | 11 | 11 | 11 | 11 | Moorvale | MOOR | MOOR!$J$25:$T$25 | MOOR!$U$25:$AQ$25 | MOOR!$J$26:$T$26 | MOOR!$U$26:$AQ$26
Moranbah Town (132/11kV) | Zone Substation | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | Moranbah Town | MORA | MORA!$J$25:$T$25 | MORA!$U$25:$AQ$25 | MORA!$J$26:$T$26 | MORA!$U$26:$AQ$26
Mossman (66/22kV) | Zone Substation | 18.5 | 18.5 | 18.5 | 18.5 | 18.5 | 20.6 | 20.6 | 20.6 | 20.6 | 20.6 | Mossman | MOSS | MOSS!$J$25:$T$25 | MOSS!$U$25:$AQ$25 | MOSS!$J$26:$T$26 | MOSS!$U$26:$AQ$26
Mount Fox (66/33kV) | Zone Substation | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | Mount Fox | MOFO | MOFO!$J$25:$T$25 | MOFO!$U$25:$AQ$25 | MOFO!$J$26:$T$26 | MOFO!$U$26:$AQ$26
Mount Leyshon Pump (66/11kV) | Zone Substation | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | Mount Leyshon Pump | MLEP | MLEP!$J$25:$T$25 | MLEP!$U$25:$AQ$25 | MLEP!$J$26:$T$26 | MLEP!$U$26:$AQ$26
Mount Rooper (66/11kV) | Zone Substation | 5.8 | 5.8 | 5.8 | 5.8 | 5.8 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | Mount Rooper | MORO | MORO!$J$25:$T$25 | MORO!$U$25:$AQ$25 | MORO!$J$26:$T$26 | MORO!$U$26:$AQ$26
Moura (66/22kV) | Zone Substation | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | Moura | MOUR | MOUR!$J$25:$T$25 | MOUR!$U$25:$AQ$25 | MOUR!$J$26:$T$26 | MOUR!$U$26:$AQ$26
Mt Bassett (33/11kV) | Zone Substation | 39 | 39 | 39 | 39 | 39 | 42 | 42 | 42 | 42 | 42 | Mt Bassett | MOBA | MOBA!$J$25:$T$25 | MOBA!$U$25:$AQ$25 | MOBA!$J$26:$T$26 | MOBA!$U$26:$AQ$26
Mt Garnet (66/22kV) | Zone Substation | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 9.3 | 9.3 | 9.3 | 9.3 | 9.3 | Mt Garnet | MOGA | MOGA!$J$25:$T$25 | MOGA!$U$25:$AQ$25 | MOGA!$J$26:$T$26 | MOGA!$U$26:$AQ$26
Mt Molloy (66/22kV) | Zone Substation | 16.4 | 16.4 | 16.4 | 16.4 | 16.4 | 18 | 18 | 18 | 18 | 18 | Mt Molloy | MOMO | MOMO!$J$25:$T$25 | MOMO!$U$25:$AQ$25 | MOMO!$J$26:$T$26 | MOMO!$U$26:$AQ$26
Mt Morgan (66/11kV) | Zone Substation | 15.8 | 15.8 | 15.8 | 15.8 | 15.8 | 18 | 18 | 18 | 18 | 18 | Mt Morgan | MOMR | MOMR!$J$25:$T$25 | MOMR!$U$25:$AQ$25 | MOMR!$J$26:$T$26 | MOMR!$U$26:$AQ$26
Mt Mowbullan (33/11kV) | Zone Substation | [10 empty] | Mt Mowbullan | MOMW | MOMW!$J$25:$T$25 | MOMW!$U$25:$AQ$25 | MOMW!$J$26:$T$26 | MOMW!$U$26:$AQ$26 | bar: SUMMER 2020/21 to WINTER 2024
Mt Sibley (33/11kV) | Zone Substation | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | Mt Sibley | MOSI | MOSI!$J$25:$T$25 | MOSI!$U$25:$AQ$25 | MOSI!$J$26:$T$26 | MOSI!$U$26:$AQ$26
Mundubbera Town (66/11kV) | Zone Substation | 49.4 | 49.4 | 49.4 | 49.4 | 49.4 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | Mundubbera Town | MUTO | MUTO!$J$25:$T$25 | MUTO!$U$25:$AQ$25 | MUTO!$J$26:$T$26 | MUTO!$U$26:$AQ$26
Murgon (66/11kV) | Zone Substation | 29.6 | 29.6 | 29.6 | 29.6 | 29.6 | 35.4 | 35.4 | 35.4 | 35.4 | 35.4 | Murgon | MURG | MURG!$J$25:$T$25 | MURG!$U$25:$AQ$25 | MURG!$J$26:$T$26 | MURG!$U$26:$AQ$26
Mutarnee (66/11kV) | Zone Substation | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | Mutarnee | MUTA | MUTA!$J$25:$T$25 | MUTA!$U$25:$AQ$25 | MUTA!$J$26:$T$26 | MUTA!$U$26:$AQ$26
Nanango (66/11kV) | Zone Substation | 13.7 | 13.7 | 13.7 | 13.7 | 13.7 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | Nanango | NANA | NANA!$J$25:$T$25 | NANA!$U$25:$AQ$25 | NANA!$J$26:$T$26 | NANA!$U$26:$AQ$26
Nandi (33/11kV) | Zone Substation | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | Nandi | NAND | NAND!$J$25:$T$25 | NAND!$U$25:$AQ$25 | NAND!$J$26:$T$26 | NAND!$U$26:$AQ$26
Nebo (132/11kV) | Zone Substation | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | Nebo | NEBO | NEBO!$J$25:$T$25 | NEBO!$U$25:$AQ$25 | NEBO!$J$26:$T$26 | NEBO!$U$26:$AQ$26
Neil Smith (66/11kV) | Zone Substation | 65.5 | 65.5 | 65.5 | 65.5 | 65.5 | 68 | 68 | 68 | 68 | 68 | Neil Smith | NESM | NESM!$J$25:$T$25 | NESM!$U$25:$AQ$25 | NESM!$J$26:$T$26 | NESM!$U$26:$AQ$26
Normanton (66/22kV) | Zone Substation | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | 10.2 | Normanton | NORM | NORM!$J$25:$T$25 | NORM!$U$25:$AQ$25 | NORM!$J$26:$T$26 | NORM!$U$26:$AQ$26
North Cloncurry (66/11kV) | Zone Substation | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 13.1 | 13.1 | 13.1 | 13.1 | 13.1 | North Cloncurry | NOCL | NOCL!$J$25:$T$25 | NOCL!$U$25:$AQ$25 | NOCL!$J$26:$T$26 | NOCL!$U$26:$AQ$26
North Mackay (33/11kV) | Zone Substation | 47.7 | 47.7 | 47.7 | 47.7 | 47.7 | 53.1 | 53.1 | 53.1 | 53.1 | 53.1 | North Mackay | NOMA | NOMA!$J$25:$T$25 | NOMA!$U$25:$AQ$25 | NOMA!$J$26:$T$26 | NOMA!$U$26:$AQ$26
North Street (33/11kV) | Zone Substation | 31.1 | 31.1 | 31.1 | 31.1 | 31.1 | 34.5 | 34.5 | 34.5 | 34.5 | 34.5 | North Street | NOST | NOST!$J$25:$T$25 | NOST!$U$25:$AQ$25 | NOST!$J$26:$T$26 | NOST!$U$26:$AQ$26
Norwin (33/11kV) | Zone Substation | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | Norwin | NORW | NORW!$J$25:$T$25 | NORW!$U$25:$AQ$25 | NORW!$J$26:$T$26 | NORW!$U$26:$AQ$26
Oakey (33/11kV) | Zone Substation | 49.7 | 49.7 | 49.7 | 49.7 | 49.7 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | Oakey | OAKE | OAKE!$J$25:$T$25 | OAKE!$U$25:$AQ$25 | OAKE!$J$26:$T$26 | OAKE!$U$26:$AQ$26
Oakey BSP (110/33kV) | Bulk Supply | 147.2 | 147.2 | 147.2 | 147.2 | 147.2 | 165.2 | 165.2 | 165.2 | 165.2 | 165.2 | Oakey BSP | T189 | 'T189'!$I$23:$S$23 | 'T189'!$T$23:$AQ$23 | 'T189'!$I$24:$S$24 | 'T189'!$T$24:$AQ$24
Oonoonba (66/11kV) | Zone Substation | 74.2 | 74.2 | 74.2 | 74.2 | 74.2 | 77.6 | 77.6 | 77.6 | 77.6 | 77.6 | Oonoonba | OONN | OONN!$J$25:$T$25 | OONN!$U$25:$AQ$25 | OONN!$J$26:$T$26 | OONN!$U$26:$AQ$26
Owanyilla (66/11kV) | Zone Substation | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | Owanyilla | OWAN | OWAN!$J$25:$T$25 | OWAN!$U$25:$AQ$25 | OWAN!$J$26:$T$26 | OWAN!$U$26:$AQ$26
Pampas (33/11kV) | Zone Substation | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | Pampas | PAMP | PAMP!$J$25:$T$25 | PAMP!$U$25:$AQ$25 | PAMP!$J$26:$T$26 | PAMP!$U$26:$AQ$26
Pandoin (66/22kV) | Zone Substation | 23.2 | 23.2 | 23.2 | 23.2 | 23.2 | 26.6 | 26.6 | 26.6 | 26.6 | 26.6 | Pandoin | PAND | PAND!$J$25:$T$25 | PAND!$U$25:$AQ$25 | PAND!$J$26:$T$26 | PAND!$U$26:$AQ$26
Parkhurst (66/11kV) | Zone Substation | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | Parkhurst | PARK | PARK!$J$25:$T$25 | PARK!$U$25:$AQ$25 | PARK!$J$26:$T$26 | PARK!$U$26:$AQ$26
Peranga (33/11kV) | Zone Substation | 4.7 | 4.7 | 4.7 | 4.7 | 4.7 | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | Peranga | PERA | PERA!$J$25:$T$25 | PERA!$U$25:$AQ$25 | PERA!$J$26:$T$26 | PERA!$U$26:$AQ$26
Peter Arlett (66/11kV) | Zone Substation | 78.9 | 78.9 | 78.9 | 78.9 | 78.9 | 87.4 | 87.4 | 87.4 | 87.4 | 87.4 | Peter Arlett | PEAR | PEAR!$J$25:$T$25 | PEAR!$U$25:$AQ$25 | PEAR!$J$26:$T$26 | PEAR!$U$26:$AQ$26
Pialba (66/11kV) | Zone Substation | 33.2 | 33.2 | 33.2 | 33.2 | 33.2 | 37.2 | 37.2 | 37.2 | 37.2 | 37.2 | Pialba | PIAL | PIAL!$J$25:$T$25 | PIAL!$U$25:$AQ$25 | PIAL!$J$26:$T$26 | PIAL!$U$26:$AQ$26
Pinnacle (66/11kV) | Zone Substation | 11 | 11 | 11 | 11 | 11 | 12 | 12 | 12 | 12 | 12 | Pinnacle | PINN | PINN!$J$25:$T$25 | PINN!$U$25:$AQ$25 | PINN!$J$26:$T$26 | PINN!$U$26:$AQ$26
Pirrinuan (33/11kV) | Zone Substation | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | Pirrinuan | PIRR | PIRR!$J$25:$T$25 | PIRR!$U$25:$AQ$25 | PIRR!$J$26:$T$26 | PIRR!$U$26:$AQ$26
Planella (66/11kV) | Zone Substation | 30.6 | 30.6 | 30.6 | 30.6 | 30.6 | 30.6 | 30.6 | 30.6 | 30.6 | 30.6 | Planella | PLAN | PLAN!$J$25:$T$25 | PLAN!$U$25:$AQ$25 | PLAN!$J$26:$T$26 | PLAN!$U$26:$AQ$26
Pleystowe (33/11kV) | Zone Substation | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | Pleystowe | PLEY | PLEY!$J$25:$T$25 | PLEY!$U$25:$AQ$25 | PLEY!$J$26:$T$26 | PLEY!$U$26:$AQ$26
Point Vernon (66/11kV) | Zone Substation | 84.6 | 84.6 | 84.6 | 84.6 | 84.6 | 95.7 | 95.7 | 95.7 | 95.7 | 95.7 | Point Vernon | POVE | POVE!$J$25:$T$25 | POVE!$U$25:$AQ$25 | POVE!$J$26:$T$26 | POVE!$U$26:$AQ$26
Pozieres (33/11kV) | Zone Substation | 7.1 | 7.1 | 7.1 | 7.1 | 7.1 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | Pozieres | POZI | POZI!$J$25:$T$25 | POZI!$U$25:$AQ$25 | POZI!$J$26:$T$26 | POZI!$U$26:$AQ$26
Proserpine Mill (66/11kV) | Zone Substation | 14.4 | 14.4 | 14.4 | 14.4 | 14.4 | 15.2 | 15.2 | 15.2 | 15.2 | 15.2 | Proserpine Mill | PRMI | PRMI!$J$25:$T$25 | PRMI!$U$25:$AQ$25 | PRMI!$J$26:$T$26 | PRMI!$U$26:$AQ$26
Proston (66/11kV) | Zone Substation | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 6 | 6 | 6 | 6 | 6 | Proston | PROT | PROT!$J$25:$T$25 | PROT!$U$25:$AQ$25 | PROT!$J$26:$T$26 | PROT!$U$26:$AQ$26
Purrawunda (33/11kV) | Zone Substation | 14 | 14 | 14 | 14 | 14 | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | Purrawunda | PURR | PURR!$J$25:$T$25 | PURR!$U$25:$AQ$25 | PURR!$J$26:$T$26 | PURR!$U$26:$AQ$26
Quilpie (66/11kV) | Zone Substation | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | Quilpie | QUIL | QUIL!$J$25:$T$25 | QUIL!$U$25:$AQ$25 | QUIL!$J$26:$T$26 | QUIL!$U$26:$AQ$26
Raglan (66/22kV) | Zone Substation | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 14 | 14 | 14 | 14 | 14 | Raglan | RAGL | RAGL!$J$25:$T$25 | RAGL!$U$25:$AQ$25 | RAGL!$J$26:$T$26 | RAGL!$U$26:$AQ$26
Rasmussen (66/11kV) | Zone Substation | 80.4 | 80.4 | 80.4 | 80.4 | 80.4 | 84.4 | 84.4 | 84.4 | 84.4 | 84.4 | Rasmussen | RASM | RASM!$J$25:$T$25 | RASM!$U$25:$AQ$25 | RASM!$J$26:$T$26 | RASM!$U$26:$AQ$26
Ravenshoe (66/22kV) | Zone Substation | 19.6 | 19.6 | 19.6 | 19.6 | 19.6 | 22.3 | 22.3 | 22.3 | 22.3 | 22.3 | Ravenshoe | RAVE | RAVE!$J$25:$T$25 | RAVE!$U$25:$AQ$25 | RAVE!$J$26:$T$26 | RAVE!$U$26:$AQ$26
Ravenswood (66/11kV) | Zone Substation | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | Ravenswood | RAVN | RAVN!$J$25:$T$25 | RAVN!$U$25:$AQ$25 | RAVN!$J$26:$T$26 | RAVN!$U$26:$AQ$26
Richmond (66/33kV) | Zone Substation | 14.6 | 14.6 | 14.6 | 14.6 | 14.6 | 16.3 | 16.3 | 16.3 | 16.3 | 16.3 | Richmond | RICH | RICH!$J$25:$T$25 | RICH!$U$25:$AQ$25 | RICH!$J$26:$T$26 | RICH!$U$26:$AQ$26
Rockhampton Glenmore (66/11kV) | Zone Substation | 81.4 | 81.4 | 81.4 | 81.4 | 81.4 | 82.5 | 82.5 | 82.5 | 82.5 | 82.5 | Rockhampton Glenmore | ROGL | ROGL!$J$25:$T$25 | ROGL!$U$25:$AQ$25 | ROGL!$J$26:$T$26 | ROGL!$U$26:$AQ$26
Rockhampton South (66/11kV) | Zone Substation | 32.7 | 32.7 | 32.7 | 32.7 | 32.7 | 32.7 | 32.7 | 32.7 | 32.7 | 32.7 | Rockhampton South | ROSO | ROSO!$J$25:$T$25 | ROSO!$U$25:$AQ$25 | ROSO!$J$26:$T$26 | ROSO!$U$26:$AQ$26
Rocky Street (66/11kV) | Zone Substation | 57.5 | 57.5 | 57.5 | 57.5 | 57.5 | 64.3 | 64.3 | 64.3 | 64.3 | 64.3 | Rocky Street | ROST | ROST!$J$25:$T$25 | ROST!$U$25:$AQ$25 | ROST!$J$26:$T$26 | ROST!$U$26:$AQ$26
Rolleston (66/22kV) | Zone Substation | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | Rolleston | ROLE | ROLE!$J$25:$T$25 | ROLE!$U$25:$AQ$25 | ROLE!$J$26:$T$26 | ROLE!$U$26:$AQ$26
Rolleston BSP (132/66kV) | Bulk Supply | 89.3 | 89.3 | 89.3 | 89.3 | 89.3 | 97.7 | 97.7 | 97.7 | 97.7 | 97.7 | Rolleston BSP | T163 | 'T163'!$I$23:$S$23 | 'T163'!$T$23:$AQ$23 | 'T163'!$I$24:$S$24 | 'T163'!$T$24:$AQ$24
Rollingstone (66/11kV) | Zone Substation | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | Rollingstone | ROLL | ROLL!$J$25:$T$25 | ROLL!$U$25:$AQ$25 | ROLL!$J$26:$T$26 | ROLL!$U$26:$AQ$26
Roma 33kV BSP (132/33kV) | Bulk Supply | 97.8 | 97.8 | 97.8 | 97.8 | 97.8 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | Roma 33kV BSP | T083 | 'T083'!$I$23:$S$23 | 'T083'!$T$23:$AQ$23 | 'T083'!$I$24:$S$24 | 'T083'!$T$24:$AQ$24
Roma 66kV BSP (132/66kV) | Bulk Supply | 101.4 | 101.4 | 101.4 | 101.4 | 101.4 | 119.6 | 119.6 | 119.6 | 119.6 | 119.6 | Roma 66kV BSP | ROMA | ROMA!$I$23:$S$23 | ROMA!$T$23:$AQ$23 | ROMA!$I$24:$S$24 | ROMA!$T$24:$AQ$24
Roma East (33/11kV) | Zone Substation | 14 | 14 | 14 | 14 | 14 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | Roma East | ROEA | ROEA!$J$25:$T$25 | ROEA!$U$25:$AQ$25 | ROEA!$J$26:$T$26 | ROEA!$U$26:$AQ$26
Roma West (33/11kV) | Zone Substation | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | Roma West | ROWE | ROWE!$J$25:$T$25 | ROWE!$U$25:$AQ$25 | ROWE!$J$26:$T$26 | ROWE!$U$26:$AQ$26
Roo Works (33/11kV) | Zone Substation | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | Roo Works | ROWO | ROWO!$J$25:$T$25 | ROWO!$U$25:$AQ$25 | ROWO!$J$26:$T$26 | ROWO!$U$26:$AQ$26
Rosella (33/11kV) | Zone Substation | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 12.3 | 12.3 | 12.3 | 12.3 | 12.3 | Rosella | ROSE | ROSE!$J$25:$T$25 | ROSE!$U$25:$AQ$25 | ROSE!$J$26:$T$26 | ROSE!$U$26:$AQ$26
Ross Plains (66/11kV) | Zone Substation | 33 | 33 | 33 | 33 | 33 | 37.8 | 37.8 | 37.8 | 37.8 | 37.8 | Ross Plains | ROPL | ROPL!$J$25:$T$25 | ROPL!$U$25:$AQ$25 | ROPL!$J$26:$T$26 | ROPL!$U$26:$AQ$26
Sarina (33/11kV) | Zone Substation | 24 | 24 | 24 | 24 | 24 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | Sarina | SARI | SARI!$J$25:$T$25 | SARI!$U$25:$AQ$25 | SARI!$J$26:$T$26 | SARI!$U$26:$AQ$26
Saunders (66/11kV) | Zone Substation | 5.1 | 5.1 | 5.1 | 5.1 | 5.1 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | Saunders | SAUN | SAUN!$J$25:$T$25 | SAUN!$U$25:$AQ$25 | SAUN!$J$26:$T$26 | SAUN!$U$26:$AQ$26
Shutehaven (66/22kV) | Zone Substation | 30.4 | 30.4 | 30.4 | 30.4 | 30.4 | 33.2 | 33.2 | 33.2 | 33.2 | 33.2 | Shutehaven | SHUT | SHUT!$J$25:$T$25 | SHUT!$U$25:$AQ$25 | SHUT!$J$26:$T$26 | SHUT!$U$26:$AQ$26
South Blackwater (66/22kV) | Zone Substation | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | South Blackwater | SOBL | SOBL!$J$25:$T$25 | SOBL!$U$25:$AQ$25 | SOBL!$J$26:$T$26 | SOBL!$U$26:$AQ$26
South Bundaberg (66/11kV) | Zone Substation | 42.4 | 42.4 | 42.4 | 42.4 | 42.4 | 46.6 | 46.6 | 46.6 | 46.6 | 46.6 | South Bundaberg | SOBU | SOBU!$J$25:$T$25 | SOBU!$U$25:$AQ$25 | SOBU!$J$26:$T$26 | SOBU!$U$26:$AQ$26
South Kolan (66/11kV) | Zone Substation | 27.5 | 27.5 | 27.5 | 27.5 | 27.5 | 29.9 | 29.9 | 29.9 | 29.9 | 29.9 | South Kolan | SOKO | SOKO!$J$25:$T$25 | SOKO!$U$25:$AQ$25 | SOKO!$J$26:$T$26 | SOKO!$U$26:$AQ$26
South Mackay (33/11kV) | Zone Substation | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | South Mackay | SOMA | SOMA!$J$25:$T$25 | SOMA!$U$25:$AQ$25 | SOMA!$J$26:$T$26 | SOMA!$U$26:$AQ$26
South Toowoomba (33/11kV) | Zone Substation | 37.4 | 37.4 | 37.4 | 37.4 | 37.4 | 42.4 | 42.4 | 42.4 | 42.4 | 42.4 | South Toowoomba | SOTO | SOTO!$J$25:$T$25 | SOTO!$U$25:$AQ$25 | SOTO!$J$26:$T$26 | SOTO!$U$26:$AQ$26
South Toowoomba BSP (110/33kV) | Bulk Supply | 144.9 | 144.9 | 144.9 | 144.9 | 144.9 | 163.6 | 163.6 | 163.6 | 163.6 | 163.6 | South Toowoomba BSP | T043 | 'T043'!$I$23:$S$23 | 'T043'!$T$23:$AQ$23 | 'T043'!$I$24:$S$24 | 'T043'!$T$24:$AQ$24
St. George (66/33kV) | Zone Substation | 48.7 | 48.7 | 48.7 | 48.7 | 48.7 | 55.9 | 55.9 | 55.9 | 55.9 | 55.9 | St. George | SAGE | SAGE!$J$25:$T$25 | SAGE!$U$25:$AQ$25 | SAGE!$J$26:$T$26 | SAGE!$U$26:$AQ$26
St. George Town (33/11kV) | Zone Substation | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | 6.6 | St. George Town | SAGT | SAGT!$J$25:$T$25 | SAGT!$U$25:$AQ$25 | SAGT!$J$26:$T$26 | SAGT!$U$26:$AQ$26
Stamford (66/33kV) | Zone Substation | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | Stamford | STAM | STAM!$J$25:$T$25 | STAM!$U$25:$AQ$25 | STAM!$J$26:$T$26 | STAM!$U$26:$AQ$26
Stanthorpe BSP (110/33kV) | Bulk Supply | 71.3 | 71.3 | 71.3 | 71.3 | 71.3 | 80.4 | 80.4 | 80.4 | 80.4 | 80.4 | Stanthorpe BSP | STAN | STAN!$I$23:$S$23 | STAN!$T$23:$AQ$23 | STAN!$I$24:$S$24 | STAN!$T$24:$AQ$24
Stanthorpe Town (33/11kV) | Zone Substation | 27.1 | 27.1 | 27.1 | 27.1 | 27.1 | 29.2 | 29.2 | 29.2 | 29.2 | 29.2 | Stanthorpe Town | STTO | STTO!$J$25:$T$25 | STTO!$U$25:$AQ$25 | STTO!$J$26:$T$26 | STTO!$U$26:$AQ$26
Stuart (66/11kV) | Zone Substation | 76.7 | 76.7 | 76.7 | 76.7 | 76.7 | 81.6 | 81.6 | 81.6 | 81.6 | 81.6 | Stuart | STUA | STUA!$J$25:$T$25 | STUA!$U$25:$AQ$25 | STUA!$J$26:$T$26 | STUA!$U$26:$AQ$26
Tanby (66/22kV) | Zone Substation | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 56.6 | 56.6 | 56.6 | 56.6 | 56.6 | Tanby | TANB | TANB!$J$25:$T$25 | TANB!$U$25:$AQ$25 | TANB!$J$26:$T$26 | TANB!$U$26:$AQ$26
Tara (33/11kV) | Zone Substation | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | Tara | TARA | TARA!$J$25:$T$25 | TARA!$U$25:$AQ$25 | TARA!$J$26:$T$26 | TARA!$U$26:$AQ$26
Tennyson Street (33/11kV) | Zone Substation | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | Tennyson Street | TEST | TEST!$J$25:$T$25 | TEST!$U$25:$AQ$25 | TEST!$J$26:$T$26 | TEST!$U$26:$AQ$26
Theodore (66/22kV) | Zone Substation | 16.6 | 16.6 | 16.6 | 16.6 | 16.6 | 18.2 | 18.2 | 18.2 | 18.2 | 18.2 | Theodore | THEO | THEO!$J$25:$T$25 | THEO!$U$25:$AQ$25 | THEO!$J$26:$T$26 | THEO!$U$26:$AQ$26
Tieri (66/22kV) | Zone Substation | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | Tieri | TIER | TIER!$J$25:$T$25 | TIER!$U$25:$AQ$25 | TIER!$J$26:$T$26 | TIER!$U$26:$AQ$26
Toowoomba Central (110/11kV) | Zone Substation | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | Toowoomba Central | TWCE | TWCE!$J$25:$T$25 | TWCE!$U$25:$AQ$25 | TWCE!$J$26:$T$26 | TWCE!$U$26:$AQ$26
Torquay (66/11kV) | Zone Substation | 91.1 | 91.1 | 91.1 | 91.1 | 91.1 | 99 | 99 | 99 | 99 | 99 | Torquay | TORQ | TORQ!$J$25:$T$25 | TORQ!$U$25:$AQ$25 | TORQ!$J$26:$T$26 | TORQ!$U$26:$AQ$26
Torrington (33/11kV) | Zone Substation | 56.7 | 56.7 | 56.7 | 56.7 | 56.7 | 67.5 | 67.5 | 67.5 | 67.5 | 67.5 | Torrington | TORR | TORR!$J$25:$T$25 | TORR!$U$25:$AQ$25 | TORR!$J$26:$T$26 | TORR!$U$26:$AQ$26
Torrington BSP (110/33kV) | Bulk Supply | 239 | 239 | 239 | 239 | 239 | 286.2 | 286.2 | 286.2 | 286.2 | 286.2 | Torrington BSP | T116 | 'T116'!$I$23:$S$23 | 'T116'!$T$23:$AQ$23 | 'T116'!$I$24:$S$24 | 'T116'!$T$24:$AQ$24
Townsville Port (66/11kV) | Zone Substation | 83.2 | 83.2 | 83.2 | 83.2 | 83.2 | 83.2 | 83.2 | 83.2 | 83.2 | 83.2 | Townsville Port | TOPO | TOPO!$J$25:$T$25 | TOPO!$U$25:$AQ$25 | TOPO!$J$26:$T$26 | TOPO!$U$26:$AQ$26
Tuan (66/11kV) | Zone Substation | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | Tuan | TUAN | TUAN!$J$25:$T$25 | TUAN!$U$25:$AQ$25 | TUAN!$J$26:$T$26 | TUAN!$U$26:$AQ$26
Vermont (66/22kV) | Zone Substation | 22.1 | 22.1 | 22.1 | 22.1 | 22.1 | 24.3 | 24.3 | 24.3 | 24.3 | 24.3 | Vermont | VERM | VERM!$J$25:$T$25 | VERM!$U$25:$AQ$25 | VERM!$J$26:$T$26 | VERM!$U$26:$AQ$26
Wallaville (66/11kV) | Zone Substation | 25.6 | 25.6 | 25.6 | 25.6 | 25.6 | 27 | 27 | 27 | 27 | 27 | Wallaville | WALL | WALL!$J$25:$T$25 | WALL!$U$25:$AQ$25 | WALL!$J$26:$T$26 | WALL!$U$26:$AQ$26
Wandoan (33/22kV) | Zone Substation | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 14.5 | 14.5 | 14.5 | 14.5 | 14.5 | Wandoan | WAND | WAND!$J$25:$T$25 | WAND!$U$25:$AQ$25 | WAND!$J$26:$T$26 | WAND!$U$26:$AQ$26
Warwick BSP (110/33kV) | Bulk Supply | 118.5 | 118.5 | 118.5 | 118.5 | 118.5 | 135.6 | 135.6 | 135.6 | 135.6 | 135.6 | Warwick BSP | T058 | 'T058'!$I$23:$S$23 | 'T058'!$T$23:$AQ$23 | 'T058'!$I$24:$S$24 | 'T058'!$T$24:$AQ$24
Warwick East (33/11kV) | Zone Substation | 69.6 | 69.6 | 69.6 | 69.6 | 69.6 | 79.2 | 79.2 | 79.2 | 79.2 | 79.2 | Warwick East | WAEA | WAEA!$J$25:$T$25 | WAEA!$U$25:$AQ$25 | WAEA!$J$26:$T$26 | WAEA!$U$26:$AQ$26
West Bundaberg (66/11kV) | Zone Substation | 61.3 | 61.3 | 61.3 | 61.3 | 61.3 | 65 | 65 | 65 | 65 | 65 | West Bundaberg | WEBU | WEBU!$J$25:$T$25 | WEBU!$U$25:$AQ$25 | WEBU!$J$26:$T$26 | WEBU!$U$26:$AQ$26
West Dalby (33/11kV) | Zone Substation | 14.6 | 14.6 | 14.6 | 14.6 | 14.6 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | West Dalby | WEDA | WEDA!$J$25:$T$25 | WEDA!$U$25:$AQ$25 | WEDA!$J$26:$T$26 | WEDA!$U$26:$AQ$26
West Mackay (33/11kV) | Zone Substation | 38.7 | 38.7 | 38.7 | 38.7 | 38.7 | 40.9 | 40.9 | 40.9 | 40.9 | 40.9 | West Mackay | WEMA | WEMA!$J$25:$T$25 | WEMA!$U$25:$AQ$25 | WEMA!$J$26:$T$26 | WEMA!$U$26:$AQ$26
West Toowoomba (33/11kV) | Zone Substation | 30 | 30 | 30 | 30 | 30 | 36.2 | 36.2 | 36.2 | 36.2 | 36.2 | West Toowoomba | WETO | WETO!$J$25:$T$25 | WETO!$U$25:$AQ$25 | WETO!$J$26:$T$26 | WETO!$U$26:$AQ$26
West Warwick (33/11kV) | Zone Substation | 27 | 27 | 27 | 27 | 27 | 30 | 30 | 30 | 30 | 30 | West Warwick | WEWA | WEWA!$J$25:$T$25 | WEWA!$U$25:$AQ$25 | WEWA!$J$26:$T$26 | WEWA!$U$26:$AQ$26
Winton (66/11kV) | Zone Substation | 9.4 | 9.4 | 9.4 | 9.4 | 9.4 | 10.9 | 10.9 | 10.9 | 10.9 | 10.9 | Winton | WINT | WINT!$J$25:$T$25 | WINT!$U$25:$AQ$25 | WINT!$J$26:$T$26 | WINT!$U$26:$AQ$26
Wirralie (66/33kV) | Zone Substation | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | Wirralie | WIRR | WIRR!$J$25:$T$25 | WIRR!$U$25:$AQ$25 | WIRR!$J$26:$T$26 | WIRR!$U$26:$AQ$26
Woodgate (66/11kV) | Zone Substation | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | Woodgate | WOOG | WOOG!$J$25:$T$25 | WOOG!$U$25:$AQ$25 | WOOG!$J$26:$T$26 | WOOG!$U$26:$AQ$26
Woodhouse Station (66/11kV) | Zone Substation | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | Woodhouse Station | WOOD | WOOD!$J$25:$T$25 | WOOD!$U$25:$AQ$25 | WOOD!$J$26:$T$26 | WOOD!$U$26:$AQ$26
Woodstock South (66/11kV) | Zone Substation | 8.6 | 8.6 | 8.6 | 8.6 | 8.6 | 9.4 | 9.4 | 9.4 | 9.4 | 9.4 | Woodstock South | WOSO | WOSO!$J$25:$T$25 | WOSO!$U$25:$AQ$25 | WOSO!$J$26:$T$26 | WOSO!$U$26:$AQ$26
Woolooga (66/11kV) | Zone Substation | 17.7 | 17.7 | 17.7 | 17.7 | 17.7 | 18.7 | 18.7 | 18.7 | 18.7 | 18.7 | Woolooga | WOOL | WOOL!$J$25:$T$25 | WOOL!$U$25:$AQ$25 | WOOL!$J$26:$T$26 | WOOL!$U$26:$AQ$26
Wowan (66/22kV) | Zone Substation | 16.1 | 16.1 | 16.1 | 16.1 | 16.1 | 18 | 18 | 18 | 18 | 18 | Wowan | WOWA | WOWA!$J$25:$T$25 | WOWA!$U$25:$AQ$25 | WOWA!$J$26:$T$26 | WOWA!$U$26:$AQ$26
Yarraman (66/11kV) | Zone Substation | 15.5 | 15.5 | 15.5 | 15.5 | 15.5 | 17.9 | 17.9 | 17.9 | 17.9 | 17.9 | Yarraman | YARR | YARR!$J$25:$T$25 | YARR!$U$25:$AQ$25 | YARR!$J$26:$T$26 | YARR!$U$26:$AQ$26
Yarranlea BSP (110/33kV) | Bulk Supply | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | Yarranlea BSP | YARA | YARA!$I$23:$S$23 | YARA!$T$23:$AQ$23 | YARA!$I$24:$S$24 | YARA!$T$24:$AQ$24
Yarranlea South (33/11kV) | Zone Substation | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | Yarranlea South | YASO | YASO!$J$25:$T$25 | YASO!$U$25:$AQ$25 | YASO!$J$26:$T$26 | YASO!$U$26:$AQ$26
Yeppoon (66/11kV) | Zone Substation | 59 | 59 | 59 | 59 | 59 | 67.8 | 67.8 | 67.8 | 67.8 | 67.8 | Yeppoon | YEPP | YEPP!$J$25:$T$25 | YEPP!$U$25:$AQ$25 | YEPP!$J$26:$T$26 | YEPP!$U$26:$AQ$26

## AGWA
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | AGWA - Agnes Water (66/22kV) | [8 empty] | Supply |  | T166 - Granite Creek BSP
| Description |  |  |  | Region is Capricornia
Transformer size is 2x66/22kV 15/20MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.2%, 2021 S 0.2% W 0.2%, 2022 S 0.0% W 0.0%, 2023 S 0.2% W 0.2%, 2024 S -0.1% W -0.1
|  |  | Latest Peak Compensated Load | [5 empty] | 5 MVA on 02/01/2020 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 48 | 48 | 48 |  | 48 |  | 48 | 55.6 |  | 55.6 |  | 55.6 | 55.6 | 55.6
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 5.1 | 5.1 | 5.1 |  | 5.1 |  | 5.2 | 4.3 |  | 4.3 |  | 4.2 | 4.2 | 4.2
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.997 | 0.997 | 0.997 |  | 0.997 |  | 0.997 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | ECC Rating (MVA) |  | 24 | 24 | 24 |  | 24 |  | 24 | 27.8 |  | 27.8 |  | 27.8 | 27.8 | 27.8
|  |  |  | 50 PoE Load (MVA) |  | 4.8 | 4.8 | 4.8 |  | 4.8 |  | 4.8 | 4.1 |  | 4.1 |  | 4.1 | 4.1 | 4.1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 6.5 | 6.5 | 6.5 |  | 6.5 |  | 6.5 | 6.5 |  | 6.5 |  | 6.5 | 6.5 | 6.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 2.5 | 2.5 | 2.5 |  | 2.5 |  | 2.5 | 2.5 |  | 2.5 |  | 2.5 | 2.5 | 2.5
|  |  |  | Mobile Plant Avail (MVA) |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## AITK
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | AITK - Aitkenvale (66/11kV) | [8 empty] | Supply |  | TMES - Townsville Mesh
| Description |  |  |  | Region is Nth Queensland
Transformer size is 2x66/11kV 15/20/25MVA ONAN/ONAF/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.1%, 2021 S -0.2% W -0.2%2022 S -0.5% W -0.5%2023 S -0.3% W -0.3%2024 S -0.4% W -0.4
|  |  | Latest Peak Compensated Load | [5 empty] | 20.6 MVA on 11/02/2020 at 16:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 61.6 | 61.6 | 61.6 |  | 61.6 |  | 61.6 | 64.7 |  | 64.7 |  | 64.7 | 64.7 | 64.7
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 23.2 | 23.1 | 23 |  | 23 |  | 23 | 12.8 |  | 12.7 |  | 12.6 | 12.5 | 12.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | ECC Rating (MVA) |  | 34.3 | 34.3 | 34.3 |  | 34.3 |  | 34.3 | 35.8 |  | 35.8 |  | 35.8 | 35.8 | 35.8
|  |  |  | 50 PoE Load (MVA) |  | 20.4 | 20.3 | 20.2 |  | 20.2 |  | 20.2 | 12.3 |  | 12.3 |  | 12.1 | 12.3 | 12.3
|  |  |  | 50 PoE Load > 95% (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  |  | Hours PA > 95% Peak Load |  | 8 | 8 | 8 |  | 8 |  | 8 | 8 |  | 8 |  | 8 | 8 | 8
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## ALLO
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | ALLO - Allora (33/11kV) | [8 empty] | Supply |  | T058 - Warwick BSP
| Description |  |  |  | Region is South West
Transformer size is 2x33/11kV 3MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.0%, 2021 S 0.4% W 0.4%, 2022 S 0.2% W 0.2%, 2023 S 0.4% W 0.4%, 2024 S 0.1% W 0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 4.7 MVA on 05/01/2020 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 7.3 | 7.3 | 7.3 |  | 7.3 |  | 7.3 | 7.9 |  | 7.9 |  | 7.9 | 7.9 | 7.9
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 5.3 | 5.3 | 5.3 |  | 5.4 |  | 5.4 | 4.7 |  | 4.7 |  | 4.7 | 4.7 | 4.7
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.928 | 0.928 | 0.928 |  | 0.928 |  | 0.928 | 0.963 |  | 0.963 |  | 0.963 | 0.963 | 0.963
|  |  |  | ECC Rating (MVA) |  | 4.2 | 4.2 | 4.2 |  | 4.2 |  | 4.2 | 4.4 |  | 4.4 |  | 4.4 | 4.4 | 4.4
|  |  |  | 50 PoE Load (MVA) |  | 4.7 | 4.7 | 4.7 |  | 4.8 |  | 4.8 | 4.5 |  | 4.5 |  | 4.5 | 4.5 | 4.5
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 6 | 6 | 6 |  | 6 |  | 6 | 6 |  | 6 |  | 6 | 6 | 6
|  |  |  | Raw LAR (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.6 |  | 0.6 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## ALSH
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | ALSH - Alan Sherriff (132/11kV) | [8 empty] | Supply |  | QASF - Alan Sherriff TCP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 2x132/11kV 18/22.5/30MVA ONAN/OFAF/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.0%, 2021 S -0.2% W -0.2%2022 S -0.4% W -0.4%2023 S -0.2% W -0.2%2024 S -0.4% W -0.4
|  |  | Latest Peak Compensated Load | [5 empty] | 29 MVA on 12/02/2020 at 17:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 70 | 70 | 70 |  | 70 |  | 70 | 73.5 |  | 73.5 |  | 73.5 | 73.5 | 73.5
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 35.2 | 35.1 | 35.1 |  | 35.1 |  | 35.1 | 16.8 |  | 16.7 |  | 16.5 | 16.4 | 16.4
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.964 | 0.964 | 0.964 |  | 0.964 |  | 0.964 | 0.978 |  | 0.978 |  | 0.978 | 0.978 | 0.978
|  |  |  | ECC Rating (MVA) |  | 38.5 | 38.5 | 38.5 |  | 38.5 |  | 38.5 | 40.3 |  | 40.3 |  | 40.3 | 40.3 | 40.3
|  |  |  | 50 PoE Load (MVA) |  | 29.7 | 29.6 | 29.5 |  | 29.6 |  | 29.6 | 16.5 |  | 16.4 |  | 16.3 | 16.2 | 16.2
|  |  |  | 50 PoE Load > 95% (MVA) |  | 1.5 | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 0.8 |  | 0.8 |  | 0.8 | 0.8 | 0.8
|  |  |  | Hours PA > 95% Peak Load |  | 12.5 | 12.5 | 12.5 |  | 12.5 |  | 12.5 | 12.5 |  | 12.5 |  | 12.5 | 12.5 | 12.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## ALST
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | ALST - Alfred Street (33/11kV) | [8 empty] | Supply |  | MACK - Mackay BSP
| Description |  |  |  | Region is Mackay
Transformer size is 2x33/11kV 35/40MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.8%, 2021 S -0.4% W -0.4%2022 S -0.7% W -0.7%2023 S -0.4% W -0.4%2024 S -0.4% W -0.4
|  |  | Latest Peak Compensated Load | [5 empty] | 21.4 MVA on 05/12/2019 at 15:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 90.7 | 90.7 | 90.7 |  | 90.7 |  | 90.7 | 93.7 |  | 93.7 |  | 93.7 | 93.7 | 93.7
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 23.3 | 23.1 | 23 |  | 23 |  | 23 | 14.4 |  | 14.3 |  | 14.1 | 14 | 14
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.995 | 0.995 | 0.995 |  | 0.995 |  | 0.995 | 0.962 |  | 0.962 |  | 0.962 | 0.962 | 0.962
|  |  |  | ECC Rating (MVA) |  | 48 | 48 | 48 |  | 48 |  | 48 | 50.4 |  | 50.4 |  | 50.4 | 50.4 | 50.4
|  |  |  | 50 PoE Load (MVA) |  | 21.4 | 21.3 | 21.2 |  | 21.2 |  | 21.2 | 14 |  | 13.9 |  | 13.7 | 13.6 | 13.6
|  |  |  | 50 PoE Load > 95% (MVA) |  | 1.1 | 1.1 | 1.1 |  | 1.1 |  | 1.1 | 0.7 |  | 0.7 |  | 0.7 | 0.7 | 0.7
|  |  |  | Hours PA > 95% Peak Load |  | 18 | 18 | 18 |  | 18 |  | 18 | 18 |  | 18 |  | 18 | 18 | 18
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## ATHE
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | ATHE - Atherton (66/22kV) | [8 empty] | Supply |  | TURK - Turkinje 66kV BSP
| Description |  |  |  | Region is Far North
Transformer size is 1x66/22kV 24/30/40MVA ONAN/ODAN/ODAF;1x66/22kV 24/30/40MVA ONAN/ONAF/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 1.7 MVA
Growth Rates |  |  |  |  | 2020 W 0.5%, 2021 S 0.6% W 0.6%, 2022 S 0.5% W 0.5%, 2023 S 0.6% W 0.6%, 2024 S 0.3% W 0.3%
|  |  | Latest Peak Compensated Load | [5 empty] | 24.4 MVA on 06/06/2019 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 88.1 | 88.1 | 88.1 |  | 88.1 |  | 88.1 | 97.4 |  | 97.4 |  | 97.4 | 97.4 | 97.4
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 25.4 | 25.5 | 25.7 |  | 25.9 |  | 26.1 | 24.6 |  | 24.7 |  | 24.6 | 24.7 | 24.9
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.999 | 0.998 | 0.998 |  | 0.998 |  | 0.998 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | ECC Rating (MVA) |  | 50.8 | 50.8 | 50.8 |  | 50.8 |  | 50.8 | 53.5 |  | 53.5 |  | 53.5 | 53.5 | 53.5
|  |  |  | 50 PoE Load (MVA) |  | 24.2 | 24.3 | 24.5 |  | 24.7 |  | 24.8 | 23.8 |  | 23.9 |  | 23.8 | 23.9 | 24.1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 1.2 | 1.2 | 1.2 |  | 1.2 |  | 1.2 | 1.2 |  | 1.2 |  | 1.2 | 1.2 | 1.2
|  |  |  | Hours PA > 95% Peak Load |  | 9 | 9 | 9 |  | 9 |  | 9 | 9 |  | 9 |  | 9 | 9 | 9
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## AWOO
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | AWOO - Awoonga (66/11kV) | [8 empty] | Supply |  | T019 - Gladstone South BSP
| Description |  |  |  | Region is Capricornia
Transformer size is 2x66/11kV 7.5/10MVA ON/OB
Capacity of commissioned Embedded Generation (with Connection Agreements) is 1.1 MVA
Growth Rates |  |  |  |  | 2020 W 0.2%, 2021 S 0.1% W 0.1%, 2022 S -0.0% W -0.0%2023 S 0.2% W 0.2%, 2024 S -0.1% W -0.1
|  |  | Latest Peak Compensated Load | [5 empty] | 7.2 MVA on 15/03/2020 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 24.4 | 24.4 | 24.4 |  | 24.4 |  | 24.4 | 25.7 |  | 25.7 |  | 25.7 | 25.7 | 25.7
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 7.5 | 7.5 | 7.5 |  | 7.5 |  | 7.6 | 6.1 |  | 6.1 |  | 6 | 6 | 6
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.969 | 0.969 | 0.969 |  | 0.969 |  | 0.969 | 0.954 |  | 0.954 |  | 0.954 | 0.954 | 0.954
|  |  |  | ECC Rating (MVA) |  | 14 | 14 | 14 |  | 14 |  | 14 | 14.5 |  | 14.5 |  | 14.5 | 14.5 | 14.5
|  |  |  | 50 PoE Load (MVA) |  | 7.3 | 7.3 | 7.3 |  | 7.4 |  | 7.4 | 5.9 |  | 5.9 |  | 5.9 | 5.9 | 5.9
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.4 | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Hours PA > 95% Peak Load |  | 8 | 8 | 8 |  | 8 |  | 8 | 8 |  | 8 |  | 8 | 8 | 8
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## AYRZ
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | AYRZ - Ayr (66/11kV) | [8 empty] | Supply |  | T193 - Clare South BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/11kV 7.5/10MVA ON/OB;1x66/11kV 7.5/10MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.0%, 2021 S -0.1% W -0.1%2022 S -0.2% W -0.2%2023 S 0.0% W 0.0%, 2024 S -0.2% W -0.2
|  |  | Latest Peak Compensated Load | [5 empty] | 10.7 MVA on 16/12/2019 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 23.9 | 23.9 | 23.9 |  | 23.9 |  | 23.9 | 25.4 |  | 25.4 |  | 25.4 | 25.4 | 25.4
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 10.1 | 10.1 | 10.1 |  | 10.1 |  | 10.1 | 4.9 |  | 4.8 |  | 4.8 | 4.8 | 4.8
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.988 | 0.988 | 0.988 |  | 0.988 |  | 0.988 | 0.916 |  | 0.916 |  | 0.916 | 0.916 | 0.916
|  |  |  | ECC Rating (MVA) |  | 13.6 | 13.6 | 13.6 |  | 13.6 |  | 13.6 | 14.2 |  | 14.2 |  | 14.2 | 14.2 | 14.2
|  |  |  | 50 PoE Load (MVA) |  | 9.8 | 9.8 | 9.8 |  | 9.8 |  | 9.8 | 4.8 |  | 4.8 |  | 4.7 | 4.7 | 4.7
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 8.5 | 8.5 | 8.5 |  | 8.5 |  | 8.5 | 8.5 |  | 8.5 |  | 8.5 | 8.5 | 8.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## BALB
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | BALB - Balberra (33/11kV) | [8 empty] | Supply |  | T065 - Alligator Creek BSP
| Description |  |  |  | Region is Mackay
Transformer size is 1x33/11kV 5MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.2%, 2021 S 0.1% W 0.1%, 2022 S 0.0% W 0.0%, 2023 S 0.1% W 0.1%, 2024 S 0.0% W 0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 3 MVA on 14/12/2019 at 19:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 7 | 7 | 7 |  | 7 |  | 7 | 7.5 |  | 7.5 |  | 7.5 | 7.5 | 7.5
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 3.1 | 3.1 | 3.1 |  | 3.1 |  | 3.1 | 1.6 |  | 1.6 |  | 1.6 | 1.5 | 1.6
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.937 | 0.937 | 0.937 |  | 0.937 |  | 0.937 | 0.951 |  | 0.951 |  | 0.951 | 0.951 | 0.951
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 3 | 3 | 3 |  | 3 |  | 3 | 1.4 |  | 1.4 |  | 1.4 | 1.4 | 1.4
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 3 | 3 | 3 |  | 3 |  | 3 | 3 |  | 3 |  | 3 | 3 | 3
|  |  |  | Raw LAR (MVA) |  | 3 | 3 | 3 |  | 3 |  | 3 | 1.4 |  | 1.4 |  | 1.4 | 1.4 | 1.4
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 1.9 | 1.9 | 1.9 |  | 1.9 |  | 1.9 | 1.9 |  | 1.9 |  | 1.9 | 1.9 | 1.9
|  |  |  | Mobile Plant Avail (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 | 2 | 2
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## BAMB
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | BAMB - Bambaroo (66/11kV) | [8 empty] | Supply |  | T047 - Ingham BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/11kV 1.5MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.2%, 2021 S -0.3% W -0.3%2022 S -0.3% W -0.3%2023 S -0.3% W -0.3%2024 S -0.4% W -0.4
|  |  | Latest Peak Compensated Load | [5 empty] | 0.6 MVA on 14/11/2019 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 2.2 | 2.2 | 2.2 |  | 2.2 |  | 2.2 | 2.2 |  | 2.2 |  | 2.2 | 2.2 | 2.2
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 0.7 | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.909 | 0.909 | 0.909 |  | 0.909 |  | 0.909 | 0.902 |  | 0.902 |  | 0.902 | 0.902 | 0.902
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 22 | 22 | 22 |  | 22 |  | 22 | 22 |  | 22 |  | 22 | 22 | 22
|  |  |  | Raw LAR (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## BARC
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | BARC - Barcaldine (66/22kV) | [8 empty] | Supply |  | T072 - Barcaldine BSP
| Description |  |  |  | Region is Capricornia
Transformer size is 2x66/22kV 8/10MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 28.4 MVA
Growth Rates |  |  |  |  | 2020 W -0.7%, 2021 S -0.3% W -0.3%2022 S -0.3% W -0.3%2023 S -0.2% W -0.2%2024 S -0.4% W -0.4
|  |  | Latest Peak Compensated Load | [5 empty] | 7.5 MVA on 17/12/2019 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 25.8 | 25.8 | 25.8 |  | 25.8 |  | 25.8 | 30 |  | 30 |  | 30 | 30 | 30
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 7.9 | 7.9 | 7.9 |  | 7.9 |  | 7.9 | 5.8 |  | 5.8 |  | 5.7 | 5.7 | 5.7
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 1 | 1 | 1 |  | 1 |  | 1 | 0.993 |  | 0.993 |  | 0.993 | 0.993 | 0.993
|  |  |  | ECC Rating (MVA) |  | 14.2 | 14.2 | 14.2 |  | 14.2 |  | 14.2 | 15 |  | 15 |  | 15 | 15 | 15
|  |  |  | 50 PoE Load (MVA) |  | 7.3 | 7.3 | 7.3 |  | 7.3 |  | 7.2 | 5.5 |  | 5.5 |  | 5.4 | 5.4 | 5.4
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.4 | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Hours PA > 95% Peak Load |  | 196 | 196 | 196 |  | 196 |  | 196 | 196 |  | 196 |  | 196 | 196 | 196
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## BARG
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | BARG - Bargara (66/11kV) | [8 empty] | Supply |  | BUND - Bundaberg BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 2x66/11kV 15/18/25MVA ONAN/ODAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 1.9%, 2021 S 1.4% W 1.4%, 2022 S 1.2% W 1.2%, 2023 S 1.3% W 1.3%, 2024 S 1.0% W 1.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 14.3 MVA on 16/02/2020 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 69.9 | 69.9 | 69.9 |  | 69.9 |  | 69.9 | 74.8 |  | 74.8 |  | 74.8 | 74.8 | 74.8
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 15.2 | 15.2 | 15.4 |  | 15.6 |  | 15.8 | 13.3 |  | 13.5 |  | 13.6 | 13.7 | 13.9
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.986 | 1 | 1 |  | 1 |  | 1 | 0.993 |  | 0.993 |  | 0.993 | 0.993 | 0.993
|  |  |  | ECC Rating (MVA) |  | 37.4 | 37.4 | 37.4 |  | 37.4 |  | 37.4 | 37.4 |  | 37.4 |  | 37.4 | 37.4 | 37.4
|  |  |  | 50 PoE Load (MVA) |  | 14.1 | 14.3 | 14.5 |  | 14.7 |  | 15 | 12.7 |  | 12.8 |  | 12.9 | 13 | 13.2
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.7 | 0.7 | 0.7 |  | 0.7 |  | 0.8 | 0.6 |  | 0.6 |  | 0.6 | 0.7 | 0.7
|  |  |  | Hours PA > 95% Peak Load |  | 6.5 | 6.5 | 6.5 |  | 6.5 |  | 6.5 | 6.5 |  | 6.5 |  | 6.5 | 6.5 | 6.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## BARR
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | BARR - Barratta (66/11kV) | [8 empty] | Supply |  | T193 - Clare South BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1xBARR TX NO 1-66/11KV TRANSF 1
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.0%, 2021 S -0.1% W -0.1%2022 S -0.2% W -0.2%2023 S -0.0% W -0.0%2024 S -0.2% W -0.2
|  |  | Latest Peak Compensated Load | [5 empty] | 3 MVA on 05/12/2019 at 08:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 4 | 4 | 4 |  | 4 |  | 4 | 4 |  | 4 |  | 4 | 4 | 4
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 3 | 3 | 3 |  | 3 |  | 3 | 1.3 |  | 1.3 |  | 1.3 | 1.3 | 1.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.854 | 0.854 | 0.854 |  | 0.854 |  | 0.854 | 0.861 |  | 0.861 |  | 0.861 | 0.861 | 0.871
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 2.9 | 2.9 | 2.9 |  | 2.9 |  | 2.9 | 1.3 |  | 1.3 |  | 1.3 | 1.2 | 1.3
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 6 | 6 | 6 |  | 6 |  | 6 | 6 |  | 6 |  | 6 | 6 | 6
|  |  |  | Raw LAR (MVA) |  | 2.9 | 2.9 | 2.9 |  | 2.9 |  | 2.9 | 1.3 |  | 1.3 |  | 1.3 | 1.2 | 1.3
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | Mobile Plant Avail (MVA) |  | 2.4 | 2.4 | 2.4 |  | 2.4 |  | 2.4 | 2.4 |  | 2.4 |  | 2.4 | 2.4 | 2.4
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## BEGA
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | BEGA - Belgian Gardens (66/11kV) | [8 empty] | Supply |  | TMES - Townsville Mesh
| Description |  |  |  | Region is Nth Queensland
Transformer size is 2x66/11kV 19/26/32MVA ONAN/ODAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 1.0%, 2021 S 0.8% W 0.8%, 2022 S 0.7% W 0.7%, 2023 S 0.8% W 0.8%, 2024 S 0.6% W 0.6%
|  |  | Latest Peak Compensated Load | [5 empty] | 14.5 MVA on 11/02/2020 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 73.9 | 73.9 | 73.9 |  | 73.9 |  | 73.9 | 76.6 |  | 76.6 |  | 76.6 | 76.6 | 76.6
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 16.2 | 16.3 | 16.5 |  | 16.6 |  | 16.8 | 8.7 |  | 8.8 |  | 8.8 | 8.8 | 8.9
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.992 | 0.992 | 0.992 |  | 0.992 |  | 0.992 | 0.995 |  | 0.995 |  | 0.995 | 0.995 | 0.995
|  |  |  | ECC Rating (MVA) |  | 40.9 | 40.9 | 40.9 |  | 40.9 |  | 40.9 | 42.2 |  | 42.2 |  | 42.2 | 42.2 | 42.2
|  |  |  | 50 PoE Load (MVA) |  | 14.5 | 14.6 | 14.7 |  | 14.9 |  | 15 | 8.6 |  | 8.6 |  | 8.6 | 8.6 | 8.7
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.7 | 0.7 | 0.7 |  | 0.7 |  | 0.8 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  |  | Hours PA > 95% Peak Load |  | 10.5 | 10.5 | 10.5 |  | 10.5 |  | 10.5 | 10.5 |  | 10.5 |  | 10.5 | 10.5 | 10.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## BERS
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | BERS - Berserker (66/11kV) | [8 empty] | Supply |  | RMES - Rockhampton Mesh
| Description |  |  |  | Region is Capricornia
Transformer size is 2x66/11kV 19/26/32MVA ONAN/ODAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.2%, 2021 S -0.2% W -0.2%2022 S -0.5% W -0.5%2023 S -0.3% W -0.3%2024 S -0.3% W -0.3
|  |  | Latest Peak Compensated Load | [5 empty] | 21.4 MVA on 16/12/2019 at 16:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 78.5 | 78.5 | 78.5 |  | 78.5 |  | 78.5 | 88 |  | 88 |  | 88 | 88 | 88
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 23.7 | 23.6 | 23.5 |  | 23.6 |  | 23.6 | 11.1 |  | 11 |  | 10.9 | 10.8 | 10.8
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 1 | 1 | 1 |  | 1 |  | 1 | 0.999 |  | 0.999 |  | 0.999 | 0.999 | 0.999
|  |  |  | ECC Rating (MVA) |  | 42.7 | 42.7 | 42.7 |  | 42.7 |  | 42.7 | 46.5 |  | 46.5 |  | 46.5 | 46.5 | 46.5
|  |  |  | 50 PoE Load (MVA) |  | 21.5 | 21.4 | 21.4 |  | 21.4 |  | 21.4 | 10.7 |  | 10.7 |  | 10.5 | 10.5 | 10.5
|  |  |  | 50 PoE Load > 95% (MVA) |  | 1.1 | 1.1 | 1.1 |  | 1.1 |  | 1.1 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | Hours PA > 95% Peak Load |  | 7.5 | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 | 7.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## BEWE
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | BEWE - Bedford Weir (66/22kV) | [8 empty] | Supply |  | T032 - Blackwater BSP
| Description |  |  |  | Region is Capricornia
Transformer size is 1x66/22kV 10MVA ONAN;1x66/22kV 7.5/10MVA ON/OB
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.5%, 2021 S -0.2% W -0.2%2022 S -0.4% W -0.4%2023 S -0.1% W -0.1%2024 S -0.5% W -0.5
|  |  | Latest Peak Compensated Load | [5 empty] | 7.6 MVA on 20/11/2019 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 20.9 | 20.9 | 20.9 |  | 20.9 |  | 20.9 | 23.3 |  | 23.3 |  | 23.3 | 23.3 | 23.3
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 8.7 | 8.7 | 8.7 |  | 8.7 |  | 8.6 | 6.2 |  | 6.2 |  | 6.1 | 6.1 | 6.1
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.959 | 0.959 | 0.959 |  | 0.959 |  | 0.959 | 0.959 |  | 0.959 |  | 0.959 | 0.959 | 0.959
|  |  |  | ECC Rating (MVA) |  | 12 | 12 | 12 |  | 12 |  | 12 | 12.9 |  | 12.9 |  | 12.9 | 12.9 | 12.9
|  |  |  | 50 PoE Load (MVA) |  | 8.1 | 8.1 | 8.1 |  | 8.1 |  | 8 | 6 |  | 6 |  | 5.9 | 5.9 | 5.9
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.4 | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Hours PA > 95% Peak Load |  | 12.5 | 12.5 | 12.5 |  | 12.5 |  | 12.5 | 12.5 |  | 12.5 |  | 12.5 | 12.5 | 12.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## BILO
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | BILO - Biloela (66/11kV) | [8 empty] | Supply |  | T026 - Biloela BSP
| Description |  |  |  | Region is Capricornia
Transformer size is 1x66/11kV 15/20MVA ONAN/ONAF;1x66/11kV 25/32MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -1.2%, 2021 S -0.4% W -0.4%2022 S -0.7% W -0.7%2023 S -0.5% W -0.5%2024 S -0.5% W -0.5
|  |  | Latest Peak Compensated Load | [5 empty] | 15.9 MVA on 11/12/2019 at 15:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 47.3 | 47.3 | 47.3 |  | 47.3 |  | 47.3 | 55 |  | 55 |  | 55 | 55 | 55
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 18.1 | 18 | 17.9 |  | 17.9 |  | 17.8 | 10.8 |  | 10.7 |  | 10.6 | 10.5 | 10.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.952 | 0.952 | 0.952 |  | 0.952 |  | 0.952 | 0.967 |  | 0.967 |  | 0.967 | 0.967 | 0.967
|  |  |  | ECC Rating (MVA) |  | 27.2 | 27.2 | 27.2 |  | 27.2 |  | 27.2 | 29.9 |  | 29.9 |  | 29.9 | 29.9 | 29.9
|  |  |  | 50 PoE Load (MVA) |  | 16.4 | 16.3 | 16.3 |  | 16.3 |  | 16.2 | 10.5 |  | 10.4 |  | 10.2 | 10.2 | 10.1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.8 | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | Hours PA > 95% Peak Load |  | 10.5 | 10.5 | 10.5 |  | 10.5 |  | 10.5 | 10.5 |  | 10.5 |  | 10.5 | 10.5 | 10.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 6.1 | 6.1 | 6.1 |  | 6.1 |  | 6.1 | 6.1 |  | 6.1 |  | 6.1 | 6.1 | 6.1
|  |  |  | Mobile Plant Avail (MVA) |  | 3.3 | 3.3 | 3.3 |  | 3.3 |  | 3.3 | 3.3 |  | 3.3 |  | 3.3 | 3.3 | 3.3
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 1.9 | 1.9 | 1.9 |  | 1.9 |  | 1.9 | 1.9 |  | 1.9 |  | 1.9 | 1.9 | 1.9
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## BING
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | BING - Bingegang (66/22kV) | [8 empty] | Supply |  | T032 - Blackwater BSP
| Description |  |  |  | Region is Capricornia
Transformer size is 2x66/22kV 5MVA ON
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.7%, 2021 S -0.1% W -0.1%2022 S -0.3% W -0.3%2023 S 0.1% W 0.1%, 2024 S -0.4% W -0.4
|  |  | Latest Peak Compensated Load | [5 empty] | 2 MVA on 17/11/2019 at 19:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 11 | 11 | 11 |  | 11 |  | 11 | 12 |  | 12 |  | 12 | 12 | 12
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 1.4 |  | 1.4 |  | 1.4 | 1.4 | 1.4
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.977 | 0.977 | 0.977 |  | 0.977 |  | 0.977 | 0.99 |  | 0.99 |  | 0.99 | 0.99 | 0.99
|  |  |  | ECC Rating (MVA) |  | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6 | 7.1 |  | 7.1 |  | 7.1 | 7.1 | 7.1
|  |  |  | 50 PoE Load (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 1.4 |  | 1.4 |  | 1.4 | 1.3 | 1.3
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 26.5 | 26.5 | 26.5 |  | 26.5 |  | 26.5 | 26.5 |  | 26.5 |  | 26.5 | 26.5 | 26.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## BLAC
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | BLAC - Blackwater (11/22kV) | [8 empty] | Supply |  | T032 - Blackwater BSP
| Description |  |  |  | Region is Capricornia
Transformer size is 2x11/22kV 7.5/10MVA ONAN/ONAF;2x132/22kV 160 MVA
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.4%, 2021 S -0.3% W -0.3%2022 S -0.4% W -0.4%2023 S -0.2% W -0.2%2024 S -0.5% W -0.5
|  |  | Latest Peak Compensated Load | [5 empty] | 9.6 MVA on 16/12/2019 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 20 | 20 | 20 |  | 20 |  | 20 | 22 |  | 22 |  | 22 | 22 | 22
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 11 | 11 | 11 |  | 11 |  | 10.9 | 6.9 |  | 6.9 |  | 6.8 | 6.8 | 6.8
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.974 | 0.974 | 0.974 |  | 0.974 |  | 0.974 | 0.978 |  | 0.978 |  | 0.978 | 0.978 | 0.978
|  |  |  | ECC Rating (MVA) |  | 33 | 33 | 33 |  | 33 |  | 33 | 36 |  | 36 |  | 36 | 36 | 36
|  |  |  | 50 PoE Load (MVA) |  | 10.1 | 10.1 | 10 |  | 10 |  | 10 | 6.6 |  | 6.6 |  | 6.5 | 6.5 | 6.5
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Hours PA > 95% Peak Load |  | 5.5 | 5.5 | 5.5 |  | 5.5 |  | 5.5 | 5.5 |  | 5.5 |  | 5.5 | 5.5 | 5.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## BLAK
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | BLAK - Blackall (66/22kV) | [8 empty] | Supply |  | T072 - Barcaldine BSP
| Description |  |  |  | Region is Capricornia
Transformer size is 2x66/22kV 5/6.25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.9%, 2021 S -0.3% W -0.3%2022 S -0.4% W -0.4%2023 S -0.3% W -0.3%2024 S -0.5% W -0.5
|  |  | Latest Peak Compensated Load | [5 empty] | 4.2 MVA on 17/12/2019 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 13.9 | 13.9 | 13.9 |  | 13.9 |  | 13.9 | 16.5 |  | 16.5 |  | 16.5 | 16.5 | 16.5
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 4.7 | 4.7 | 4.7 |  | 4.7 |  | 4.6 | 3.5 |  | 3.4 |  | 3.4 | 3.4 | 3.4
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.999 | 0.999 | 0.999 |  | 0.999 |  | 0.999 | 0.99 |  | 0.99 |  | 0.99 | 0.99 | 0.99
|  |  |  | ECC Rating (MVA) |  | 8.1 | 8.1 | 8.1 |  | 8.1 |  | 8.1 | 9.3 |  | 9.3 |  | 9.3 | 9.3 | 9.3
|  |  |  | 50 PoE Load (MVA) |  | 4.3 | 4.2 | 4.2 |  | 4.2 |  | 4.2 | 3.2 |  | 3.2 |  | 3.1 | 3.1 | 3.1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 3.5 | 3.5 | 3.5 |  | 3.5 |  | 3.5 | 3.5 |  | 3.5 |  | 3.5 | 3.5 | 3.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## BLRI
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | BLRI - Black River (66/11kV) | [8 empty] | Supply |  | TMES - Townsville Mesh
| Description |  |  |  | Region is Nth Queensland
Transformer size is 2x66/11kV 16/20MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 1.6%, 2021 S 2.3% W 2.3%, 2022 S 2.1% W 2.1%, 2023 S 2.1% W 2.1%, 2024 S 1.9% W 1.9%
|  |  | Latest Peak Compensated Load | [5 empty] | 23.6 MVA on 12/02/2020 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 56 | 56 | 56 |  | 56 |  | 56 | 59.1 |  | 59.1 |  | 59.1 | 59.1 | 59.1
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 26.9 | 27.5 | 28.1 |  | 28.8 |  | 29.4 | 11.6 |  | 11.8 |  | 12 | 12.2 | 12.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.996 | 0.996 | 0.996 |  | 0.996 |  | 0.996 | 0.999 |  | 0.999 |  | 0.999 | 0.999 | 0.999
|  |  |  | ECC Rating (MVA) |  | 29.9 | 29.9 | 29.9 |  | 29.9 |  | 29.9 | 29.9 |  | 29.9 |  | 29.9 | 29.9 | 29.9
|  |  |  | 50 PoE Load (MVA) |  | 23.5 | 24 | 24.5 |  | 25 |  | 25.6 | 11.5 |  | 11.7 |  | 11.9 | 12.1 | 12.4
|  |  |  | 50 PoE Load > 95% (MVA) |  | 1.2 | 1.2 | 1.2 |  | 1.3 |  | 1.3 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  |  | Hours PA > 95% Peak Load |  | 10.5 | 10.5 | 10.5 |  | 10.5 |  | 10.5 | 10.5 |  | 10.5 |  | 10.5 | 10.5 | 10.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## BLUE
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | BLUE - Bluewater (66/11kV) | [8 empty] | Supply |  | TMES - Townsville Mesh
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/11kV 5MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 1.1%, 2021 S 0.4% W 0.4%, 2022 S 0.2% W 0.2%, 2023 S 0.3% W 0.3%, 2024 S 0.1% W 0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 3.9 MVA on 11/02/2020 at 19:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 5.3 | 5.3 | 5.3 |  | 5.3 |  | 5.3 | 5.5 |  | 5.5 |  | 5.5 | 5.5 | 5.5
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 4.6 | 4.7 | 4.7 |  | 4.7 |  | 4.7 | 2.5 |  | 2.5 |  | 2.5 | 2.5 | 2.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.993 | 0.993 | 0.993 |  | 0.993 |  | 0.993 | 0.995 |  | 0.995 |  | 0.995 | 0.995 | 0.995
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 4 | 4 | 4 |  | 4.1 |  | 4.1 | 2.4 |  | 2.4 |  | 2.4 | 2.4 | 2.4
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 12 | 12 | 12 |  | 12 |  | 12 | 12 |  | 12 |  | 12 | 12 | 12
|  |  |  | Raw LAR (MVA) |  | 4 | 4 | 4 |  | 4.1 |  | 4.1 | 2.4 |  | 2.4 |  | 2.4 | 2.4 | 2.4
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 3.5 | 3.5 | 3.5 |  | 3.5 |  | 3.5 | 3.5 |  | 3.5 |  | 3.5 | 3.5 | 3.5
|  |  |  | Mobile Plant Avail (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## BODA
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | BODA - Boondooma Dam (66/11kV) | [8 empty] | Supply |  | H018 - Tarong BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 1x66/11kV 4.1MVA ONAN;1x66/11kV 1MVA ONAN(Standby)
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.0%, 2021 S 0.0% W 0.0%, 2022 S 0.0% W 0.0%, 2023 S 0.0% W 0.0%, 2024 S 0.0% W 0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 2.2 MVA on 18/07/2019 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 5.2 | 5.2 | 5.2 |  | 5.2 |  | 5.2 | 5.5 |  | 5.5 |  | 5.5 | 5.5 | 5.5
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 2.1 | 2.1 | 2.1 |  | 2.1 |  | 2.1 | 2.2 |  | 2.2 |  | 2.1 | 2.1 | 2.1
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.951 | 0.951 | 0.951 |  | 0.951 |  | 0.951 | 0.901 |  | 0.901 |  | 0.901 | 0.901 | 0.901
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 2.1 | 2.1 | 2.1 |  | 2.1 |  | 2.1 | 2.1 |  | 2.1 |  | 2.1 | 2.1 | 2.1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 2794 | 2794 | 2794 |  | 2794 |  | 2794 | 2794 |  | 2794 |  | 2794 | 2794 | 2794
|  |  |  | Raw LAR (MVA) |  | 2.1 | 2.1 | 2.1 |  | 2.1 |  | 2.1 | 2.1 |  | 2.1 |  | 2.1 | 2.1 | 2.1
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 1.1 | 1.1 | 1.1 |  | 1.1 |  | 1.1 | 1.1 |  | 1.1 |  | 1.1 | 1.1 | 1.1
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 2.1 | 2.1 | 2.1 |  | 2.1 |  | 2.1 | 2.1 |  | 2.1 |  | 2.1 | 2.1 | 2.1
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## BOHL
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | BOHL - Bohle (66/11kV) | [8 empty] | Supply |  | TMES - Townsville Mesh
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/11kV 15/20/25MVA ODAN/ONAF/ODAF;1x66/11kV 15/20/25MVA ONAN/ONAF/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.8%, 2021 S 1.2% W 1.2%, 2022 S 1.1% W 1.1%, 2023 S 1.3% W 1.3%, 2024 S 1.0% W 1.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 24.2 MVA on 11/02/2020 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 52.7 | 52.7 | 52.7 |  | 52.7 |  | 52.7 | 55.3 |  | 55.3 |  | 55.3 | 55.3 | 55.3
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 28.1 | 28.5 | 28.8 |  | 29.2 |  | 29.6 | 15.9 |  | 16 |  | 16.1 | 16.2 | 16.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.984 | 0.984 | 0.984 |  | 0.984 |  | 0.984 | 0.969 |  | 0.969 |  | 0.969 | 0.969 | 0.969
|  |  |  | ECC Rating (MVA) |  | 26.4 | 26.4 | 26.4 |  | 26.4 |  | 26.4 | 27.8 |  | 27.8 |  | 27.8 | 27.8 | 27.8
|  |  |  | 50 PoE Load (MVA) |  | 24.9 | 25.2 | 25.5 |  | 25.8 |  | 26.2 | 15.5 |  | 15.6 |  | 15.7 | 15.8 | 16.1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 1.2 | 1.3 | 1.3 |  | 1.3 |  | 1.3 | 0.8 |  | 0.8 |  | 0.8 | 0.8 | 0.8
|  |  |  | Hours PA > 95% Peak Load |  | 9 | 9 | 9 |  | 9 |  | 9 | 9 |  | 9 |  | 9 | 9 | 9
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0.8 | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.8 | 0.8
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## BORE
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | BORE - Boyne Residential (66/11kV) | [8 empty] | Supply |  | T019 - Gladstone South BSP
| Description |  |  |  | Region is Capricornia
Transformer size is 2x66/11kV 7.5/10MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.4%, 2021 S 0.4% W 0.4%, 2022 S 0.3% W 0.3%, 2023 S 0.4% W 0.4%, 2024 S 0.2% W 0.2%
|  |  | Latest Peak Compensated Load | [5 empty] | 11.3 MVA on 17/02/2020 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 26 | 26 | 26 |  | 26 |  | 26 | 29.9 |  | 29.9 |  | 29.9 | 29.9 | 29.9
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 12.4 | 12.5 | 12.5 |  | 12.6 |  | 12.7 | 8.8 |  | 8.8 |  | 8.8 | 8.8 | 8.9
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.99 | 0.99 | 0.99 |  | 0.99 |  | 0.99 | 0.994 |  | 0.994 |  | 0.994 | 0.994 | 0.994
|  |  |  | ECC Rating (MVA) |  | 14.3 | 14.3 | 14.3 |  | 14.3 |  | 14.3 | 15 |  | 15 |  | 15 | 15 | 15
|  |  |  | 50 PoE Load (MVA) |  | 11.3 | 11.4 | 11.4 |  | 11.5 |  | 11.5 | 8.7 |  | 8.7 |  | 8.6 | 8.6 | 8.7
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  |  | Hours PA > 95% Peak Load |  | 7 | 7 | 7 |  | 7 |  | 7 | 7 |  | 7 |  | 7 | 7 | 7
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## BOWE
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | BOWE - Bowen (66/11kV) | [8 empty] | Supply |  | T181 - Bowen North BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 2x66/11kV 15/16MVA ONAN/OFDAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.1%, 2021 S 0.6% W 0.6%, 2022 S 0.5% W 0.5%, 2023 S 0.6% W 0.6%, 2024 S 0.4% W 0.4%
|  |  | Latest Peak Compensated Load | [5 empty] | 12.2 MVA on 18/02/2020 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 39.8 | 39.8 | 39.8 |  | 39.8 |  | 39.8 | 44.4 |  | 44.4 |  | 44.4 | 44.4 | 44.4
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 13.9 | 14 | 14.1 |  | 14.2 |  | 14.3 | 9.1 |  | 9.1 |  | 9.1 | 9.1 | 9.2
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.986 | 0.986 | 0.986 |  | 0.986 |  | 0.986 | 0.982 |  | 0.982 |  | 0.982 | 0.982 | 0.982
|  |  |  | ECC Rating (MVA) |  | 22.4 | 22.4 | 22.4 |  | 22.4 |  | 22.4 | 23.9 |  | 23.9 |  | 23.9 | 23.9 | 23.9
|  |  |  | 50 PoE Load (MVA) |  | 12.4 | 12.5 | 12.6 |  | 12.7 |  | 12.7 | 9 |  | 9 |  | 9 | 9 | 9.1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | Hours PA > 95% Peak Load |  | 15.5 | 15.5 | 15.5 |  | 15.5 |  | 15.5 | 15.5 |  | 15.5 |  | 15.5 | 15.5 | 15.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## BROX
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | BROX - Broxburn (33/11kV) | [8 empty] | Supply |  | YARA - Yarranlea BSP
| Description |  |  |  | Region is South West
Transformer size is 2x33/11kV 5MVA ON
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.4%, 2021 S 0.0% W 0.0%, 2022 S -0.2% W -0.2%2023 S 0.0% W 0.0%, 2024 S -0.1% W -0.1
|  |  | Latest Peak Compensated Load | [5 empty] | 8.6 MVA on 16/12/2019 at 17:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 11 | 11 | 11 |  | 11 |  | 11 | 11 |  | 11 |  | 11 | 11 | 11
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 10.8 | 10.8 | 10.8 |  | 10.8 |  | 10.9 | 7.8 |  | 9.1 |  | 9.1 | 9 | 9.1
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.953 | 0.953 | 0.953 |  | 0.953 |  | 0.953 | 0.98 |  | 0.98 |  | 0.98 | 0.98 | 0.98
|  |  |  | ECC Rating (MVA) |  | 5.8 | 5.8 | 5.8 |  | 5.8 |  | 5.8 | 6 |  | 6 |  | 6 | 6 | 6
|  |  |  | 50 PoE Load (MVA) |  | 9.7 | 9.7 | 9.7 |  | 9.8 |  | 9.8 | 7.4 |  | 8.6 |  | 8.6 | 8.5 | 8.6
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  |  | Hours PA > 95% Peak Load |  | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 | 5 | 5
|  |  |  | Raw LAR (MVA) |  | 3.9 | 3.9 | 3.9 |  | 4 |  | 4 | 1.4 |  | 2.6 |  | 2.6 | 2.5 | 2.6
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | Mobile Plant Avail (MVA) |  | 3.3 | 3.3 | 3.3 |  | 3.3 |  | 3.3 | 3.3 |  | 3.3 |  | 3.3 | 3.3 | 3.3
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | LARc (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.2 |  | 0.2
|  |  |  | LARc (MW) |  | 0.1 | 0.1 | 0.1 |  | 0.2 |  | 0.2
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | No | No | No |  | No |  | No | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## BUCE
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | BUCE - Bundaberg Central (66/11kV) | [8 empty] | Supply |  | BUND - Bundaberg BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 2x66/11kV 19/26/32MVA ONAN/ODAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -1.0%, 2021 S -0.7% W -0.7%2022 S -1.2% W -1.2%2023 S -0.5% W -0.5%2024 S -0.3% W -0.3
|  |  | Latest Peak Compensated Load | [5 empty] | 16.8 MVA on 20/02/2020 at 13:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 80.3 | 80.3 | 80.3 |  | 80.3 |  | 80.3 | 87.4 |  | 87.4 |  | 87.4 | 87.4 | 87.4
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 17.6 | 17.4 | 17.3 |  | 17.3 |  | 17.3 | 13.9 |  | 13.7 |  | 13.4 | 13.3 | 13.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.992 | 0.992 | 0.993 |  | 0.993 |  | 0.993 | 0.945 |  | 0.936 |  | 0.936 | 0.945 | 0.936
|  |  |  | ECC Rating (MVA) |  | 43.1 | 43.1 | 43.1 |  | 43.1 |  | 43.1 | 45.8 |  | 45.8 |  | 45.8 | 45.8 | 45.8
|  |  |  | 50 PoE Load (MVA) |  | 16.4 | 16.2 | 16.1 |  | 16.1 |  | 16.1 | 13 |  | 12.8 |  | 12.6 | 12.5 | 12.5
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.8 | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.7 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  |  | Hours PA > 95% Peak Load |  | 6 | 6 | 6 |  | 6 |  | 6 | 6 |  | 6 |  | 6 | 6 | 6
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## BULL
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | BULL - Bullyard (66/11kV) | [8 empty] | Supply |  | BUND - Bundaberg BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 1x66/11kV 5MVA ON;1x66/11kV 5MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.3%, 2021 S 0.2% W 0.2%, 2022 S 0.1% W 0.1%, 2023 S 0.2% W 0.2%, 2024 S 0.0% W 0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 3.5 MVA on 16/12/2019 at 19:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 14.2 | 14.2 | 14.2 |  | 14.2 |  | 14.2 | 15 |  | 15 |  | 15 | 15 | 15
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 3.6 | 3.6 | 3.6 |  | 3.7 |  | 3.7 | 1.9 |  | 1.9 |  | 1.8 | 1.8 | 1.9
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.917 | 0.917 | 0.917 |  | 0.917 |  | 0.917 | 0.921 |  | 0.921 |  | 0.921 | 0.921 | 0.921
|  |  |  | ECC Rating (MVA) |  | 7.5 | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 | 7.5
|  |  |  | 50 PoE Load (MVA) |  | 3.5 | 3.5 | 3.5 |  | 3.6 |  | 3.6 | 1.8 |  | 1.8 |  | 1.8 | 1.8 | 1.8
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 7.5 | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 | 7.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## BUND
Bulk Summary Information and Peak Load Forecast
Substation |  |  |  | T020 - Bundaberg BSP (132/66kV) | [8 empty] | Supply |  | QGNG - Gin Gin TCP
Description |  |  |  | Region is Wide Bay
Transformer size is 1x132/66kV 36/70MVA ONAN/ONAF;2x132/66kV 40/50/60MVA ON/OFN/OFB
Capacity of commissioned Embedded Generation (with Connection Agreements) is 2.8 MVA
|  | Latest Peak Compensated Load | [5 empty] | 117.3 MVA on 04/12/2019 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[5 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  | NCC Rating (MVA) |  | 226.4 | 226.4 | 226.4 |  | 226.4 |  | 226.4 | 250.8 |  | 250.8 |  | 250.8 | 250.8 | 250.8
|  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  | 10 PoE Load (MVA) |  | 127.8 | 129.1 | 130.8 |  | 132.1 |  | 132.9 | 94.5 |  | 95.4 |  | 96.3 | 96.7 | 97.4
LARn (MVA)
LARn (MW)
|  |  | Power Factor at Peak Load |  | 0.983 | 0.983 | 0.983 |  | 0.983 |  | 0.983 | 0.997 |  | 0.997 |  | 0.997 | 0.997 | 0.997
|  |  | ECC Rating (MVA) |  | 170.2 | 170.2 | 170.2 |  | 170.2 |  | 170.2 | 179.4 |  | 179.4 |  | 179.4 | 179.4 | 179.4
|  |  | 50 PoE Load (MVA) |  | 118.6 | 119.7 | 121.3 |  | 122.5 |  | 123.2 | 89.5 |  | 90.3 |  | 91 | 91.4 | 92.1
|  |  | 50 PoE Load > 95% (MVA) |  | 5.9 | 6 | 6.1 |  | 6.1 |  | 6.2 | 4.5 |  | 4.5 |  | 4.6 | 4.6 | 4.6
|  |  | Hours PA > 95% Peak Load |  | 21 | 21 | 21 |  | 21 |  | 21 | 21 |  | 21 |  | 21 | 21 | 21
Raw LAR (MVA)
|  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## CACI
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | CACI - Cairns City (132/22kV) | [8 empty] | Supply |  | QCNS - Cairns 132kV TCP
| Description |  |  |  | Region is Far North
Transformer size is 1x132/22kV 55/80MVA ONAN/ODAN;1x132/22kV 64/80MVA ONAN/ODAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.3%, 2021 S -0.3% W -0.3%2022 S -0.7% W -0.7%2023 S -0.2% W -0.2%2024 S -0.5% W -0.5
|  |  | Latest Peak Compensated Load | [5 empty] | 43 MVA on 14/02/2020 at 15:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 182.3 | 182.3 | 182.3 |  | 182.3 |  | 182.3 | 187.9 |  | 187.9 |  | 187.9 | 187.9 | 187.9
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 45.2 | 44.9 | 44.8 |  | 44.8 |  | 44.7 | 30.8 |  | 30.6 |  | 30.2 | 30 | 30
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.999 | 0.999 | 0.999 |  | 0.999 |  | 0.999 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | ECC Rating (MVA) |  | 101.6 | 101.6 | 101.6 |  | 101.6 |  | 101.6 | 103.8 |  | 103.8 |  | 103.8 | 103.8 | 103.8
|  |  |  | 50 PoE Load (MVA) |  | 43.3 | 43 | 42.9 |  | 42.9 |  | 42.8 | 29.6 |  | 29.4 |  | 29 | 28.8 | 28.8
|  |  |  | 50 PoE Load > 95% (MVA) |  | 2.2 | 2.2 | 2.1 |  | 2.1 |  | 2.1 | 1.5 |  | 1.5 |  | 1.5 | 1.4 | 1.4
|  |  |  | Hours PA > 95% Peak Load |  | 50.5 | 50.5 | 50.5 |  | 50.5 |  | 50.5 | 50.5 |  | 50.5 |  | 50.5 | 50.5 | 50.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## CAFE
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | CAFE - Cape Ferguson (66/11kV) | [8 empty] | Supply |  | TMES - Townsville Mesh
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/11kV 2.3MVA ONAN;1x66/11kV 2MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.9%, 2021 S 2.3% W 2.3%, 2022 S 2.2% W 2.2%, 2023 S 2.2% W 2.2%, 2024 S 1.9% W 1.9%
|  |  | Latest Peak Compensated Load | [5 empty] | 1.9 MVA on 04/07/2019 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 4.4 | 4.4 | 4.4 |  | 4.4 |  | 4.4 | 4.7 |  | 4.7 |  | 4.7 | 4.7 | 4.7
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 2 | 2 | 2 |  | 2.1 |  | 2.1 | 2 |  | 2 |  | 2.1 | 2.1 | 2.2
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.995 | 0.995 | 0.995 |  | 0.995 |  | 0.995 | 0.993 |  | 0.993 |  | 0.993 | 0.993 | 0.993
|  |  |  | ECC Rating (MVA) |  | 2.6 | 2.6 | 2.6 |  | 2.6 |  | 2.6 | 2.7 |  | 2.7 |  | 2.7 | 2.7 | 2.7
|  |  |  | 50 PoE Load (MVA) |  | 1.9 | 1.9 | 1.9 |  | 2 |  | 2 | 2 |  | 2 |  | 2 | 2.1 | 2.1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 33 | 33 | 33 |  | 33 |  | 33 | 33 |  | 33 |  | 33 | 33 | 33
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## CALE
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | CALE - Calen (66/11kV) | [8 empty] | Supply |  | PROS - Proserpine BSP
| Description |  |  |  | Region is Mackay
Transformer size is 2x66/11kV 5MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.3%, 2021 S 0.4% W 0.4%, 2022 S 0.3% W 0.3%, 2023 S 0.4% W 0.4%, 2024 S 0.3% W 0.3%
|  |  | Latest Peak Compensated Load | [5 empty] | 4.6 MVA on 08/12/2019 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 11 | 11 | 11 |  | 11 |  | 11 | 12 |  | 12 |  | 12 | 12 | 12
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 4.8 | 4.8 | 4.9 |  | 4.9 |  | 4.9 | 2.2 |  | 2.2 |  | 2.2 | 2.2 | 2.2
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.938 | 0.938 | 0.938 |  | 0.938 |  | 0.938 | 0.951 |  | 0.951 |  | 0.951 | 0.951 | 0.951
|  |  |  | ECC Rating (MVA) |  | 6.3 | 6.3 | 6.3 |  | 6.3 |  | 6.3 | 6.5 |  | 6.5 |  | 6.5 | 6.5 | 6.5
|  |  |  | 50 PoE Load (MVA) |  | 4.7 | 4.7 | 4.7 |  | 4.8 |  | 4.8 | 2.1 |  | 2.1 |  | 2.1 | 2.1 | 2.1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 4 | 4 | 4 |  | 4 |  | 4 | 4 |  | 4 |  | 4 | 4 | 4
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## CALL
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | CALL - Calliope (66/11kV) | [8 empty] | Supply |  | T019 - Gladstone South BSP
| Description |  |  |  | Region is Capricornia
Transformer size is 1x66/11kV 7.5/10MVA ON/OB;1x66/11kV 7.5/10MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.3%, 2021 S 0.7% W 0.7%, 2022 S 0.6% W 0.6%, 2023 S 0.6% W 0.6%, 2024 S 0.4% W 0.4%
|  |  | Latest Peak Compensated Load | [5 empty] | 9 MVA on 16/12/2019 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 26.7 | 26.7 | 26.7 |  | 26.7 |  | 26.7 | 29.9 |  | 29.9 |  | 29.9 | 29.9 | 29.9
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 9.8 | 9.9 | 9.9 |  | 10 |  | 10.1 | 6.2 |  | 6.3 |  | 6.2 | 6.3 | 6.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.976 | 0.976 | 0.976 |  | 0.976 |  | 0.976 | 0.992 |  | 0.992 |  | 0.992 | 0.992 | 0.992
|  |  |  | ECC Rating (MVA) |  | 14.7 | 14.7 | 14.7 |  | 14.7 |  | 14.7 | 15 |  | 15 |  | 15 | 15 | 15
|  |  |  | 50 PoE Load (MVA) |  | 8.9 | 9 | 9.1 |  | 9.1 |  | 9.2 | 6.1 |  | 6.1 |  | 6.1 | 6.1 | 6.2
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.4 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Hours PA > 95% Peak Load |  | 7 | 7 | 7 |  | 7 |  | 7 | 7 |  | 7 |  | 7 | 7 | 7
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## CANN
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | CANN - Cannonvale (66/11kV) | [8 empty] | Supply |  | PROS - Proserpine BSP
| Description |  |  |  | Region is Mackay
Transformer size is 2x66/11kV 15MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.9%, 2021 S 0.8% W 0.8%, 2022 S 0.5% W 0.5%, 2023 S 0.7% W 0.7%, 2024 S 0.5% W 0.5%
|  |  | Latest Peak Compensated Load | [5 empty] | 15.9 MVA on 14/02/2020 at 14:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 34.9 | 34.9 | 34.9 |  | 34.9 |  | 34.9 | 37.8 |  | 37.8 |  | 37.8 | 37.8 | 37.8
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 19 | 19.1 | 19.2 |  | 19.4 |  | 19.5 | 11.1 |  | 11.1 |  | 11.1 | 11.1 | 11.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.982 | 0.982 | 0.982 |  | 0.982 |  | 0.982 | 0.993 |  | 0.993 |  | 0.993 | 0.993 | 0.993
|  |  |  | ECC Rating (MVA) |  | 20 | 20 | 20 |  | 20 |  | 20 | 21.9 |  | 21.9 |  | 21.9 | 21.9 | 21.9
|  |  |  | 50 PoE Load (MVA) |  | 16.6 | 16.7 | 16.8 |  | 17 |  | 17.1 | 10.8 |  | 10.8 |  | 10.8 | 10.9 | 11
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.8 | 0.8 | 0.8 |  | 0.9 |  | 0.9 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.6
|  |  |  | Hours PA > 95% Peak Load |  | 32.5 | 32.5 | 32.5 |  | 32.5 |  | 32.5 | 32.5 |  | 32.5 |  | 32.5 | 32.5 | 32.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## CANO
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | CANO - Cairns North (132/22kV) | [8 empty] | Supply |  | QWRE - Woree TCP
| Description |  |  |  | Region is Far North
Transformer size is 2x132/22kV 50/63MVA ONAN/ODAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.9%, 2021 S 0.5% W 0.5%, 2022 S 0.3% W 0.3%, 2023 S 0.5% W 0.5%, 2024 S 0.2% W 0.2%
|  |  | Latest Peak Compensated Load | [5 empty] | 46.8 MVA on 12/02/2020 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 142.8 | 142.8 | 142.8 |  | 142.8 |  | 142.8 | 147.1 |  | 147.1 |  | 147.1 | 147.1 | 147.1
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 48.6 | 48.8 | 49.1 |  | 49.4 |  | 49.7 | 31.3 |  | 31.3 |  | 31.2 | 31.2 | 31.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.998 | 0.998 | 0.998 |  | 0.998 |  | 0.998 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | ECC Rating (MVA) |  | 79.4 | 79.4 | 79.4 |  | 79.4 |  | 79.4 | 81.1 |  | 81.1 |  | 81.1 | 81.1 | 81.1
|  |  |  | 50 PoE Load (MVA) |  | 45.2 | 45.4 | 45.7 |  | 46 |  | 46.2 | 30.9 |  | 30.9 |  | 30.8 | 30.8 | 31
|  |  |  | 50 PoE Load > 95% (MVA) |  | 2.3 | 2.3 | 2.3 |  | 2.3 |  | 2.3 | 1.5 |  | 1.5 |  | 1.5 | 1.5 | 1.6
|  |  |  | Hours PA > 95% Peak Load |  | 16 | 16 | 16 |  | 16 |  | 16 | 16 |  | 16 |  | 16 | 16 | 16
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## CARI
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | CARI - Cape River (66/11kV) | [8 empty] | Supply |  | T095 - Millchester BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/11kV 1MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.3%, 2021 S 0.1% W 0.1%, 2022 S 0.0% W 0.0%, 2023 S 0.1% W 0.1%, 2024 S -0.1% W -0.1
|  |  | Latest Peak Compensated Load | [5 empty] | 0.8 MVA on 08/12/2019 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1.1 |  | 1.1 |  | 1.1 | 1.1 | 1.1
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 0.9 | 0.9 | 0.9 |  | 0.9 |  | 0.9 | 0.8 |  | 0.8 |  | 0.8 | 0.8 | 0.8
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.965 | 0.965 | 0.965 |  | 0.965 |  | 0.965 | 0.951 |  | 0.951 |  | 0.951 | 0.951 | 0.951
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 0.8 | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.7 |  | 0.7 |  | 0.7 | 0.7 | 0.7
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 9 | 9 | 9 |  | 9 |  | 9 | 9 |  | 9 |  | 9 | 9 | 9
|  |  |  | Raw LAR (MVA) |  | 0.8 | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.7 |  | 0.7 |  | 0.7 | 0.7 | 0.7
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## CARM
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | CARM - Carmila (33/11kV) | [8 empty] | Supply |  | T065 - Alligator Creek BSP
| Description |  |  |  | Region is Mackay
Transformer size is 1x33/11kV 1MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -1.5%, 2021 S -0.3% W -0.3%2022 S -0.4% W -0.4%2023 S -0.2% W -0.2%2024 S -0.4% W -0.4
|  |  | Latest Peak Compensated Load | [5 empty] | 0.7 MVA on 12/12/2019 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 1.3 | 1.3 | 1.3 |  | 1.3 |  | 1.3 | 1.4 |  | 1.4 |  | 1.4 | 1.4 | 1.4
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 0.8 | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.956 | 0.956 | 0.956 |  | 0.956 |  | 0.956 | 0.963 |  | 0.963 |  | 0.963 | 0.963 | 0.963
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 0.7 | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 8.5 | 8.5 | 8.5 |  | 8.5 |  | 8.5 | 8.5 |  | 8.5 |  | 8.5 | 8.5 | 8.5
|  |  |  | Raw LAR (MVA) |  | 0.7 | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Mobile Plant Avail (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## CAST
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | CAST - Canning Street (66/11kV) | [8 empty] | Supply |  | RMES - Rockhampton Mesh
| Description |  |  |  | Region is Capricornia
Transformer size is 2x16/20 MVA 66/11 ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.8%, 2021 S -0.2% W -0.2%2022 S -0.3% W -0.3%2023 S -0.2% W -0.2%2024 S -0.4% W -0.4
|  |  | Latest Peak Compensated Load | [5 empty] | 23.1 MVA on 04/02/2020 at 16:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 46.3 | 46.3 | 46.3 |  | 46.3 |  | 46.3 | 54.2 |  | 54.2 |  | 54.2 | 54.2 | 54.2
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 25.9 | 25.8 | 25.8 |  | 25.8 |  | 25.8 | 13.6 |  | 13.5 |  | 13.4 | 13.3 | 13.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.999 | 0.999 | 0.999 |  | 0.999 |  | 0.999 | 0.978 |  | 0.978 |  | 0.978 | 0.978 | 0.978
|  |  |  | ECC Rating (MVA) |  | 26.9 | 26.9 | 26.9 |  | 26.9 |  | 26.9 | 29.9 |  | 29.9 |  | 29.9 | 29.9 | 29.9
|  |  |  | 50 PoE Load (MVA) |  | 23.3 | 23.2 | 23.2 |  | 23.2 |  | 23.2 | 13.2 |  | 13.1 |  | 13 | 12.9 | 12.9
|  |  |  | 50 PoE Load > 95% (MVA) |  | 1.2 | 1.2 | 1.2 |  | 1.2 |  | 1.2 | 0.7 |  | 0.7 |  | 0.7 | 0.6 | 0.6
|  |  |  | Hours PA > 95% Peak Load |  | 14.5 | 14.5 | 14.5 |  | 14.5 |  | 14.5 | 14.5 |  | 14.5 |  | 14.5 | 14.5 | 14.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## CAUP
Zone Summary Information and Peak Load Forecast
| Substation |  |  | CAUP - Cape Upstart (66/11kV) | [6 empty] | Supply |  |  | T193 - Clare South BSP
| Description |  |  | Region is Nth Queensland
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  | 2021 W 0.0%, 2022 S 0.0% W 0.0%, 2023 S 0.0% W 0.0%, 2024 S 0.0% W 0.0%
No current information, due to be commissioned Winter 2021
Hours PA Exceeding 95% Peak Load
|  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[5 empty] | 2020/21 |  | 2021/22 | 2022/23 | 2023/24 | 2024/25 |  | 2020 | 2021 |  | 2022 | 2023 | 2024
|  |  | NCC Rating (MVA) |  |  |  | 10 | 10 | 10 | 10 |  |  | 10 |  | 10 | 10 | 10
|  |  | Contracted non-network (MVA) |  |  |  | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0
|  |  | 10 PoE Load (MVA) |  |  |  | 2.4 | 4.9 | 4.9 | 4.9 |  |  | 1.3 |  | 2.6 | 2.5 | 2.6
LARn (MVA)
LARn (MW)
|  |  | Power Factor at Peak Load |  |  |  | 0.85 | 0.85 | 0.85 | 0.85 |  |  | 0.85 |  | 0.85 | 0.85 | 0.85
|  |  | ECC Rating (MVA) |  |  |  | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0
|  |  | 50 PoE Load (MVA) |  |  |  | 2.4 | 4.8 | 4.9 | 4.9 |  |  | 1.3 |  | 2.5 | 2.5 | 2.5
|  |  | 50 PoE Load > (MVA) |  |  |  | 0.1 | 0.2 | 0.2 | 0.2 |  |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  | Hours PA > Peak Load |  |  |  | N/A | N/A | N/A | N/A |  |  | N/A |  | N/A | N/A | N/A
|  |  | Raw LAR (MVA) |  |  |  | 2.4 | 4.8 | 4.9 | 4.9 |  |  | 1.3 |  | 2.5 | 2.5 | 2.5
|  |  | Auto Trans Avail (MVA) |  |  |  | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0
|  |  | Remote Trans Avail (MVA) |  |  |  | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0
|  |  | Manual Trans Avail (MVA) |  |  |  | 6 | 6 | 6 | 6 |  |  | 6 |  | 6 | 6 | 6
|  |  | Mobile Plant Avail (MVA) |  |  |  | 4 | 4 | 4 | 4 |  |  | 4 |  | 4 | 4 | 4
|  |  | Shed(30min) |  |  |  | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0
|  |  | Shed(4Hour) |  |  |  | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  | Substation Category |  |  |  | Regional Centre | Regional Centre | Regional Centre | Regional Centre |  |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  | Meets Security Standard |  |  |  | Yes | Yes | Yes | Yes |  |  | Yes |  | Yes | Yes | Yes

## CAWD
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | CAWD - Skid B (Cawdor) (33/11kV) | [8 empty] | Supply |  | T116 - Torrington BSP
| Description |  |  |  | Region is South West
Transformer size is 1x10MVA Skid transformer
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.0%, 2021 S 1.7% W 1.7%, 2022 S 1.4% W 1.4%, 2023 S 1.4% W 1.4%, 2024 S 1.1% W 1.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 5.5 MVA on 04/06/2019 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 11 | 11 | 11 |  | 11 |  | 11 | 11 |  | 11 |  | 11 | 11 | 11
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 5.4 | 5.5 | 5.6 |  | 5.7 |  | 5.8 | 5.2 |  | 5.2 |  | 5.3 | 5.3 | 5.4
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.838 | 0.838 | 0.838 |  | 0.838 |  | 0.838 | 0.856 |  | 0.856 |  | 0.856 | 0.856 | 0.856
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 4.5 | 4.6 | 4.7 |  | 4.7 |  | 4.8 | 4.8 |  | 4.8 |  | 4.9 | 4.9 | 5
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.3
|  |  |  | Hours PA > 95% Peak Load |  | 24 | 24 | 24 |  | 24 |  | 24 | 24 |  | 24 |  | 24 | 24 | 24
|  |  |  | Raw LAR (MVA) |  | 4.5 | 4.6 | 4.7 |  | 4.7 |  | 4.8 | 4.8 |  | 4.8 |  | 4.9 | 4.9 | 5
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 3.6 | 3.6 | 3.6 |  | 3.6 |  | 3.6 | 3.6 |  | 3.6 |  | 3.6 | 3.6 | 3.6
|  |  |  | Mobile Plant Avail (MVA) |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## CEPL
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | CEPL - Cecil Plains (33/11kV) | [8 empty] | Supply |  | YARA - Yarranlea BSP
| Description |  |  |  | Region is South West
Transformer size is 2x33/11kV 5MVA ON
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -2.4%, 2021 S -0.3% W -0.3%2022 S -0.7% W -0.7%2023 S -0.3% W -0.3%2024 S -0.6% W -0.6
|  |  | Latest Peak Compensated Load | [5 empty] | 3.8 MVA on 04/06/2019 at 20:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 1.7 | 1.7 | 1.7 |  | 1.7 |  | 1.7 | 3.8 |  | 3.7 |  | 3.7 | 3.7 | 3.6
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.999 | 0.999 | 0.999 |  | 0.999 |  | 0.999 | 0.993 |  | 0.993 |  | 0.993 | 0.993 | 0.993
|  |  |  | ECC Rating (MVA) |  | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 | 5 | 5
|  |  |  | 50 PoE Load (MVA) |  | 1.5 | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 3.7 |  | 3.6 |  | 3.6 | 3.6 | 3.6
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 42 | 42 | 42 |  | 42 |  | 42 | 42 |  | 42 |  | 42 | 42 | 42
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## CHAL
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | CHAL - Skid K (Charlton) (33/11kV) | [8 empty] | Supply |  | T116 - Torrington BSP
| Description |  |  |  | Region is South West
Transformer size is 1x7.5/10MVA ONAN/ONAF 33/11kV
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.5%, 2021 S -0.4% W -0.4%2022 S -0.9% W -0.9%2023 S -0.4% W -0.4%2024 S -0.2% W -0.2
|  |  | Latest Peak Compensated Load | [5 empty] | 4.7 MVA on 24/06/2019 at 07:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 11 | 11 | 11 |  | 11 |  | 11 | 11 |  | 11 |  | 11 | 11 | 11
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 4.3 | 4.3 | 4.3 |  | 4.3 |  | 4.3 | 4.9 |  | 4.8 |  | 4.8 | 4.7 | 4.8
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.854 | 0.854 | 0.854 |  | 0.854 |  | 0.854 | 0.847 |  | 0.847 |  | 0.847 | 0.847 | 0.847
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 4.2 | 4.2 | 4.2 |  | 4.2 |  | 4.2 | 4.6 |  | 4.6 |  | 4.5 | 4.5 | 4.5
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 11.5 | 11.5 | 11.5 |  | 11.5 |  | 11.5 | 11.5 |  | 11.5 |  | 11.5 | 11.5 | 11.5
|  |  |  | Raw LAR (MVA) |  | 4.2 | 4.2 | 4.2 |  | 4.2 |  | 4.2 | 4.6 |  | 4.6 |  | 4.5 | 4.5 | 4.5
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 4.8 | 4.8 | 4.8 |  | 4.8 |  | 4.8 | 4.8 |  | 4.8 |  | 4.8 | 4.8 | 4.8
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## CHAR
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | CHAR - Charleville (66/22/11kV) | [8 empty] | Supply |  | ROMA - Roma 66kV BSP
| Description |  |  |  | Region is South West
Transformer size is 1x66/11kV 7.5MVA ONAN;1x66/22kV 7.5MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.0%, 2021 S 0.0% W 0.0%, 2022 S 0.0% W 0.0%, 2023 S 0.0% W 0.0%, 2024 S 0.0% W 0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 11.5 MVA on 17/12/2019 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 18.6 | 18.6 | 18.6 |  | 18.6 |  | 18.6 | 18.6 |  | 18.6 |  | 18.6 | 18.6 | 18.6
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 11.5 | 11.6 | 11.6 |  | 11.6 |  | 11.6 | 9.7 |  | 9.7 |  | 9.6 | 9.6 | 9.6
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.94 | 0.94 | 0.94 |  | 0.939 |  | 0.939 | 0.912 |  | 0.912 |  | 0.912 | 0.912 | 0.912
|  |  |  | ECC Rating (MVA) |  | 9.3 | 9.3 | 9.3 |  | 9.3 |  | 9.3 | 9.3 |  | 9.3 |  | 9.3 | 9.3 | 9.3
|  |  |  | 50 PoE Load (MVA) |  | 10.5 | 10.5 | 10.5 |  | 10.5 |  | 10.6 | 9.2 |  | 9.1 |  | 9.1 | 9 | 9.1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | Hours PA > 95% Peak Load |  | 13.5 | 13.5 | 13.5 |  | 13.5 |  | 13.5 | 13.5 |  | 13.5 |  | 13.5 | 13.5 | 13.5
|  |  |  | Raw LAR (MVA) |  | 1.2 | 1.2 | 1.2 |  | 1.2 |  | 1.3
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 3.2 | 3.2 | 3.2 |  | 3.2 |  | 3.2 | 3.2 |  | 3.2 |  | 3.2 | 3.2 | 3.2
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## CHIA
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | CHIA - Chillagoe (66/22kV) | [8 empty] | Supply |  | TURK - Turkinje 66kV BSP
| Description |  |  |  | Region is Far North
Transformer size is 1x66/22kV 6.3MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 5.0%, 2021 S 0.1% W 0.1%, 2022 S -1.6% W -1.6%2023 S 2.2% W 2.2%, 2024 S -2.6% W -2.6
|  |  | Latest Peak Compensated Load | [5 empty] | 0.5 MVA on 14/12/2019 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 8.9 | 8.9 | 8.9 |  | 8.9 |  | 8.9 | 9.2 |  | 9.2 |  | 9.2 | 9.2 | 9.2
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 0.5 | 0.5 | 0.6 |  | 0.5 |  | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.991 | 0.991 | 0.991 |  | 0.991 |  | 0.991 | 0.965 |  | 0.965 |  | 0.965 | 0.965 | 0.965
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 15 | 15 | 15 |  | 15 |  | 15 | 15 |  | 15 |  | 15 | 15 | 15
|  |  |  | Raw LAR (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Mobile Plant Avail (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## CHIL
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | CHIL - Childers (66/11kV) | [8 empty] | Supply |  | ISIS - Isis BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 1x66/11kV 10/7.5MVA ONB/ON;1x66/11kV 7.5/10MVA ON/ONB
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.6%, 2021 S 0.6% W 0.6%, 2022 S 0.4% W 0.4%, 2023 S 0.6% W 0.6%, 2024 S 0.3% W 0.3%
|  |  | Latest Peak Compensated Load | [5 empty] | 7.3 MVA on 02/12/2019 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 20.9 | 20.9 | 20.9 |  | 20.9 |  | 20.9 | 22.4 |  | 22.4 |  | 22.4 | 22.4 | 22.4
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 9.1 | 9.7 | 10.4 |  | 10.4 |  | 10.5 | 5.3 |  | 5.8 |  | 6.2 | 6.2 | 6.2
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.946 | 0.946 | 0.946 |  | 0.946 |  | 0.946 | 0.965 |  | 0.965 |  | 0.965 | 0.965 | 0.965
|  |  |  | ECC Rating (MVA) |  | 11.2 | 11.2 | 11.2 |  | 11.2 |  | 11.2 | 11.2 |  | 11.2 |  | 11.2 | 11.2 | 11.2
|  |  |  | 50 PoE Load (MVA) |  | 7.8 | 8.4 | 9 |  | 9.1 |  | 9.2 | 5.1 |  | 5.6 |  | 6 | 6 | 6
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.4 | 0.4 | 0.5 |  | 0.5 |  | 0.5 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Hours PA > 95% Peak Load |  | 12.5 | 12.5 | 12.5 |  | 12.5 |  | 12.5 | 12.5 |  | 12.5 |  | 12.5 | 12.5 | 12.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## CHIN
Bulk Summary Information and Peak Load Forecast
Substation |  |  |  | CHIN - Chinchilla BSP (132/33kV) | [8 empty] | Supply |  | QCHA - Chinchilla TCP
Description |  |  |  | Region is South West
Transformer size is 1x132/110kV 30MVA ONAN;1x132/33/11kV 50/63MVA ONAN/ONAF;2x106/33/11kV 20MVA ON(Standby)
Capacity of commissioned Embedded Generation (with Connection Agreements) is 15.3 MVA
|  | Latest Peak Compensated Load | [5 empty] | 21.7 MVA on 16/12/2019 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[5 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  | NCC Rating (MVA) |  | 66 | 66 | 66 |  | 66 |  | 66 | 78.9 |  | 78.9 |  | 78.9 | 78.9 | 78.9
|  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | 10 PoE Load (MVA) |  | 23.9 | 24 | 24.1 |  | 24.2 |  | 24.3 | 18.5 |  | 18.5 |  | 18.5 | 18.4 | 18.5
LARn (MVA)
LARn (MW)
|  |  | Power Factor at Peak Load |  | 0.999 | 0.999 | 0.999 |  | 0.999 |  | 0.999 | 0.998 |  | 0.998 |  | 0.998 | 0.998 | 0.998
|  |  | ECC Rating (MVA) |  | 37.7 | 37.7 | 37.7 |  | 37.7 |  | 37.7 | 43.5 |  | 43.5 |  | 43.5 | 43.5 | 43.5
|  |  | 50 PoE Load (MVA) |  | 22 | 22 | 22.1 |  | 22.2 |  | 22.4 | 17.6 |  | 17.6 |  | 17.5 | 17.5 | 17.6
|  |  | 50 PoE Load > 95% (MVA) |  | 1.1 | 1.1 | 1.1 |  | 1.1 |  | 1.1 | 0.9 |  | 0.9 |  | 0.9 | 0.9 | 0.9
|  |  | Hours PA > 95% Peak Load |  | 27 | 27 | 27 |  | 27 |  | 27 | 27 |  | 27 |  | 27 | 27 | 27
Raw LAR (MVA)
|  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## CHTO
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | CHTO - Charters Towers (66/11kV) | [8 empty] | Supply |  | T095 - Millchester BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/11kV 7.5/10MVA ONAN/ONAF;1x66/11kV 8/10MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.2%, 2021 S 0.1% W 0.1%, 2022 S -0.1% W -0.1%2023 S 0.1% W 0.1%, 2024 S -0.2% W -0.2
|  |  | Latest Peak Compensated Load | [5 empty] | 9.7 MVA on 19/02/2020 at 19:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 21 | 21 | 21 |  | 21 |  | 21 | 23 |  | 23 |  | 23 | 23 | 23
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 11.5 | 11.5 | 11.6 |  | 11.6 |  | 11.6 | 7.6 |  | 7.6 |  | 7.5 | 7.5 | 7.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.999 | 0.999 | 0.999 |  | 0.999 |  | 0.999 | 0.998 |  | 0.998 |  | 0.998 | 0.998 | 0.998
|  |  |  | ECC Rating (MVA) |  | 10.5 | 10.5 | 10.5 |  | 10.5 |  | 10.5 | 11.5 |  | 11.5 |  | 11.5 | 11.5 | 11.5
|  |  |  | 50 PoE Load (MVA) |  | 10.4 | 10.4 | 10.4 |  | 10.5 |  | 10.5 | 7.3 |  | 7.3 |  | 7.3 | 7.3 | 7.3
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  |  | Hours PA > 95% Peak Load |  | 31 | 31 | 31 |  | 31 |  | 31 | 31 |  | 31 |  | 31 | 31 | 31
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## CHTW
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | CHTW - Chinchilla Town (33/11kV) | [8 empty] | Supply |  | CHIN - Chinchilla BSP
| Description |  |  |  | Region is South West
Transformer size is 2x33/11kV 5MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.1%, 2021 S 0.3% W 0.3%, 2022 S 0.1% W 0.1%, 2023 S 0.2% W 0.2%, 2024 S 0.2% W 0.2%
|  |  | Latest Peak Compensated Load | [5 empty] | 7.8 MVA on 11/12/2019 at 16:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 13.7 | 13.7 | 13.7 |  | 13.7 |  | 13.7 | 15 |  | 15 |  | 15 | 15 | 15
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 9 | 9 | 9 |  | 9.1 |  | 9.1 | 5.9 |  | 5.9 |  | 5.9 | 5.8 | 5.9
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.96 | 0.96 | 0.96 |  | 0.96 |  | 0.96 | 0.97 |  | 0.97 |  | 0.97 | 0.964 | 0.97
|  |  |  | ECC Rating (MVA) |  | 7.5 | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 | 7.5
|  |  |  | 50 PoE Load (MVA) |  | 8.1 | 8.1 | 8.1 |  | 8.2 |  | 8.2 | 5.6 |  | 5.6 |  | 5.6 | 5.5 | 5.6
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.4 | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Hours PA > 95% Peak Load |  | 12 | 12 | 12 |  | 12 |  | 12 | 12 |  | 12 |  | 12 | 12 | 12
|  |  |  | Raw LAR (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.7 |  | 0.7
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0.7 | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.7 | 0.7
|  |  |  | Mobile Plant Avail (MVA) |  | 2.5 | 2.5 | 2.5 |  | 2.5 |  | 2.5 | 2.5 |  | 2.5 |  | 2.5 | 2.5 | 2.5
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## CHUM
Bulk Summary Information and Peak Load Forecast
Substation |  |  |  | CHUM - Chumvale BSP (220/66kV) | [8 empty] | Supply |  | QMCH - Mica Creek 220kV TCP
Description |  |  |  | Region is Nth Queensland
Transformer size is 1x220/66kV 30/40MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
|  | Latest Peak Compensated Load | [5 empty] | 7.1 MVA on 18/12/2019 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[5 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  | NCC Rating (MVA) |  | 49.8 | 49.8 | 49.8 |  | 49.8 |  | 49.8 | 59.8 |  | 59.8 |  | 59.8 | 59.8 | 59.8
|  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | 10 PoE Load (MVA) |  | 8 | 8 | 8 |  | 8 |  | 7.9 | 3.9 |  | 3.9 |  | 3.9 | 3.8 | 3.8
LARn (MVA)
LARn (MW)
|  |  | Power Factor at Peak Load |  | 0.987 | 0.987 | 0.987 |  | 0.987 |  | 0.987 | 0.995 |  | 0.995 |  | 0.995 | 0.995 | 0.995
|  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | 50 PoE Load (MVA) |  | 7.4 | 7.4 | 7.4 |  | 7.3 |  | 7.3 | 3.7 |  | 3.7 |  | 3.7 | 3.6 | 3.6
|  |  | 50 PoE Load > 95% (MVA) |  | 0.4 | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  | Hours PA > 95% Peak Load |  | 16.5 | 16.5 | 16.5 |  | 16.5 |  | 16.5 | 16.5 |  | 16.5 |  | 16.5 | 16.5 | 16.5
|  |  | Raw LAR (MVA) |  | 7.4 | 7.4 | 7.4 |  | 7.3 |  | 7.3 | 3.7 |  | 3.7 |  | 3.7 | 3.6 | 3.6
|  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Manual Trans Avail (MVA) |  | 6.8 | 6.8 | 6.8 |  | 6.8 |  | 6.8 | 6.8 |  | 6.8 |  | 6.8 | 6.8 | 6.8
|  |  | Mobile Plant Avail (MVA) |  | 1.3 | 1.3 | 1.3 |  | 1.3 |  | 1.3 | 1.3 |  | 1.3 |  | 1.3 | 1.3 | 1.3
|  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## CLBS
Bulk Summary Information and Peak Load Forecast
Substation |  |  |  | CLBS - Clermont BSP (132/66kV) | [8 empty] | Supply |  | QLCM - Lilyvale (Barcaldine & Clermont) TCP
Description |  |  |  | Region is Capricornia
Transformer size is 2x132/69/11kV 30MVA OFDAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 75.0 MVA
|  | Latest Peak Compensated Load | [5 empty] | 19.8 MVA on 12/12/2019 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[5 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  | NCC Rating (MVA) |  | 80.9 | 80.9 | 80.9 |  | 80.9 |  | 80.9 | 86.9 |  | 86.9 |  | 86.9 | 86.9 | 86.9
|  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | 10 PoE Load (MVA) |  | 21.6 | 21.6 | 21.7 |  | 21.8 |  | 21.9 | 17.9 |  | 17.9 |  | 17.8 | 17.8 | 17.9
LARn (MVA)
LARn (MW)
|  |  | Power Factor at Peak Load |  | 0.993 | 0.993 | 0.993 |  | 0.993 |  | 0.993 | 0.993 |  | 0.993 |  | 0.993 | 0.993 | 0.993
|  |  | ECC Rating (MVA) |  | 44.9 | 44.9 | 44.9 |  | 44.9 |  | 44.9 | 44.9 |  | 44.9 |  | 44.9 | 44.9 | 44.9
|  |  | 50 PoE Load (MVA) |  | 20.2 | 20.3 | 20.3 |  | 20.5 |  | 20.5 | 17.2 |  | 17.2 |  | 17.1 | 17.1 | 17.2
|  |  | 50 PoE Load > 95% (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 0.9 |  | 0.9 |  | 0.9 | 0.9 | 0.9
|  |  | Hours PA > 95% Peak Load |  | 13 | 13 | 13 |  | 13 |  | 13 | 13 |  | 13 |  | 13 | 13 | 13
Raw LAR (MVA)
|  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## CLER
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | CLER - Clermont (66/22kV) | [8 empty] | Supply |  | CLBS - Clermont BSP
| Description |  |  |  | Region is Capricornia
Transformer size is 1xCLERSS CL-T6 11KV TRANSF 6 TRANSF CL-T6;1xCLERSS TRANSF 5 TRANSFORMER
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.9%, 2021 S 0.5% W 0.5%, 2022 S 0.4% W 0.4%, 2023 S 0.5% W 0.5%, 2024 S 0.4% W 0.4%
|  |  | Latest Peak Compensated Load | [5 empty] | 9.9 MVA on 17/12/2019 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 22 | 22 | 22 |  | 22 |  | 22 | 22 |  | 22 |  | 22 | 22 | 22
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 11.2 | 11.3 | 11.3 |  | 11.4 |  | 11.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 | 7.6
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.997 | 0.997 | 0.997 |  | 0.997 |  | 0.996 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | ECC Rating (MVA) |  | 11.5 | 11.5 | 11.5 |  | 11.5 |  | 11.5 | 13 |  | 13 |  | 13 | 13 | 13
|  |  |  | 50 PoE Load (MVA) |  | 10.1 | 10.1 | 10.2 |  | 10.3 |  | 10.3 | 7 |  | 7 |  | 7 | 7 | 7.1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  |  | Hours PA > 95% Peak Load |  | 7.5 | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 | 7.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## CLIF
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | CLIF - Clifton (33/11kV) | [8 empty] | Supply |  | T043 - South Toowoomba BSP
| Description |  |  |  | Region is South West
Transformer size is 2x33/11kV 3MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.6%, 2021 S 0.3% W 0.3%, 2022 S 0.2% W 0.2%, 2023 S 0.4% W 0.4%, 2024 S 0.1% W 0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 4 MVA on 20/11/2019 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 8 | 8 | 8 |  | 8 |  | 8 | 8.7 |  | 8.7 |  | 8.7 | 8.7 | 8.7
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 4.3 | 4.3 | 4.3 |  | 4.3 |  | 4.3 | 3.8 |  | 3.8 |  | 3.7 | 3.7 | 3.8
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.999 | 0.999 | 0.999 |  | 0.999 |  | 0.999 | 0.998 |  | 0.998 |  | 0.998 | 0.998 | 0.998
|  |  |  | ECC Rating (MVA) |  | 4.4 | 4.4 | 4.4 |  | 4.4 |  | 4.4 | 4.5 |  | 4.5 |  | 4.5 | 4.5 | 4.5
|  |  |  | 50 PoE Load (MVA) |  | 3.8 | 3.8 | 3.8 |  | 3.9 |  | 3.9 | 3.5 |  | 3.5 |  | 3.5 | 3.5 | 3.5
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 4.5 | 4.5 | 4.5 |  | 4.5 |  | 4.5 | 4.5 |  | 4.5 |  | 4.5 | 4.5 | 4.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## CLIN
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | CLIN - Clinton (66/11kV) | [8 empty] | Supply |  | GLNO - Gladstone North BSP
| Description |  |  |  | Region is Capricornia
Transformer size is 2x66/11kV 16/20/25MVA ONAN/ONAF/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.3%, 2021 S -0.3% W -0.3%2022 S -0.9% W -0.9%2023 S -0.7% W -0.7%2024 S -0.4% W -0.4
|  |  | Latest Peak Compensated Load | [5 empty] | 14.9 MVA on 10/02/2020 at 14:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 70.4 | 70.4 | 70.4 |  | 70.4 |  | 70.4 | 74.8 |  | 74.8 |  | 74.8 | 74.8 | 74.8
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 15.3 | 15.2 | 15.1 |  | 15.1 |  | 15.1 | 9.2 |  | 9.1 |  | 9 | 8.9 | 8.9
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 1 | 1 | 1 |  | 1 |  | 1 | 0.924 |  | 0.924 |  | 0.924 | 0.924 | 0.924
|  |  |  | ECC Rating (MVA) |  | 37.4 | 37.4 | 37.4 |  | 37.4 |  | 37.4 | 37.4 |  | 37.4 |  | 37.4 | 37.4 | 37.4
|  |  |  | 50 PoE Load (MVA) |  | 15 | 14.9 | 14.8 |  | 14.8 |  | 14.7 | 9 |  | 8.9 |  | 8.8 | 8.7 | 8.7
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.8 | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.5 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  |  | Hours PA > 95% Peak Load |  | 6.5 | 6.5 | 6.5 |  | 6.5 |  | 6.5 | 6.5 |  | 6.5 |  | 6.5 | 6.5 | 6.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 3 | 3 | 3 |  | 3 |  | 3 | 3 |  | 3 |  | 3 | 3 | 3
|  |  |  | Mobile Plant Avail (MVA) |  | 4 | 4 | 4 |  | 4 |  | 4 | 4 |  | 4 |  | 4 | 4 | 4
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## CLON
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | CLON - Cloncurry (66/11kV) | [8 empty] | Supply |  | CHUM - Chumvale BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/11kV 2/2.3MVA ONAN/ONAF;1x66/11kV 3MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.4%, 2021 S -0.4% W -0.4%2022 S -0.6% W -0.6%2023 S -0.4% W -0.4%2024 S -0.6% W -0.6
|  |  | Latest Peak Compensated Load | [5 empty] | 3.5 MVA on 18/12/2019 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 6.7 | 6.7 | 6.7 |  | 6.7 |  | 6.7 | 6.9 |  | 6.9 |  | 6.9 | 6.9 | 6.9
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 4 | 4 | 4 |  | 4 |  | 4 | 1.9 |  | 1.8 |  | 1.9 | 1.9 | 1.9
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.977 | 0.977 | 0.977 |  | 0.977 |  | 0.977 | 0.984 |  | 0.99 |  | 0.984 | 0.984 | 0.984
|  |  |  | ECC Rating (MVA) |  | 3.4 | 3.4 | 3.4 |  | 3.4 |  | 3.4 | 3.4 |  | 3.4 |  | 3.4 | 3.4 | 3.4
|  |  |  | 50 PoE Load (MVA) |  | 3.7 | 3.7 | 3.6 |  | 3.6 |  | 3.6 | 1.9 |  | 1.8 |  | 1.8 | 1.8 | 1.8
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 40 | 40 | 40 |  | 40 |  | 40 | 40 |  | 40 |  | 40 | 40 | 40
|  |  |  | Raw LAR (MVA) |  | 0.3 | 0.3 | 0.2 |  | 0.2 |  | 0.2
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 1.7 | 1.7 | 1.7 |  | 1.7 |  | 1.7 | 1.7 |  | 1.7 |  | 1.7 | 1.7 | 1.7
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## CLSO
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | CLSO - Clare South (66/11kV) | [8 empty] | Supply |  | T193 - Clare South BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/11kV 6.3MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.0%, 2021 S -0.1% W -0.1%2022 S -0.2% W -0.2%2023 S 0.1% W 0.1%, 2024 S -0.2% W -0.2
|  |  | Latest Peak Compensated Load | [5 empty] | 2.8 MVA on 04/12/2019 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 7.5 | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 8.3 |  | 8.3 |  | 8.3 | 8.3 | 8.3
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 3 | 3 | 3 |  | 3 |  | 3 | 1.7 |  | 1.6 |  | 1.6 | 1.6 | 1.6
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.896 | 0.896 | 0.896 |  | 0.896 |  | 0.896 | 0.877 |  | 0.877 |  | 0.877 | 0.877 | 0.877
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 2.9 | 2.9 | 2.9 |  | 2.9 |  | 2.9 | 1.6 |  | 1.6 |  | 1.6 | 1.6 | 1.6
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 6 | 6 | 6 |  | 6 |  | 6 | 6 |  | 6 |  | 6 | 6 | 6
|  |  |  | Raw LAR (MVA) |  | 2.9 | 2.9 | 2.9 |  | 2.9 |  | 2.9 | 1.6 |  | 1.6 |  | 1.6 | 1.6 | 1.6
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 2.2 | 2.2 | 2.2 |  | 2.2 |  | 2.2 | 2.2 |  | 2.2 |  | 2.2 | 2.2 | 2.2
|  |  |  | Mobile Plant Avail (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## COLU
Bulk Summary Information and Peak Load Forecast
Substation |  |  |  | COLU - Columboola BSP (132/33kV) | [8 empty] | Supply |  | T194 - Columboola TCP
Description |  |  |  | Region is South West
Transformer size is 1xCOLU 132/33KV TRANSF 1
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
|  | Latest Peak Compensated Load | [5 empty] | 13.9 MVA on 16/12/2019 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[5 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  | NCC Rating (MVA) |  | 40.2 | 40.2 | 40.2 |  | 40.2 |  | 40.2 | 47.4 |  | 47.4 |  | 47.4 | 47.4 | 47.4
|  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | 10 PoE Load (MVA) |  | 15.9 | 15.9 | 15.9 |  | 15.9 |  | 15.9 | 13.6 |  | 13.6 |  | 13.5 | 13.4 | 13.5
LARn (MVA)
LARn (MW)
|  |  | Power Factor at Peak Load |  | 0.986 | 0.986 | 0.986 |  | 0.986 |  | 0.986 | 0.997 |  | 0.997 |  | 0.997 | 0.997 | 0.997
|  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | 50 PoE Load (MVA) |  | 14.5 | 14.5 | 14.5 |  | 14.5 |  | 14.5 | 12.9 |  | 12.8 |  | 12.7 | 12.7 | 12.7
|  |  | 50 PoE Load > 95% (MVA) |  | 0.7 | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  | Hours PA > 95% Peak Load |  | 29.5 | 29.5 | 29.5 |  | 29.5 |  | 29.5 | 29.5 |  | 29.5 |  | 29.5 | 29.5 | 29.5
|  |  | Raw LAR (MVA) |  | 14.5 | 14.5 | 14.5 |  | 14.5 |  | 14.5 | 12.9 |  | 12.8 |  | 12.7 | 12.7 | 12.7
|  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Manual Trans Avail (MVA) |  | 14 | 14 | 14 |  | 14 |  | 14 | 14 |  | 14 |  | 14 | 14 | 14
|  |  | Mobile Plant Avail (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 | 2 | 2
|  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## COME
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | COME - Comet (66/22kV) | [8 empty] | Supply |  | T032 - Blackwater BSP
| Description |  |  |  | Region is Capricornia
Transformer size is 1x66/22kV 5MVA ON;1x66/22kV 2MVA ON(Standby)
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.8%, 2021 S 0.0% W 0.0%, 2022 S -0.1% W -0.1%2023 S 0.1% W 0.1%, 2024 S -0.1% W -0.1
|  |  | Latest Peak Compensated Load | [5 empty] | 3.3 MVA on 10/08/2019 at 16:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 6.9 | 6.9 | 6.9 |  | 6.9 |  | 6.9 | 6.9 |  | 6.9 |  | 6.9 | 6.9 | 6.9
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2.5 |  | 2.5 |  | 2.5 | 2.5 | 2.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.872 | 0.872 | 0.872 |  | 0.872 |  | 0.872 | 0.673 |  | 0.673 |  | 0.673 | 0.673 | 0.673
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2.4 |  | 2.4 |  | 2.4 | 2.4 | 2.4
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 22.5 | 22.5 | 22.5 |  | 22.5 |  | 22.5 | 22.5 |  | 22.5 |  | 22.5 | 22.5 | 22.5
|  |  |  | Raw LAR (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2.4 |  | 2.4 |  | 2.4 | 2.4 | 2.4
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 2.4 | 2.4 | 2.4 |  | 2.4 |  | 2.4 | 2.4 |  | 2.4 |  | 2.4 | 2.4 | 2.4
|  |  |  | Mobile Plant Avail (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## COOK
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | COOK - Cooktown (66/22kV) | [8 empty] | Supply |  | T159 - Lakeland BSP
| Description |  |  |  | Region is Far North
Transformer size is 2x66/22kV 8/10MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.7%, 2021 S 0.3% W 0.3%, 2022 S 0.1% W 0.1%, 2023 S 0.3% W 0.3%, 2024 S 0.0% W 0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 4.4 MVA on 13/02/2020 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 21.5 | 21.5 | 21.5 |  | 21.5 |  | 21.5 | 24.6 |  | 24.6 |  | 24.6 | 24.6 | 24.6
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 4.7 | 4.7 | 4.7 |  | 4.8 |  | 4.8 | 3 |  | 3 |  | 3 | 3 | 3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.976 | 0.976 | 0.976 |  | 0.976 |  | 0.976 | 0.989 |  | 0.989 |  | 0.989 | 0.989 | 0.989
|  |  |  | ECC Rating (MVA) |  | 12.6 | 12.6 | 12.6 |  | 12.6 |  | 12.6 | 13.6 |  | 13.6 |  | 13.6 | 13.6 | 13.6
|  |  |  | 50 PoE Load (MVA) |  | 4.3 | 4.3 | 4.3 |  | 4.3 |  | 4.3 | 3 |  | 3 |  | 2.9 | 2.9 | 3
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 |  | 0.2 |  | 0.1 | 0.1 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 9 | 9 | 9 |  | 9 |  | 9 | 9 |  | 9 |  | 9 | 9 | 9
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## COOM
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | COOM - Coominglah (66/22kV) | [8 empty] | Supply |  | T026 - Biloela BSP
| Description |  |  |  | Region is Capricornia
Transformer size is 1x66/22kV 2MVA ONAN;1x66/22kV 2MVA ONAN(Standby)
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.2%, 2021 S -0.1% W -0.1%2022 S -0.2% W -0.2%2023 S -0.1% W -0.1%2024 S -0.2% W -0.2
|  |  | Latest Peak Compensated Load | [5 empty] | 1.5 MVA on 12/07/2019 at 07:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 2.6 | 2.6 | 2.6 |  | 2.6 |  | 2.6 | 3 |  | 3 |  | 3 | 3 | 3
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 1.7 | 1.7 | 1.7 |  | 1.7 |  | 1.7 | 1.6 |  | 1.6 |  | 1.6 | 1.6 | 1.6
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.939 | 0.939 | 0.939 |  | 0.939 |  | 0.939 | 0.889 |  | 0.889 |  | 0.889 | 0.889 | 0.889
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 1.4 | 1.4 | 1.4 |  | 1.4 |  | 1.4 | 1.5 |  | 1.5 |  | 1.5 | 1.5 | 1.5
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 11.5 | 11.5 | 11.5 |  | 11.5 |  | 11.5 | 11.5 |  | 11.5 |  | 11.5 | 11.5 | 11.5
|  |  |  | Raw LAR (MVA) |  | 1.4 | 1.4 | 1.4 |  | 1.4 |  | 1.4 | 1.5 |  | 1.5 |  | 1.5 | 1.5 | 1.5
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 3 | 3 | 3 |  | 3 |  | 3 | 3 |  | 3 |  | 3 | 3 | 3
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## CRAI
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | CRAI - Craiglie (132/22kV) | [8 empty] | Supply |  | QTUH - Turkinje 132kV TCP
| Description |  |  |  | Region is Far North
Transformer size is 2x132/22kV 15/20MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.6%, 2021 S 0.3% W 0.3%, 2022 S 0.0% W 0.0%, 2023 S 0.3% W 0.3%, 2024 S 0.1% W 0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 14.2 MVA on 23/01/2020 at 16:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 47.1 | 47.1 | 47.1 |  | 47.1 |  | 47.1 | 53.4 |  | 53.4 |  | 53.4 | 53.4 | 53.4
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 14.4 | 14.4 | 14.5 |  | 14.5 |  | 14.6 | 10.3 |  | 10.3 |  | 10.3 | 10.3 | 10.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.988 | 0.988 | 0.988 |  | 0.988 |  | 0.988 | 0.994 |  | 0.994 |  | 0.994 | 0.994 | 0.994
|  |  |  | ECC Rating (MVA) |  | 27.6 | 27.6 | 27.6 |  | 27.6 |  | 27.6 | 29.8 |  | 29.8 |  | 29.8 | 29.8 | 29.8
|  |  |  | 50 PoE Load (MVA) |  | 13.3 | 13.3 | 13.4 |  | 13.4 |  | 13.5 | 10.2 |  | 10.2 |  | 10.1 | 10.1 | 10.2
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.7 | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | Hours PA > 95% Peak Load |  | 18 | 18 | 18 |  | 18 |  | 18 | 18 |  | 18 |  | 18 | 18 | 18
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 | 2 | 2
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 | 2 | 2
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## CRAN
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | CRAN - Cranbrook (66/11kV) | [8 empty] | Supply |  | TMES - Townsville Mesh
| Description |  |  |  | Region is Nth Queensland
Transformer size is 2x66/11kV 15/20/25MVA ONAN/ONAF/OFDAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.6%, 2021 S -0.3% W -0.3%2022 S -0.6% W -0.6%2023 S -0.4% W -0.4%2024 S -0.4% W -0.4
|  |  | Latest Peak Compensated Load | [5 empty] | 17.4 MVA on 12/02/2020 at 17:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 55.6 | 55.6 | 55.6 |  | 55.6 |  | 55.6 | 57.9 |  | 57.9 |  | 57.9 | 57.9 | 57.9
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 19.7 | 19.6 | 19.5 |  | 19.5 |  | 19.5 | 10 |  | 9.9 |  | 9.8 | 9.7 | 9.7
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.977 | 0.977 | 0.977 |  | 0.977 |  | 0.977 | 0.983 |  | 0.983 |  | 0.983 | 0.983 | 0.983
|  |  |  | ECC Rating (MVA) |  | 30.5 | 30.5 | 30.5 |  | 30.5 |  | 30.5 | 31.9 |  | 31.9 |  | 31.9 | 31.9 | 31.9
|  |  |  | 50 PoE Load (MVA) |  | 17.2 | 17.1 | 17.1 |  | 17.1 |  | 17 | 9.8 |  | 9.7 |  | 9.6 | 9.5 | 9.6
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.9 | 0.9 | 0.9 |  | 0.9 |  | 0.9 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | Hours PA > 95% Peak Load |  | 7 | 7 | 7 |  | 7 |  | 7 | 7 |  | 7 |  | 7 | 7 | 7
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## CRED
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | CRED - Crediton (66/11kV) | [8 empty] | Supply |  | PIVA - Pioneer Valley BSP
| Description |  |  |  | Region is Mackay
Transformer size is 1x66/11kV 1MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 1.2%, 2021 S 0.6% W 0.6%, 2022 S 0.5% W 0.5%, 2023 S 0.6% W 0.6%, 2024 S 0.5% W 0.5%
|  |  | Latest Peak Compensated Load | [5 empty] | 0.4 MVA on 16/02/2020 at 17:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 1.1 | 1.1 | 1.1 |  | 1.1 |  | 1.1 | 1.1 |  | 1.1 |  | 1.1 | 1.1 | 1.1
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.945 | 0.945 | 0.945 |  | 0.945 |  | 0.945 | 0.987 |  | 0.987 |  | 0.987 | 0.987 | 0.987
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 0.4 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 4.5 | 4.5 | 4.5 |  | 4.5 |  | 4.5 | 4.5 |  | 4.5 |  | 4.5 | 4.5 | 4.5
|  |  |  | Raw LAR (MVA) |  | 0.4 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## CRNE
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | CRNE - Crows Nest (33/11kV) | [8 empty] | Supply |  | T029 - Postmans Ridge BSP
| Description |  |  |  | Region is South West
Transformer size is 1x33/11kV 6.3MVA ONAN;1x33/11kV 1.5MVA ON(Standby)
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.3%, 2021 S 0.5% W 0.5%, 2022 S 0.4% W 0.4%, 2023 S 0.5% W 0.5%, 2024 S 0.2% W 0.2%
|  |  | Latest Peak Compensated Load | [5 empty] | 4.3 MVA on 15/07/2019 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 8.3 | 8.3 | 8.3 |  | 8.3 |  | 8.3 | 9.4 |  | 9.4 |  | 9.4 | 9.4 | 9.4
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 4.4 | 4.4 | 4.4 |  | 4.5 |  | 4.5 | 4.7 |  | 4.7 |  | 4.7 | 4.7 | 4.8
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.991 | 0.991 | 0.991 |  | 0.991 |  | 0.991 | 0.998 |  | 0.998 |  | 0.998 | 0.998 | 0.998
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 4 | 4 | 4 |  | 4.1 |  | 4.1 | 4.5 |  | 4.5 |  | 4.5 | 4.5 | 4.5
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 5.5 | 5.5 | 5.5 |  | 5.5 |  | 5.5 | 5.5 |  | 5.5 |  | 5.5 | 5.5 | 5.5
|  |  |  | Raw LAR (MVA) |  | 4 | 4 | 4 |  | 4.1 |  | 4.1 | 4.5 |  | 4.5 |  | 4.5 | 4.5 | 4.5
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 1.5 | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.5 | 1.5
|  |  |  | Mobile Plant Avail (MVA) |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## CROY
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | CROY - Croydon (66/22kV) | [8 empty] | Supply |  | GEOR - Georgetown BSP
| Description |  |  |  | Region is Far North
Transformer size is 2x66/22kV 2MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.8%, 2021 S -0.1% W -0.1%2022 S -0.2% W -0.2%2023 S -0.0% W -0.0%2024 S -0.3% W -0.3
|  |  | Latest Peak Compensated Load | [5 empty] | 0.6 MVA on 19/11/2019 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 5.1 | 5.1 | 5.1 |  | 5.1 |  | 5.1 | 5.4 |  | 5.4 |  | 5.4 | 5.4 | 5.4
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.99 | 0.99 | 0.99 |  | 0.99 |  | 0.99 | 0.961 |  | 0.961 |  | 0.961 | 0.961 | 0.961
|  |  |  | ECC Rating (MVA) |  | 3 | 3 | 3 |  | 3 |  | 3 | 3 |  | 3 |  | 3 | 3 | 3
|  |  |  | 50 PoE Load (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 13 | 13 | 13 |  | 13 |  | 13 | 13 |  | 13 |  | 13 | 13 | 13
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## CUNN
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | CUNN - Cunnamulla (66/22kV) | [8 empty] | Supply |  | ROMA - Roma 66kV BSP
| Description |  |  |  | Region is South West
Transformer size is 1x66/11kV 5 MVA;1x66/22kV 5 MVA;1x22/11kV 3 MVA(Standby)
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.0%, 2021 S 0.0% W 0.0%, 2022 S 0.0% W 0.0%, 2023 S 0.0% W 0.0%, 2024 S 0.0% W 0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 4.3 MVA on 09/01/2020 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 11.3 | 11.3 | 11.3 |  | 11.3 |  | 11.3 | 13.9 |  | 13.9 |  | 13.9 | 13.9 | 13.9
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 4.7 | 4.7 | 4.7 |  | 4.7 |  | 4.8 | 3.8 |  | 3.8 |  | 3.8 | 3.8 | 3.8
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.999 | 0.999 | 0.999 |  | 0.999 |  | 0.999 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | ECC Rating (MVA) |  | 6.5 | 6.5 | 6.5 |  | 6.5 |  | 6.5 | 7.2 |  | 7.2 |  | 7.2 | 7.2 | 7.2
|  |  |  | 50 PoE Load (MVA) |  | 4.2 | 4.2 | 4.3 |  | 4.3 |  | 4.3 | 3.6 |  | 3.6 |  | 3.6 | 3.5 | 3.6
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 14 | 14 | 14 |  | 14 |  | 14 | 14 |  | 14 |  | 14 | 14 | 14
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## DACE
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | DACE - Dalby Central (33/11kV) | [8 empty] | Supply |  | T002 - Dalby East BSP
| Description |  |  |  | Region is South West
Transformer size is 2x33/11kV 16/20MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.5%, 2021 S -0.1% W -0.1%2022 S -0.4% W -0.4%2023 S -0.3% W -0.3%2024 S -0.2% W -0.2
|  |  | Latest Peak Compensated Load | [5 empty] | 15.3 MVA on 11/12/2019 at 16:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 47.6 | 47.6 | 47.6 |  | 47.6 |  | 47.6 | 50.9 |  | 50.9 |  | 50.9 | 50.9 | 50.9
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 19.3 | 19.2 | 19.2 |  | 19.2 |  | 19.2 | 13.6 |  | 13.5 |  | 13.4 | 13.3 | 13.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.964 | 0.964 | 0.964 |  | 0.964 |  | 0.964 | 0.974 |  | 0.974 |  | 0.974 | 0.974 | 0.974
|  |  |  | ECC Rating (MVA) |  | 26.4 | 26.4 | 26.4 |  | 26.4 |  | 26.4 | 28.1 |  | 28.1 |  | 28.1 | 28.1 | 28.1
|  |  |  | 50 PoE Load (MVA) |  | 16.9 | 16.8 | 16.8 |  | 16.8 |  | 16.8 | 12.7 |  | 12.6 |  | 12.5 | 12.4 | 12.4
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.8 | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  |  | Hours PA > 95% Peak Load |  | 8 | 8 | 8 |  | 8 |  | 8 | 8 |  | 8 |  | 8 | 8 | 8
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## DAGL
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | DAGL - Dan Gleeson (66/11kV) | [8 empty] | Supply |  | TMES - Townsville Mesh
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/11kV 15/20/25MVA ONAN/ODAN/ODAF;1x66/11kV 15/20/25MVA ONAN/ONAF/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.5%, 2021 S 0.5% W 0.5%, 2022 S 0.4% W 0.4%, 2023 S 0.5% W 0.5%, 2024 S 0.3% W 0.3%
|  |  | Latest Peak Compensated Load | [5 empty] | 29 MVA on 12/02/2020 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 42.6 | 42.6 | 42.6 |  | 42.6 |  | 42.6 | 39.8 |  | 39.8 |  | 39.8 | 39.8 | 39.8
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 36.2 | 36.4 | 36.5 |  | 36.8 |  | 37.1 | 16.4 |  | 16.5 |  | 16.4 | 16.4 | 16.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.984 | 0.984 | 0.984 |  | 0.984 |  | 0.984 | 0.99 |  | 0.99 |  | 0.99 | 0.99 | 0.99
|  |  |  | ECC Rating (MVA) |  | 28.1 | 28.1 | 28.1 |  | 28.1 |  | 28.1 | 26.3 |  | 26.3 |  | 26.3 | 26.3 | 26.3
|  |  |  | 50 PoE Load (MVA) |  | 29.7 | 29.9 | 30 |  | 30.2 |  | 30.4 | 16 |  | 16 |  | 16 | 16 | 16.1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 1.5 | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 0.8 |  | 0.8 |  | 0.8 | 0.8 | 0.8
|  |  |  | Hours PA > 95% Peak Load |  | 14 | 14 | 14 |  | 14 |  | 14 | 14 |  | 14 |  | 14 | 14 | 14
|  |  |  | Raw LAR (MVA) |  | 1.6 | 1.8 | 1.9 |  | 2.1 |  | 2.3
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 2.4 | 2.4 | 2.4 |  | 2.4 |  | 2.4 | 2.4 |  | 2.4 |  | 2.4 | 2.4 | 2.4
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## DEGI
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | DEGI - Degilbo (66/11kV) | [8 empty] | Supply |  | ISIS - Isis BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 2x66/11kV 2MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 2.8 MVA
Growth Rates |  |  |  |  | 2020 W 0.2%, 2021 S 0.1% W 0.1%, 2022 S -0.1% W -0.1%2023 S 0.1% W 0.1%, 2024 S -0.2% W -0.2
|  |  | Latest Peak Compensated Load | [5 empty] | 2.4 MVA on 16/12/2019 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 5.1 | 5.1 | 5.1 |  | 5.1 |  | 5.1 | 5.9 |  | 5.9 |  | 5.9 | 5.9 | 5.9
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 2.5 | 3 | 3.5 |  | 3.5 |  | 3.5 | 2.2 |  | 2.7 |  | 3.1 | 3.1 | 3.1
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.969 | 0.969 | 0.969 |  | 0.969 |  | 0.969 | 0.982 |  | 0.982 |  | 0.982 | 0.982 | 0.982
|  |  |  | ECC Rating (MVA) |  | 2.9 | 2.9 | 2.9 |  | 2.9 |  | 2.9 | 3 |  | 3 |  | 3 | 3 | 3
|  |  |  | 50 PoE Load (MVA) |  | 2.3 | 2.8 | 3.3 |  | 3.3 |  | 3.3 | 2 |  | 2.5 |  | 2.9 | 2.9 | 2.9
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.2 |  | 0.2 |  | 0.2 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 3 | 3 | 3 |  | 3 |  | 3 | 3 |  | 3 |  | 3 | 3 | 3
|  |  |  | Raw LAR (MVA) |  |  |  | 0.4 |  | 0.4 |  | 0.4
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## DIMB
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | DIMB - Dimbulah (66/22kV) | [8 empty] | Supply |  | TURK - Turkinje 66kV BSP
| Description |  |  |  | Region is Far North
Transformer size is 2x66/22kV 10MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.3%, 2021 S -1.8% W -1.8%2022 S -2.6% W -2.6%2023 S -2.4% W -2.4%2024 S -1.5% W -1.5
|  |  | Latest Peak Compensated Load | [5 empty] | 4.8 MVA on 14/12/2019 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 24.2 | 24.2 | 24.2 |  | 24.2 |  | 24.2 | 25.9 |  | 25.9 |  | 25.9 | 25.9 | 25.9
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 5 | 4.9 | 4.8 |  | 4.7 |  | 4.7 | 4 |  | 3.9 |  | 3.8 | 3.7 | 3.6
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.928 | 0.928 | 0.928 |  | 0.928 |  | 0.928 | 0.941 |  | 0.941 |  | 0.941 | 0.941 | 0.941
|  |  |  | ECC Rating (MVA) |  | 13.2 | 13.2 | 13.2 |  | 13.2 |  | 13.2 | 14.4 |  | 14.4 |  | 14.4 | 14.4 | 14.4
|  |  |  | 50 PoE Load (MVA) |  | 4.9 | 4.8 | 4.6 |  | 4.6 |  | 4.5 | 3.7 |  | 3.6 |  | 3.5 | 3.4 | 3.4
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 3 | 3 | 3 |  | 3 |  | 3 | 3 |  | 3 |  | 3 | 3 | 3
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## DISR
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | DISR - Disraeli (66/11kV) | [8 empty] | Supply |  | T193 - Clare South BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1xDISR TX NO 1-66/11KV TRANSF 1
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.0%, 2021 S 0.0% W 0.0%, 2022 S 0.0% W 0.0%, 2023 S 0.0% W 0.0%, 2024 S 0.0% W 0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 0.1 MVA on 11/11/2019 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 4 | 4 | 4 |  | 4 |  | 4 | 4 |  | 4 |  | 4 | 4 | 4
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.95 | 0.95 | 0.95 |  | 0.95 |  | 0.95 | 0.95 |  | 0.95 |  | 0.95 | 0.95 | 0.95
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | Raw LAR (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
Substation Category
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## DURO
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | DURO - Duchess Road (132/66kV) | [8 empty] | Supply |  | QMCL - Mica Creek 132kV TCP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 2x132/11kV 40/60MVA ONAN/ONAF;1x66/11kV 5/6.25MVA ONAN/ONAF(Standby)
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.9%, 2021 S -0.2% W -0.2%2022 S -0.3% W -0.3%2023 S -0.2% W -0.2%2024 S -0.4% W -0.4
|  |  | Latest Peak Compensated Load | [5 empty] | 34 MVA on 18/02/2020 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 79.6 | 79.6 | 79.6 |  | 79.6 |  | 79.6 | 84.4 |  | 84.4 |  | 84.4 | 84.4 | 84.4
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 36.6 | 36.5 | 36.4 |  | 36.4 |  | 36.4 | 20.7 |  | 20.6 |  | 20.4 | 20.3 | 20.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.991 | 0.991 | 0.991 |  | 0.991 |  | 0.991 | 0.996 |  | 0.996 |  | 0.996 | 0.996 | 0.996
|  |  |  | ECC Rating (MVA) |  | 39.8 | 39.8 | 39.8 |  | 39.8 |  | 39.8 | 42.2 |  | 42.2 |  | 42.2 | 42.2 | 42.2
|  |  |  | 50 PoE Load (MVA) |  | 33.9 | 33.8 | 33.8 |  | 33.8 |  | 33.8 | 19.7 |  | 19.6 |  | 19.4 | 19.3 | 19.3
|  |  |  | 50 PoE Load > 95% (MVA) |  | 1.7 | 1.7 | 1.7 |  | 1.7 |  | 1.7 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Hours PA > 95% Peak Load |  | 17 | 17 | 17 |  | 17 |  | 17 | 17 |  | 17 |  | 17 | 17 | 17
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## DYSA
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | DYSA - Dysart (66/22kV) | [8 empty] | Supply |  | T035 - Dysart BSP
| Description |  |  |  | Region is Capricornia
Transformer size is 2x20MVA 66kV Transformer
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -1.7%, 2021 S -0.2% W -0.2%2022 S -0.3% W -0.3%2023 S -0.1% W -0.1%2024 S -0.3% W -0.3
|  |  | Latest Peak Compensated Load | [5 empty] | 7.3 MVA on 16/12/2019 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 44 | 44 | 44 |  | 44 |  | 44 | 44 |  | 44 |  | 44 | 44 | 44
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 8.7 | 8.7 | 8.7 |  | 8.7 |  | 8.7 | 5 |  | 5 |  | 5 | 4.9 | 4.9
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.999 | 0.999 | 0.999 |  | 0.999 |  | 0.999 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | ECC Rating (MVA) |  | 23 | 23 | 23 |  | 23 |  | 23 | 26 |  | 26 |  | 26 | 26 | 26
|  |  |  | 50 PoE Load (MVA) |  | 7.8 | 7.8 | 7.8 |  | 7.8 |  | 7.8 | 4.8 |  | 4.7 |  | 4.7 | 4.7 | 4.7
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.4 | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 7.5 | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 | 7.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## EAAY
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | EAAY - East Ayr (66/11kV) | [8 empty] | Supply |  | T193 - Clare South BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 2x66/11kV 15/18/25MVA ONAN/ODAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.1%, 2021 S 0.3% W 0.3%, 2022 S 0.2% W 0.2%, 2023 S 0.4% W 0.4%, 2024 S 0.1% W 0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 13.7 MVA on 17/02/2020 at 20:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 64.9 | 64.9 | 64.9 |  | 64.9 |  | 64.9 | 69.9 |  | 69.9 |  | 69.9 | 69.9 | 69.9
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 16.3 | 16.3 | 16.4 |  | 16.4 |  | 16.5 | 9.1 |  | 9.1 |  | 9 | 9 | 9.1
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.999 | 0.999 | 1 |  | 1 |  | 1 | 0.999 |  | 0.999 |  | 0.999 | 0.999 | 0.999
|  |  |  | ECC Rating (MVA) |  | 37.1 | 37.1 | 37.1 |  | 37.1 |  | 37.1 | 37.4 |  | 37.4 |  | 37.4 | 37.4 | 37.4
|  |  |  | 50 PoE Load (MVA) |  | 13.8 | 13.9 | 13.9 |  | 14 |  | 14.1 | 8.8 |  | 8.8 |  | 8.8 | 8.8 | 8.8
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.7 | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  |  | Hours PA > 95% Peak Load |  | 12 | 12 | 12 |  | 12 |  | 12 | 12 |  | 12 |  | 12 | 12 | 12
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## EABU
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | EABU - East Bundaberg (66/11kV) | [8 empty] | Supply |  | BUND - Bundaberg BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 2x66/11kV 12/16MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 1.8 MVA
Growth Rates |  |  |  |  | 2020 W 1.2%, 2021 S 1.0% W 1.0%, 2022 S 0.9% W 0.9%, 2023 S 1.0% W 1.0%, 2024 S 0.7% W 0.7%
|  |  | Latest Peak Compensated Load | [5 empty] | 19.6 MVA on 17/02/2020 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 34.7 | 34.7 | 34.7 |  | 34.7 |  | 34.7 | 40.8 |  | 40.8 |  | 40.8 | 40.8 | 40.8
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 21.5 | 22.5 | 24 |  | 24.8 |  | 25 | 19.3 |  | 20.1 |  | 21.4 | 22 | 22.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 1 | 1 | 1 |  | 0.999 |  | 0.999 | 0.999 |  | 0.999 |  | 1 | 1 | 1
|  |  |  | ECC Rating (MVA) |  | 20.4 | 20.4 | 20.4 |  | 20.4 |  | 20.4 | 23.3 |  | 23.3 |  | 23.3 | 23.3 | 23.3
|  |  |  | 50 PoE Load (MVA) |  | 19.9 | 20.7 | 22.1 |  | 22.8 |  | 23.1 | 18.1 |  | 18.9 |  | 20 | 20.5 | 20.7
|  |  |  | 50 PoE Load > 95% (MVA) |  | 1 | 1 | 1.1 |  | 1.1 |  | 1.2 | 0.9 |  | 0.9 |  | 1 | 1 | 1
|  |  |  | Hours PA > 95% Peak Load |  | 23 | 23 | 23 |  | 23 |  | 23 | 23 |  | 23 |  | 23 | 23 | 23
|  |  |  | Raw LAR (MVA) |  |  | 0.3 | 1.7 |  | 2.4 |  | 2.7
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 2.1 | 2.1 | 2.1 |  | 2.1 |  | 2.1 | 2.1 |  | 2.1 |  | 2.1 | 2.1 | 2.1
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | LARc (MVA) | [5 empty] | 0.3 |  | 0.6
|  |  |  | LARc (MW) | [5 empty] | 0.3 |  | 0.6
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | No |  | No | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## EATO
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | EATO - East Toowoomba (33/11kV) | [8 empty] | Supply |  | T043 - South Toowoomba BSP
| Description |  |  |  | Region is South West
Transformer size is 2x33/11kV 15/18/25MVA ONAN/OFDAN/OFDAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -1.0%, 2021 S -0.1% W -0.1%2022 S -0.5% W -0.5%2023 S -0.4% W -0.4%2024 S -0.3% W -0.3
|  |  | Latest Peak Compensated Load | [5 empty] | 31.2 MVA on 15/07/2019 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 56.3 | 56.3 | 56.3 |  | 56.3 |  | 56.3 | 66.1 |  | 66.1 |  | 66.1 | 66.1 | 66.1
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 26.9 | 26.7 | 26.6 |  | 26.7 |  | 26.7 | 33.4 |  | 33.3 |  | 32.9 | 32.6 | 32.7
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.981 | 0.981 | 0.981 |  | 0.981 |  | 0.981 | 0.991 |  | 0.991 |  | 0.991 | 0.991 | 0.991
|  |  |  | ECC Rating (MVA) |  | 28.1 | 28.1 | 28.1 |  | 28.1 |  | 28.1 | 34.3 |  | 34.3 |  | 34.3 | 34.3 | 34.3
|  |  |  | 50 PoE Load (MVA) |  | 23.5 | 23.4 | 23.4 |  | 23.4 |  | 23.4 | 30.4 |  | 30.2 |  | 29.8 | 29.6 | 29.7
|  |  |  | 50 PoE Load > 95% (MVA) |  | 1.2 | 1.2 | 1.2 |  | 1.2 |  | 1.2 | 1.5 |  | 1.5 |  | 1.5 | 1.5 | 1.5
|  |  |  | Hours PA > 95% Peak Load |  | 3.5 | 3.5 | 3.5 |  | 3.5 |  | 3.5 | 3.5 |  | 3.5 |  | 3.5 | 3.5 | 3.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 5.5 | 5.5 | 5.5 |  | 5.5 |  | 5.5 | 5.5 |  | 5.5 |  | 5.5 | 5.5 | 5.5
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## EDMO
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | EDMO - Edmonton (132/22kV) | [8 empty] | Supply |  | QEMT - Edmonton TCP
| Description |  |  |  | Region is Far North
Transformer size is 2xEDMOSS TRANSFORMER
Capacity of commissioned Embedded Generation (with Connection Agreements) is 16.3 MVA
Growth Rates |  |  |  |  | 2020 W 0.7%, 2021 S 0.9% W 0.9%, 2022 S 0.8% W 0.8%, 2023 S 0.9% W 0.9%, 2024 S 0.7% W 0.7%
|  |  | Latest Peak Compensated Load | [5 empty] | 45.9 MVA on 14/02/2020 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 75 | 75 | 75 |  | 75 |  | 75 | 75 |  | 75 |  | 75 | 75 | 75
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 48.7 | 49.1 | 49.6 |  | 50.2 |  | 50.7 | 29.5 |  | 29.7 |  | 29.8 | 29.9 | 30.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 1 | 1 | 1 |  | 1 |  | 1 | 0.998 |  | 0.998 |  | 0.998 | 0.998 | 0.998
|  |  |  | ECC Rating (MVA) |  | 50 | 50 | 50 |  | 50 |  | 50 | 50 |  | 50 |  | 50 | 50 | 50
|  |  |  | 50 PoE Load (MVA) |  | 44.5 | 44.9 | 45.4 |  | 45.9 |  | 46.4 | 29.2 |  | 29.3 |  | 29.4 | 29.5 | 29.9
|  |  |  | 50 PoE Load > 95% (MVA) |  | 2.2 | 2.2 | 2.3 |  | 2.3 |  | 2.3 | 1.5 |  | 1.5 |  | 1.5 | 1.5 | 1.5
|  |  |  | Hours PA > 95% Peak Load |  | 9.5 | 9.5 | 9.5 |  | 9.5 |  | 9.5 | 9.5 |  | 9.5 |  | 9.5 | 9.5 | 9.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 6 | 6 | 6 |  | 6 |  | 6 | 6 |  | 6 |  | 6 | 6 | 6
|  |  |  | Mobile Plant Avail (MVA) |  | 4 | 4 | 4 |  | 4 |  | 4 | 4 |  | 4 |  | 4 | 4 | 4
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## EIDS
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | EIDS - Eidsvold (66/11kV) | [8 empty] | Supply |  | ISIS - Isis BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 1x62/11kV 2MVA ON;1x66/11kV 2MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.0%, 2021 S -0.0% W -0.0%2022 S -0.2% W -0.2%2023 S 0.0% W 0.0%, 2024 S -0.2% W -0.2
|  |  | Latest Peak Compensated Load | [5 empty] | 1.8 MVA on 10/12/2019 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 4.5 | 4.5 | 4.5 |  | 4.5 |  | 4.5 | 5.3 |  | 5.3 |  | 5.3 | 5.3 | 5.3
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 2.2 | 2.2 | 2.2 |  | 2.2 |  | 2.2 | 1.5 |  | 1.5 |  | 1.5 | 1.5 | 1.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.987 | 0.984 | 0.987 |  | 0.987 |  | 0.987 | 0.993 |  | 0.993 |  | 0.993 | 0.993 | 0.993
|  |  |  | ECC Rating (MVA) |  | 2.7 | 2.7 | 2.7 |  | 2.7 |  | 2.7 | 3 |  | 3 |  | 3 | 3 | 3
|  |  |  | 50 PoE Load (MVA) |  | 2 | 1.9 | 2 |  | 2 |  | 2 | 1.4 |  | 1.4 |  | 1.4 | 1.4 | 1.4
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 18 | 18 | 18 |  | 18 |  | 18 | 18 |  | 18 |  | 18 | 18 | 18
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## ELRO
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | ELRO - Ellwoods Road (66/11kV) | [8 empty] | Supply |  | H018 - Tarong BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 1x66/11kV 4.1MVA ONAN;1x66/11kV 4.1MVA ONAN(Standby)
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -1.1%, 2021 S -0.1% W -0.1%2022 S -0.3% W -0.3%2023 S 0.1% W 0.1%, 2024 S -0.3% W -0.3
|  |  | Latest Peak Compensated Load | [5 empty] | 2.5 MVA on 27/06/2019 at 07:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 10 | 10 | 10 |  | 10 |  | 10 | 11 |  | 11 |  | 11 | 11 | 11
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 4.4 | 7.3 | 7.3 |  | 7.3 |  | 7.3 | 2.5 |  | 3 |  | 3.5 | 3.5 | 3.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.932 | 0.945 | 0.945 |  | 0.945 |  | 0.945 | 0.904 |  | 0.904 |  | 0.904 | 0.904 | 0.904
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 3 | 3.4 | 3.4 |  | 3.4 |  | 3.4 | 2.4 |  | 2.9 |  | 3.4 | 3.3 | 3.4
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.1 |  | 0.1 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 58.5 | 58.5 | 58.5 |  | 58.5 |  | 58.5 | 58.5 |  | 58.5 |  | 58.5 | 58.5 | 58.5
|  |  |  | Raw LAR (MVA) |  | 3 | 3.4 | 3.4 |  | 3.4 |  | 3.4 | 2.4 |  | 2.9 |  | 3.4 | 3.3 | 3.4
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 4.1 | 4.1 | 4.1 |  | 4.1 |  | 4.1 | 4.1 |  | 4.1 |  | 4.1 | 4.1 | 4.1
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## EMER
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | EMER - Emerald (66/22kV) | [8 empty] | Supply |  | H015 - Lilyvale BSP
| Description |  |  |  | Region is Capricornia
Transformer size is 2x66/22kV 15/20MVA ONAN/ONAF;1x66/22kV 16/20MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.6%, 2021 S 0.1% W 0.1%, 2022 S -0.1% W -0.1%2023 S 0.1% W 0.1%, 2024 S -0.1% W -0.1
|  |  | Latest Peak Compensated Load | [5 empty] | 32.9 MVA on 16/12/2019 at 17:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 69.6 | 69.6 | 69.6 |  | 69.6 |  | 69.6 | 81.1 |  | 81.1 |  | 81.1 | 81.1 | 81.1
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 38.6 | 38.6 | 38.7 |  | 38.8 |  | 38.8 | 24.4 |  | 24.3 |  | 24.2 | 24.1 | 24.2
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 1 | 1 | 1 |  | 1 |  | 1 | 0.993 |  | 0.993 |  | 0.993 | 0.993 | 0.993
|  |  |  | ECC Rating (MVA) |  | 52.9 | 52.9 | 52.9 |  | 52.9 |  | 52.9 | 58.4 |  | 58.4 |  | 58.4 | 58.4 | 58.4
|  |  |  | 50 PoE Load (MVA) |  | 34.7 | 34.7 | 34.7 |  | 34.8 |  | 34.9 | 22.8 |  | 22.8 |  | 22.6 | 22.5 | 22.6
|  |  |  | 50 PoE Load > 95% (MVA) |  | 1.7 | 1.7 | 1.7 |  | 1.7 |  | 1.7 | 1.1 |  | 1.1 |  | 1.1 | 1.1 | 1.1
|  |  |  | Hours PA > 95% Peak Load |  | 9.5 | 9.5 | 9.5 |  | 9.5 |  | 9.5 | 9.5 |  | 9.5 |  | 9.5 | 9.5 | 9.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## ETON
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | ETON - Eton (33/11kV) | [8 empty] | Supply |  | T065 - Alligator Creek BSP
| Description |  |  |  | Region is Mackay
Transformer size is 2x33/11kV 7.5/5MVA ONAF/ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.1%, 2021 S 0.1% W 0.1%, 2022 S 0.0% W 0.0%, 2023 S 0.1% W 0.1%, 2024 S 0.0% W 0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 7.8 MVA on 14/12/2019 at 19:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 14.1 | 14.1 | 14.1 |  | 14.1 |  | 14.1 | 15 |  | 15 |  | 15 | 15 | 15
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 7.9 | 7.9 | 7.9 |  | 7.9 |  | 8 | 4.2 |  | 4.2 |  | 4.2 | 4.2 | 4.2
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 1 | 1 | 1 |  | 1 |  | 1 | 0.92 |  | 0.92 |  | 0.92 | 0.92 | 0.92
|  |  |  | ECC Rating (MVA) |  | 7.5 | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 | 7.5
|  |  |  | 50 PoE Load (MVA) |  | 7.7 | 7.7 | 7.7 |  | 7.7 |  | 7.8 | 3.6 |  | 3.5 |  | 3.5 | 3.5 | 3.5
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.4 | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 11 | 11 | 11 |  | 11 |  | 11 | 11 |  | 11 |  | 11 | 11 | 11
|  |  |  | Raw LAR (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.3
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 1.5 | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.5 | 1.5
|  |  |  | Mobile Plant Avail (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## EUDA
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | EUDA - Eungella Dam (66/11kV) | [8 empty] | Supply |  | PIVA - Pioneer Valley BSP
| Description |  |  |  | Region is Mackay
Transformer size is 1x66/11kV 1MVA ONAN;1x66/11kV 5MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.0%, 2021 S 0.0% W 0.0%, 2022 S 0.0% W 0.0%, 2023 S 0.0% W 0.0%, 2024 S 0.0% W 0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 0.9 MVA on 01/01/2020 at 17:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6 | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 0.9 | 0.9 | 0.9 |  | 0.9 |  | 0.9 | 0.9 |  | 0.9 |  | 0.9 | 0.9 | 0.9
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.888 | 0.888 | 0.888 |  | 0.888 |  | 0.888 | 0.889 |  | 0.889 |  | 0.889 | 0.889 | 0.889
|  |  |  | ECC Rating (MVA) |  | 1.1 | 1.1 | 1.1 |  | 1.1 |  | 1.1 | 1.2 |  | 1.2 |  | 1.2 | 1.2 | 1.2
|  |  |  | 50 PoE Load (MVA) |  | 0.9 | 0.9 | 0.9 |  | 0.9 |  | 0.9 | 0.9 |  | 0.9 |  | 0.9 | 0.9 | 0.9
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 6989 | 6989 | 6989 |  | 6989 |  | 6989 | 6989 |  | 6989 |  | 6989 | 6989 | 6989
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## EVEL
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | EVEL - Evelyn (66/22kV) | [8 empty] | Supply |  | TURK - Turkinje 66kV BSP
| Description |  |  |  | Region is Far North
Transformer size is 1x66/22kV 6.3 MVA
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.2%, 2021 S 0.1% W 0.1%, 2022 S -0.1% W -0.1%2023 S 0.1% W 0.1%, 2024 S -0.1% W -0.1
|  |  | Latest Peak Compensated Load | [5 empty] | 1.5 MVA on 30/11/2019 at 17:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 9.4 | 9.4 | 9.4 |  | 9.4 |  | 9.4 | 9.4 |  | 9.4 |  | 9.4 | 9.4 | 9.4
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 1.5 | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.5 | 1.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.957 | 0.957 | 0.957 |  | 0.957 |  | 0.957 | 0.977 |  | 0.977 |  | 0.976 | 0.976 | 0.976
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 1.4 | 1.4 | 1.4 |  | 1.4 |  | 1.4 | 1.5 |  | 1.5 |  | 1.4 | 1.4 | 1.4
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 28.5 | 28.5 | 28.5 |  | 28.5 |  | 28.5 | 28.5 |  | 28.5 |  | 28.5 | 28.5 | 28.5
|  |  |  | Raw LAR (MVA) |  | 1.4 | 1.4 | 1.4 |  | 1.4 |  | 1.4 | 1.5 |  | 1.5 |  | 1.4 | 1.4 | 1.4
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 2.5 | 2.5 | 2.5 |  | 2.5 |  | 2.5 | 2.5 |  | 2.5 |  | 2.5 | 2.5 | 2.5
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 1.3 | 1.3 | 1.3 |  | 1.3 |  | 1.3 | 1.3 |  | 1.3 |  | 1.3 | 1.3 | 1.3
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## FARL
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | FARL - Farleigh (33/11kV) | [8 empty] | Supply |  | MACK - Mackay BSP
| Description |  |  |  | Region is Mackay
Transformer size is 1x33/11kV 5/7.5MVA ONAF/ONAN;1x33/11kV 5/7.5MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 14.4 MVA
Growth Rates |  |  |  |  | 2020 W 0.7%, 2021 S 0.0% W 0.0%, 2022 S -0.3% W -0.3%2023 S -0.2% W -0.2%2024 S -0.2% W -0.2
|  |  | Latest Peak Compensated Load | [5 empty] | 3.9 MVA on 22/01/2020 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 11 | 11 | 11 |  | 11 |  | 11 | 11 |  | 11 |  | 11 | 11 | 11
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 4.4 | 4.4 | 4.4 |  | 4.4 |  | 4.4 | 3.9 |  | 3.9 |  | 3.9 | 3.9 | 3.9
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.982 | 0.982 | 0.982 |  | 0.982 |  | 0.982 | 0.989 |  | 0.989 |  | 0.989 | 0.989 | 0.989
|  |  |  | ECC Rating (MVA) |  | 6 | 6 | 6 |  | 6 |  | 6 | 6 |  | 6 |  | 6 | 6 | 6
|  |  |  | 50 PoE Load (MVA) |  | 4 | 4 | 4 |  | 4 |  | 4 | 3.8 |  | 3.8 |  | 3.8 | 3.7 | 3.7
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 16.5 | 16.5 | 16.5 |  | 16.5 |  | 16.5 | 16.5 |  | 16.5 |  | 16.5 | 16.5 | 16.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 | 2 | 2
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## FARN
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | FARN - Farnsfield (66/11kV) | [8 empty] | Supply |  | ISIS - Isis BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 2x66/11kV 10/12.5MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.1%, 2021 S 0.1% W 0.1%, 2022 S 0.0% W 0.0%, 2023 S 0.1% W 0.1%, 2024 S -0.0% W -0.0
|  |  | Latest Peak Compensated Load | [5 empty] | 11.9 MVA on 10/01/2020 at 20:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 28.9 | 28.9 | 28.9 |  | 28.9 |  | 28.9 | 37.4 |  | 37.4 |  | 37.4 | 37.4 | 37.4
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 12.3 | 12.3 | 12.3 |  | 12.4 |  | 12.4 | 9.3 |  | 9.3 |  | 9.2 | 9.2 | 9.2
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.854 | 0.854 | 0.854 |  | 0.854 |  | 0.854 | 0.824 |  | 0.824 |  | 0.824 | 0.824 | 0.824
|  |  |  | ECC Rating (MVA) |  | 15.9 | 15.9 | 15.9 |  | 15.9 |  | 15.9 | 18.7 |  | 18.7 |  | 18.7 | 18.7 | 18.7
|  |  |  | 50 PoE Load (MVA) |  | 12 | 12 | 12 |  | 12.1 |  | 12.1 | 8.1 |  | 8 |  | 8 | 8 | 8
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  |  | Hours PA > 95% Peak Load |  | 9.5 | 9.5 | 9.5 |  | 9.5 |  | 9.5 | 9.5 |  | 9.5 |  | 9.5 | 9.5 | 9.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## FREN
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | FREN - Frenchville (66/11kV) | [8 empty] | Supply |  | RMES - Rockhampton Mesh
| Description |  |  |  | Region is Capricornia
Transformer size is 2x66/11kV 15/20MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.4%, 2021 S 0.5% W 0.5%, 2022 S 0.4% W 0.4%, 2023 S 0.4% W 0.4%, 2024 S 0.2% W 0.2%
|  |  | Latest Peak Compensated Load | [5 empty] | 18.8 MVA on 16/12/2019 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 48 | 48 | 48 |  | 48 |  | 48 | 48 |  | 48 |  | 48 | 48 | 48
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 21.4 | 21.5 | 21.6 |  | 21.8 |  | 21.9 | 10.9 |  | 10.9 |  | 10.9 | 10.9 | 11
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.985 | 0.985 | 0.985 |  | 0.985 |  | 0.985 | 0.994 |  | 0.994 |  | 0.994 | 0.994 | 0.994
|  |  |  | ECC Rating (MVA) |  | 24 | 24 | 24 |  | 24 |  | 24 | 24 |  | 24 |  | 24 | 24 | 24
|  |  |  | 50 PoE Load (MVA) |  | 18.8 | 18.9 | 19 |  | 19.1 |  | 19.2 | 10.5 |  | 10.5 |  | 10.4 | 10.4 | 10.5
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.9 | 0.9 | 1 |  | 1 |  | 1 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | Hours PA > 95% Peak Load |  | 3 | 3 | 3 |  | 3 |  | 3 | 3 |  | 3 |  | 3 | 3 | 3
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## GARB
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | GARB - Garbutt (66/11kV) | [8 empty] | Supply |  | TMES - Townsville Mesh
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/11kV 21/26.25/35MVA ONAN/ODAN/ODAF;1x66/11kV 21/26.25/35MVA ONAN/ONAF/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.0%, 2021 S -0.7% W -0.7%2022 S -0.9% W -0.9%2023 S -0.6% W -0.6%2024 S -0.6% W -0.6
|  |  | Latest Peak Compensated Load | [5 empty] | 29.1 MVA on 20/01/2020 at 13:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 53.8 | 53.8 | 53.8 |  | 53.8 |  | 53.8 | 54 |  | 54 |  | 54 | 54 | 54
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 31.2 | 30.9 | 30.7 |  | 30.7 |  | 30.6 | 19.4 |  | 19.2 |  | 18.9 | 18.7 | 18.6
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.944 | 0.944 | 0.944 |  | 0.944 |  | 0.944 | 0.934 |  | 0.934 |  | 0.934 | 0.934 | 0.934
|  |  |  | ECC Rating (MVA) |  | 29.8 | 29.8 | 29.8 |  | 29.8 |  | 29.8 | 30.8 |  | 30.8 |  | 30.8 | 30.8 | 30.8
|  |  |  | 50 PoE Load (MVA) |  | 28.7 | 28.5 | 28.3 |  | 28.3 |  | 28.2 | 18.6 |  | 18.4 |  | 18.1 | 17.9 | 17.9
|  |  |  | 50 PoE Load > 95% (MVA) |  | 1.4 | 1.4 | 1.4 |  | 1.4 |  | 1.4 | 0.9 |  | 0.9 |  | 0.9 | 0.9 | 0.9
|  |  |  | Hours PA > 95% Peak Load |  | 17.5 | 17.5 | 17.5 |  | 17.5 |  | 17.5 | 17.5 |  | 17.5 |  | 17.5 | 17.5 | 17.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 11.8 | 11.8 | 11.8 |  | 11.8 |  | 11.8 | 11.8 |  | 11.8 |  | 11.8 | 11.8 | 11.8
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 6 | 6 | 6 |  | 6 |  | 6 | 6 |  | 6 |  | 6 | 6 | 6
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## GAYN
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | GAYN - Gayndah (66/11kV) | [8 empty] | Supply |  | ISIS - Isis BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 2x66/11kV 7.5/10MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.3%, 2021 S -0.6% W -0.6%2022 S -0.9% W -0.9%2023 S -0.7% W -0.7%2024 S -0.6% W -0.6
|  |  | Latest Peak Compensated Load | [5 empty] | 5.7 MVA on 16/12/2019 at 17:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 24.6 | 24.6 | 24.6 |  | 24.6 |  | 24.6 | 27.1 |  | 27.1 |  | 27.1 | 27.1 | 27.1
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 6.5 | 6.5 | 6.4 |  | 6.4 |  | 6.4 | 5 |  | 5 |  | 4.9 | 4.8 | 4.8
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.954 | 0.954 | 0.954 |  | 0.954 |  | 0.954 | 0.953 |  | 0.953 |  | 0.953 | 0.953 | 0.953
|  |  |  | ECC Rating (MVA) |  | 14.3 | 14.3 | 14.3 |  | 14.3 |  | 14.3 | 15 |  | 15 |  | 15 | 15 | 15
|  |  |  | 50 PoE Load (MVA) |  | 6 | 5.9 | 5.9 |  | 5.9 |  | 5.8 | 4.7 |  | 4.7 |  | 4.6 | 4.5 | 4.5
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 13 | 13 | 13 |  | 13 |  | 13 | 13 |  | 13 |  | 13 | 13 | 13
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## GEOR
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | GEOR - Georgetown (66/22kV) | [8 empty] | Supply |  | GEOR - Georgetown BSP
| Description |  |  |  | Region is Far North
Transformer size is 2x66/22kV 2MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.6%, 2021 S -0.2% W -0.2%2022 S -0.3% W -0.3%2023 S -0.1% W -0.1%2024 S -0.4% W -0.4
|  |  | Latest Peak Compensated Load | [5 empty] | 1.6 MVA on 04/12/2019 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 5.5 | 5.5 | 5.5 |  | 5.5 |  | 5.5 | 6 |  | 6 |  | 6 | 6 | 6
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 1.8 | 1.8 | 1.8 |  | 1.8 |  | 1.8 | 1.3 |  | 1.3 |  | 1.3 | 1.3 | 1.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.982 | 0.982 | 0.982 |  | 0.982 |  | 0.982 | 0.961 |  | 0.961 |  | 0.961 | 0.961 | 0.961
|  |  |  | ECC Rating (MVA) |  | 3 | 3 | 3 |  | 3 |  | 3 | 3 |  | 3 |  | 3 | 3 | 3
|  |  |  | 50 PoE Load (MVA) |  | 1.7 | 1.7 | 1.7 |  | 1.7 |  | 1.7 | 1.3 |  | 1.3 |  | 1.3 | 1.3 | 1.3
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 9.5 | 9.5 | 9.5 |  | 9.5 |  | 9.5 | 9.5 |  | 9.5 |  | 9.5 | 9.5 | 9.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## GEOR1
Bulk Summary Information and Peak Load Forecast
Substation |  |  |  | GEOR - Georgetown BSP (132/66kV) | [8 empty] | Supply |  | QROS - Ross (Kidston and Milchester) TCP
Description |  |  |  | Region is Far North
Transformer size is 2x132/66/6.6kV 8MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 5.3 MVA
|  | Latest Peak Compensated Load | [5 empty] | 7.6 MVA on 04/12/2019 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[5 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  | NCC Rating (MVA) |  | 16.7 | 16.7 | 16.7 |  | 16.7 |  | 16.7 | 18 |  | 18 |  | 18 | 18 | 18
|  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | 10 PoE Load (MVA) |  | 8.4 | 8.4 | 8.4 |  | 8.4 |  | 8.4 | 6.2 |  | 6.1 |  | 6.1 | 6.1 | 6.1
LARn (MVA)
LARn (MW)
|  |  | Power Factor at Peak Load |  | 0.9 | 0.9 | 0.9 |  | 0.9 |  | 0.9 | 0.866 |  | 0.866 |  | 0.866 | 0.866 | 0.866
|  |  | ECC Rating (MVA) |  | 9.6 | 9.6 | 9.6 |  | 9.6 |  | 9.6 | 10 |  | 10 |  | 10 | 10 | 10
|  |  | 50 PoE Load (MVA) |  | 7.9 | 7.9 | 7.9 |  | 8 |  | 8 | 5.9 |  | 5.8 |  | 5.8 | 5.8 | 5.8
|  |  | 50 PoE Load > 95% (MVA) |  | 0.4 | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  | Hours PA > 95% Peak Load |  | 36 | 36 | 36 |  | 36 |  | 36 | 36 |  | 36 |  | 36 | 36 | 36
Raw LAR (MVA)
|  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## GIRU
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | GIRU - Giru (66/11kV) | [8 empty] | Supply |  | T193 - Clare South BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 2x66/11kV 4MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.2%, 2021 S 0.1% W 0.1%, 2022 S 0.0% W 0.0%, 2023 S 0.2% W 0.2%, 2024 S -0.1% W -0.1
|  |  | Latest Peak Compensated Load | [5 empty] | 2.2 MVA on 03/12/2019 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 9.5 | 9.5 | 9.5 |  | 9.5 |  | 9.5 | 10.5 |  | 10.5 |  | 10.5 | 10.5 | 10.5
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 2.2 | 2.2 | 2.2 |  | 2.3 |  | 2.3 | 1.5 |  | 1.5 |  | 1.5 | 1.5 | 1.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.897 | 0.897 | 0.897 |  | 0.897 |  | 0.897 | 0.896 |  | 0.896 |  | 0.896 | 0.896 | 0.896
|  |  |  | ECC Rating (MVA) |  | 5 | 5 | 5 |  | 5 |  | 5 | 5.4 |  | 5.4 |  | 5.4 | 5.4 | 5.4
|  |  |  | 50 PoE Load (MVA) |  | 2.2 | 2.2 | 2.2 |  | 2.2 |  | 2.2 | 1.5 |  | 1.5 |  | 1.5 | 1.5 | 1.5
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 333 | 333 | 333 |  | 333 |  | 333 | 333 |  | 333 |  | 333 | 333 | 333
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## GIVE
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | GIVE - Givelda (66/11kV) | [8 empty] | Supply |  | BUND - Bundaberg BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 1x66/11kV 10MVA ONAN;1x66/11kV 7.5/10MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.1%, 2021 S 0.0% W 0.0%, 2022 S -0.1% W -0.1%2023 S 0.1% W 0.1%, 2024 S -0.1% W -0.1
|  |  | Latest Peak Compensated Load | [5 empty] | 9 MVA on 21/11/2019 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 24.4 | 24.4 | 24.4 |  | 24.4 |  | 24.4 | 29.6 |  | 29.6 |  | 29.6 | 29.6 | 29.6
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 9.2 | 9.2 | 9.2 |  | 9.3 |  | 9.3 | 5.5 |  | 5.5 |  | 5.5 | 5.5 | 5.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.868 | 0.868 | 0.868 |  | 0.868 |  | 0.868 | 0.863 |  | 0.863 |  | 0.863 | 0.863 | 0.863
|  |  |  | ECC Rating (MVA) |  | 14.3 | 14.3 | 14.3 |  | 14.3 |  | 14.3 | 15 |  | 15 |  | 15 | 15 | 15
|  |  |  | 50 PoE Load (MVA) |  | 9 | 9 | 9 |  | 9 |  | 9 | 5.4 |  | 5.4 |  | 5.3 | 5.3 | 5.4
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Hours PA > 95% Peak Load |  | 99.5 | 99.5 | 99.5 |  | 99.5 |  | 99.5 | 99.5 |  | 99.5 |  | 99.5 | 99.5 | 99.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## GLEE
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | GLEE - Glenelg (66/33kV) | [8 empty] | Supply |  | T095 - Millchester BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/0.0191kV 0.63 MVA
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.1%, 2021 S -0.2% W -0.2%2022 S -0.2% W -0.2%2023 S -0.1% W -0.1%2024 S -0.3% W -0.3
|  |  | Latest Peak Compensated Load | [5 empty] | 0.6 MVA on 19/01/2020 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 0.7 | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.7 | 0.7
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.969 | 0.969 | 0.969 |  | 0.969 |  | 0.969 | 0.95 |  | 0.95 |  | 0.95 | 0.95 | 0.95
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 14 | 14 | 14 |  | 14 |  | 14 | 14 |  | 14 |  | 14 | 14 | 14
|  |  |  | Raw LAR (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## GLEL
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | GLEL - Glenella 11kV (66/11kV) | [8 empty] | Supply |  | PIVA - Pioneer Valley BSP
| Description |  |  |  | Region is Mackay
Transformer size is 2x66/11kV 19/26/32MVA ONAN/ODAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.3%, 2021 S 0.1% W 0.1%, 2022 S 0.0% W 0.0%, 2023 S 0.1% W 0.1%, 2024 S 0.0% W 0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 11 MVA on 20/02/2020 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 75.2 | 75.2 | 75.2 |  | 75.2 |  | 75.2 | 83.8 |  | 83.8 |  | 83.8 | 83.8 | 83.8
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 15.4 | 15.4 | 15.4 |  | 15.4 |  | 15.5 | 6.6 |  | 8.1 |  | 8 | 8 | 8
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.981 | 0.981 | 0.981 |  | 0.981 |  | 0.981 | 0.99 |  | 0.99 |  | 0.99 | 0.99 | 0.99
|  |  |  | ECC Rating (MVA) |  | 41.9 | 41.9 | 41.9 |  | 41.9 |  | 41.9 | 44.7 |  | 44.7 |  | 44.7 | 44.7 | 44.7
|  |  |  | 50 PoE Load (MVA) |  | 13.9 | 13.9 | 13.9 |  | 14 |  | 14 | 6.5 |  | 8 |  | 7.9 | 7.9 | 7.9
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.7 | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.3 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  |  | Hours PA > 95% Peak Load |  | 7 | 7 | 7 |  | 7 |  | 7 | 7 |  | 7 |  | 7 | 7 | 7
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## GLEN
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | GLEN - Glenden (66/11kV) | [8 empty] | Supply |  | NEWL - Newlands BSP
| Description |  |  |  | Region is Mackay
Transformer size is 2x66/11kV 7.5MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -1.7%, 2021 S -0.2% W -0.2%2022 S -0.3% W -0.3%2023 S -0.1% W -0.1%2024 S -0.3% W -0.3
|  |  | Latest Peak Compensated Load | [5 empty] | 1.6 MVA on 04/12/2019 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 15.6 | 15.6 | 15.6 |  | 15.6 |  | 15.6 | 16.7 |  | 16.7 |  | 16.7 | 16.7 | 16.7
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 1.7 | 1.7 | 1.7 |  | 1.7 |  | 1.7 | 1.3 |  | 1.3 |  | 1.3 | 1.2 | 1.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.996 | 0.996 | 0.996 |  | 0.996 |  | 0.996 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | ECC Rating (MVA) |  | 9.7 | 9.7 | 9.7 |  | 9.7 |  | 9.7 | 10.2 |  | 10.2 |  | 10.2 | 10.2 | 10.2
|  |  |  | 50 PoE Load (MVA) |  | 1.6 | 1.6 | 1.6 |  | 1.6 |  | 1.6 | 1.2 |  | 1.2 |  | 1.2 | 1.2 | 1.2
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 4.5 | 4.5 | 4.5 |  | 4.5 |  | 4.5 | 4.5 |  | 4.5 |  | 4.5 | 4.5 | 4.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 7.5 | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 | 7.5
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## GLFS
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | GLFS - Friend Street (66/11kV) | [8 empty] | Supply |  | T019 - Gladstone South BSP
| Description |  |  |  | Region is Capricornia
Transformer size is 1x66/11kV 16/20MVA ONAN/ONAF;1x66/11kV 24/32MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -1.1%, 2021 S -0.2% W -0.2%2022 S -0.5% W -0.5%2023 S -0.3% W -0.3%2024 S -0.3% W -0.3
|  |  | Latest Peak Compensated Load | [5 empty] | 18.4 MVA on 20/02/2020 at 16:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 47.4 | 47.4 | 47.4 |  | 47.4 |  | 47.4 | 53.3 |  | 53.3 |  | 53.3 | 53.3 | 53.3
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 20.2 | 20.1 | 20 |  | 20.1 |  | 20.1 | 10.4 |  | 10.4 |  | 10.3 | 10.2 | 10.2
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.998 | 0.998 | 0.998 |  | 0.998 |  | 0.998 | 0.945 |  | 0.945 |  | 0.945 | 0.945 | 0.945
|  |  |  | ECC Rating (MVA) |  | 27.2 | 27.2 | 27.2 |  | 27.2 |  | 27.2 | 29.8 |  | 29.8 |  | 29.8 | 29.8 | 29.8
|  |  |  | 50 PoE Load (MVA) |  | 18.5 | 18.4 | 18.4 |  | 18.4 |  | 18.4 | 9.7 |  | 9.7 |  | 9.6 | 9.5 | 9.5
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.9 | 0.9 | 0.9 |  | 0.9 |  | 0.9 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | Hours PA > 95% Peak Load |  | 1175 | 1175 | 1175 |  | 1175 |  | 1175 | 1175 |  | 1175 |  | 1175 | 1175 | 1175
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 2.2 | 2.2 | 2.2 |  | 2.2 |  | 2.2 | 2.2 |  | 2.2 |  | 2.2 | 2.2 | 2.2
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## GLNO
Bulk Summary Information and Peak Load Forecast
Substation |  |  |  | GLNO - Gladstone North BSP (132/66kV) | [8 empty] | Supply |  | H067 - Calliope River TCP
Description |  |  |  | Region is Capricornia
Transformer size is 2x132/66/11kV 60/80MVA ONAN/ODAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
|  | Latest Peak Compensated Load | [5 empty] | 50.2 MVA on 16/12/2019 at 17:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[5 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  | NCC Rating (MVA) |  | 184 | 184 | 184 |  | 184 |  | 184 | 208.8 |  | 208.8 |  | 208.8 | 208.8 | 208.8
|  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | 10 PoE Load (MVA) |  | 53.3 | 53.1 | 52.9 |  | 53 |  | 53 | 43.2 |  | 43 |  | 42.6 | 42.3 | 42.5
LARn (MVA)
LARn (MW)
|  |  | Power Factor at Peak Load |  | 0.994 | 0.994 | 0.994 |  | 0.994 |  | 0.994 | 0.997 |  | 0.997 |  | 0.997 | 0.997 | 0.997
|  |  | ECC Rating (MVA) |  | 105.3 | 105.3 | 105.3 |  | 105.3 |  | 105.3 | 115.9 |  | 115.9 |  | 115.9 | 115.9 | 115.9
|  |  | 50 PoE Load (MVA) |  | 50.7 | 50.5 | 50.4 |  | 50.5 |  | 50.5 | 42.2 |  | 42 |  | 41.6 | 41.4 | 41.5
|  |  | 50 PoE Load > 95% (MVA) |  | 2.5 | 2.5 | 2.5 |  | 2.5 |  | 2.5 | 2.1 |  | 2.1 |  | 2.1 | 2.1 | 2.1
|  |  | Hours PA > 95% Peak Load |  | 9.5 | 9.5 | 9.5 |  | 9.5 |  | 9.5 | 9.5 |  | 9.5 |  | 9.5 | 9.5 | 9.5
Raw LAR (MVA)
|  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## GLSO
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | GLSO - Gladstone South (66/11kV) | [8 empty] | Supply |  | T019 - Gladstone South BSP
| Description |  |  |  | Region is Capricornia
Transformer size is 1x66/11kV 15/20 MVA ONAN/ONAF;1x66/11kV 15/20MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.2%, 2021 S 0.4% W 0.4%, 2022 S 0.0% W 0.0%, 2023 S 0.1% W 0.1%, 2024 S 0.2% W 0.2%
|  |  | Latest Peak Compensated Load | [5 empty] | 21.1 MVA on 16/12/2019 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 54.7 | 54.7 | 54.7 |  | 54.7 |  | 54.7 | 59.8 |  | 59.8 |  | 59.8 | 59.8 | 59.8
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 23.1 | 23.1 | 23.2 |  | 23.3 |  | 23.4 | 18.6 |  | 18.6 |  | 18.5 | 18.4 | 18.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.99 | 0.99 | 0.99 |  | 0.99 |  | 0.99 | 0.996 |  | 0.996 |  | 0.996 | 0.996 | 0.996
|  |  |  | ECC Rating (MVA) |  | 29.6 | 29.6 | 29.6 |  | 29.6 |  | 29.6 | 29.9 |  | 29.9 |  | 29.9 | 29.9 | 29.9
|  |  |  | 50 PoE Load (MVA) |  | 21.1 | 21.1 | 21.2 |  | 21.3 |  | 21.3 | 17.8 |  | 17.8 |  | 17.7 | 17.6 | 17.7
|  |  |  | 50 PoE Load > 95% (MVA) |  | 1.1 | 1.1 | 1.1 |  | 1.1 |  | 1.1 | 0.9 |  | 0.9 |  | 0.9 | 0.9 | 0.9
|  |  |  | Hours PA > 95% Peak Load |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 7.8 | 7.8 | 7.8 |  | 7.8 |  | 7.8 | 7.8 |  | 7.8 |  | 7.8 | 7.8 | 7.8
|  |  |  | Mobile Plant Avail (MVA) |  | 0.8 | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.8 | 0.8
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## GOOB
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | GOOB - Gooburrum (66/11kV) | [8 empty] | Supply |  | BUND - Bundaberg BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 2x66/11kV 5MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.3%, 2021 S 0.2% W 0.2%, 2022 S 0.1% W 0.1%, 2023 S 0.2% W 0.2%, 2024 S 0.1% W 0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 5.2 MVA on 09/01/2020 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 14.3 | 14.3 | 14.3 |  | 14.3 |  | 14.3 | 15 |  | 15 |  | 15 | 15 | 15
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 5.4 | 5.4 | 5.4 |  | 5.4 |  | 5.4 | 3.3 |  | 3.3 |  | 3.2 | 3.2 | 3.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.907 | 0.907 | 0.907 |  | 0.907 |  | 0.907 | 0.938 |  | 0.938 |  | 0.938 | 0.938 | 0.938
|  |  |  | ECC Rating (MVA) |  | 7.5 | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 | 7.5
|  |  |  | 50 PoE Load (MVA) |  | 5.2 | 5.2 | 5.2 |  | 5.3 |  | 5.3 | 3 |  | 3 |  | 3 | 3 | 3
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 14.5 | 14.5 | 14.5 |  | 14.5 |  | 14.5 | 14.5 |  | 14.5 |  | 14.5 | 14.5 | 14.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## GOOT
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | GOOT - Gootchie (66/11kV) | [8 empty] | Supply |  | MARY - Maryborough BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 1x62/11kV 2MVA ON;1x66/11kV 6.3MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.3%, 2021 S -0.6% W -0.6%2022 S 0.1% W 0.1%, 2023 S 0.5% W 0.5%, 2024 S 0.2% W 0.2%
|  |  | Latest Peak Compensated Load | [5 empty] | 4.1 MVA on 16/12/2019 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 5 | 5 | 5 |  | 5 |  | 5 | 5.8 |  | 5.8 |  | 5.8 | 5.8 | 5.8
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 4.2 | 4.2 | 4.2 |  | 4.3 |  | 4.3 | 2.9 |  | 2.8 |  | 2.8 | 2.8 | 2.8
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.968 | 0.968 | 0.968 |  | 0.968 |  | 0.968 | 0.986 |  | 0.986 |  | 0.986 | 0.986 | 0.986
|  |  |  | ECC Rating (MVA) |  | 2.8 | 2.8 | 2.8 |  | 2.8 |  | 2.8 | 3 |  | 3 |  | 3 | 3 | 3
|  |  |  | 50 PoE Load (MVA) |  | 3.8 | 3.8 | 3.8 |  | 3.8 |  | 3.9 | 2.8 |  | 2.7 |  | 2.7 | 2.7 | 2.7
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 2.5 | 2.5 | 2.5 |  | 2.5 |  | 2.5 | 2.5 |  | 2.5 |  | 2.5 | 2.5 | 2.5
|  |  |  | Raw LAR (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1.1
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 | 2 | 2
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## Gracem
Zone Summary Information and Peak Load Forecast
| Substation |  |  | Gracem - Gracemere (66/11kV) | [6 empty] | Supply |  |  | RMES - Rockhampton Mesh
| Description |  |  | Region is Capricornia
Transformer size is 1x10MVA 66kV Transformer
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  | 2022 W 1.0%, 2023 S 1.0% W 1.0%, 2024 S 0.9% W 0.9%
No current information, due to be commissioned Winter 2022
Hours PA Exceeding 95% Peak Load
|  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[5 empty] | 2020/21 |  | 2021/22 | 2022/23 | 2023/24 | 2024/25 |  | 2020 | 2021 |  | 2022 | 2023 | 2024
|  |  | NCC Rating (MVA) |  |  |  |  | 11 | 11 | 11 |  |  |  |  | 11 | 11 | 11
|  |  | Contracted non-network (MVA) |  |  |  |  | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0
|  |  | 10 PoE Load (MVA) |  |  |  |  | 7.1 | 7.2 | 7.3 |  |  |  |  | 5.3 | 5.3 | 5.4
LARn (MVA)
LARn (MW)
|  |  | Power Factor at Peak Load |  |  |  |  | 0.979 | 0.979 | 0.979 |  |  |  |  | 0.988 | 0.988 | 0.988
|  |  | ECC Rating (MVA) |  |  |  |  | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0
|  |  | 50 PoE Load (MVA) |  |  |  |  | 7.1 | 7.2 | 7.3 |  |  |  |  | 5.3 | 5.3 | 5.4
|  |  | 50 PoE Load > (MVA) |  |  |  |  | 0.4 | 0.4 | 0.4 |  |  |  |  | 0.3 | 0.3 | 0.3
|  |  | Hours PA > Peak Load |  |  |  |  | N/A | N/A | N/A |  |  |  |  | N/A | N/A | N/A
|  |  | Raw LAR (MVA) |  |  |  |  | 7.1 | 7.2 | 7.3 |  |  |  |  | 5.3 | 5.3 | 5.4
|  |  | Auto Trans Avail (MVA) |  |  |  |  | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0
|  |  | Remote Trans Avail (MVA) |  |  |  |  | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0
|  |  | Manual Trans Avail (MVA) |  |  |  |  | 10 | 10 | 10 |  |  |  |  | 10 | 10 | 10
|  |  | Mobile Plant Avail (MVA) |  |  |  |  | 4 | 4 | 4 |  |  |  |  | 4 | 4 | 4
|  |  | Shed(30min) |  |  |  |  | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0
|  |  | Shed(4Hour) |  |  |  |  | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  | Substation Category |  |  |  |  | Regional Centre | Regional Centre | Regional Centre |  |  |  |  | Regional Centre | Regional Centre | Regional Centre
|  |  | Meets Security Standard |  |  |  |  | Yes | Yes | Yes |  |  |  |  | Yes | Yes | Yes
Return to Index

## GRCR
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | GRCR - Granite Creek (66/22kV) | [8 empty] | Supply |  | T166 - Granite Creek BSP
| Description |  |  |  | Region is Capricornia
Transformer size is 1xGRCRSS 22/22KV REGULATOR 1 REG 1
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.2%, 2021 S 0.3% W 0.3%, 2022 S 0.1% W 0.1%, 2023 S 0.2% W 0.2%, 2024 S 0.1% W 0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 0.3 MVA on 16/12/2019 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 3.8 | 3.8 | 3.8 |  | 3.8 |  | 3.8 | 3.8 |  | 3.8 |  | 3.8 | 3.8 | 3.8
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 |  | 0.3 |  | 0.2 | 0.2 | 0.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.947 | 0.947 | 0.947 |  | 0.947 |  | 0.947 | 0.908 |  | 0.908 |  | 0.871 | 0.871 | 0.908
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 |  | 0.3 |  | 0.2 | 0.2 | 0.3
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 3.5 | 3.5 | 3.5 |  | 3.5 |  | 3.5 | 3.5 |  | 3.5 |  | 3.5 | 3.5 | 3.5
|  |  |  | Raw LAR (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 |  | 0.3 |  | 0.2 | 0.2 | 0.3
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## GREN
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | GREN - Greenvale (66/11kV) | [8 empty] | Supply |  | T047 - Ingham BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/11kV 0.5MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.3%, 2021 S 0.2% W 0.2%, 2022 S 0.1% W 0.1%, 2023 S 0.2% W 0.2%, 2024 S 0.1% W 0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 0.5 MVA on 02/12/2019 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 0.7 | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.7 | 0.7
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.986 | 0.986 | 0.986 |  | 0.986 |  | 0.986 | 0.991 |  | 0.991 |  | 0.991 | 0.991 | 0.991
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 7.5 | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 | 7.5
|  |  |  | Raw LAR (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## GUML
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | GUML - Gumlu (66/11kV) | [8 empty] | Supply |  | T193 - Clare South BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/11kV 0.5MVA ONAN;1x66/11kV 1MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -1.7%, 2021 S -0.2% W -0.2%2022 S -0.3% W -0.3%2023 S -0.1% W -0.1%2024 S -0.4% W -0.4
|  |  | Latest Peak Compensated Load | [5 empty] | 1.2 MVA on 02/11/2019 at 14:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 1.7 | 1.7 | 1.7 |  | 1.7 |  | 1.7 | 1.8 |  | 1.8 |  | 1.8 | 1.8 | 1.8
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 1.3 | 1.3 | 1.3 |  | 1.3 |  | 1.3 | 1.3 |  | 1.3 |  | 1.3 | 1.3 | 1.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.88 | 0.88 | 0.88 |  | 0.88 |  | 0.88 | 0.882 |  | 0.882 |  | 0.882 | 0.882 | 0.882
|  |  |  | ECC Rating (MVA) |  | 0.7 | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.8 |  | 0.8 |  | 0.8 | 0.8 | 0.8
|  |  |  | 50 PoE Load (MVA) |  | 1.3 | 1.3 | 1.3 |  | 1.3 |  | 1.3 | 1.2 |  | 1.2 |  | 1.2 | 1.2 | 1.2
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 159 | 159 | 159 |  | 159 |  | 159 | 159 |  | 159 |  | 159 | 159 | 159
|  |  |  | Raw LAR (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## GUTH
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | GUTH - Guthalungra (66/11kV) | [8 empty] | Supply |  | T193 - Clare South BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/11kV 0.5MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.0%, 2021 S 0.0% W 0.0%, 2022 S 0.0% W 0.0%, 2023 S 0.0% W 0.0%, 2024 S 0.0% W 0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 0.5 MVA on 01/01/2020 at 17:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.85 | 0.85 | 0.85 |  | 0.85 |  | 0.85 | 0.85 |  | 0.85 |  | 0.85 | 0.85 | 0.85
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 8750 | 8750 | 8750 |  | 8750 |  | 8750 | 8750 |  | 8750 |  | 8750 | 8750 | 8750
|  |  |  | Raw LAR (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## HAPU
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | HAPU - Haughton (66/11kV) | [8 empty] | Supply |  | T193 - Clare South BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/11kV 2.5MVA ONAN;1x66/11kV 4MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.2%, 2021 S 0.3% W 0.3%, 2022 S 0.2% W 0.2%, 2023 S 0.3% W 0.3%, 2024 S 0.2% W 0.2%
|  |  | Latest Peak Compensated Load | [5 empty] | 4.8 MVA on 19/12/2019 at 13:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 6.2 | 6.2 | 6.2 |  | 6.2 |  | 6.2 | 6.7 |  | 6.7 |  | 6.7 | 6.7 | 6.7
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 4.9 | 4.9 | 5 |  | 5 |  | 5 | 4.5 |  | 4.5 |  | 4.5 | 4.4 | 4.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.84 | 0.84 | 0.84 |  | 0.84 |  | 0.84 | 0.848 |  | 0.848 |  | 0.848 | 0.848 | 0.848
|  |  |  | ECC Rating (MVA) |  | 3.7 | 3.7 | 3.7 |  | 3.7 |  | 3.7 | 3.7 |  | 3.7 |  | 3.7 | 3.7 | 3.7
|  |  |  | 50 PoE Load (MVA) |  | 4.8 | 4.8 | 4.8 |  | 4.9 |  | 4.9 | 4.4 |  | 4.4 |  | 4.4 | 4.3 | 4.4
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 169.5 | 169.5 | 169.5 |  | 169.5 |  | 169.5 | 169.5 |  | 169.5 |  | 169.5 | 169.5 | 169.5
|  |  |  | Raw LAR (MVA) |  | 1.1 | 1.1 | 1.1 |  | 1.2 |  | 1.2 | 0.7 |  | 0.7 |  | 0.7 | 0.6 | 0.7
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0.8 | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.8 | 0.8
|  |  |  | Mobile Plant Avail (MVA) |  | 0.7 | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.7 | 0.7
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## HELE
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | HELE - Helenvale (66/22kV) | [8 empty] | Supply |  | T159 - Lakeland BSP
| Description |  |  |  | Region is Far North
Transformer size is 1x66/22kV 4MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.0%, 2021 S 0.0% W 0.0%, 2022 S 0.0% W 0.0%, 2023 S 0.0% W 0.0%, 2024 S 0.0% W 0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 0.8 MVA on 13/02/2020 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 5.7 | 5.7 | 5.7 |  | 5.7 |  | 5.7 | 6.3 |  | 6.3 |  | 6.3 | 6.3 | 6.3
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 0.8 | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.984 | 0.984 | 0.984 |  | 0.984 |  | 0.984 | 0.957 |  | 0.957 |  | 0.957 | 0.957 | 0.957
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 0.8 | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 6 | 6 | 6 |  | 6 |  | 6 | 6 |  | 6 |  | 6 | 6 | 6
|  |  |  | Raw LAR (MVA) |  | 0.8 | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 1.2 | 1.2 | 1.2 |  | 1.2 |  | 1.2 | 1.2 |  | 1.2 |  | 1.2 | 1.2 | 1.2
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## HEPA
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | HEPA - Hermit Park (66/11kV) | [8 empty] | Supply |  | TMES - Townsville Mesh
| Description |  |  |  | Region is Nth Queensland
Transformer size is 2x66/11kV 15/20/25MVA ONAN/ONAF/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.1%, 2021 S 0.0% W 0.0%, 2022 S -0.3% W -0.3%2023 S -0.1% W -0.1%2024 S -0.2% W -0.2
|  |  | Latest Peak Compensated Load | [5 empty] | 18.6 MVA on 14/02/2020 at 16:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 56.6 | 56.6 | 56.6 |  | 56.6 |  | 56.6 | 58.6 |  | 58.6 |  | 58.6 | 58.6 | 58.6
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 21.3 | 21.3 | 21.3 |  | 21.3 |  | 21.3 | 11.5 |  | 11.5 |  | 11.4 | 11.3 | 11.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.969 | 0.969 | 0.969 |  | 0.969 |  | 0.969 | 0.976 |  | 0.976 |  | 0.976 | 0.976 | 0.976
|  |  |  | ECC Rating (MVA) |  | 31.5 | 31.5 | 31.5 |  | 31.5 |  | 31.5 | 32.6 |  | 32.6 |  | 32.6 | 32.6 | 32.6
|  |  |  | 50 PoE Load (MVA) |  | 18.6 | 18.5 | 18.5 |  | 18.5 |  | 18.6 | 11.2 |  | 11.2 |  | 11.1 | 11 | 11.1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.9 | 0.9 | 0.9 |  | 0.9 |  | 0.9 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  |  | Hours PA > 95% Peak Load |  | 5.5 | 5.5 | 5.5 |  | 5.5 |  | 5.5 | 5.5 |  | 5.5 |  | 5.5 | 5.5 | 5.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 3.5 | 3.5 | 3.5 |  | 3.5 |  | 3.5 | 3.5 |  | 3.5 |  | 3.5 | 3.5 | 3.5
|  |  |  | Mobile Plant Avail (MVA) |  | 1.2 | 1.2 | 1.2 |  | 1.2 |  | 1.2 | 1.2 |  | 1.2 |  | 1.2 | 1.2 | 1.2
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## HIGH
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | HIGH - Highfields (33/11kV) | [8 empty] | Supply |  | T029 - Postmans Ridge BSP
| Description |  |  |  | Region is South West
Transformer size is 1x33/11kV 5MVA ON
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.9%, 2021 S 0.6% W 0.6%, 2022 S 0.5% W 0.5%, 2023 S 0.5% W 0.5%, 2024 S 0.3% W 0.3%
|  |  | Latest Peak Compensated Load | [5 empty] | 3.6 MVA on 15/07/2019 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 | 5 | 5
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 4 | 4 | 3.9 |  | 4 |  | 4.1 | 4.1 |  | 4.1 |  | 4.1 | 4.1 | 4.1
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.981 | 0.981 | 0.978 |  | 0.978 |  | 0.981 | 0.99 |  | 0.99 |  | 0.99 | 0.99 | 0.99
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 3.5 | 3.5 | 3.5 |  | 3.5 |  | 3.6 | 3.8 |  | 3.8 |  | 3.8 | 3.8 | 3.8
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 46 | 46 | 46 |  | 46 |  | 46 | 46 |  | 46 |  | 46 | 46 | 46
|  |  |  | Raw LAR (MVA) |  | 3.5 | 3.5 | 3.5 |  | 3.5 |  | 3.6 | 3.8 |  | 3.8 |  | 3.8 | 3.8 | 3.8
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 5.5 | 5.5 | 5.5 |  | 5.5 |  | 5.5 | 5.5 |  | 5.5 |  | 5.5 | 5.5 | 5.5
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## HILL
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | HILL - Hillsborough (66/11kV) | [8 empty] | Supply |  | T193 - Clare South BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/11kV 0.05MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.0%, 2021 S 0.0% W 0.0%, 2022 S 0.0% W 0.0%, 2023 S 0.0% W 0.0%, 2024 S 0.0% W 0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 0.1 MVA on 01/01/2020 at 17:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.85 | 0.85 | 0.85 |  | 0.85 |  | 0.85 | 0.85 |  | 0.85 |  | 0.85 | 0.85 | 0.85
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 8742.5 | 8742.5 | 8742.5 |  | 8742.5 |  | 8742.5 | 8742.5 |  | 8742.5 |  | 8742.5 | 8742.5 | 8742.5
|  |  |  | Raw LAR (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## HOHI
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | HOHI - Home Hill (66/11kV) | [8 empty] | Supply |  | T193 - Clare South BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/11kV 15/20/25MVA ONAN/ODAN/ODAF;1x66/11kV 15/20/25MVA ONAN/ONAF/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 15.1 MVA
Growth Rates |  |  |  |  | 2020 W -0.2%, 2021 S -0.2% W -0.2%2022 S -0.3% W -0.3%2023 S -0.1% W -0.1%2024 S -0.3% W -0.3
|  |  | Latest Peak Compensated Load | [5 empty] | 14.1 MVA on 13/01/2020 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 59.3 | 59.3 | 59.3 |  | 59.3 |  | 59.3 | 65.1 |  | 65.1 |  | 65.1 | 65.1 | 65.1
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 14.6 | 14.6 | 14.6 |  | 14.6 |  | 14.6 | 7.7 |  | 7.7 |  | 7.6 | 7.5 | 7.6
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.894 | 0.894 | 0.894 |  | 0.894 |  | 0.894 | 0.936 |  | 0.936 |  | 0.936 | 0.936 | 0.936
|  |  |  | ECC Rating (MVA) |  | 34.6 | 34.6 | 34.6 |  | 34.6 |  | 34.6 | 36.8 |  | 36.8 |  | 36.8 | 36.8 | 36.8
|  |  |  | 50 PoE Load (MVA) |  | 14.3 | 14.2 | 14.2 |  | 14.2 |  | 14.2 | 7.2 |  | 7.2 |  | 7.1 | 7.1 | 7.1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.7 | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  |  | Hours PA > 95% Peak Load |  | 8 | 8 | 8 |  | 8 |  | 8 | 8 |  | 8 |  | 8 | 8 | 8
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## HOWA
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | HOWA - Howard (66/11kV) | [8 empty] | Supply |  | ISIS - Isis BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 2x62/11kV 7.5MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 1.4%, 2021 S 1.2% W 1.2%, 2022 S 1.0% W 1.0%, 2023 S 1.0% W 1.0%, 2024 S 0.7% W 0.7%
|  |  | Latest Peak Compensated Load | [5 empty] | 8.3 MVA on 22/01/2020 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 16.1 | 16.1 | 16.1 |  | 16.1 |  | 16.1 | 16.1 |  | 16.1 |  | 16.1 | 16.1 | 16.1
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 9.5 | 9.6 | 9.7 |  | 9.8 |  | 9.9 | 8 |  | 8.1 |  | 8.1 | 8.1 | 8.2
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.985 | 0.985 | 0.985 |  | 0.985 |  | 0.985 | 0.993 |  | 0.993 |  | 0.993 | 0.993 | 0.993
|  |  |  | ECC Rating (MVA) |  | 8.3 | 8.3 | 8.3 |  | 8.3 |  | 8.3 | 8.6 |  | 8.6 |  | 8.6 | 8.6 | 8.6
|  |  |  | 50 PoE Load (MVA) |  | 8.8 | 8.8 | 8.9 |  | 9 |  | 9.2 | 7.6 |  | 7.6 |  | 7.7 | 7.7 | 7.8
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.4 | 0.4 | 0.4 |  | 0.5 |  | 0.5 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  |  | Hours PA > 95% Peak Load |  | 7 | 7 | 7 |  | 7 |  | 7 | 7 |  | 7 |  | 7 | 7 | 7
|  |  |  | Raw LAR (MVA) |  | 0.5 | 0.5 | 0.6 |  | 0.7 |  | 0.9
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0.9 | 0.9 | 0.9 |  | 0.9 |  | 0.9 | 0.9 |  | 0.9 |  | 0.9 | 0.9 | 0.9
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## HUGH
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | HUGH - Hughenden (66/33kV) | [8 empty] | Supply |  | T095 - Millchester BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 2x66/33/6.6kV 8/5.5MVA ONAF/ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 10.0 MVA
Growth Rates |  |  |  |  | 2020 W -1.7%, 2021 S -0.4% W -0.4%2022 S -0.5% W -0.5%2023 S -0.3% W -0.3%2024 S -0.5% W -0.5
|  |  | Latest Peak Compensated Load | [5 empty] | 3.9 MVA on 17/12/2019 at 19:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 20 | 20 | 20 |  | 20 |  | 20 | 22.9 |  | 22.9 |  | 22.9 | 22.9 | 22.9
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 4.1 | 4.1 | 4.1 |  | 4.1 |  | 4.1 | 2.5 |  | 2.5 |  | 2.4 | 2.4 | 2.4
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.999 | 0.999 | 0.999 |  | 0.999 |  | 0.999 | 0.972 |  | 0.972 |  | 0.972 | 0.972 | 0.972
|  |  |  | ECC Rating (MVA) |  | 11.4 | 11.4 | 11.4 |  | 11.4 |  | 11.4 | 11.4 |  | 11.4 |  | 11.4 | 11.4 | 11.4
|  |  |  | 50 PoE Load (MVA) |  | 3.8 | 3.8 | 3.8 |  | 3.8 |  | 3.8 | 2.4 |  | 2.4 |  | 2.3 | 2.3 | 2.3
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 12 | 12 | 12 |  | 12 |  | 12 | 12 |  | 12 |  | 12 | 12 | 12
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## ILBI
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | ILBI - Ilbilbie (33/11kV) | [8 empty] | Supply |  | T065 - Alligator Creek BSP
| Description |  |  |  | Region is Mackay
Transformer size is 1x33/11kV 1MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -1.7%, 2021 S -0.3% W -0.3%2022 S -0.4% W -0.4%2023 S -0.3% W -0.3%2024 S -0.5% W -0.5
|  |  | Latest Peak Compensated Load | [5 empty] | 0.7 MVA on 11/12/2019 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 1.2 | 1.2 | 1.2 |  | 1.2 |  | 1.2 | 1.4 |  | 1.4 |  | 1.4 | 1.4 | 1.4
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 0.9 | 0.9 | 0.9 |  | 0.9 |  | 0.9 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.948 | 0.948 | 0.948 |  | 0.948 |  | 0.948 | 0.979 |  | 0.979 |  | 0.979 | 0.979 | 0.979
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 0.8 | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 196 | 196 | 196 |  | 196 |  | 196 | 196 |  | 196 |  | 196 | 196 | 196
|  |  |  | Raw LAR (MVA) |  | 0.8 | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0.9 | 0.9 | 0.9 |  | 0.9 |  | 0.9 | 0.9 |  | 0.9 |  | 0.9 | 0.9 | 0.9
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## INGH
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | INGH - Ingham (66/11kV) | [8 empty] | Supply |  | T047 - Ingham BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 2x66/11kV 7.5/10MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -2.3%, 2021 S -0.6% W -0.6%2022 S -0.9% W -0.9%2023 S -0.6% W -0.6%2024 S -0.5% W -0.5
|  |  | Latest Peak Compensated Load | [5 empty] | 11.3 MVA on 14/02/2020 at 17:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 26.7 | 26.7 | 26.7 |  | 26.7 |  | 26.7 | 28.1 |  | 28.1 |  | 28.1 | 28.1 | 28.1
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 13.1 | 13 | 12.9 |  | 12.9 |  | 12.9 | 6.1 |  | 6.1 |  | 6 | 5.9 | 5.9
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 1 | 1 | 1 |  | 1 |  | 1 | 0.979 |  | 0.979 |  | 0.979 | 0.979 | 0.979
|  |  |  | ECC Rating (MVA) |  | 14.1 | 14.1 | 14.1 |  | 14.1 |  | 14.1 | 15 |  | 15 |  | 15 | 15 | 15
|  |  |  | 50 PoE Load (MVA) |  | 11.1 | 11.1 | 11 |  | 11 |  | 11 | 5.8 |  | 5.8 |  | 5.7 | 5.6 | 5.6
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Hours PA > 95% Peak Load |  | 27 | 27 | 27 |  | 27 |  | 27 | 27 |  | 27 |  | 27 | 27 | 27
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## ISIS
Bulk Summary Information and Peak Load Forecast
Substation |  |  |  | ISIS - Isis BSP (132/66kV) | [8 empty] | Supply |  | QTBC - Teebar Creek TCP
Description |  |  |  | Region is Wide Bay
Transformer size is 1x132/66/11kV 80/100MVA ONAN/ODAN;1x132/66kV 32/40/52MVA ONAN/ODAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 91.8 MVA
|  | Latest Peak Compensated Load | [5 empty] | 47.2 MVA on 16/12/2019 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[5 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  | NCC Rating (MVA) |  | 134 | 134 | 134 |  | 134 |  | 134 | 145 |  | 145 |  | 145 | 145 | 145
|  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6
|  |  | 10 PoE Load (MVA) |  | 52.3 | 53.3 | 54.4 |  | 54.6 |  | 54.8 | 37.4 |  | 38 |  | 38.4 | 38.3 | 38.5
LARn (MVA)
LARn (MW)
|  |  | Power Factor at Peak Load |  | 0.991 | 0.991 | 0.991 |  | 0.991 |  | 0.991 | 0.998 |  | 0.998 |  | 0.997 | 0.997 | 0.997
|  |  | ECC Rating (MVA) |  | 75.3 | 75.3 | 75.3 |  | 75.3 |  | 75.3 | 77.8 |  | 77.8 |  | 77.8 | 77.8 | 77.8
|  |  | 50 PoE Load (MVA) |  | 48.3 | 49.3 | 50.3 |  | 50.6 |  | 50.8 | 35.3 |  | 35.9 |  | 36.2 | 36.2 | 36.4
|  |  | 50 PoE Load > 95% (MVA) |  | 2.4 | 2.5 | 2.5 |  | 2.5 |  | 2.5 | 1.8 |  | 1.8 |  | 1.8 | 1.8 | 1.8
|  |  | Hours PA > 95% Peak Load |  | 7.5 | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 | 7.5
Raw LAR (MVA)
|  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## JAND
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | JAND - Jandowae (33/11kV) | [8 empty] | Supply |  | CHIN - Chinchilla BSP
| Description |  |  |  | Region is South West
Transformer size is 1x33/11 3.15MVA ON;1x33/11kV 0.75MVA ON(Standby)
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.0%, 2021 S 0.4% W 0.4%, 2022 S 0.3% W 0.3%, 2023 S 0.4% W 0.4%, 2024 S 0.2% W 0.2%
|  |  | Latest Peak Compensated Load | [5 empty] | 1.4 MVA on 08/12/2019 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 3.5 | 3.5 | 3.5 |  | 3.5 |  | 3.5 | 3.5 |  | 3.5 |  | 3.5 | 3.5 | 3.5
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 1.6 | 1.6 | 1.6 |  | 1.7 |  | 1.7 | 1.3 |  | 1.3 |  | 1.3 | 1.2 | 1.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.98 | 0.98 | 0.98 |  | 0.98 |  | 0.98 | 0.989 |  | 0.989 |  | 0.989 | 0.989 | 0.989
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 1.5 | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.2 |  | 1.2 |  | 1.2 | 1.1 | 1.2
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 7.5 | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 | 7.5
|  |  |  | Raw LAR (MVA) |  | 1.5 | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.2 |  | 1.2 |  | 1.2 | 1.1 | 1.2
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0.8 | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.8 | 0.8
|  |  |  | Mobile Plant Avail (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## JARV
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | JARV - Jarvisfield (66/11kV) | [8 empty] | Supply |  | T193 - Clare South BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 2x66/11kV 5MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.0%, 2021 S -0.0% W -0.0%2022 S -0.1% W -0.1%2023 S 0.0% W 0.0%, 2024 S -0.2% W -0.2
|  |  | Latest Peak Compensated Load | [5 empty] | 6.4 MVA on 14/01/2020 at 20:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 12.1 | 12.1 | 12.1 |  | 12.1 |  | 12.1 | 12.4 |  | 12.4 |  | 12.4 | 12.4 | 12.4
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 6.7 | 6.7 | 6.7 |  | 6.7 |  | 6.7 | 2.8 |  | 2.8 |  | 2.7 | 2.7 | 2.7
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.851 | 0.851 | 0.851 |  | 0.851 |  | 0.851 | 0.869 |  | 0.869 |  | 0.869 | 0.869 | 0.869
|  |  |  | ECC Rating (MVA) |  | 7 | 7 | 7 |  | 7 |  | 7 | 7.1 |  | 7.1 |  | 7.1 | 7.1 | 7.1
|  |  |  | 50 PoE Load (MVA) |  | 6.5 | 6.5 | 6.5 |  | 6.5 |  | 6.5 | 2.6 |  | 2.6 |  | 2.6 | 2.6 | 2.6
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 9.5 | 9.5 | 9.5 |  | 9.5 |  | 9.5 | 9.5 |  | 9.5 |  | 9.5 | 9.5 | 9.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## JUCR
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | JUCR - Julia Creek (66/33kV) | [8 empty] | Supply |  | T095 - Millchester BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/33kV 7.5/6.3MVA ONAF/ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.5%, 2021 S -0.2% W -0.2%2022 S -0.3% W -0.3%2023 S -0.2% W -0.2%2024 S -0.4% W -0.4
|  |  | Latest Peak Compensated Load | [5 empty] | 2.9 MVA on 11/12/2019 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 7.4 | 7.4 | 7.4 |  | 7.4 |  | 7.4 | 8.8 |  | 8.8 |  | 8.8 | 8.8 | 8.8
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 3.1 | 3.1 | 3.1 |  | 3.1 |  | 3 | 2.1 |  | 2 |  | 2 | 2 | 2
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.971 | 0.971 | 0.971 |  | 0.971 |  | 0.971 | 0.991 |  | 0.991 |  | 0.991 | 0.991 | 0.991
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 2.9 | 2.9 | 2.9 |  | 2.9 |  | 2.9 | 1.7 |  | 1.7 |  | 1.7 | 1.7 | 1.7
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 17 | 17 | 17 |  | 17 |  | 17 | 17 |  | 17 |  | 17 | 17 | 17
|  |  |  | Raw LAR (MVA) |  | 2.9 | 2.9 | 2.9 |  | 2.9 |  | 2.9 | 1.7 |  | 1.7 |  | 1.7 | 1.7 | 1.7
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 2.7 | 2.7 | 2.7 |  | 2.7 |  | 2.7 | 2.7 |  | 2.7 |  | 2.7 | 2.7 | 2.7
|  |  |  | Mobile Plant Avail (MVA) |  | 0.4 | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## JUPO
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | JUPO - Jubilee Pocket (66/11kV) | [8 empty] | Supply |  | PROS - Proserpine BSP
| Description |  |  |  | Region is Mackay
Transformer size is 1x66/11kV 19/26/32MVA ONAN/ODAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 1.4%, 2021 S 1.3% W 1.3%, 2022 S 1.2% W 1.2%, 2023 S 1.3% W 1.3%, 2024 S 1.1% W 1.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 4.5 MVA on 19/02/2020 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 39.6 | 39.6 | 39.6 |  | 39.6 |  | 39.6 | 43.4 |  | 43.4 |  | 43.4 | 43.4 | 43.4
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 5 | 5.1 | 5.2 |  | 5.2 |  | 5.3 | 3.4 |  | 3.5 |  | 3.5 | 3.5 | 3.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.991 | 0.991 | 0.991 |  | 0.991 |  | 0.991 | 0.994 |  | 0.994 |  | 0.994 | 0.994 | 0.994
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 4.7 | 4.7 | 4.8 |  | 4.8 |  | 4.9 | 3.2 |  | 3.3 |  | 3.3 | 3.3 | 3.4
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 21.5 | 21.5 | 21.5 |  | 21.5 |  | 21.5 | 21.5 |  | 21.5 |  | 21.5 | 21.5 | 21.5
|  |  |  | Raw LAR (MVA) |  | 4.7 | 4.7 | 4.8 |  | 4.8 |  | 4.9 | 3.2 |  | 3.3 |  | 3.3 | 3.3 | 3.4
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 4.3 | 4.3 | 4.3 |  | 4.3 |  | 4.3 | 4.3 |  | 4.3 |  | 4.3 | 4.3 | 4.3
|  |  |  | Mobile Plant Avail (MVA) |  | 1.5 | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.5 | 1.5
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## KAIM
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | KAIM - Kaimkillenbun (33/11kV) | [8 empty] | Supply |  | T002 - Dalby East BSP
| Description |  |  |  | Region is South West
Transformer size is 1x33/11kV 1MVA ONAN;1x33/11kV 1MVA ONAN(Standby)
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.0%, 2021 S 0.4% W 0.4%, 2022 S 0.3% W 0.3%, 2023 S 0.4% W 0.4%, 2024 S 0.2% W 0.2%
|  |  | Latest Peak Compensated Load | [5 empty] | 0.9 MVA on 16/12/2019 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 0.9 |  | 0.9 |  | 0.9 | 0.9 | 0.9
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.972 | 0.972 | 0.972 |  | 0.972 |  | 0.972 | 0.989 |  | 0.989 |  | 0.989 | 0.989 | 0.989
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 0.9 | 0.9 | 0.9 |  | 0.9 |  | 0.9 | 0.9 |  | 0.9 |  | 0.9 | 0.9 | 0.9
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 9 | 9 | 9 |  | 9 |  | 9 | 9 |  | 9 |  | 9 | 9 | 9
|  |  |  | Raw LAR (MVA) |  | 0.9 | 0.9 | 0.9 |  | 0.9 |  | 0.9 | 0.9 |  | 0.9 |  | 0.9 | 0.9 | 0.9
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 1.1 | 1.1 | 1.1 |  | 1.1 |  | 1.1 | 1.1 |  | 1.1 |  | 1.1 | 1.1 | 1.1
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## KALA
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | KALA - Kalamia (66/11kV) | [8 empty] | Supply |  | T193 - Clare South BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/11kV 7.5/10MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 11.3 MVA
Growth Rates |  |  |  |  | 2020 W 0.0%, 2021 S 0.0% W 0.0%, 2022 S -0.1% W -0.1%2023 S 0.1% W 0.1%, 2024 S -0.2% W -0.2
|  |  | Latest Peak Compensated Load | [5 empty] | 4.3 MVA on 20/01/2020 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 13 | 13 | 13 |  | 13 |  | 13 | 14.2 |  | 14.2 |  | 14.2 | 14.2 | 14.2
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 4.4 | 4.4 | 4.4 |  | 4.4 |  | 4.4 | 3.8 |  | 3.8 |  | 3.8 | 3.8 | 3.8
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.909 | 0.909 | 0.909 |  | 0.909 |  | 0.909 | 0.991 |  | 0.991 |  | 0.991 | 0.991 | 0.991
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 4.3 | 4.3 | 4.3 |  | 4.3 |  | 4.3 | 3.7 |  | 3.7 |  | 3.7 | 3.7 | 3.7
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 13.5 | 13.5 | 13.5 |  | 13.5 |  | 13.5 | 13.5 |  | 13.5 |  | 13.5 | 13.5 | 13.5
|  |  |  | Raw LAR (MVA) |  | 4.3 | 4.3 | 4.3 |  | 4.3 |  | 4.3 | 3.7 |  | 3.7 |  | 3.7 | 3.7 | 3.7
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 1.3 | 1.3 | 1.3 |  | 1.3 |  | 1.3 | 1.3 |  | 1.3 |  | 1.3 | 1.3 | 1.3
|  |  |  | Mobile Plant Avail (MVA) |  | 1.8 | 1.8 | 1.8 |  | 1.8 |  | 1.8 | 1.8 |  | 1.8 |  | 1.8 | 1.8 | 1.8
|  |  |  | Shed(30min) |  | 3 | 3 | 3 |  | 3 |  | 3 | 3 |  | 3 |  | 3 | 3 | 3
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## KECE
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | KECE - Kelsey Creek East (66/11kV) | [8 empty] | Supply |  | PROS - Proserpine BSP
| Description |  |  |  | Region is Mackay
Transformer size is 1x66/11kV 12.5/16MVA ONAN/ONAF;1x66/11kV 16/20MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.1%, 2021 S 0.5% W 0.5%, 2022 S 0.4% W 0.4%, 2023 S 0.5% W 0.5%, 2024 S 0.3% W 0.3%
|  |  | Latest Peak Compensated Load | [5 empty] | 14.5 MVA on 04/12/2019 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 36.8 | 36.8 | 36.8 |  | 36.8 |  | 36.8 | 38.4 |  | 38.4 |  | 38.4 | 38.4 | 38.4
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 19.9 | 19.9 | 20.1 |  | 20.2 |  | 20.4 | 8.6 |  | 8.6 |  | 8.6 | 8.6 | 8.6
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.954 | 0.954 | 0.954 |  | 0.954 |  | 0.954 | 0.97 |  | 0.97 |  | 0.97 | 0.97 | 0.97
|  |  |  | ECC Rating (MVA) |  | 18.4 | 18.4 | 18.4 |  | 18.4 |  | 18.4 | 20 |  | 20 |  | 20 | 20 | 20
|  |  |  | 50 PoE Load (MVA) |  | 16 | 16 | 16.1 |  | 16.3 |  | 16.4 | 8.1 |  | 8.1 |  | 8.1 | 8.1 | 8.1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.8 | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  |  | Hours PA > 95% Peak Load |  | 5.5 | 5.5 | 5.5 |  | 5.5 |  | 5.5 | 5.5 |  | 5.5 |  | 5.5 | 5.5 | 5.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Mobile Plant Avail (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 | 2 | 2
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## KESP
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | KESP - Kearneys Spring (110/11kV) | [8 empty] | Supply |  | QMRG - Middle Ridge (Ergon) TCP
| Description |  |  |  | Region is South West
Transformer size is 2x110/11kV 30/40MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.4%, 2021 S -0.7% W -0.7%2022 S -0.2% W -0.2%2023 S 0.6% W 0.6%, 2024 S 0.4% W 0.4%
|  |  | Latest Peak Compensated Load | [5 empty] | 28.5 MVA on 04/06/2019 at 17:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 79.1 | 79.1 | 79.1 |  | 79.1 |  | 79.1 | 89.8 |  | 89.8 |  | 89.8 | 89.8 | 89.8
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 23.3 | 23.2 | 23.4 |  | 23.6 |  | 23.8 | 26.6 |  | 26.3 |  | 26.1 | 26.1 | 26.4
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.992 | 0.992 | 0.992 |  | 0.992 |  | 0.992 | 0.998 |  | 0.998 |  | 0.998 | 0.998 | 0.998
|  |  |  | ECC Rating (MVA) |  | 44.8 | 44.8 | 44.8 |  | 44.8 |  | 44.8 | 49.3 |  | 49.3 |  | 49.3 | 49.3 | 49.3
|  |  |  | 50 PoE Load (MVA) |  | 20.4 | 20.4 | 20.5 |  | 20.7 |  | 20.9 | 24.1 |  | 23.8 |  | 23.6 | 23.7 | 23.9
|  |  |  | 50 PoE Load > 95% (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1.2 |  | 1.2 |  | 1.2 | 1.2 | 1.2
|  |  |  | Hours PA > 95% Peak Load |  | 6 | 6 | 6 |  | 6 |  | 6 | 6 |  | 6 |  | 6 | 6 | 6
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## KIDS
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | KIDS - Kidston (132/6.6kV) | [8 empty] | Supply |  | QROS - Ross (Kidston and Milchester) TCP
| Description |  |  |  | Region is Far North
Transformer size is 2x132/6.6kV 20MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.1%, 2021 S 0.0% W 0.0%, 2022 S 0.0% W 0.0%, 2023 S 0.0% W 0.0%, 2024 S -0.0% W -0.0
|  |  | Latest Peak Compensated Load | [5 empty] | 0.3 MVA on 11/03/2020 at 16:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 42.5 | 42.5 | 42.5 |  | 42.5 |  | 42.5 | 44.9 |  | 44.9 |  | 44.9 | 44.9 | 44.9
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.852 | 0.852 | 0.852 |  | 0.852 |  | 0.852 | 0.866 |  | 0.866 |  | 0.866 | 0.866 | 0.866
|  |  |  | ECC Rating (MVA) |  | 25.4 | 25.4 | 25.4 |  | 25.4 |  | 25.4 | 25.8 |  | 25.8 |  | 25.8 | 25.8 | 25.8
|  |  |  | 50 PoE Load (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 6 | 6 | 6 |  | 6 |  | 6 | 6 |  | 6 |  | 6 | 6 | 6
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## KILK
Bulk Summary Information and Peak Load Forecast
Substation |  |  |  | KILK - Kilkivan BSP (132/66kV) | [8 empty] | Supply |  | QWLN - Woolooga TCP
Description |  |  |  | Region is Wide Bay
Transformer size is 1x132/66/11kV 34MVA ONAF;1x132/66kV 15/18MVA ON/ONB(Standby)
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
|  | Latest Peak Compensated Load | [5 empty] | 15.2 MVA on 16/12/2019 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[5 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  | NCC Rating (MVA) |  | 34 | 34 | 34 |  | 34 |  | 34 | 34 |  | 34 |  | 34 | 34 | 34
|  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | 10 PoE Load (MVA) |  | 17.2 | 17.6 | 17.6 |  | 17.7 |  | 17.8 | 14.6 |  | 14.9 |  | 15.2 | 15.2 | 15.2
LARn (MVA)
LARn (MW)
|  |  | Power Factor at Peak Load |  | 0.966 | 0.966 | 0.966 |  | 0.966 |  | 0.966 | 0.988 |  | 0.988 |  | 0.988 | 0.988 | 0.988
|  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | 50 PoE Load (MVA) |  | 15.6 | 16 | 16 |  | 16 |  | 16.1 | 13.8 |  | 14.2 |  | 14.4 | 14.4 | 14.4
|  |  | 50 PoE Load > 95% (MVA) |  | 0.8 | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.7 |  | 0.7 |  | 0.7 | 0.7 | 0.7
|  |  | Hours PA > 95% Peak Load |  | 15 | 15 | 15 |  | 15 |  | 15 | 15 |  | 15 |  | 15 | 15 | 15
|  |  | Raw LAR (MVA) |  | 15.6 | 16 | 16 |  | 16 |  | 16.1 | 13.8 |  | 14.2 |  | 14.4 | 14.4 | 14.4
|  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Manual Trans Avail (MVA) |  | 25.7 | 25.7 | 25.7 |  | 25.7 |  | 25.7 | 28.4 |  | 28.4 |  | 28.4 | 28.4 | 28.4
|  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## KILL
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | KILL - Killarney (33/11kV) | [8 empty] | Supply |  | T058 - Warwick BSP
| Description |  |  |  | Region is South West
Transformer size is 2x33/11kV 3MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -3.7%, 2021 S 1.8% W 1.8%, 2022 S 1.6% W 1.6%, 2023 S 2.2% W 2.2%, 2024 S 2.6% W 2.6%
|  |  | Latest Peak Compensated Load | [5 empty] | 2.1 MVA on 19/07/2019 at 07:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 7.5 | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 8.9 |  | 8.9 |  | 8.9 | 8.9 | 8.9
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 1.9 | 2 | 2 |  | 2.1 |  | 2.1 | 2.1 |  | 2.1 |  | 2.2 | 2.2 | 2.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.949 | 0.949 | 0.949 |  | 0.949 |  | 0.949 | 0.957 |  | 0.957 |  | 0.957 | 0.957 | 0.957
|  |  |  | ECC Rating (MVA) |  | 4.3 | 4.3 | 4.3 |  | 4.3 |  | 4.3 | 4.5 |  | 4.5 |  | 4.5 | 4.5 | 4.5
|  |  |  | 50 PoE Load (MVA) |  | 1.8 | 1.8 | 1.8 |  | 1.9 |  | 1.9 | 2 |  | 2 |  | 2 | 2.1 | 2.1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 4.5 | 4.5 | 4.5 |  | 4.5 |  | 4.5 | 4.5 |  | 4.5 |  | 4.5 | 4.5 | 4.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## KING
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | KING - Kingaroy (66/11kV) | [8 empty] | Supply |  | H018 - Tarong BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 2x66/11kV 20/25/27MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -1.7%, 2021 S 0.1% W 0.1%, 2022 S -0.3% W -0.3%2023 S 0.0% W 0.0%, 2024 S -0.2% W -0.2
|  |  | Latest Peak Compensated Load | [5 empty] | 24.4 MVA on 16/12/2019 at 17:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 57.4 | 57.4 | 57.4 |  | 57.4 |  | 57.4 | 64.7 |  | 64.7 |  | 64.7 | 64.7 | 64.7
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 25.8 | 25.8 | 25.8 |  | 25.9 |  | 25.9 | 22.8 |  | 22.7 |  | 22.5 | 22.4 | 22.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.964 | 0.964 | 0.964 |  | 0.964 |  | 0.964 | 0.979 |  | 0.979 |  | 0.979 | 0.979 | 0.979
|  |  |  | ECC Rating (MVA) |  | 32.5 | 32.5 | 32.5 |  | 32.5 |  | 32.5 | 36.2 |  | 36.2 |  | 36.2 | 36.2 | 36.2
|  |  |  | 50 PoE Load (MVA) |  | 23.8 | 23.8 | 23.8 |  | 23.8 |  | 23.8 | 21.7 |  | 21.6 |  | 21.4 | 21.3 | 21.4
|  |  |  | 50 PoE Load > 95% (MVA) |  | 1.2 | 1.2 | 1.2 |  | 1.2 |  | 1.2 | 1.1 |  | 1.1 |  | 1.1 | 1.1 | 1.1
|  |  |  | Hours PA > 95% Peak Load |  | 16 | 16 | 16 |  | 16 |  | 16 | 16 |  | 16 |  | 16 | 16 | 16
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## KIRK
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | KIRK - Kirknie (66/11kV) | [8 empty] | Supply |  | T193 - Clare South BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/11kV 10MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.0%, 2021 S -0.4% W -0.4%2022 S -0.7% W -0.7%2023 S -0.1% W -0.1%2024 S -0.5% W -0.5
|  |  | Latest Peak Compensated Load | [5 empty] | 8.4 MVA on 13/02/2020 at 19:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 9.7 | 9.7 | 9.7 |  | 9.7 |  | 9.7 | 10.9 |  | 10.9 |  | 10.9 | 10.9 | 10.9
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 8.6 | 8.5 | 8.5 |  | 8.5 |  | 8.5 | 4.1 |  | 4.1 |  | 4.1 | 4 | 4
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.853 | 0.853 | 0.853 |  | 0.853 |  | 0.853 | 0.75 |  | 0.75 |  | 0.75 | 0.75 | 0.75
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 8.4 | 8.3 | 8.3 |  | 8.3 |  | 8.3 | 4 |  | 4 |  | 4 | 3.9 | 3.9
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.4 | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 62 | 62 | 62 |  | 62 |  | 62 | 62 |  | 62 |  | 62 | 62 | 62
|  |  |  | Raw LAR (MVA) |  | 8.4 | 8.3 | 8.3 |  | 8.3 |  | 8.3 | 4 |  | 4 |  | 4 | 3.9 | 3.9
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 | 2 | 2
|  |  |  | Mobile Plant Avail (MVA) |  | 1.3 | 1.3 | 1.3 |  | 1.3 |  | 1.3 | 1.3 |  | 1.3 |  | 1.3 | 1.3 | 1.3
|  |  |  | Shed(30min) |  | 7 | 7 | 7 |  | 7 |  | 7 | 7 |  | 7 |  | 7 | 7 | 7
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## KITO
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | KITO - Kilkivan Town (66/11kV) | [8 empty] | Supply |  | KILK - Kilkivan BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 2x62/11kV 1MVA ON
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.0%, 2021 S 0.5% W 0.5%, 2022 S 0.3% W 0.3%, 2023 S 0.5% W 0.5%, 2024 S 0.2% W 0.2%
|  |  | Latest Peak Compensated Load | [5 empty] | 1.1 MVA on 05/12/2019 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 | 2 | 2
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 1.2 | 1.2 | 1.2 |  | 1.2 |  | 1.2 | 1 |  | 1 |  | 1 | 1 | 1
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.954 | 0.954 | 0.954 |  | 0.954 |  | 0.954 | 0.958 |  | 0.958 |  | 0.958 | 0.958 | 0.958
|  |  |  | ECC Rating (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | 50 PoE Load (MVA) |  | 1.1 | 1.1 | 1.1 |  | 1.1 |  | 1.1 | 0.9 |  | 0.9 |  | 0.9 | 0.9 | 0.9
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 5.5 | 5.5 | 5.5 |  | 5.5 |  | 5.5 | 5.5 |  | 5.5 |  | 5.5 | 5.5 | 5.5
|  |  |  | Raw LAR (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## KOCR
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | KOCR - Kogan Creek (33/11kV) | [8 empty] | Supply |  | CHIN - Chinchilla BSP
| Description |  |  |  | Region is South West
Transformer size is 1xKOCR TFR1-66/33KV TRANSF 1
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 7.2%, 2021 S 0.5% W 0.5%, 2022 S 0.4% W 0.4%, 2023 S 0.4% W 0.4%, 2024 S 0.3% W 0.3%
|  |  | Latest Peak Compensated Load | [5 empty] | 0.5 MVA on 11/02/2020 at 21:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 | 5 | 5
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.755 | 0.755 | 0.755 |  | 0.755 |  | 0.755 | 0.925 |  | 0.925 |  | 0.925 | 0.925 | 0.925
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 69 | 69 | 69 |  | 69 |  | 69 | 69 |  | 69 |  | 69 | 69 | 69
|  |  |  | Raw LAR (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Mobile Plant Avail (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## KOUM
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | KOUM - Koumala (33/11kV) | [8 empty] | Supply |  | T065 - Alligator Creek BSP
| Description |  |  |  | Region is Mackay
Transformer size is 1x33/11kV 5MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.3%, 2021 S 0.4% W 0.4%, 2022 S 0.3% W 0.3%, 2023 S 0.4% W 0.4%, 2024 S 0.3% W 0.3%
|  |  | Latest Peak Compensated Load | [5 empty] | 2.3 MVA on 04/12/2019 at 21:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 7 | 7 | 7 |  | 7 |  | 7 | 7.5 |  | 7.5 |  | 7.5 | 7.5 | 7.5
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 2.4 | 2.4 | 2.4 |  | 2.4 |  | 2.4 | 1.6 |  | 1.6 |  | 1.5 | 1.5 | 1.6
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.888 | 0.888 | 0.888 |  | 0.888 |  | 0.888 | 0.888 |  | 0.888 |  | 0.888 | 0.888 | 0.888
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 2.3 | 2.3 | 2.3 |  | 2.4 |  | 2.4 | 1.5 |  | 1.5 |  | 1.5 | 1.5 | 1.5
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 3.5 | 3.5 | 3.5 |  | 3.5 |  | 3.5 | 3.5 |  | 3.5 |  | 3.5 | 3.5 | 3.5
|  |  |  | Raw LAR (MVA) |  | 2.3 | 2.3 | 2.3 |  | 2.4 |  | 2.4 | 1.5 |  | 1.5 |  | 1.5 | 1.5 | 1.5
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 1.9 | 1.9 | 1.9 |  | 1.9 |  | 1.9 | 1.9 |  | 1.9 |  | 1.9 | 1.9 | 1.9
|  |  |  | Mobile Plant Avail (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## LACR
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | LACR - Lakes Creek (66/11kV) | [8 empty] | Supply |  | RMES - Rockhampton Mesh
| Description |  |  |  | Region is Capricornia
Transformer size is 2x66/11kV 16/20MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.6%, 2021 S -0.1% W -0.1%2022 S -0.4% W -0.4%2023 S -0.0% W -0.0%2024 S -0.4% W -0.4
|  |  | Latest Peak Compensated Load | [5 empty] | 13.7 MVA on 16/12/2019 at 17:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 45.9 | 45.9 | 45.9 |  | 45.9 |  | 45.9 | 50.9 |  | 50.9 |  | 50.9 | 50.9 | 50.9
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 15 | 14.9 | 14.9 |  | 14.9 |  | 15.7 | 12 |  | 11.9 |  | 11.8 | 11.8 | 11.8
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 1 | 1 | 1 |  | 1 |  | 0.948 | 0.935 |  | 0.935 |  | 0.935 | 0.935 | 0.935
|  |  |  | ECC Rating (MVA) |  | 27 | 27 | 27 |  | 27 |  | 27 | 29.3 |  | 29.3 |  | 29.3 | 29.3 | 29.3
|  |  |  | 50 PoE Load (MVA) |  | 14.6 | 14.5 | 14.5 |  | 14.6 |  | 14.5 | 11.7 |  | 11.7 |  | 11.6 | 11.5 | 11.5
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.7 | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  |  | Hours PA > 95% Peak Load |  | 6.5 | 6.5 | 6.5 |  | 6.5 |  | 6.5 | 6.5 |  | 6.5 |  | 6.5 | 6.5 | 6.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## LAKE
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | LAKE - Lakeland (66/22kV) | [8 empty] | Supply |  | T159 - Lakeland BSP
| Description |  |  |  | Region is Far North
Transformer size is 2x20MVA
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.3%, 2021 S 0.1% W 0.1%, 2022 S -0.1% W -0.1%2023 S 0.2% W 0.2%, 2024 S -0.1% W -0.1
|  |  | Latest Peak Compensated Load | [5 empty] | 1.5 MVA on 16/07/2019 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 16 | 16 | 16 |  | 16 |  | 16 | 16 |  | 16 |  | 16 | 16 | 16
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 1.6 |  | 1.6 |  | 1.6 | 1.6 | 1.6
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.74 | 0.74 | 0.74 |  | 0.74 |  | 0.74 | 0.975 |  | 0.975 |  | 0.975 | 0.975 | 0.975
|  |  |  | ECC Rating (MVA) |  | 8 | 8 | 8 |  | 8 |  | 8 | 8 |  | 8 |  | 8 | 8 | 8
|  |  |  | 50 PoE Load (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 1.5 |  | 1.5 |  | 1.5 | 1.5 | 1.5
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 7 | 7 | 7 |  | 7 |  | 7 | 7 |  | 7 |  | 7 | 7 | 7
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## LANN
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | LANN - Lannercost (66/11kV) | [8 empty] | Supply |  | T047 - Ingham BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/11kV 6.3MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.3%, 2021 S -0.4% W -0.4%2022 S -0.5% W -0.5%2023 S -0.4% W -0.4%2024 S -0.5% W -0.5
|  |  | Latest Peak Compensated Load | [5 empty] | 2.1 MVA on 11/02/2020 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 8.2 | 8.2 | 8.2 |  | 8.2 |  | 8.2 | 8.7 |  | 8.7 |  | 8.7 | 8.7 | 8.7
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 2.2 | 2.2 | 2.2 |  | 2.2 |  | 2.2 | 1.3 |  | 1.3 |  | 1.2 | 1.2 | 1.2
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.984 | 0.984 | 0.984 |  | 0.984 |  | 0.984 | 0.991 |  | 0.991 |  | 0.991 | 0.991 | 0.991
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 1.2 |  | 1.2 |  | 1.2 | 1.2 | 1.2
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 4 | 4 | 4 |  | 4 |  | 4 | 4 |  | 4 |  | 4 | 4 | 4
|  |  |  | Raw LAR (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 1.2 |  | 1.2 |  | 1.2 | 1.2 | 1.2
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 | 2 | 2
|  |  |  | Mobile Plant Avail (MVA) |  | 0.4 | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## LAQU
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | LAQU - Laguna Quays (66/11kV) | [8 empty] | Supply |  | PROS - Proserpine BSP
| Description |  |  |  | Region is Mackay
Transformer size is 2x66/11kV 7.5MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.4%, 2021 S 0.6% W 0.6%, 2022 S 0.5% W 0.5%, 2023 S 0.6% W 0.6%, 2024 S 0.4% W 0.4%
|  |  | Latest Peak Compensated Load | [5 empty] | 2 MVA on 05/12/2019 at 19:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 17.6 | 17.6 | 17.6 |  | 17.6 |  | 17.6 | 19 |  | 19 |  | 19 | 19 | 19
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 2.3 | 2.4 | 2.4 |  | 2.4 |  | 2.4 | 1.2 |  | 1.2 |  | 1.2 | 1.2 | 1.2
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.98 | 0.98 | 0.98 |  | 0.98 |  | 0.98 | 0.987 |  | 0.987 |  | 0.987 | 0.987 | 0.987
|  |  |  | ECC Rating (MVA) |  | 9.7 | 9.7 | 9.7 |  | 9.7 |  | 9.7 | 10.3 |  | 10.3 |  | 10.3 | 10.3 | 10.3
|  |  |  | 50 PoE Load (MVA) |  | 2 | 2 | 2 |  | 2.1 |  | 2.1 | 1.1 |  | 1.1 |  | 1.1 | 1.1 | 1.1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 9.5 | 9.5 | 9.5 |  | 9.5 |  | 9.5 | 9.5 |  | 9.5 |  | 9.5 | 9.5 | 9.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## LARO
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | LARO - Skid D (Landing Road) (66/11kV) | [8 empty] | Supply |  | T130 - Boat Creek BSP
| Description |  |  |  | Region is Capricornia
Transformer size is 1x10MVA Skid Transformer ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.0%, 2021 S 0.0% W 0.0%, 2022 S 0.0% W 0.0%, 2023 S 0.0% W 0.0%, 2024 S 0.0% W 0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 1.7 MVA on 05/12/2019 at 15:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 11 | 11 | 11 |  | 11 |  | 11 | 11 |  | 11 |  | 11 | 11 | 11
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 1.6 | 1.6 | 1.6 |  | 1.6 |  | 1.6 | 1.5 |  | 1.5 |  | 1.5 | 1.5 | 1.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.765 | 0.765 | 0.765 |  | 0.765 |  | 0.765 | 0.756 |  | 0.756 |  | 0.756 | 0.756 | 0.756
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 1.6 | 1.6 | 1.6 |  | 1.6 |  | 1.6 | 1.4 |  | 1.4 |  | 1.4 | 1.4 | 1.4
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 62.5 | 62.5 | 62.5 |  | 62.5 |  | 62.5 | 62.5 |  | 62.5 |  | 62.5 | 62.5 | 62.5
|  |  |  | Raw LAR (MVA) |  | 1.6 | 1.6 | 1.6 |  | 1.6 |  | 1.6 | 1.4 |  | 1.4 |  | 1.4 | 1.4 | 1.4
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 2.4 | 2.4 | 2.4 |  | 2.4 |  | 2.4 | 2.4 |  | 2.4 |  | 2.4 | 2.4 | 2.4
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 3.1 | 3.1 | 3.1 |  | 3.1 |  | 3.1 | 3.1 |  | 3.1 |  | 3.1 | 3.1 | 3.1
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## LITT
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | LITT - Littlemore (66/11kV) | [8 empty] | Supply |  | T019 - Gladstone South BSP
| Description |  |  |  | Region is Capricornia
Transformer size is 1x66/11kV 2MVA ON;1x66/11kV 2MVA ON(Standby)
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.2%, 2021 S 0.8% W 0.8%, 2022 S 0.2% W 0.2%, 2023 S 1.5% W 1.5%, 2024 S -0.2% W -0.2
|  |  | Latest Peak Compensated Load | [5 empty] | 0.7 MVA on 16/12/2019 at 15:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 2.2 | 2.2 | 2.2 |  | 2.2 |  | 2.2 | 2.2 |  | 2.2 |  | 2.2 | 2.2 | 2.2
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.877 | 0.877 | 0.877 |  | 0.877 |  | 0.877 | 0.927 |  | 0.927 |  | 0.927 | 0.927 | 0.927
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 5.5 | 5.5 | 5.5 |  | 5.5 |  | 5.5 | 5.5 |  | 5.5 |  | 5.5 | 5.5 | 5.5
|  |  |  | Raw LAR (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 | 2 | 2
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## LOCR
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | LOCR - Louisa Creek (33/11kV) | [8 empty] | Supply |  | T176 - Louisa Creek BSP
| Description |  |  |  | Region is Mackay
Transformer size is 1x33/11kV 6.3MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.7%, 2021 S 0.9% W 0.9%, 2022 S 0.8% W 0.8%, 2023 S 0.9% W 0.9%, 2024 S 0.7% W 0.7%
|  |  | Latest Peak Compensated Load | [5 empty] | 2.4 MVA on 16/02/2020 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 7.4 | 7.4 | 7.4 |  | 7.4 |  | 7.4 | 7.8 |  | 7.8 |  | 7.8 | 7.8 | 7.8
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 2.6 | 2.7 | 2.7 |  | 2.7 |  | 2.7 | 1.9 |  | 1.9 |  | 1.9 | 1.9 | 1.9
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 1 | 1 | 1 |  | 1 |  | 1 | 0.998 |  | 0.998 |  | 0.998 | 0.998 | 0.998
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 2.5 | 2.5 | 2.5 |  | 2.5 |  | 2.6 | 1.9 |  | 1.9 |  | 1.9 | 1.9 | 1.9
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 6 | 6 | 6 |  | 6 |  | 6 | 6 |  | 6 |  | 6 | 6 | 6
|  |  |  | Raw LAR (MVA) |  | 2.5 | 2.5 | 2.5 |  | 2.5 |  | 2.6 | 1.9 |  | 1.9 |  | 1.9 | 1.9 | 1.9
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 1.2 | 1.2 | 1.2 |  | 1.2 |  | 1.2 | 1.2 |  | 1.2 |  | 1.2 | 1.2 | 1.2
|  |  |  | Mobile Plant Avail (MVA) |  | 1.6 | 1.6 | 1.6 |  | 1.6 |  | 1.6 | 1.6 |  | 1.6 |  | 1.6 | 1.6 | 1.6
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## LONG
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | LONG - Longreach (66/22kV) | [8 empty] | Supply |  | T072 - Barcaldine BSP
| Description |  |  |  | Region is Capricornia
Transformer size is 2x66/22kV 8/10MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -1.9%, 2021 S -0.8% W -0.8%2022 S -0.9% W -0.9%2023 S -0.4% W -0.4%2024 S -0.6% W -0.6
|  |  | Latest Peak Compensated Load | [5 empty] | 9.1 MVA on 18/02/2020 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 24.4 | 24.4 | 24.4 |  | 24.4 |  | 24.4 | 28.6 |  | 28.6 |  | 28.6 | 28.6 | 28.6
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 10.1 | 10 | 9.9 |  | 9.9 |  | 9.9 | 7.2 |  | 7.1 |  | 7 | 7 | 7
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.994 | 0.994 | 0.994 |  | 0.994 |  | 0.994 | 0.995 |  | 0.995 |  | 0.995 | 0.995 | 0.995
|  |  |  | ECC Rating (MVA) |  | 13.9 | 13.9 | 13.9 |  | 13.9 |  | 13.9 | 15 |  | 15 |  | 15 | 15 | 15
|  |  |  | 50 PoE Load (MVA) |  | 9.3 | 9.2 | 9.2 |  | 9.2 |  | 9.2 | 6.7 |  | 6.7 |  | 6.6 | 6.5 | 6.5
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Hours PA > 95% Peak Load |  | 11 | 11 | 11 |  | 11 |  | 11 | 11 |  | 11 |  | 11 | 11 | 11
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## LUCI
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | LUCI - Lucinda (66/11kV) | [8 empty] | Supply |  | T047 - Ingham BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/11kV 5/4MVA ONAF/ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.4%, 2021 S -0.2% W -0.2%2022 S -0.3% W -0.3%2023 S -0.2% W -0.2%2024 S -0.3% W -0.3
|  |  | Latest Peak Compensated Load | [5 empty] | 2.8 MVA on 25/08/2019 at 17:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 5.9 | 5.9 | 5.9 |  | 5.9 |  | 5.9 | 6 |  | 6 |  | 6 | 6 | 6
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 2.7 | 2.7 | 2.7 |  | 2.7 |  | 2.7 | 2.8 |  | 2.7 |  | 2.8 | 2.8 | 2.8
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.881 | 0.881 | 0.881 |  | 0.881 |  | 0.881 | 0.88 |  | 0.884 |  | 0.88 | 0.88 | 0.88
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 2.7 | 2.7 | 2.7 |  | 2.7 |  | 2.7 | 2.8 |  | 2.7 |  | 2.7 | 2.7 | 2.7
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 34 | 34 | 34 |  | 34 |  | 34 | 34 |  | 34 |  | 34 | 34 | 34
|  |  |  | Raw LAR (MVA) |  | 2.7 | 2.7 | 2.7 |  | 2.7 |  | 2.7 | 2.8 |  | 2.7 |  | 2.7 | 2.7 | 2.7
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 1.1 | 1.1 | 1.1 |  | 1.1 |  | 1.1 | 1.1 |  | 1.1 |  | 1.1 | 1.1 | 1.1
|  |  |  | Mobile Plant Avail (MVA) |  | 0.4 | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  |  | Shed(30min) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 | 2 | 2
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## LYLA
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | LYLA - Lyndley Lane (33/22kV) | [8 empty] | Supply |  | T002 - Dalby East BSP
| Description |  |  |  | Region is South West
Transformer size is 1x33/22kV 0.3MVA ON;1x33/22kV 0.75MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.0%, 2021 S 0.3% W 0.3%, 2022 S 0.2% W 0.2%, 2023 S 0.3% W 0.3%, 2024 S 0.1% W 0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 0.7 MVA on 02/01/2020 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 1.1 | 1.1 | 1.1 |  | 1.1 |  | 1.1 | 1.1 |  | 1.1 |  | 1.1 | 1.1 | 1.1
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 0.7 | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.993 | 0.993 | 0.993 |  | 0.993 |  | 0.993 | 0.986 |  | 0.986 |  | 0.986 | 0.986 | 0.986
|  |  |  | ECC Rating (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | 50 PoE Load (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 7.5 | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 | 7.5
|  |  |  | Raw LAR (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Mobile Plant Avail (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MACI
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MACI - Maryborough City (66/11kV) | [8 empty] | Supply |  | MARY - Maryborough BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 2x66/11kV 14/19MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 73.0 MVA
Growth Rates |  |  |  |  | 2020 W -1.6%, 2021 S -0.4% W -0.4%2022 S -0.8% W -0.8%2023 S -0.6% W -0.6%2024 S -0.4% W -0.4
|  |  | Latest Peak Compensated Load | [5 empty] | 14.5 MVA on 16/12/2019 at 16:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 39.6 | 39.6 | 39.6 |  | 39.6 |  | 39.6 | 42.7 |  | 42.7 |  | 42.7 | 42.7 | 42.7
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 16.9 | 17.2 | 17.5 |  | 17.6 |  | 17.5 | 13.1 |  | 13 |  | 13.1 | 13.4 | 13.4
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | ECC Rating (MVA) |  | 22.7 | 22.7 | 22.7 |  | 22.7 |  | 22.7 | 24.4 |  | 24.4 |  | 24.4 | 24.4 | 24.4
|  |  |  | 50 PoE Load (MVA) |  | 15.5 | 15.8 | 16.1 |  | 16.1 |  | 16.1 | 12 |  | 11.9 |  | 12.1 | 12.3 | 12.3
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.8 | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  |  | Hours PA > 95% Peak Load |  | 9 | 9 | 9 |  | 9 |  | 9 | 9 |  | 9 |  | 9 | 9 | 9
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 | 2 | 2
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MACN
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MACN - Macknade (66/11kV) | [8 empty] | Supply |  | T047 - Ingham BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/11kV 8/10MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 8.8 MVA
Growth Rates |  |  |  |  | 2020 W -0.3%, 2021 S -0.4% W -0.4%2022 S -0.5% W -0.5%2023 S -0.4% W -0.4%2024 S -0.6% W -0.6
|  |  | Latest Peak Compensated Load | [5 empty] | 4.5 MVA on 20/01/2020 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 13.5 | 13.5 | 13.5 |  | 13.5 |  | 13.5 | 13.4 |  | 13.4 |  | 13.4 | 13.4 | 13.4
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 5.7 | 5.6 | 5.6 |  | 5.6 |  | 5.6 | 3.8 |  | 3.8 |  | 3.8 | 3.7 | 3.7
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.956 | 0.956 | 0.956 |  | 0.956 |  | 0.956 | 0.991 |  | 0.991 |  | 0.991 | 0.991 | 0.991
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 5 | 5 | 5 |  | 5 |  | 5 | 3.7 |  | 3.7 |  | 3.7 | 3.6 | 3.6
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 4.5 | 4.5 | 4.5 |  | 4.5 |  | 4.5 | 4.5 |  | 4.5 |  | 4.5 | 4.5 | 4.5
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MAFU
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MAFU - Max Fulton (66/11kV) | [8 empty] | Supply |  | TMES - Townsville Mesh
| Description |  |  |  | Region is Nth Queensland
Transformer size is 2x66/11kV 21/26.25/35MVA ONAN/ODAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.1%, 2021 S -0.3% W -0.3%2022 S -0.5% W -0.5%2023 S -0.2% W -0.2%2024 S -0.3% W -0.3
|  |  | Latest Peak Compensated Load | [5 empty] | 13.9 MVA on 14/02/2020 at 16:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 76.3 | 76.3 | 76.3 |  | 76.3 |  | 76.3 | 77.7 |  | 77.7 |  | 77.7 | 77.7 | 77.7
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 15.4 | 15.3 | 15.3 |  | 15.3 |  | 15.3 | 10 |  | 9.9 |  | 9.8 | 9.7 | 9.7
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.999 | 1 | 1 |  | 1 |  | 1 | 0.971 |  | 0.971 |  | 0.971 | 0.971 | 0.971
|  |  |  | ECC Rating (MVA) |  | 38.5 | 38.5 | 38.5 |  | 38.5 |  | 38.5 | 39.2 |  | 39.2 |  | 39.2 | 39.2 | 39.2
|  |  |  | 50 PoE Load (MVA) |  | 14 | 14 | 13.9 |  | 14 |  | 14 | 9.4 |  | 9.3 |  | 9.2 | 9.1 | 9.2
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.7 | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | Hours PA > 95% Peak Load |  | 21 | 21 | 21 |  | 21 |  | 21 | 21 |  | 21 |  | 21 | 21 | 21
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MALC
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MALC - Malchi (66/11kV) | [8 empty] | Supply |  | RMES - Rockhampton Mesh
| Description |  |  |  | Region is Capricornia
Transformer size is 2x66/11kV 7.5/10MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 1.0%, 2021 S 1.2% W 1.2%, 2022 S 1.0% W 1.0%, 2023 S 1.0% W 1.0%, 2024 S 0.9% W 0.9%
|  |  | Latest Peak Compensated Load | [5 empty] | 19 MVA on 16/12/2019 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 23.8 | 23.8 | 23.8 |  | 23.8 |  | 23.8 | 28.7 |  | 28.7 |  | 28.7 | 28.7 | 28.7
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 20.4 | 20.6 | 13.6 |  | 13.8 |  | 14 | 9.5 |  | 9.6 |  | 4.3 | 4.3 | 4.4
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.982 | 0.982 | 0.983 |  | 0.983 |  | 0.983 | 0.993 |  | 0.992 |  | 0.996 | 0.996 | 0.996
|  |  |  | ECC Rating (MVA) |  | 13.3 | 13.3 | 13.3 |  | 13.3 |  | 13.3 | 15 |  | 15 |  | 15 | 15 | 15
|  |  |  | 50 PoE Load (MVA) |  | 17.7 | 17.9 | 10.9 |  | 11.1 |  | 11.2 | 9.1 |  | 9.2 |  | 3.9 | 3.9 | 4
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.9 | 0.9 | 0.5 |  | 0.6 |  | 0.6 | 0.5 |  | 0.5 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 4.5 | 4.5 | 4.5 |  | 4.5 |  | 4.5 | 4.5 |  | 4.5 |  | 4.5 | 4.5 | 4.5
|  |  |  | Raw LAR (MVA) |  | 4.4 | 4.6
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 1.5 | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.5 | 1.5
|  |  |  | Mobile Plant Avail (MVA) |  | 2.5 | 2.5 | 2.5 |  | 2.5 |  | 2.5 | 2.5 |  | 2.5 |  | 2.5 | 2.5 | 2.5
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | LARc (MVA) |  | 0.4 | 0.6
|  |  |  | LARc (MW) |  | 0.4 | 0.6
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | No | No | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MARE
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MARE - Mareeba (66/22kV) | [8 empty] | Supply |  | TURK - Turkinje 66kV BSP
| Description |  |  |  | Region is Far North
Transformer size is 2x66/22kV 20/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 1.0%, 2021 S 0.7% W 0.7%, 2022 S 0.5% W 0.5%, 2023 S 0.7% W 0.7%, 2024 S 0.4% W 0.4%
|  |  | Latest Peak Compensated Load | [5 empty] | 20.2 MVA on 05/12/2019 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 51.2 | 51.2 | 51.2 |  | 51.2 |  | 51.2 | 63.6 |  | 63.6 |  | 63.6 | 63.6 | 63.6
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 22.7 | 22.8 | 23 |  | 23.2 |  | 23.4 | 17.6 |  | 17.7 |  | 17.6 | 17.7 | 17.8
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.999 | 0.999 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | ECC Rating (MVA) |  | 32.8 | 32.8 | 32.8 |  | 32.8 |  | 32.8 | 35.2 |  | 35.2 |  | 35.2 | 35.2 | 35.2
|  |  |  | 50 PoE Load (MVA) |  | 21.1 | 21.2 | 21.4 |  | 21.6 |  | 21.7 | 17.2 |  | 17.3 |  | 17.3 | 17.3 | 17.5
|  |  |  | 50 PoE Load > 95% (MVA) |  | 1.1 | 1.1 | 1.1 |  | 1.1 |  | 1.1 | 0.9 |  | 0.9 |  | 0.9 | 0.9 | 0.9
|  |  |  | Hours PA > 95% Peak Load |  | 17 | 17 | 17 |  | 17 |  | 17 | 17 |  | 17 |  | 17 | 17 | 17
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MARY
Bulk Summary Information and Peak Load Forecast
Substation |  |  |  | MARY - Maryborough BSP (132/66kV) | [8 empty] | Supply |  | QTBC - Teebar Creek TCP
Description |  |  |  | Region is Wide Bay
Transformer size is 2x132/66/11kV 80/100MVA ONAN/ODAN;1x132/66kV 64/80/90MVA ONAN/ODAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 148.4 MVA
|  | Latest Peak Compensated Load | [5 empty] | 121.9 MVA on 20/02/2020 at 17:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[5 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  | NCC Rating (MVA) |  | 356.1 | 356.1 | 356.1 |  | 356.1 |  | 356.1 | 403.7 |  | 403.7 |  | 403.7 | 403.7 | 403.7
|  |  | Contracted non-network (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  | 10 PoE Load (MVA) |  | 132.8 | 136.9 | 139.3 |  | 140 |  | 140.6 | 111.2 |  | 112.7 |  | 114.3 | 116.2 | 116.9
LARn (MVA)
LARn (MW)
|  |  | Power Factor at Peak Load |  | 0.993 | 0.993 | 0.993 |  | 0.993 |  | 0.993 | 0.999 |  | 0.999 |  | 0.999 | 0.999 | 0.999
|  |  | ECC Rating (MVA) |  | 266.8 | 266.8 | 266.8 |  | 266.8 |  | 266.8 | 269.1 |  | 269.1 |  | 269.1 | 269.1 | 269.1
|  |  | 50 PoE Load (MVA) |  | 123.9 | 127.1 | 129.4 |  | 130.1 |  | 130.6 | 106.2 |  | 107.3 |  | 108.9 | 110.8 | 111.5
|  |  | 50 PoE Load > 95% (MVA) |  | 6.2 | 6.4 | 6.5 |  | 6.5 |  | 6.5 | 5.3 |  | 5.4 |  | 5.4 | 5.5 | 5.6
|  |  | Hours PA > 95% Peak Load |  | 9 | 9 | 9 |  | 9 |  | 9 | 9 |  | 9 |  | 9 | 9 | 9
Raw LAR (MVA)
|  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MASO
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MASO - Marian South (66/11kV) | [8 empty] | Supply |  | PIVA - Pioneer Valley BSP
| Description |  |  |  | Region is Mackay
Transformer size is 1x10MVA 66/11kV Transformer
Capacity of commissioned Embedded Generation (with Connection Agreements) is 23.4 MVA
Growth Rates |  |  |  |  | 2020 W 0.7%, 2021 S 0.3% W 0.3%, 2022 S 0.2% W 0.2%, 2023 S 0.3% W 0.3%, 2024 S 0.1% W 0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 6.3 MVA on 26/11/2019 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 15 | 15 | 15 |  | 15 |  | 15 | 15 |  | 15 |  | 15 | 15 | 15
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 6.5 | 6.5 | 6.6 |  | 6.6 |  | 6.6 | 5.7 |  | 5.7 |  | 5.6 | 5.6 | 5.7
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.995 | 0.995 | 0.995 |  | 0.995 |  | 0.995 | 0.998 |  | 0.998 |  | 0.998 | 0.998 | 0.998
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 5.8 | 5.8 | 5.8 |  | 5.9 |  | 5.9 | 5.2 |  | 5.2 |  | 5.2 | 5.2 | 5.2
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Hours PA > 95% Peak Load |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10
|  |  |  | Raw LAR (MVA) |  | 5.8 | 5.8 | 5.8 |  | 5.9 |  | 5.9 | 5.2 |  | 5.2 |  | 5.2 | 5.2 | 5.2
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 3.4 | 3.4 | 3.4 |  | 3.4 |  | 3.4 | 3.4 |  | 3.4 |  | 3.4 | 3.4 | 3.4
|  |  |  | Mobile Plant Avail (MVA) |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 2.8 | 2.8 | 2.8 |  | 2.8 |  | 2.8 | 2.8 |  | 2.8 |  | 2.8 | 2.8 | 2.8
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MCCR
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MCCR - McKinley Creek (66/11kV) | [8 empty] | Supply |  | PIVA - Pioneer Valley BSP
| Description |  |  |  | Region is Mackay
Transformer size is 1x66/11kV 5/6.3MVA ONAN/ONAF;1xMCCR TX NO 1-66/11KV TRANSF 1
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.5%, 2021 S 0.8% W 0.8%, 2022 S 0.6% W 0.6%, 2023 S 0.7% W 0.7%, 2024 S 0.5% W 0.5%
|  |  | Latest Peak Compensated Load | [5 empty] | 3.5 MVA on 14/02/2020 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 15.1 | 15.1 | 15.1 |  | 15.1 |  | 15.1 | 15.1 |  | 15.1 |  | 15.1 | 15.1 | 15.1
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 3.9 | 3.9 | 3.9 |  | 4 |  | 4 | 2.5 |  | 2.6 |  | 2.6 | 2.6 | 2.6
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.98 | 0.98 | 0.98 |  | 0.98 |  | 0.98 | 0.988 |  | 0.988 |  | 0.988 | 0.988 | 0.988
|  |  |  | ECC Rating (MVA) |  | 7.9 | 7.9 | 7.9 |  | 7.9 |  | 7.9 | 8.2 |  | 8.2 |  | 8.2 | 8.2 | 8.2
|  |  |  | 50 PoE Load (MVA) |  | 3.5 | 3.5 | 3.6 |  | 3.6 |  | 3.6 | 2.5 |  | 2.5 |  | 2.5 | 2.5 | 2.5
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 5.5 | 5.5 | 5.5 |  | 5.5 |  | 5.5 | 5.5 |  | 5.5 |  | 5.5 | 5.5 | 5.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MEAD
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MEAD - Meadowvale (66/11kV) | [8 empty] | Supply |  | BUND - Bundaberg BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 1x66/11kV 12/14MVA ONAN/ONAF;1x62/11kV 7.5MVA ONAN(Standby)
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.4%, 2021 S 0.2% W 0.2%, 2022 S 0.1% W 0.1%, 2023 S 0.2% W 0.2%, 2024 S -0.1% W -0.1
|  |  | Latest Peak Compensated Load | [5 empty] | 9.5 MVA on 03/12/2019 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 15.9 | 15.9 | 15.9 |  | 15.9 |  | 15.9 | 17.3 |  | 17.3 |  | 17.3 | 17.3 | 17.3
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 10.9 | 10.9 | 10.9 |  | 11 |  | 11 | 9.1 |  | 9.1 |  | 9 | 9 | 9
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.982 | 0.982 | 0.982 |  | 0.982 |  | 0.982 | 0.981 |  | 0.981 |  | 0.981 | 0.981 | 0.981
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 9.7 | 9.7 | 9.7 |  | 9.8 |  | 9.8 | 8.6 |  | 8.6 |  | 8.5 | 8.5 | 8.5
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  |  | Hours PA > 95% Peak Load |  | 15 | 15 | 15 |  | 15 |  | 15 | 15 |  | 15 |  | 15 | 15 | 15
|  |  |  | Raw LAR (MVA) |  | 9.7 | 9.7 | 9.7 |  | 9.8 |  | 9.8 | 8.6 |  | 8.6 |  | 8.5 | 8.5 | 8.5
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 11.2 | 11.2 | 11.2 |  | 11.2 |  | 11.2 | 11.2 |  | 11.2 |  | 11.2 | 11.2 | 11.2
|  |  |  | Manual Trans Avail (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 | 2 | 2
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MEAN
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MEAN - Meandarra (33/22kV) | [8 empty] | Supply |  | COLU - Columboola BSP
| Description |  |  |  | Region is South West
Transformer size is 1x33/22kV 1MVA ONAN;1x33/22kV 1MVA ONAN(Standby)
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.2%, 2021 S 0.0% W 0.0%, 2022 S -0.1% W -0.1%2023 S 0.0% W 0.0%, 2024 S -0.2% W -0.2
|  |  | Latest Peak Compensated Load | [5 empty] | 0.7 MVA on 16/12/2019 at 19:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1.1 |  | 1.1 |  | 1.1 | 1.1 | 1.1
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 0.8 | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.7 |  | 0.6 |  | 0.7 | 0.7 | 0.7
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 0.7 | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.7 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 14.5 | 14.5 | 14.5 |  | 14.5 |  | 14.5 | 14.5 |  | 14.5 |  | 14.5 | 14.5 | 14.5
|  |  |  | Raw LAR (MVA) |  | 0.7 | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.7 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MERI
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MERI - Merinda (66/11kV) | [8 empty] | Supply |  | T181 - Bowen North BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/11kV 6.3MVA ONAN;1x66/11kV 8/10MVA ONAN/ONAF(Standby)
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.5%, 2021 S -0.4% W -0.4%2022 S -0.5% W -0.5%2023 S -0.2% W -0.2%2024 S -0.6% W -0.6
|  |  | Latest Peak Compensated Load | [5 empty] | 5.3 MVA on 28/08/2019 at 14:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 8.1 | 8.1 | 8.1 |  | 8.1 |  | 8.1 | 8.3 |  | 8.3 |  | 8.3 | 8.3 | 8.3
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 4.4 | 4.4 | 4.4 |  | 4.4 |  | 4.4 | 5.2 |  | 5.2 |  | 5.1 | 5.1 | 5.1
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.859 | 0.859 | 0.859 |  | 0.859 |  | 0.859 | 0.887 |  | 0.887 |  | 0.887 | 0.887 | 0.887
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 4.3 | 4.3 | 4.3 |  | 4.3 |  | 4.3 | 4.9 |  | 4.9 |  | 4.8 | 4.8 | 4.8
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 147.5 | 147.5 | 147.5 |  | 147.5 |  | 147.5 | 147.5 |  | 147.5 |  | 147.5 | 147.5 | 147.5
|  |  |  | Raw LAR (MVA) |  | 4.3 | 4.3 | 4.3 |  | 4.3 |  | 4.3 | 4.9 |  | 4.9 |  | 4.8 | 4.8 | 4.8
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 11 | 11 | 11 |  | 11 |  | 11 | 11 |  | 11 |  | 11 | 11 | 11
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MERN
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MERN - Meringandan (33/11kV) | [8 empty] | Supply |  | T116 - Torrington BSP
| Description |  |  |  | Region is South West
Transformer size is 2x66/11kV 6.3MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.9%, 2021 S 1.2% W 1.2%, 2022 S 1.0% W 1.0%, 2023 S 1.1% W 1.1%, 2024 S 0.9% W 0.9%
|  |  | Latest Peak Compensated Load | [5 empty] | 11.4 MVA on 04/06/2019 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 16.9 | 16.9 | 16.9 |  | 16.9 |  | 16.9 | 18.5 |  | 18.5 |  | 18.5 | 18.5 | 18.5
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 9.1 | 9.2 | 9.3 |  | 9.4 |  | 9.6 | 12 |  | 12.1 |  | 12.2 | 12.3 | 12.4
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.991 | 0.991 | 0.991 |  | 0.991 |  | 0.991 | 0.998 |  | 0.998 |  | 0.998 | 0.998 | 0.998
|  |  |  | ECC Rating (MVA) |  | 9.2 | 9.2 | 9.2 |  | 9.2 |  | 9.2 | 9.4 |  | 9.4 |  | 9.4 | 9.4 | 9.4
|  |  |  | 50 PoE Load (MVA) |  | 7.9 | 8 | 8.1 |  | 8.2 |  | 8.3 | 10.7 |  | 10.8 |  | 10.9 | 10.9 | 11.1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.4 | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.6
|  |  |  | Hours PA > 95% Peak Load |  | 2.5 | 2.5 | 2.5 |  | 2.5 |  | 2.5 | 2.5 |  | 2.5 |  | 2.5 | 2.5 | 2.5
|  |  |  | Raw LAR (MVA) | [8 empty] | 1.3 |  | 1.4 |  | 1.5 | 1.5 | 1.7
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 1.5 | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.5 | 1.5
|  |  |  | Mobile Plant Avail (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MICO
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MICO - Miles-Condamine (33/22kV) | [8 empty] | Supply |  | COLU - Columboola BSP
| Description |  |  |  | Region is South West
Transformer size is 1x33/22kV 0.75MVA ON;1x33/22kV 0.75MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.1%, 2021 S 0.0% W 0.0%, 2022 S -0.1% W -0.1%2023 S 0.0% W 0.0%, 2024 S -0.1% W -0.1
|  |  | Latest Peak Compensated Load | [5 empty] | 0.7 MVA on 16/12/2019 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 1.5 | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.6 |  | 1.6 |  | 1.6 | 1.6 | 1.6
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 0.8 | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.7 |  | 0.7 |  | 0.7 | 0.7 | 0.7
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.992 | 0.992 | 0.992 |  | 0.992 |  | 0.992 | 0.995 |  | 0.995 |  | 0.995 | 0.995 | 0.995
|  |  |  | ECC Rating (MVA) |  | 0.8 | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.8 | 0.8
|  |  |  | 50 PoE Load (MVA) |  | 0.7 | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 13 | 13 | 13 |  | 13 |  | 13 | 13 |  | 13 |  | 13 | 13 | 13
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0.8 | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.8 | 0.8
|  |  |  | Mobile Plant Avail (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MIDD
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MIDD - Middlemount (66/22kV) | [8 empty] | Supply |  | H015 - Lilyvale BSP
| Description |  |  |  | Region is Capricornia
Transformer size is 2x66/22kV 5MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -1.1%, 2021 S -0.1% W -0.1%2022 S -0.2% W -0.2%2023 S 0.0% W 0.0%, 2024 S -0.3% W -0.3
|  |  | Latest Peak Compensated Load | [5 empty] | 5.3 MVA on 16/12/2019 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 15.3 | 15.3 | 15.3 |  | 15.3 |  | 15.3 | 18.6 |  | 18.6 |  | 18.6 | 18.6 | 18.6
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 5.9 | 5.9 | 5.9 |  | 5.9 |  | 5.9 | 3.3 |  | 3.3 |  | 3.3 | 3.3 | 3.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.99 | 0.99 | 0.99 |  | 0.99 |  | 0.99 | 0.99 |  | 0.99 |  | 0.99 | 0.99 | 0.99
|  |  |  | ECC Rating (MVA) |  | 8.7 | 8.7 | 8.7 |  | 8.7 |  | 8.7 | 9.3 |  | 9.3 |  | 9.3 | 9.3 | 9.3
|  |  |  | 50 PoE Load (MVA) |  | 5.4 | 5.4 | 5.4 |  | 5.4 |  | 5.4 | 3.2 |  | 3.2 |  | 3.2 | 3.2 | 3.2
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 3.5 | 3.5 | 3.5 |  | 3.5 |  | 3.5 | 3.5 |  | 3.5 |  | 3.5 | 3.5 | 3.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MILC
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MILC - Millchester (66/11kV) | [8 empty] | Supply |  | T095 - Millchester BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/11kV 10MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.6%, 2021 S 0.1% W 0.1%, 2022 S -0.0% W -0.0%2023 S 0.1% W 0.1%, 2024 S -0.1% W -0.1
|  |  | Latest Peak Compensated Load | [5 empty] | 6 MVA on 19/02/2020 at 19:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 10.6 | 10.6 | 10.6 |  | 10.6 |  | 10.6 | 12.2 |  | 12.2 |  | 12.2 | 12.2 | 12.2
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 6.4 | 6.4 | 6.4 |  | 6.4 |  | 6.4 | 3.8 |  | 3.8 |  | 3.8 | 3.8 | 3.8
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.977 | 0.977 | 0.977 |  | 0.977 |  | 0.977 | 0.993 |  | 0.993 |  | 0.993 | 0.993 | 0.993
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 5.6 | 5.6 | 5.6 |  | 5.6 |  | 5.6 | 3.6 |  | 3.6 |  | 3.6 | 3.6 | 3.6
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 4.5 | 4.5 | 4.5 |  | 4.5 |  | 4.5 | 4.5 |  | 4.5 |  | 4.5 | 4.5 | 4.5
|  |  |  | Raw LAR (MVA) |  | 5.6 | 5.6 | 5.6 |  | 5.6 |  | 5.6 | 3.6 |  | 3.6 |  | 3.6 | 3.6 | 3.6
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 6.5 | 6.5 | 6.5 |  | 6.5 |  | 6.5 | 6.5 |  | 6.5 |  | 6.5 | 6.5 | 6.5
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MILE
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MILE - Miles (33/11kV) | [8 empty] | Supply |  | COLU - Columboola BSP
| Description |  |  |  | Region is South West
Transformer size is 1x33/11kV 6.3MVA ONAN;1x33/11KV 1.5MVA ONAN(Standby)
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.3%, 2021 S 0.0% W 0.0%, 2022 S -0.2% W -0.2%2023 S 0.1% W 0.1%, 2024 S -0.4% W -0.4
|  |  | Latest Peak Compensated Load | [5 empty] | 3.3 MVA on 30/01/2020 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 8.1 | 8.1 | 8.1 |  | 8.1 |  | 8.1 | 9.4 |  | 9.4 |  | 9.4 | 9.4 | 9.4
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 4 | 4 | 4 |  | 4 |  | 4 | 3 |  | 3 |  | 2.9 | 2.9 | 2.9
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.983 | 0.983 | 0.983 |  | 0.983 |  | 0.983 | 0.987 |  | 0.987 |  | 0.985 | 0.985 | 0.985
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 3.6 | 3.6 | 3.6 |  | 3.6 |  | 3.6 | 2.8 |  | 2.8 |  | 2.7 | 2.7 | 2.7
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 14.5 | 14.5 | 14.5 |  | 14.5 |  | 14.5 | 14.5 |  | 14.5 |  | 14.5 | 14.5 | 14.5
|  |  |  | Raw LAR (MVA) |  | 3.6 | 3.6 | 3.6 |  | 3.6 |  | 3.6 | 2.8 |  | 2.8 |  | 2.7 | 2.7 | 2.7
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 1.5 | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.5 | 1.5
|  |  |  | Mobile Plant Avail (MVA) |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MILL
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MILL - Millaroo (66/11kV) | [8 empty] | Supply |  | T193 - Clare South BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/11kV 5MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.1%, 2021 S -0.1% W -0.1%2022 S -0.2% W -0.2%2023 S 0.1% W 0.1%, 2024 S -0.2% W -0.2
|  |  | Latest Peak Compensated Load | [5 empty] | 2.5 MVA on 20/12/2019 at 19:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 5.6 | 5.6 | 5.6 |  | 5.6 |  | 5.6 | 6.5 |  | 6.5 |  | 6.5 | 6.5 | 6.5
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 2.6 | 2.6 | 2.6 |  | 2.6 |  | 2.6 | 1.8 |  | 1.8 |  | 1.8 | 1.8 | 1.8
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.871 | 0.871 | 0.871 |  | 0.871 |  | 0.871 | 0.874 |  | 0.874 |  | 0.874 | 0.874 | 0.874
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 2.6 | 2.6 | 2.6 |  | 2.6 |  | 2.6 | 1.7 |  | 1.7 |  | 1.7 | 1.7 | 1.7
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 36 | 36 | 36 |  | 36 |  | 36 | 36 |  | 36 |  | 36 | 36 | 36
|  |  |  | Raw LAR (MVA) |  | 2.6 | 2.6 | 2.6 |  | 2.6 |  | 2.6 | 1.7 |  | 1.7 |  | 1.7 | 1.7 | 1.7
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MILM
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MILM - Millmerran (33/11kV) | [8 empty] | Supply |  | YARA - Yarranlea BSP
| Description |  |  |  | Region is South West
Transformer size is 1x33/11kV 6.3MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.4%, 2021 S 0.1% W 0.1%, 2022 S 0.0% W 0.0%, 2023 S 0.1% W 0.1%, 2024 S 0.0% W 0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 3.9 MVA on 16/12/2019 at 17:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 7.6 | 7.6 | 7.6 |  | 7.6 |  | 7.6 | 8.5 |  | 8.5 |  | 8.5 | 8.5 | 8.5
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 4.2 | 4.2 | 4.2 |  | 4.2 |  | 4.2 | 3.1 |  | 3.1 |  | 3.1 | 3.1 | 3.1
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 1 | 1 | 1 |  | 1 |  | 1 | 0.979 |  | 0.979 |  | 0.979 | 0.979 | 0.979
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 3.8 | 3.8 | 3.8 |  | 3.8 |  | 3.8 | 3 |  | 3 |  | 2.9 | 2.9 | 2.9
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 |  | 0.2 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 5391 | 5391 | 5391 |  | 5391 |  | 5391 | 5391 |  | 5391 |  | 5391 | 5391 | 5391
|  |  |  | Raw LAR (MVA) |  | 3.8 | 3.8 | 3.8 |  | 3.8 |  | 3.8 | 3 |  | 3 |  | 2.9 | 2.9 | 2.9
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MING
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MING - Mingela (66/11kV) | [8 empty] | Supply |  | TMES - Townsville Mesh
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1xMING TX NO 1-66/11KV TRANSF 1
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.2%, 2021 S 0.0% W 0.0%, 2022 S 0.0% W 0.0%, 2023 S 0.0% W 0.0%, 2024 S 0.0% W 0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 0.3 MVA on 01/01/2020 at 17:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.85 | 0.85 | 0.85 |  | 0.85 |  | 0.85 | 0.85 |  | 0.85 |  | 0.85 | 0.85 | 0.85
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 2709 | 2709 | 2709 |  | 2709 |  | 2709 | 2709 |  | 2709 |  | 2709 | 2709 | 2709
|  |  |  | Raw LAR (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MIRA
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MIRA - Mirani (66/11kV) | [8 empty] | Supply |  | PIVA - Pioneer Valley BSP
| Description |  |  |  | Region is Mackay
Transformer size is 1x66/11kV 5MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.6%, 2021 S 0.3% W 0.3%, 2022 S 0.2% W 0.2%, 2023 S 0.3% W 0.3%, 2024 S 0.1% W 0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 4.3 MVA on 14/12/2019 at 20:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 6.1 | 6.1 | 6.1 |  | 6.1 |  | 6.1 | 7 |  | 7 |  | 7 | 7 | 7
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 4.4 | 4.5 | 4.5 |  | 4.5 |  | 4.5 | 2.5 |  | 2.5 |  | 2.5 | 2.5 | 2.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.951 | 0.951 | 0.951 |  | 0.951 |  | 0.951 | 0.953 |  | 0.953 |  | 0.953 | 0.953 | 0.953
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 4.3 | 4.4 | 4.4 |  | 4.4 |  | 4.4 | 2.4 |  | 2.4 |  | 2.4 | 2.4 | 2.4
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 9 | 9 | 9 |  | 9 |  | 9 | 9 |  | 9 |  | 9 | 9 | 9
|  |  |  | Raw LAR (MVA) |  | 4.3 | 4.4 | 4.4 |  | 4.4 |  | 4.4 | 2.4 |  | 2.4 |  | 2.4 | 2.4 | 2.4
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 3.2 | 3.2 | 3.2 |  | 3.2 |  | 3.2 | 3.2 |  | 3.2 |  | 3.2 | 3.2 | 3.2
|  |  |  | Mobile Plant Avail (MVA) |  | 1.6 | 1.6 | 1.6 |  | 1.6 |  | 1.6 | 1.6 |  | 1.6 |  | 1.6 | 1.6 | 1.6
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MITC
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MITC - Mitchell (33/11kV) | [8 empty] | Supply |  | T083 - Roma 33kV BSP
| Description |  |  |  | Region is South West
Transformer size is 3x33/11kV 0.75MVA ON
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -1.7%, 2021 S -0.4% W -0.4%2022 S -0.7% W -0.7%2023 S -0.3% W -0.3%2024 S -0.5% W -0.5
|  |  | Latest Peak Compensated Load | [5 empty] | 2 MVA on 11/12/2019 at 15:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 2.3 | 2.3 | 2.3 |  | 2.3 |  | 2.3 | 2.3 |  | 2.3 |  | 2.3 | 2.3 | 2.3
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 2.3 | 2.3 | 2.3 |  | 2.3 |  | 2.3 | 2 |  | 2 |  | 2 | 2 | 2
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.918 | 0.918 | 0.918 |  | 0.918 |  | 0.918 | 0.953 |  | 0.953 |  | 0.953 | 0.953 | 0.953
|  |  |  | ECC Rating (MVA) |  | 1.5 | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.5 | 1.5
|  |  |  | 50 PoE Load (MVA) |  | 2.1 | 2.1 | 2.1 |  | 2.1 |  | 2.1 | 1.9 |  | 1.9 |  | 1.9 | 1.8 | 1.8
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 11.5 | 11.5 | 11.5 |  | 11.5 |  | 11.5 | 11.5 |  | 11.5 |  | 11.5 | 11.5 | 11.5
|  |  |  | Raw LAR (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.4 |  | 0.4 |  | 0.4 | 0.3 | 0.3
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MIVA
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MIVA - Miriam Vale (66/22kV) | [8 empty] | Supply |  | T019 - Gladstone South BSP
| Description |  |  |  | Region is South West
Transformer size is 1x66/22kV 6.3MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.2%, 2021 S 0.2% W 0.2%, 2022 S 0.0% W 0.0%, 2023 S 0.1% W 0.1%, 2024 S -0.1% W -0.1
|  |  | Latest Peak Compensated Load | [5 empty] | 1.9 MVA on 16/12/2019 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 9.1 | 9.1 | 9.1 |  | 9.1 |  | 9.1 | 9.4 |  | 9.4 |  | 9.4 | 9.4 | 9.4
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 2.1 | 2.1 | 2.1 |  | 2.1 |  | 2.1 | 1.6 |  | 1.6 |  | 1.6 | 1.6 | 1.6
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.997 | 0.997 | 0.997 |  | 0.997 |  | 0.997 | 0.998 |  | 0.998 |  | 0.998 | 0.998 | 0.998
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 1.6 |  | 1.6 |  | 1.6 | 1.6 | 1.6
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 235.5 | 235.5 | 235.5 |  | 235.5 |  | 235.5 | 235.5 |  | 235.5 |  | 235.5 | 235.5 | 235.5
|  |  |  | Raw LAR (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 1.6 |  | 1.6 |  | 1.6 | 1.6 | 1.6
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 1.6 | 1.6 | 1.6 |  | 1.6 |  | 1.6 | 1.6 |  | 1.6 |  | 1.6 | 1.6 | 1.6
|  |  |  | Manual Trans Avail (MVA) |  | 3.1 | 3.1 | 3.1 |  | 3.1 |  | 3.1 | 3.1 |  | 3.1 |  | 3.1 | 3.1 | 3.1
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MLEP
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MLEP - Mount Leyshon Pump (66/11kV) | [8 empty] | Supply |  | T095 - Millchester BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/11kV 0MVA
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.0%, 2021 S 0.0% W 0.0%, 2022 S 0.0% W 0.0%, 2023 S 0.0% W 0.0%, 2024 S 0.0% W 0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 0.1 MVA on 01/01/2020 at 17:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.82 | 0.82 | 0.82 |  | 0.82 |  | 0.82 | 0.85 |  | 0.85 |  | 0.85 | 0.85 | 0.85
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 635 | 635 | 635 |  | 635 |  | 635 | 635 |  | 635 |  | 635 | 635 | 635
|  |  |  | Raw LAR (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MOBA
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MOBA - Mt Bassett (33/11kV) | [8 empty] | Supply |  | MACK - Mackay BSP
| Description |  |  |  | Region is Mackay
Transformer size is 1x33/11kV 10MVA ONAN;2x33/11kV 12.5MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 1.0%, 2021 S 0.4% W 0.4%, 2022 S 0.3% W 0.3%, 2023 S 0.5% W 0.5%, 2024 S 0.2% W 0.2%
|  |  | Latest Peak Compensated Load | [5 empty] | 11.8 MVA on 10/02/2020 at 14:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 39 | 39 | 39 |  | 39 |  | 39 | 42 |  | 42 |  | 42 | 42 | 42
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 12.7 | 12.7 | 12.8 |  | 12.9 |  | 12.9 | 8.5 |  | 8.5 |  | 8.5 | 8.5 | 8.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.962 | 0.962 | 0.962 |  | 0.962 |  | 0.962 | 0.973 |  | 0.973 |  | 0.973 | 0.973 | 0.973
|  |  |  | ECC Rating (MVA) |  | 27.9 | 27.9 | 27.9 |  | 27.9 |  | 27.9 | 27.9 |  | 27.9 |  | 27.9 | 27.9 | 27.9
|  |  |  | 50 PoE Load (MVA) |  | 11.7 | 11.7 | 11.8 |  | 11.8 |  | 11.9 | 8.4 |  | 8.4 |  | 8.4 | 8.4 | 8.4
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  |  | Hours PA > 95% Peak Load |  | 6 | 6 | 6 |  | 6 |  | 6 | 6 |  | 6 |  | 6 | 6 | 6
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MODA
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MODA - Monduran Dam (66/11kV) | [8 empty] | Supply |  | BUND - Bundaberg BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 1xMODA TX NO 2-66/11/3.3KV TRANSF 2(Standby);1xMODA TX NO 1-66/11/3.3KV TRANSF 1
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.3%, 2021 S 0.7% W 0.7%, 2022 S 0.3% W 0.3%, 2023 S 0.9% W 0.9%, 2024 S -0.0% W -0.0
|  |  | Latest Peak Compensated Load | [5 empty] | 0.2 MVA on 04/06/2019 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 1.5 | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.5 | 1.5
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.998 | 0.998 | 0.998 |  | 0.998 |  | 0.998 | 0.991 |  | 0.991 |  | 0.991 | 0.991 | 0.991
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 4 | 4 | 4 |  | 4 |  | 4 | 4 |  | 4 |  | 4 | 4 | 4
|  |  |  | Raw LAR (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 1.5 | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.5 | 1.5
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MOFO
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MOFO - Mount Fox (66/33kV) | [8 empty] | Supply |  | T047 - Ingham BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/11kV 0.63MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.4%, 2021 S -0.4% W -0.4%2022 S -0.4% W -0.4%2023 S -0.3% W -0.3%2024 S -0.4% W -0.4
|  |  | Latest Peak Compensated Load | [5 empty] | 0.1 MVA on 06/12/2019 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 0.7 | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.7 | 0.7
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.886 | 0.886 | 0.886 |  | 0.886 |  | 0.886 | 0.77 |  | 0.77 |  | 0.77 | 0.77 | 0.77
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Raw LAR (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MOGA
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MOGA - Mt Garnet (66/22kV) | [8 empty] | Supply |  | TURK - Turkinje 66kV BSP
| Description |  |  |  | Region is Far North
Transformer size is 2x66/22kV 4MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -2.8%, 2021 S 0.0% W 0.0%, 2022 S -0.3% W -0.3%2023 S 0.4% W 0.4%, 2024 S -0.5% W -0.5
|  |  | Latest Peak Compensated Load | [5 empty] | 1.8 MVA on 04/12/2019 at 15:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 8.5 | 8.5 | 8.5 |  | 8.5 |  | 8.5 | 9.3 |  | 9.3 |  | 9.3 | 9.3 | 9.3
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 1.9 | 1.9 | 1.9 |  | 1.9 |  | 1.9 | 1.7 |  | 1.7 |  | 1.7 | 1.7 | 1.7
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.977 | 0.977 | 0.977 |  | 0.977 |  | 0.977 | 0.989 |  | 0.989 |  | 0.989 | 0.989 | 0.989
|  |  |  | ECC Rating (MVA) |  | 4.2 | 4.2 | 4.2 |  | 4.2 |  | 4.2 | 4.7 |  | 4.7 |  | 4.7 | 4.7 | 4.7
|  |  |  | 50 PoE Load (MVA) |  | 1.8 | 1.8 | 1.8 |  | 1.8 |  | 1.8 | 1.6 |  | 1.6 |  | 1.5 | 1.5 | 1.5
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 6.5 | 6.5 | 6.5 |  | 6.5 |  | 6.5 | 6.5 |  | 6.5 |  | 6.5 | 6.5 | 6.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MOMO
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MOMO - Mt Molloy (66/22kV) | [8 empty] | Supply |  | TURK - Turkinje 66kV BSP
| Description |  |  |  | Region is Far North
Transformer size is 1x66/22kV 10/12.5MVA ONAN/ONAF;1x66/22kV 1.5MVA ONAN(Standby)
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.6%, 2021 S 0.3% W 0.3%, 2022 S 0.2% W 0.2%, 2023 S 0.3% W 0.3%, 2024 S 0.0% W 0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 1.1 MVA on 15/02/2020 at 16:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 16.4 | 16.4 | 16.4 |  | 16.4 |  | 16.4 | 18 |  | 18 |  | 18 | 18 | 18
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 1.1 | 1.1 | 1.1 |  | 1.1 |  | 1.1 | 1.1 |  | 1.1 |  | 1.1 | 1.1 | 1.1
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.984 | 0.984 | 0.984 |  | 0.984 |  | 0.984 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 4 | 4 | 4 |  | 4 |  | 4 | 4 |  | 4 |  | 4 | 4 | 4
|  |  |  | Raw LAR (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 1.5 | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.5 | 1.5
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MOMR
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MOMR - Mt Morgan (66/11kV) | [8 empty] | Supply |  | RMES - Rockhampton Mesh
| Description |  |  |  | Region is Capricornia
Transformer size is 2x66/11kV 5/6.25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.2%, 2021 S 0.0% W 0.0%, 2022 S -0.1% W -0.1%2023 S 0.0% W 0.0%, 2024 S -0.2% W -0.2
|  |  | Latest Peak Compensated Load | [5 empty] | 3.3 MVA on 16/12/2019 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 15.8 | 15.8 | 15.8 |  | 15.8 |  | 15.8 | 18 |  | 18 |  | 18 | 18 | 18
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 3.4 | 3.4 | 3.4 |  | 3.4 |  | 3.4 | 2.8 |  | 2.8 |  | 2.8 | 2.8 | 2.8
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.971 | 0.971 | 0.971 |  | 0.971 |  | 0.971 | 0.989 |  | 0.989 |  | 0.989 | 0.989 | 0.989
|  |  |  | ECC Rating (MVA) |  | 8.7 | 8.7 | 8.7 |  | 8.7 |  | 8.7 | 9.3 |  | 9.3 |  | 9.3 | 9.3 | 9.3
|  |  |  | 50 PoE Load (MVA) |  | 3.2 | 3.2 | 3.2 |  | 3.2 |  | 3.2 | 2.7 |  | 2.7 |  | 2.7 | 2.6 | 2.7
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 8.5 | 8.5 | 8.5 |  | 8.5 |  | 8.5 | 8.5 |  | 8.5 |  | 8.5 | 8.5 | 8.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MOMW
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MOMW - Mt Mowbullan (33/11kV) | [8 empty] | Supply |  | T002 - Dalby East BSP
| Description |  |  |  | Region is South West
Transformer size is 1x33/11kV 1MVA ON
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.1%, 2021 S 0.5% W 0.5%, 2022 S 0.3% W 0.3%, 2023 S 0.6% W 0.6%, 2024 S 0.2% W 0.2%
|  |  | Latest Peak Compensated Load | [5 empty] | 0.7 MVA on 01/06/2019 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.7 |  | 0.7 |  | 0.7 | 0.7 | 0.7
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.995 | 0.995 | 0.995 |  | 0.995 |  | 0.995 | 0.994 |  | 0.994 |  | 0.994 | 0.994 | 0.994
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.7 |  | 0.7 |  | 0.7 | 0.7 | 0.7
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 3.5 | 3.5 | 3.5 |  | 3.5 |  | 3.5 | 3.5 |  | 3.5 |  | 3.5 | 3.5 | 3.5
|  |  |  | Raw LAR (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.7 |  | 0.7 |  | 0.7 | 0.7 | 0.7
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MONT
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MONT - Monto (66/11kV) | [8 empty] | Supply |  | T026 - Biloela BSP
| Description |  |  |  | Region is Capricornia
Transformer size is 2x66/11kV 6.25MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.0%, 2021 S 0.0% W 0.0%, 2022 S -0.1% W -0.1%2023 S 0.0% W 0.0%, 2024 S -0.2% W -0.2
|  |  | Latest Peak Compensated Load | [5 empty] | 5.2 MVA on 15/12/2019 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 14 | 14 | 14 |  | 14 |  | 14 | 16.7 |  | 16.7 |  | 16.7 | 16.7 | 16.7
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 5.6 | 5.6 | 5.6 |  | 5.6 |  | 5.6 | 4.4 |  | 4.4 |  | 4.4 | 4.4 | 4.4
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.997 | 0.997 | 0.997 |  | 0.997 |  | 0.997 | 0.996 |  | 0.995 |  | 0.995 | 0.995 | 0.995
|  |  |  | ECC Rating (MVA) |  | 8 | 8 | 8 |  | 8 |  | 8 | 9.3 |  | 9.3 |  | 9.3 | 9.3 | 9.3
|  |  |  | 50 PoE Load (MVA) |  | 5 | 5 | 5 |  | 5 |  | 5 | 4.3 |  | 4.2 |  | 4.2 | 4.2 | 4.2
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 4.5 | 4.5 | 4.5 |  | 4.5 |  | 4.5 | 4.5 |  | 4.5 |  | 4.5 | 4.5 | 4.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MOOR
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MOOR - Moorvale (66/11kV) | [8 empty] | Supply |  | T198 - Broadlea BSP
| Description |  |  |  | Region is Mackay
Transformer size is 1x66/11kV 7.5/10MVA ON/OB
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.8%, 2021 S 0.0% W 0.0%, 2022 S -0.1% W -0.1%2023 S 0.1% W 0.1%, 2024 S -0.1% W -0.1
|  |  | Latest Peak Compensated Load | [5 empty] | 5.8 MVA on 18/11/2019 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 10.5 | 10.5 | 10.5 |  | 10.5 |  | 10.5 | 11 |  | 11 |  | 11 | 11 | 11
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 6.1 | 6.1 | 6.1 |  | 6.1 |  | 6.1 | 5.3 |  | 5.2 |  | 5.2 | 5.2 | 5.2
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.978 | 0.978 | 0.978 |  | 0.978 |  | 0.978 | 0.975 |  | 0.975 |  | 0.975 | 0.975 | 0.975
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 5.9 | 5.9 | 5.9 |  | 6 |  | 6 | 5.1 |  | 5.1 |  | 5.1 | 5.1 | 5.1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Hours PA > 95% Peak Load |  | 10.5 | 10.5 | 10.5 |  | 10.5 |  | 10.5 | 10.5 |  | 10.5 |  | 10.5 | 10.5 | 10.5
|  |  |  | Raw LAR (MVA) |  | 5.9 | 5.9 | 5.9 |  | 6 |  | 6 | 5.1 |  | 5.1 |  | 5.1 | 5.1 | 5.1
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 11.5 | 11.5 | 11.5 |  | 11.5 |  | 11.5 | 11.5 |  | 11.5 |  | 11.5 | 11.5 | 11.5
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 3.1 | 3.1 | 3.1 |  | 3.1 |  | 3.1 | 3.1 |  | 3.1 |  | 3.1 | 3.1 | 3.1
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MOPA
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MOPA - Mona Park (66/11kV) | [8 empty] | Supply |  | T193 - Clare South BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 2x66/11kV 4MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.0%, 2021 S -0.4% W -0.4%2022 S -0.7% W -0.7%2023 S -0.2% W -0.2%2024 S -0.4% W -0.4
|  |  | Latest Peak Compensated Load | [5 empty] | 5.8 MVA on 12/12/2019 at 19:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 7.6 | 7.6 | 7.6 |  | 7.6 |  | 7.6 | 8 |  | 8 |  | 8 | 8 | 8
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 6.2 | 6.1 | 6.1 |  | 6.1 |  | 6.1 | 3.8 |  | 3.8 |  | 3.8 | 3.7 | 3.8
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.855 | 0.855 | 0.855 |  | 0.855 |  | 0.855 | 0.856 |  | 0.856 |  | 0.856 | 0.856 | 0.856
|  |  |  | ECC Rating (MVA) |  | 4 | 4 | 4 |  | 4 |  | 4 | 4 |  | 4 |  | 4 | 4 | 4
|  |  |  | 50 PoE Load (MVA) |  | 6 | 6 | 6 |  | 6 |  | 6 | 3.8 |  | 3.7 |  | 3.7 | 3.7 | 3.7
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 29 | 29 | 29 |  | 29 |  | 29 | 29 |  | 29 |  | 29 | 29 | 29
|  |  |  | Raw LAR (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 2.3 | 2.3 | 2.3 |  | 2.3 |  | 2.3 | 2.3 |  | 2.3 |  | 2.3 | 2.3 | 2.3
|  |  |  | Mobile Plant Avail (MVA) |  | 0.8 | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.8 | 0.8
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MORA
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MORA - Moranbah Town (132/11kV) | [8 empty] | Supply |  | QMRL - Moranbah 11kV TCP
| Description |  |  |  | Region is Mackay
Transformer size is 1x20 MVA;1x20MVA
Capacity of commissioned Embedded Generation (with Connection Agreements) is 19.3 MVA
Growth Rates |  |  |  |  | 2020 W 0.4%, 2021 S 0.8% W 0.8%, 2022 S 0.7% W 0.7%, 2023 S 0.9% W 0.9%, 2024 S 0.6% W 0.6%
|  |  | Latest Peak Compensated Load | [5 empty] | 13 MVA on 18/02/2020 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 40 | 40 | 40 |  | 40 |  | 40 | 40 |  | 40 |  | 40 | 40 | 40
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 23.7 | 23.9 | 24.1 |  | 24.3 |  | 24.5 | 7.9 |  | 14.3 |  | 14.3 | 14.4 | 14.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 0.999 |  | 0.999 | 0.999 | 0.999
|  |  |  | ECC Rating (MVA) |  | 20 | 20 | 20 |  | 20 |  | 20 | 20 |  | 20 |  | 20 | 20 | 20
|  |  |  | 50 PoE Load (MVA) |  | 22 | 22.2 | 22.4 |  | 22.6 |  | 22.8 | 7.6 |  | 14 |  | 14 | 14.1 | 14.2
|  |  |  | 50 PoE Load > 95% (MVA) |  | 1.1 | 1.1 | 1.1 |  | 1.1 |  | 1.1 | 0.4 |  | 0.7 |  | 0.7 | 0.7 | 0.7
|  |  |  | Hours PA > 95% Peak Load |  | 12 | 12 | 12 |  | 12 |  | 12 | 12 |  | 12 |  | 12 | 12 | 12
|  |  |  | Raw LAR (MVA) |  | 2 | 2.2 | 2.4 |  | 2.6 |  | 2.8
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 4 | 4 | 4 |  | 4 |  | 4 | 4 |  | 4 |  | 4 | 4 | 4
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MORO
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MORO - Mount Rooper (66/11kV) | [8 empty] | Supply |  | PROS - Proserpine BSP
| Description |  |  |  | Region is Mackay
Transformer size is 1x66/11kV 5MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.6%, 2021 S 0.0% W 0.0%, 2022 S -0.2% W -0.2%2023 S -0.1% W -0.1%2024 S -0.1% W -0.1
|  |  | Latest Peak Compensated Load | [5 empty] | 1.1 MVA on 14/02/2020 at 13:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 5.8 | 5.8 | 5.8 |  | 5.8 |  | 5.8 | 6.4 |  | 6.4 |  | 6.4 | 6.4 | 6.4
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 1.1 | 1.1 | 1.1 |  | 1.1 |  | 1.1 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.98 | 0.98 | 0.98 |  | 0.98 |  | 0.98 | 0.979 |  | 0.979 |  | 0.979 | 0.979 | 0.979
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 1.1 | 1.1 | 1.1 |  | 1.1 |  | 1.1 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 85 | 85 | 85 |  | 85 |  | 85 | 85 |  | 85 |  | 85 | 85 | 85
|  |  |  | Raw LAR (MVA) |  | 1.1 | 1.1 | 1.1 |  | 1.1 |  | 1.1 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 1.1 | 1.1 | 1.1 |  | 1.1 |  | 1.1 | 1.1 |  | 1.1 |  | 1.1 | 1.1 | 1.1
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MOSI
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MOSI - Mt Sibley (33/11kV) | [8 empty] | Supply |  | T043 - South Toowoomba BSP
| Description |  |  |  | Region is South West
Transformer size is 1x33/11kV 3MVA ON;1x33/11KV 5MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.5%, 2021 S 0.3% W 0.3%, 2022 S 0.2% W 0.2%, 2023 S 0.3% W 0.3%, 2024 S 0.1% W 0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 4.4 MVA on 16/12/2019 at 17:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 6.3 | 6.3 | 6.3 |  | 6.3 |  | 6.3 | 6.3 |  | 6.3 |  | 6.3 | 6.3 | 6.3
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 5.2 | 5.3 | 5.3 |  | 5.3 |  | 5.3 | 4.4 |  | 4.4 |  | 4.3 | 4.3 | 4.4
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.899 | 0.899 | 0.899 |  | 0.899 |  | 0.899 | 0.908 |  | 0.908 |  | 0.908 | 0.908 | 0.908
|  |  |  | ECC Rating (MVA) |  | 3.3 | 3.3 | 3.3 |  | 3.3 |  | 3.3 | 3.5 |  | 3.5 |  | 3.5 | 3.5 | 3.5
|  |  |  | 50 PoE Load (MVA) |  | 4.7 | 4.7 | 4.7 |  | 4.8 |  | 4.8 | 4.1 |  | 4.1 |  | 4.1 | 4.1 | 4.1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 510 | 510 | 510 |  | 510 |  | 510 | 510 |  | 510 |  | 510 | 510 | 510
|  |  |  | Raw LAR (MVA) |  | 1.4 | 1.4 | 1.4 |  | 1.5 |  | 1.5 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0.8 | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.8 | 0.8
|  |  |  | Mobile Plant Avail (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MOSS
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MOSS - Mossman (66/22kV) | [8 empty] | Supply |  | TURK - Turkinje 66kV BSP
| Description |  |  |  | Region is Far North
Transformer size is 2x66/22kV 10MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 11.3 MVA
Growth Rates |  |  |  |  | 2020 W 0.3%, 2021 S 0.3% W 0.3%, 2022 S 0.1% W 0.1%, 2023 S 0.3% W 0.3%, 2024 S 0.0% W 0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 7.9 MVA on 13/02/2020 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 18.5 | 18.5 | 18.5 |  | 18.5 |  | 18.5 | 20.6 |  | 20.6 |  | 20.6 | 20.6 | 20.6
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 8.4 | 8.4 | 8.5 |  | 8.5 |  | 8.5 | 6.5 |  | 6.5 |  | 6.4 | 6.4 | 6.4
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.988 | 0.988 | 0.988 |  | 0.988 |  | 0.988 | 0.983 |  | 0.983 |  | 0.983 | 0.983 | 0.983
|  |  |  | ECC Rating (MVA) |  | 9.3 | 9.3 | 9.3 |  | 9.3 |  | 9.3 | 10.3 |  | 10.3 |  | 10.3 | 10.3 | 10.3
|  |  |  | 50 PoE Load (MVA) |  | 7.5 | 7.5 | 7.5 |  | 7.5 |  | 7.6 | 6.2 |  | 6.2 |  | 6.2 | 6.2 | 6.2
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.4 | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Hours PA > 95% Peak Load |  | 10.5 | 10.5 | 10.5 |  | 10.5 |  | 10.5 | 10.5 |  | 10.5 |  | 10.5 | 10.5 | 10.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MOUR
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MOUR - Moura (66/22kV) | [8 empty] | Supply |  | T027 - Moura BSP
| Description |  |  |  | Region is Capricornia
Transformer size is 2x7.5/10 MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.5%, 2021 S -0.3% W -0.3%2022 S -0.4% W -0.4%2023 S -0.2% W -0.2%2024 S -0.5% W -0.5
|  |  | Latest Peak Compensated Load | [5 empty] | 7.9 MVA on 17/02/2020 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 20 | 20 | 20 |  | 20 |  | 20 | 20 |  | 20 |  | 20 | 20 | 20
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 8.9 | 8.9 | 8.9 |  | 8.9 |  | 8.8 | 6.8 |  | 6.8 |  | 6.7 | 6.6 | 6.6
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.983 | 0.983 | 0.983 |  | 0.983 |  | 0.983 | 0.992 |  | 0.992 |  | 0.993 | 0.993 | 0.993
|  |  |  | ECC Rating (MVA) |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10
|  |  |  | 50 PoE Load (MVA) |  | 8.1 | 8.1 | 8.1 |  | 8.1 |  | 8.1 | 6.2 |  | 6.1 |  | 6.1 | 6 | 6
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.4 | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Hours PA > 95% Peak Load |  | 7 | 7 | 7 |  | 7 |  | 7 | 7 |  | 7 |  | 7 | 7 | 7
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MURG
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MURG - Murgon (66/11kV) | [8 empty] | Supply |  | KILK - Kilkivan BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 2x66/11kV 8.5/12.5MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.1%, 2021 S 0.5% W 0.5%, 2022 S 0.4% W 0.4%, 2023 S 0.6% W 0.6%, 2024 S 0.3% W 0.3%
|  |  | Latest Peak Compensated Load | [5 empty] | 12.2 MVA on 16/12/2019 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 29.6 | 29.6 | 29.6 |  | 29.6 |  | 29.6 | 35.4 |  | 35.4 |  | 35.4 | 35.4 | 35.4
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 14.1 | 14.7 | 14.8 |  | 14.9 |  | 15 | 12.3 |  | 12.8 |  | 13.2 | 13.2 | 13.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.942 | 0.942 | 0.942 |  | 0.942 |  | 0.942 | 0.965 |  | 0.965 |  | 0.965 | 0.965 | 0.965
|  |  |  | ECC Rating (MVA) |  | 17 | 17 | 17 |  | 17 |  | 17 | 18.7 |  | 18.7 |  | 18.7 | 18.7 | 18.7
|  |  |  | 50 PoE Load (MVA) |  | 12.8 | 13.4 | 13.4 |  | 13.5 |  | 13.6 | 11.7 |  | 12.1 |  | 12.5 | 12.5 | 12.6
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.6 | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  |  | Hours PA > 95% Peak Load |  | 6 | 6 | 6 |  | 6 |  | 6 | 6 |  | 6 |  | 6 | 6 | 6
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MUTA
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MUTA - Mutarnee (66/11kV) | [8 empty] | Supply |  | T047 - Ingham BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/11kV 1MVA ON
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.5%, 2021 S 0.2% W 0.2%, 2022 S 0.1% W 0.1%, 2023 S 0.3% W 0.3%, 2024 S 0.1% W 0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 0.4 MVA on 07/12/2019 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 1.1 | 1.1 | 1.1 |  | 1.1 |  | 1.1 | 1.1 |  | 1.1 |  | 1.1 | 1.1 | 1.1
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 0.4 | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.965 | 0.965 | 0.965 |  | 0.965 |  | 0.965 | 0.966 |  | 0.966 |  | 0.966 | 0.966 | 0.966
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 0.4 | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 6 | 6 | 6 |  | 6 |  | 6 | 6 |  | 6 |  | 6 | 6 | 6
|  |  |  | Raw LAR (MVA) |  | 0.4 | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## MUTO
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | MUTO - Mundubbera Town (66/11kV) | [8 empty] | Supply |  | ISIS - Isis BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 1x66/11kV 16/20MVA ONAN/ONAF;1xMUTO 66/11kV TRANSF 2 TX02T01
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.1%, 2021 S -0.2% W -0.2%2022 S -0.4% W -0.4%2023 S -0.1% W -0.1%2024 S -0.4% W -0.4
|  |  | Latest Peak Compensated Load | [5 empty] | 7.1 MVA on 11/12/2019 at 17:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 49.4 | 49.4 | 49.4 |  | 49.4 |  | 49.4 | 54.6 |  | 54.6 |  | 54.6 | 54.6 | 54.6
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 7.9 | 7.9 | 7.9 |  | 7.9 |  | 7.9 | 5 |  | 5 |  | 4.9 | 4.9 | 4.9
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.998 | 0.998 | 0.998 |  | 0.998 |  | 0.998 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | ECC Rating (MVA) |  | 28.4 | 28.4 | 28.4 |  | 28.4 |  | 28.4 | 29.9 |  | 29.9 |  | 29.9 | 29.9 | 29.9
|  |  |  | 50 PoE Load (MVA) |  | 7 | 7 | 7 |  | 7 |  | 7 | 5.3 |  | 5.3 |  | 5.2 | 5.2 | 5.2
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.4 | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Hours PA > 95% Peak Load |  | 6 | 6 | 6 |  | 6 |  | 6 | 6 |  | 6 |  | 6 | 6 | 6
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## NANA
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | NANA - Nanango (66/11kV) | [8 empty] | Supply |  | H018 - Tarong BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 2x66/11kV 5/6.25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.5%, 2021 S 0.8% W 0.8%, 2022 S 0.7% W 0.7%, 2023 S 0.8% W 0.8%, 2024 S 0.6% W 0.6%
|  |  | Latest Peak Compensated Load | [5 empty] | 7.3 MVA on 16/12/2019 at 17:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 13.7 | 13.7 | 13.7 |  | 13.7 |  | 13.7 | 15.6 |  | 15.6 |  | 15.6 | 15.6 | 15.6
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 7.9 | 8 | 8 |  | 8.1 |  | 8.2 | 6.5 |  | 6.5 |  | 6.5 | 6.6 | 6.6
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.971 | 0.971 | 0.971 |  | 0.971 |  | 0.971 | 0.985 |  | 0.985 |  | 0.985 | 0.985 | 0.985
|  |  |  | ECC Rating (MVA) |  | 6.8 | 6.8 | 6.8 |  | 6.8 |  | 6.8 | 7.8 |  | 7.8 |  | 7.8 | 7.8 | 7.8
|  |  |  | 50 PoE Load (MVA) |  | 7.2 | 7.2 | 7.3 |  | 7.4 |  | 7.4 | 6.2 |  | 6.2 |  | 6.2 | 6.2 | 6.3
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.4 | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Hours PA > 95% Peak Load |  | 8.5 | 8.5 | 8.5 |  | 8.5 |  | 8.5 | 8.5 |  | 8.5 |  | 8.5 | 8.5 | 8.5
|  |  |  | Raw LAR (MVA) |  | 0.4 | 0.4 | 0.5 |  | 0.6 |  | 0.6
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0.8 | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.8 | 0.8
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## NAND
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | NAND - Nandi (33/11kV) | [8 empty] | Supply |  | T002 - Dalby East BSP
| Description |  |  |  | Region is South West
Transformer size is 1x33/11 3.15MVA ON;1x33/11kV 1MVA ON
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.0%, 2021 S 0.0% W 0.0%, 2022 S -0.0% W -0.0%2023 S 0.2% W 0.2%, 2024 S -0.1% W -0.1
|  |  | Latest Peak Compensated Load | [5 empty] | 1.1 MVA on 16/12/2019 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 | 2 | 2
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 1.2 | 1.2 | 1.2 |  | 1.2 |  | 1.2 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.925 | 0.925 | 0.925 |  | 0.925 |  | 0.925 | 0.958 |  | 0.958 |  | 0.958 | 0.958 | 0.958
|  |  |  | ECC Rating (MVA) |  | 1.1 | 1.1 | 1.1 |  | 1.1 |  | 1.1 | 1.1 |  | 1.1 |  | 1.1 | 1.1 | 1.1
|  |  |  | 50 PoE Load (MVA) |  | 1.2 | 1.2 | 1.2 |  | 1.2 |  | 1.2 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 4.5 | 4.5 | 4.5 |  | 4.5 |  | 4.5 | 4.5 |  | 4.5 |  | 4.5 | 4.5 | 4.5
|  |  |  | Raw LAR (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## NEBO
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | NEBO - Nebo (132/11kV) | [8 empty] | Supply |  | QNEB - Nebo TCP
| Description |  |  |  | Region is Mackay
Transformer size is 1xNEBOSS 3T 132/11KV TRANSF 3 3T;1xNEBOSS TRANSF 4
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -1.0%, 2021 S -0.1% W -0.1%2022 S -0.3% W -0.3%2023 S 0.0% W 0.0%, 2024 S -0.3% W -0.3
|  |  | Latest Peak Compensated Load | [5 empty] | 3.2 MVA on 04/12/2019 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 3.8 | 3.8 | 3.8 |  | 3.8 |  | 3.8 | 2.5 |  | 2.5 |  | 2.4 | 2.4 | 2.4
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.991 | 0.991 | 0.991 |  | 0.991 |  | 0.991 | 0.995 |  | 0.995 |  | 0.995 | 0.995 | 0.995
|  |  |  | ECC Rating (MVA) |  | 5 | 5 | 5 |  | 5 |  | 5 | 5 |  | 5 |  | 5 | 5 | 5
|  |  |  | 50 PoE Load (MVA) |  | 3.5 | 3.4 | 3.4 |  | 3.4 |  | 3.4 | 2.4 |  | 2.3 |  | 2.3 | 2.3 | 2.3
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 12.5 | 12.5 | 12.5 |  | 12.5 |  | 12.5 | 12.5 |  | 12.5 |  | 12.5 | 12.5 | 12.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## NESM
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | NESM - Neil Smith (66/11kV) | [8 empty] | Supply |  | TMES - Townsville Mesh
| Description |  |  |  | Region is Nth Queensland
Transformer size is 2x66/11kV 15/20/25MVA ON/OB/OFB
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.2%, 2021 S 0.1% W 0.1%, 2022 S -0.1% W -0.1%2023 S 0.1% W 0.1%, 2024 S -0.1% W -0.1
|  |  | Latest Peak Compensated Load | [5 empty] | 15.9 MVA on 20/01/2020 at 13:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 65.5 | 65.5 | 65.5 |  | 65.5 |  | 65.5 | 68 |  | 68 |  | 68 | 68 | 68
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 16.7 | 16.7 | 16.7 |  | 16.8 |  | 16.8 | 10.8 |  | 10.7 |  | 10.6 | 10.6 | 10.6
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.984 | 0.984 | 0.984 |  | 0.984 |  | 0.984 | 0.995 |  | 0.995 |  | 0.995 | 0.995 | 0.995
|  |  |  | ECC Rating (MVA) |  | 36.8 | 36.8 | 36.8 |  | 36.8 |  | 36.8 | 37.4 |  | 37.4 |  | 37.4 | 37.4 | 37.4
|  |  |  | 50 PoE Load (MVA) |  | 15.5 | 15.5 | 15.5 |  | 15.6 |  | 15.6 | 10.3 |  | 10.3 |  | 10.2 | 10.2 | 10.2
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.8 | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | Hours PA > 95% Peak Load |  | 25.5 | 25.5 | 25.5 |  | 25.5 |  | 25.5 | 25.5 |  | 25.5 |  | 25.5 | 25.5 | 25.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## NOCL
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | NOCL - North Cloncurry (66/11kV) | [8 empty] | Supply |  | CHUM - Chumvale BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/11kV 5/6.5MVA ONAN/ONAF;1x66/11kV 6.5/5MVA ONAF/ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.3%, 2021 S -0.4% W -0.4%2022 S -0.5% W -0.5%2023 S -0.4% W -0.4%2024 S -0.6% W -0.6
|  |  | Latest Peak Compensated Load | [5 empty] | 3.6 MVA on 18/12/2019 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 10.8 | 10.8 | 10.8 |  | 10.8 |  | 10.8 | 13.1 |  | 13.1 |  | 13.1 | 13.1 | 13.1
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 3.9 | 3.9 | 3.9 |  | 3.9 |  | 3.9 | 2 |  | 2 |  | 2 | 2 | 2
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.994 | 0.994 | 0.994 |  | 0.994 |  | 0.994 | 0.998 |  | 0.998 |  | 0.998 | 0.998 | 0.998
|  |  |  | ECC Rating (MVA) |  | 6.2 | 6.2 | 6.2 |  | 6.2 |  | 6.2 | 7.2 |  | 7.2 |  | 7.2 | 7.2 | 7.2
|  |  |  | 50 PoE Load (MVA) |  | 3.6 | 3.6 | 3.6 |  | 3.6 |  | 3.6 | 1.9 |  | 1.9 |  | 1.9 | 1.9 | 1.9
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 18.5 | 18.5 | 18.5 |  | 18.5 |  | 18.5 | 18.5 |  | 18.5 |  | 18.5 | 18.5 | 18.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## NOMA
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | NOMA - North Mackay (33/11kV) | [8 empty] | Supply |  | GZSA - Glenella ZS Accumulator
| Description |  |  |  | Region is Mackay
Transformer size is 2x33/11kV 15/20MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.5%, 2021 S 0.7% W 0.7%, 2022 S 0.6% W 0.6%, 2023 S 0.6% W 0.6%, 2024 S 0.5% W 0.5%
|  |  | Latest Peak Compensated Load | [5 empty] | 22.9 MVA on 16/02/2020 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 47.7 | 47.7 | 47.7 |  | 47.7 |  | 47.7 | 53.1 |  | 53.1 |  | 53.1 | 53.1 | 53.1
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 26.5 | 26.7 | 26.9 |  | 27.1 |  | 27.3 | 15.9 |  | 15.9 |  | 15.9 | 15.9 | 16.1
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 1 | 1 | 1 |  | 1 |  | 1 | 0.999 |  | 0.999 |  | 0.999 | 0.999 | 0.999
|  |  |  | ECC Rating (MVA) |  | 26.9 | 26.9 | 26.9 |  | 26.9 |  | 26.9 | 29.1 |  | 29.1 |  | 29.1 | 29.1 | 29.1
|  |  |  | 50 PoE Load (MVA) |  | 23.9 | 24 | 24.2 |  | 24.4 |  | 24.6 | 15.4 |  | 15.4 |  | 15.4 | 15.4 | 15.6
|  |  |  | 50 PoE Load > 95% (MVA) |  | 1.2 | 1.2 | 1.2 |  | 1.2 |  | 1.2 | 0.8 |  | 0.8 |  | 0.8 | 0.8 | 0.8
|  |  |  | Hours PA > 95% Peak Load |  | 18.5 | 18.5 | 18.5 |  | 18.5 |  | 18.5 | 18.5 |  | 18.5 |  | 18.5 | 18.5 | 18.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## NORM
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | NORM - Normanton (66/22kV) | [8 empty] | Supply |  | GEOR - Georgetown BSP
| Description |  |  |  | Region is Far North
Transformer size is 1xNORM TX NO 1-66/22KV TRANSF 1;1xNORM TX NO 2-66/22KV TRANSF 2
Capacity of commissioned Embedded Generation (with Connection Agreements) is 5.3 MVA
Growth Rates |  |  |  |  | 2020 W -0.6%, 2021 S 0.0% W 0.0%, 2022 S -0.2% W -0.2%2023 S 0.1% W 0.1%, 2024 S -0.1% W -0.1
|  |  | Latest Peak Compensated Load | [5 empty] | 4.4 MVA on 04/12/2019 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 10.2 | 10.2 | 10.2 |  | 10.2 |  | 10.2 | 10.2 |  | 10.2 |  | 10.2 | 10.2 | 10.2
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 4.9 | 4.9 | 4.9 |  | 5 |  | 5 | 3.5 |  | 3.5 |  | 3.6 | 3.6 | 3.6
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.991 | 0.991 | 0.991 |  | 0.991 |  | 0.991 | 0.926 |  | 0.926 |  | 0.991 | 0.991 | 0.991
|  |  |  | ECC Rating (MVA) |  | 5.2 | 5.2 | 5.2 |  | 5.2 |  | 5.2 | 5.8 |  | 5.8 |  | 5.8 | 5.8 | 5.8
|  |  |  | 50 PoE Load (MVA) |  | 4.7 | 4.7 | 4.7 |  | 4.7 |  | 4.7 | 3.4 |  | 3.4 |  | 3.4 | 3.4 | 3.4
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 66 | 66 | 66 |  | 66 |  | 66 | 66 |  | 66 |  | 66 | 66 | 66
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 1.3 | 1.3 | 1.3 |  | 1.3 |  | 1.3 | 1.3 |  | 1.3 |  | 1.3 | 1.3 | 1.3
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 1.3 | 1.3 | 1.3 |  | 1.3 |  | 1.3 | 1.3 |  | 1.3 |  | 1.3 | 1.3 | 1.3
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## NORW
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | NORW - Norwin (33/11kV) | [8 empty] | Supply |  | YARA - Yarranlea BSP
| Description |  |  |  | Region is South West
Transformer size is 2x7.5/10MVA ONAN/ONAF 33/11kV
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.0%, 2021 S 0.0% W 0.0%, 2022 S -0.0% W -0.0%2023 S 0.1% W 0.1%, 2024 S -0.1% W -0.1
|  |  | Latest Peak Compensated Load | [5 empty] | 2.2 MVA on 16/12/2019 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 22 | 22 | 22 |  | 22 |  | 22 | 22 |  | 22 |  | 22 | 22 | 22
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 2.2 | 2.2 | 2.2 |  | 2.2 |  | 2.3 | 1.2 |  | 1.2 |  | 1.2 | 1.2 | 1.2
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.869 | 0.869 | 0.869 |  | 0.869 |  | 0.877 | 0.901 |  | 0.901 |  | 0.901 | 0.901 | 0.901
|  |  |  | ECC Rating (MVA) |  | 11.5 | 11.5 | 11.5 |  | 11.5 |  | 11.5 | 13 |  | 13 |  | 13 | 13 | 13
|  |  |  | 50 PoE Load (MVA) |  | 2.2 | 2.2 | 2.2 |  | 2.2 |  | 2.3 | 1.1 |  | 1.1 |  | 1.1 | 1.1 | 1.1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 7.5 | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 | 7.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## NOST
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | NOST - North Street (33/11kV) | [8 empty] | Supply |  | T116 - Torrington BSP
| Description |  |  |  | Region is South West
Transformer size is 3x33/11kV 10MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.7%, 2021 S -0.1% W -0.1%2022 S -0.0% W -0.0%2023 S 0.4% W 0.4%, 2024 S 0.1% W 0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 22.8 MVA on 04/06/2019 at 15:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 31.1 | 31.1 | 31.1 |  | 31.1 |  | 31.1 | 34.5 |  | 34.5 |  | 34.5 | 34.5 | 34.5
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 20.2 | 20.2 | 20.3 |  | 20.4 |  | 20.5 | 19.4 |  | 19.3 |  | 19.2 | 19.2 | 19.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.839 | 0.839 | 0.839 |  | 0.839 |  | 0.839 | 0.929 |  | 0.929 |  | 0.929 | 0.929 | 0.929
|  |  |  | ECC Rating (MVA) |  | 23.6 | 23.6 | 23.6 |  | 23.6 |  | 23.6 | 26.5 |  | 26.5 |  | 26.5 | 26.5 | 26.5
|  |  |  | 50 PoE Load (MVA) |  | 18.1 | 18.1 | 18.2 |  | 18.3 |  | 18.4 | 17.9 |  | 17.9 |  | 17.7 | 17.7 | 17.8
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.9 | 0.9 | 0.9 |  | 0.9 |  | 0.9 | 0.9 |  | 0.9 |  | 0.9 | 0.9 | 0.9
|  |  |  | Hours PA > 95% Peak Load |  | 14.5 | 14.5 | 14.5 |  | 14.5 |  | 14.5 | 14.5 |  | 14.5 |  | 14.5 | 14.5 | 14.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## OAKE
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | OAKE - Oakey (33/11kV) | [8 empty] | Supply |  | T189 - Oakey BSP
| Description |  |  |  | Region is South West
Transformer size is 2x33/11kV 20/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -1.4%, 2021 S -0.5% W -0.5%2022 S -1.1% W -1.1%2023 S -0.5% W -0.5%2024 S -0.8% W -0.8
|  |  | Latest Peak Compensated Load | [5 empty] | 16.6 MVA on 11/12/2019 at 14:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 49.7 | 49.7 | 49.7 |  | 49.7 |  | 49.7 | 56.3 |  | 56.3 |  | 56.3 | 56.3 | 56.3
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 16.8 | 16.6 | 16.5 |  | 16.5 |  | 16.4 | 15 |  | 14.8 |  | 14.6 | 14.4 | 14.4
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.961 | 0.961 | 0.961 |  | 0.961 |  | 0.961 | 0.969 |  | 0.969 |  | 0.969 | 0.969 | 0.969
|  |  |  | ECC Rating (MVA) |  | 28.4 | 28.4 | 28.4 |  | 28.4 |  | 28.4 | 32.3 |  | 32.3 |  | 32.3 | 32.3 | 32.3
|  |  |  | 50 PoE Load (MVA) |  | 15.7 | 15.5 | 15.5 |  | 15.4 |  | 15.3 | 14.5 |  | 14.3 |  | 14.1 | 13.9 | 13.9
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.8 | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.7 |  | 0.7 |  | 0.7 | 0.7 | 0.7
|  |  |  | Hours PA > 95% Peak Load |  | 8.5 | 8.5 | 8.5 |  | 8.5 |  | 8.5 | 8.5 |  | 8.5 |  | 8.5 | 8.5 | 8.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## OONN
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | OONN - Oonoonba (66/11kV) | [8 empty] | Supply |  | TMES - Townsville Mesh
| Description |  |  |  | Region is Nth Queensland
Transformer size is 2x66/11kV 19/26/32MVA ONAN/ODAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 1.8%, 2021 S 1.6% W 1.6%, 2022 S 1.4% W 1.4%, 2023 S 1.5% W 1.5%, 2024 S 1.3% W 1.3%
|  |  | Latest Peak Compensated Load | [5 empty] | 14.7 MVA on 12/02/2020 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 74.2 | 74.2 | 74.2 |  | 74.2 |  | 74.2 | 77.6 |  | 77.6 |  | 77.6 | 77.6 | 77.6
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 16.3 | 16.5 | 16.8 |  | 17.1 |  | 17.4 | 7.1 |  | 7.2 |  | 7.2 | 7.3 | 7.4
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.989 | 0.989 | 0.989 |  | 0.989 |  | 0.989 | 0.987 |  | 0.987 |  | 0.987 | 0.987 | 0.987
|  |  |  | ECC Rating (MVA) |  | 41.2 | 41.2 | 41.2 |  | 41.2 |  | 41.2 | 42.8 |  | 42.8 |  | 42.8 | 42.8 | 42.8
|  |  |  | 50 PoE Load (MVA) |  | 14.7 | 14.9 | 15.2 |  | 15.4 |  | 15.7 | 7 |  | 7.1 |  | 7.1 | 7.2 | 7.3
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.7 | 0.7 | 0.8 |  | 0.8 |  | 0.8 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  |  | Hours PA > 95% Peak Load |  | 11.5 | 11.5 | 11.5 |  | 11.5 |  | 11.5 | 11.5 |  | 11.5 |  | 11.5 | 11.5 | 11.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## OWAN
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | OWAN - Owanyilla (66/11kV) | [8 empty] | Supply |  | MARY - Maryborough BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 1x66/11kV 10MVA ONAN;1xOWAN TX NO 1 TRANSF 1 RG91765711 10 MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.5%, 2021 S 0.5% W 0.5%, 2022 S 0.4% W 0.4%, 2023 S 0.5% W 0.5%, 2024 S 0.3% W 0.3%
|  |  | Latest Peak Compensated Load | [5 empty] | 6.2 MVA on 09/12/2019 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 22 | 22 | 22 |  | 22 |  | 22 | 22 |  | 22 |  | 22 | 22 | 22
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 8.7 | 8.7 | 8.8 |  | 8.9 |  | 8.9 | 3.5 |  | 3.6 |  | 3.5 | 3.6 | 3.6
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.931 | 0.931 | 0.931 |  | 0.931 |  | 0.931 | 0.957 |  | 0.957 |  | 0.957 | 0.957 | 0.957
|  |  |  | ECC Rating (MVA) |  | 12 | 12 | 12 |  | 12 |  | 12 | 13 |  | 13 |  | 13 | 13 | 13
|  |  |  | 50 PoE Load (MVA) |  | 7.1 | 7.1 | 7.1 |  | 7.2 |  | 7.2 | 3.4 |  | 3.4 |  | 3.4 | 3.4 | 3.4
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.4 | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 4.5 | 4.5 | 4.5 |  | 4.5 |  | 4.5 | 4.5 |  | 4.5 |  | 4.5 | 4.5 | 4.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## PAMP
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | PAMP - Pampas (33/11kV) | [8 empty] | Supply |  | YARA - Yarranlea BSP
| Description |  |  |  | Region is South West
Transformer size is 2x33/11kV 5MVA ON
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -1.3%, 2021 S -0.1% W -0.1%2022 S -0.0% W -0.0%2023 S 0.1% W 0.1%, 2024 S -0.1% W -0.1
|  |  | Latest Peak Compensated Load | [5 empty] | 7.8 MVA on 15/02/2020 at 16:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 8.8 | 8.8 | 8.8 |  | 8.8 |  | 8.8 | 3.3 |  | 3.2 |  | 3.2 | 3.2 | 3.2
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.774 | 0.774 | 0.774 |  | 0.774 |  | 0.774 | 0.783 |  | 0.783 |  | 0.783 | 0.783 | 0.783
|  |  |  | ECC Rating (MVA) |  | 5.5 | 5.5 | 5.5 |  | 5.5 |  | 5.5 | 5.5 |  | 5.5 |  | 5.5 | 5.5 | 5.5
|  |  |  | 50 PoE Load (MVA) |  | 8.6 | 8.6 | 8.6 |  | 8.6 |  | 8.6 | 3.2 |  | 3.1 |  | 3.1 | 3.1 | 3.1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.4 | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 13 | 13 | 13 |  | 13 |  | 13 | 13 |  | 13 |  | 13 | 13 | 13
|  |  |  | Raw LAR (MVA) |  | 3.1 | 3.1 | 3.1 |  | 3.1 |  | 3.1
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## PAND
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | PAND - Pandoin (66/22kV) | [8 empty] | Supply |  | RMES - Rockhampton Mesh
| Description |  |  |  | Region is Capricornia
Transformer size is 2x66/22kV 8/10MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.1%, 2021 S 0.1% W 0.1%, 2022 S -0.0% W -0.0%2023 S 0.1% W 0.1%, 2024 S -0.1% W -0.1
|  |  | Latest Peak Compensated Load | [5 empty] | 10.7 MVA on 02/12/2019 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 23.2 | 23.2 | 23.2 |  | 23.2 |  | 23.2 | 26.6 |  | 26.6 |  | 26.6 | 26.6 | 26.6
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 11.2 | 11.2 | 11.2 |  | 11.2 |  | 11.2 | 8.8 |  | 8.8 |  | 8.8 | 8.7 | 8.8
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.977 | 0.977 | 0.977 |  | 0.977 |  | 0.977 | 0.989 |  | 0.989 |  | 0.989 | 0.989 | 0.989
|  |  |  | ECC Rating (MVA) |  | 13.6 | 13.6 | 13.6 |  | 13.6 |  | 13.6 | 14.5 |  | 14.5 |  | 14.5 | 14.5 | 14.5
|  |  |  | 50 PoE Load (MVA) |  | 10.1 | 10.1 | 10.1 |  | 10.2 |  | 10.2 | 8.3 |  | 8.2 |  | 8.2 | 8.2 | 8.2
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  |  | Hours PA > 95% Peak Load |  | 16.5 | 16.5 | 16.5 |  | 16.5 |  | 16.5 | 16.5 |  | 16.5 |  | 16.5 | 16.5 | 16.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## PARK
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | PARK - Parkhurst (66/11kV) | [8 empty] | Supply |  | RMES - Rockhampton Mesh
| Description |  |  |  | Region is Capricornia
Transformer size is 2x66/11kV 15/20MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.4%, 2021 S 0.1% W 0.1%, 2022 S -0.1% W -0.1%2023 S 0.1% W 0.1%, 2024 S 0.0% W 0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 15.6 MVA on 16/12/2019 at 16:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 48.3 | 48.3 | 48.3 |  | 48.3 |  | 48.3 | 55.4 |  | 55.4 |  | 55.4 | 55.4 | 55.4
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 16.9 | 16.9 | 16.9 |  | 17 |  | 17 | 10.9 |  | 10.9 |  | 10.8 | 10.8 | 10.9
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 1 | 1 | 1 |  | 1 |  | 1 | 0.95 |  | 0.95 |  | 0.95 | 0.95 | 0.95
|  |  |  | ECC Rating (MVA) |  | 28 | 28 | 28 |  | 28 |  | 28 | 29.9 |  | 29.9 |  | 29.9 | 29.9 | 29.9
|  |  |  | 50 PoE Load (MVA) |  | 16 | 16 | 16 |  | 16.1 |  | 16.1 | 10.5 |  | 10.5 |  | 10.4 | 10.4 | 10.4
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.8 | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | Hours PA > 95% Peak Load |  | 14.5 | 14.5 | 14.5 |  | 14.5 |  | 14.5 | 14.5 |  | 14.5 |  | 14.5 | 14.5 | 14.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## PEAR
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | PEAR - Peter Arlett (66/11kV) | [8 empty] | Supply |  | TMES - Townsville Mesh
| Description |  |  |  | Region is Nth Queensland
Transformer size is 2x66/11kV 21/26.25/35MVA ONAN/ODAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.9%, 2021 S 0.6% W 0.6%, 2022 S 0.5% W 0.5%, 2023 S 0.7% W 0.7%, 2024 S 0.4% W 0.4%
|  |  | Latest Peak Compensated Load | [5 empty] | 22.9 MVA on 12/02/2020 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 78.9 | 78.9 | 78.9 |  | 78.9 |  | 78.9 | 87.4 |  | 87.4 |  | 87.4 | 87.4 | 87.4
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 24.9 | 25.1 | 25.3 |  | 25.5 |  | 25.6 | 16.4 |  | 16.4 |  | 16.4 | 16.4 | 16.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.977 | 0.977 | 0.977 |  | 0.977 |  | 0.977 | 0.982 |  | 0.982 |  | 0.982 | 0.982 | 0.982
|  |  |  | ECC Rating (MVA) |  | 44.4 | 44.4 | 44.4 |  | 44.4 |  | 44.4 | 47.1 |  | 47.1 |  | 47.1 | 47.1 | 47.1
|  |  |  | 50 PoE Load (MVA) |  | 23 | 23.1 | 23.3 |  | 23.4 |  | 23.6 | 15.8 |  | 15.8 |  | 15.8 | 15.8 | 16
|  |  |  | 50 PoE Load > 95% (MVA) |  | 1.2 | 1.2 | 1.2 |  | 1.2 |  | 1.2 | 0.8 |  | 0.8 |  | 0.8 | 0.8 | 0.8
|  |  |  | Hours PA > 95% Peak Load |  | 6.5 | 6.5 | 6.5 |  | 6.5 |  | 6.5 | 6.5 |  | 6.5 |  | 6.5 | 6.5 | 6.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## PERA
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | PERA - Peranga (33/11kV) | [8 empty] | Supply |  | T189 - Oakey BSP
| Description |  |  |  | Region is South West
Transformer size is 1x33/11kV 0.75MVA ON;1x33/11kV 3MVA ON
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.1%, 2021 S 0.1% W 0.1%, 2022 S -0.1% W -0.1%2023 S 0.2% W 0.2%, 2024 S -0.1% W -0.1
|  |  | Latest Peak Compensated Load | [5 empty] | 1.7 MVA on 16/12/2019 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 4.7 | 4.7 | 4.7 |  | 4.7 |  | 4.7 | 5.1 |  | 5.1 |  | 5.1 | 5.1 | 5.1
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 1.8 | 1.8 | 1.8 |  | 1.8 |  | 1.8 | 1.6 |  | 1.6 |  | 1.5 | 1.5 | 1.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.909 | 0.909 | 0.909 |  | 0.909 |  | 0.909 | 0.892 |  | 0.892 |  | 0.892 | 0.892 | 0.892
|  |  |  | ECC Rating (MVA) |  | 0.8 | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.8 | 0.8
|  |  |  | 50 PoE Load (MVA) |  | 1.7 | 1.7 | 1.7 |  | 1.7 |  | 1.7 | 1.5 |  | 1.5 |  | 1.5 | 1.5 | 1.5
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 2.5 | 2.5 | 2.5 |  | 2.5 |  | 2.5 | 2.5 |  | 2.5 |  | 2.5 | 2.5 | 2.5
|  |  |  | Raw LAR (MVA) |  | 0.9 | 0.9 | 0.9 |  | 0.9 |  | 0.9 | 0.7 |  | 0.7 |  | 0.7 | 0.7 | 0.7
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## PIAL
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | PIAL - Pialba (66/11kV) | [8 empty] | Supply |  | MARY - Maryborough BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 2x66/11kV 12.5/16MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.4 MVA
Growth Rates |  |  |  |  | 2020 W 0.3%, 2021 S 0.1% W 0.1%, 2022 S -0.4% W -0.4%2023 S -0.3% W -0.3%2024 S -0.2% W -0.2
|  |  | Latest Peak Compensated Load | [5 empty] | 16.2 MVA on 20/02/2020 at 16:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 33.2 | 33.2 | 33.2 |  | 33.2 |  | 33.2 | 37.2 |  | 37.2 |  | 37.2 | 37.2 | 37.2
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 17.6 | 17.5 | 17.5 |  | 17.5 |  | 17.6 | 13.4 |  | 13.4 |  | 13.2 | 13.1 | 13.2
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.997 | 0.997 | 0.997 |  | 0.997 |  | 0.997 | 0.993 |  | 0.993 |  | 0.993 | 0.993 | 0.993
|  |  |  | ECC Rating (MVA) |  | 19.1 | 19.1 | 19.1 |  | 19.1 |  | 19.1 | 21 |  | 21 |  | 21 | 21 | 21
|  |  |  | 50 PoE Load (MVA) |  | 16.2 | 16.1 | 16.1 |  | 16.1 |  | 16.2 | 12.7 |  | 12.7 |  | 12.5 | 12.5 | 12.5
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.8 | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  |  | Hours PA > 95% Peak Load |  | 8 | 8 | 8 |  | 8 |  | 8 | 8 |  | 8 |  | 8 | 8 | 8
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 4 | 4 | 4 |  | 4 |  | 4 | 4 |  | 4 |  | 4 | 4 | 4
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## PINN
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | PINN - Pinnacle (66/11kV) | [8 empty] | Supply |  | PIVA - Pioneer Valley BSP
| Description |  |  |  | Region is Mackay
Transformer size is 2x66/11kV 5MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.9%, 2021 S 0.3% W 0.3%, 2022 S 0.2% W 0.2%, 2023 S 0.3% W 0.3%, 2024 S 0.2% W 0.2%
|  |  | Latest Peak Compensated Load | [5 empty] | 3.9 MVA on 17/11/2019 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 11 | 11 | 11 |  | 11 |  | 11 | 12 |  | 12 |  | 12 | 12 | 12
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 5.3 | 5.3 | 5.3 |  | 5.3 |  | 5.4 | 2.4 |  | 2.4 |  | 2.4 | 2.4 | 2.4
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.971 | 0.97 | 0.97 |  | 0.97 |  | 0.969 | 0.874 |  | 0.874 |  | 0.874 | 0.874 | 0.874
|  |  |  | ECC Rating (MVA) |  | 6.3 | 6.3 | 6.3 |  | 6.3 |  | 6.3 | 6.5 |  | 6.5 |  | 6.5 | 6.5 | 6.5
|  |  |  | 50 PoE Load (MVA) |  | 4.1 | 4.1 | 4.1 |  | 4.1 |  | 4.2 | 2.2 |  | 2.2 |  | 2.1 | 2.1 | 2.2
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 8 | 8 | 8 |  | 8 |  | 8 | 8 |  | 8 |  | 8 | 8 | 8
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## PIRR
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | PIRR - Pirrinuan (33/11kV) | [8 empty] | Supply |  | T002 - Dalby East BSP
| Description |  |  |  | Region is South West
Transformer size is 1x33/11kV 3.15MVA ONAN;1x33/11kV 1MVA ON(Standby)
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.0%, 2021 S -3.4% W -3.4%2022 S -5.1% W -5.1%2023 S -5.0% W -5.0%2024 S -2.8% W -2.8
|  |  | Latest Peak Compensated Load | [5 empty] | 2.4 MVA on 25/06/2019 at 07:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 3.2 | 3.2 | 3.2 |  | 3.2 |  | 3.2 | 3.2 |  | 3.2 |  | 3.2 | 3.2 | 3.2
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 0.9 | 0.9 | 0.8 |  | 0.8 |  | 0.8 | 1.3 |  | 1.3 |  | 1.2 | 1.1 | 1.1
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.677 | 0.677 | 0.677 |  | 0.677 |  | 0.677 | 0.481 |  | 0.481 |  | 0.481 | 0.481 | 0.481
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 0.8 | 0.8 | 0.8 |  | 0.7 |  | 0.7 | 1.3 |  | 1.2 |  | 1.1 | 1.1 | 1.1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 22 | 22 | 22 |  | 22 |  | 22 | 22 |  | 22 |  | 22 | 22 | 22
|  |  |  | Raw LAR (MVA) |  | 0.8 | 0.8 | 0.8 |  | 0.7 |  | 0.7 | 1.3 |  | 1.2 |  | 1.1 | 1.1 | 1.1
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Mobile Plant Avail (MVA) |  | 1.5 | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.5 | 1.5
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## PLAN
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | PLAN - Planella (66/11kV) | [8 empty] | Supply |  | PIVA - Pioneer Valley BSP
| Description |  |  |  | Region is Mackay
Transformer size is 2x33/11kV 13MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 1.2%, 2021 S 1.3% W 1.3%, 2022 S 1.2% W 1.2%, 2023 S 1.2% W 1.2%, 2024 S 1.1% W 1.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 19.3 MVA on 16/02/2020 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 30.6 | 30.6 | 30.6 |  | 30.6 |  | 30.6 | 30.6 |  | 30.6 |  | 30.6 | 30.6 | 30.6
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 19.7 | 20 | 20.2 |  | 20.5 |  | 20.8 | 11.6 |  | 10.3 |  | 10.3 | 10.4 | 10.6
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.996 | 0.996 | 0.996 |  | 0.996 |  | 0.996 | 0.999 |  | 0.999 |  | 0.999 | 0.999 | 0.999
|  |  |  | ECC Rating (MVA) |  | 15.3 | 15.3 | 15.3 |  | 15.3 |  | 15.3 | 15.3 |  | 15.3 |  | 15.3 | 15.3 | 15.3
|  |  |  | 50 PoE Load (MVA) |  | 17.3 | 17.5 | 17.7 |  | 18 |  | 18.2 | 11.4 |  | 10.1 |  | 10.1 | 10.2 | 10.4
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.9 | 0.9 | 0.9 |  | 0.9 |  | 0.9 | 0.6 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | Hours PA > 95% Peak Load |  | 17 | 17 | 17 |  | 17 |  | 17 | 17 |  | 17 |  | 17 | 17 | 17
|  |  |  | Raw LAR (MVA) |  | 2 | 2.2 | 2.4 |  | 2.7 |  | 2.9
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 2.3 | 2.3 | 2.3 |  | 2.3 |  | 2.3 | 2.3 |  | 2.3 |  | 2.3 | 2.3 | 2.3
|  |  |  | Mobile Plant Avail (MVA) |  | 1.5 | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.5 | 1.5
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## PLEY
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | PLEY - Pleystowe (33/11kV) | [8 empty] | Supply |  | MACK - Mackay BSP
| Description |  |  |  | Region is Mackay
Transformer size is 3x33/11kV 5MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.3%, 2021 S 0.2% W 0.2%, 2022 S 0.1% W 0.1%, 2023 S 0.2% W 0.2%, 2024 S 0.0% W 0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 7.7 MVA on 02/12/2019 at 20:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 13.5 | 13.5 | 13.5 |  | 13.5 |  | 13.5 | 13.5 |  | 13.5 |  | 13.5 | 13.5 | 13.5
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 9.6 | 9.6 | 9.6 |  | 9.6 |  | 9.7 | 4.9 |  | 4.9 |  | 4.9 | 4.9 | 4.9
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.976 | 0.976 | 0.976 |  | 0.976 |  | 0.976 | 0.984 |  | 0.984 |  | 0.984 | 0.984 | 0.984
|  |  |  | ECC Rating (MVA) |  | 9 | 9 | 9 |  | 9 |  | 9 | 9 |  | 9 |  | 9 | 9 | 9
|  |  |  | 50 PoE Load (MVA) |  | 8.1 | 8.2 | 8.2 |  | 8.2 |  | 8.2 | 4.7 |  | 4.7 |  | 4.7 | 4.7 | 4.7
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.4 | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 3.5 | 3.5 | 3.5 |  | 3.5 |  | 3.5 | 3.5 |  | 3.5 |  | 3.5 | 3.5 | 3.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 | 2 | 2
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## POVE
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | POVE - Point Vernon (66/11kV) | [8 empty] | Supply |  | MARY - Maryborough BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 1xPoint Vernon Tx No 1;1xPoint Vernon Tx No 2
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.3%, 2021 S 0.0% W 0.0%, 2022 S -0.4% W -0.4%2023 S -0.4% W -0.4%2024 S -0.3% W -0.3
|  |  | Latest Peak Compensated Load | [5 empty] | 21.3 MVA on 20/02/2020 at 16:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 84.6 | 84.6 | 84.6 |  | 84.6 |  | 84.6 | 95.7 |  | 95.7 |  | 95.7 | 95.7 | 95.7
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 23.3 | 23.2 | 23.1 |  | 23.1 |  | 23.1 | 17.5 |  | 17.4 |  | 17.2 | 17.1 | 17.1
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 1 | 1 | 1 |  | 1 |  | 1 | 0.994 |  | 0.994 |  | 0.994 | 0.994 | 0.994
|  |  |  | ECC Rating (MVA) |  | 47.6 | 47.6 | 47.6 |  | 47.6 |  | 47.6 | 47.8 |  | 47.8 |  | 47.8 | 47.8 | 47.8
|  |  |  | 50 PoE Load (MVA) |  | 21.3 | 21.2 | 21.1 |  | 21.2 |  | 21.1 | 16.4 |  | 16.3 |  | 16.1 | 16 | 16
|  |  |  | 50 PoE Load > 95% (MVA) |  | 1.1 | 1.1 | 1.1 |  | 1.1 |  | 1.1 | 0.8 |  | 0.8 |  | 0.8 | 0.8 | 0.8
|  |  |  | Hours PA > 95% Peak Load |  | 4.5 | 4.5 | 4.5 |  | 4.5 |  | 4.5 | 4.5 |  | 4.5 |  | 4.5 | 4.5 | 4.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## POZI
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | POZI - Pozieres (33/11kV) | [8 empty] | Supply |  | STAN - Stanthorpe BSP
| Description |  |  |  | Region is South West
Transformer size is 2x33/11kV 3MVA ON
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -2.3%, 2021 S -0.3% W -0.3%2022 S -0.6% W -0.6%2023 S -0.3% W -0.3%2024 S -0.5% W -0.5
|  |  | Latest Peak Compensated Load | [5 empty] | 2.5 MVA on 03/02/2020 at 15:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 7.1 | 7.1 | 7.1 |  | 7.1 |  | 7.1 | 7.5 |  | 7.5 |  | 7.5 | 7.5 | 7.5
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 2.9 | 2.8 | 2.8 |  | 2.8 |  | 2.8 | 2.3 |  | 2.3 |  | 2.3 | 2.3 | 2.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.866 | 0.866 | 0.866 |  | 0.866 |  | 0.866 | 0.913 |  | 0.913 |  | 0.913 | 0.913 | 0.913
|  |  |  | ECC Rating (MVA) |  | 3.9 | 3.9 | 3.9 |  | 3.9 |  | 3.9 | 4 |  | 4 |  | 4 | 4 | 4
|  |  |  | 50 PoE Load (MVA) |  | 2.7 | 2.7 | 2.7 |  | 2.7 |  | 2.7 | 2.3 |  | 2.2 |  | 2.2 | 2.2 | 2.2
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 45.5 | 45.5 | 45.5 |  | 45.5 |  | 45.5 | 45.5 |  | 45.5 |  | 45.5 | 45.5 | 45.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## PRMI
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | PRMI - Proserpine Mill (66/11kV) | [8 empty] | Supply |  | PROS - Proserpine BSP
| Description |  |  |  | Region is Mackay
Transformer size is 1x66/11kV 10/12.5MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 20.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.2%, 2021 S -0.6% W -0.6%2022 S -0.8% W -0.8%2023 S -0.6% W -0.6%2024 S -0.4% W -0.4
|  |  | Latest Peak Compensated Load | [5 empty] | 4.1 MVA on 27/08/2019 at 12:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 14.4 | 14.4 | 14.4 |  | 14.4 |  | 14.4 | 15.2 |  | 15.2 |  | 15.2 | 15.2 | 15.2
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 3.6 | 3.6 | 3.5 |  | 3.5 |  | 3.5 | 4.4 |  | 4.4 |  | 4.3 | 4.3 | 4.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.989 | 0.989 | 0.989 |  | 0.989 |  | 0.989 | 0.918 |  | 0.918 |  | 0.918 | 0.918 | 0.918
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 3.5 | 3.5 | 3.5 |  | 3.5 |  | 3.5 | 4.3 |  | 4.3 |  | 4.2 | 4.2 | 4.2
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 6 | 6 | 6 |  | 6 |  | 6 | 6 |  | 6 |  | 6 | 6 | 6
|  |  |  | Raw LAR (MVA) |  | 3.5 | 3.5 | 3.5 |  | 3.5 |  | 3.5 | 4.3 |  | 4.3 |  | 4.2 | 4.2 | 4.2
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 1.8 | 1.8 | 1.8 |  | 1.8 |  | 1.8 | 1.8 |  | 1.8 |  | 1.8 | 1.8 | 1.8
|  |  |  | Mobile Plant Avail (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 2.3 | 2.3 | 2.3 |  | 2.3 |  | 2.3 | 2.3 |  | 2.3 |  | 2.3 | 2.3 | 2.3
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## PROT
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | PROT - Proston (66/11kV) | [8 empty] | Supply |  | KILK - Kilkivan BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 1x66/11kV 2.3MVA ONAN;1x66/11kV 2MVA ON
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.2%, 2021 S 0.2% W 0.2%, 2022 S 0.1% W 0.1%, 2023 S 0.2% W 0.2%, 2024 S -0.1% W -0.1
|  |  | Latest Peak Compensated Load | [5 empty] | 1.5 MVA on 17/07/2019 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 5.4 | 5.4 | 5.4 |  | 5.4 |  | 5.4 | 6 |  | 6 |  | 6 | 6 | 6
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 1.6 | 1.6 | 1.6 |  | 1.6 |  | 1.6 | 1.5 |  | 1.5 |  | 1.5 | 1.4 | 1.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.975 | 0.975 | 0.975 |  | 0.975 |  | 0.975 | 0.985 |  | 0.985 |  | 0.985 | 0.985 | 0.985
|  |  |  | ECC Rating (MVA) |  | 3 | 3 | 3 |  | 3 |  | 3 | 3 |  | 3 |  | 3 | 3 | 3
|  |  |  | 50 PoE Load (MVA) |  | 1.5 | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.4 |  | 1.4 |  | 1.4 | 1.4 | 1.4
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 7 | 7 | 7 |  | 7 |  | 7 | 7 |  | 7 |  | 7 | 7 | 7
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## PURR
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | PURR - Purrawunda (33/11kV) | [8 empty] | Supply |  | T116 - Torrington BSP
| Description |  |  |  | Region is South West
Transformer size is 2x33/11kV 6.25MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.0%, 2021 S 0.0% W 0.0%, 2022 S -0.1% W -0.1%2023 S 0.2% W 0.2%, 2024 S -0.2% W -0.2
|  |  | Latest Peak Compensated Load | [5 empty] | 6.3 MVA on 16/12/2019 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 14 | 14 | 14 |  | 14 |  | 14 | 15.5 |  | 15.5 |  | 15.5 | 15.5 | 15.5
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 6.7 | 6.7 | 6.7 |  | 6.7 |  | 6.7 | 6 |  | 6 |  | 6 | 6 | 6
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 1 | 1 | 1 |  | 1 |  | 1 | 0.999 |  | 0.999 |  | 0.999 | 0.999 | 0.999
|  |  |  | ECC Rating (MVA) |  | 8.2 | 8.2 | 8.2 |  | 8.2 |  | 8.2 | 8.8 |  | 8.8 |  | 8.8 | 8.8 | 8.8
|  |  |  | 50 PoE Load (MVA) |  | 6.4 | 6.4 | 6.4 |  | 6.4 |  | 6.4 | 5.9 |  | 5.9 |  | 5.9 | 5.9 | 5.9
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Hours PA > 95% Peak Load |  | 23.5 | 23.5 | 23.5 |  | 23.5 |  | 23.5 | 23.5 |  | 23.5 |  | 23.5 | 23.5 | 23.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## QUIL
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | QUIL - Quilpie (66/11kV) | [8 empty] | Supply |  | ROMA - Roma 66kV BSP
| Description |  |  |  | Region is South West
Transformer size is 2x66/11kV 3MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -1.2%, 2021 S -0.5% W -0.5%2022 S -0.6% W -0.6%2023 S -0.5% W -0.5%2024 S -0.7% W -0.7
|  |  | Latest Peak Compensated Load | [5 empty] | 2.3 MVA on 10/01/2020 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 6.3 | 6.3 | 6.3 |  | 6.3 |  | 6.3 | 7.4 |  | 7.4 |  | 7.4 | 7.4 | 7.4
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 2.6 | 2.6 | 2.6 |  | 2.6 |  | 2.6 | 1.6 |  | 1.6 |  | 1.6 | 1.6 | 1.6
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.982 | 0.982 | 0.982 |  | 0.982 |  | 0.982 | 0.923 |  | 0.923 |  | 0.923 | 0.923 | 0.923
|  |  |  | ECC Rating (MVA) |  | 3.7 | 3.7 | 3.7 |  | 3.7 |  | 3.7 | 4.3 |  | 4.3 |  | 4.3 | 4.3 | 4.3
|  |  |  | 50 PoE Load (MVA) |  | 2.3 | 2.3 | 2.3 |  | 2.3 |  | 2.3 | 1.5 |  | 1.5 |  | 1.5 | 1.5 | 1.5
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 17.5 | 17.5 | 17.5 |  | 17.5 |  | 17.5 | 17.5 |  | 17.5 |  | 17.5 | 17.5 | 17.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## RAGL
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | RAGL - Raglan (66/22kV) | [8 empty] | Supply |  | RMES - Rockhampton Mesh
| Description |  |  |  | Region is Capricornia
Transformer size is 2x66/22kV 5MVA ON
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.2%, 2021 S 0.4% W 0.4%, 2022 S 0.2% W 0.2%, 2023 S 0.5% W 0.5%, 2024 S 0.1% W 0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 4 MVA on 16/12/2019 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 12.5 | 12.5 | 12.5 |  | 12.5 |  | 12.5 | 14 |  | 14 |  | 14 | 14 | 14
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 4.2 | 4.2 | 4.2 |  | 4.3 |  | 4.3 | 3.2 |  | 3.2 |  | 3.2 | 3.2 | 3.2
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.982 | 0.982 | 0.982 |  | 0.982 |  | 0.982 | 0.952 |  | 0.952 |  | 0.952 | 0.952 | 0.952
|  |  |  | ECC Rating (MVA) |  | 7.5 | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 | 7.5
|  |  |  | 50 PoE Load (MVA) |  | 3.9 | 3.9 | 4 |  | 4 |  | 4 | 3.1 |  | 3.1 |  | 3.1 | 3.1 | 3.1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 5.5 | 5.5 | 5.5 |  | 5.5 |  | 5.5 | 5.5 |  | 5.5 |  | 5.5 | 5.5 | 5.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## RASM
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | RASM - Rasmussen (66/11kV) | [8 empty] | Supply |  | TMES - Townsville Mesh
| Description |  |  |  | Region is Nth Queensland
Transformer size is 2x66/11kV 19/26/32MVA ONAN/ODAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.1%, 2021 S 0.5% W 0.5%, 2022 S 0.4% W 0.4%, 2023 S 0.5% W 0.5%, 2024 S 0.3% W 0.3%
|  |  | Latest Peak Compensated Load | [5 empty] | 19.6 MVA on 19/01/2020 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 80.4 | 80.4 | 80.4 |  | 80.4 |  | 80.4 | 84.4 |  | 84.4 |  | 84.4 | 84.4 | 84.4
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 23.4 | 23.5 | 23.6 |  | 23.8 |  | 24 | 11.4 |  | 11.4 |  | 11.4 | 11.4 | 11.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.999 | 0.999 | 0.999 |  | 0.999 |  | 0.999 | 0.992 |  | 0.992 |  | 0.992 | 0.992 | 0.992
|  |  |  | ECC Rating (MVA) |  | 42.9 | 42.9 | 42.9 |  | 42.9 |  | 42.9 | 45 |  | 45 |  | 45 | 45 | 45
|  |  |  | 50 PoE Load (MVA) |  | 19.3 | 19.4 | 19.5 |  | 19.6 |  | 19.8 | 11.2 |  | 11.2 |  | 11.2 | 11.2 | 11.3
|  |  |  | 50 PoE Load > 95% (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  |  | Hours PA > 95% Peak Load |  | 9 | 9 | 9 |  | 9 |  | 9 | 9 |  | 9 |  | 9 | 9 | 9
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## RAVE
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | RAVE - Ravenshoe (66/22kV) | [8 empty] | Supply |  | TURK - Turkinje 66kV BSP
| Description |  |  |  | Region is Far North
Transformer size is 1x66/22kV 12/15MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 12.0 MVA
Growth Rates |  |  |  |  | 2020 W -3.1%, 2021 S -0.5% W -0.5%2022 S -1.0% W -1.0%2023 S -0.9% W -0.9%2024 S -0.5% W -0.5
|  |  | Latest Peak Compensated Load | [5 empty] | 2.6 MVA on 18/07/2019 at 07:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 19.6 | 19.6 | 19.6 |  | 19.6 |  | 19.6 | 22.3 |  | 22.3 |  | 22.3 | 22.3 | 22.3
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 2.4 | 2.4 | 2.4 |  | 2.4 |  | 2.4 | 2.7 |  | 2.7 |  | 2.7 | 2.6 | 2.6
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.916 | 0.916 | 0.916 |  | 0.916 |  | 0.916 | 0.918 |  | 0.918 |  | 0.918 | 0.918 | 0.918
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 2.3 | 2.2 | 2.2 |  | 2.2 |  | 2.2 | 2.6 |  | 2.6 |  | 2.5 | 2.5 | 2.5
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 26.5 | 26.5 | 26.5 |  | 26.5 |  | 26.5 | 26.5 |  | 26.5 |  | 26.5 | 26.5 | 26.5
|  |  |  | Raw LAR (MVA) |  | 2.3 | 2.2 | 2.2 |  | 2.2 |  | 2.2 | 2.6 |  | 2.6 |  | 2.5 | 2.5 | 2.5
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 3.9 | 3.9 | 3.9 |  | 3.9 |  | 3.9 | 3.9 |  | 3.9 |  | 3.9 | 3.9 | 3.9
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## RAVN
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | RAVN - Ravenswood (66/11kV) | [8 empty] | Supply |  | T193 - Clare South BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/11kV 2.5MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.3%, 2021 S -0.1% W -0.1%2022 S -0.3% W -0.3%2023 S 0.0% W 0.0%, 2024 S -0.2% W -0.2
|  |  | Latest Peak Compensated Load | [5 empty] | 1.4 MVA on 27/03/2020 at 00:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 2.5 | 2.5 | 2.5 |  | 2.5 |  | 2.5 | 2.5 |  | 2.5 |  | 2.5 | 2.5 | 2.5
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 1.2 | 1.2 | 1.2 |  | 1.2 |  | 1.2 | 0.8 |  | 0.8 |  | 0.8 | 0.8 | 0.8
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.877 | 0.877 | 0.877 |  | 0.877 |  | 0.877 | 0.925 |  | 0.925 |  | 0.925 | 0.925 | 0.925
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 1.2 | 1.2 | 1.2 |  | 1.2 |  | 1.2 | 0.8 |  | 0.8 |  | 0.8 | 0.8 | 0.8
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 14 | 14 | 14 |  | 14 |  | 14 | 14 |  | 14 |  | 14 | 14 | 14
|  |  |  | Raw LAR (MVA) |  | 1.2 | 1.2 | 1.2 |  | 1.2 |  | 1.2 | 0.8 |  | 0.8 |  | 0.8 | 0.8 | 0.8
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 | 2 | 2
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## RICH
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | RICH - Richmond (66/33kV) | [8 empty] | Supply |  | T095 - Millchester BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/33kV 6.3MVA ONAN;1x66/33kV 7.5/6.3MVA ONAF/ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.8%, 2021 S -0.3% W -0.3%2022 S -0.4% W -0.4%2023 S -0.3% W -0.3%2024 S -0.5% W -0.5
|  |  | Latest Peak Compensated Load | [5 empty] | 2.4 MVA on 26/11/2019 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 14.6 | 14.6 | 14.6 |  | 14.6 |  | 14.6 | 16.3 |  | 16.3 |  | 16.3 | 16.3 | 16.3
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 2.6 | 2.6 | 2.6 |  | 2.6 |  | 2.6 | 1.6 |  | 1.6 |  | 1.5 | 1.5 | 1.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.992 | 0.992 | 0.992 |  | 0.992 |  | 0.992 | 0.952 |  | 0.952 |  | 0.952 | 0.952 | 0.952
|  |  |  | ECC Rating (MVA) |  | 8.5 | 8.5 | 8.5 |  | 8.5 |  | 8.5 | 9.4 |  | 9.4 |  | 9.4 | 9.4 | 9.4
|  |  |  | 50 PoE Load (MVA) |  | 2.4 | 2.4 | 2.4 |  | 2.4 |  | 2.4 | 1.5 |  | 1.5 |  | 1.5 | 1.5 | 1.5
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 724.5 | 724.5 | 724.5 |  | 724.5 |  | 724.5 | 724.5 |  | 724.5 |  | 724.5 | 724.5 | 724.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## ROEA
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | ROEA - Roma East (33/11kV) | [8 empty] | Supply |  | T083 - Roma 33kV BSP
| Description |  |  |  | Region is South West
Transformer size is 2x33/11kV 6.3MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.7%, 2021 S -0.2% W -0.2%2022 S -0.5% W -0.5%2023 S -0.3% W -0.3%2024 S -0.3% W -0.3
|  |  | Latest Peak Compensated Load | [5 empty] | 9.3 MVA on 11/12/2019 at 15:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 14 | 14 | 14 |  | 14 |  | 14 | 17.5 |  | 17.5 |  | 17.5 | 17.5 | 17.5
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 11.1 | 11.1 | 11.1 |  | 11.1 |  | 11.1 | 8.5 |  | 8.4 |  | 8.3 | 8.3 | 8.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.961 | 0.961 | 0.961 |  | 0.961 |  | 0.961 | 0.97 |  | 0.969 |  | 0.969 | 0.97 | 0.969
|  |  |  | ECC Rating (MVA) |  | 8 | 8 | 8 |  | 8 |  | 8 | 9.4 |  | 9.4 |  | 9.4 | 9.4 | 9.4
|  |  |  | 50 PoE Load (MVA) |  | 10.2 | 10.1 | 10.1 |  | 10.1 |  | 10.1 | 7.9 |  | 7.8 |  | 7.7 | 7.7 | 7.7
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  |  | Hours PA > 95% Peak Load |  | 23 | 23 | 23 |  | 23 |  | 23 | 23 |  | 23 |  | 23 | 23 | 23
|  |  |  | Raw LAR (MVA) |  | 2.2 | 2.1 | 2.1 |  | 2.1 |  | 2.1
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 | 2 | 2
|  |  |  | Mobile Plant Avail (MVA) |  | 11.5 | 11.5 | 11.5 |  | 11.5 |  | 11.5 | 11.5 |  | 11.5 |  | 11.5 | 11.5 | 11.5
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## ROGL
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | ROGL - Rockhampton Glenmore (66/11kV) | [8 empty] | Supply |  | RMES - Rockhampton Mesh
| Description |  |  |  | Region is Capricornia
Transformer size is 1x25MVA 66kV Transformer;2x66/11kV 20/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.3%, 2021 S -0.2% W -0.2%2022 S -0.5% W -0.5%2023 S -0.2% W -0.2%2024 S -0.3% W -0.3
|  |  | Latest Peak Compensated Load | [5 empty] | 21.1 MVA on 16/12/2019 at 16:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 81.4 | 81.4 | 81.4 |  | 81.4 |  | 81.4 | 82.5 |  | 82.5 |  | 82.5 | 82.5 | 82.5
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 22.9 | 22.8 | 22.7 |  | 22.8 |  | 22.8 | 12.4 |  | 12.3 |  | 12.2 | 12.1 | 12.1
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.994 | 0.994 | 0.995 |  | 0.994 |  | 0.994 | 0.959 |  | 0.959 |  | 0.959 | 0.959 | 0.959
|  |  |  | ECC Rating (MVA) |  | 57.5 | 57.5 | 57.5 |  | 57.5 |  | 57.5 | 65 |  | 65 |  | 65 | 65 | 65
|  |  |  | 50 PoE Load (MVA) |  | 20.5 | 20.4 | 20.4 |  | 20.4 |  | 20.4 | 12.1 |  | 12.1 |  | 11.9 | 11.9 | 11.9
|  |  |  | 50 PoE Load > 95% (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  |  | Hours PA > 95% Peak Load |  | 9.5 | 9.5 | 9.5 |  | 9.5 |  | 9.5 | 9.5 |  | 9.5 |  | 9.5 | 9.5 | 9.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## ROLE
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | ROLE - Rolleston (66/22kV) | [8 empty] | Supply |  | T163 - Rolleston BSP
| Description |  |  |  | Region is Capricornia
Transformer size is 2x12.5 MVA
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.5%, 2021 S -0.0% W -0.0%2022 S -0.1% W -0.1%2023 S 0.0% W 0.0%, 2024 S -0.1% W -0.1
|  |  | Latest Peak Compensated Load | [5 empty] | 7.1 MVA on 16/12/2019 at 17:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 25 | 25 | 25 |  | 25 |  | 25 | 25 |  | 25 |  | 25 | 25 | 25
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 7.9 | 7.9 | 7.9 |  | 7.9 |  | 7.9 | 6.3 |  | 6.3 |  | 6.2 | 6.2 | 6.2
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.996 | 0.996 | 0.996 |  | 0.996 |  | 0.996 | 0.998 |  | 0.998 |  | 0.998 | 0.998 | 0.998
|  |  |  | ECC Rating (MVA) |  | 12.5 | 12.5 | 12.5 |  | 12.5 |  | 12.5 | 12.5 |  | 12.5 |  | 12.5 | 12.5 | 12.5
|  |  |  | 50 PoE Load (MVA) |  | 7.2 | 7.2 | 7.2 |  | 7.2 |  | 7.3 | 5.9 |  | 5.9 |  | 5.9 | 5.9 | 5.9
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.4 | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Hours PA > 95% Peak Load |  | 6 | 6 | 6 |  | 6 |  | 6 | 6 |  | 6 |  | 6 | 6 | 6
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## ROLL
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | ROLL - Rollingstone (66/11kV) | [8 empty] | Supply |  | TMES - Townsville Mesh
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/11kV 2.5/2.9MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 1.3%, 2021 S 0.5% W 0.5%, 2022 S 0.3% W 0.3%, 2023 S 0.5% W 0.5%, 2024 S 0.2% W 0.2%
|  |  | Latest Peak Compensated Load | [5 empty] | 1.4 MVA on 15/02/2020 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 4.3 | 4.3 | 4.3 |  | 4.3 |  | 4.3 | 4.3 |  | 4.3 |  | 4.3 | 4.3 | 4.3
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 1.6 | 1.6 | 1.6 |  | 1.6 |  | 1.6 | 1.1 |  | 1.1 |  | 1.1 | 1.1 | 1.1
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.982 | 0.982 | 0.982 |  | 0.982 |  | 0.982 | 0.99 |  | 0.99 |  | 0.99 | 0.99 | 0.99
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 1.4 | 1.4 | 1.4 |  | 1.4 |  | 1.4 | 1.1 |  | 1.1 |  | 1.1 | 1.1 | 1.1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 3.5 | 3.5 | 3.5 |  | 3.5 |  | 3.5 | 3.5 |  | 3.5 |  | 3.5 | 3.5 | 3.5
|  |  |  | Raw LAR (MVA) |  | 1.4 | 1.4 | 1.4 |  | 1.4 |  | 1.4 | 1.1 |  | 1.1 |  | 1.1 | 1.1 | 1.1
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 | 2 | 2
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## ROMA
Bulk Summary Information and Peak Load Forecast
Substation |  |  |  | ROMA - Roma 66kV BSP (132/66kV) | [8 empty] | Supply |  | T194 - Columboola TCP
Description |  |  |  | Region is South West
Transformer size is 1x132/66/11kV 60/80MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
|  | Latest Peak Compensated Load | [5 empty] | 32.2 MVA on 16/02/2020 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[5 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  | NCC Rating (MVA) |  | 101.4 | 101.4 | 101.4 |  | 101.4 |  | 101.4 | 119.6 |  | 119.6 |  | 119.6 | 119.6 | 119.6
|  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | 10 PoE Load (MVA) |  | 36 | 36 | 36 |  | 36.1 |  | 36.2 | 27.6 |  | 27.5 |  | 27.3 | 27.2 | 27.3
LARn (MVA)
LARn (MW)
|  |  | Power Factor at Peak Load |  | 0.978 | 0.978 | 0.978 |  | 0.978 |  | 0.978 | 0.955 |  | 0.955 |  | 0.955 | 0.955 | 0.955
|  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | 50 PoE Load (MVA) |  | 32.5 | 32.5 | 32.5 |  | 32.6 |  | 32.6 | 26 |  | 25.9 |  | 25.7 | 25.6 | 25.7
|  |  | 50 PoE Load > 95% (MVA) |  | 1.6 | 1.6 | 1.6 |  | 1.6 |  | 1.6 | 1.3 |  | 1.3 |  | 1.3 | 1.3 | 1.3
|  |  | Hours PA > 95% Peak Load |  | 36 | 36 | 36 |  | 36 |  | 36 | 36 |  | 36 |  | 36 | 36 | 36
|  |  | Raw LAR (MVA) |  | 32.5 | 32.5 | 32.5 |  | 32.6 |  | 32.6 | 26 |  | 25.9 |  | 25.7 | 25.6 | 25.7
|  |  | Auto Trans Avail (MVA) |  | 50 | 50 | 50 |  | 50 |  | 50 | 50 |  | 50 |  | 50 | 50 | 50
|  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## ROPL
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | ROPL - Ross Plains (66/11kV) | [8 empty] | Supply |  | TMES - Townsville Mesh
| Description |  |  |  | Region is Nth Queensland
Transformer size is 2x66/11kV 12/15MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.1%, 2021 S 0.0% W 0.0%, 2022 S -0.1% W -0.1%2023 S -0.1% W -0.1%2024 S -0.2% W -0.2
|  |  | Latest Peak Compensated Load | [5 empty] | 16.4 MVA on 02/02/2020 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 33 | 33 | 33 |  | 33 |  | 33 | 37.8 |  | 37.8 |  | 37.8 | 37.8 | 37.8
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 17.1 | 17.1 | 17.1 |  | 17.1 |  | 17.1 | 8.2 |  | 8.2 |  | 8.1 | 8.1 | 8.1
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 1 | 1 | 1 |  | 1 |  | 1 | 0.995 |  | 0.995 |  | 0.995 | 0.995 | 0.995
|  |  |  | ECC Rating (MVA) |  | 19.2 | 19.2 | 19.2 |  | 19.2 |  | 19.2 | 20.8 |  | 20.8 |  | 20.8 | 20.8 | 20.8
|  |  |  | 50 PoE Load (MVA) |  | 15 | 14.9 | 14.9 |  | 15 |  | 15 | 8.1 |  | 8 |  | 8 | 7.9 | 8
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.8 | 0.7 | 0.7 |  | 0.8 |  | 0.8 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  |  | Hours PA > 95% Peak Load |  | 7 | 7 | 7 |  | 7 |  | 7 | 7 |  | 7 |  | 7 | 7 | 7
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## ROSE
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | ROSE - Rosella (33/11kV) | [8 empty] | Supply |  | T065 - Alligator Creek BSP
| Description |  |  |  | Region is Mackay
Transformer size is 2x33/11kV 4.5MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.4%, 2021 S 0.2% W 0.2%, 2022 S -0.1% W -0.1%2023 S 0.2% W 0.2%, 2024 S -0.1% W -0.1
|  |  | Latest Peak Compensated Load | [5 empty] | 6.4 MVA on 04/12/2019 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 11.5 | 11.5 | 11.5 |  | 11.5 |  | 11.5 | 12.3 |  | 12.3 |  | 12.3 | 12.3 | 12.3
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 8 | 8 | 8.1 |  | 8.1 |  | 8.1 | 4.8 |  | 4.8 |  | 4.7 | 4.7 | 4.7
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.96 | 0.96 | 0.96 |  | 0.96 |  | 0.96 | 0.962 |  | 0.962 |  | 0.962 | 0.962 | 0.962
|  |  |  | ECC Rating (MVA) |  | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6 | 6.7 |  | 6.7 |  | 6.7 | 6.7 | 6.7
|  |  |  | 50 PoE Load (MVA) |  | 7.1 | 7.1 | 7.1 |  | 7.2 |  | 7.2 | 4.7 |  | 4.7 |  | 4.6 | 4.6 | 4.6
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.4 | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 9.5 | 9.5 | 9.5 |  | 9.5 |  | 9.5 | 9.5 |  | 9.5 |  | 9.5 | 9.5 | 9.5
|  |  |  | Raw LAR (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.6 |  | 0.6
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 1.6 | 1.6 | 1.6 |  | 1.6 |  | 1.6 | 1.6 |  | 1.6 |  | 1.6 | 1.6 | 1.6
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 1.2 | 1.2 | 1.2 |  | 1.2 |  | 1.2 | 1.2 |  | 1.2 |  | 1.2 | 1.2 | 1.2
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## ROSO
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | ROSO - Rockhampton South (66/11kV) | [8 empty] | Supply |  | RMES - Rockhampton Mesh
| Description |  |  |  | Region is Capricornia
Transformer size is 2x66/11kV 15/20MVA ONAN/OFDAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.7%, 2021 S -0.8% W -0.8%2022 S -1.2% W -1.2%2023 S -0.9% W -0.9%2024 S -0.6% W -0.6
|  |  | Latest Peak Compensated Load | [5 empty] | 15.2 MVA on 21/01/2020 at 14:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 32.7 | 32.7 | 32.7 |  | 32.7 |  | 32.7 | 32.7 |  | 32.7 |  | 32.7 | 32.7 | 32.7
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 16.4 | 16.2 | 16 |  | 16 |  | 16 | 8.8 |  | 8.7 |  | 8.6 | 8.4 | 8.4
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.907 | 0.907 | 0.907 |  | 0.907 |  | 0.907 | 0.899 |  | 0.899 |  | 0.899 | 0.899 | 0.899
|  |  |  | ECC Rating (MVA) |  | 16.5 | 16.5 | 16.5 |  | 16.5 |  | 16.5 | 18 |  | 18 |  | 18 | 18 | 18
|  |  |  | 50 PoE Load (MVA) |  | 15.2 | 15.1 | 14.9 |  | 14.9 |  | 14.9 | 8.5 |  | 8.4 |  | 8.2 | 8.1 | 8.1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.8 | 0.8 | 0.7 |  | 0.7 |  | 0.7 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  |  | Hours PA > 95% Peak Load |  | 11.5 | 11.5 | 11.5 |  | 11.5 |  | 11.5 | 11.5 |  | 11.5 |  | 11.5 | 11.5 | 11.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## ROST
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | ROST - Rocky Street (66/11kV) | [8 empty] | Supply |  | MARY - Maryborough BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 2x66/11kV 15/20/25MVA ONAN/ONAF/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.2%, 2021 S -0.1% W -0.1%2022 S 0.2% W 0.2%, 2023 S 0.3% W 0.3%, 2024 S 0.0% W 0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 20.2 MVA on 02/12/2019 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 57.5 | 57.5 | 57.5 |  | 57.5 |  | 57.5 | 64.3 |  | 64.3 |  | 64.3 | 64.3 | 64.3
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 23.2 | 23.3 | 23.4 |  | 23.5 |  | 23.5 | 19.3 |  | 19.2 |  | 19.1 | 19.1 | 19.1
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.999 | 0.999 | 0.998 |  | 0.998 |  | 0.998 | 0.998 |  | 0.998 |  | 0.998 | 0.998 | 0.998
|  |  |  | ECC Rating (MVA) |  | 32.1 | 32.1 | 32.1 |  | 32.1 |  | 32.1 | 36.1 |  | 36.1 |  | 36.1 | 36.1 | 36.1
|  |  |  | 50 PoE Load (MVA) |  | 21.4 | 21.4 | 21.5 |  | 21.6 |  | 21.7 | 18.3 |  | 18.2 |  | 18.1 | 18.1 | 18.2
|  |  |  | 50 PoE Load > 95% (MVA) |  | 1.1 | 1.1 | 1.1 |  | 1.1 |  | 1.1 | 0.9 |  | 0.9 |  | 0.9 | 0.9 | 0.9
|  |  |  | Hours PA > 95% Peak Load |  | 10.5 | 10.5 | 10.5 |  | 10.5 |  | 10.5 | 10.5 |  | 10.5 |  | 10.5 | 10.5 | 10.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## ROWE
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | ROWE - Roma West (33/11kV) | [8 empty] | Supply |  | T083 - Roma 33kV BSP
| Description |  |  |  | Region is South West
Transformer size is 1x33/11kV 2.5MVA ONAN;1xROWESS T1 33KV TRANSF 1 TRANSF T1
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.8%, 2021 S 0.1% W 0.1%, 2022 S -0.1% W -0.1%2023 S 0.0% W 0.0%, 2024 S 0.0% W 0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 4.3 MVA on 20/11/2019 at 16:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 6.3 | 6.3 | 6.3 |  | 6.3 |  | 6.3 | 6.3 |  | 6.3 |  | 6.3 | 6.3 | 6.3
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 5.3 | 5.3 | 5.3 |  | 5.4 |  | 5.4 | 4.5 |  | 4.5 |  | 4.4 | 4.4 | 4.4
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.963 | 0.963 | 0.963 |  | 0.963 |  | 0.963 | 0.988 |  | 0.988 |  | 0.988 | 0.988 | 0.988
|  |  |  | ECC Rating (MVA) |  | 3.2 | 3.2 | 3.2 |  | 3.2 |  | 3.2 | 3.2 |  | 3.2 |  | 3.2 | 3.2 | 3.2
|  |  |  | 50 PoE Load (MVA) |  | 4.8 | 4.8 | 4.8 |  | 4.8 |  | 4.8 | 4.1 |  | 4.1 |  | 4.1 | 4 | 4.1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 18 | 18 | 18 |  | 18 |  | 18 | 18 |  | 18 |  | 18 | 18 | 18
|  |  |  | Raw LAR (MVA) |  | 1.6 | 1.6 | 1.6 |  | 1.6 |  | 1.6 | 0.9 |  | 0.9 |  | 0.9 | 0.8 | 0.9
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 4 | 4 | 4 |  | 4 |  | 4 | 4 |  | 4 |  | 4 | 4 | 4
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## ROWO
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | ROWO - Roo Works (33/11kV) | [8 empty] | Supply |  | SGZA - St George ZS Accumulator
| Description |  |  |  | Region is South West
Transformer size is 1x33/11kV 2MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.2%, 2021 S -0.1% W -0.1%2022 S -0.2% W -0.2%2023 S -0.2% W -0.2%2024 S -0.3% W -0.3
|  |  | Latest Peak Compensated Load | [5 empty] | 1.1 MVA on 18/02/2020 at 14:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 2.4 | 2.4 | 2.4 |  | 2.4 |  | 2.4 | 2.4 |  | 2.4 |  | 2.4 | 2.4 | 2.4
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 1.4 | 1.4 | 1.4 |  | 1.4 |  | 1.4 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.927 | 0.927 | 0.927 |  | 0.927 |  | 0.927 | 0.968 |  | 0.968 |  | 0.968 | 0.968 | 0.968
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 1.1 | 1.1 | 1.1 |  | 1.1 |  | 1.1 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 20.5 | 20.5 | 20.5 |  | 20.5 |  | 20.5 | 20.5 |  | 20.5 |  | 20.5 | 20.5 | 20.5
|  |  |  | Raw LAR (MVA) |  | 1.1 | 1.1 | 1.1 |  | 1.1 |  | 1.1 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 1.2 | 1.2 | 1.2 |  | 1.2 |  | 1.2 | 1.2 |  | 1.2 |  | 1.2 | 1.2 | 1.2
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## SAGE
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | SAGE - St. George (66/33kV) | [8 empty] | Supply |  | ROMA - Roma 66kV BSP
| Description |  |  |  | Region is South West
Transformer size is 2x66/33/11kV 20MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.1%, 2021 S -0.1% W -0.1%2022 S -0.1% W -0.1%2023 S -0.1% W -0.1%2024 S -0.2% W -0.2
|  |  | Latest Peak Compensated Load | [5 empty] | 11.3 MVA on 02/03/2020 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 48.7 | 48.7 | 48.7 |  | 48.7 |  | 48.7 | 55.9 |  | 55.9 |  | 55.9 | 55.9 | 55.9
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 13.2 | 13.2 | 13.2 |  | 13.3 |  | 13.3 | 11.5 |  | 11.4 |  | 11.4 | 11.3 | 11.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.931 | 0.931 | 0.931 |  | 0.931 |  | 0.931 | 0.953 |  | 0.953 |  | 0.953 | 0.953 | 0.953
|  |  |  | ECC Rating (MVA) |  | 27.6 | 27.6 | 27.6 |  | 27.6 |  | 27.6 | 29.9 |  | 29.9 |  | 29.9 | 29.9 | 29.9
|  |  |  | 50 PoE Load (MVA) |  | 11.8 | 11.8 | 11.8 |  | 11.8 |  | 11.8 | 10.8 |  | 10.8 |  | 10.7 | 10.6 | 10.7
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | Hours PA > 95% Peak Load |  | 18 | 18 | 18 |  | 18 |  | 18 | 18 |  | 18 |  | 18 | 18 | 18
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## SAGT
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | SAGT - St. George Town (33/11kV) | [8 empty] | Supply |  | SGZA - St George ZS Accumulator
| Description |  |  |  | Region is South West
Transformer size is 2x33/11kV 3MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.8%, 2021 S -0.5% W -0.5%2022 S -0.5% W -0.5%2023 S -0.2% W -0.2%2024 S -0.4% W -0.4
|  |  | Latest Peak Compensated Load | [5 empty] | 4.9 MVA on 30/01/2020 at 15:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 6.6 | 6.6 | 6.6 |  | 6.6 |  | 6.6 | 6.6 |  | 6.6 |  | 6.6 | 6.6 | 6.6
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 5.7 | 5.7 | 5.7 |  | 5.7 |  | 5.7 | 4.2 |  | 4.2 |  | 4.1 | 4.1 | 4.1
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.958 | 0.958 | 0.958 |  | 0.958 |  | 0.958 | 0.964 |  | 0.964 |  | 0.964 | 0.964 | 0.964
|  |  |  | ECC Rating (MVA) |  | 3.5 | 3.5 | 3.5 |  | 3.5 |  | 3.5 | 3.6 |  | 3.6 |  | 3.6 | 3.6 | 3.6
|  |  |  | 50 PoE Load (MVA) |  | 5.1 | 5.1 | 5.1 |  | 5.1 |  | 5.1 | 4 |  | 3.9 |  | 3.9 | 3.9 | 3.9
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 12.5 | 12.5 | 12.5 |  | 12.5 |  | 12.5 | 12.5 |  | 12.5 |  | 12.5 | 12.5 | 12.5
|  |  |  | Raw LAR (MVA) |  | 1.6 | 1.6 | 1.6 |  | 1.6 |  | 1.6 | 0.4 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0.8 | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.8 |  | 0.8 |  | 0.8 | 0.8 | 0.8
|  |  |  | Mobile Plant Avail (MVA) |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## SARI
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | SARI - Sarina (33/11kV) | [8 empty] | Supply |  | T065 - Alligator Creek BSP
| Description |  |  |  | Region is Mackay
Transformer size is 2x33/11kV 10/12.5MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 17.5 MVA
Growth Rates |  |  |  |  | 2020 W 0.4%, 2021 S 0.7% W 0.7%, 2022 S 0.5% W 0.5%, 2023 S 0.7% W 0.7%, 2024 S 0.4% W 0.4%
|  |  | Latest Peak Compensated Load | [5 empty] | 13.9 MVA on 17/02/2020 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 24 | 24 | 24 |  | 24 |  | 24 | 26.8 |  | 26.8 |  | 26.8 | 26.8 | 26.8
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 16.3 | 16.4 | 16.5 |  | 16.6 |  | 16.8 | 11.9 |  | 11.9 |  | 11.9 | 11.9 | 12
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.971 | 0.971 | 0.971 |  | 0.971 |  | 0.971 | 0.981 |  | 0.981 |  | 0.981 | 0.981 | 0.981
|  |  |  | ECC Rating (MVA) |  | 13.7 | 13.7 | 13.7 |  | 13.7 |  | 13.7 | 14.9 |  | 14.9 |  | 14.9 | 14.9 | 14.9
|  |  |  | 50 PoE Load (MVA) |  | 14.8 | 14.9 | 15 |  | 15.1 |  | 15.3 | 11.6 |  | 11.6 |  | 11.6 | 11.6 | 11.7
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.7 | 0.7 | 0.8 |  | 0.8 |  | 0.8 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  |  | Hours PA > 95% Peak Load |  | 16 | 16 | 16 |  | 16 |  | 16 | 16 |  | 16 |  | 16 | 16 | 16
|  |  |  | Raw LAR (MVA) |  | 1.1 | 1.2 | 1.3 |  | 1.4 |  | 1.6
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 1.1 | 1.1 | 1.1 |  | 1.1 |  | 1.1 | 1.1 |  | 1.1 |  | 1.1 | 1.1 | 1.1
|  |  |  | Mobile Plant Avail (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## SAUN
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | SAUN - Saunders (66/11kV) | [8 empty] | Supply |  | TMES - Townsville Mesh
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/11kV 4MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.1%, 2021 S 0.2% W 0.2%, 2022 S 0.1% W 0.1%, 2023 S 0.2% W 0.2%, 2024 S 0.0% W 0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 1.4 MVA on 21/01/2020 at 13:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 5.1 | 5.1 | 5.1 |  | 5.1 |  | 5.1 | 5.4 |  | 5.4 |  | 5.4 | 5.4 | 5.4
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 1.7 | 1.7 | 1.7 |  | 1.7 |  | 1.7 | 1.3 |  | 1.3 |  | 1.3 | 1.3 | 1.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.946 | 0.946 | 0.946 |  | 0.946 |  | 0.946 | 0.847 |  | 0.847 |  | 0.847 | 0.847 | 0.847
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 1.5 | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.2 |  | 1.2 |  | 1.2 | 1.2 | 1.2
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 21 | 21 | 21 |  | 21 |  | 21 | 21 |  | 21 |  | 21 | 21 | 21
|  |  |  | Raw LAR (MVA) |  | 1.5 | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.2 |  | 1.2 |  | 1.2 | 1.2 | 1.2
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 2.7 | 2.7 | 2.7 |  | 2.7 |  | 2.7 | 2.7 |  | 2.7 |  | 2.7 | 2.7 | 2.7
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## SHUT
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | SHUT - Shutehaven (66/22kV) | [8 empty] | Supply |  | PROS - Proserpine BSP
| Description |  |  |  | Region is Mackay
Transformer size is 1x66/22kV 15/20/25MVA ONAN/ONAF/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.4%, 2021 S 0.0% W 0.0%, 2022 S -0.2% W -0.2%2023 S 0.3% W 0.3%, 2024 S -0.4% W -0.4
|  |  | Latest Peak Compensated Load | [5 empty] | 9.2 MVA on 20/01/2020 at 16:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 30.4 | 30.4 | 30.4 |  | 30.4 |  | 30.4 | 33.2 |  | 33.2 |  | 33.2 | 33.2 | 33.2
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 10.1 | 10.1 | 10.2 |  | 10.2 |  | 10.2 | 5.6 |  | 5.6 |  | 5.5 | 5.5 | 5.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.993 | 0.993 | 0.993 |  | 0.993 |  | 0.993 | 0.997 |  | 0.997 |  | 0.997 | 0.997 | 0.997
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 9.4 | 9.4 | 9.4 |  | 9.4 |  | 9.4 | 5.5 |  | 5.4 |  | 5.4 | 5.4 | 5.4
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Hours PA > 95% Peak Load |  | 17 | 17 | 17 |  | 17 |  | 17 | 17 |  | 17 |  | 17 | 17 | 17
|  |  |  | Raw LAR (MVA) |  | 9.4 | 9.4 | 9.4 |  | 9.4 |  | 9.4 | 5.5 |  | 5.4 |  | 5.4 | 5.4 | 5.4
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 13.3 | 13.3 | 13.3 |  | 13.3 |  | 13.3 | 13.3 |  | 13.3 |  | 13.3 | 13.3 | 13.3
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## SKIE
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | SKIE - Skid E (Chinchilla) (33/11kV) | [8 empty] | Supply |  | CHIN - Chinchilla BSP
| Description |  |  |  | Region is South West
Transformer size is 1xSkid 33/11kV 5MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.7%, 2021 S 0.7% W 0.7%, 2022 S 0.6% W 0.6%, 2023 S 0.7% W 0.7%, 2024 S 0.5% W 0.5%
|  |  | Latest Peak Compensated Load | [5 empty] | 5.6 MVA on 16/12/2019 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 6 | 6 | 6 |  | 6 |  | 6 | 6 |  | 6 |  | 6 | 6 | 6
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 6.5 | 6.6 | 6.6 |  | 6.7 |  | 6.7 | 5.2 |  | 5.2 |  | 5.2 | 5.2 | 5.3
|  |  |  | LARn (MVA) |  | 0.5 | 0.6 | 0.6 |  | 0.7 |  | 0.7
|  |  |  | LARn (MW) |  | 0.5 | 0.6 | 0.6 |  | 0.7 |  | 0.7
|  |  |  | Power Factor at Peak Load |  | 0.983 | 0.983 | 0.983 |  | 0.983 |  | 0.983 | 0.988 |  | 0.988 |  | 0.988 | 0.988 | 0.988
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 5.8 | 5.8 | 5.9 |  | 5.9 |  | 6 | 4.8 |  | 4.8 |  | 4.8 | 4.8 | 4.9
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 6 | 6 | 6 |  | 6 |  | 6 | 6 |  | 6 |  | 6 | 6 | 6
|  |  |  | Raw LAR (MVA) |  | 5.8 | 5.8 | 5.9 |  | 5.9 |  | 6 | 4.8 |  | 4.8 |  | 4.8 | 4.8 | 4.9
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 2.2 | 2.2 | 2.2 |  | 2.2 |  | 2.2 | 2.2 |  | 2.2 |  | 2.2 | 2.2 | 2.2
|  |  |  | Mobile Plant Avail (MVA) |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | No | No | No |  | No |  | No | Yes |  | Yes |  | Yes | Yes | Yes
Note: Cyclic overload is accepted as substation load is a short duration evening peak
Return to Index

## SOBL
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | SOBL - South Blackwater (66/22kV) | [8 empty] | Supply |  | T032 - Blackwater BSP
| Description |  |  |  | Region is Capricornia
Transformer size is 1x66/22kV 0.3MVA ON
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.1%, 2021 S -0.1% W -0.1%2022 S -0.2% W -0.2%2023 S -0.0% W -0.0%2024 S -0.3% W -0.3
|  |  | Latest Peak Compensated Load | [5 empty] | 0.4 MVA on 16/12/2019 at 19:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | LARn (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2
|  |  |  | LARn (MW) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2
|  |  |  | Power Factor at Peak Load |  | 0.847 | 0.847 | 0.847 |  | 0.847 |  | 0.847 | 0.848 |  | 0.848 |  | 0.848 | 0.848 | 0.848
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 6 | 6 | 6 |  | 6 |  | 6 | 6 |  | 6 |  | 6 | 6 | 6
|  |  |  | Raw LAR (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Mobile Plant Avail (MVA) |  | 0.4 | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Note: System spare is kept on hand and some additional overloading is accepted in this case
Return to Index

## SOBU
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | SOBU - South Bundaberg (66/11kV) | [8 empty] | Supply |  | BUND - Bundaberg BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 2x66/11kV 14/19MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.7%, 2021 S 0.7% W 0.7%, 2022 S 0.5% W 0.5%, 2023 S 0.7% W 0.7%, 2024 S 0.4% W 0.4%
|  |  | Latest Peak Compensated Load | [5 empty] | 12.5 MVA on 09/12/2019 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 42.4 | 42.4 | 42.4 |  | 42.4 |  | 42.4 | 46.6 |  | 46.6 |  | 46.6 | 46.6 | 46.6
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 14.1 | 14.1 | 14.3 |  | 14.4 |  | 14.5 | 10 |  | 10.1 |  | 10 | 10.1 | 10.2
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.999 | 0.999 | 0.999 |  | 0.999 |  | 0.999 | 0.997 |  | 0.997 |  | 0.997 | 0.997 | 0.997
|  |  |  | ECC Rating (MVA) |  | 24.2 | 24.2 | 24.2 |  | 24.2 |  | 24.2 | 25.4 |  | 25.4 |  | 25.4 | 25.4 | 25.4
|  |  |  | 50 PoE Load (MVA) |  | 12.7 | 12.8 | 12.9 |  | 13 |  | 13.1 | 9.6 |  | 9.7 |  | 9.6 | 9.7 | 9.8
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.7 |  | 0.7 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | Hours PA > 95% Peak Load |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## SOKO
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | SOKO - South Kolan (66/11kV) | [8 empty] | Supply |  | BUND - Bundaberg BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 2x66/11kV 7.5/10MVA ON/ONB
Capacity of commissioned Embedded Generation (with Connection Agreements) is 1.0 MVA
Growth Rates |  |  |  |  | 2020 W -1.8%, 2021 S 0.5% W 0.5%, 2022 S 0.3% W 0.3%, 2023 S 0.4% W 0.4%, 2024 S 0.2% W 0.2%
|  |  | Latest Peak Compensated Load | [5 empty] | 5.4 MVA on 21/12/2019 at 19:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 27.5 | 27.5 | 27.5 |  | 27.5 |  | 27.5 | 29.9 |  | 29.9 |  | 29.9 | 29.9 | 29.9
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 6.6 | 6.9 | 6.9 |  | 7 |  | 7 | 4 |  | 4.3 |  | 4.5 | 4.5 | 4.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.955 | 0.955 | 0.955 |  | 0.955 |  | 0.955 | 0.956 |  | 0.956 |  | 0.956 | 0.956 | 0.956
|  |  |  | ECC Rating (MVA) |  | 15 | 15 | 15 |  | 15 |  | 15 | 15 |  | 15 |  | 15 | 15 | 15
|  |  |  | 50 PoE Load (MVA) |  | 5.8 | 6.2 | 6.2 |  | 6.2 |  | 6.3 | 3.8 |  | 4 |  | 4.2 | 4.2 | 4.2
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 7 | 7 | 7 |  | 7 |  | 7 | 7 |  | 7 |  | 7 | 7 | 7
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## SOMA
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | SOMA - South Mackay (33/11kV) | [8 empty] | Supply |  | MACK - Mackay BSP
| Description |  |  |  | Region is Mackay
Transformer size is 1x33/11kV 12.5/15/20MVA ONAN/ONAF/ODAF;1x33/11kV 12.5/15/21MVA ONAN/ONAF/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 2.4 MVA
Growth Rates |  |  |  |  | 2020 W -0.3%, 2021 S -1.2% W -1.2%2022 S -1.9% W -1.9%2023 S -1.7% W -1.7%2024 S -1.2% W -1.2
|  |  | Latest Peak Compensated Load | [5 empty] | 18.4 MVA on 23/01/2020 at 14:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 40 | 40 | 40 |  | 40 |  | 40 | 40 |  | 40 |  | 40 | 40 | 40
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 19.6 | 19.2 | 18.9 |  | 18.8 |  | 18.6 | 14.9 |  | 15.3 |  | 14.9 | 14.6 | 14.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.994 | 0.995 | 0.995 |  | 0.995 |  | 0.995 | 0.954 |  | 0.945 |  | 0.945 | 0.945 | 0.945
|  |  |  | ECC Rating (MVA) |  | 21 | 21 | 21 |  | 21 |  | 21 | 22 |  | 22 |  | 22 | 22 | 22
|  |  |  | 50 PoE Load (MVA) |  | 18.4 | 18.1 | 17.8 |  | 17.6 |  | 17.5 | 14.7 |  | 15.1 |  | 14.7 | 14.4 | 14.3
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.9 | 0.9 | 0.9 |  | 0.9 |  | 0.9 | 0.7 |  | 0.8 |  | 0.7 | 0.7 | 0.7
|  |  |  | Hours PA > 95% Peak Load |  | 46.5 | 46.5 | 46.5 |  | 46.5 |  | 46.5 | 46.5 |  | 46.5 |  | 46.5 | 46.5 | 46.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 1.8 | 1.8 | 1.8 |  | 1.8 |  | 1.8 | 1.8 |  | 1.8 |  | 1.8 | 1.8 | 1.8
|  |  |  | Mobile Plant Avail (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 | 2 | 2
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## SOTO
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | SOTO - South Toowoomba (33/11kV) | [8 empty] | Supply |  | T043 - South Toowoomba BSP
| Description |  |  |  | Region is South West
Transformer size is 3x33/11kV 11.5MVA ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.3%, 2021 S 0.9% W 0.9%, 2022 S 0.7% W 0.7%, 2023 S 0.9% W 0.9%, 2024 S 0.6% W 0.6%
|  |  | Latest Peak Compensated Load | [5 empty] | 25.7 MVA on 04/06/2019 at 20:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 37.4 | 37.4 | 37.4 |  | 37.4 |  | 37.4 | 42.4 |  | 42.4 |  | 42.4 | 42.4 | 42.4
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 23.2 | 23.4 | 23.6 |  | 23.9 |  | 24.1 | 26.7 |  | 26.9 |  | 26.9 | 27 | 27.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.967 | 0.967 | 0.967 |  | 0.967 |  | 0.967 | 0.981 |  | 0.981 |  | 0.981 | 0.981 | 0.981
|  |  |  | ECC Rating (MVA) |  | 28.3 | 28.3 | 28.3 |  | 28.3 |  | 28.3 | 31.2 |  | 31.2 |  | 31.2 | 31.2 | 31.2
|  |  |  | 50 PoE Load (MVA) |  | 20.9 | 21.1 | 21.2 |  | 21.5 |  | 21.7 | 24.7 |  | 24.8 |  | 24.9 | 25 | 25.2
|  |  |  | 50 PoE Load > 95% (MVA) |  | 1 | 1.1 | 1.1 |  | 1.1 |  | 1.1 | 1.2 |  | 1.2 |  | 1.2 | 1.3 | 1.3
|  |  |  | Hours PA > 95% Peak Load |  | 4 | 4 | 4 |  | 4 |  | 4 | 4 |  | 4 |  | 4 | 4 | 4
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## STAM
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | STAM - Stamford (66/33kV) | [8 empty] | Supply |  | T095 - Millchester BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/33/19kV 0.63MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.8%, 2021 S -0.3% W -0.3%2022 S -0.4% W -0.4%2023 S -0.3% W -0.3%2024 S -0.5% W -0.5
|  |  | Latest Peak Compensated Load | [5 empty] | 0.3 MVA on 05/07/2019 at 21:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 0.7 | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.7 | 0.7
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.3 |  | 0.3 |  | 0.3 | 0.2 | 0.2
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.907 | 0.907 | 0.907 |  | 0.907 |  | 0.907 | 0.758 |  | 0.758 |  | 0.758 | 0.739 | 0.739
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.3 |  | 0.3 |  | 0.3 | 0.2 | 0.2
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 4 | 4 | 4 |  | 4 |  | 4 | 4 |  | 4 |  | 4 | 4 | 4
|  |  |  | Raw LAR (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.3 |  | 0.3 |  | 0.3 | 0.2 | 0.2
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## STAN
Bulk Summary Information and Peak Load Forecast
Substation |  |  |  | STAN - Stanthorpe BSP (110/33kV) | [8 empty] | Supply |  | QMRG - Middle Ridge (Ergon) TCP
Description |  |  |  | Region is South West
Transformer size is 2x103/33kV 20/30MVA ON/OB
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
|  | Latest Peak Compensated Load | [5 empty] | 14 MVA on 24/06/2019 at 17:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[5 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  | NCC Rating (MVA) |  | 71.3 | 71.3 | 71.3 |  | 71.3 |  | 71.3 | 80.4 |  | 80.4 |  | 80.4 | 80.4 | 80.4
|  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | 10 PoE Load (MVA) |  | 12.5 | 12.4 | 12.5 |  | 12.5 |  | 12.5 | 14.8 |  | 14.8 |  | 14.7 | 14.6 | 14.7
LARn (MVA)
LARn (MW)
|  |  | Power Factor at Peak Load |  | 0.997 | 0.997 | 0.997 |  | 0.997 |  | 0.997 | 1 |  | 1 |  | 1 | 1 | 1
|  |  | ECC Rating (MVA) |  | 40.5 | 40.5 | 40.5 |  | 40.5 |  | 40.5 | 43.8 |  | 43.8 |  | 43.8 | 43.8 | 43.8
|  |  | 50 PoE Load (MVA) |  | 11.6 | 11.6 | 11.6 |  | 11.6 |  | 11.6 | 14 |  | 13.9 |  | 13.8 | 13.7 | 13.8
|  |  | 50 PoE Load > 95% (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.7 |  | 0.7 |  | 0.7 | 0.7 | 0.7
|  |  | Hours PA > 95% Peak Load |  | 13 | 13 | 13 |  | 13 |  | 13 | 13 |  | 13 |  | 13 | 13 | 13
Raw LAR (MVA)
|  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## STTO
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | STTO - Stanthorpe Town (33/11kV) | [8 empty] | Supply |  | STAN - Stanthorpe BSP
| Description |  |  |  | Region is South West
Transformer size is 2x33/11kV 10/12.5MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.1%, 2021 S 0.1% W 0.1%, 2022 S -0.1% W -0.1%2023 S 0.1% W 0.1%, 2024 S -0.2% W -0.2
|  |  | Latest Peak Compensated Load | [5 empty] | 11.7 MVA on 24/06/2019 at 17:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 27.1 | 27.1 | 27.1 |  | 27.1 |  | 27.1 | 29.2 |  | 29.2 |  | 29.2 | 29.2 | 29.2
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 10.2 | 10.2 | 10.2 |  | 10.2 |  | 10.3 | 12.5 |  | 12.5 |  | 12.4 | 12.4 | 12.4
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.952 | 0.952 | 0.952 |  | 0.952 |  | 0.952 | 0.986 |  | 0.986 |  | 0.986 | 0.986 | 0.986
|  |  |  | ECC Rating (MVA) |  | 14.9 | 14.9 | 14.9 |  | 14.9 |  | 14.9 | 15.9 |  | 15.9 |  | 15.9 | 15.9 | 15.9
|  |  |  | 50 PoE Load (MVA) |  | 9.4 | 9.4 | 9.5 |  | 9.5 |  | 9.5 | 11.7 |  | 11.7 |  | 11.6 | 11.6 | 11.6
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  |  | Hours PA > 95% Peak Load |  | 5.5 | 5.5 | 5.5 |  | 5.5 |  | 5.5 | 5.5 |  | 5.5 |  | 5.5 | 5.5 | 5.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 10 | 10 | 10 |  | 10 |  | 10 | 10 |  | 10 |  | 10 | 10 | 10
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## STUA
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | STUA - Stuart (66/11kV) | [8 empty] | Supply |  | TMES - Townsville Mesh
| Description |  |  |  | Region is Nth Queensland
Transformer size is 2x66/11kV 21/26/35MVA ONAN/ODAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.7%, 2021 S 1.4% W 1.4%, 2022 S 1.3% W 1.3%, 2023 S 1.4% W 1.4%, 2024 S 1.2% W 1.2%
|  |  | Latest Peak Compensated Load | [5 empty] | 26.4 MVA on 17/01/2020 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 76.7 | 76.7 | 76.7 |  | 76.7 |  | 76.7 | 81.6 |  | 81.6 |  | 81.6 | 81.6 | 81.6
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 29.7 | 30.1 | 15 |  | 15.5 |  | 15.9 | 26.8 |  | 27.1 |  | 27.3 | 9.1 | 9.4
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.951 | 0.951 | 0.951 |  | 0.951 |  | 0.951 | 0.934 |  | 0.934 |  | 0.934 | 0.934 | 0.934
|  |  |  | ECC Rating (MVA) |  | 45.5 | 45.5 | 45.5 |  | 45.5 |  | 45.5 | 47.2 |  | 47.2 |  | 47.2 | 47.2 | 47.2
|  |  |  | 50 PoE Load (MVA) |  | 27.5 | 27.9 | 13.3 |  | 13.7 |  | 14.1 | 26.1 |  | 26.4 |  | 26.6 | 12.4 | 12.7
|  |  |  | 50 PoE Load > 95% (MVA) |  | 1.4 | 1.4 | 0.7 |  | 0.7 |  | 0.7 | 1.3 |  | 1.3 |  | 1.3 | 0.6 | 0.6
|  |  |  | Hours PA > 95% Peak Load |  | 68.5 | 68.5 | 68.5 |  | 68.5 |  | 68.5 | 68.5 |  | 68.5 |  | 68.5 | 68.5 | 68.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## T002
Bulk Summary Information and Peak Load Forecast
Substation |  |  |  | T002 - Dalby East BSP (110/33kV) | [8 empty] | Supply |  | QTKM - Tangkam TCP
Description |  |  |  | Region is South West
Transformer size is 2x110/33kV 50/63MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
|  | Latest Peak Compensated Load | [5 empty] | 30.4 MVA on 16/12/2019 at 16:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[5 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  | NCC Rating (MVA) |  | 130.3 | 130.3 | 130.3 |  | 130.3 |  | 130.3 | 149.7 |  | 149.7 |  | 149.7 | 149.7 | 149.7
|  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | 10 PoE Load (MVA) |  | 34.5 | 34.4 | 34.4 |  | 34.5 |  | 34.5 | 30.9 |  | 30.7 |  | 30.4 | 30.3 | 30.4
LARn (MVA)
LARn (MW)
|  |  | Power Factor at Peak Load |  | 1 | 1 | 1 |  | 1 |  | 1 | 0.979 |  | 0.979 |  | 0.979 | 0.979 | 0.979
|  |  | ECC Rating (MVA) |  | 74.4 | 74.4 | 74.4 |  | 74.4 |  | 74.4 | 85.5 |  | 85.5 |  | 85.5 | 85.5 | 85.5
|  |  | 50 PoE Load (MVA) |  | 31 | 30.9 | 30.9 |  | 31 |  | 31 | 29.3 |  | 29.1 |  | 28.8 | 28.7 | 28.8
|  |  | 50 PoE Load > 95% (MVA) |  | 1.6 | 1.5 | 1.5 |  | 1.6 |  | 1.6 | 1.5 |  | 1.5 |  | 1.4 | 1.4 | 1.4
|  |  | Hours PA > 95% Peak Load |  | 8.5 | 8.5 | 8.5 |  | 8.5 |  | 8.5 | 8.5 |  | 8.5 |  | 8.5 | 8.5 | 8.5
Raw LAR (MVA)
|  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## T043
Bulk Summary Information and Peak Load Forecast
Substation |  |  |  | T043 - South Toowoomba BSP (110/33kV) | [8 empty] | Supply |  | QMRG - Middle Ridge (Ergon) TCP
Description |  |  |  | Region is South West
Transformer size is 1x106/33kV 35/60MVA ON/OFB;1x106/33kV 37/48/60MVA ON/OB/OFB
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
|  | Latest Peak Compensated Load | [5 empty] | 64.5 MVA on 15/07/2019 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[5 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  | NCC Rating (MVA) |  | 144.9 | 144.9 | 144.9 |  | 144.9 |  | 144.9 | 163.6 |  | 163.6 |  | 163.6 | 163.6 | 163.6
|  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | 10 PoE Load (MVA) |  | 62.9 | 63 | 63.2 |  | 63.5 |  | 63.8 | 67.8 |  | 67.8 |  | 67.4 | 67.2 | 67.6
LARn (MVA)
LARn (MW)
|  |  | Power Factor at Peak Load |  | 0.976 | 0.976 | 0.976 |  | 0.976 |  | 0.976 | 0.982 |  | 0.982 |  | 0.982 | 0.982 | 0.982
|  |  | ECC Rating (MVA) |  | 81.4 | 81.4 | 81.4 |  | 81.4 |  | 81.4 | 89.3 |  | 89.3 |  | 89.3 | 89.3 | 89.3
|  |  | 50 PoE Load (MVA) |  | 55.9 | 55.9 | 56.1 |  | 56.4 |  | 56.7 | 62.3 |  | 62.2 |  | 61.9 | 61.7 | 62.1
|  |  | 50 PoE Load > 95% (MVA) |  | 2.8 | 2.8 | 2.8 |  | 2.8 |  | 2.8 | 3.1 |  | 3.1 |  | 3.1 | 3.1 | 3.1
|  |  | Hours PA > 95% Peak Load |  | 24 | 24 | 24 |  | 24 |  | 24 | 24 |  | 24 |  | 24 | 24 | 24
Raw LAR (MVA)
|  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## T058
Bulk Summary Information and Peak Load Forecast
Substation |  |  |  | T058 - Warwick BSP (110/33kV) | [8 empty] | Supply |  | QMRG - Middle Ridge (Ergon) TCP
Description |  |  |  | Region is South West
Transformer size is 1x110/33/11kV 40/50MVA ONAN/ONAF;1x110/33kV 40/50MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
|  | Latest Peak Compensated Load | [5 empty] | 35.3 MVA on 29/01/2020 at 17:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[5 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  | NCC Rating (MVA) |  | 118.5 | 118.5 | 118.5 |  | 118.5 |  | 118.5 | 135.6 |  | 135.6 |  | 135.6 | 135.6 | 135.6
|  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | 10 PoE Load (MVA) |  | 39.6 | 39.5 | 39.5 |  | 39.6 |  | 39.7 | 34 |  | 33.9 |  | 33.6 | 33.4 | 33.6
LARn (MVA)
LARn (MW)
|  |  | Power Factor at Peak Load |  | 1 | 1 | 1 |  | 1 |  | 1 | 0.999 |  | 0.999 |  | 0.999 | 0.999 | 0.999
|  |  | ECC Rating (MVA) |  | 68 | 68 | 68 |  | 68 |  | 68 | 74.8 |  | 74.8 |  | 74.8 | 74.8 | 74.8
|  |  | 50 PoE Load (MVA) |  | 34.8 | 34.7 | 34.7 |  | 34.8 |  | 34.8 | 32.1 |  | 32 |  | 31.7 | 31.6 | 31.7
|  |  | 50 PoE Load > 95% (MVA) |  | 1.7 | 1.7 | 1.7 |  | 1.7 |  | 1.7 | 1.6 |  | 1.6 |  | 1.6 | 1.6 | 1.6
|  |  | Hours PA > 95% Peak Load |  | 17 | 17 | 17 |  | 17 |  | 17 | 17 |  | 17 |  | 17 | 17 | 17
Raw LAR (MVA)
|  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## T065
Bulk Summary Information and Peak Load Forecast
Substation |  |  |  | T065 - Alligator Creek BSP (132/33kV) | [8 empty] | Supply |  | QALC - Alligator Creek 33kV TCP
Description |  |  |  | Region is Mackay
Transformer size is 1xALCR TFMR-2-2 TRANSFORMER 132/33/11KV-100 MVA;1xALCR TFMR-3 TRANSFORMER 132/33/11KV-100 MVA
Capacity of commissioned Embedded Generation (with Connection Agreements) is 17.5 MVA
|  | Latest Peak Compensated Load | [5 empty] | 41.9 MVA on 13/12/2019 at 19:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[5 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  | NCC Rating (MVA) |  | 200 | 200 | 200 |  | 200 |  | 200 | 200 |  | 200 |  | 200 | 200 | 200
|  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | 10 PoE Load (MVA) |  | 47.2 | 47.3 | 47.5 |  | 47.8 |  | 48 | 19.5 |  | 19.5 |  | 19.4 | 19.4 | 19.6
LARn (MVA)
LARn (MW)
|  |  | Power Factor at Peak Load |  | 0.99 | 0.99 | 0.99 |  | 0.99 |  | 0.99 | 0.995 |  | 0.995 |  | 0.995 | 0.995 | 0.995
|  |  | ECC Rating (MVA) |  | 100 | 100 | 100 |  | 100 |  | 100 | 100 |  | 100 |  | 100 | 100 | 100
|  |  | 50 PoE Load (MVA) |  | 43.7 | 43.8 | 44 |  | 44.2 |  | 44.4 | 18.5 |  | 18.5 |  | 18.4 | 18.4 | 18.6
|  |  | 50 PoE Load > 95% (MVA) |  | 2.2 | 2.2 | 2.2 |  | 2.2 |  | 2.2 | 0.9 |  | 0.9 |  | 0.9 | 0.9 | 0.9
|  |  | Hours PA > 95% Peak Load |  | 8 | 8 | 8 |  | 8 |  | 8 | 8 |  | 8 |  | 8 | 8 | 8
Raw LAR (MVA)
|  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Manual Trans Avail (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  | Mobile Plant Avail (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 | 2 | 2
|  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## T072
Bulk Summary Information and Peak Load Forecast
Substation |  |  |  | T072 - Barcaldine BSP (132/66kV) | [8 empty] | Supply |  | QLCM - Lilyvale (Barcaldine & Clermont) TCP
Description |  |  |  | Region is Capricornia
Transformer size is 1xBARC TX NO 1-132/66KV TRANSF 1;1xBARC TX NO 2-132/66KV TRANSF 2
Capacity of commissioned Embedded Generation (with Connection Agreements) is 43.4 MVA
|  | Latest Peak Compensated Load | [5 empty] | 20.9 MVA on 17/12/2019 at 19:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[5 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  | NCC Rating (MVA) |  | 26.6 | 26.6 | 26.6 |  | 26.6 |  | 26.6 | 26.6 |  | 26.6 |  | 26.6 | 26.6 | 26.6
|  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  | 10 PoE Load (MVA) |  | 21.9 | 21.5 | 21.4 |  | 21.3 |  | 21.2 | 16.6 |  | 16.4 |  | 16.3 | 16.2 | 16.1
LARn (MVA)
LARn (MW)
|  |  | Power Factor at Peak Load |  | 0.998 | 0.998 | 0.998 |  | 0.998 |  | 0.998 | 0.973 |  | 0.973 |  | 0.973 | 0.973 | 0.973
|  |  | ECC Rating (MVA) |  | 13.3 | 13.3 | 13.3 |  | 13.3 |  | 13.3 | 14.6 |  | 14.6 |  | 14.6 | 14.6 | 14.6
|  |  | 50 PoE Load (MVA) |  | 20.4 | 20.1 | 19.9 |  | 19.9 |  | 19.9 | 15.1 |  | 14.9 |  | 14.8 | 14.7 | 14.7
|  |  | 50 PoE Load > 95% (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 0.8 |  | 0.8 |  | 0.7 | 0.7 | 0.7
|  |  | Hours PA > 95% Peak Load |  | 8 | 8 | 8 |  | 8 |  | 8 | 8 |  | 8 |  | 8 | 8 | 8
|  |  | Raw LAR (MVA) |  | 7.1 | 6.8 | 6.6 |  | 6.6 |  | 6.6 | 0.5 |  | 0.3 |  | 0.2 | 0.1 | 0.1
|  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Remote Trans Avail (MVA) * |  | 6.7 | 6.7 | 6.7 |  | 6.7 |  | 6.7 | 6.7 |  | 6.7 |  | 6.7 | 6.7 | 6.7
|  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Mobile Plant Avail (MVA) |  | 0.7 | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.7 |  | 0.7 |  | 0.7 | 0.7 | 0.7
|  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index
*Represents increased transformer rating by switching off the 11kV reactors at Barcaldine.

## T083
Bulk Summary Information and Peak Load Forecast
Substation |  |  |  | T083 - Roma 33kV BSP (132/33kV) | [8 empty] | Supply |  | T194 - Columboola TCP
Description |  |  |  | Region is South West
Transformer size is 1xROMA 132/33/11KV TRANSF 6
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
|  | Latest Peak Compensated Load | [5 empty] | 25.3 MVA on 16/12/2019 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[5 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  | NCC Rating (MVA) |  | 97.8 | 97.8 | 97.8 |  | 97.8 |  | 97.8 | 115.2 |  | 115.2 |  | 115.2 | 115.2 | 115.2
|  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | 10 PoE Load (MVA) |  | 29.7 | 29.6 | 29.6 |  | 29.7 |  | 29.7 | 23 |  | 22.9 |  | 22.7 | 22.6 | 22.6
LARn (MVA)
LARn (MW)
|  |  | Power Factor at Peak Load |  | 0.986 | 0.986 | 0.986 |  | 0.986 |  | 0.986 | 0.998 |  | 0.998 |  | 0.998 | 0.998 | 0.998
|  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | 50 PoE Load (MVA) |  | 26.7 | 26.6 | 26.6 |  | 26.7 |  | 26.7 | 21.4 |  | 21.3 |  | 21.1 | 21 | 21.1
|  |  | 50 PoE Load > 95% (MVA) |  | 1.3 | 1.3 | 1.3 |  | 1.3 |  | 1.3 | 1.1 |  | 1.1 |  | 1.1 | 1.1 | 1.1
|  |  | Hours PA > 95% Peak Load |  | 374.5 | 374.5 | 374.5 |  | 374.5 |  | 374.5 | 374.5 |  | 374.5 |  | 374.5 | 374.5 | 374.5
|  |  | Raw LAR (MVA) |  | 26.7 | 26.6 | 26.6 |  | 26.7 |  | 26.7 | 21.4 |  | 21.3 |  | 21.1 | 21 | 21.1
|  |  | Auto Trans Avail (MVA) |  | 50 | 50 | 50 |  | 50 |  | 50 | 50 |  | 50 |  | 50 | 50 | 50
|  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## T095
Bulk Summary Information and Peak Load Forecast
Substation |  |  |  | T095 - Millchester BSP (132/66kV) | [8 empty] | Supply |  | QROS - Ross (Kidston and Milchester) TCP
Description |  |  |  | Region is Nth Queensland
Transformer size is 1x132/66/11kV 25/34/40MVA ONAN/ONAF/ODAF;1x132/66kV 20/27MVA ON/OB
Capacity of commissioned Embedded Generation (with Connection Agreements) is 55.0 MVA
|  | Latest Peak Compensated Load | [5 empty] | 28.7 MVA on 19/02/2020 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[5 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  | NCC Rating (MVA) |  | 68 | 68 | 68 |  | 68 |  | 68 | 68 |  | 68 |  | 68 | 68 | 68
|  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | 10 PoE Load (MVA) |  | 32.7 | 32.6 | 32.6 |  | 32.7 |  | 32.7 | 30.4 |  | 31.9 |  | 31.7 | 31.5 | 31.6
LARn (MVA)
LARn (MW)
|  |  | Power Factor at Peak Load |  | 0.987 | 0.987 | 0.987 |  | 0.987 |  | 0.987 | 0.984 |  | 0.984 |  | 0.984 | 0.984 | 0.984
|  |  | ECC Rating (MVA) |  | 37.4 | 37.4 | 37.4 |  | 37.4 |  | 37.4 | 37.4 |  | 37.4 |  | 37.4 | 37.4 | 37.4
|  |  | 50 PoE Load (MVA) |  | 30.5 | 30.4 | 30.4 |  | 30.5 |  | 30.5 | 29 |  | 30.6 |  | 30.3 | 30.2 | 30.3
|  |  | 50 PoE Load > 95% (MVA) |  | 1.5 | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.5 | 1.5
|  |  | Hours PA > 95% Peak Load |  | 24.5 | 24.5 | 24.5 |  | 24.5 |  | 24.5 | 24.5 |  | 24.5 |  | 24.5 | 24.5 | 24.5
Raw LAR (MVA)
|  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Manual Trans Avail (MVA) |  | 19.1 | 19.1 | 19.1 |  | 19.1 |  | 19.1 | 19.1 |  | 19.1 |  | 19.1 | 19.1 | 19.1
|  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(30min) |  | 7.9 | 7.9 | 7.9 |  | 7.9 |  | 7.9 | 7.9 |  | 7.9 |  | 7.9 | 7.9 | 7.9
|  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## T116
Bulk Summary Information and Peak Load Forecast
Substation |  |  |  | T116 - Torrington BSP (110/33kV) | [8 empty] | Supply |  | QMRG - Middle Ridge (Ergon) TCP
Description |  |  |  | Region is South West
Transformer size is 2x110/33/11kV 64/80/106MVA ONAN/ODAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
|  | Latest Peak Compensated Load | [5 empty] | 98.7 MVA on 04/06/2019 at 17:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[5 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  | NCC Rating (MVA) |  | 239 | 239 | 239 |  | 239 |  | 239 | 286.2 |  | 286.2 |  | 286.2 | 286.2 | 286.2
|  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | 10 PoE Load (MVA) |  | 97.2 | 97.3 | 97.8 |  | 98.5 |  | 99.3 | 97.9 |  | 97.8 |  | 97.2 | 97.2 | 98.1
LARn (MVA)
LARn (MW)
|  |  | Power Factor at Peak Load |  | 0.999 | 0.999 | 0.999 |  | 0.999 |  | 0.999 | 1 |  | 1 |  | 1 | 1 | 1
|  |  | ECC Rating (MVA) |  | 132.3 | 132.3 | 132.3 |  | 132.3 |  | 132.3 | 157.1 |  | 157.1 |  | 157.1 | 157.1 | 157.1
|  |  | 50 PoE Load (MVA) |  | 86 | 86 | 86.4 |  | 87.1 |  | 87.7 | 92.7 |  | 92.7 |  | 92.1 | 92.1 | 92.9
|  |  | 50 PoE Load > 95% (MVA) |  | 4.3 | 4.3 | 4.3 |  | 4.4 |  | 4.4 | 4.6 |  | 4.6 |  | 4.6 | 4.6 | 4.6
|  |  | Hours PA > 95% Peak Load |  | 14 | 14 | 14 |  | 14 |  | 14 | 14 |  | 14 |  | 14 | 14 | 14
Raw LAR (MVA)
|  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## T130
Bulk Summary Information and Peak Load Forecast
Substation |  |  |  | T130 - Boat Creek BSP (132/66kV) | [8 empty] | Supply |  | QYAE - Boat Creek TCP
Description |  |  |  | Region is Capricornia
Transformer size is 2x132/66/11kV 60/80MVA ONAN/ODAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
|  | Latest Peak Compensated Load | [5 empty] | 44.9 MVA on 16/08/2019 at 01:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[5 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  | NCC Rating (MVA) |  | 151.2 | 151.2 | 151.2 |  | 151.2 |  | 151.2 | 162 |  | 162 |  | 162 | 162 | 162
|  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | 10 PoE Load (MVA) |  | 45.7 | 45.7 | 45.7 |  | 45.9 |  | 46 | 45.4 |  | 45.2 |  | 44.9 | 44.7 | 44.9
LARn (MVA)
LARn (MW)
|  |  | Power Factor at Peak Load |  | 0.932 | 0.932 | 0.932 |  | 0.932 |  | 0.932 | 0.944 |  | 0.944 |  | 0.944 | 0.944 | 0.944
|  |  | ECC Rating (MVA) |  | 90.9 | 90.9 | 90.9 |  | 90.9 |  | 90.9 | 95.7 |  | 95.7 |  | 95.7 | 95.7 | 95.7
|  |  | 50 PoE Load (MVA) |  | 44.6 | 44.6 | 44.6 |  | 44.8 |  | 44.9 | 44.2 |  | 44.1 |  | 43.8 | 43.6 | 43.8
|  |  | 50 PoE Load > 95% (MVA) |  | 2.2 | 2.2 | 2.2 |  | 2.2 |  | 2.2 | 2.2 |  | 2.2 |  | 2.2 | 2.2 | 2.2
|  |  | Hours PA > 95% Peak Load |  | 232 | 232 | 232 |  | 232 |  | 232 | 232 |  | 232 |  | 232 | 232 | 232
Raw LAR (MVA)
|  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## T159
Bulk Summary Information and Peak Load Forecast
Substation |  |  |  | T159 - Lakeland BSP (132/66kV) | [8 empty] | Supply |  | QTUH - Turkinje 132kV TCP
Description |  |  |  | Region is Far North
Transformer size is 2x132/66/22kV 15/20MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 10.5 MVA
|  | Latest Peak Compensated Load | [5 empty] | 5.9 MVA on 15/02/2020 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[5 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  | NCC Rating (MVA) |  | 49.8 | 49.8 | 49.8 |  | 49.8 |  | 49.8 | 55.8 |  | 55.8 |  | 55.8 | 55.8 | 55.8
|  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | 10 PoE Load (MVA) |  | 6.2 | 6.2 | 6.2 |  | 6.3 |  | 6.3 | 5 |  | 5 |  | 4.9 | 4.9 | 5
LARn (MVA)
LARn (MW)
|  |  | Power Factor at Peak Load |  | 0.999 | 0.999 | 0.999 |  | 0.999 |  | 0.999 | 0.993 |  | 0.993 |  | 0.993 | 0.993 | 0.993
|  |  | ECC Rating (MVA) |  | 29.4 | 29.4 | 29.4 |  | 29.4 |  | 29.4 | 29.9 |  | 29.9 |  | 29.9 | 29.9 | 29.9
|  |  | 50 PoE Load (MVA) |  | 5.8 | 5.8 | 5.8 |  | 5.8 |  | 5.8 | 4.8 |  | 4.8 |  | 4.8 | 4.8 | 4.8
|  |  | 50 PoE Load > 95% (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  | Hours PA > 95% Peak Load |  | 17.5 | 17.5 | 17.5 |  | 17.5 |  | 17.5 | 17.5 |  | 17.5 |  | 17.5 | 17.5 | 17.5
Raw LAR (MVA)
|  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## T163
Bulk Summary Information and Peak Load Forecast
Substation |  |  |  | T163 - Rolleston BSP (132/66kV) | [8 empty] | Supply |  | QBWH - Blackwater 132kV TCP
Description |  |  |  | Region is Capricornia
Transformer size is 2x132/66/22kV 30/40/37.5MVA ONAN/ODAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
|  | Latest Peak Compensated Load | [5 empty] | 20.5 MVA on 20/07/2019 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[5 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  | NCC Rating (MVA) |  | 89.3 | 89.3 | 89.3 |  | 89.3 |  | 89.3 | 97.7 |  | 97.7 |  | 97.7 | 97.7 | 97.7
|  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | 10 PoE Load (MVA) |  | 21.4 | 21.4 | 21.4 |  | 21.5 |  | 21.5 | 20.9 |  | 20.9 |  | 20.7 | 20.6 | 20.7
LARn (MVA)
LARn (MW)
|  |  | Power Factor at Peak Load |  | 0.971 | 0.971 | 0.971 |  | 0.971 |  | 0.971 | 0.957 |  | 0.957 |  | 0.957 | 0.957 | 0.957
|  |  | ECC Rating (MVA) |  | 52.3 | 52.3 | 52.3 |  | 52.3 |  | 52.3 | 56.1 |  | 56.1 |  | 56.1 | 56.1 | 56.1
|  |  | 50 PoE Load (MVA) |  | 20.5 | 20.5 | 20.5 |  | 20.5 |  | 20.6 | 20.2 |  | 20.2 |  | 20 | 19.9 | 20
|  |  | 50 PoE Load > 95% (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  | Hours PA > 95% Peak Load |  | 11.5 | 11.5 | 11.5 |  | 11.5 |  | 11.5 | 11.5 |  | 11.5 |  | 11.5 | 11.5 | 11.5
Raw LAR (MVA)
|  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## T166
Bulk Summary Information and Peak Load Forecast
Substation |  |  |  | T166 - Granite Creek BSP (132/66kV) | [8 empty] | Supply |  | QGNG - Gin Gin TCP
Description |  |  |  | Region is Capricornia
Transformer size is 1xGRCR TRANSF 1-132/66/22KV TRANSF 1;1xGRCR TRANSF 2-132/66/11KV TRANSF 2(Standby)
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
|  | Latest Peak Compensated Load | [5 empty] | 6.6 MVA on 02/01/2020 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[5 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  | NCC Rating (MVA) |  | 32 | 32 | 32 |  | 32 |  | 32 | 32 |  | 32 |  | 32 | 32 | 32
|  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | 10 PoE Load (MVA) |  | 5.7 | 5.7 | 5.7 |  | 5.7 |  | 5.7 | 4.8 |  | 4.8 |  | 4.8 | 4.8 | 4.8
LARn (MVA)
LARn (MW)
|  |  | Power Factor at Peak Load |  | 0.952 | 0.952 | 0.952 |  | 0.952 |  | 0.952 | 0.941 |  | 0.941 |  | 0.941 | 0.941 | 0.941
|  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | 50 PoE Load (MVA) |  | 5.3 | 5.3 | 5.3 |  | 5.3 |  | 5.4 | 4.7 |  | 4.7 |  | 4.6 | 4.6 | 4.7
|  |  | 50 PoE Load > 95% (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  | Hours PA > 95% Peak Load |  | 7.5 | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 | 7.5
|  |  | Raw LAR (MVA) |  | 5.3 | 5.3 | 5.3 |  | 5.3 |  | 5.4 | 4.7 |  | 4.7 |  | 4.6 | 4.6 | 4.7
|  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Manual Trans Avail (MVA) |  | 15 | 15 | 15 |  | 15 |  | 15 | 15 |  | 15 |  | 15 | 15 | 15
|  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## T176
Bulk Summary Information and Peak Load Forecast
Substation |  |  |  | T176 - Louisa Creek BSP (132/33kV) | [8 empty] | Supply |  | QALH - Alligator Creek 132kV TCP
Description |  |  |  | Region is Mackay
Transformer size is 2x132/33/11kV 60/80MVA ONAN/ODAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
|  | Latest Peak Compensated Load | [5 empty] | 45.8 MVA on 18/01/2020 at 11:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[5 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  | NCC Rating (MVA) |  | 175.8 | 175.8 | 175.8 |  | 175.8 |  | 175.8 | 185.2 |  | 185.2 |  | 185.2 | 185.2 | 185.2
|  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | 10 PoE Load (MVA) |  | 47.9 | 47.9 | 48 |  | 48.2 |  | 48.3 | 43.3 |  | 43.2 |  | 42.9 | 42.8 | 43
LARn (MVA)
LARn (MW)
|  |  | Power Factor at Peak Load |  | 0.969 | 0.969 | 0.969 |  | 0.969 |  | 0.969 | 0.953 |  | 0.953 |  | 0.953 | 0.953 | 0.953
|  |  | ECC Rating (MVA) |  | 100.4 | 100.4 | 100.4 |  | 100.4 |  | 100.4 | 105.5 |  | 105.5 |  | 105.5 | 105.5 | 105.5
|  |  | 50 PoE Load (MVA) |  | 46.6 | 46.7 | 46.7 |  | 46.9 |  | 47 | 42.3 |  | 42.1 |  | 41.9 | 41.7 | 41.9
|  |  | 50 PoE Load > 95% (MVA) |  | 2.3 | 2.3 | 2.3 |  | 2.3 |  | 2.4 | 2.1 |  | 2.1 |  | 2.1 | 2.1 | 2.1
|  |  | Hours PA > 95% Peak Load |  | 12.5 | 12.5 | 12.5 |  | 12.5 |  | 12.5 | 12.5 |  | 12.5 |  | 12.5 | 12.5 | 12.5
Raw LAR (MVA)
|  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## T188
Bulk Summary Information and Peak Load Forecast
Substation |  |  |  | T188 - Daandine BSP (110/33kV) | [8 empty] | Supply |  | QTKM - Tangkam TCP
Description |  |  |  | Region is South West
Transformer size is 1x110/33/11kV 24/32MVA ONAN/ODAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 30.0 MVA
|  | Latest Peak Compensated Load | [5 empty] | 2.9 MVA on 11/02/2020 at 07:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[5 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  | NCC Rating (MVA) |  | 37.3 | 37.3 | 37.3 |  | 37.3 |  | 37.3 | 40.5 |  | 40.5 |  | 40.5 | 40.5 | 40.5
|  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | 10 PoE Load (MVA) |  | 3 | 3 | 3 |  | 3 |  | 3.1 | 1.7 |  | 1.7 |  | 1.7 | 1.7 | 1.7
LARn (MVA)
LARn (MW)
|  |  | Power Factor at Peak Load |  | 0.648 | 0.648 | 0.648 |  | 0.648 |  | 0.648 | 0.64 |  | 0.64 |  | 0.64 | 0.64 | 0.64
|  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | 50 PoE Load (MVA) |  | 3 | 3 | 3 |  | 3 |  | 3 | 1.7 |  | 1.6 |  | 1.6 | 1.6 | 1.6
|  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  | Hours PA > 95% Peak Load |  | 19 | 19 | 19 |  | 19 |  | 19 | 19 |  | 19 |  | 19 | 19 | 19
|  |  | Raw LAR (MVA) |  | 3 | 3 | 3 |  | 3 |  | 3 | 1.7 |  | 1.6 |  | 1.6 | 1.6 | 1.6
|  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Manual Trans Avail (MVA) |  | 3.6 | 3.6 | 3.6 |  | 3.6 |  | 3.6 | 3.6 |  | 3.6 |  | 3.6 | 3.6 | 3.6
|  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## T189
Bulk Summary Information and Peak Load Forecast
Substation |  |  |  | T189 - Oakey BSP (110/33kV) | [8 empty] | Supply |  | QOKT - Oakey TCP
Description |  |  |  | Region is South West
Transformer size is 2x110/33/11kV 48/63MVA ONAN/ODAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 27.5 MVA
|  | Latest Peak Compensated Load | [5 empty] | 20.3 MVA on 16/12/2019 at 16:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[5 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  | NCC Rating (MVA) |  | 147.2 | 147.2 | 147.2 |  | 147.2 |  | 147.2 | 165.2 |  | 165.2 |  | 165.2 | 165.2 | 165.2
|  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | 10 PoE Load (MVA) |  | 21.1 | 20.9 | 20.8 |  | 20.8 |  | 20.7 | 20.8 |  | 20.6 |  | 20.4 | 20.2 | 20.2
LARn (MVA)
LARn (MW)
|  |  | Power Factor at Peak Load |  | 0.948 | 0.948 | 0.948 |  | 0.948 |  | 0.948 | 0.959 |  | 0.959 |  | 0.959 | 0.959 | 0.959
|  |  | ECC Rating (MVA) |  | 82 | 82 | 82 |  | 82 |  | 82 | 92.5 |  | 92.5 |  | 92.5 | 92.5 | 92.5
|  |  | 50 PoE Load (MVA) |  | 19.8 | 19.7 | 19.6 |  | 19.6 |  | 19.5 | 20.1 |  | 20 |  | 19.7 | 19.5 | 19.5
|  |  | 50 PoE Load > 95% (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  | Hours PA > 95% Peak Load |  | 136 | 136 | 136 |  | 136 |  | 136 | 136 |  | 136 |  | 136 | 136 | 136
Raw LAR (MVA)
|  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## T198
Bulk Summary Information and Peak Load Forecast
Substation |  |  |  | T198 - Broadlea BSP (132/66kV) | [8 empty] | Supply |  | QMRH - Moranbah 132kV TCP
Description |  |  |  | Region is Mackay
Transformer size is 2x132/66/11kV 80/100MVA ONAN/ODAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
|  | Latest Peak Compensated Load | [5 empty] | 44 MVA on 11/01/2020 at 10:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[5 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  | NCC Rating (MVA) |  | 223.1 | 223.1 | 223.1 |  | 223.1 |  | 223.1 | 241.4 |  | 241.4 |  | 241.4 | 241.4 | 241.4
|  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | 10 PoE Load (MVA) |  | 45.2 | 52.1 | 58.9 |  | 59.2 |  | 59.2 | 42.2 |  | 42 |  | 47.8 | 53.6 | 53.8
LARn (MVA)
LARn (MW)
|  |  | Power Factor at Peak Load |  | 0.975 | 0.975 | 0.975 |  | 0.975 |  | 0.975 | 0.983 |  | 0.983 |  | 0.983 | 0.983 | 0.983
|  |  | ECC Rating (MVA) |  | 132.4 | 132.4 | 132.4 |  | 132.4 |  | 132.4 | 140.1 |  | 140.1 |  | 140.1 | 140.1 | 140.1
|  |  | 50 PoE Load (MVA) |  | 44.1 | 51 | 57.8 |  | 58.1 |  | 58.1 | 41.2 |  | 41 |  | 46.8 | 52.5 | 52.8
|  |  | 50 PoE Load > 95% (MVA) |  | 2.2 | 2.6 | 2.9 |  | 2.9 |  | 2.9 | 2.1 |  | 2.1 |  | 2.3 | 2.6 | 2.6
|  |  | Hours PA > 95% Peak Load |  | 66 | 66 | 66 |  | 66 |  | 66 | 66 |  | 66 |  | 66 | 66 | 66
Raw LAR (MVA)
|  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## TANB
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | TANB - Tanby (66/22kV) | [8 empty] | Supply |  | RMES - Rockhampton Mesh
| Description |  |  |  | Region is Capricornia
Transformer size is 2x66/22kV 15/20MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 1.4%, 2021 S 1.8% W 1.8%, 2022 S 1.6% W 1.6%, 2023 S 1.7% W 1.7%, 2024 S 1.5% W 1.5%
|  |  | Latest Peak Compensated Load | [5 empty] | 11.8 MVA on 16/02/2020 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 50.4 | 50.4 | 50.4 |  | 50.4 |  | 50.4 | 56.6 |  | 56.6 |  | 56.6 | 56.6 | 56.6
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 12.7 | 12.9 | 13.1 |  | 13.4 |  | 13.6 | 9.1 |  | 9.3 |  | 9.3 | 9.4 | 9.6
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.994 | 0.994 | 0.994 |  | 0.994 |  | 0.994 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | ECC Rating (MVA) |  | 27.4 | 27.4 | 27.4 |  | 27.4 |  | 27.4 | 29.9 |  | 29.9 |  | 29.9 | 29.9 | 29.9
|  |  |  | 50 PoE Load (MVA) |  | 11.6 | 11.8 | 12 |  | 12.3 |  | 12.5 | 8.7 |  | 8.8 |  | 8.9 | 9 | 9.2
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.4 |  | 0.4 |  | 0.4 | 0.5 | 0.5
|  |  |  | Hours PA > 95% Peak Load |  | 6.5 | 6.5 | 6.5 |  | 6.5 |  | 6.5 | 6.5 |  | 6.5 |  | 6.5 | 6.5 | 6.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## TARA
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | TARA - Tara (33/11kV) | [8 empty] | Supply |  | COLU - Columboola BSP
| Description |  |  |  | Region is South West
Transformer size is 1x33/11kV 1.5MVA ON;1x33/11kV 1MVA ON
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -1.4%, 2021 S -0.3% W -0.3%2022 S -0.1% W -0.1%2023 S 0.1% W 0.1%, 2024 S -0.1% W -0.1
|  |  | Latest Peak Compensated Load | [5 empty] | 1.4 MVA on 11/12/2019 at 14:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 | 2 | 2
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 1.7 | 1.7 | 1.7 |  | 1.7 |  | 1.7 | 1.3 |  | 1.3 |  | 1.3 | 1.3 | 1.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.956 | 0.956 | 0.956 |  | 0.956 |  | 0.956 | 0.983 |  | 0.983 |  | 0.983 | 0.983 | 0.983
|  |  |  | ECC Rating (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | 50 PoE Load (MVA) |  | 1.5 | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.3 |  | 1.2 |  | 1.2 | 1.2 | 1.2
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 12 | 12 | 12 |  | 12 |  | 12 | 12 |  | 12 |  | 12 | 12 | 12
|  |  |  | Raw LAR (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.3 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## TEST
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | TEST - Tennyson Street (33/11kV) | [8 empty] | Supply |  | MACK - Mackay BSP
| Description |  |  |  | Region is Mackay
Transformer size is 1x33/11kV 10/12.5MVA ONAN/ONAF;1x33/11kV 12.5MVA ON
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -1.3%, 2021 S -0.5% W -0.5%2022 S -0.9% W -0.9%2023 S -0.7% W -0.7%2024 S -0.5% W -0.5
|  |  | Latest Peak Compensated Load | [5 empty] | 17.7 MVA on 12/02/2020 at 16:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 25 | 25 | 25 |  | 25 |  | 25 | 25 |  | 25 |  | 25 | 25 | 25
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 20.1 | 19.9 | 19.8 |  | 19.8 |  | 19.7 | 9.4 |  | 9.3 |  | 9.2 | 9.1 | 9.1
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.935 | 0.935 | 0.935 |  | 0.935 |  | 0.935 | 0.943 |  | 0.943 |  | 0.943 | 0.943 | 0.943
|  |  |  | ECC Rating (MVA) |  | 12.5 | 12.5 | 12.5 |  | 12.5 |  | 12.5 | 12.5 |  | 12.5 |  | 12.5 | 12.5 | 12.5
|  |  |  | 50 PoE Load (MVA) |  | 18 | 17.9 | 17.8 |  | 17.8 |  | 17.7 | 9.2 |  | 9.1 |  | 8.9 | 8.8 | 8.8
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.9 | 0.9 | 0.9 |  | 0.9 |  | 0.9 | 0.5 |  | 0.5 |  | 0.4 | 0.4 | 0.4
|  |  |  | Hours PA > 95% Peak Load |  | 11.5 | 11.5 | 11.5 |  | 11.5 |  | 11.5 | 11.5 |  | 11.5 |  | 11.5 | 11.5 | 11.5
|  |  |  | Raw LAR (MVA) |  | 5.5 | 5.4 | 5.3 |  | 5.3 |  | 5.2
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 5.5 | 5.5 | 5.5 |  | 5.5 |  | 5.5 | 5.5 |  | 5.5 |  | 5.5 | 5.5 | 5.5
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## THEO
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | THEO - Theodore (66/22kV) | [8 empty] | Supply |  | T027 - Moura BSP
| Description |  |  |  | Region is Capricornia
Transformer size is 2x66/22kV 5MVA ON;1x66/22kV 5MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.9%, 2021 S -0.2% W -0.2%2022 S -0.5% W -0.5%2023 S -0.0% W -0.0%2024 S -0.6% W -0.6
|  |  | Latest Peak Compensated Load | [5 empty] | 11.6 MVA on 07/12/2019 at 16:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 16.6 | 16.6 | 16.6 |  | 16.6 |  | 16.6 | 18.2 |  | 18.2 |  | 18.2 | 18.2 | 18.2
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 12.1 | 12 | 12 |  | 12 |  | 12 | 10.3 |  | 10.3 |  | 10.1 | 10.1 | 10.1
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.998 | 0.998 | 0.998 |  | 0.998 |  | 0.998 | 0.999 |  | 0.999 |  | 0.999 | 0.999 | 0.999
|  |  |  | ECC Rating (MVA) |  | 11.4 | 11.4 | 11.4 |  | 11.4 |  | 11.4 | 12.5 |  | 12.5 |  | 12.5 | 12.5 | 12.5
|  |  |  | 50 PoE Load (MVA) |  | 11.6 | 11.5 | 11.5 |  | 11.5 |  | 11.4 | 10 |  | 10 |  | 9.9 | 9.8 | 9.8
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | Hours PA > 95% Peak Load |  | 27 | 27 | 27 |  | 27 |  | 27 | 27 |  | 27 |  | 27 | 27 | 27
|  |  |  | Raw LAR (MVA) |  | 0.2 | 0.1 | 0.1 |  | 0.1
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 5.2 | 5.2 | 5.2 |  | 5.2 |  | 5.2 | 5.2 |  | 5.2 |  | 5.2 | 5.2 | 5.2
|  |  |  | Shed(4Hour) |  | 1.8 | 1.8 | 1.8 |  | 1.8 |  | 1.8 | 1.8 |  | 1.8 |  | 1.8 | 1.8 | 1.8
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## TIER
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | TIER - Tieri (66/22kV) | [8 empty] | Supply |  | H015 - Lilyvale BSP
| Description |  |  |  | Region is Capricornia
Transformer size is 2x66/22kV 5MVA ON
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.8%, 2021 S 0.0% W 0.0%, 2022 S -0.1% W -0.1%2023 S 0.1% W 0.1%, 2024 S -0.2% W -0.2
|  |  | Latest Peak Compensated Load | [5 empty] | 2 MVA on 16/12/2019 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 11 | 11 | 11 |  | 11 |  | 11 | 11 |  | 11 |  | 11 | 11 | 11
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 2.3 | 2.3 | 2.3 |  | 2.3 |  | 2.3 | 1.4 |  | 1.4 |  | 1.3 | 1.3 | 1.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.989 | 0.989 | 0.989 |  | 0.989 |  | 0.989 | 0.985 |  | 0.985 |  | 0.985 | 0.985 | 0.985
|  |  |  | ECC Rating (MVA) |  | 6 | 6 | 6 |  | 6 |  | 6 | 6.8 |  | 6.8 |  | 6.8 | 6.8 | 6.8
|  |  |  | 50 PoE Load (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 1.3 |  | 1.3 |  | 1.2 | 1.2 | 1.2
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 6 | 6 | 6 |  | 6 |  | 6 | 6 |  | 6 |  | 6 | 6 | 6
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## TOPO
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | TOPO - Townsville Port (66/11kV) | [8 empty] | Supply |  | TMES - Townsville Mesh
| Description |  |  |  | Region is Nth Queensland
Transformer size is 2x66/11kV 19.2/24/32MVA ONAN/ODAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.3%, 2021 S 0.0% W 0.0%, 2022 S -0.1% W -0.1%2023 S 0.1% W 0.1%, 2024 S -0.1% W -0.1
|  |  | Latest Peak Compensated Load | [5 empty] | 10.1 MVA on 14/02/2020 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 83.2 | 83.2 | 83.2 |  | 83.2 |  | 83.2 | 83.2 |  | 83.2 |  | 83.2 | 83.2 | 83.2
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 10.8 | 10.8 | 10.8 |  | 10.8 |  | 10.8 | 10.3 |  | 10.3 |  | 10.2 | 10.2 | 10.2
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.97 | 0.97 | 0.97 |  | 0.97 |  | 0.97 | 0.97 |  | 0.97 |  | 0.97 | 0.97 | 0.97
|  |  |  | ECC Rating (MVA) |  | 41.6 | 41.6 | 41.6 |  | 41.6 |  | 41.6 | 41.6 |  | 41.6 |  | 41.6 | 41.6 | 41.6
|  |  |  | 50 PoE Load (MVA) |  | 9.8 | 9.8 | 9.8 |  | 9.8 |  | 9.8 | 9.8 |  | 9.8 |  | 9.7 | 9.7 | 9.7
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.5 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | Hours PA > 95% Peak Load |  | 24.5 | 24.5 | 24.5 |  | 24.5 |  | 24.5 | 24.5 |  | 24.5 |  | 24.5 | 24.5 | 24.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## TORQ
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | TORQ - Torquay (66/11kV) | [8 empty] | Supply |  | MARY - Maryborough BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 2x66/11kV 21/26.25/35MVA ONAN/ODAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 1.0%, 2021 S 1.4% W 1.4%, 2022 S 1.3% W 1.3%, 2023 S 1.3% W 1.3%, 2024 S 1.1% W 1.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 28.8 MVA on 20/02/2020 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 91.1 | 91.1 | 91.1 |  | 91.1 |  | 91.1 | 99 |  | 99 |  | 99 | 99 | 99
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 31.5 | 31.9 | 32.4 |  | 32.9 |  | 33.4 | 27.2 |  | 27.5 |  | 27.6 | 27.9 | 28.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 1 | 1 | 1 |  | 0.999 |  | 0.999 | 0.991 |  | 0.991 |  | 0.991 | 0.991 | 0.991
|  |  |  | ECC Rating (MVA) |  | 48.8 | 48.8 | 48.8 |  | 48.8 |  | 48.8 | 52.3 |  | 52.3 |  | 52.3 | 52.3 | 52.3
|  |  |  | 50 PoE Load (MVA) |  | 29.3 | 29.6 | 30.1 |  | 30.5 |  | 31 | 25.9 |  | 26.1 |  | 26.3 | 26.5 | 26.9
|  |  |  | 50 PoE Load > 95% (MVA) |  | 1.5 | 1.5 | 1.5 |  | 1.5 |  | 1.6 | 1.3 |  | 1.3 |  | 1.3 | 1.3 | 1.3
|  |  |  | Hours PA > 95% Peak Load |  | 10.5 | 10.5 | 10.5 |  | 10.5 |  | 10.5 | 10.5 |  | 10.5 |  | 10.5 | 10.5 | 10.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## TORR
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | TORR - Torrington (33/11kV) | [8 empty] | Supply |  | T116 - Torrington BSP
| Description |  |  |  | Region is South West
Transformer size is 2x33/11kV 15/18.5/25 ONAN/ODAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.0%, 2021 S 0.4% W 0.4%, 2022 S -0.2% W -0.2%2023 S 0.9% W 0.9%, 2024 S 1.3% W 1.3%
|  |  | Latest Peak Compensated Load | [5 empty] | 23.9 MVA on 04/06/2019 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 56.7 | 56.7 | 56.7 |  | 56.7 |  | 56.7 | 67.5 |  | 67.5 |  | 67.5 | 67.5 | 67.5
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 23.2 | 23.2 | 23.4 |  | 23.8 |  | 24.2 | 25.2 |  | 25.2 |  | 25 | 25.1 | 25.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.968 | 0.968 | 0.968 |  | 0.968 |  | 0.968 | 0.977 |  | 0.977 |  | 0.977 | 0.977 | 0.977
|  |  |  | ECC Rating (MVA) |  | 31.6 | 31.6 | 31.6 |  | 31.6 |  | 31.6 | 37.4 |  | 37.4 |  | 37.4 | 37.4 | 37.4
|  |  |  | 50 PoE Load (MVA) |  | 20.8 | 20.7 | 20.9 |  | 21.3 |  | 21.7 | 23.4 |  | 23.5 |  | 23.3 | 23.4 | 23.8
|  |  |  | 50 PoE Load > 95% (MVA) |  | 1 | 1 | 1 |  | 1.1 |  | 1.1 | 1.2 |  | 1.2 |  | 1.2 | 1.2 | 1.2
|  |  |  | Hours PA > 95% Peak Load |  | 32 | 32 | 32 |  | 32 |  | 32 | 32 |  | 32 |  | 32 | 32 | 32
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## TUAN
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | TUAN - Tuan (66/11kV) | [8 empty] | Supply |  | MARY - Maryborough BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 1x66/11kV 7.5/10MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.4%, 2021 S 0.4% W 0.4%, 2022 S 0.2% W 0.2%, 2023 S 0.6% W 0.6%, 2024 S 0.0% W 0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 5.6 MVA on 10/07/2019 at 23:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 10.8 | 10.8 | 10.8 |  | 10.8 |  | 10.8 | 11.4 |  | 11.4 |  | 11.4 | 11.4 | 11.4
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 7.9 | 12.3 | 12.3 |  | 12.3 |  | 12.4 | 7.8 |  | 10.1 |  | 10 | 10 | 10.1
|  |  |  | LARn (MVA) |  |  | 1.5 | 1.5 |  | 1.5 |  | 1.6
|  |  |  | LARn (MW) |  |  | 1.3 | 1.3 |  | 1.3 |  | 1.4
|  |  |  | Power Factor at Peak Load |  | 0.846 | 0.854 | 0.854 |  | 0.854 |  | 0.854 | 0.855 |  | 0.853 |  | 0.855 | 0.855 | 0.853
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 7.2 | 9.1 | 9.1 |  | 9.2 |  | 9.2 | 7.1 |  | 8.9 |  | 8.8 | 8.8 | 8.9
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.4 | 0.5 | 0.5 |  | 0.5 |  | 0.5 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  |  | Hours PA > 95% Peak Load |  | 197.5 | 197.5 | 197.5 |  | 197.5 |  | 197.5 | 197.5 |  | 197.5 |  | 197.5 | 197.5 | 197.5
|  |  |  | Raw LAR (MVA) |  | 7.2 | 9.1 | 9.1 |  | 9.2 |  | 9.2 | 7.1 |  | 8.9 |  | 8.8 | 8.8 | 8.9
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 2.1 | 2.1 | 2.1 |  | 2.1 |  | 2.1 | 2.1 |  | 2.1 |  | 2.1 | 2.1 | 2.1
|  |  |  | Mobile Plant Avail (MVA) |  | 1.6 | 1.6 | 1.6 |  | 1.6 |  | 1.6 | 1.6 |  | 1.6 |  | 1.6 | 1.6 | 1.6
|  |  |  | Shed(30min) |  | 6 | 6 | 6 |  | 6 |  | 6 | 6 |  | 6 |  | 6 | 6 | 6
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | No | No |  | No |  | No | Yes |  | Yes |  | Yes | Yes | Yes
Note: Load at risk is acceptable as Block load increase will be less than initially planned. Future 10 POE load is not expected exceed the NCC Rating.
Return to Index

## TWCE
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | TWCE - Toowoomba Central (110/11kV) | [8 empty] | Supply |  | QMRG - Middle Ridge (Ergon) TCP
| Description |  |  |  | Region is South West
Transformer size is 2x40MVA 110/11kV Transformer
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.5%, 2021 S -0.5% W -0.5%2022 S -0.7% W -0.7%2023 S -0.4% W -0.4%2024 S -0.5% W -0.5
|  |  | Latest Peak Compensated Load | [5 empty] | 23.9 MVA on 22/01/2020 at 12:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 88 | 88 | 88 |  | 88 |  | 88 | 88 |  | 88 |  | 88 | 88 | 88
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 25 | 24.9 | 24.8 |  | 24.8 |  | 24.7 | 18.3 |  | 18.2 |  | 17.9 | 17.8 | 17.8
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.968 | 0.968 | 0.968 |  | 0.968 |  | 0.968 | 0.979 |  | 0.979 |  | 0.979 | 0.979 | 0.979
|  |  |  | ECC Rating (MVA) |  | 46 | 46 | 46 |  | 46 |  | 46 | 52 |  | 52 |  | 52 | 52 | 52
|  |  |  | 50 PoE Load (MVA) |  | 23.5 | 23.3 | 23.2 |  | 23.2 |  | 23.2 | 17.5 |  | 17.4 |  | 17.1 | 17 | 17
|  |  |  | 50 PoE Load > 95% (MVA) |  | 1.2 | 1.2 | 1.2 |  | 1.2 |  | 1.2 | 0.9 |  | 0.9 |  | 0.9 | 0.9 | 0.9
|  |  |  | Hours PA > 95% Peak Load |  | 22.5 | 22.5 | 22.5 |  | 22.5 |  | 22.5 | 22.5 |  | 22.5 |  | 22.5 | 22.5 | 22.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## VERM
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | VERM - Vermont (66/22kV) | [8 empty] | Supply |  | T035 - Dysart BSP
| Description |  |  |  | Region is Capricornia
Transformer size is 1x66/22kV 10MVA ONAN;1xVERMSS TRANSF 2
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -1.0%, 2021 S 0.0% W 0.0%, 2022 S 0.0% W 0.0%, 2023 S 0.0% W 0.0%, 2024 S 0.0% W 0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 13.5 MVA on 02/07/2019 at 00:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 22.1 | 22.1 | 22.1 |  | 22.1 |  | 22.1 | 24.3 |  | 24.3 |  | 24.3 | 24.3 | 24.3
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 11.8 | 11.8 | 11.8 |  | 11.9 |  | 11.9 | 13.3 |  | 13.3 |  | 13.2 | 13.1 | 13.2
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.937 | 0.937 | 0.937 |  | 0.937 |  | 0.937 | 0.932 |  | 0.932 |  | 0.932 | 0.932 | 0.932
|  |  |  | ECC Rating (MVA) |  | 13.7 | 13.7 | 13.7 |  | 13.7 |  | 13.7 | 14.7 |  | 14.7 |  | 14.7 | 14.7 | 14.7
|  |  |  | 50 PoE Load (MVA) |  | 11.5 | 11.5 | 11.5 |  | 11.6 |  | 11.6 | 13 |  | 12.9 |  | 12.8 | 12.8 | 12.9
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.7 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  |  | Hours PA > 95% Peak Load |  | 11.5 | 11.5 | 11.5 |  | 11.5 |  | 11.5 | 11.5 |  | 11.5 |  | 11.5 | 11.5 | 11.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## WAEA
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | WAEA - Warwick East (33/11kV) | [8 empty] | Supply |  | T058 - Warwick BSP
| Description |  |  |  | Region is South West
Transformer size is 2x33/11kV 25/32MVA ONAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -1.0%, 2021 S -0.3% W -0.3%2022 S -0.7% W -0.7%2023 S -0.4% W -0.4%2024 S -0.4% W -0.4
|  |  | Latest Peak Compensated Load | [5 empty] | 18.6 MVA on 29/01/2020 at 16:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 69.6 | 69.6 | 69.6 |  | 69.6 |  | 69.6 | 79.2 |  | 79.2 |  | 79.2 | 79.2 | 79.2
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 21.5 | 21.3 | 21.3 |  | 21.3 |  | 21.3 | 18.2 |  | 18 |  | 17.8 | 17.7 | 17.7
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.984 | 0.984 | 0.984 |  | 0.984 |  | 0.984 | 0.99 |  | 0.99 |  | 0.99 | 0.99 | 0.99
|  |  |  | ECC Rating (MVA) |  | 38.8 | 38.8 | 38.8 |  | 38.8 |  | 38.8 | 42.2 |  | 42.2 |  | 42.2 | 42.2 | 42.2
|  |  |  | 50 PoE Load (MVA) |  | 18.8 | 18.7 | 18.6 |  | 18.7 |  | 18.6 | 17.2 |  | 17 |  | 16.8 | 16.7 | 16.7
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.9 | 0.9 | 0.9 |  | 0.9 |  | 0.9 | 0.9 |  | 0.9 |  | 0.8 | 0.8 | 0.8
|  |  |  | Hours PA > 95% Peak Load |  | 13 | 13 | 13 |  | 13 |  | 13 | 13 |  | 13 |  | 13 | 13 | 13
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## WALL
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | WALL - Wallaville (66/11kV) | [8 empty] | Supply |  | BUND - Bundaberg BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 2x66/11kV 8/10MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.3%, 2021 S 0.3% W 0.3%, 2022 S 0.1% W 0.1%, 2023 S 0.3% W 0.3%, 2024 S 0.0% W 0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 8.9 MVA on 16/12/2019 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 25.6 | 25.6 | 25.6 |  | 25.6 |  | 25.6 | 27 |  | 27 |  | 27 | 27 | 27
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 9.3 | 9.4 | 9.4 |  | 9.4 |  | 9.5 | 5.5 |  | 5.5 |  | 5.5 | 5.5 | 5.5
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.974 | 0.974 | 0.974 |  | 0.974 |  | 0.974 | 0.958 |  | 0.958 |  | 0.958 | 0.958 | 0.958
|  |  |  | ECC Rating (MVA) |  | 14.7 | 14.7 | 14.7 |  | 14.7 |  | 14.7 | 15 |  | 15 |  | 15 | 15 | 15
|  |  |  | 50 PoE Load (MVA) |  | 8.6 | 8.7 | 8.7 |  | 8.7 |  | 8.8 | 5.2 |  | 5.2 |  | 5.2 | 5.2 | 5.2
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.4 | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Hours PA > 95% Peak Load |  | 7.5 | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 | 7.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## WAND
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | WAND - Wandoan (33/22kV) | [8 empty] | Supply |  | COLU - Columboola BSP
| Description |  |  |  | Region is South West
Transformer size is 2x33/22kV 5MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.1%, 2021 S 0.0% W 0.0%, 2022 S -0.1% W -0.1%2023 S 0.0% W 0.0%, 2024 S -0.2% W -0.2
|  |  | Latest Peak Compensated Load | [5 empty] | 2.9 MVA on 16/12/2019 at 19:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 12.2 | 12.2 | 12.2 |  | 12.2 |  | 12.2 | 14.5 |  | 14.5 |  | 14.5 | 14.5 | 14.5
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 3.1 | 3.1 | 3.1 |  | 3.1 |  | 3.1 | 2.8 |  | 2.8 |  | 2.8 | 2.8 | 2.8
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.996 | 0.996 | 0.996 |  | 0.996 |  | 0.996 | 0.997 |  | 0.997 |  | 0.997 | 0.997 | 0.997
|  |  |  | ECC Rating (MVA) |  | 7.1 | 7.1 | 7.1 |  | 7.1 |  | 7.1 | 7.5 |  | 7.5 |  | 7.5 | 7.5 | 7.5
|  |  |  | 50 PoE Load (MVA) |  | 2.8 | 2.8 | 2.8 |  | 2.8 |  | 2.8 | 2.6 |  | 2.6 |  | 2.6 | 2.6 | 2.6
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 48 | 48 | 48 |  | 48 |  | 48 | 48 |  | 48 |  | 48 | 48 | 48
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## WEBU
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | WEBU - West Bundaberg (66/11kV) | [8 empty] | Supply |  | BUND - Bundaberg BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 2x66/11kV 15/18/25MVA ONAN/ODAN/ODAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -1.0%, 2021 S 0.1% W 0.1%, 2022 S -0.2% W -0.2%2023 S 0.0% W 0.0%, 2024 S 0.0% W 0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 29.4 MVA on 20/02/2020 at 14:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 61.3 | 61.3 | 61.3 |  | 61.3 |  | 61.3 | 65 |  | 65 |  | 65 | 65 | 65
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 31.8 | 31.8 | 31.8 |  | 32 |  | 32.1 | 21.9 |  | 21.9 |  | 21.7 | 21.6 | 21.7
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 1 | 1 | 1 |  | 1 |  | 1 | 0.999 |  | 0.999 |  | 0.999 | 0.999 | 0.999
|  |  |  | ECC Rating (MVA) |  | 34.3 | 34.3 | 34.3 |  | 34.3 |  | 34.3 | 36.5 |  | 36.5 |  | 36.5 | 36.5 | 36.5
|  |  |  | 50 PoE Load (MVA) |  | 29.4 | 29.3 | 29.4 |  | 29.5 |  | 29.6 | 20.8 |  | 20.7 |  | 20.6 | 20.5 | 20.6
|  |  |  | 50 PoE Load > 95% (MVA) |  | 1.5 | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Hours PA > 95% Peak Load |  | 7 | 7 | 7 |  | 7 |  | 7 | 7 |  | 7 |  | 7 | 7 | 7
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## WEDA
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | WEDA - West Dalby (33/11kV) | [8 empty] | Supply |  | T002 - Dalby East BSP
| Description |  |  |  | Region is South West
Transformer size is 1x33/11KV 6.25MVA ONAN;1x33/11KV 6.3MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -2.2%, 2021 S -0.9% W -0.9%2022 S -0.3% W -0.3%2023 S 0.7% W 0.7%, 2024 S -0.2% W -0.2
|  |  | Latest Peak Compensated Load | [5 empty] | 4.7 MVA on 09/12/2019 at 15:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 14.6 | 14.6 | 14.6 |  | 14.6 |  | 14.6 | 17.5 |  | 17.5 |  | 17.5 | 17.5 | 17.5
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 5.9 | 5.9 | 5.9 |  | 5.9 |  | 6 | 4.8 |  | 4.7 |  | 4.7 | 4.7 | 4.7
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.917 | 0.917 | 0.917 |  | 0.917 |  | 0.917 | 0.932 |  | 0.932 |  | 0.932 | 0.932 | 0.932
|  |  |  | ECC Rating (MVA) |  | 8.2 | 8.2 | 8.2 |  | 8.2 |  | 8.2 | 9.3 |  | 9.3 |  | 9.3 | 9.3 | 9.3
|  |  |  | 50 PoE Load (MVA) |  | 5.2 | 5.2 | 5.2 |  | 5.2 |  | 5.3 | 4.5 |  | 4.4 |  | 4.4 | 4.4 | 4.4
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 11.5 | 11.5 | 11.5 |  | 11.5 |  | 11.5 | 11.5 |  | 11.5 |  | 11.5 | 11.5 | 11.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## WEMA
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | WEMA - West Mackay (33/11kV) | [8 empty] | Supply |  | MACK - Mackay BSP
| Description |  |  |  | Region is Mackay
Transformer size is 2x33/11kV 15/20MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.3%, 2021 S -0.1% W -0.1%2022 S -0.4% W -0.4%2023 S -0.1% W -0.1%2024 S -0.3% W -0.3
|  |  | Latest Peak Compensated Load | [5 empty] | 17.9 MVA on 12/02/2020 at 16:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 38.7 | 38.7 | 38.7 |  | 38.7 |  | 38.7 | 40.9 |  | 40.9 |  | 40.9 | 40.9 | 40.9
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 21 | 21 | 21 |  | 21 |  | 21 | 11.2 |  | 11.1 |  | 11 | 10.9 | 11
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.972 | 0.972 | 0.972 |  | 0.972 |  | 0.972 | 0.985 |  | 0.985 |  | 0.985 | 0.985 | 0.985
|  |  |  | ECC Rating (MVA) |  | 22.3 | 22.3 | 22.3 |  | 22.3 |  | 22.3 | 23.4 |  | 23.4 |  | 23.4 | 23.4 | 23.4
|  |  |  | 50 PoE Load (MVA) |  | 18.6 | 18.5 | 18.5 |  | 18.5 |  | 18.5 | 10.9 |  | 10.8 |  | 10.7 | 10.7 | 10.7
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.9 | 0.9 | 0.9 |  | 0.9 |  | 0.9 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | Hours PA > 95% Peak Load |  | 9.5 | 9.5 | 9.5 |  | 9.5 |  | 9.5 | 9.5 |  | 9.5 |  | 9.5 | 9.5 | 9.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## WETO
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | WETO - West Toowoomba (33/11kV) | [8 empty] | Supply |  | T116 - Torrington BSP
| Description |  |  |  | Region is South West
Transformer size is 3x33/11kV 10MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.9%, 2021 S -0.1% W -0.1%2022 S -0.3% W -0.3%2023 S -0.1% W -0.1%2024 S -0.3% W -0.3
|  |  | Latest Peak Compensated Load | [5 empty] | 27.2 MVA on 04/06/2019 at 15:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 30 | 30 | 30 |  | 30 |  | 30 | 36.2 |  | 36.2 |  | 36.2 | 36.2 | 36.2
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 22.5 | 22.4 | 22.4 |  | 22.4 |  | 22.4 | 22.6 |  | 22.5 |  | 22.3 | 22.2 | 22.2
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.967 | 0.967 | 0.967 |  | 0.967 |  | 0.967 | 0.988 |  | 0.988 |  | 0.988 | 0.988 | 0.988
|  |  |  | ECC Rating (MVA) |  | 23.8 | 23.8 | 23.8 |  | 23.8 |  | 23.8 | 26.9 |  | 26.9 |  | 26.9 | 26.9 | 26.9
|  |  |  | 50 PoE Load (MVA) |  | 20.5 | 20.4 | 20.4 |  | 20.4 |  | 20.4 | 21.2 |  | 21.1 |  | 20.9 | 20.8 | 20.9
|  |  |  | 50 PoE Load > 95% (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1.1 |  | 1.1 |  | 1 | 1 | 1
|  |  |  | Hours PA > 95% Peak Load |  | 9 | 9 | 9 |  | 9 |  | 9 | 9 |  | 9 |  | 9 | 9 | 9
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 6 | 6 | 6 |  | 6 |  | 6 | 6 |  | 6 |  | 6 | 6 | 6
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## WEWA
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | WEWA - West Warwick (33/11kV) | [8 empty] | Supply |  | T058 - Warwick BSP
| Description |  |  |  | Region is South West
Transformer size is 2x33/11kV 10/12.5MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.4%, 2021 S 0.1% W 0.1%, 2022 S -0.2% W -0.2%2023 S -0.1% W -0.1%2024 S -0.2% W -0.2
|  |  | Latest Peak Compensated Load | [5 empty] | 10.8 MVA on 29/01/2020 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 27 | 27 | 27 |  | 27 |  | 27 | 30 |  | 30 |  | 30 | 30 | 30
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 12.7 | 12.7 | 12.7 |  | 12.7 |  | 12.7 | 10.3 |  | 10.2 |  | 10.1 | 10.1 | 10.1
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.953 | 0.953 | 0.953 |  | 0.953 |  | 0.953 | 0.97 |  | 0.97 |  | 0.97 | 0.97 | 0.97
|  |  |  | ECC Rating (MVA) |  | 15.2 | 15.2 | 15.2 |  | 15.2 |  | 15.2 | 16.9 |  | 16.9 |  | 16.9 | 16.9 | 16.9
|  |  |  | 50 PoE Load (MVA) |  | 11 | 11 | 11 |  | 11 |  | 11 | 9.6 |  | 9.6 |  | 9.5 | 9.4 | 9.5
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.5 |  | 0.5 |  | 0.5 | 0.5 | 0.5
|  |  |  | Hours PA > 95% Peak Load |  | 5.5 | 5.5 | 5.5 |  | 5.5 |  | 5.5 | 5.5 |  | 5.5 |  | 5.5 | 5.5 | 5.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## WINT
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | WINT - Winton (66/11kV) | [8 empty] | Supply |  | T095 - Millchester BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 2x66/11kV 4MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.1%, 2021 S -1.1% W -1.1%2022 S -1.5% W -1.5%2023 S -1.2% W -1.2%2024 S -1.0% W -1.0
|  |  | Latest Peak Compensated Load | [5 empty] | 2.9 MVA on 17/12/2019 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 9.4 | 9.4 | 9.4 |  | 9.4 |  | 9.4 | 10.9 |  | 10.9 |  | 10.9 | 10.9 | 10.9
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 3.2 | 3.2 | 3.2 |  | 3.1 |  | 3.1 | 2 |  | 1.9 |  | 1.9 | 1.9 | 1.9
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.994 | 0.994 | 0.994 |  | 0.994 |  | 0.994 | 0.995 |  | 0.995 |  | 0.995 | 0.995 | 0.995
|  |  |  | ECC Rating (MVA) |  | 5.4 | 5.4 | 5.4 |  | 5.4 |  | 5.4 | 6 |  | 6 |  | 6 | 6 | 6
|  |  |  | 50 PoE Load (MVA) |  | 3 | 3 | 2.9 |  | 2.9 |  | 2.9 | 1.9 |  | 1.8 |  | 1.8 | 1.8 | 1.8
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 52 | 52 | 52 |  | 52 |  | 52 | 52 |  | 52 |  | 52 | 52 | 52
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## WIRR
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | WIRR - Wirralie (66/33kV) | [8 empty] | Supply |  | NEWL - Newlands BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1xWIRRSS TX01 66/33KV TRANSF 1
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.7%, 2021 S -0.2% W -0.2%2022 S -0.3% W -0.3%2023 S -0.2% W -0.2%2024 S -0.3% W -0.3
|  |  | Latest Peak Compensated Load | [5 empty] | 0.3 MVA on 17/12/2019 at 19:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 0.63 | 0.63 | 0.63 |  | 0.63 |  | 0.63 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 0.4 | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.916 | 0.916 | 0.916 |  | 0.916 |  | 0.916 | 0.921 |  | 0.921 |  | 0.921 | 0.921 | 0.921
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 0.4 | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 6.5 | 6.5 | 6.5 |  | 6.5 |  | 6.5 | 6.5 |  | 6.5 |  | 6.5 | 6.5 | 6.5
|  |  |  | Raw LAR (MVA) |  | 0.4 | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 1 | 1 | 1 |  | 1 |  | 1 | 1 |  | 1 |  | 1 | 1 | 1
|  |  |  | Mobile Plant Avail (MVA) |  | 2 | 2 | 2 |  | 2 |  | 2 | 2 |  | 2 |  | 2 | 2 | 2
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## WOOD
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | WOOD - Woodhouse Station (66/11kV) | [8 empty] | Supply |  | T193 - Clare South BSP
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1x66/11kV 0.25MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.0%, 2021 S 0.0% W 0.0%, 2022 S 0.0% W 0.0%, 2023 S 0.0% W 0.0%, 2024 S 0.0% W 0.0%
|  |  | Latest Peak Compensated Load | [5 empty] | 0.1 MVA on 01/01/2020 at 17:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.3 | 0.3
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.85 | 0.85 | 0.85 |  | 0.85 |  | 0.85 | 0.85 |  | 0.85 |  | 0.85 | 0.85 | 0.85
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Hours PA > 95% Peak Load |  | 8648 | 8648 | 8648 |  | 8648 |  | 8648 | 8648 |  | 8648 |  | 8648 | 8648 | 8648
|  |  |  | Raw LAR (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## WOOG
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | WOOG - Woodgate (66/11kV) | [8 empty] | Supply |  | ISIS - Isis BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 1x66/11kV 5MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 1.2%, 2021 S 1.2% W 1.2%, 2022 S 1.0% W 1.0%, 2023 S 1.0% W 1.0%, 2024 S 0.7% W 0.7%
|  |  | Latest Peak Compensated Load | [5 empty] | 2.5 MVA on 24/12/2019 at 19:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 5.3 | 5.3 | 5.3 |  | 5.3 |  | 5.3 | 5.3 |  | 5.3 |  | 5.3 | 5.3 | 5.3
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 2.6 | 2.7 | 2.7 |  | 2.7 |  | 2.7 | 2.2 |  | 2.2 |  | 2.2 | 2.2 | 2.2
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.983 | 0.983 | 0.983 |  | 0.983 |  | 0.983 | 0.986 |  | 0.986 |  | 0.986 | 0.986 | 0.986
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 2.4 | 2.5 | 2.5 |  | 2.5 |  | 2.5 | 2 |  | 2.1 |  | 2.1 | 2.1 | 2.1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 8 | 8 | 8 |  | 8 |  | 8 | 8 |  | 8 |  | 8 | 8 | 8
|  |  |  | Raw LAR (MVA) |  | 2.4 | 2.5 | 2.5 |  | 2.5 |  | 2.5 | 2 |  | 2.1 |  | 2.1 | 2.1 | 2.1
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 2.2 | 2.2 | 2.2 |  | 2.2 |  | 2.2 | 2.2 |  | 2.2 |  | 2.2 | 2.2 | 2.2
|  |  |  | Mobile Plant Avail (MVA) |  | 0.6 | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.6 |  | 0.6 |  | 0.6 | 0.6 | 0.6
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## WOOL
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | WOOL - Woolooga (66/11kV) | [8 empty] | Supply |  | KILK - Kilkivan BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 2x66/11kV 5/6.25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.3%, 2021 S -0.2% W -0.2%2022 S -1.2% W -1.2%2023 S -1.3% W -1.3%2024 S -1.9% W -1.9
|  |  | Latest Peak Compensated Load | [5 empty] | 4.4 MVA on 16/12/2019 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 17.7 | 17.7 | 17.7 |  | 17.7 |  | 17.7 | 18.7 |  | 18.7 |  | 18.7 | 18.7 | 18.7
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 4.9 | 4.8 | 4.8 |  | 4.7 |  | 4.7 | 3.5 |  | 3.5 |  | 3.4 | 3.3 | 3.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.963 | 0.963 | 0.963 |  | 0.963 |  | 0.963 | 0.982 |  | 0.982 |  | 0.982 | 0.982 | 0.982
|  |  |  | ECC Rating (MVA) |  | 9.3 | 9.3 | 9.3 |  | 9.3 |  | 9.3 | 9.3 |  | 9.3 |  | 9.3 | 9.3 | 9.3
|  |  |  | 50 PoE Load (MVA) |  | 4.4 | 4.3 | 4.3 |  | 4.2 |  | 4.2 | 3.3 |  | 3.3 |  | 3.2 | 3.2 | 3.1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 1.5 | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.5 | 1.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## WOSO
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | WOSO - Woodstock South (66/11kV) | [8 empty] | Supply |  | TMES - Townsville Mesh
| Description |  |  |  | Region is Nth Queensland
Transformer size is 1xWOSO TX01 66/11kV TRANSF 1
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 2.3%, 2021 S 3.1% W 3.1%, 2022 S 2.8% W 2.8%, 2023 S 2.8% W 2.8%, 2024 S 2.5% W 2.5%
|  |  | Latest Peak Compensated Load | [5 empty] | 1.3 MVA on 19/01/2020 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 8.6 | 8.6 | 8.6 |  | 8.6 |  | 8.6 | 9.4 |  | 9.4 |  | 9.4 | 9.4 | 9.4
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 1.4 | 1.4 | 1.5 |  | 1.5 |  | 1.5 | 1 |  | 1 |  | 1 | 1 | 1.1
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.98 | 0.98 | 0.98 |  | 0.98 |  | 0.98 | 0.892 |  | 0.892 |  | 0.892 | 0.892 | 0.892
|  |  |  | ECC Rating (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 50 PoE Load (MVA) |  | 1.3 | 1.3 | 1.3 |  | 1.4 |  | 1.4 | 0.9 |  | 1 |  | 1 | 1 | 1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 8 | 8 | 8 |  | 8 |  | 8 | 8 |  | 8 |  | 8 | 8 | 8
|  |  |  | Raw LAR (MVA) |  | 1.3 | 1.3 | 1.3 |  | 1.4 |  | 1.4 | 0.9 |  | 1 |  | 1 | 1 | 1
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 1.8 | 1.8 | 1.8 |  | 1.8 |  | 1.8 | 1.8 |  | 1.8 |  | 1.8 | 1.8 | 1.8
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## WOWA
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | WOWA - Wowan (66/22kV) | [8 empty] | Supply |  | T026 - Biloela BSP
| Description |  |  |  | Region is Capricornia
Transformer size is 2x66/22kV 5/6.3MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W -0.5%, 2021 S -0.3% W -0.3%2022 S -0.4% W -0.4%2023 S -0.2% W -0.2%2024 S -0.4% W -0.4
|  |  | Latest Peak Compensated Load | [5 empty] | 5.5 MVA on 16/12/2019 at 19:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 16.1 | 16.1 | 16.1 |  | 16.1 |  | 16.1 | 18 |  | 18 |  | 18 | 18 | 18
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 6.4 | 6.4 | 6.4 |  | 6.4 |  | 6.4 | 4.9 |  | 4.8 |  | 4.8 | 4.7 | 4.8
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.98 | 0.98 | 0.98 |  | 0.98 |  | 0.98 | 0.997 |  | 0.997 |  | 0.997 | 0.997 | 0.997
|  |  |  | ECC Rating (MVA) |  | 9 | 9 | 9 |  | 9 |  | 9 | 9.4 |  | 9.4 |  | 9.4 | 9.4 | 9.4
|  |  |  | 50 PoE Load (MVA) |  | 5.8 | 5.8 | 5.7 |  | 5.7 |  | 5.7 | 4.6 |  | 4.5 |  | 4.5 | 4.5 | 4.5
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.3 | 0.3 | 0.3 |  | 0.3 |  | 0.3 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 8 | 8 | 8 |  | 8 |  | 8 | 8 |  | 8 |  | 8 | 8 | 8
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## YARA
Bulk Summary Information and Peak Load Forecast
Substation |  |  |  | YARA - Yarranlea BSP (110/33kV) | [8 empty] | Supply |  | QMRG - Middle Ridge (Ergon) TCP
Description |  |  |  | Region is South West
Transformer size is 2x106/33/11kV 15MVA ON
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
|  | Latest Peak Compensated Load | [5 empty] | 23.8 MVA on 16/12/2019 at 17:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[5 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  | NCC Rating (MVA) |  | 30 | 30 | 30 |  | 30 |  | 30 | 30 |  | 30 |  | 30 | 30 | 30
|  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | 10 PoE Load (MVA) |  | 27.2 | 27.2 | 27.2 |  | 27.3 |  | 27.3 | 19.9 |  | 21.3 |  | 21.1 | 21 | 21
LARn (MVA)
LARn (MW)
|  |  | Power Factor at Peak Load |  | 0.932 | 0.932 | 0.932 |  | 0.932 |  | 0.932 | 0.979 |  | 0.979 |  | 0.979 | 0.979 | 0.979
|  |  | ECC Rating (MVA) |  | 15 | 15 | 15 |  | 15 |  | 15 | 15 |  | 15 |  | 15 | 15 | 15
|  |  | 50 PoE Load (MVA) |  | 25.1 | 25.1 | 25.1 |  | 25.2 |  | 25.2 | 19 |  | 20.2 |  | 20.1 | 20 | 20
|  |  | 50 PoE Load > 95% (MVA) |  | 1.3 | 1.3 | 1.3 |  | 1.3 |  | 1.3 | 1 |  | 1 |  | 1 | 1 | 1
|  |  | Hours PA > 95% Peak Load |  | 39.5 | 39.5 | 39.5 |  | 39.5 |  | 39.5 | 39.5 |  | 39.5 |  | 39.5 | 39.5 | 39.5
|  |  | Raw LAR (MVA) |  | 10.1 | 10.1 | 10.1 |  | 10.2 |  | 10.2 | 4 |  | 5.2 |  | 5.1 | 5 | 5
|  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Remote Trans Avail (MVA) |  | 7 | 7 | 7 |  | 7 |  | 7 | 7 |  | 7 |  | 7 | 7 | 7
|  |  | Manual Trans Avail (MVA) |  | 1.7 | 1.7 | 1.7 |  | 1.7 |  | 1.7 | 1.7 |  | 1.7 |  | 1.7 | 1.7 | 1.7
|  |  | Mobile Plant Avail (MVA) |  | 2.5 | 2.5 | 2.5 |  | 2.5 |  | 2.5 | 2.5 |  | 2.5 |  | 2.5 | 2.5 | 2.5
|  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## YARR
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | YARR - Yarraman (66/11kV) | [8 empty] | Supply |  | H018 - Tarong BSP
| Description |  |  |  | Region is Wide Bay
Transformer size is 2x66/11kV 5/6MVA ON/ONB
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.2%, 2021 S 0.5% W 0.5%, 2022 S -1.7% W -1.7%2023 S -0.5% W -0.5%2024 S 0.1% W 0.1%
|  |  | Latest Peak Compensated Load | [5 empty] | 4 MVA on 03/02/2020 at 18:00
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 15.5 | 15.5 | 15.5 |  | 15.5 |  | 15.5 | 17.9 |  | 17.9 |  | 17.9 | 17.9 | 17.9
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 4.8 | 4.8 | 4.8 |  | 4.8 |  | 4.8 | 3.3 |  | 3.3 |  | 3.3 | 3.2 | 3.3
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.966 | 0.966 | 0.966 |  | 0.966 |  | 0.966 | 0.979 |  | 0.979 |  | 0.979 | 0.979 | 0.979
|  |  |  | ECC Rating (MVA) |  | 8.5 | 8.5 | 8.5 |  | 8.5 |  | 8.5 | 9 |  | 9 |  | 9 | 9 | 9
|  |  |  | 50 PoE Load (MVA) |  | 4.3 | 4.2 | 4.2 |  | 4.2 |  | 4.2 | 3.2 |  | 3.2 |  | 3.1 | 3.1 | 3.1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 |  | 0.2 |  | 0.2 | 0.2 | 0.2
|  |  |  | Hours PA > 95% Peak Load |  | 9.5 | 9.5 | 9.5 |  | 9.5 |  | 9.5 | 9.5 |  | 9.5 |  | 9.5 | 9.5 | 9.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## YASO
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | YASO - Yarranlea South (33/11kV) | [8 empty] | Supply |  | YARA - Yarranlea BSP
| Description |  |  |  | Region is South West
Transformer size is 1x33/11kV 1.5MVA ONAN;1x33/11kV 1MVA ONAN
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.0%, 2021 S 0.1% W 0.1%, 2022 S -0.1% W -0.1%2023 S 0.2% W 0.2%, 2024 S -0.2% W -0.2
|  |  | Latest Peak Compensated Load | [5 empty] | 1.4 MVA on 16/12/2019 at 17:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 2.8 | 2.8 | 2.8 |  | 2.8 |  | 2.8 | 2.8 |  | 2.8 |  | 2.8 | 2.8 | 2.8
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 1.5 | 1.5 | 1.6 |  | 1.6 |  | 1.6 | 1.1 |  | 1.1 |  | 1.1 | 1.1 | 1.1
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.85 | 0.85 | 0.85 |  | 0.85 |  | 0.85 | 0.85 |  | 0.85 |  | 0.85 | 0.85 | 0.85
|  |  |  | ECC Rating (MVA) |  | 1.2 | 1.2 | 1.2 |  | 1.2 |  | 1.2 | 1.3 |  | 1.3 |  | 1.3 | 1.3 | 1.3
|  |  |  | 50 PoE Load (MVA) |  | 1.4 | 1.4 | 1.4 |  | 1.4 |  | 1.4 | 1.1 |  | 1 |  | 1 | 1 | 1
|  |  |  | 50 PoE Load > 95% (MVA) |  | 0.1 | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 |  | 0.1 |  | 0.1 | 0.1 | 0.1
|  |  |  | Hours PA > 95% Peak Load |  | 9 | 9 | 9 |  | 9 |  | 9 | 9 |  | 9 |  | 9 | 9 | 9
|  |  |  | Raw LAR (MVA) |  | 0.2 | 0.2 | 0.2 |  | 0.2 |  | 0.2
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 1.2 | 1.2 | 1.2 |  | 1.2 |  | 1.2 | 1.2 |  | 1.2 |  | 1.2 | 1.2 | 1.2
|  |  |  | Mobile Plant Avail (MVA) |  | 0.4 | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.4 |  | 0.4 |  | 0.4 | 0.4 | 0.4
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Rural/ Remote | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote |  | Rural/ Remote |  | Rural/ Remote | Rural/ Remote | Rural/ Remote
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index

## YEPP
Zone Summary Information and Peak Load Forecast
| Substation |  |  |  | YEPP - Yeppoon (66/11kV) | [8 empty] | Supply |  | RMES - Rockhampton Mesh
| Description |  |  |  | Region is Capricornia
Transformer size is 2x66/11kV 16/25MVA ONAN/ONAF
Capacity of commissioned Embedded Generation (with Connection Agreements) is 0.0 MVA
Growth Rates |  |  |  |  | 2020 W 0.3%, 2021 S 0.6% W 0.6%, 2022 S 0.6% W 0.6%, 2023 S 0.6% W 0.6%, 2024 S 0.5% W 0.5%
|  |  | Latest Peak Compensated Load | [5 empty] | 22.5 MVA on 20/02/2020 at 18:30
Hours PA Exceeding 95% Peak Load
Hours PA Exceeding 95% Peak Load
|  |  |  | PEAK LOAD FORECAST AND CAPACITY |  | SUMMER | [6 empty] | WINTER
[6 empty] | 2020/21 | 2021/22 | 2022/23 |  | 2023/24 |  | 2024/25 | 2020 |  | 2021 |  | 2022 | 2023 | 2024
|  |  |  | NCC Rating (MVA) |  | 59 | 59 | 59 |  | 59 |  | 59 | 67.8 |  | 67.8 |  | 67.8 | 67.8 | 67.8
|  |  |  | Contracted non-network (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | 10 PoE Load (MVA) |  | 24 | 24.2 | 24.3 |  | 24.2 |  | 24.4 | 17.4 |  | 17.4 |  | 17.4 | 17.4 | 17.6
LARn (MVA)
LARn (MW)
|  |  |  | Power Factor at Peak Load |  | 0.987 | 0.987 | 0.987 |  | 1 |  | 1 | 0.994 |  | 0.994 |  | 0.994 | 0.994 | 0.994
|  |  |  | ECC Rating (MVA) |  | 32.3 | 32.3 | 32.3 |  | 32.3 |  | 32.3 | 36.3 |  | 36.3 |  | 36.3 | 36.3 | 36.3
|  |  |  | 50 PoE Load (MVA) |  | 22.2 | 22.4 | 22.5 |  | 22.7 |  | 22.9 | 16.7 |  | 16.7 |  | 16.7 | 16.8 | 16.9
|  |  |  | 50 PoE Load > 95% (MVA) |  | 1.1 | 1.1 | 1.1 |  | 1.1 |  | 1.1 | 0.8 |  | 0.8 |  | 0.8 | 0.8 | 0.8
|  |  |  | Hours PA > 95% Peak Load |  | 7.5 | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 |  | 7.5 |  | 7.5 | 7.5 | 7.5
Raw LAR (MVA)
|  |  |  | Auto Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Remote Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Manual Trans Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Mobile Plant Avail (MVA) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(30min) |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 |  | 0 |  | 0 | 0 | 0
|  |  |  | Shed(4Hour) |  | 1.5 | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.5 |  | 1.5 |  | 1.5 | 1.5 | 1.5
LARc (MVA)
LARc (MW)
|  |  |  | Substation Category |  | Regional Centre | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre |  | Regional Centre |  | Regional Centre | Regional Centre | Regional Centre
|  |  |  | Meets Security Standard |  | Yes | Yes | Yes |  | Yes |  | Yes | Yes |  | Yes |  | Yes | Yes | Yes
Return to Index