## Disclaimer & Introduction
1. Disclaimer and Introduction
1.1 Disclaimer
These set of Subtransmission load flow studies results are prepared and made available solely for information purposes as part of the Distribution Annual Planning Report (DAPR). Whilst care was taken in the preparation of the information in this report, and it is provided with the best intentions and good faith, the Network Modelling Team accepts no responsibility or liability (including without limitation, liability to any person by reason of negligence or negligent mis-statement) for any loss or damage that may be incurred by any person acting in reliance on this information or assumptions drawn from it, except to the extent that liability under any applicable Queensland or Commonwealth of Australia statute cannot be excluded.
Ergon Energy makes no representation or warranty as to the accuracy, reliability, completeness or suitability for any particular purpose of the information in this document. All information should be independently investigated, reviewed, analysed, and verified, and must not be relied upon in connection with any investment proposal or decision. The information contained in this report is subject to annual review.
The Known Issues section below outlines some factors that could affect the accuracy of the results presented in this studies summary and should be considered when making network augmentation or financial decisions based on these values. The basis of the disclosed studies results are the network demand forecasts obtained from the SIFT system/database. The Network Modelling Team obtain these forecast values as populated by the Strategic Forecasting Team following quality assurance processes for accuracy.
1.2 Introduction and Methodology
This load flow studies summary is prepared to provide a reference for Strategic Planners during the preparation of the DAPR. Engineers should carry out their own due diligence on the information provided by this summary prior to applying it to engineering activities. The results of these studies contained herein are produced as per the methodology described below.
In preparing the load flow summary results:
· The subtransmission network model was developed and prepared using Power Factory 2021 SP4. The reported studies results summary was produced using the same software.
· All approved projects (in the form of variations) and new connection load/generators are incorporated into the model.
· Obtain 10 and 50 PoE demand forecasts from SIFT and minimum demand forecast from Tableau.
· Using Python automation to pull demand forecasts into Power Factory model.
· Run Load Flow studies for each of the following scenarios and document result summaries:
Ergon Energy Network (EE)
a) Time of Day conditions with SIFT 10% PoE profile (10PoE_EE_NNC);
b) Static normal conditions with minimum demand profile (MinLoad_EE_NNC);
c) N-1 conditions with SIFT 50% PoE profile (50PoE_EE_N-1);
d) N-1 conditions with minimum demand profile (MinLoad_EE_N-1);
1.3 High level Process Summary
1. Derive Master Model
2. Activate Model
3. Activate Load Characteristic Application Study Case (ie. 2023TransLF-ErgonSubtrans-WithVars for EE, EnergexST_AppPrjs[DAPR2023] for EX)
4. Run Forecast Load script for required conditions (e.g. 10PoE Day SUMWIN for 10PoE peak conditions)
5. Run Power Factory Information Producer (ie. a Report Nearly Anything Sequential Creator and Task Automation or SubtransFeederForecastProducer)
6. Repeat steps 3-5 for other Load Characteristic Configurations if required
7. Repeat 5 and 6 for WD
8. Run a Python Interpreter that reads the output files and produces the formatted document
1.4 Definition of Terms Feeder Capacity and Forecast Tables
Term | Definition
10 PoE Load (A) | Peak load forecast with 10% probability of being exceeded (one in every 10 years will be exceeded). Based on normal expected growth rates and weather corrected starting loads.
50 PoE Load (A) | Peak load forecast with 50% probability of being exceeded (one in every two years will be exceeded). Based on normal expected growth rates & weather corrected starting loads. This is the worst case (highest) load forecast beween summer day and summer night.
ECC Rating (A) | Emergency Cyclic Capacity – the long term firm delivery capacity under single contingency conditions. Some underground cables are installed in close proximity to other circuits and are normally de‑rated to allow for the heat generated by the adjacent cables. ECC is the higher capacity available when any adjacent circuits have been unloaded. For overhead conductors which do not benefit from this phenomenon, the ECC is synonymous with the NCC.
Hours PA > 95% Peak Load | The forecast number of hours per annum where the load exceeded 95% of the peak 50 PoE demand. This information is not readily available for every feeder without significant analysis being undertaken. As such, this has only been provided where a feeder does not meet the Safety Net criteria or is otherwise in the Limitations and Proposed Solutions table.
NNC | Normal Network Configuration
NCC Rating (A) | Normal Cyclic Capacity - the total capacity with all network components and equipment intact. This is the maximum permissible peak daily loading for a given load cycle that a feeder can supply each day of its life. For overhead feeders, the NCC is the conductor rating with an assumed 1m/s wind, orthogonal to the line. For underground cables, the NCC assumes that there are sufficient temperature and current operating margins from the thermal inertia of the cable and its surroundings.
Power Factor (System Normal) | Lowest power factor along the feeder at 10 PoE Peak Load. Where the Power Factor is either 0 or blank, the feeder is a normally open feeder that does not have load under System Normal conditions.
Security Standard | For security standard application, the general type of customer a sub-transmission, or transmission feeder is supplying.
Transfers | This is the total amount of load transfers that are available following the worst case network contingency. This includes automatic transfers that are controlled automatically through SCADA and are generally implemented within a minute, load transfers that can be implemented through screen switching by a network controller, manual transfers that are deployed via manually controlled switchgear locally by field staff, and mobile generation which can be deployed by field staff by moving generation to specific sites.
Note: It should be noted under the Safety Net in the Distribution Authority, it is generally assumed that 4MVA (70A) of generation is available for Urban feeders and 10MVA (170A) for Rural feeders to meet specific criteria. These values have been used as a default in the forecast tables where these are sufficient to reduce the 50PoE load below the ECC rating. Where the load is still above the ECC rating, specific load transfers have been calculated for the feeder to determine whether the Safety Net criteria is met.

## Important Info-MinLF_EE_NNC
2. Important Information
2.1 Study Information - MinLF_EE_NNC
A summary of most information used as inputs is given in the Study Info Worksheet referenced below. This includes what Project Version was used, Study times, Variations, what Generators are included etc.
2.2 Results
The results of this study are referenced in the documented versions disclosed below.
Result Version: | MinLF_EE_NNC_20231015_0911 MinLF_EE_NNC_20231016_1653
2.3 Known Issues and Limitations
· The List of Subtransmission Projects to be stored as Variations has been produced manually from Copperleaf and SIFT for the next 10 years. The list provided by Josh Hockey 2023/08/01 is being checked against the list.
· The project information dumps do not contain the list of Generators that are active. It is not expected that any EQL connected generators are involved in this calculation except for the isolated NWPS covering Mount Isa.
· The Report is not suitable to determine "directionality" of the real or reactive power-flows due to the use of absolute value functions prior to the limits being calculated.
· N-1 Ratings are not considered in the report (eg. a feeder in a shared cable trench will have an increased rating when the other feeder is unloaded).
3. Additional Information
2.1 Information About Variables
The Values for a given timeslot shown are calculated as follows. All of the values will be for the line element in Power Factory with the Loading Constraint.
This means that the Power Factor and Voltage values are recorded at the line that is considered the most "limited" not the minimum voltage on the feeder or the minimum Power Factor on the feeder.
For each Contingency Event the values for each line are recorded with them eventually ending up in the following fields
% of Rated A: The % Utilisation called "loading" in Power Factory [c:loading]
Loading (A): Absolute Maximum Current for Both Ends in kA
Loading (MVA): Absolute Maximum Apparent Power for Both Ends in MVA
Loading (MW): Absolute Maximum Real Power for Both Ends in MW
Power Factor: Absolute Min Power Factor for Both Ends
Rating (A): Line Nominal Rating using [e:Inom_a]
Min Voltage at Constrained Conductor: Min Voltage seen on both sides of the feeder line
Once they are calculated for each feeder and Timeslot the Limiting entry is determined. This will be the values for a single line limited in the following order.
At each step all lines that share the "limiting" value will be recorded, provided their float representative is identical.
Minor differences in the float representation will result in the Min or Max value being utilised even if the value when considering real life significant figures are otherwise identical.
1. % of Rated A - Max
2. Rating (A) - Min
3. Loading (MVA) - Max
The following limit calculations are applied to ensure only 1 line's values are recorded even if all entries have the same electrical loading characteristics.
4. Contingency Outage: Alphabetical Max
Note that "_NNC" is used with is a "Normal Network Configuration" contingency where nothing is taken out of service. If it is displayed, then taking a feeder out of service did not make a recordable difference to the feeder loading.
If multiple feeder outage contingencies have the same effect on the feeder, then the higher alphabetical name will be recorded.
5. Limiting Line Name: Alphabetical Min: This is to ensure there is a unique value
6. Current Study Case Time: Alphabetical Min: This is a stopgap to ensure there is a unique value

## MinLF_EE_NNC
Grid Association | Associated Feeders | Variable | 2024 SD | 2025 SD | 2026 SD | 2027 SD | 2028 SD
CA-Dysart | 6064_Dysart - Saraji Mine 66 kV | % of Rated A | 4.932% | 4.932% | 4.932% | 4.932% | 4.932%
CA-Dysart | 6064_Dysart - Saraji Mine 66 kV | Limiting Line Name | 3-Phase Link 66kV_Term7_6064 SARAJI MINE | 3-Phase Link 66kV_Term7_6064 SARAJI MINE | 3-Phase Link 66kV_Term7_6064 SARAJI MINE | 3-Phase Link 66kV_Term7_6064 SARAJI MINE | 3-Phase Link 66kV_Term7_6064 SARAJI MINE
CA-Dysart | 6064_Dysart - Saraji Mine 66 kV | Loading (A) | 246.6115 | 246.6111 | 246.6109 | 246.6107 | 246.6106
CA-Dysart | 6064_Dysart - Saraji Mine 66 kV | Loading (MVA) | 29.5 | 29.5 | 29.5 | 29.5 | 29.5
CA-Dysart | 6064_Dysart - Saraji Mine 66 kV | Loading (MW) | 29.5 | 29.5 | 29.5 | 29.5 | 29.5
CA-Dysart | 6064_Dysart - Saraji Mine 66 kV | Power Factor | 1 | 1 | 1 | 1 | 1
CA-Dysart | 6064_Dysart - Saraji Mine 66 kV | Rating (A) | 5000 | 5000 | 5000 | 5000 | 5000
CA-Dysart | 6064_Dysart - Saraji Mine 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Dysart | 6064_Dysart - Saraji Mine 66 kV | Min Voltage at Constrained Conductor | 69.0634 | 69.0635 | 69.0635 | 69.0636 | 69.0636
CA-Dysart | 6064_Dysart - Saraji Mine 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Dysart | 6130_Dysart - Vermont 66 kV | % of Rated A | 14.3% | 14.3% | 14.3% | 14.3% | 14.3%
CA-Dysart | 6130_Dysart - Vermont 66 kV | Limiting Line Name | TR_LINE 82005_1 | TR_LINE 82005_1 | TR_LINE 82005_1 | TR_LINE 82005_1 | TR_LINE 82005_1
CA-Dysart | 6130_Dysart - Vermont 66 kV | Loading (A) | 31.1711 | 31.171 | 31.171 | 31.171 | 31.171
CA-Dysart | 6130_Dysart - Vermont 66 kV | Loading (MVA) | 3.7287 | 3.7287 | 3.7287 | 3.7287 | 3.7287
CA-Dysart | 6130_Dysart - Vermont 66 kV | Loading (MW) | 3.7272 | 3.7272 | 3.7272 | 3.7272 | 3.7272
CA-Dysart | 6130_Dysart - Vermont 66 kV | Power Factor | 0.99959 | 0.99959 | 0.99959 | 0.99959 | 0.99959
CA-Dysart | 6130_Dysart - Vermont 66 kV | Rating (A) | 218 | 218 | 218 | 218 | 218
CA-Dysart | 6130_Dysart - Vermont 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Dysart | 6130_Dysart - Vermont 66 kV | Min Voltage at Constrained Conductor | 68.9911 | 68.9912 | 68.9913 | 68.9913 | 68.9914
CA-Dysart | 6130_Dysart - Vermont 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
6073
CA-Emerald | 6011_Blackwater - Comet 66 kV | % of Rated A | 23.18% | 23.01% | 22.99% | 22.9% | 22.55%
CA-Emerald | 6011_Blackwater - Comet 66 kV | Limiting Line Name | TR_LINE 22148_1 | TR_LINE 22148_1 | TR_LINE 22148_1 | TR_LINE 22148_1 | TR_LINE 22148_1
CA-Emerald | 6011_Blackwater - Comet 66 kV | Loading (A) | 64.2179 | 63.7417 | 63.6695 | 63.4243 | 62.462
CA-Emerald | 6011_Blackwater - Comet 66 kV | Loading (MVA) | 7.6419 | 7.5853 | 7.5765 | 7.5474 | 7.4327
CA-Emerald | 6011_Blackwater - Comet 66 kV | Loading (MW) | 0.75858 | 0.27731 | 0.34563 | 0.074216 | 0.50349
CA-Emerald | 6011_Blackwater - Comet 66 kV | Power Factor | 0.099236 | 0.036521 | 0.045582 | 0.0097921 | 0.0677
CA-Emerald | 6011_Blackwater - Comet 66 kV | Rating (A) | 277 | 277 | 277 | 277 | 277
CA-Emerald | 6011_Blackwater - Comet 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Emerald | 6011_Blackwater - Comet 66 kV | Min Voltage at Constrained Conductor | 68.7042 | 68.7053 | 68.7032 | 68.704 | 68.7016
CA-Emerald | 6011_Blackwater - Comet 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Emerald | 6012_Blackwater - Bedford Weir 66 kV | % of Rated A | 16.39% | 15.87% | 15.44% | 15.13% | 14.94%
CA-Emerald | 6012_Blackwater - Bedford Weir 66 kV | Limiting Line Name | TR_LINE 22153_1 | TR_LINE 22153_1 | TR_LINE 22153_1 | TR_LINE 22153_1 | TR_LINE 22153_1
CA-Emerald | 6012_Blackwater - Bedford Weir 66 kV | Loading (A) | 45.5535 | 44.1159 | 42.9229 | 42.0533 | 41.5269
CA-Emerald | 6012_Blackwater - Bedford Weir 66 kV | Loading (MVA) | 5.4208 | 5.2498 | 5.1077 | 5.0043 | 4.9415
CA-Emerald | 6012_Blackwater - Bedford Weir 66 kV | Loading (MW) | 5.3344 | 5.1595 | 5.0139 | 4.9079 | 4.8435
CA-Emerald | 6012_Blackwater - Bedford Weir 66 kV | Power Factor | 0.98406 | 0.98279 | 0.98164 | 0.98074 | 0.98016
CA-Emerald | 6012_Blackwater - Bedford Weir 66 kV | Rating (A) | 278 | 278 | 278 | 278 | 278
CA-Emerald | 6012_Blackwater - Bedford Weir 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Emerald | 6012_Blackwater - Bedford Weir 66 kV | Min Voltage at Constrained Conductor | 68.704 | 68.7051 | 68.7029 | 68.7037 | 68.7014
CA-Emerald | 6012_Blackwater - Bedford Weir 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Emerald | 6014_Blackwater - South Blackwater 66 kV | % of Rated A | 11.31% | 11.31% | 11.31% | 11.31% | 11.31%
CA-Emerald | 6014_Blackwater - South Blackwater 66 kV | Limiting Line Name | TR_LINE 22149_1 | TR_LINE 22149_1 | TR_LINE 22149_1 | TR_LINE 22149_1 | TR_LINE 22149_1
CA-Emerald | 6014_Blackwater - South Blackwater 66 kV | Loading (A) | 56.083 | 56.0821 | 56.0839 | 56.0832 | 56.0851
CA-Emerald | 6014_Blackwater - South Blackwater 66 kV | Loading (MVA) | 6.6738 | 6.6738 | 6.6738 | 6.6738 | 6.6738
CA-Emerald | 6014_Blackwater - South Blackwater 66 kV | Loading (MW) | 6.651 | 6.651 | 6.651 | 6.651 | 6.651
CA-Emerald | 6014_Blackwater - South Blackwater 66 kV | Power Factor | 0.99657 | 0.99657 | 0.99657 | 0.99657 | 0.99657
CA-Emerald | 6014_Blackwater - South Blackwater 66 kV | Rating (A) | 496 | 496 | 496 | 496 | 496
CA-Emerald | 6014_Blackwater - South Blackwater 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Emerald | 6014_Blackwater - South Blackwater 66 kV | Min Voltage at Constrained Conductor | 68.7035 | 68.7046 | 68.7025 | 68.7032 | 68.7009
CA-Emerald | 6014_Blackwater - South Blackwater 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Emerald | 6015_Blackwater - Curragh Mine 66 kV | % of Rated A | 66.23% | 66.23% | 66.23% | 66.23% | 66.23%
CA-Emerald | 6015_Blackwater - Curragh Mine 66 kV | Limiting Line Name | TR_LINE 18371_1 | TR_LINE 18371_1 | TR_LINE 18371_1 | TR_LINE 18371_1 | TR_LINE 18371_1
CA-Emerald | 6015_Blackwater - Curragh Mine 66 kV | Loading (A) | 368.2294 | 368.2235 | 368.2353 | 368.2309 | 368.2436
CA-Emerald | 6015_Blackwater - Curragh Mine 66 kV | Loading (MVA) | 43.818 | 43.8179 | 43.818 | 43.818 | 43.818
CA-Emerald | 6015_Blackwater - Curragh Mine 66 kV | Loading (MW) | 43.8079 | 43.8079 | 43.8079 | 43.8079 | 43.8079
CA-Emerald | 6015_Blackwater - Curragh Mine 66 kV | Power Factor | 0.99977 | 0.99977 | 0.99977 | 0.99977 | 0.99977
CA-Emerald | 6015_Blackwater - Curragh Mine 66 kV | Rating (A) | 556 | 556 | 556 | 556 | 556
CA-Emerald | 6015_Blackwater - Curragh Mine 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Emerald | 6015_Blackwater - Curragh Mine 66 kV | Min Voltage at Constrained Conductor | 68.2151 | 68.2162 | 68.214 | 68.2148 | 68.2124
CA-Emerald | 6015_Blackwater - Curragh Mine 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Emerald | 6055 Cook Colliery-Miniere Mining 66 kV | % of Rated A | 35.15% | 35.04% | 34.95% | 34.87% | 34.8%
CA-Emerald | 6055 Cook Colliery-Miniere Mining 66 kV | Limiting Line Name | TR_LINE 22527_1 | TR_LINE 22527_1 | TR_LINE 22527_1 | TR_LINE 22527_1 | TR_LINE 22527_1
CA-Emerald | 6055 Cook Colliery-Miniere Mining 66 kV | Loading (A) | 50.2712 | 50.1121 | 49.9794 | 49.8679 | 49.7684
CA-Emerald | 6055 Cook Colliery-Miniere Mining 66 kV | Loading (MVA) | 5.9011 | 5.8827 | 5.8671 | 5.8543 | 5.8425
CA-Emerald | 6055 Cook Colliery-Miniere Mining 66 kV | Loading (MW) | 5.8969 | 5.8785 | 5.8629 | 5.85 | 5.8383
CA-Emerald | 6055 Cook Colliery-Miniere Mining 66 kV | Power Factor | 0.99929 | 0.99928 | 0.99928 | 0.99927 | 0.99927
CA-Emerald | 6055 Cook Colliery-Miniere Mining 66 kV | Rating (A) | 143 | 143 | 143 | 143 | 143
CA-Emerald | 6055 Cook Colliery-Miniere Mining 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Emerald | 6055 Cook Colliery-Miniere Mining 66 kV | Min Voltage at Constrained Conductor | 67.771 | 67.7746 | 67.7745 | 67.777 | 67.7762
CA-Emerald | 6055 Cook Colliery-Miniere Mining 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Emerald | 6056_Comet - Emerald 66 kV | % of Rated A | 21.79% | 21.66% | 21.64% | 21.54% | 21.14%
CA-Emerald | 6056_Comet - Emerald 66 kV | Limiting Line Name | TR_LINE 22146_1 | TR_LINE 22146_1 | TR_LINE 22146_1 | TR_LINE 22146_1 | TR_LINE 22146_1
CA-Emerald | 6056_Comet - Emerald 66 kV | Loading (A) | 60.3582 | 59.9844 | 59.9339 | 59.6652 | 58.5527
CA-Emerald | 6056_Comet - Emerald 66 kV | Loading (MVA) | 7.3214 | 7.282 | 7.2745 | 7.247 | 7.1146
CA-Emerald | 6056_Comet - Emerald 66 kV | Loading (MW) | 0.42867 | 0.062898 | 0.26508 | 0.017347 | 0.17154
CA-Emerald | 6056_Comet - Emerald 66 kV | Power Factor | 0.058539 | 0.0086237 | 0.036427 | 0.0023796 | 0.024097
CA-Emerald | 6056_Comet - Emerald 66 kV | Rating (A) | 277 | 277 | 277 | 277 | 277
CA-Emerald | 6056_Comet - Emerald 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Emerald | 6056_Comet - Emerald 66 kV | Min Voltage at Constrained Conductor | 70.0317 | 70.0889 | 70.0759 | 70.1256 | 70.1523
CA-Emerald | 6056_Comet - Emerald 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Emerald | 6058_Bedford Weir - Bingegang 66 kV | % of Rated A | 12.88% | 12.78% | 12.71% | 12.65% | 12.61%
CA-Emerald | 6058_Bedford Weir - Bingegang 66 kV | Limiting Line Name | TR_LINE 22154_1 | TR_LINE 22154_1 | TR_LINE 22154_1 | TR_LINE 22154_1 | TR_LINE 22154_1
CA-Emerald | 6058_Bedford Weir - Bingegang 66 kV | Loading (A) | 35.8014 | 35.5366 | 35.3353 | 35.1789 | 35.0479
CA-Emerald | 6058_Bedford Weir - Bingegang 66 kV | Loading (MVA) | 4.2409 | 4.2105 | 4.1872 | 4.1692 | 4.1539
CA-Emerald | 6058_Bedford Weir - Bingegang 66 kV | Loading (MW) | 4.1737 | 4.1424 | 4.1186 | 4.1002 | 4.0844
CA-Emerald | 6058_Bedford Weir - Bingegang 66 kV | Power Factor | 0.98414 | 0.98384 | 0.98361 | 0.98344 | 0.98328
CA-Emerald | 6058_Bedford Weir - Bingegang 66 kV | Rating (A) | 278 | 278 | 278 | 278 | 278
CA-Emerald | 6058_Bedford Weir - Bingegang 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Emerald | 6058_Bedford Weir - Bingegang 66 kV | Min Voltage at Constrained Conductor | 68.3894 | 68.4045 | 68.414 | 68.4233 | 68.4261
CA-Emerald | 6058_Bedford Weir - Bingegang 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Emerald | 6059_Leichardt - Cook Colliery 66 kV | % of Rated A | 35.21% | 35.1% | 35.01% | 34.93% | 34.86%
CA-Emerald | 6059_Leichardt - Cook Colliery 66 kV | Limiting Line Name | TR_LINE 22402_1 | TR_LINE 22402_1 | TR_LINE 22402_1 | TR_LINE 22402_1 | TR_LINE 22402_1
CA-Emerald | 6059_Leichardt - Cook Colliery 66 kV | Loading (A) | 50.3514 | 50.1926 | 50.0602 | 49.949 | 49.8497
CA-Emerald | 6059_Leichardt - Cook Colliery 66 kV | Loading (MVA) | 5.9379 | 5.9194 | 5.9037 | 5.8907 | 5.8789
CA-Emerald | 6059_Leichardt - Cook Colliery 66 kV | Loading (MW) | 5.9265 | 5.9079 | 5.8921 | 5.8791 | 5.8672
CA-Emerald | 6059_Leichardt - Cook Colliery 66 kV | Power Factor | 0.99808 | 0.99806 | 0.99805 | 0.99803 | 0.99802
CA-Emerald | 6059_Leichardt - Cook Colliery 66 kV | Rating (A) | 143 | 143 | 143 | 143 | 143
CA-Emerald | 6059_Leichardt - Cook Colliery 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Emerald | 6059_Leichardt - Cook Colliery 66 kV | Min Voltage at Constrained Conductor | 67.7723 | 67.7759 | 67.7758 | 67.7783 | 67.7775
CA-Emerald | 6059_Leichardt - Cook Colliery 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Emerald | 6062_Thiess 66 kV | % of Rated A | 19.72% | 19.72% | 19.72% | 19.72% | 19.72%
CA-Emerald | 6062_Thiess 66 kV | Limiting Line Name | TR_LINE 22551_1 | TR_LINE 22551_1 | TR_LINE 22551_1 | TR_LINE 22551_1 | TR_LINE 22551_1
CA-Emerald | 6062_Thiess 66 kV | Loading (A) | 28.2011 | 28.1991 | 28.1987 | 28.1973 | 28.1973
CA-Emerald | 6062_Thiess 66 kV | Loading (MVA) | 3.3003 | 3.3003 | 3.3003 | 3.3003 | 3.3003
CA-Emerald | 6062_Thiess 66 kV | Loading (MW) | 3.3003 | 3.3003 | 3.3003 | 3.3003 | 3.3003
CA-Emerald | 6062_Thiess 66 kV | Power Factor | 1 | 1 | 1 | 1 | 1
CA-Emerald | 6062_Thiess 66 kV | Rating (A) | 143 | 143 | 143 | 143 | 143
CA-Emerald | 6062_Thiess 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Emerald | 6062_Thiess 66 kV | Min Voltage at Constrained Conductor | 67.5607 | 67.5655 | 67.5665 | 67.5699 | 67.5698
CA-Emerald | 6062_Thiess 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Emerald | 6065_Lilyvale - Tieri Tee 66 kV | % of Rated A | 29.71% | 29.6% | 29.52% | 29.46% | 29.45%
CA-Emerald | 6065_Lilyvale - Tieri Tee 66 kV | Limiting Line Name | TR_LINE 22248_1 | TR_LINE 22248_1 | TR_LINE 22248_1 | TR_LINE 22248_1 | TR_LINE 22248_1
CA-Emerald | 6065_Lilyvale - Tieri Tee 66 kV | Loading (A) | 72.1851 | 71.9174 | 71.7271 | 71.5875 | 71.5544
CA-Emerald | 6065_Lilyvale - Tieri Tee 66 kV | Loading (MVA) | 8.5913 | 8.5611 | 8.5383 | 8.5229 | 8.5193
CA-Emerald | 6065_Lilyvale - Tieri Tee 66 kV | Loading (MW) | 8.5674 | 8.537 | 8.5139 | 8.4984 | 8.4946
CA-Emerald | 6065_Lilyvale - Tieri Tee 66 kV | Power Factor | 0.99723 | 0.99718 | 0.99715 | 0.99712 | 0.99711
CA-Emerald | 6065_Lilyvale - Tieri Tee 66 kV | Rating (A) | 243 | 243 | 243 | 243 | 243
CA-Emerald | 6065_Lilyvale - Tieri Tee 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Emerald | 6065_Lilyvale - Tieri Tee 66 kV | Min Voltage at Constrained Conductor | 68.7119 | 68.7258 | 68.7245 | 68.7346 | 68.7366
CA-Emerald | 6065_Lilyvale - Tieri Tee 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Emerald | 6067 Lilyvale - Emerald 66 kV | % of Rated A | 22.55% | 22.56% | 22.64% | 22.66% | 22.4%
CA-Emerald | 6067 Lilyvale - Emerald 66 kV | Limiting Line Name | TR_LINE 17480_1 | TR_LINE 17480_1 | TR_LINE 17480_1 | TR_LINE 17480_1 | TR_LINE 17480_1
CA-Emerald | 6067 Lilyvale - Emerald 66 kV | Loading (A) | 76.8956 | 76.9274 | 77.1912 | 77.2786 | 76.3926
CA-Emerald | 6067 Lilyvale - Emerald 66 kV | Loading (MVA) | 9.1519 | 9.1575 | 9.1888 | 9.2005 | 9.0953
CA-Emerald | 6067 Lilyvale - Emerald 66 kV | Loading (MW) | 1.494 | 0.88912 | 1.2907 | 0.82936 | 0.36698
CA-Emerald | 6067 Lilyvale - Emerald 66 kV | Power Factor | 0.16137 | 0.090622 | 0.13688 | 0.083069 | 0.030084
CA-Emerald | 6067 Lilyvale - Emerald 66 kV | Rating (A) | 341 | 341 | 341 | 341 | 341
CA-Emerald | 6067 Lilyvale - Emerald 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Emerald | 6067 Lilyvale - Emerald 66 kV | Min Voltage at Constrained Conductor | 68.7145 | 68.7283 | 68.7271 | 68.7372 | 68.7392
CA-Emerald | 6067 Lilyvale - Emerald 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Emerald | 6078_SOBL - Dragline South 66 kV | % of Rated A | 0.5581% | 0.5581% | 0.5581% | 0.5581% | 0.5582%
CA-Emerald | 6078_SOBL - Dragline South 66 kV | Limiting Line Name | TR_LINE SOBL - SOBL Dragline South | TR_LINE SOBL - SOBL Dragline South | TR_LINE SOBL - SOBL Dragline South | TR_LINE SOBL - SOBL Dragline South | TR_LINE SOBL - SOBL Dragline South
CA-Emerald | 6078_SOBL - Dragline South 66 kV | Loading (A) | 27.9066 | 27.9062 | 27.9071 | 27.9067 | 27.9077
CA-Emerald | 6078_SOBL - Dragline South 66 kV | Loading (MVA) | 3.3 | 3.3 | 3.3 | 3.3 | 3.3
CA-Emerald | 6078_SOBL - Dragline South 66 kV | Loading (MW) | 3.3 | 3.3 | 3.3 | 3.3 | 3.3
CA-Emerald | 6078_SOBL - Dragline South 66 kV | Power Factor | 1 | 1 | 1 | 1 | 1
CA-Emerald | 6078_SOBL - Dragline South 66 kV | Rating (A) | 5000 | 5000 | 5000 | 5000 | 5000
CA-Emerald | 6078_SOBL - Dragline South 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Emerald | 6078_SOBL - Dragline South 66 kV | Min Voltage at Constrained Conductor | 68.2725 | 68.2736 | 68.2714 | 68.2722 | 68.2699
CA-Emerald | 6078_SOBL - Dragline South 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Emerald | 6079_Barcaldine - Longreach 66 kV | % of Rated A | 17.93% | 17.29% | 16.85% | 16.54% | 16.33%
CA-Emerald | 6079_Barcaldine - Longreach 66 kV | Limiting Line Name | TR_CABLE 562_1 | TR_CABLE 562_1 | TR_CABLE 562_1 | TR_CABLE 562_1 | TR_CABLE 562_1
CA-Emerald | 6079_Barcaldine - Longreach 66 kV | Loading (A) | 17.9252 | 17.2865 | 16.8488 | 16.5393 | 16.3265
CA-Emerald | 6079_Barcaldine - Longreach 66 kV | Loading (MVA) | 2.2261 | 2.15 | 2.0979 | 2.0613 | 2.0362
CA-Emerald | 6079_Barcaldine - Longreach 66 kV | Loading (MW) | 1.1134 | 0.92674 | 0.77651 | 0.65048 | 0.54745
CA-Emerald | 6079_Barcaldine - Longreach 66 kV | Power Factor | 0.50015 | 0.43104 | 0.37014 | 0.31557 | 0.26885
CA-Emerald | 6079_Barcaldine - Longreach 66 kV | Rating (A) | 100 | 100 | 100 | 100 | 100
CA-Emerald | 6079_Barcaldine - Longreach 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Emerald | 6079_Barcaldine - Longreach 66 kV | Min Voltage at Constrained Conductor | 71.7015 | 71.8088 | 71.8871 | 71.955 | 72.0073
CA-Emerald | 6079_Barcaldine - Longreach 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Emerald | 6080_Barcaldine - Blackall 66 kV | % of Rated A | 3.602% | 3.593% | 3.588% | 3.584% | 3.583%
CA-Emerald | 6080_Barcaldine - Blackall 66 kV | Limiting Line Name | TR_LINE 22558_1 | TR_LINE 22558_1 | TR_LINE 22558_1 | TR_LINE 22558_1 | TR_LINE 22558_1
CA-Emerald | 6080_Barcaldine - Blackall 66 kV | Loading (A) | 13.9056 | 13.8705 | 13.8486 | 13.8357 | 13.8286
CA-Emerald | 6080_Barcaldine - Blackall 66 kV | Loading (MVA) | 1.7233 | 1.7214 | 1.7205 | 1.7205 | 1.7208
CA-Emerald | 6080_Barcaldine - Blackall 66 kV | Loading (MW) | 0.32041 | 0.27776 | 0.24506 | 0.2191 | 0.20001
CA-Emerald | 6080_Barcaldine - Blackall 66 kV | Power Factor | 0.18592 | 0.16135 | 0.14243 | 0.12735 | 0.11623
CA-Emerald | 6080_Barcaldine - Blackall 66 kV | Rating (A) | 386 | 386 | 386 | 386 | 386
CA-Emerald | 6080_Barcaldine - Blackall 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Emerald | 6080_Barcaldine - Blackall 66 kV | Min Voltage at Constrained Conductor | 71.552 | 71.6542 | 71.7286 | 71.7934 | 71.8432
CA-Emerald | 6080_Barcaldine - Blackall 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Emerald | 6085_Tieri Tee - Tieri 66 kV | % of Rated A | 2.696% | 2.69% | 2.688% | 2.693% | 2.708%
CA-Emerald | 6085_Tieri Tee - Tieri 66 kV | Limiting Line Name | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1 | TR_LINE 16931_1
CA-Emerald | 6085_Tieri Tee - Tieri 66 kV | Loading (A) | 6.5512 | 6.5358 | 6.5313 | 6.5443 | 6.5809
CA-Emerald | 6085_Tieri Tee - Tieri 66 kV | Loading (MVA) | 0.77697 | 0.77531 | 0.77477 | 0.77644 | 0.7808
CA-Emerald | 6085_Tieri Tee - Tieri 66 kV | Loading (MW) | 0.76863 | 0.76695 | 0.7664 | 0.76808 | 0.7725
CA-Emerald | 6085_Tieri Tee - Tieri 66 kV | Power Factor | 0.98927 | 0.98921 | 0.98919 | 0.98924 | 0.98936
CA-Emerald | 6085_Tieri Tee - Tieri 66 kV | Rating (A) | 243 | 243 | 243 | 243 | 243
CA-Emerald | 6085_Tieri Tee - Tieri 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Emerald | 6085_Tieri Tee - Tieri 66 kV | Min Voltage at Constrained Conductor | 68.4504 | 68.4654 | 68.4649 | 68.4756 | 68.4776
CA-Emerald | 6085_Tieri Tee - Tieri 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Emerald | 6086_Tieri Tee - Middlemount 66 kV | % of Rated A | 26.99% | 26.89% | 26.81% | 26.75% | 26.72%
CA-Emerald | 6086_Tieri Tee - Middlemount 66 kV | Limiting Line Name | TR_LINE 16972_1 | TR_LINE 16972_1 | TR_LINE 16972_1 | TR_LINE 16972_1 | TR_LINE 16972_1
CA-Emerald | 6086_Tieri Tee - Middlemount 66 kV | Loading (A) | 65.5862 | 65.3331 | 65.1468 | 64.9935 | 64.9234
CA-Emerald | 6086_Tieri Tee - Middlemount 66 kV | Loading (MVA) | 7.7773 | 7.749 | 7.7269 | 7.7099 | 7.7018
CA-Emerald | 6086_Tieri Tee - Middlemount 66 kV | Loading (MW) | 7.7637 | 7.7352 | 7.7129 | 7.6958 | 7.6877
CA-Emerald | 6086_Tieri Tee - Middlemount 66 kV | Power Factor | 0.99825 | 0.99822 | 0.99819 | 0.99817 | 0.99816
CA-Emerald | 6086_Tieri Tee - Middlemount 66 kV | Rating (A) | 243 | 243 | 243 | 243 | 243
CA-Emerald | 6086_Tieri Tee - Middlemount 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Emerald | 6086_Tieri Tee - Middlemount 66 kV | Min Voltage at Constrained Conductor | 67.7564 | 67.7746 | 67.7766 | 67.7893 | 67.7923
CA-Emerald | 6086_Tieri Tee - Middlemount 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Emerald | 7153_Lilyvale - Clermont 132 kV | % of Rated A | 17.72% | 17.61% | 17.52% | 17.45% | 17.4%
CA-Emerald | 7153_Lilyvale - Clermont 132 kV | Limiting Line Name | TR_LINE 52800_1 | TR_LINE 52800_1 | TR_LINE 52800_1 | TR_LINE 52800_1 | TR_LINE 52800_1
CA-Emerald | 7153_Lilyvale - Clermont 132 kV | Loading (A) | 125.466 | 124.6664 | 124.0513 | 123.5668 | 123.1829
CA-Emerald | 7153_Lilyvale - Clermont 132 kV | Loading (MVA) | 30.7312 | 30.5386 | 30.3883 | 30.2719 | 30.1791
CA-Emerald | 7153_Lilyvale - Clermont 132 kV | Loading (MW) | 15.7055 | 15.167 | 14.7458 | 14.4042 | 14.1306
CA-Emerald | 7153_Lilyvale - Clermont 132 kV | Power Factor | 0.51106 | 0.49665 | 0.48525 | 0.47583 | 0.46823
CA-Emerald | 7153_Lilyvale - Clermont 132 kV | Rating (A) | 708 | 708 | 708 | 708 | 708
CA-Emerald | 7153_Lilyvale - Clermont 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Emerald | 7153_Lilyvale - Clermont 132 kV | Min Voltage at Constrained Conductor | 141.414 | 141.429 | 141.431 | 141.4417 | 141.4473
CA-Emerald | 7153_Lilyvale - Clermont 132 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Emerald | 7154_Clermont - Barcaldine 132 kV | % of Rated A | 22.41% | 22.43% | 22.44% | 22.45% | 22.46%
CA-Emerald | 7154_Clermont - Barcaldine 132 kV | Limiting Line Name | TR_LINE 52329_1 | TR_LINE 52329_1 | TR_LINE 52329_1 | TR_LINE 52329_1 | TR_LINE 52329_1
CA-Emerald | 7154_Clermont - Barcaldine 132 kV | Loading (A) | 80.6924 | 80.7316 | 80.767 | 80.8071 | 80.8412
CA-Emerald | 7154_Clermont - Barcaldine 132 kV | Loading (MVA) | 20.5105 | 20.5303 | 20.5455 | 20.5619 | 20.5752
CA-Emerald | 7154_Clermont - Barcaldine 132 kV | Loading (MW) | 2.2988 | 1.9469 | 1.6696 | 1.4432 | 1.2625
CA-Emerald | 7154_Clermont - Barcaldine 132 kV | Power Factor | 0.11208 | 0.094828 | 0.081264 | 0.070159 | 0.061161
CA-Emerald | 7154_Clermont - Barcaldine 132 kV | Rating (A) | 360 | 360 | 360 | 360 | 360
CA-Emerald | 7154_Clermont - Barcaldine 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Emerald | 7154_Clermont - Barcaldine 132 kV | Min Voltage at Constrained Conductor | 146.7518 | 146.822 | 146.866 | 146.9108 | 146.9433
CA-Emerald | 7154_Clermont - Barcaldine 132 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Emerald | 7450_Memooloo - Rolleston 132 kV | % of Rated A | 10.12% | 10.08% | 10.88% | 10.85% | 10.83%
CA-Emerald | 7450_Memooloo - Rolleston 132 kV | Limiting Line Name | TR_LINE 200880_1 | TR_LINE 200880_1 | TR_LINE 200880_1 | TR_LINE 200880_1 | TR_LINE 200880_1
CA-Emerald | 7450_Memooloo - Rolleston 132 kV | Loading (A) | 71.3657 | 71.0885 | 76.6886 | 76.4964 | 76.3329
CA-Emerald | 7450_Memooloo - Rolleston 132 kV | Loading (MVA) | 17.3329 | 17.2662 | 18.6127 | 18.5665 | 18.5273
CA-Emerald | 7450_Memooloo - Rolleston 132 kV | Loading (MW) | 17.2245 | 17.1568 | 18.5216 | 18.4748 | 18.4351
CA-Emerald | 7450_Memooloo - Rolleston 132 kV | Power Factor | 0.99375 | 0.99367 | 0.99511 | 0.99506 | 0.99502
CA-Emerald | 7450_Memooloo - Rolleston 132 kV | Rating (A) | 705 | 705 | 705 | 705 | 705
CA-Emerald | 7450_Memooloo - Rolleston 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Emerald | 7450_Memooloo - Rolleston 132 kV | Min Voltage at Constrained Conductor | 139.8667 | 139.8739 | 139.7256 | 139.7308 | 139.7352
CA-Emerald | 7450_Memooloo - Rolleston 132 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Gladstone Rockhampton | 6001_Glenmore - Parkhurst 66 kV | % of Rated A | 6.545% | 5.356% | 1.778% | 0.8098% | 0.6075%
CA-Gladstone Rockhampton | 6001_Glenmore - Parkhurst 66 kV | Limiting Line Name | TR_LINE 22133_1 | TR_LINE 22133_1 | TR_LINE 22133_1 | TR_LINE 22133_1 | TR_LINE 22133_1
CA-Gladstone Rockhampton | 6001_Glenmore - Parkhurst 66 kV | Loading (A) | 26.2438 | 21.4783 | 7.1289 | 3.2474 | 2.4359
CA-Gladstone Rockhampton | 6001_Glenmore - Parkhurst 66 kV | Loading (MVA) | 3.1558 | 2.5858 | 0.85917 | 0.39159 | 0.29371
CA-Gladstone Rockhampton | 6001_Glenmore - Parkhurst 66 kV | Loading (MW) | 2.0914 | 1.2599 | 0.78649 | 0.29036 | 0.24429
CA-Gladstone Rockhampton | 6001_Glenmore - Parkhurst 66 kV | Power Factor | 0.66272 | 0.48723 | 0.91541 | 0.7415 | 0.83176
CA-Gladstone Rockhampton | 6001_Glenmore - Parkhurst 66 kV | Rating (A) | 401 | 401 | 401 | 401 | 401
CA-Gladstone Rockhampton | 6001_Glenmore - Parkhurst 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6001_Glenmore - Parkhurst 66 kV | Min Voltage at Constrained Conductor | 69.4257 | 69.5069 | 69.5817 | 69.6194 | 69.613
CA-Gladstone Rockhampton | 6001_Glenmore - Parkhurst 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Gladstone Rockhampton | 6003_Glenmore - Berserker 66 kV | % of Rated A | 18.85% | 18.71% | 21.56% | 23.07% | 25.64%
CA-Gladstone Rockhampton | 6003_Glenmore - Berserker 66 kV | Limiting Line Name | TR_LINE 22137_1 | TR_LINE 22137_1 | TR_LINE 22137_1 | TR_LINE 22137_1 | TR_LINE 22137_1
CA-Gladstone Rockhampton | 6003_Glenmore - Berserker 66 kV | Loading (A) | 75.5705 | 75.0301 | 86.4386 | 92.5126 | 102.8293
CA-Gladstone Rockhampton | 6003_Glenmore - Berserker 66 kV | Loading (MVA) | 9.0873 | 9.0328 | 10.4175 | 11.1556 | 12.3988
CA-Gladstone Rockhampton | 6003_Glenmore - Berserker 66 kV | Loading (MW) | 1.2249 | 0.56065 | 2.3879 | 4.697 | 7.2795
CA-Gladstone Rockhampton | 6003_Glenmore - Berserker 66 kV | Power Factor | 0.13477 | 0.062027 | 0.22918 | 0.42099 | 0.58708
CA-Gladstone Rockhampton | 6003_Glenmore - Berserker 66 kV | Rating (A) | 401 | 401 | 401 | 401 | 401
CA-Gladstone Rockhampton | 6003_Glenmore - Berserker 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6003_Glenmore - Berserker 66 kV | Min Voltage at Constrained Conductor | 69.4257 | 69.5069 | 69.5817 | 69.6194 | 69.613
CA-Gladstone Rockhampton | 6003_Glenmore - Berserker 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Gladstone Rockhampton | 6004_Glenmore - Rockhampton South 66 kV | % of Rated A | 4.333% | 2.494% | 5.097% | 6.77% | 6.625%
CA-Gladstone Rockhampton | 6004_Glenmore - Rockhampton South 66 kV | Limiting Line Name | TR_LINE 139201_1 | TR_LINE 139201_1 | TR_CABLE 301_1 | TR_CABLE 301_1 | TR_CABLE 301_1
CA-Gladstone Rockhampton | 6004_Glenmore - Rockhampton South 66 kV | Loading (A) | 15.9018 | 9.1529 | 18.9595 | 25.1859 | 24.6458
CA-Gladstone Rockhampton | 6004_Glenmore - Rockhampton South 66 kV | Loading (MVA) | 1.9121 | 1.1017 | 2.2851 | 3.0371 | 2.9717
CA-Gladstone Rockhampton | 6004_Glenmore - Rockhampton South 66 kV | Loading (MW) | 1.4233 | 0.025058 | 0.79727 | 2.1525 | 2.0335
CA-Gladstone Rockhampton | 6004_Glenmore - Rockhampton South 66 kV | Power Factor | 0.74438 | 0.022745 | 0.34889 | 0.70872 | 0.68429
CA-Gladstone Rockhampton | 6004_Glenmore - Rockhampton South 66 kV | Rating (A) | 367 | 367 | 372 | 372 | 372
CA-Gladstone Rockhampton | 6004_Glenmore - Rockhampton South 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6004_Glenmore - Rockhampton South 66 kV | Min Voltage at Constrained Conductor | 69.4214 | 69.4927 | 69.5863 | 69.6215 | 69.6154
CA-Gladstone Rockhampton | 6004_Glenmore - Rockhampton South 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Gladstone Rockhampton | 6005_Rockhampton Glenmore-Canning 66 kV | % of Rated A | 5.043% | 5.326% | 10.88% | 10.87% | 10.87%
CA-Gladstone Rockhampton | 6005_Rockhampton Glenmore-Canning 66 kV | Limiting Line Name | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1 | TR_LINE 22139_1
CA-Gladstone Rockhampton | 6005_Rockhampton Glenmore-Canning 66 kV | Loading (A) | 20.1223 | 21.2512 | 43.4115 | 43.3773 | 43.3873
CA-Gladstone Rockhampton | 6005_Rockhampton Glenmore-Canning 66 kV | Loading (MVA) | 2.4197 | 2.5584 | 5.2319 | 5.2306 | 5.2313
CA-Gladstone Rockhampton | 6005_Rockhampton Glenmore-Canning 66 kV | Loading (MW) | 0.3487 | 0.53743 | 0.94858 | 0.56543 | 0.021464
CA-Gladstone Rockhampton | 6005_Rockhampton Glenmore-Canning 66 kV | Power Factor | 0.14405 | 0.21006 | 0.18131 | 0.1081 | 0.0039746
CA-Gladstone Rockhampton | 6005_Rockhampton Glenmore-Canning 66 kV | Rating (A) | 399 | 399 | 399 | 399 | 399
CA-Gladstone Rockhampton | 6005_Rockhampton Glenmore-Canning 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6005_Rockhampton Glenmore-Canning 66 kV | Min Voltage at Constrained Conductor | 69.4257 | 69.5069 | 69.5817 | 69.6194 | 69.613
CA-Gladstone Rockhampton | 6005_Rockhampton Glenmore-Canning 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Gladstone Rockhampton | 6006_Glenmore - Frenchville 66 kV | % of Rated A | 4.097% | 5.689% | 7.335% | 10.46% | 13.86%
CA-Gladstone Rockhampton | 6006_Glenmore - Frenchville 66 kV | Limiting Line Name | TR_LINE 22134_1 | TR_LINE 22134_1 | TR_LINE 22134_1 | TR_LINE 22134_1 | TR_LINE 22209_1
CA-Gladstone Rockhampton | 6006_Glenmore - Frenchville 66 kV | Loading (A) | 16.4279 | 22.8144 | 29.4147 | 41.9293 | 55.5778
CA-Gladstone Rockhampton | 6006_Glenmore - Frenchville 66 kV | Loading (MVA) | 1.9754 | 2.7466 | 3.545 | 5.0562 | 6.7135
CA-Gladstone Rockhampton | 6006_Glenmore - Frenchville 66 kV | Loading (MW) | 0.19375 | 2.0373 | 3.5393 | 5.0558 | 6.7114
CA-Gladstone Rockhampton | 6006_Glenmore - Frenchville 66 kV | Power Factor | 0.098068 | 0.74173 | 0.99837 | 0.99992 | 0.99968
CA-Gladstone Rockhampton | 6006_Glenmore - Frenchville 66 kV | Rating (A) | 401 | 401 | 401 | 401 | 401
CA-Gladstone Rockhampton | 6006_Glenmore - Frenchville 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6006_Glenmore - Frenchville 66 kV | Min Voltage at Constrained Conductor | 69.4257 | 69.5069 | 69.5817 | 69.6194 | 69.7399
CA-Gladstone Rockhampton | 6006_Glenmore - Frenchville 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Gladstone Rockhampton | 6007_Biloela - Coominglah Tee 66 kV | % of Rated A | 14.55% | 14.46% | 14.41% | 14.37% | 14.36%
CA-Gladstone Rockhampton | 6007_Biloela - Coominglah Tee 66 kV | Limiting Line Name | TR_LINE 18121_1 | TR_LINE 18121_1 | TR_LINE 18121_1 | TR_LINE 18121_1 | TR_LINE 18121_1
CA-Gladstone Rockhampton | 6007_Biloela - Coominglah Tee 66 kV | Loading (A) | 19.2075 | 19.0877 | 19.0158 | 18.9728 | 18.9503
CA-Gladstone Rockhampton | 6007_Biloela - Coominglah Tee 66 kV | Loading (MVA) | 2.314 | 2.3008 | 2.2921 | 2.2863 | 2.2827
CA-Gladstone Rockhampton | 6007_Biloela - Coominglah Tee 66 kV | Loading (MW) | 0.45619 | 0.34047 | 0.24672 | 0.16747 | 0.10069
CA-Gladstone Rockhampton | 6007_Biloela - Coominglah Tee 66 kV | Power Factor | 0.19714 | 0.14798 | 0.10764 | 0.073248 | 0.044112
CA-Gladstone Rockhampton | 6007_Biloela - Coominglah Tee 66 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
CA-Gladstone Rockhampton | 6007_Biloela - Coominglah Tee 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6007_Biloela - Coominglah Tee 66 kV | Min Voltage at Constrained Conductor | 69.5562 | 69.5928 | 69.5922 | 69.5721 | 69.5455
CA-Gladstone Rockhampton | 6007_Biloela - Coominglah Tee 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Gladstone Rockhampton | 6008_Biloela - Wowan 66 kV | % of Rated A | 6.956% | 6.695% | 6.533% | 6.434% | 6.376%
CA-Gladstone Rockhampton | 6008_Biloela - Wowan 66 kV | Limiting Line Name | TR_LINE 21790_1 | TR_LINE 21790_1 | TR_LINE 21790_1 | TR_LINE 21790_1 | TR_LINE 21790_1
CA-Gladstone Rockhampton | 6008_Biloela - Wowan 66 kV | Loading (A) | 9.1825 | 8.8375 | 8.6242 | 8.4927 | 8.4158
CA-Gladstone Rockhampton | 6008_Biloela - Wowan 66 kV | Loading (MVA) | 1.1063 | 1.0653 | 1.0395 | 1.0234 | 1.0137
CA-Gladstone Rockhampton | 6008_Biloela - Wowan 66 kV | Loading (MW) | 0.47052 | 0.3554 | 0.26369 | 0.1884 | 0.12665
CA-Gladstone Rockhampton | 6008_Biloela - Wowan 66 kV | Power Factor | 0.42532 | 0.33363 | 0.25366 | 0.18409 | 0.12494
CA-Gladstone Rockhampton | 6008_Biloela - Wowan 66 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
CA-Gladstone Rockhampton | 6008_Biloela - Wowan 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6008_Biloela - Wowan 66 kV | Min Voltage at Constrained Conductor | 69.5565 | 69.5931 | 69.5926 | 69.5725 | 69.546
CA-Gladstone Rockhampton | 6008_Biloela - Wowan 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Gladstone Rockhampton | 6019_Gladstone South - Friend St 66 kV | % of Rated A | 29.2% | 28.54% | 28.66% | 28.7% | 44.52%
CA-Gladstone Rockhampton | 6019_Gladstone South - Friend St 66 kV | Limiting Line Name | TR_LINE 22252_1 | TR_LINE 22252_1 | TR_LINE 22252_1 | TR_LINE 22252_1 | TR_LINE 22252_1
CA-Gladstone Rockhampton | 6019_Gladstone South - Friend St 66 kV | Loading (A) | 71.5519 | 69.9297 | 70.2212 | 70.3077 | 109.0782
CA-Gladstone Rockhampton | 6019_Gladstone South - Friend St 66 kV | Loading (MVA) | 8.4598 | 8.2812 | 8.316 | 8.3015 | 12.9107
CA-Gladstone Rockhampton | 6019_Gladstone South - Friend St 66 kV | Loading (MW) | 4.2228 | 3.8025 | 3.7271 | 3.6006 | 2.1686
CA-Gladstone Rockhampton | 6019_Gladstone South - Friend St 66 kV | Power Factor | 0.49917 | 0.45917 | 0.44819 | 0.43372 | 0.16788
CA-Gladstone Rockhampton | 6019_Gladstone South - Friend St 66 kV | Rating (A) | 245 | 245 | 245 | 245 | 245
CA-Gladstone Rockhampton | 6019_Gladstone South - Friend St 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6019_Gladstone South - Friend St 66 kV | Min Voltage at Constrained Conductor | 68.2616 | 68.3707 | 68.3729 | 68.1703 | 68.3362
CA-Gladstone Rockhampton | 6019_Gladstone South - Friend St 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Gladstone Rockhampton | 6020_Gladstone South - BORE 66 kV | % of Rated A | 7.565% | 6.29% | 7.121% | 7.905% | 8.647%
CA-Gladstone Rockhampton | 6020_Gladstone South - BORE 66 kV | Limiting Line Name | TR_LINE 215689_1 | TR_LINE 215689_1 | TR_LINE 215689_1 | TR_LINE 215689_1 | TR_LINE 215689_1
CA-Gladstone Rockhampton | 6020_Gladstone South - BORE 66 kV | Loading (A) | 15.9628 | 13.271 | 15.0257 | 16.6793 | 18.2453
CA-Gladstone Rockhampton | 6020_Gladstone South - BORE 66 kV | Loading (MVA) | 1.889 | 1.5728 | 1.7809 | 1.9712 | 2.1616
CA-Gladstone Rockhampton | 6020_Gladstone South - BORE 66 kV | Loading (MW) | 1.5855 | 1.178 | 1.4668 | 1.7131 | 1.9396
CA-Gladstone Rockhampton | 6020_Gladstone South - BORE 66 kV | Power Factor | 0.83929 | 0.74894 | 0.82358 | 0.86904 | 0.89724
CA-Gladstone Rockhampton | 6020_Gladstone South - BORE 66 kV | Rating (A) | 211 | 211 | 211 | 211 | 211
CA-Gladstone Rockhampton | 6020_Gladstone South - BORE 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6020_Gladstone South - BORE 66 kV | Min Voltage at Constrained Conductor | 68.3227 | 68.4244 | 68.4312 | 68.2325 | 68.402
CA-Gladstone Rockhampton | 6020_Gladstone South - BORE 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Gladstone Rockhampton | 6022_Gladstone South - Calliope 66 kV | % of Rated A | 3.027% | 2.984% | 3.066% | 3.182% | 3.343%
CA-Gladstone Rockhampton | 6022_Gladstone South - Calliope 66 kV | Limiting Line Name | TR_LINE 72653_1 | TR_LINE 72653_1 | TR_LINE 72653_1 | TR_LINE 72653_1 | TR_LINE 72653_1
CA-Gladstone Rockhampton | 6022_Gladstone South - Calliope 66 kV | Loading (A) | 18.858 | 18.5893 | 19.1008 | 19.8263 | 20.8243
CA-Gladstone Rockhampton | 6022_Gladstone South - Calliope 66 kV | Loading (MVA) | 2.2335 | 2.2051 | 2.266 | 2.3453 | 2.4696
CA-Gladstone Rockhampton | 6022_Gladstone South - Calliope 66 kV | Loading (MW) | 0.25624 | 0.039654 | 0.38583 | 0.68525 | 0.96055
CA-Gladstone Rockhampton | 6022_Gladstone South - Calliope 66 kV | Power Factor | 0.11457 | 0.01783 | 0.17011 | 0.29201 | 0.38878
CA-Gladstone Rockhampton | 6022_Gladstone South - Calliope 66 kV | Rating (A) | 623 | 623 | 623 | 623 | 623
CA-Gladstone Rockhampton | 6022_Gladstone South - Calliope 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6022_Gladstone South - Calliope 66 kV | Min Voltage at Constrained Conductor | 68.3803 | 68.4852 | 68.4941 | 68.2969 | 68.4684
CA-Gladstone Rockhampton | 6022_Gladstone South - Calliope 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Gladstone Rockhampton | 6023_Friend St-Clinton Industrial 66 kV | % of Rated A | 3.401% | 3.528% | 4.155% | 4.706% | 12.71%
CA-Gladstone Rockhampton | 6023_Friend St-Clinton Industrial 66 kV | Limiting Line Name | TR_LINE 22275_1 | TR_LINE 22275_1 | TR_LINE 22275_1 | TR_LINE 22275_1 | TR_LINE 22275_1
CA-Gladstone Rockhampton | 6023_Friend St-Clinton Industrial 66 kV | Loading (A) | 14.9326 | 15.4891 | 18.2405 | 20.6586 | 55.7831
CA-Gladstone Rockhampton | 6023_Friend St-Clinton Industrial 66 kV | Loading (MVA) | 1.7688 | 1.8379 | 2.1645 | 2.4443 | 6.6316
CA-Gladstone Rockhampton | 6023_Friend St-Clinton Industrial 66 kV | Loading (MW) | 1.139 | 1.2476 | 1.6334 | 1.9323 | 0.88014
CA-Gladstone Rockhampton | 6023_Friend St-Clinton Industrial 66 kV | Power Factor | 0.64394 | 0.67883 | 0.75462 | 0.79051 | 0.13271
CA-Gladstone Rockhampton | 6023_Friend St-Clinton Industrial 66 kV | Rating (A) | 439 | 439 | 439 | 439 | 439
CA-Gladstone Rockhampton | 6023_Friend St-Clinton Industrial 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6023_Friend St-Clinton Industrial 66 kV | Min Voltage at Constrained Conductor | 68.3896 | 68.5056 | 68.5109 | 68.3118 | 68.6367
CA-Gladstone Rockhampton | 6023_Friend St-Clinton Industrial 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Gladstone Rockhampton | 6024_Awoonga - Calliope 66kV | % of Rated A | 4.418% | 4.154% | 4.089% | 4.034% | 4.015%
CA-Gladstone Rockhampton | 6024_Awoonga - Calliope 66kV | Limiting Line Name | TR_LINE 181307_1 | TR_LINE 181307_1 | TR_LINE 181307_1 | TR_LINE 181307_1 | TR_LINE 181307_1
CA-Gladstone Rockhampton | 6024_Awoonga - Calliope 66kV | Loading (A) | 7.4671 | 7.0202 | 6.9097 | 6.8168 | 6.7848
CA-Gladstone Rockhampton | 6024_Awoonga - Calliope 66kV | Loading (MVA) | 0.88538 | 0.83314 | 0.82021 | 0.80692 | 0.80521
CA-Gladstone Rockhampton | 6024_Awoonga - Calliope 66kV | Loading (MW) | 0.43444 | 0.24689 | 0.28629 | 0.32027 | 0.35603
CA-Gladstone Rockhampton | 6024_Awoonga - Calliope 66kV | Power Factor | 0.49068 | 0.2958 | 0.34853 | 0.39639 | 0.44164
CA-Gladstone Rockhampton | 6024_Awoonga - Calliope 66kV | Rating (A) | 169 | 169 | 169 | 169 | 169
CA-Gladstone Rockhampton | 6024_Awoonga - Calliope 66kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6024_Awoonga - Calliope 66kV | Min Voltage at Constrained Conductor | 68.4567 | 68.5186 | 68.534 | 68.3422 | 68.5187
CA-Gladstone Rockhampton | 6024_Awoonga - Calliope 66kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Gladstone Rockhampton | 6029_Littlemore - Miriam Vale 66 kV | % of Rated A | 3.317% | 3.577% | 3.793% | 3.986% | 4.144%
CA-Gladstone Rockhampton | 6029_Littlemore - Miriam Vale 66 kV | Limiting Line Name | TR_LINE 16162_1 | TR_LINE 16162_1 | TR_LINE 16162_1 | TR_LINE 16162_1 | TR_LINE 16162_1
CA-Gladstone Rockhampton | 6029_Littlemore - Miriam Vale 66 kV | Loading (A) | 4.378 | 4.7217 | 5.0067 | 5.261 | 5.4697
CA-Gladstone Rockhampton | 6029_Littlemore - Miriam Vale 66 kV | Loading (MVA) | 0.52569 | 0.56798 | 0.60256 | 0.63155 | 0.6584
CA-Gladstone Rockhampton | 6029_Littlemore - Miriam Vale 66 kV | Loading (MW) | 0.43394 | 0.48399 | 0.52427 | 0.55842 | 0.58795
CA-Gladstone Rockhampton | 6029_Littlemore - Miriam Vale 66 kV | Power Factor | 0.82547 | 0.85213 | 0.87007 | 0.88421 | 0.89299
CA-Gladstone Rockhampton | 6029_Littlemore - Miriam Vale 66 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
CA-Gladstone Rockhampton | 6029_Littlemore - Miriam Vale 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6029_Littlemore - Miriam Vale 66 kV | Min Voltage at Constrained Conductor | 69.3253 | 69.4505 | 69.4846 | 69.3067 | 69.4978
CA-Gladstone Rockhampton | 6029_Littlemore - Miriam Vale 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Gladstone Rockhampton | 6030_Littlemore - Monto 66 kV | % of Rated A | 5.321% | 5.331% | 5.334% | 5.32% | 5.335%
CA-Gladstone Rockhampton | 6030_Littlemore - Monto 66 kV | Limiting Line Name | TR_LINE 19505_1 | TR_LINE 19505_1 | TR_LINE 19505_1 | TR_LINE 19505_1 | TR_LINE 19505_1
CA-Gladstone Rockhampton | 6030_Littlemore - Monto 66 kV | Loading (A) | 7.0242 | 7.0369 | 7.0404 | 7.0223 | 7.0417
CA-Gladstone Rockhampton | 6030_Littlemore - Monto 66 kV | Loading (MVA) | 0.84347 | 0.84651 | 0.84735 | 0.84301 | 0.84767
CA-Gladstone Rockhampton | 6030_Littlemore - Monto 66 kV | Loading (MW) | 0.0015424 | 0.001548 | 0.0015495 | 0.0015416 | 0.0015501
CA-Gladstone Rockhampton | 6030_Littlemore - Monto 66 kV | Power Factor | 0.001768 | 0.001768 | 0.001768 | 0.001768 | 0.001768
CA-Gladstone Rockhampton | 6030_Littlemore - Monto 66 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
CA-Gladstone Rockhampton | 6030_Littlemore - Monto 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6030_Littlemore - Monto 66 kV | Min Voltage at Constrained Conductor | 69.3281 | 69.4533 | 69.4874 | 69.3095 | 69.5006
CA-Gladstone Rockhampton | 6030_Littlemore - Monto 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Gladstone Rockhampton | 6031_Calliope - Littlemore 66 kV | % of Rated A | 13.42% | 13.55% | 13.65% | 13.71% | 13.81%
CA-Gladstone Rockhampton | 6031_Calliope - Littlemore 66 kV | Limiting Line Name | TR_LINE 13872_1 | TR_LINE 13872_1 | TR_LINE 13872_1 | TR_LINE 13872_1 | TR_LINE 13872_1
CA-Gladstone Rockhampton | 6031_Calliope - Littlemore 66 kV | Loading (A) | 17.7206 | 17.8897 | 18.0209 | 18.0929 | 18.2342
CA-Gladstone Rockhampton | 6031_Calliope - Littlemore 66 kV | Loading (MVA) | 2.1021 | 2.1253 | 2.1414 | 2.1439 | 2.1663
CA-Gladstone Rockhampton | 6031_Calliope - Littlemore 66 kV | Loading (MW) | 0.49446 | 0.5641 | 0.61951 | 0.66521 | 0.7044
CA-Gladstone Rockhampton | 6031_Calliope - Littlemore 66 kV | Power Factor | 0.23503 | 0.26522 | 0.28911 | 0.31008 | 0.32497
CA-Gladstone Rockhampton | 6031_Calliope - Littlemore 66 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
CA-Gladstone Rockhampton | 6031_Calliope - Littlemore 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6031_Calliope - Littlemore 66 kV | Min Voltage at Constrained Conductor | 68.4894 | 68.5904 | 68.6057 | 68.4138 | 68.5905
CA-Gladstone Rockhampton | 6031_Calliope - Littlemore 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Gladstone Rockhampton | 6032_Boyne Residential Tee-Awoonga 66 kV | % of Rated A | 3.16% | 4.76% | 4.526% | 4.327% | 4.136%
CA-Gladstone Rockhampton | 6032_Boyne Residential Tee-Awoonga 66 kV | Limiting Line Name | TR_LINE 69280_1 | TR_LINE 69280_1 | TR_LINE 69280_1 | TR_LINE 69280_1 | TR_LINE 69280_1
CA-Gladstone Rockhampton | 6032_Boyne Residential Tee-Awoonga 66 kV | Loading (A) | 6.6683 | 10.0427 | 9.5502 | 9.1299 | 8.7273
CA-Gladstone Rockhampton | 6032_Boyne Residential Tee-Awoonga 66 kV | Loading (MVA) | 0.79028 | 1.1917 | 1.1335 | 1.0806 | 1.0356
CA-Gladstone Rockhampton | 6032_Boyne Residential Tee-Awoonga 66 kV | Loading (MW) | 0.20665 | 0.89929 | 0.84531 | 0.79987 | 0.75473
CA-Gladstone Rockhampton | 6032_Boyne Residential Tee-Awoonga 66 kV | Power Factor | 0.26148 | 0.75461 | 0.74573 | 0.74021 | 0.72877
CA-Gladstone Rockhampton | 6032_Boyne Residential Tee-Awoonga 66 kV | Rating (A) | 211 | 211 | 211 | 211 | 211
CA-Gladstone Rockhampton | 6032_Boyne Residential Tee-Awoonga 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6032_Boyne Residential Tee-Awoonga 66 kV | Min Voltage at Constrained Conductor | 68.4234 | 68.5121 | 68.5269 | 68.335 | 68.5107
CA-Gladstone Rockhampton | 6032_Boyne Residential Tee-Awoonga 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Gladstone Rockhampton | 6034_Boyne Residential Tee - BORE 66 kV | % of Rated A | 9.207% | 10.64% | 11.84% | 12.9% | 13.79%
CA-Gladstone Rockhampton | 6034_Boyne Residential Tee - BORE 66 kV | Limiting Line Name | TR_LINE 18809_1 | TR_LINE 18809_1 | TR_LINE 18809_1 | TR_LINE 18809_1 | TR_LINE 18809_1
CA-Gladstone Rockhampton | 6034_Boyne Residential Tee - BORE 66 kV | Loading (A) | 15.1919 | 17.5598 | 19.5302 | 21.2795 | 22.7525
CA-Gladstone Rockhampton | 6034_Boyne Residential Tee - BORE 66 kV | Loading (MVA) | 1.8004 | 2.0838 | 2.3181 | 2.5186 | 2.6999
CA-Gladstone Rockhampton | 6034_Boyne Residential Tee - BORE 66 kV | Loading (MW) | 1.7938 | 2.0785 | 2.3137 | 2.5149 | 2.6966
CA-Gladstone Rockhampton | 6034_Boyne Residential Tee - BORE 66 kV | Power Factor | 0.9963 | 0.99742 | 0.99804 | 0.99846 | 0.99872
CA-Gladstone Rockhampton | 6034_Boyne Residential Tee - BORE 66 kV | Rating (A) | 165 | 165 | 165 | 165 | 165
CA-Gladstone Rockhampton | 6034_Boyne Residential Tee - BORE 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6034_Boyne Residential Tee - BORE 66 kV | Min Voltage at Constrained Conductor | 68.4234 | 68.5121 | 68.5269 | 68.335 | 68.5107
CA-Gladstone Rockhampton | 6034_Boyne Residential Tee - BORE 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Gladstone Rockhampton | 6039_Clinton Industrial - Beecher 66 kV | % of Rated A | 6.465% | 6.456% | 6.456% | 6.472% | 6.432%
CA-Gladstone Rockhampton | 6039_Clinton Industrial - Beecher 66 kV | Limiting Line Name | TR_LINE 33766_1 | TR_LINE 33766_1 | TR_LINE 33766_1 | TR_LINE 33766_1 | TR_LINE 33766_1
CA-Gladstone Rockhampton | 6039_Clinton Industrial - Beecher 66 kV | Loading (A) | 15.8391 | 15.817 | 15.817 | 15.8563 | 15.7579
CA-Gladstone Rockhampton | 6039_Clinton Industrial - Beecher 66 kV | Loading (MVA) | 1.8757 | 1.8762 | 1.8762 | 1.8753 | 1.8776
CA-Gladstone Rockhampton | 6039_Clinton Industrial - Beecher 66 kV | Loading (MW) | 1.8179 | 1.8179 | 1.8179 | 1.818 | 1.8177
CA-Gladstone Rockhampton | 6039_Clinton Industrial - Beecher 66 kV | Power Factor | 0.9692 | 0.96891 | 0.96891 | 0.96943 | 0.96811
CA-Gladstone Rockhampton | 6039_Clinton Industrial - Beecher 66 kV | Rating (A) | 245 | 245 | 245 | 245 | 245
CA-Gladstone Rockhampton | 6039_Clinton Industrial - Beecher 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6039_Clinton Industrial - Beecher 66 kV | Min Voltage at Constrained Conductor | 68.3712 | 68.4852 | 68.4857 | 68.2831 | 68.793
CA-Gladstone Rockhampton | 6039_Clinton Industrial - Beecher 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Gladstone Rockhampton | 6041_Yarwun - Boat Creek 66 kV | % of Rated A | 11.95% | 11.93% | 11.93% | 11.96% | 11.88%
CA-Gladstone Rockhampton | 6041_Yarwun - Boat Creek 66 kV | Limiting Line Name | TR_LINE 15181_1 | TR_LINE 15181_1 | TR_LINE 15181_1 | TR_LINE 15181_1 | TR_LINE 15181_1
CA-Gladstone Rockhampton | 6041_Yarwun - Boat Creek 66 kV | Loading (A) | 15.7699 | 15.7474 | 15.7473 | 15.7874 | 15.687
CA-Gladstone Rockhampton | 6041_Yarwun - Boat Creek 66 kV | Loading (MVA) | 1.867 | 1.8675 | 1.8675 | 1.8667 | 1.8687
CA-Gladstone Rockhampton | 6041_Yarwun - Boat Creek 66 kV | Loading (MW) | 1.8172 | 1.8172 | 1.8172 | 1.8173 | 1.817
CA-Gladstone Rockhampton | 6041_Yarwun - Boat Creek 66 kV | Power Factor | 0.97333 | 0.97307 | 0.97307 | 0.97353 | 0.97236
CA-Gladstone Rockhampton | 6041_Yarwun - Boat Creek 66 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
CA-Gladstone Rockhampton | 6041_Yarwun - Boat Creek 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6041_Yarwun - Boat Creek 66 kV | Min Voltage at Constrained Conductor | 68.3094 | 68.4236 | 68.4241 | 68.2211 | 68.7319
CA-Gladstone Rockhampton | 6041_Yarwun - Boat Creek 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Gladstone Rockhampton | 6044_Raglan-East End Quarry/Yarwun 66 kV | % of Rated A | 1.512% | 1.513% | 1.517% | 1.518% | 1.518%
CA-Gladstone Rockhampton | 6044_Raglan-East End Quarry/Yarwun 66 kV | Limiting Line Name | TR_LINE 22122_1 | TR_LINE 22122_1 | TR_LINE 22122_1 | TR_LINE 22122_1 | TR_LINE 22122_1
CA-Gladstone Rockhampton | 6044_Raglan-East End Quarry/Yarwun 66 kV | Loading (A) | 1.9958 | 1.9969 | 2.003 | 2.0039 | 2.0036
CA-Gladstone Rockhampton | 6044_Raglan-East End Quarry/Yarwun 66 kV | Loading (MVA) | 0.24005 | 0.24031 | 0.24177 | 0.24201 | 0.24192
CA-Gladstone Rockhampton | 6044_Raglan-East End Quarry/Yarwun 66 kV | Loading (MW) | 3.5733e-05 | 3.5772e-05 | 3.5989e-05 | 3.6024e-05 | 3.6011e-05
CA-Gladstone Rockhampton | 6044_Raglan-East End Quarry/Yarwun 66 kV | Power Factor | 0.00014836 | 0.00014836 | 0.00014836 | 0.00014836 | 0.00014836
CA-Gladstone Rockhampton | 6044_Raglan-East End Quarry/Yarwun 66 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
CA-Gladstone Rockhampton | 6044_Raglan-East End Quarry/Yarwun 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6044_Raglan-East End Quarry/Yarwun 66 kV | Min Voltage at Constrained Conductor | 69.4415 | 69.4789 | 69.69 | 69.7235 | 69.7107
CA-Gladstone Rockhampton | 6044_Raglan-East End Quarry/Yarwun 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Gladstone Rockhampton | 6045_Coominglah Tee - Monto 66 kV | % of Rated A | 10.79% | 10.68% | 10.61% | 10.57% | 10.54%
CA-Gladstone Rockhampton | 6045_Coominglah Tee - Monto 66 kV | Limiting Line Name | TR_LINE 75765_1 | TR_LINE 75765_1 | TR_LINE 75765_1 | TR_LINE 75765_1 | TR_LINE 75765_1
CA-Gladstone Rockhampton | 6045_Coominglah Tee - Monto 66 kV | Loading (A) | 14.2365 | 14.0979 | 14.0102 | 13.9524 | 13.9165
CA-Gladstone Rockhampton | 6045_Coominglah Tee - Monto 66 kV | Loading (MVA) | 1.7261 | 1.7112 | 1.7012 | 1.6944 | 1.6899
CA-Gladstone Rockhampton | 6045_Coominglah Tee - Monto 66 kV | Loading (MW) | 0.42573 | 0.33329 | 0.25981 | 0.19859 | 0.14899
CA-Gladstone Rockhampton | 6045_Coominglah Tee - Monto 66 kV | Power Factor | 0.24664 | 0.19477 | 0.15272 | 0.11721 | 0.088165
CA-Gladstone Rockhampton | 6045_Coominglah Tee - Monto 66 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
CA-Gladstone Rockhampton | 6045_Coominglah Tee - Monto 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6045_Coominglah Tee - Monto 66 kV | Min Voltage at Constrained Conductor | 70.002 | 70.077 | 70.1072 | 70.1128 | 70.1078
CA-Gladstone Rockhampton | 6045_Coominglah Tee - Monto 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Gladstone Rockhampton | 6046_Mt Morgan - Wowan 66 kV | % of Rated A | 4.354% | 43.55% | 85.51% | 85.48% | 85.5%
CA-Gladstone Rockhampton | 6046_Mt Morgan - Wowan 66 kV | Limiting Line Name | TR_LINE 22233_1 | TR_LINE 22233_1 | TR_LINE 22233_1 | TR_LINE 22233_1 | TR_LINE 22233_1
CA-Gladstone Rockhampton | 6046_Mt Morgan - Wowan 66 kV | Loading (A) | 5.7474 | 57.4831 | 112.876 | 112.8312 | 112.8589
CA-Gladstone Rockhampton | 6046_Mt Morgan - Wowan 66 kV | Loading (MVA) | 0.6938 | 6.8401 | 13.2649 | 13.2649 | 13.2649
CA-Gladstone Rockhampton | 6046_Mt Morgan - Wowan 66 kV | Loading (MW) | 0.30049 | 6.8142 | 13.2539 | 13.2538 | 13.2539
CA-Gladstone Rockhampton | 6046_Mt Morgan - Wowan 66 kV | Power Factor | 0.43311 | 0.99622 | 0.99917 | 0.99916 | 0.99917
CA-Gladstone Rockhampton | 6046_Mt Morgan - Wowan 66 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
CA-Gladstone Rockhampton | 6046_Mt Morgan - Wowan 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6046_Mt Morgan - Wowan 66 kV | Min Voltage at Constrained Conductor | 69.6945 | 68.6994 | 67.8461 | 67.8729 | 67.8563
CA-Gladstone Rockhampton | 6046_Mt Morgan - Wowan 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Gladstone Rockhampton | 6047_Coominglah Sub Tee 66 kV | % of Rated A | 0.06264% | 0.06098% | 0.168% | 0.2638% | 0.3553%
CA-Gladstone Rockhampton | 6047_Coominglah Sub Tee 66 kV | Limiting Line Name | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1 | TR_LINE 22254_1
CA-Gladstone Rockhampton | 6047_Coominglah Sub Tee 66 kV | Loading (A) | 0.096473 | 0.093907 | 0.25876 | 0.40626 | 0.54719
CA-Gladstone Rockhampton | 6047_Coominglah Sub Tee 66 kV | Loading (MVA) | 0.011697 | 0.011398 | 0.031421 | 0.049336 | 0.066445
CA-Gladstone Rockhampton | 6047_Coominglah Sub Tee 66 kV | Loading (MW) | 0.01163 | 0.01133 | 0.031397 | 0.049322 | 0.066436
CA-Gladstone Rockhampton | 6047_Coominglah Sub Tee 66 kV | Power Factor | 0.99431 | 0.99398 | 0.99924 | 0.99971 | 0.99986
CA-Gladstone Rockhampton | 6047_Coominglah Sub Tee 66 kV | Rating (A) | 154 | 154 | 154 | 154 | 154
CA-Gladstone Rockhampton | 6047_Coominglah Sub Tee 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6047_Coominglah Sub Tee 66 kV | Min Voltage at Constrained Conductor | 70.002 | 70.0769 | 70.1071 | 70.1127 | 70.1078
CA-Gladstone Rockhampton | 6047_Coominglah Sub Tee 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Gladstone Rockhampton | 6050_Parkhurst - Frenchville 66 kV | % of Rated A | 8.448% | 9.167% | 9.717% | 11.05% | 12.52%
CA-Gladstone Rockhampton | 6050_Parkhurst - Frenchville 66 kV | Limiting Line Name | TR_LINE 22210_1 | TR_LINE 22210_1 | TR_LINE 22210_1 | TR_LINE 22210_1 | TR_LINE 22210_1
CA-Gladstone Rockhampton | 6050_Parkhurst - Frenchville 66 kV | Loading (A) | 33.8775 | 36.7612 | 38.9671 | 44.3295 | 50.2146
CA-Gladstone Rockhampton | 6050_Parkhurst - Frenchville 66 kV | Loading (MVA) | 4.0779 | 4.4322 | 4.7014 | 5.3532 | 6.0657
CA-Gladstone Rockhampton | 6050_Parkhurst - Frenchville 66 kV | Loading (MW) | 3.5932 | 4.0169 | 4.6899 | 5.3437 | 6.0573
CA-Gladstone Rockhampton | 6050_Parkhurst - Frenchville 66 kV | Power Factor | 0.88114 | 0.90631 | 0.99754 | 0.99821 | 0.99861
CA-Gladstone Rockhampton | 6050_Parkhurst - Frenchville 66 kV | Rating (A) | 401 | 401 | 401 | 401 | 401
CA-Gladstone Rockhampton | 6050_Parkhurst - Frenchville 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6050_Parkhurst - Frenchville 66 kV | Min Voltage at Constrained Conductor | 69.4961 | 69.6095 | 69.6567 | 69.7198 | 69.74
CA-Gladstone Rockhampton | 6050_Parkhurst - Frenchville 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Gladstone Rockhampton | 6051_Parkhurst - Keppel 66 kV | % of Rated A | 11.95% | 18.31% | 25.53% | 32.43% | 40.03%
CA-Gladstone Rockhampton | 6051_Parkhurst - Keppel 66 kV | Limiting Line Name | TR_LINE 19655_1 | TR_LINE 19655_1 | TR_LINE 19655_1 | TR_LINE 19655_1 | TR_LINE 19655_1
CA-Gladstone Rockhampton | 6051_Parkhurst - Keppel 66 kV | Loading (A) | 25.336 | 38.814 | 54.12 | 68.7547 | 84.8621
CA-Gladstone Rockhampton | 6051_Parkhurst - Keppel 66 kV | Loading (MVA) | 3.0774 | 4.7354 | 6.6249 | 8.4492 | 10.4664
CA-Gladstone Rockhampton | 6051_Parkhurst - Keppel 66 kV | Loading (MW) | 2.3472 | 4.3213 | 6.2495 | 8.1838 | 10.277
CA-Gladstone Rockhampton | 6051_Parkhurst - Keppel 66 kV | Power Factor | 0.76229 | 0.91185 | 0.94239 | 0.96784 | 0.98158
CA-Gladstone Rockhampton | 6051_Parkhurst - Keppel 66 kV | Rating (A) | 212 | 212 | 212 | 212 | 212
CA-Gladstone Rockhampton | 6051_Parkhurst - Keppel 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6051_Parkhurst - Keppel 66 kV | Min Voltage at Constrained Conductor | 70.1259 | 70.4386 | 70.6737 | 70.9158 | 71.1229
CA-Gladstone Rockhampton | 6051_Parkhurst - Keppel 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Gladstone Rockhampton | 6053_Parkhurst - Pandoin 66 kV | % of Rated A | 7.121% | 4.223% | 10.01% | 11.04% | 13.57%
CA-Gladstone Rockhampton | 6053_Parkhurst - Pandoin 66 kV | Limiting Line Name | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1 | TR_LINE 19773_1
CA-Gladstone Rockhampton | 6053_Parkhurst - Pandoin 66 kV | Loading (A) | 37.2413 | 22.0874 | 52.3685 | 57.7465 | 70.9719
CA-Gladstone Rockhampton | 6053_Parkhurst - Pandoin 66 kV | Loading (MVA) | 4.4845 | 2.6627 | 6.2908 | 6.9389 | 8.5254
CA-Gladstone Rockhampton | 6053_Parkhurst - Pandoin 66 kV | Loading (MW) | 4.4664 | 2.6095 | 0.19242 | 2.9028 | 5.7904
CA-Gladstone Rockhampton | 6053_Parkhurst - Pandoin 66 kV | Power Factor | 0.99598 | 0.98001 | 0.029678 | 0.41733 | 0.67796
CA-Gladstone Rockhampton | 6053_Parkhurst - Pandoin 66 kV | Rating (A) | 523 | 523 | 523 | 523 | 523
CA-Gladstone Rockhampton | 6053_Parkhurst - Pandoin 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6053_Parkhurst - Pandoin 66 kV | Min Voltage at Constrained Conductor | 69.4897 | 69.5925 | 69.3541 | 69.3755 | 69.353
CA-Gladstone Rockhampton | 6053_Parkhurst - Pandoin 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Gladstone Rockhampton | 6066_Bocoolima Tee -Wooderson 66 kV | % of Rated A | 3.189% | 3.194% | 3.195% | 3.186% | 3.194%
CA-Gladstone Rockhampton | 6066_Bocoolima Tee -Wooderson 66 kV | Limiting Line Name | TR_LINE 22217_1 | TR_LINE 22217_1 | TR_LINE 22217_1 | TR_LINE 22217_1 | TR_LINE 22217_1
CA-Gladstone Rockhampton | 6066_Bocoolima Tee -Wooderson 66 kV | Loading (A) | 5.39 | 5.3979 | 5.3991 | 5.3841 | 5.3979
CA-Gladstone Rockhampton | 6066_Bocoolima Tee -Wooderson 66 kV | Loading (MVA) | 0.63939 | 0.64127 | 0.64156 | 0.63798 | 0.64127
CA-Gladstone Rockhampton | 6066_Bocoolima Tee -Wooderson 66 kV | Loading (MW) | 0.033148 | 0.033149 | 0.033169 | 0.033168 | 0.033169
CA-Gladstone Rockhampton | 6066_Bocoolima Tee -Wooderson 66 kV | Power Factor | 0.051844 | 0.051693 | 0.051701 | 0.051988 | 0.051724
CA-Gladstone Rockhampton | 6066_Bocoolima Tee -Wooderson 66 kV | Rating (A) | 169 | 169 | 169 | 169 | 169
CA-Gladstone Rockhampton | 6066_Bocoolima Tee -Wooderson 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6066_Bocoolima Tee -Wooderson 66 kV | Min Voltage at Constrained Conductor | 68.4882 | 68.5892 | 68.6045 | 68.4125 | 68.5893
CA-Gladstone Rockhampton | 6066_Bocoolima Tee -Wooderson 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Gladstone Rockhampton | 6074_Lakes Creek - Tanby 66 kV | % of Rated A | 5.369% | 8.742% | 11.86% | 15.09% | 18.54%
CA-Gladstone Rockhampton | 6074_Lakes Creek - Tanby 66 kV | Limiting Line Name | TR_LINE 19802_1 | TR_LINE 19802_1 | TR_LINE 19802_1 | TR_LINE 19802_1 | TR_LINE 19802_1
CA-Gladstone Rockhampton | 6074_Lakes Creek - Tanby 66 kV | Loading (A) | 21.4242 | 34.8803 | 47.3396 | 60.1991 | 73.9634
CA-Gladstone Rockhampton | 6074_Lakes Creek - Tanby 66 kV | Loading (MVA) | 2.587 | 4.2183 | 5.7384 | 7.3053 | 8.9802
CA-Gladstone Rockhampton | 6074_Lakes Creek - Tanby 66 kV | Loading (MW) | 2.0275 | 3.9063 | 5.6108 | 7.2176 | 8.9228
CA-Gladstone Rockhampton | 6074_Lakes Creek - Tanby 66 kV | Power Factor | 0.78348 | 0.92589 | 0.97765 | 0.98791 | 0.99354
CA-Gladstone Rockhampton | 6074_Lakes Creek - Tanby 66 kV | Rating (A) | 399 | 399 | 399 | 399 | 399
CA-Gladstone Rockhampton | 6074_Lakes Creek - Tanby 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6074_Lakes Creek - Tanby 66 kV | Min Voltage at Constrained Conductor | 69.717 | 69.8226 | 69.9855 | 70.0626 | 70.0982
CA-Gladstone Rockhampton | 6074_Lakes Creek - Tanby 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Gladstone Rockhampton | 6075_Keppel - Farnborough 66 kV | % of Rated A | 0.3206% | 0.3221% | 0.3233% | 0.3245% | 0.3255%
CA-Gladstone Rockhampton | 6075_Keppel - Farnborough 66 kV | Limiting Line Name | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2 | TR_LINE 168739_2
CA-Gladstone Rockhampton | 6075_Keppel - Farnborough 66 kV | Loading (A) | 1.2118 | 1.2175 | 1.222 | 1.2265 | 1.2304
CA-Gladstone Rockhampton | 6075_Keppel - Farnborough 66 kV | Loading (MVA) | 0.1473 | 0.1487 | 0.14979 | 0.15089 | 0.15186
CA-Gladstone Rockhampton | 6075_Keppel - Farnborough 66 kV | Loading (MW) | 3.6706e-06 | 3.7052e-06 | 3.7326e-06 | 3.7601e-06 | 3.784e-06
CA-Gladstone Rockhampton | 6075_Keppel - Farnborough 66 kV | Power Factor | 2.192e-06 | 2.188e-06 | 2.1901e-06 | 2.1926e-06 | 2.1903e-06
CA-Gladstone Rockhampton | 6075_Keppel - Farnborough 66 kV | Rating (A) | 378 | 378 | 378 | 378 | 378
CA-Gladstone Rockhampton | 6075_Keppel - Farnborough 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6075_Keppel - Farnborough 66 kV | Min Voltage at Constrained Conductor | 70.1804 | 70.5124 | 70.7711 | 71.0312 | 71.2573
CA-Gladstone Rockhampton | 6075_Keppel - Farnborough 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Gladstone Rockhampton | 6077_Farnborough - Capricorn Resort 66kV | % of Rated A | 0.07071% | 0.07104% | 0.0713% | 0.07156% | 0.07179%
CA-Gladstone Rockhampton | 6077_Farnborough - Capricorn Resort 66kV | Limiting Line Name | TR_LINE FARB-FARE | TR_LINE FARB-FARE | TR_LINE FARB-FARE | TR_LINE FARB-FARE | TR_LINE FARB-FARE
CA-Gladstone Rockhampton | 6077_Farnborough - Capricorn Resort 66kV | Loading (A) | 0.26868 | 0.26995 | 0.27094 | 0.27194 | 0.2728
CA-Gladstone Rockhampton | 6077_Farnborough - Capricorn Resort 66kV | Loading (MVA) | 0.032662 | 0.032971 | 0.033214 | 0.033458 | 0.033672
CA-Gladstone Rockhampton | 6077_Farnborough - Capricorn Resort 66kV | Loading (MW) | 4.6182e-08 | 4.662e-08 | 4.6963e-08 | 4.7309e-08 | 4.761e-08
CA-Gladstone Rockhampton | 6077_Farnborough - Capricorn Resort 66kV | Power Factor | 1.414e-06 | 1.414e-06 | 1.414e-06 | 1.414e-06 | 1.414e-06
CA-Gladstone Rockhampton | 6077_Farnborough - Capricorn Resort 66kV | Rating (A) | 380 | 380 | 380 | 380 | 380
CA-Gladstone Rockhampton | 6077_Farnborough - Capricorn Resort 66kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6077_Farnborough - Capricorn Resort 66kV | Min Voltage at Constrained Conductor | 70.1846 | 70.5166 | 70.7754 | 71.0354 | 71.2616
CA-Gladstone Rockhampton | 6077_Farnborough - Capricorn Resort 66kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Gladstone Rockhampton | 6082_Farnborough Tee - Yeppoon 66 kV | % of Rated A | 11.5% | 18.02% | 25.29% | 32.26% | 39.9%
CA-Gladstone Rockhampton | 6082_Farnborough Tee - Yeppoon 66 kV | Limiting Line Name | TR_LINE 19629_1 | TR_LINE 19629_1 | TR_LINE 19629_1 | TR_LINE 19629_1 | TR_LINE 19629_1
CA-Gladstone Rockhampton | 6082_Farnborough Tee - Yeppoon 66 kV | Loading (A) | 24.3775 | 38.2104 | 53.6244 | 68.3813 | 84.5776
CA-Gladstone Rockhampton | 6082_Farnborough Tee - Yeppoon 66 kV | Loading (MVA) | 2.9632 | 4.6667 | 6.5732 | 8.413 | 10.439
CA-Gladstone Rockhampton | 6082_Farnborough Tee - Yeppoon 66 kV | Loading (MW) | 2.3473 | 4.3214 | 6.2497 | 8.1841 | 10.2775
CA-Gladstone Rockhampton | 6082_Farnborough Tee - Yeppoon 66 kV | Power Factor | 0.79211 | 0.92598 | 0.95076 | 0.97276 | 0.98451
CA-Gladstone Rockhampton | 6082_Farnborough Tee - Yeppoon 66 kV | Rating (A) | 212 | 212 | 212 | 212 | 212
CA-Gladstone Rockhampton | 6082_Farnborough Tee - Yeppoon 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6082_Farnborough Tee - Yeppoon 66 kV | Min Voltage at Constrained Conductor | 70.1804 | 70.5124 | 70.7711 | 71.0312 | 71.2573
CA-Gladstone Rockhampton | 6082_Farnborough Tee - Yeppoon 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Gladstone Rockhampton | 6090_Egan's Hill - Raglan 66 kV | % of Rated A | 6.494% | 5.98% | 5.623% | 5.36% | 5.17%
CA-Gladstone Rockhampton | 6090_Egan's Hill - Raglan 66 kV | Limiting Line Name | TR_LINE 160589_1 | TR_LINE 160589_1 | TR_LINE 160589_1 | TR_LINE 160589_1 | TR_LINE 160589_1
CA-Gladstone Rockhampton | 6090_Egan's Hill - Raglan 66 kV | Loading (A) | 8.5715 | 7.8932 | 7.4224 | 7.0753 | 6.8239
CA-Gladstone Rockhampton | 6090_Egan's Hill - Raglan 66 kV | Loading (MVA) | 1.0322 | 0.95067 | 0.89642 | 0.85472 | 0.82407
CA-Gladstone Rockhampton | 6090_Egan's Hill - Raglan 66 kV | Loading (MW) | 0.78986 | 0.67776 | 0.59368 | 0.527 | 0.47544
CA-Gladstone Rockhampton | 6090_Egan's Hill - Raglan 66 kV | Power Factor | 0.76522 | 0.71293 | 0.66228 | 0.61658 | 0.57694
CA-Gladstone Rockhampton | 6090_Egan's Hill - Raglan 66 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
CA-Gladstone Rockhampton | 6090_Egan's Hill - Raglan 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6090_Egan's Hill - Raglan 66 kV | Min Voltage at Constrained Conductor | 69.5244 | 69.5369 | 69.7284 | 69.7464 | 69.7217
CA-Gladstone Rockhampton | 6090_Egan's Hill - Raglan 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Gladstone Rockhampton | 6091_Egan's Hill - Gavial 66 kV | % of Rated A | 34.01% | 40.35% | 78.99% | 78.96% | 78.98%
CA-Gladstone Rockhampton | 6091_Egan's Hill - Gavial 66 kV | Limiting Line Name | TR_LINE 13465_1 | TR_LINE 22265_1 | TR_LINE 22265_1 | TR_LINE 22265_1 | TR_LINE 22265_1
CA-Gladstone Rockhampton | 6091_Egan's Hill - Gavial 66 kV | Loading (A) | 48.6334 | 57.7007 | 112.957 | 112.9124 | 112.9401
CA-Gladstone Rockhampton | 6091_Egan's Hill - Gavial 66 kV | Loading (MVA) | 5.8539 | 6.9494 | 13.617 | 13.6167 | 13.6169
CA-Gladstone Rockhampton | 6091_Egan's Hill - Gavial 66 kV | Loading (MW) | 5.7728 | 6.9066 | 13.6091 | 13.6087 | 13.6089
CA-Gladstone Rockhampton | 6091_Egan's Hill - Gavial 66 kV | Power Factor | 0.98614 | 0.99384 | 0.99942 | 0.99941 | 0.99942
CA-Gladstone Rockhampton | 6091_Egan's Hill - Gavial 66 kV | Rating (A) | 143 | 143 | 143 | 143 | 143
CA-Gladstone Rockhampton | 6091_Egan's Hill - Gavial 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6091_Egan's Hill - Gavial 66 kV | Min Voltage at Constrained Conductor | 69.4933 | 69.5258 | 69.5788 | 69.6048 | 69.5887
CA-Gladstone Rockhampton | 6091_Egan's Hill - Gavial 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Gladstone Rockhampton | 6093_Gavial - Mt Morgan 66 kV | % of Rated A | 5.273% | 43.63% | 85.55% | 85.51% | 85.53%
CA-Gladstone Rockhampton | 6093_Gavial - Mt Morgan 66 kV | Limiting Line Name | TR_LINE 19113_1 | TR_LINE 19767_1 | TR_LINE 19767_1 | TR_LINE 19767_1 | TR_LINE 19767_1
CA-Gladstone Rockhampton | 6093_Gavial - Mt Morgan 66 kV | Loading (A) | 7.5403 | 57.5977 | 112.9228 | 112.8781 | 112.9058
CA-Gladstone Rockhampton | 6093_Gavial - Mt Morgan 66 kV | Loading (MVA) | 0.9096 | 6.9038 | 13.4745 | 13.4743 | 13.4744
CA-Gladstone Rockhampton | 6093_Gavial - Mt Morgan 66 kV | Loading (MW) | 0.30157 | 6.8692 | 13.4657 | 13.4654 | 13.4656
CA-Gladstone Rockhampton | 6093_Gavial - Mt Morgan 66 kV | Power Factor | 0.33154 | 0.995 | 0.99917 | 0.99917 | 0.99917
CA-Gladstone Rockhampton | 6093_Gavial - Mt Morgan 66 kV | Rating (A) | 143 | 132 | 132 | 132 | 132
CA-Gladstone Rockhampton | 6093_Gavial - Mt Morgan 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6093_Gavial - Mt Morgan 66 kV | Min Voltage at Constrained Conductor | 69.6473 | 68.7023 | 67.8522 | 67.879 | 67.8624
CA-Gladstone Rockhampton | 6093_Gavial - Mt Morgan 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Gladstone Rockhampton | 6094_Malchi Tee - Malchi 66 kV | % of Rated A | 29.85% | 35.3% | 39.97% | 44.22% | 48.48%
CA-Gladstone Rockhampton | 6094_Malchi Tee - Malchi 66 kV | Limiting Line Name | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1 | TR_LINE 22172_1
CA-Gladstone Rockhampton | 6094_Malchi Tee - Malchi 66 kV | Loading (A) | 50.4513 | 59.6511 | 67.5487 | 74.7365 | 81.9329
CA-Gladstone Rockhampton | 6094_Malchi Tee - Malchi 66 kV | Loading (MVA) | 6.1047 | 7.2112 | 8.1773 | 9.0545 | 9.9281
CA-Gladstone Rockhampton | 6094_Malchi Tee - Malchi 66 kV | Loading (MW) | 6.103 | 7.2084 | 8.1732 | 9.0489 | 9.9208
CA-Gladstone Rockhampton | 6094_Malchi Tee - Malchi 66 kV | Power Factor | 0.99972 | 0.99961 | 0.9995 | 0.99939 | 0.99926
CA-Gladstone Rockhampton | 6094_Malchi Tee - Malchi 66 kV | Rating (A) | 169 | 169 | 169 | 169 | 169
CA-Gladstone Rockhampton | 6094_Malchi Tee - Malchi 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6094_Malchi Tee - Malchi 66 kV | Min Voltage at Constrained Conductor | 69.6407 | 69.5387 | 69.6039 | 69.6302 | 69.6144
CA-Gladstone Rockhampton | 6094_Malchi Tee - Malchi 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Gladstone Rockhampton | 6095_Egan's Hill-Rockhampton South 66 kV | % of Rated A | 12.56% | 6.108% | 5.764% | 5.889% | 6.709%
CA-Gladstone Rockhampton | 6095_Egan's Hill-Rockhampton South 66 kV | Limiting Line Name | TR_LINE 20983_1 | TR_LINE 20983_1 | TR_LINE 20972_1 | TR_LINE 20972_1 | TR_LINE 20972_1
CA-Gladstone Rockhampton | 6095_Egan's Hill-Rockhampton South 66 kV | Loading (A) | 31.1439 | 15.1473 | 14.2952 | 14.6046 | 16.6371
CA-Gladstone Rockhampton | 6095_Egan's Hill-Rockhampton South 66 kV | Loading (MVA) | 3.7476 | 1.8234 | 1.7237 | 1.7616 | 2.0065
CA-Gladstone Rockhampton | 6095_Egan's Hill-Rockhampton South 66 kV | Loading (MW) | 3.5489 | 1.4997 | 0.0027466 | 0.32875 | 0.9807
CA-Gladstone Rockhampton | 6095_Egan's Hill-Rockhampton South 66 kV | Power Factor | 0.947 | 0.82249 | 0.0013103 | 0.18662 | 0.48875
CA-Gladstone Rockhampton | 6095_Egan's Hill-Rockhampton South 66 kV | Rating (A) | 248 | 248 | 248 | 248 | 248
CA-Gladstone Rockhampton | 6095_Egan's Hill-Rockhampton South 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6095_Egan's Hill-Rockhampton South 66 kV | Min Voltage at Constrained Conductor | 69.4609 | 69.4987 | 69.6173 | 69.6407 | 69.6317
CA-Gladstone Rockhampton | 6095_Egan's Hill-Rockhampton South 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Gladstone Rockhampton | 6097_Egan's Hill - Canning 66 kV | % of Rated A | 15.08% | 9.308% | 1.27% | 3.433% | 6.102%
CA-Gladstone Rockhampton | 6097_Egan's Hill - Canning 66 kV | Limiting Line Name | TR_LINE 20992_1 | TR_LINE 20992_1 | TR_LINE 21003_1 | TR_LINE 21003_1 | TR_LINE 21003_1
CA-Gladstone Rockhampton | 6097_Egan's Hill - Canning 66 kV | Loading (A) | 37.3955 | 23.0827 | 3.1496 | 8.5132 | 15.1324
CA-Gladstone Rockhampton | 6097_Egan's Hill - Canning 66 kV | Loading (MVA) | 4.5015 | 2.7797 | 0.38008 | 1.0279 | 1.827
CA-Gladstone Rockhampton | 6097_Egan's Hill - Canning 66 kV | Loading (MW) | 3.7677 | 1.5925 | 0.060843 | 0.93762 | 1.7686
CA-Gladstone Rockhampton | 6097_Egan's Hill - Canning 66 kV | Power Factor | 0.83699 | 0.57291 | 0.16008 | 0.91217 | 0.96805
CA-Gladstone Rockhampton | 6097_Egan's Hill - Canning 66 kV | Rating (A) | 248 | 248 | 248 | 248 | 248
CA-Gladstone Rockhampton | 6097_Egan's Hill - Canning 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6097_Egan's Hill - Canning 66 kV | Min Voltage at Constrained Conductor | 69.4926 | 69.5272 | 69.6713 | 69.7027 | 69.6882
CA-Gladstone Rockhampton | 6097_Egan's Hill - Canning 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Gladstone Rockhampton | 6100_Boat Creek - ICI 66 kV | % of Rated A | 1.61% | 1.594% | 1.594% | 1.594% | 1.609%
CA-Gladstone Rockhampton | 6100_Boat Creek - ICI 66 kV | Limiting Line Name | TR_LINE 50343_1 | TR_LINE 50343_1 | TR_LINE 50343_1 | TR_LINE 50343_1 | TR_LINE 50343_1
CA-Gladstone Rockhampton | 6100_Boat Creek - ICI 66 kV | Loading (A) | 11.9164 | 11.7953 | 11.797 | 11.795 | 11.9081
CA-Gladstone Rockhampton | 6100_Boat Creek - ICI 66 kV | Loading (MVA) | 1.3864 | 1.3864 | 1.3864 | 1.3864 | 1.3864
CA-Gladstone Rockhampton | 6100_Boat Creek - ICI 66 kV | Loading (MW) | 1.3864 | 1.3864 | 1.3864 | 1.3864 | 1.3864
CA-Gladstone Rockhampton | 6100_Boat Creek - ICI 66 kV | Power Factor | 0.99999 | 0.99999 | 0.99999 | 0.99999 | 0.99999
CA-Gladstone Rockhampton | 6100_Boat Creek - ICI 66 kV | Rating (A) | 740 | 740 | 740 | 740 | 740
CA-Gladstone Rockhampton | 6100_Boat Creek - ICI 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6100_Boat Creek - ICI 66 kV | Min Voltage at Constrained Conductor | 67.1714 | 67.8611 | 67.8514 | 67.8631 | 67.2184
CA-Gladstone Rockhampton | 6100_Boat Creek - ICI 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Gladstone Rockhampton | 6101_Boat Creek - Orica 66 kV | % of Rated A | 15.8% | 15.64% | 15.64% | 15.64% | 15.79%
CA-Gladstone Rockhampton | 6101_Boat Creek - Orica 66 kV | Limiting Line Name | TR_LINE pole4158700 to ORIC | TR_LINE pole4158700 to ORIC | TR_LINE pole4158700 to ORIC | TR_LINE pole4158700 to ORIC | TR_LINE pole4158700 to ORIC
CA-Gladstone Rockhampton | 6101_Boat Creek - Orica 66 kV | Loading (A) | 116.9169 | 115.7282 | 115.7447 | 115.7249 | 116.8351
CA-Gladstone Rockhampton | 6101_Boat Creek - Orica 66 kV | Loading (MVA) | 13.6011 | 13.6011 | 13.6011 | 13.6011 | 13.6011
CA-Gladstone Rockhampton | 6101_Boat Creek - Orica 66 kV | Loading (MW) | 13.6011 | 13.6011 | 13.6011 | 13.6011 | 13.6011
CA-Gladstone Rockhampton | 6101_Boat Creek - Orica 66 kV | Power Factor | 1 | 1 | 1 | 1 | 1
CA-Gladstone Rockhampton | 6101_Boat Creek - Orica 66 kV | Rating (A) | 740 | 740 | 740 | 740 | 740
CA-Gladstone Rockhampton | 6101_Boat Creek - Orica 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6101_Boat Creek - Orica 66 kV | Min Voltage at Constrained Conductor | 67.1585 | 67.8483 | 67.8386 | 67.8503 | 67.2055
CA-Gladstone Rockhampton | 6101_Boat Creek - Orica 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Gladstone Rockhampton | 6102_Boat Creek - Yarwun 66 kV | % of Rated A | 2.835% | 2.757% | 4.077% | 5.403% | 5.418%
CA-Gladstone Rockhampton | 6102_Boat Creek - Yarwun 66 kV | Limiting Line Name | TR_LINE 16859_1 | TR_LINE 16859_1 | TR_LINE 16861_2 | TR_LINE 16861_2 | TR_LINE 16861_2
CA-Gladstone Rockhampton | 6102_Boat Creek - Yarwun 66 kV | Loading (A) | 20.9786 | 20.3988 | 30.1665 | 39.9814 | 40.0925
CA-Gladstone Rockhampton | 6102_Boat Creek - Yarwun 66 kV | Loading (MVA) | 2.4408 | 2.3977 | 3.5451 | 4.6988 | 4.6671
CA-Gladstone Rockhampton | 6102_Boat Creek - Yarwun 66 kV | Loading (MW) | 2.4403 | 2.3971 | 3.5451 | 4.6984 | 4.6667
CA-Gladstone Rockhampton | 6102_Boat Creek - Yarwun 66 kV | Power Factor | 0.99981 | 0.99977 | 0.99996 | 0.9998 | 0.99979
CA-Gladstone Rockhampton | 6102_Boat Creek - Yarwun 66 kV | Rating (A) | 740 | 740 | 740 | 740 | 740
CA-Gladstone Rockhampton | 6102_Boat Creek - Yarwun 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6102_Boat Creek - Yarwun 66 kV | Min Voltage at Constrained Conductor | 67.1715 | 67.8612 | 67.8361 | 67.8416 | 67.1968
CA-Gladstone Rockhampton | 6102_Boat Creek - Yarwun 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Gladstone Rockhampton | 6103_Fisherman Landing-Boat Creek 66 kV | % of Rated A | 83.84% | 82.98% | 83% | 82.98% | 83.78%
CA-Gladstone Rockhampton | 6103_Fisherman Landing-Boat Creek 66 kV | Limiting Line Name | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1 | TR_LINE 22202_1
CA-Gladstone Rockhampton | 6103_Fisherman Landing-Boat Creek 66 kV | Loading (A) | 234.7607 | 232.3547 | 232.388 | 232.3478 | 234.5951
CA-Gladstone Rockhampton | 6103_Fisherman Landing-Boat Creek 66 kV | Loading (MVA) | 27.2031 | 27.2031 | 27.2031 | 27.2031 | 27.2031
CA-Gladstone Rockhampton | 6103_Fisherman Landing-Boat Creek 66 kV | Loading (MW) | 27.2031 | 27.2031 | 27.2031 | 27.2031 | 27.2031
CA-Gladstone Rockhampton | 6103_Fisherman Landing-Boat Creek 66 kV | Power Factor | 1 | 1 | 1 | 1 | 1
CA-Gladstone Rockhampton | 6103_Fisherman Landing-Boat Creek 66 kV | Rating (A) | 280 | 280 | 280 | 280 | 280
CA-Gladstone Rockhampton | 6103_Fisherman Landing-Boat Creek 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6103_Fisherman Landing-Boat Creek 66 kV | Min Voltage at Constrained Conductor | 66.8933 | 67.586 | 67.5763 | 67.588 | 66.9406
CA-Gladstone Rockhampton | 6103_Fisherman Landing-Boat Creek 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Gladstone Rockhampton | 6106_Shale Oil Tee - Shale Oil 66kV | % of Rated A | 1.176% | 1.164% | 1.164% | 1.164% | 1.175%
CA-Gladstone Rockhampton | 6106_Shale Oil Tee - Shale Oil 66kV | Limiting Line Name | TR_LINE 21402_1 | TR_LINE 21402_1 | TR_LINE 21402_1 | TR_LINE 21402_1 | TR_LINE 21402_1
CA-Gladstone Rockhampton | 6106_Shale Oil Tee - Shale Oil 66kV | Loading (A) | 5.1605 | 5.1079 | 5.109 | 5.1087 | 5.1577
CA-Gladstone Rockhampton | 6106_Shale Oil Tee - Shale Oil 66kV | Loading (MVA) | 0.6002 | 0.60019 | 0.60019 | 0.6002 | 0.6002
CA-Gladstone Rockhampton | 6106_Shale Oil Tee - Shale Oil 66kV | Loading (MW) | 0.60019 | 0.60018 | 0.60018 | 0.60019 | 0.60019
CA-Gladstone Rockhampton | 6106_Shale Oil Tee - Shale Oil 66kV | Power Factor | 0.99996 | 0.99996 | 0.99996 | 0.99996 | 0.99996
CA-Gladstone Rockhampton | 6106_Shale Oil Tee - Shale Oil 66kV | Rating (A) | 439 | 439 | 439 | 439 | 439
CA-Gladstone Rockhampton | 6106_Shale Oil Tee - Shale Oil 66kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6106_Shale Oil Tee - Shale Oil 66kV | Min Voltage at Constrained Conductor | 67.1505 | 67.8407 | 67.8252 | 67.8306 | 67.1858
CA-Gladstone Rockhampton | 6106_Shale Oil Tee - Shale Oil 66kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Gladstone Rockhampton | 6109_Gladstone North - Clinton 66 kV | % of Rated A | 17.18% | 15.28% | 12.92% | 10.66% | 8.14%
CA-Gladstone Rockhampton | 6109_Gladstone North - Clinton 66 kV | Limiting Line Name | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 60722_1 | TR_LINE 61921_1
CA-Gladstone Rockhampton | 6109_Gladstone North - Clinton 66 kV | Loading (A) | 62.3477 | 55.464 | 46.8831 | 38.71 | 29.5491
CA-Gladstone Rockhampton | 6109_Gladstone North - Clinton 66 kV | Loading (MVA) | 7.3864 | 6.5815 | 5.563 | 4.5794 | 3.5229
CA-Gladstone Rockhampton | 6109_Gladstone North - Clinton 66 kV | Loading (MW) | 6.7722 | 5.8728 | 4.7381 | 3.6055 | 3.3785
CA-Gladstone Rockhampton | 6109_Gladstone North - Clinton 66 kV | Power Factor | 0.91684 | 0.89233 | 0.85171 | 0.78732 | 0.95892
CA-Gladstone Rockhampton | 6109_Gladstone North - Clinton 66 kV | Rating (A) | 363 | 363 | 363 | 363 | 363
CA-Gladstone Rockhampton | 6109_Gladstone North - Clinton 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6109_Gladstone North - Clinton 66 kV | Min Voltage at Constrained Conductor | 68.3993 | 68.5095 | 68.5065 | 68.3012 | 68.832
CA-Gladstone Rockhampton | 6109_Gladstone North - Clinton 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Gladstone Rockhampton | 6196_Callide Mine 66 kV | % of Rated A | 57.58% | 57.55% | 57.55% | 57.57% | 57.59%
CA-Gladstone Rockhampton | 6196_Callide Mine 66 kV | Limiting Line Name | TR_LINE 22328_1 | TR_LINE 22328_1 | TR_LINE 22328_1 | TR_LINE 22328_1 | TR_LINE 22328_1
CA-Gladstone Rockhampton | 6196_Callide Mine 66 kV | Loading (A) | 77.1626 | 77.1212 | 77.1218 | 77.1447 | 77.1748
CA-Gladstone Rockhampton | 6196_Callide Mine 66 kV | Loading (MVA) | 9.2008 | 9.2008 | 9.2008 | 9.2008 | 9.2008
CA-Gladstone Rockhampton | 6196_Callide Mine 66 kV | Loading (MW) | 9.2008 | 9.2008 | 9.2008 | 9.2008 | 9.2008
CA-Gladstone Rockhampton | 6196_Callide Mine 66 kV | Power Factor | 1 | 1 | 1 | 1 | 1
CA-Gladstone Rockhampton | 6196_Callide Mine 66 kV | Rating (A) | 134 | 134 | 134 | 134 | 134
CA-Gladstone Rockhampton | 6196_Callide Mine 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6196_Callide Mine 66 kV | Min Voltage at Constrained Conductor | 68.8367 | 68.8737 | 68.8731 | 68.8528 | 68.8259
CA-Gladstone Rockhampton | 6196_Callide Mine 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Gladstone Rockhampton | 6298_Tanby - Yeppoon 66 kV | % of Rated A | 2.961% | 2.319% | 1.793% | 2.721% | 4.068%
CA-Gladstone Rockhampton | 6298_Tanby - Yeppoon 66 kV | Limiting Line Name | TR_LINE 112499_1 | TR_LINE 112499_1 | TR_LINE 155369_1 | TR_LINE 112499_1 | TR_LINE 112499_1
CA-Gladstone Rockhampton | 6298_Tanby - Yeppoon 66 kV | Loading (A) | 11.193 | 8.7665 | 7.8699 | 10.2872 | 15.3768
CA-Gladstone Rockhampton | 6298_Tanby - Yeppoon 66 kV | Loading (MVA) | 1.3618 | 1.0719 | 0.96533 | 1.2679 | 1.9016
CA-Gladstone Rockhampton | 6298_Tanby - Yeppoon 66 kV | Loading (MW) | 0.92489 | 0.24823 | 0.38283 | 1.022 | 1.7431
CA-Gladstone Rockhampton | 6298_Tanby - Yeppoon 66 kV | Power Factor | 0.67915 | 0.23158 | 0.39658 | 0.80605 | 0.91661
CA-Gladstone Rockhampton | 6298_Tanby - Yeppoon 66 kV | Rating (A) | 378 | 378 | 439 | 378 | 378
CA-Gladstone Rockhampton | 6298_Tanby - Yeppoon 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6298_Tanby - Yeppoon 66 kV | Min Voltage at Constrained Conductor | 70.2448 | 70.5927 | 70.8184 | 71.1577 | 71.3998
CA-Gladstone Rockhampton | 6298_Tanby - Yeppoon 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Gladstone Rockhampton | 6310_Lakes Creek - Berserker 66 kV | % of Rated A | 6.653% | 6.9% | 9.188% | 10.04% | 11.09%
CA-Gladstone Rockhampton | 6310_Lakes Creek - Berserker 66 kV | Limiting Line Name | TR_CABLE 51_1 | TR_CABLE 51_1 | TR_CABLE 51_1 | TR_CABLE 51_1 | TR_CABLE 51_1
CA-Gladstone Rockhampton | 6310_Lakes Creek - Berserker 66 kV | Loading (A) | 24.7481 | 25.6668 | 34.1785 | 37.3316 | 41.2419
CA-Gladstone Rockhampton | 6310_Lakes Creek - Berserker 66 kV | Loading (MVA) | 2.9884 | 3.104 | 4.1431 | 4.5303 | 5.0073
CA-Gladstone Rockhampton | 6310_Lakes Creek - Berserker 66 kV | Loading (MW) | 1.8244 | 2.0449 | 2.3083 | 2.9709 | 3.7015
CA-Gladstone Rockhampton | 6310_Lakes Creek - Berserker 66 kV | Power Factor | 0.61042 | 0.65871 | 0.55709 | 0.65575 | 0.73917
CA-Gladstone Rockhampton | 6310_Lakes Creek - Berserker 66 kV | Rating (A) | 372 | 372 | 372 | 372 | 372
CA-Gladstone Rockhampton | 6310_Lakes Creek - Berserker 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6310_Lakes Creek - Berserker 66 kV | Min Voltage at Constrained Conductor | 69.7169 | 69.8226 | 69.9855 | 70.0626 | 70.0981
CA-Gladstone Rockhampton | 6310_Lakes Creek - Berserker 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Gladstone Rockhampton | 7195_Gladstone PS - Boat Creek 132 kV | % of Rated A | 1.167% | 1.116% | 1.052% | 0.9908% | 0.9622%
CA-Gladstone Rockhampton | 7195_Gladstone PS - Boat Creek 132 kV | Limiting Line Name | Link_7195 CALLIOPE RIVER_Term4 | Link_7195 CALLIOPE RIVER_Term4 | Link_7195 CALLIOPE RIVER_Term4 | Link_7195 CALLIOPE RIVER_Term4 | Link_7195 CALLIOPE RIVER_Term4
CA-Gladstone Rockhampton | 7195_Gladstone PS - Boat Creek 132 kV | Loading (A) | 58.3742 | 55.7838 | 52.5953 | 49.5409 | 48.1098
CA-Gladstone Rockhampton | 7195_Gladstone PS - Boat Creek 132 kV | Loading (MVA) | 14.1514 | 13.5447 | 12.77 | 11.9926 | 11.6316
CA-Gladstone Rockhampton | 7195_Gladstone PS - Boat Creek 132 kV | Loading (MW) | 13.9561 | 13.3357 | 12.5533 | 11.7725 | 11.6272
CA-Gladstone Rockhampton | 7195_Gladstone PS - Boat Creek 132 kV | Power Factor | 0.9862 | 0.98457 | 0.98303 | 0.98164 | 0.99962
CA-Gladstone Rockhampton | 7195_Gladstone PS - Boat Creek 132 kV | Rating (A) | 5000 | 5000 | 5000 | 5000 | 5000
CA-Gladstone Rockhampton | 7195_Gladstone PS - Boat Creek 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 7195_Gladstone PS - Boat Creek 132 kV | Min Voltage at Constrained Conductor | 139.9644 | 140.1842 | 140.179 | 139.7623 | 139.5874
CA-Gladstone Rockhampton | 7195_Gladstone PS - Boat Creek 132 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Gladstone Rockhampton | 7290_Boat Creek - Yarwun 132 kV | % of Rated A | 10.52% | 10.54% | 10.81% | 11.08% | 11.04%
CA-Gladstone Rockhampton | 7290_Boat Creek - Yarwun 132 kV | Limiting Line Name | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1 | TR_LINE 71520_1
CA-Gladstone Rockhampton | 7290_Boat Creek - Yarwun 132 kV | Loading (A) | 93.5652 | 93.6667 | 96.0867 | 98.488 | 98.1536
CA-Gladstone Rockhampton | 7290_Boat Creek - Yarwun 132 kV | Loading (MVA) | 22.3423 | 22.3202 | 22.895 | 23.4729 | 23.4573
CA-Gladstone Rockhampton | 7290_Boat Creek - Yarwun 132 kV | Loading (MW) | 22.3326 | 22.3107 | 22.8842 | 23.4604 | 23.4447
CA-Gladstone Rockhampton | 7290_Boat Creek - Yarwun 132 kV | Power Factor | 0.99955 | 0.99956 | 0.99951 | 0.99945 | 0.99945
CA-Gladstone Rockhampton | 7290_Boat Creek - Yarwun 132 kV | Rating (A) | 889 | 889 | 889 | 889 | 889
CA-Gladstone Rockhampton | 7290_Boat Creek - Yarwun 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 7290_Boat Creek - Yarwun 132 kV | Min Voltage at Constrained Conductor | 137.863 | 137.5775 | 137.5661 | 137.5995 | 137.9768
CA-Gladstone Rockhampton | 7290_Boat Creek - Yarwun 132 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Gladstone Rockhampton | 7291_Boat Creek - Yarwun 132 kV | % of Rated A | 10.58% | 10.59% | 10.86% | 11.13% | 11.1%
CA-Gladstone Rockhampton | 7291_Boat Creek - Yarwun 132 kV | Limiting Line Name | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1 | TR_LINE 71529_1
CA-Gladstone Rockhampton | 7291_Boat Creek - Yarwun 132 kV | Loading (A) | 94.0239 | 94.1168 | 96.5485 | 98.9614 | 98.6348
CA-Gladstone Rockhampton | 7291_Boat Creek - Yarwun 132 kV | Loading (MVA) | 22.452 | 22.4276 | 23.0052 | 23.5858 | 23.5725
CA-Gladstone Rockhampton | 7291_Boat Creek - Yarwun 132 kV | Loading (MW) | 22.442 | 22.4178 | 22.9941 | 23.573 | 23.5596
CA-Gladstone Rockhampton | 7291_Boat Creek - Yarwun 132 kV | Power Factor | 0.99955 | 0.99955 | 0.99951 | 0.99945 | 0.99944
CA-Gladstone Rockhampton | 7291_Boat Creek - Yarwun 132 kV | Rating (A) | 889 | 889 | 889 | 889 | 889
CA-Gladstone Rockhampton | 7291_Boat Creek - Yarwun 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 7291_Boat Creek - Yarwun 132 kV | Min Voltage at Constrained Conductor | 137.8643 | 137.5788 | 137.5674 | 137.6009 | 137.9782
CA-Gladstone Rockhampton | 7291_Boat Creek - Yarwun 132 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Gladstone Rockhampton | 7414_Gladstone North - Wiggins Is 132 kV | % of Rated A | 2.563% | 2.559% | 2.559% | 2.567% | 2.57%
CA-Gladstone Rockhampton | 7414_Gladstone North - Wiggins Is 132 kV | Limiting Line Name | TR_LINE 193931_1 | TR_LINE 193931_1 | TR_LINE 193931_1 | TR_LINE 193931_1 | TR_LINE 193931_1
CA-Gladstone Rockhampton | 7414_Gladstone North - Wiggins Is 132 kV | Loading (A) | 20.6579 | 20.6254 | 20.6262 | 20.6878 | 20.7137
CA-Gladstone Rockhampton | 7414_Gladstone North - Wiggins Is 132 kV | Loading (MVA) | 5.0076 | 5.0076 | 5.0076 | 5.0076 | 5.0076
CA-Gladstone Rockhampton | 7414_Gladstone North - Wiggins Is 132 kV | Loading (MW) | 5.0076 | 5.0076 | 5.0076 | 5.0076 | 5.0076
CA-Gladstone Rockhampton | 7414_Gladstone North - Wiggins Is 132 kV | Power Factor | 1 | 1 | 1 | 1 | 1
CA-Gladstone Rockhampton | 7414_Gladstone North - Wiggins Is 132 kV | Rating (A) | 806 | 806 | 806 | 806 | 806
CA-Gladstone Rockhampton | 7414_Gladstone North - Wiggins Is 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 7414_Gladstone North - Wiggins Is 132 kV | Min Voltage at Constrained Conductor | 139.9536 | 140.1735 | 140.1683 | 139.7514 | 139.5765
CA-Gladstone Rockhampton | 7414_Gladstone North - Wiggins Is 132 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Gladstone Rockhampton | 7415_Gladstone North - Wiggins Is 132 kV | % of Rated A | 2.326% | 2.322% | 2.322% | 2.329% | 2.332%
CA-Gladstone Rockhampton | 7415_Gladstone North - Wiggins Is 132 kV | Limiting Line Name | TR_LINE 60739_1 | TR_LINE 60739_1 | TR_LINE 60739_1 | TR_LINE 60739_1 | TR_LINE 60739_1
CA-Gladstone Rockhampton | 7415_Gladstone North - Wiggins Is 132 kV | Loading (A) | 20.6766 | 20.6447 | 20.6454 | 20.706 | 20.7316
CA-Gladstone Rockhampton | 7415_Gladstone North - Wiggins Is 132 kV | Loading (MVA) | 5.0125 | 5.0127 | 5.0127 | 5.0124 | 5.0123
CA-Gladstone Rockhampton | 7415_Gladstone North - Wiggins Is 132 kV | Loading (MW) | 4.9968 | 4.9967 | 4.9967 | 4.9968 | 4.9968
CA-Gladstone Rockhampton | 7415_Gladstone North - Wiggins Is 132 kV | Power Factor | 0.99685 | 0.99683 | 0.99683 | 0.99688 | 0.9969
CA-Gladstone Rockhampton | 7415_Gladstone North - Wiggins Is 132 kV | Rating (A) | 889 | 889 | 889 | 889 | 889
CA-Gladstone Rockhampton | 7415_Gladstone North - Wiggins Is 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 7415_Gladstone North - Wiggins Is 132 kV | Min Voltage at Constrained Conductor | 139.9641 | 140.184 | 140.1788 | 139.762 | 139.5871
CA-Gladstone Rockhampton | 7415_Gladstone North - Wiggins Is 132 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Gladstone Rockhampton | AW113_Awoonga Rurals 11 kV | % of Rated A | 6.019% | 6.016% | 6.014% | 6.032% | 6.016%
CA-Gladstone Rockhampton | AW113_Awoonga Rurals 11 kV | Limiting Line Name | HV_LINE 235473_1 | HV_LINE 235473_1 | HV_LINE 235473_1 | HV_LINE 235473_1 | HV_LINE 235473_1
CA-Gladstone Rockhampton | AW113_Awoonga Rurals 11 kV | Loading (A) | 12.7606 | 12.7531 | 12.75 | 12.7879 | 12.7529
CA-Gladstone Rockhampton | AW113_Awoonga Rurals 11 kV | Loading (MVA) | 0.24836 | 0.24836 | 0.24835 | 0.24839 | 0.24836
CA-Gladstone Rockhampton | AW113_Awoonga Rurals 11 kV | Loading (MW) | 0.20453 | 0.20453 | 0.20452 | 0.20453 | 0.20453
CA-Gladstone Rockhampton | AW113_Awoonga Rurals 11 kV | Power Factor | 0.82332 | 0.82334 | 0.82335 | 0.82325 | 0.82334
CA-Gladstone Rockhampton | AW113_Awoonga Rurals 11 kV | Rating (A) | 212 | 212 | 212 | 212 | 212
CA-Gladstone Rockhampton | AW113_Awoonga Rurals 11 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | AW113_Awoonga Rurals 11 kV | Min Voltage at Constrained Conductor | 11.2372 | 11.2435 | 11.2461 | 11.2144 | 11.2436
CA-Gladstone Rockhampton | AW113_Awoonga Rurals 11 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Gladstone Rockhampton | CN101_Base Hospital No.1 11kV | % of Rated A | 0.1947% | 0.1927% | 0.1931% | 0.1932% | 0.1933%
CA-Gladstone Rockhampton | CN101_Base Hospital No.1 11kV | Limiting Line Name | HV_CABLE 393680_1 | HV_CABLE 393680_1 | HV_CABLE 393680_1 | HV_CABLE 393680_1 | HV_CABLE 393680_1
CA-Gladstone Rockhampton | CN101_Base Hospital No.1 11kV | Loading (A) | 0.77894 | 0.77092 | 0.77238 | 0.77297 | 0.77309
CA-Gladstone Rockhampton | CN101_Base Hospital No.1 11kV | Loading (MVA) | 0.014688 | 0.014387 | 0.014441 | 0.014463 | 0.014468
CA-Gladstone Rockhampton | CN101_Base Hospital No.1 11kV | Loading (MW) | 0.0041167 | 0.0040324 | 0.0040476 | 0.0040538 | 0.0040551
CA-Gladstone Rockhampton | CN101_Base Hospital No.1 11kV | Power Factor | 0.27966 | 0.27966 | 0.27966 | 0.27966 | 0.27966
CA-Gladstone Rockhampton | CN101_Base Hospital No.1 11kV | Rating (A) | 400 | 400 | 400 | 400 | 400
CA-Gladstone Rockhampton | CN101_Base Hospital No.1 11kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | CN101_Base Hospital No.1 11kV | Min Voltage at Constrained Conductor | 10.8864 | 10.7744 | 10.7947 | 10.803 | 10.8047
CA-Gladstone Rockhampton | CN101_Base Hospital No.1 11kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Gladstone Rockhampton | CN109_Base Hospital No.2 11kV | % of Rated A | 0.7072% | 0.714% | 0.7128% | 0.7122% | 0.7121%
CA-Gladstone Rockhampton | CN109_Base Hospital No.2 11kV | Limiting Line Name | HV_CABLE 536964_1 | HV_CABLE 536964_1 | HV_CABLE 536964_1 | HV_CABLE 536964_1 | HV_CABLE 536964_1
CA-Gladstone Rockhampton | CN109_Base Hospital No.2 11kV | Loading (A) | 3.4228 | 3.4557 | 3.4497 | 3.4473 | 3.4468
CA-Gladstone Rockhampton | CN109_Base Hospital No.2 11kV | Loading (MVA) | 0.06454 | 0.064489 | 0.064498 | 0.064502 | 0.064503
CA-Gladstone Rockhampton | CN109_Base Hospital No.2 11kV | Loading (MW) | 0.058671 | 0.058656 | 0.058658 | 0.05866 | 0.05866
CA-Gladstone Rockhampton | CN109_Base Hospital No.2 11kV | Power Factor | 0.90661 | 0.90714 | 0.90704 | 0.907 | 0.90699
CA-Gladstone Rockhampton | CN109_Base Hospital No.2 11kV | Rating (A) | 484 | 484 | 484 | 484 | 484
CA-Gladstone Rockhampton | CN109_Base Hospital No.2 11kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | CN109_Base Hospital No.2 11kV | Min Voltage at Constrained Conductor | 10.8863 | 10.7742 | 10.7946 | 10.8029 | 10.8045
CA-Gladstone Rockhampton | CN109_Base Hospital No.2 11kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Gladstone Rockhampton | 6096_Egan's Hill - Lakes Creek 66 kV | % of Rated A | 11.63% | 10.2% | 8.224% | 10.66% | 13.6%
CA-Gladstone Rockhampton | 6096_Egan's Hill - Lakes Creek 66 kV | Limiting Line Name | TR_LINE 19756_1 | TR_LINE 19756_1 | TR_LINE 19756_1 | TR_LINE 19756_1 | TR_LINE 19756_1
CA-Gladstone Rockhampton | 6096_Egan's Hill - Lakes Creek 66 kV | Loading (A) | 37.3343 | 32.7566 | 26.3987 | 34.2244 | 43.6564
CA-Gladstone Rockhampton | 6096_Egan's Hill - Lakes Creek 66 kV | Loading (MVA) | 4.5082 | 3.9615 | 3.2 | 4.1532 | 5.3005
CA-Gladstone Rockhampton | 6096_Egan's Hill - Lakes Creek 66 kV | Loading (MW) | 2.0102 | 0.13588 | 2.0082 | 3.3535 | 4.7308
CA-Gladstone Rockhampton | 6096_Egan's Hill - Lakes Creek 66 kV | Power Factor | 0.44589 | 0.034068 | 0.62726 | 0.80722 | 0.89236
CA-Gladstone Rockhampton | 6096_Egan's Hill - Lakes Creek 66 kV | Rating (A) | 321 | 321 | 321 | 321 | 321
CA-Gladstone Rockhampton | 6096_Egan's Hill - Lakes Creek 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Gladstone Rockhampton | 6096_Egan's Hill - Lakes Creek 66 kV | Min Voltage at Constrained Conductor | 69.7169 | 69.8224 | 69.9853 | 70.0624 | 70.0979
CA-Gladstone Rockhampton | 6096_Egan's Hill - Lakes Creek 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
CA-Moura | 6026_Moura - Theodore 66 kV | % of Rated A | 5.211% | 5.096% | 5.006% | 4.934% | 4.878%
CA-Moura | 6026_Moura - Theodore 66 kV | Limiting Line Name | TR_LINE 59683_1 | TR_LINE 59683_1 | TR_LINE 59683_1 | TR_LINE 59683_1 | TR_LINE 59683_1
CA-Moura | 6026_Moura - Theodore 66 kV | Loading (A) | 37.9916 | 37.1513 | 36.4963 | 35.9691 | 35.5638
CA-Moura | 6026_Moura - Theodore 66 kV | Loading (MVA) | 4.5526 | 4.452 | 4.3736 | 4.3104 | 4.2619
CA-Moura | 6026_Moura - Theodore 66 kV | Loading (MW) | 4.4854 | 4.3821 | 4.3012 | 4.2361 | 4.1859
CA-Moura | 6026_Moura - Theodore 66 kV | Power Factor | 0.98524 | 0.9843 | 0.98346 | 0.98275 | 0.98218
CA-Moura | 6026_Moura - Theodore 66 kV | Rating (A) | 729 | 729 | 729 | 729 | 729
CA-Moura | 6026_Moura - Theodore 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
CA-Moura | 6026_Moura - Theodore 66 kV | Min Voltage at Constrained Conductor | 69.1839 | 69.1861 | 69.187 | 69.1876 | 69.1878
CA-Moura | 6026_Moura - Theodore 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
FN-Cairns Area | 7206 Woree-Cairns Terminal-Cairns City | % of Rated A | 9.682% | 9.438% | 9.214% | 8.992% | 8.781%
FN-Cairns Area | 7206 Woree-Cairns Terminal-Cairns City | Limiting Line Name | TR_CABLE 11_1 | TR_CABLE 11_1 | TR_CABLE 11_1 | TR_CABLE 11_1 | TR_CABLE 11_1
FN-Cairns Area | 7206 Woree-Cairns Terminal-Cairns City | Loading (A) | 46.3746 | 45.2059 | 44.1349 | 43.0693 | 42.0607
FN-Cairns Area | 7206 Woree-Cairns Terminal-Cairns City | Loading (MVA) | 12.341 | 12.0349 | 11.7519 | 11.4678 | 11.1961
FN-Cairns Area | 7206 Woree-Cairns Terminal-Cairns City | Loading (MW) | 12.3278 | 12.0199 | 11.7352 | 11.4494 | 11.176
FN-Cairns Area | 7206 Woree-Cairns Terminal-Cairns City | Power Factor | 0.99893 | 0.99875 | 0.99858 | 0.99839 | 0.9982
FN-Cairns Area | 7206 Woree-Cairns Terminal-Cairns City | Rating (A) | 479 | 479 | 479 | 479 | 479
FN-Cairns Area | 7206 Woree-Cairns Terminal-Cairns City | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Cairns Area | 7206 Woree-Cairns Terminal-Cairns City | Min Voltage at Constrained Conductor | 153.6409 | 153.7033 | 153.731 | 153.7261 | 153.6838
FN-Cairns Area | 7206 Woree-Cairns Terminal-Cairns City | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
FN-Cairns Area | 7227 Woree-Cairns Terminal-Cairns City | % of Rated A | 11.1% | 10.83% | 10.58% | 10.33% | 10.1%
FN-Cairns Area | 7227 Woree-Cairns Terminal-Cairns City | Limiting Line Name | TR_LINE 176513_1 | TR_LINE 176513_1 | TR_LINE 176513_1 | TR_LINE 176513_1 | TR_LINE 176513_1
FN-Cairns Area | 7227 Woree-Cairns Terminal-Cairns City | Loading (A) | 46.3931 | 45.2579 | 44.2181 | 43.1826 | 42.205
FN-Cairns Area | 7227 Woree-Cairns Terminal-Cairns City | Loading (MVA) | 12.3493 | 12.0521 | 11.7773 | 11.5012 | 11.2377
FN-Cairns Area | 7227 Woree-Cairns Terminal-Cairns City | Loading (MW) | 12.3252 | 12.0257 | 11.7487 | 11.4703 | 11.2047
FN-Cairns Area | 7227 Woree-Cairns Terminal-Cairns City | Power Factor | 0.99804 | 0.99781 | 0.99757 | 0.99732 | 0.99706
FN-Cairns Area | 7227 Woree-Cairns Terminal-Cairns City | Rating (A) | 418 | 418 | 418 | 418 | 418
FN-Cairns Area | 7227 Woree-Cairns Terminal-Cairns City | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Cairns Area | 7227 Woree-Cairns Terminal-Cairns City | Min Voltage at Constrained Conductor | 153.6825 | 153.7454 | 153.7734 | 153.7688 | 153.7267
FN-Cairns Area | 7227 Woree-Cairns Terminal-Cairns City | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
FN-Cairns Area | 7332_Cairns North 132 kV | % of Rated A | 8.644% | 8.382% | 8.378% | 8.604% | 9.071%
FN-Cairns Area | 7332_Cairns North 132 kV | Limiting Line Name | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2 | TR_LINE 99879_2
FN-Cairns Area | 7332_Cairns North 132 kV | Loading (A) | 40.886 | 39.6449 | 39.6297 | 40.6947 | 42.9051
FN-Cairns Area | 7332_Cairns North 132 kV | Loading (MVA) | 10.8846 | 10.5583 | 10.5561 | 10.8393 | 11.4247
FN-Cairns Area | 7332_Cairns North 132 kV | Loading (MW) | 2.9298 | 0.9678 | 0.87067 | 2.6738 | 4.5869
FN-Cairns Area | 7332_Cairns North 132 kV | Power Factor | 0.26917 | 0.091662 | 0.082477 | 0.24667 | 0.40149
FN-Cairns Area | 7332_Cairns North 132 kV | Rating (A) | 473 | 473 | 473 | 473 | 473
FN-Cairns Area | 7332_Cairns North 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Cairns Area | 7332_Cairns North 132 kV | Min Voltage at Constrained Conductor | 153.7012 | 153.7616 | 153.7873 | 153.7806 | 153.7364
FN-Cairns Area | 7332_Cairns North 132 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
FN-Cairns Area | 7333_Cairns North 132 kV | % of Rated A | 8.291% | 8.043% | 8.04% | 8.253% | 8.695%
FN-Cairns Area | 7333_Cairns North 132 kV | Limiting Line Name | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2 | TR_LINE 99845_2
FN-Cairns Area | 7333_Cairns North 132 kV | Loading (A) | 39.2173 | 38.0418 | 38.0272 | 39.0354 | 41.1294
FN-Cairns Area | 7333_Cairns North 132 kV | Loading (MVA) | 10.4404 | 10.1314 | 10.1292 | 10.3973 | 10.9519
FN-Cairns Area | 7333_Cairns North 132 kV | Loading (MW) | 2.8049 | 0.93435 | 0.8184 | 2.5375 | 4.3614
FN-Cairns Area | 7333_Cairns North 132 kV | Power Factor | 0.26866 | 0.092223 | 0.080792 | 0.24405 | 0.39823
FN-Cairns Area | 7333_Cairns North 132 kV | Rating (A) | 473 | 473 | 473 | 473 | 473
FN-Cairns Area | 7333_Cairns North 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Cairns Area | 7333_Cairns North 132 kV | Min Voltage at Constrained Conductor | 153.7012 | 153.7616 | 153.7873 | 153.7806 | 153.7364
FN-Cairns Area | 7333_Cairns North 132 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
FN-Cairns Area | EDMO-2GO1_Gordonvale 1 22kV | % of Rated A | 34.06% | 34.08% | 34.08% | 34.08% | 34.06%
FN-Cairns Area | EDMO-2GO1_Gordonvale 1 22kV | Limiting Line Name | HV_LINE 1182348_1 | HV_LINE 1182348_1 | HV_LINE 1182348_1 | HV_LINE 1182348_1 | HV_LINE 1182348_1
FN-Cairns Area | EDMO-2GO1_Gordonvale 1 22kV | Loading (A) | 26.5682 | 26.579 | 26.5824 | 26.5791 | 26.5679
FN-Cairns Area | EDMO-2GO1_Gordonvale 1 22kV | Loading (MVA) | 1.1555 | 1.1567 | 1.1571 | 1.1567 | 1.1555
FN-Cairns Area | EDMO-2GO1_Gordonvale 1 22kV | Loading (MW) | 0.29336 | 0.29325 | 0.29321 | 0.29325 | 0.29336
FN-Cairns Area | EDMO-2GO1_Gordonvale 1 22kV | Power Factor | 0.25337 | 0.25301 | 0.2529 | 0.25301 | 0.25337
FN-Cairns Area | EDMO-2GO1_Gordonvale 1 22kV | Rating (A) | 78 | 78 | 78 | 78 | 78
FN-Cairns Area | EDMO-2GO1_Gordonvale 1 22kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Cairns Area | EDMO-2GO1_Gordonvale 1 22kV | Min Voltage at Constrained Conductor | 25.1079 | 25.1234 | 25.1283 | 25.1236 | 25.1076
FN-Cairns Area | EDMO-2GO1_Gordonvale 1 22kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
FN-Cairns Area | EDMO-2GO2_Gordonvale 2 22kV | % of Rated A | 25.13% | 25.15% | 25.15% | 25.15% | 25.13%
FN-Cairns Area | EDMO-2GO2_Gordonvale 2 22kV | Limiting Line Name | HV_LINE 650000_1 | HV_LINE 650000_1 | HV_LINE 650000_1 | HV_LINE 650000_1 | HV_LINE 650000_1
FN-Cairns Area | EDMO-2GO2_Gordonvale 2 22kV | Loading (A) | 19.6011 | 19.614 | 19.6181 | 19.6142 | 19.6008
FN-Cairns Area | EDMO-2GO2_Gordonvale 2 22kV | Loading (MVA) | 0.8527 | 0.85379 | 0.85413 | 0.8538 | 0.85268
FN-Cairns Area | EDMO-2GO2_Gordonvale 2 22kV | Loading (MW) | 0.21437 | 0.21429 | 0.21427 | 0.21429 | 0.21437
FN-Cairns Area | EDMO-2GO2_Gordonvale 2 22kV | Power Factor | 0.24948 | 0.24907 | 0.24894 | 0.24907 | 0.24949
FN-Cairns Area | EDMO-2GO2_Gordonvale 2 22kV | Rating (A) | 78 | 78 | 78 | 78 | 78
FN-Cairns Area | EDMO-2GO2_Gordonvale 2 22kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Cairns Area | EDMO-2GO2_Gordonvale 2 22kV | Min Voltage at Constrained Conductor | 25.1101 | 25.1255 | 25.1304 | 25.1257 | 25.1097
FN-Cairns Area | EDMO-2GO2_Gordonvale 2 22kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
FN-Cairns Area | EDMO-2GO3_Gordonvale 3 22kV | % of Rated A | 30.12% | 30.14% | 30.14% | 30.14% | 30.12%
FN-Cairns Area | EDMO-2GO3_Gordonvale 3 22kV | Limiting Line Name | HV_LINE 58939_1 | HV_LINE 58939_1 | HV_LINE 58939_1 | HV_LINE 58939_1 | HV_LINE 58939_1
FN-Cairns Area | EDMO-2GO3_Gordonvale 3 22kV | Loading (A) | 39.7553 | 39.781 | 39.7892 | 39.7813 | 39.7547
FN-Cairns Area | EDMO-2GO3_Gordonvale 3 22kV | Loading (MVA) | 1.7327 | 1.7349 | 1.7356 | 1.7349 | 1.7327
FN-Cairns Area | EDMO-2GO3_Gordonvale 3 22kV | Loading (MW) | 0.63799 | 0.63798 | 0.63798 | 0.63798 | 0.63799
FN-Cairns Area | EDMO-2GO3_Gordonvale 3 22kV | Power Factor | 0.36808 | 0.36762 | 0.36747 | 0.36761 | 0.36809
FN-Cairns Area | EDMO-2GO3_Gordonvale 3 22kV | Rating (A) | 132 | 132 | 132 | 132 | 132
FN-Cairns Area | EDMO-2GO3_Gordonvale 3 22kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Cairns Area | EDMO-2GO3_Gordonvale 3 22kV | Min Voltage at Constrained Conductor | 25.1634 | 25.1788 | 25.1837 | 25.179 | 25.163
FN-Cairns Area | EDMO-2GO3_Gordonvale 3 22kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
FN-Cairns Area | GORD-2RIV_Riverstone Rd 22kV | % of Rated A | 4.355% | 4.352% | 4.351% | 4.352% | 4.355%
FN-Cairns Area | GORD-2RIV_Riverstone Rd 22kV | Limiting Line Name | HV_LINE 53928_1 | HV_LINE 53928_1 | HV_LINE 53928_1 | HV_LINE 53928_1 | HV_LINE 53928_1
FN-Cairns Area | GORD-2RIV_Riverstone Rd 22kV | Loading (A) | 5.7482 | 5.7446 | 5.7435 | 5.7446 | 5.7483
FN-Cairns Area | GORD-2RIV_Riverstone Rd 22kV | Loading (MVA) | 0.25069 | 0.25069 | 0.25069 | 0.25069 | 0.25069
FN-Cairns Area | GORD-2RIV_Riverstone Rd 22kV | Loading (MW) | 0.21538 | 0.21538 | 0.21538 | 0.21538 | 0.21538
FN-Cairns Area | GORD-2RIV_Riverstone Rd 22kV | Power Factor | 0.85913 | 0.85914 | 0.85914 | 0.85914 | 0.85913
FN-Cairns Area | GORD-2RIV_Riverstone Rd 22kV | Rating (A) | 132 | 132 | 132 | 132 | 132
FN-Cairns Area | GORD-2RIV_Riverstone Rd 22kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Cairns Area | GORD-2RIV_Riverstone Rd 22kV | Min Voltage at Constrained Conductor | 25.1797 | 25.1952 | 25.2001 | 25.1953 | 25.1793
FN-Cairns Area | GORD-2RIV_Riverstone Rd 22kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
FN-Cairns Area | KAME-2CO1 Cook No 1 22kV | % of Rated A | 39.09% | 39.12% | 39.13% | 39.13% | 39.14%
FN-Cairns Area | KAME-2CO1 Cook No 1 22kV | Limiting Line Name | HV_CABLE_12128692_1 | HV_CABLE_12128692_1 | HV_CABLE_12128692_1 | HV_CABLE_12128692_1 | HV_CABLE_12128692_1
FN-Cairns Area | KAME-2CO1 Cook No 1 22kV | Loading (A) | 52.7766 | 52.8179 | 52.8266 | 52.832 | 52.8334
FN-Cairns Area | KAME-2CO1 Cook No 1 22kV | Loading (MVA) | 2.2673 | 2.272 | 2.2745 | 2.276 | 2.2764
FN-Cairns Area | KAME-2CO1 Cook No 1 22kV | Loading (MW) | 0.90679 | 0.9066 | 0.90651 | 0.90646 | 0.90645
FN-Cairns Area | KAME-2CO1 Cook No 1 22kV | Power Factor | 0.39992 | 0.39901 | 0.39853 | 0.39825 | 0.39818
FN-Cairns Area | KAME-2CO1 Cook No 1 22kV | Rating (A) | 135 | 135 | 135 | 135 | 135
FN-Cairns Area | KAME-2CO1 Cook No 1 22kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Cairns Area | KAME-2CO1 Cook No 1 22kV | Min Voltage at Constrained Conductor | 24.8029 | 24.8354 | 24.8582 | 24.8721 | 24.8757
FN-Cairns Area | KAME-2CO1 Cook No 1 22kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
FN-Cairns Area | KAME-2CO2 Cook No 2 22kV | % of Rated A | 15.36% | 15.39% | 15.4% | 15.41% | 15.41%
FN-Cairns Area | KAME-2CO2 Cook No 2 22kV | Limiting Line Name | HV_CABLE_12173517_1 | HV_CABLE_12173517_1 | HV_CABLE_12173517_1 | HV_CABLE_12173517_1 | HV_CABLE_12173517_1
FN-Cairns Area | KAME-2CO2 Cook No 2 22kV | Loading (A) | 20.7293 | 20.7734 | 20.7928 | 20.8046 | 20.8076
FN-Cairns Area | KAME-2CO2 Cook No 2 22kV | Loading (MVA) | 0.89902 | 0.90208 | 0.90374 | 0.90474 | 0.905
FN-Cairns Area | KAME-2CO2 Cook No 2 22kV | Loading (MW) | 0.46971 | 0.46967 | 0.46964 | 0.46962 | 0.46962
FN-Cairns Area | KAME-2CO2 Cook No 2 22kV | Power Factor | 0.52247 | 0.52065 | 0.51967 | 0.51907 | 0.51891
FN-Cairns Area | KAME-2CO2 Cook No 2 22kV | Rating (A) | 135 | 135 | 135 | 135 | 135
FN-Cairns Area | KAME-2CO2 Cook No 2 22kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Cairns Area | KAME-2CO2 Cook No 2 22kV | Min Voltage at Constrained Conductor | 25.0366 | 25.0686 | 25.0912 | 25.1049 | 25.1085
FN-Cairns Area | KAME-2CO2 Cook No 2 22kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
FN-Cairns Area | KAME-2CO3 Cook No 3 22kV | % of Rated A | 15.37% | 15.4% | 15.42% | 15.43% | 15.43%
FN-Cairns Area | KAME-2CO3 Cook No 3 22kV | Limiting Line Name | HV_CABLE_12128762_1 | HV_CABLE_12128762_1 | HV_CABLE_12128762_1 | HV_CABLE_12128762_1 | HV_CABLE_12128762_1
FN-Cairns Area | KAME-2CO3 Cook No 3 22kV | Loading (A) | 20.7492 | 20.7929 | 20.8122 | 20.8239 | 20.8269
FN-Cairns Area | KAME-2CO3 Cook No 3 22kV | Loading (MVA) | 0.89988 | 0.90293 | 0.90458 | 0.90558 | 0.90584
FN-Cairns Area | KAME-2CO3 Cook No 3 22kV | Loading (MW) | 0.49168 | 0.49173 | 0.49175 | 0.49176 | 0.49177
FN-Cairns Area | KAME-2CO3 Cook No 3 22kV | Power Factor | 0.54639 | 0.5446 | 0.54363 | 0.54304 | 0.54288
FN-Cairns Area | KAME-2CO3 Cook No 3 22kV | Rating (A) | 135 | 135 | 135 | 135 | 135
FN-Cairns Area | KAME-2CO3 Cook No 3 22kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Cairns Area | KAME-2CO3 Cook No 3 22kV | Min Voltage at Constrained Conductor | 25.0368 | 25.0688 | 25.0914 | 25.1051 | 25.1086
FN-Cairns Area | KAME-2CO3 Cook No 3 22kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
FN-Gulf | 3CRO_Croydon 66 kV | % of Rated A | 4.293% | 4.053% | 3.877% | 3.739% | 3.628%
FN-Gulf | 3CRO_Croydon 66 kV | Limiting Line Name | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1 | TR_LINE 1379_1
FN-Gulf | 3CRO_Croydon 66 kV | Loading (A) | 19.6195 | 18.5244 | 17.7176 | 17.0883 | 16.5803
FN-Gulf | 3CRO_Croydon 66 kV | Loading (MVA) | 2.3586 | 2.2274 | 2.1308 | 2.0554 | 1.9945
FN-Gulf | 3CRO_Croydon 66 kV | Loading (MW) | 1.0235 | 0.82941 | 0.67569 | 0.54697 | 0.43549
FN-Gulf | 3CRO_Croydon 66 kV | Power Factor | 0.43397 | 0.37236 | 0.31711 | 0.26612 | 0.21835
FN-Gulf | 3CRO_Croydon 66 kV | Rating (A) | 457 | 457 | 457 | 457 | 457
FN-Gulf | 3CRO_Croydon 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Gulf | 3CRO_Croydon 66 kV | Min Voltage at Constrained Conductor | 69.4064 | 69.4219 | 69.4335 | 69.4431 | 69.4515
FN-Gulf | 3CRO_Croydon 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
FN-Gulf | 3NOR_Normanton 66 kV | % of Rated A | 4.493% | 4.51% | 4.539% | 4.575% | 4.614%
FN-Gulf | 3NOR_Normanton 66 kV | Limiting Line Name | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1 | TR_LINE 1692_1
FN-Gulf | 3NOR_Normanton 66 kV | Loading (A) | 20.535 | 20.6111 | 20.7442 | 20.9061 | 21.084
FN-Gulf | 3NOR_Normanton 66 kV | Loading (MVA) | 2.4419 | 2.4517 | 2.4681 | 2.4879 | 2.5095
FN-Gulf | 3NOR_Normanton 66 kV | Loading (MW) | 0.87801 | 0.70869 | 0.57354 | 0.4596 | 0.35989
FN-Gulf | 3NOR_Normanton 66 kV | Power Factor | 0.35547 | 0.28521 | 0.22863 | 0.18103 | 0.1397
FN-Gulf | 3NOR_Normanton 66 kV | Rating (A) | 457 | 457 | 457 | 457 | 457
FN-Gulf | 3NOR_Normanton 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Gulf | 3NOR_Normanton 66 kV | Min Voltage at Constrained Conductor | 68.6552 | 68.6766 | 68.6934 | 68.7072 | 68.7192
FN-Gulf | 3NOR_Normanton 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
FN-Gulf | 4KID_Ross - Kidston 132 kV | % of Rated A | 18.35% | 18.21% | 18.1% | 18.01% | 17.94%
FN-Gulf | 4KID_Ross - Kidston 132 kV | Limiting Line Name | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1 | TR_LINE 384_1
FN-Gulf | 4KID_Ross - Kidston 132 kV | Loading (A) | 65.1398 | 64.6432 | 64.264 | 63.9508 | 63.6808
FN-Gulf | 4KID_Ross - Kidston 132 kV | Loading (MVA) | 15.6391 | 15.5199 | 15.4289 | 15.3537 | 15.2889
FN-Gulf | 4KID_Ross - Kidston 132 kV | Loading (MW) | 2.6286 | 2.3252 | 2.0891 | 1.8895 | 1.7135
FN-Gulf | 4KID_Ross - Kidston 132 kV | Power Factor | 0.16808 | 0.14982 | 0.1354 | 0.12306 | 0.11207
FN-Gulf | 4KID_Ross - Kidston 132 kV | Rating (A) | 355 | 355 | 355 | 355 | 355
FN-Gulf | 4KID_Ross - Kidston 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Gulf | 4KID_Ross - Kidston 132 kV | Min Voltage at Constrained Conductor | 138.6131 | 138.6133 | 138.6134 | 138.6135 | 138.6136
FN-Gulf | 4KID_Ross - Kidston 132 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
FN-Gulf | 7216_4GEO (Georgetown) 132 kV | % of Rated A | 8.783% | 8.837% | 8.892% | 8.947% | 9.003%
FN-Gulf | 7216_4GEO (Georgetown) 132 kV | Limiting Line Name | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1 | TR_LINE 795_1
FN-Gulf | 7216_4GEO (Georgetown) 132 kV | Loading (A) | 26.1722 | 26.3337 | 26.4972 | 26.6629 | 26.8292
FN-Gulf | 7216_4GEO (Georgetown) 132 kV | Loading (MVA) | 6.4779 | 6.5207 | 6.5634 | 6.6063 | 6.6491
FN-Gulf | 7216_4GEO (Georgetown) 132 kV | Loading (MW) | 1.3715 | 1.0848 | 0.85411 | 0.65886 | 0.48654
FN-Gulf | 7216_4GEO (Georgetown) 132 kV | Power Factor | 0.20957 | 0.16421 | 0.12797 | 0.097558 | 0.070982
FN-Gulf | 7216_4GEO (Georgetown) 132 kV | Rating (A) | 298 | 298 | 298 | 298 | 298
FN-Gulf | 7216_4GEO (Georgetown) 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Gulf | 7216_4GEO (Georgetown) 132 kV | Min Voltage at Constrained Conductor | 142.9006 | 142.9625 | 143.01 | 143.0498 | 143.0845
FN-Gulf | 7216_4GEO (Georgetown) 132 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
FN-Gulf | Kidston Solar Farm (Genex) | % of Rated A | 0.02864% | 0.02865% | 0.02866% | 0.02867% | 0.02867%
FN-Gulf | Kidston Solar Farm (Genex) | Limiting Line Name | Genex_Interconnection | Genex_Interconnection | Genex_Interconnection | Genex_Interconnection | Genex_Interconnection
FN-Gulf | Kidston Solar Farm (Genex) | Loading (A) | 0.28643 | 0.28653 | 0.2866 | 0.28666 | 0.28672
FN-Gulf | Kidston Solar Farm (Genex) | Loading (MVA) | 0.071473 | 0.071523 | 0.07156 | 0.071592 | 0.071619
FN-Gulf | Kidston Solar Farm (Genex) | Loading (MW) | 5.1938e-08 | 5.1971e-08 | 5.1998e-08 | 5.2019e-08 | 5.2041e-08
FN-Gulf | Kidston Solar Farm (Genex) | Power Factor | 7.2668e-07 | 7.2664e-07 | 7.2663e-07 | 7.2661e-07 | 7.2664e-07
FN-Gulf | Kidston Solar Farm (Genex) | Rating (A) | 1000 | 1000 | 1000 | 1000 | 1000
FN-Gulf | Kidston Solar Farm (Genex) | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Gulf | Kidston Solar Farm (Genex) | Min Voltage at Constrained Conductor | 144.0687 | 144.1188 | 144.1565 | 144.1879 | 144.2153
FN-Gulf | Kidston Solar Farm (Genex) | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
FN-Innisfail | 2BA1_Babinda No 1 22 kV | % of Rated A | 2.983% | 2.981% | 2.98% | 2.98% | 2.98%
FN-Innisfail | 2BA1_Babinda No 1 22 kV | Limiting Line Name | HV_LINE 20534_1 | HV_LINE 20534_1 | HV_LINE 20534_1 | HV_LINE 20534_1 | HV_LINE 20534_1
FN-Innisfail | 2BA1_Babinda No 1 22 kV | Loading (A) | 3.9374 | 3.9351 | 3.9338 | 3.9334 | 3.9338
FN-Innisfail | 2BA1_Babinda No 1 22 kV | Loading (MVA) | 0.16323 | 0.16324 | 0.16325 | 0.16325 | 0.16325
FN-Innisfail | 2BA1_Babinda No 1 22 kV | Loading (MW) | 0.16293 | 0.16293 | 0.16293 | 0.16293 | 0.16293
FN-Innisfail | 2BA1_Babinda No 1 22 kV | Power Factor | 0.99815 | 0.99811 | 0.99808 | 0.99807 | 0.99808
FN-Innisfail | 2BA1_Babinda No 1 22 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
FN-Innisfail | 2BA1_Babinda No 1 22 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Innisfail | 2BA1_Babinda No 1 22 kV | Min Voltage at Constrained Conductor | 23.934 | 23.949 | 23.9577 | 23.9608 | 23.9579
FN-Innisfail | 2BA1_Babinda No 1 22 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
FN-Innisfail | 2BA2_Babinda No 2 22 kV | % of Rated A | 3.41% | 3.408% | 3.407% | 3.406% | 3.407%
FN-Innisfail | 2BA2_Babinda No 2 22 kV | Limiting Line Name | HV_LINE 51735_1 | HV_LINE 51735_1 | HV_LINE 51735_1 | HV_LINE 51735_1 | HV_LINE 51735_1
FN-Innisfail | 2BA2_Babinda No 2 22 kV | Loading (A) | 4.5012 | 4.4984 | 4.4968 | 4.4962 | 4.4967
FN-Innisfail | 2BA2_Babinda No 2 22 kV | Loading (MVA) | 0.18657 | 0.18657 | 0.18657 | 0.18657 | 0.18657
FN-Innisfail | 2BA2_Babinda No 2 22 kV | Loading (MW) | 0.18639 | 0.1864 | 0.1864 | 0.1864 | 0.1864
FN-Innisfail | 2BA2_Babinda No 2 22 kV | Power Factor | 0.999 | 0.99903 | 0.99905 | 0.99905 | 0.99905
FN-Innisfail | 2BA2_Babinda No 2 22 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
FN-Innisfail | 2BA2_Babinda No 2 22 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Innisfail | 2BA2_Babinda No 2 22 kV | Min Voltage at Constrained Conductor | 23.9308 | 23.9458 | 23.9545 | 23.9576 | 23.9548
FN-Innisfail | 2BA2_Babinda No 2 22 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
FN-Innisfail | 2MOU_Mourilyan 22 kV | % of Rated A | 4.203% | 4.203% | 4.203% | 4.203% | 4.203%
FN-Innisfail | 2MOU_Mourilyan 22 kV | Limiting Line Name | HV_CABLE 1415_1 | HV_CABLE 1415_1 | HV_CABLE 1415_1 | HV_CABLE 1415_1 | HV_CABLE 1415_1
FN-Innisfail | 2MOU_Mourilyan 22 kV | Loading (A) | 4.203 | 4.2033 | 4.2034 | 4.2035 | 4.2034
FN-Innisfail | 2MOU_Mourilyan 22 kV | Loading (MVA) | 0.17426 | 0.17438 | 0.17445 | 0.17447 | 0.17445
FN-Innisfail | 2MOU_Mourilyan 22 kV | Loading (MW) | 0.07999 | 0.079991 | 0.079991 | 0.079991 | 0.079991
FN-Innisfail | 2MOU_Mourilyan 22 kV | Power Factor | 0.45899 | 0.45867 | 0.45849 | 0.45842 | 0.45848
FN-Innisfail | 2MOU_Mourilyan 22 kV | Rating (A) | 100 | 100 | 100 | 100 | 100
FN-Innisfail | 2MOU_Mourilyan 22 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Innisfail | 2MOU_Mourilyan 22 kV | Min Voltage at Constrained Conductor | 23.9373 | 23.9523 | 23.961 | 23.9641 | 23.9613
FN-Innisfail | 2MOU_Mourilyan 22 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
FN-Innisfail | 2SI1_Silkwood No 1 22 kV | % of Rated A | 0.9982% | 0.9977% | 0.9974% | 0.9973% | 0.9973%
FN-Innisfail | 2SI1_Silkwood No 1 22 kV | Limiting Line Name | HV_LINE 54592_1 | HV_LINE 54592_1 | HV_LINE 54592_1 | HV_LINE 54592_1 | HV_LINE 54592_1
FN-Innisfail | 2SI1_Silkwood No 1 22 kV | Loading (A) | 1.3176 | 1.3169 | 1.3165 | 1.3164 | 1.3165
FN-Innisfail | 2SI1_Silkwood No 1 22 kV | Loading (MVA) | 0.054616 | 0.054622 | 0.054625 | 0.054626 | 0.054625
FN-Innisfail | 2SI1_Silkwood No 1 22 kV | Loading (MW) | 0.047871 | 0.047873 | 0.047874 | 0.047874 | 0.047874
FN-Innisfail | 2SI1_Silkwood No 1 22 kV | Power Factor | 0.8765 | 0.87644 | 0.87641 | 0.87639 | 0.87641
FN-Innisfail | 2SI1_Silkwood No 1 22 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
FN-Innisfail | 2SI1_Silkwood No 1 22 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Innisfail | 2SI1_Silkwood No 1 22 kV | Min Voltage at Constrained Conductor | 23.932 | 23.947 | 23.9557 | 23.9588 | 23.9559
FN-Innisfail | 2SI1_Silkwood No 1 22 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
FN-Innisfail | 2SI2_Silkwood No 2 22 kV | % of Rated A | 1.441% | 1.44% | 1.44% | 1.44% | 1.44%
FN-Innisfail | 2SI2_Silkwood No 2 22 kV | Limiting Line Name | HV_CABLE 217_1 | HV_CABLE 217_1 | HV_CABLE 217_1 | HV_CABLE 217_1 | HV_CABLE 217_1
FN-Innisfail | 2SI2_Silkwood No 2 22 kV | Loading (A) | 1.4414 | 1.4405 | 1.4399 | 1.4397 | 1.4399
FN-Innisfail | 2SI2_Silkwood No 2 22 kV | Loading (MVA) | 0.059763 | 0.05976 | 0.059759 | 0.059758 | 0.059759
FN-Innisfail | 2SI2_Silkwood No 2 22 kV | Loading (MW) | 0.058094 | 0.058095 | 0.058096 | 0.058096 | 0.058096
FN-Innisfail | 2SI2_Silkwood No 2 22 kV | Power Factor | 0.9692 | 0.96926 | 0.96929 | 0.9693 | 0.96929
FN-Innisfail | 2SI2_Silkwood No 2 22 kV | Rating (A) | 100 | 100 | 100 | 100 | 100
FN-Innisfail | 2SI2_Silkwood No 2 22 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Innisfail | 2SI2_Silkwood No 2 22 kV | Min Voltage at Constrained Conductor | 23.9375 | 23.9525 | 23.9611 | 23.9642 | 23.9614
FN-Innisfail | 2SI2_Silkwood No 2 22 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
FN-Tablelands Cooktown | 2HEL_Helenvale 22 kV | % of Rated A | 1.79% | 1.775% | 1.792% | 1.776% | 1.781%
FN-Tablelands Cooktown | 2HEL_Helenvale 22 kV | Limiting Line Name | HV_LINE 42881_2 | HV_LINE 42881_2 | HV_LINE 42881_2 | HV_LINE 42881_2 | HV_LINE 42881_2
FN-Tablelands Cooktown | 2HEL_Helenvale 22 kV | Loading (A) | 1.5572 | 1.5443 | 1.5592 | 1.5451 | 1.5496
FN-Tablelands Cooktown | 2HEL_Helenvale 22 kV | Loading (MVA) | 0.059909 | 0.058914 | 0.060057 | 0.058979 | 0.059321
FN-Tablelands Cooktown | 2HEL_Helenvale 22 kV | Loading (MW) | 2.5804e-05 | 2.5375e-05 | 2.5867e-05 | 2.5403e-05 | 2.555e-05
FN-Tablelands Cooktown | 2HEL_Helenvale 22 kV | Power Factor | 0.00040912 | 0.00040912 | 0.00040912 | 0.00040912 | 0.00040912
FN-Tablelands Cooktown | 2HEL_Helenvale 22 kV | Rating (A) | 87 | 87 | 87 | 87 | 87
FN-Tablelands Cooktown | 2HEL_Helenvale 22 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Tablelands Cooktown | 2HEL_Helenvale 22 kV | Min Voltage at Constrained Conductor | 22.2115 | 22.0262 | 22.2389 | 22.0382 | 22.1021
FN-Tablelands Cooktown | 2HEL_Helenvale 22 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
FN-Tablelands Cooktown | 2KAT_Atherton 22 kV | % of Rated A | 1.445% | 1.44% | 1.439% | 1.436% | 1.442%
FN-Tablelands Cooktown | 2KAT_Atherton 22 kV | Limiting Line Name | HV_CABLE 122_1 | HV_CABLE 122_1 | HV_CABLE 122_1 | HV_CABLE 122_1 | HV_CABLE 122_1
FN-Tablelands Cooktown | 2KAT_Atherton 22 kV | Loading (A) | 1.4448 | 1.4402 | 1.4394 | 1.4362 | 1.4422
FN-Tablelands Cooktown | 2KAT_Atherton 22 kV | Loading (MVA) | 0.055637 | 0.055625 | 0.055623 | 0.055614 | 0.05563
FN-Tablelands Cooktown | 2KAT_Atherton 22 kV | Loading (MW) | 0.054321 | 0.054332 | 0.054334 | 0.054342 | 0.054327
FN-Tablelands Cooktown | 2KAT_Atherton 22 kV | Power Factor | 0.96987 | 0.97023 | 0.9703 | 0.97056 | 0.97008
FN-Tablelands Cooktown | 2KAT_Atherton 22 kV | Rating (A) | 100 | 100 | 100 | 100 | 100
FN-Tablelands Cooktown | 2KAT_Atherton 22 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Tablelands Cooktown | 2KAT_Atherton 22 kV | Min Voltage at Constrained Conductor | 22.2323 | 22.2983 | 22.3097 | 22.3572 | 22.2702
FN-Tablelands Cooktown | 2KAT_Atherton 22 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
FN-Tablelands Cooktown | 2MOS_Mossman 22 kV | % of Rated A | 5.302% | 5.275% | 4.967% | 4.955% | 4.942%
FN-Tablelands Cooktown | 2MOS_Mossman 22 kV | Limiting Line Name | HV_LINE 27084_1 | HV_LINE 27084_1 | HV_LINE 27084_1 | HV_LINE 27084_1 | HV_LINE 27084_1
FN-Tablelands Cooktown | 2MOS_Mossman 22 kV | Loading (A) | 6.9991 | 6.9632 | 6.5567 | 6.5402 | 6.5236
FN-Tablelands Cooktown | 2MOS_Mossman 22 kV | Loading (MVA) | 0.27301 | 0.27315 | 0.27501 | 0.27509 | 0.27518
FN-Tablelands Cooktown | 2MOS_Mossman 22 kV | Loading (MW) | 0.23655 | 0.23667 | 0.23816 | 0.23823 | 0.2383
FN-Tablelands Cooktown | 2MOS_Mossman 22 kV | Power Factor | 0.86644 | 0.86641 | 0.86601 | 0.86599 | 0.86597
FN-Tablelands Cooktown | 2MOS_Mossman 22 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
FN-Tablelands Cooktown | 2MOS_Mossman 22 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Tablelands Cooktown | 2MOS_Mossman 22 kV | Min Voltage at Constrained Conductor | 22.5202 | 22.6483 | 24.2158 | 24.2845 | 24.3538
FN-Tablelands Cooktown | 2MOS_Mossman 22 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
FN-Tablelands Cooktown | 2WH1_Ravenshoe 22 kV | % of Rated A | 0.8596% | 0.8627% | 0.8636% | 0.8658% | 0.8681%
FN-Tablelands Cooktown | 2WH1_Ravenshoe 22 kV | Limiting Line Name | HV_CABLE 272_1 | HV_CABLE 272_1 | HV_CABLE 272_1 | HV_CABLE 272_1 | HV_CABLE 272_1
FN-Tablelands Cooktown | 2WH1_Ravenshoe 22 kV | Loading (A) | 0.8596 | 0.86266 | 0.86355 | 0.8658 | 0.86809
FN-Tablelands Cooktown | 2WH1_Ravenshoe 22 kV | Loading (MVA) | 0.034001 | 0.034244 | 0.034315 | 0.034494 | 0.034677
FN-Tablelands Cooktown | 2WH1_Ravenshoe 22 kV | Loading (MW) | 0.00067991 | 0.00068477 | 0.00068619 | 0.00068976 | 0.00069342
FN-Tablelands Cooktown | 2WH1_Ravenshoe 22 kV | Power Factor | 0.019997 | 0.019997 | 0.019997 | 0.019997 | 0.019997
FN-Tablelands Cooktown | 2WH1_Ravenshoe 22 kV | Rating (A) | 100 | 100 | 100 | 100 | 100
FN-Tablelands Cooktown | 2WH1_Ravenshoe 22 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Tablelands Cooktown | 2WH1_Ravenshoe 22 kV | Min Voltage at Constrained Conductor | 22.8371 | 22.9184 | 22.9422 | 23.0019 | 23.0629
FN-Tablelands Cooktown | 2WH1_Ravenshoe 22 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
FN-Tablelands Cooktown | 2WH2_Ravenshoe 22kV | % of Rated A | 0.2406% | 0.2414% | 0.2417% | 0.2423% | 0.2429%
FN-Tablelands Cooktown | 2WH2_Ravenshoe 22kV | Limiting Line Name | HV_LINE 35947_1 | HV_LINE 35947_1 | HV_LINE 35947_1 | HV_LINE 35947_1 | HV_LINE 35947_1
FN-Tablelands Cooktown | 2WH2_Ravenshoe 22kV | Loading (A) | 0.59899 | 0.60113 | 0.60175 | 0.60332 | 0.60491
FN-Tablelands Cooktown | 2WH2_Ravenshoe 22kV | Loading (MVA) | 0.023692 | 0.023861 | 0.023911 | 0.024035 | 0.024163
FN-Tablelands Cooktown | 2WH2_Ravenshoe 22kV | Loading (MW) | 0.00037286 | 0.00037552 | 0.0003763 | 0.00037826 | 0.00038027
FN-Tablelands Cooktown | 2WH2_Ravenshoe 22kV | Power Factor | 0.015738 | 0.015738 | 0.015738 | 0.015738 | 0.015738
FN-Tablelands Cooktown | 2WH2_Ravenshoe 22kV | Rating (A) | 249 | 249 | 249 | 249 | 249
FN-Tablelands Cooktown | 2WH2_Ravenshoe 22kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Tablelands Cooktown | 2WH2_Ravenshoe 22kV | Min Voltage at Constrained Conductor | 22.836 | 22.9173 | 22.9411 | 23.0008 | 23.0617
FN-Tablelands Cooktown | 2WH2_Ravenshoe 22kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
FN-Tablelands Cooktown | 3AT1_Atherton No 1 66 kV | % of Rated A | 5.178% | 4.429% | 3.955% | 3.715% | 3.734%
FN-Tablelands Cooktown | 3AT1_Atherton No 1 66 kV | Limiting Line Name | TR_LINE 4407_1 | TR_LINE 4407_1 | TR_LINE 4407_1 | TR_LINE 4407_1 | TR_LINE 4407_1
FN-Tablelands Cooktown | 3AT1_Atherton No 1 66 kV | Loading (A) | 28.3735 | 24.2722 | 21.6724 | 20.3584 | 20.4629
FN-Tablelands Cooktown | 3AT1_Atherton No 1 66 kV | Loading (MVA) | 3.3982 | 2.9135 | 2.6012 | 2.4474 | 2.4639
FN-Tablelands Cooktown | 3AT1_Atherton No 1 66 kV | Loading (MW) | 2.4399 | 1.6638 | 1.0029 | 0.41213 | 0.14807
FN-Tablelands Cooktown | 3AT1_Atherton No 1 66 kV | Power Factor | 0.71799 | 0.57108 | 0.38555 | 0.1684 | 0.06003
FN-Tablelands Cooktown | 3AT1_Atherton No 1 66 kV | Rating (A) | 548 | 548 | 548 | 548 | 548
FN-Tablelands Cooktown | 3AT1_Atherton No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Tablelands Cooktown | 3AT1_Atherton No 1 66 kV | Min Voltage at Constrained Conductor | 69.1482 | 69.3021 | 69.2954 | 69.4055 | 69.517
FN-Tablelands Cooktown | 3AT1_Atherton No 1 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
FN-Tablelands Cooktown | 3AT2_Atherton No 2 66 kV | % of Rated A | 5.181% | 4.433% | 3.959% | 3.719% | 3.739%
FN-Tablelands Cooktown | 3AT2_Atherton No 2 66 kV | Limiting Line Name | TR_LINE 4672_1 | TR_LINE 4672_1 | TR_LINE 4672_1 | TR_LINE 4672_1 | TR_LINE 4672_1
FN-Tablelands Cooktown | 3AT2_Atherton No 2 66 kV | Loading (A) | 28.3898 | 24.2919 | 21.6949 | 20.3826 | 20.4873
FN-Tablelands Cooktown | 3AT2_Atherton No 2 66 kV | Loading (MVA) | 3.4002 | 2.9159 | 2.6039 | 2.4503 | 2.4668
FN-Tablelands Cooktown | 3AT2_Atherton No 2 66 kV | Loading (MW) | 2.4398 | 1.6638 | 1.0029 | 0.41214 | 0.14802
FN-Tablelands Cooktown | 3AT2_Atherton No 2 66 kV | Power Factor | 0.71754 | 0.57059 | 0.38514 | 0.1682 | 0.059937
FN-Tablelands Cooktown | 3AT2_Atherton No 2 66 kV | Rating (A) | 548 | 548 | 548 | 548 | 548
FN-Tablelands Cooktown | 3AT2_Atherton No 2 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Tablelands Cooktown | 3AT2_Atherton No 2 66 kV | Min Voltage at Constrained Conductor | 69.1482 | 69.3021 | 69.2954 | 69.4055 | 69.517
FN-Tablelands Cooktown | 3AT2_Atherton No 2 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
FN-Tablelands Cooktown | 3CHI_Chillagoe 66 kV | % of Rated A | 8.279% | 7.993% | 7.674% | 7.278% | 6.782%
FN-Tablelands Cooktown | 3CHI_Chillagoe 66 kV | Limiting Line Name | TR_LINE 104006_1 | TR_LINE 104006_1 | TR_LINE 104006_1 | TR_LINE 104006_1 | TR_LINE 104006_1
FN-Tablelands Cooktown | 3CHI_Chillagoe 66 kV | Loading (A) | 45.3707 | 43.8028 | 42.0541 | 39.8838 | 37.1637
FN-Tablelands Cooktown | 3CHI_Chillagoe 66 kV | Loading (MVA) | 5.3782 | 5.21 | 5.007 | 4.7619 | 4.4502
FN-Tablelands Cooktown | 3CHI_Chillagoe 66 kV | Loading (MW) | 5.2175 | 5.0369 | 4.8214 | 4.5586 | 4.2234
FN-Tablelands Cooktown | 3CHI_Chillagoe 66 kV | Power Factor | 0.97013 | 0.96678 | 0.96293 | 0.95731 | 0.94903
FN-Tablelands Cooktown | 3CHI_Chillagoe 66 kV | Rating (A) | 548 | 548 | 548 | 548 | 548
FN-Tablelands Cooktown | 3CHI_Chillagoe 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Tablelands Cooktown | 3CHI_Chillagoe 66 kV | Min Voltage at Constrained Conductor | 68.4386 | 68.6712 | 68.7392 | 68.9318 | 69.1359
FN-Tablelands Cooktown | 3CHI_Chillagoe 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
FN-Tablelands Cooktown | 3COO_Cooktown 66 kV | % of Rated A | 3.231% | 2.453% | 1.802% | 1.247% | 1.089%
FN-Tablelands Cooktown | 3COO_Cooktown 66 kV | Limiting Line Name | TR_CABLE 12_1 | TR_CABLE 12_1 | TR_CABLE 12_1 | TR_LINE 138000_1 | TR_LINE 138000_1
FN-Tablelands Cooktown | 3COO_Cooktown 66 kV | Loading (A) | 8.0129 | 6.0825 | 4.47 | 4.9742 | 4.3445
FN-Tablelands Cooktown | 3COO_Cooktown 66 kV | Loading (MVA) | 0.95804 | 0.73007 | 0.53538 | 0.59749 | 0.52335
FN-Tablelands Cooktown | 3COO_Cooktown 66 kV | Loading (MW) | 0.94882 | 0.71734 | 0.51771 | 0.33761 | 0.16523
FN-Tablelands Cooktown | 3COO_Cooktown 66 kV | Power Factor | 0.99037 | 0.98257 | 0.96701 | 0.56505 | 0.31572
FN-Tablelands Cooktown | 3COO_Cooktown 66 kV | Rating (A) | 248 | 248 | 248 | 399 | 399
FN-Tablelands Cooktown | 3COO_Cooktown 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Tablelands Cooktown | 3COO_Cooktown 66 kV | Min Voltage at Constrained Conductor | 69.0295 | 69.2981 | 69.1503 | 69.3505 | 69.5504
FN-Tablelands Cooktown | 3COO_Cooktown 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
FN-Tablelands Cooktown | 3DIM_Dimbulah 66 kV | % of Rated A | 35.15% | 33.64% | 32.19% | 30.6% | 28.81%
FN-Tablelands Cooktown | 3DIM_Dimbulah 66 kV | Limiting Line Name | TR_LINE 88168_1 | TR_LINE 88168_1 | TR_LINE 88168_1 | TR_LINE 88168_1 | TR_LINE 88168_1
FN-Tablelands Cooktown | 3DIM_Dimbulah 66 kV | Loading (A) | 76.6342 | 73.3346 | 70.179 | 66.7161 | 62.8019
FN-Tablelands Cooktown | 3DIM_Dimbulah 66 kV | Loading (MVA) | 9.1783 | 8.8027 | 8.4231 | 8.0202 | 7.5618
FN-Tablelands Cooktown | 3DIM_Dimbulah 66 kV | Loading (MW) | 9.0138 | 8.6211 | 8.2254 | 7.8016 | 7.3177
FN-Tablelands Cooktown | 3DIM_Dimbulah 66 kV | Power Factor | 0.98207 | 0.97937 | 0.97652 | 0.97275 | 0.96772
FN-Tablelands Cooktown | 3DIM_Dimbulah 66 kV | Rating (A) | 218 | 218 | 218 | 218 | 218
FN-Tablelands Cooktown | 3DIM_Dimbulah 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Tablelands Cooktown | 3DIM_Dimbulah 66 kV | Min Voltage at Constrained Conductor | 69.1449 | 69.299 | 69.2925 | 69.4029 | 69.5147
FN-Tablelands Cooktown | 3DIM_Dimbulah 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
FN-Tablelands Cooktown | 3EVE_Evelyn 66 kV | % of Rated A | 2.674% | 2.811% | 3.158% | 4.14% | 5.175%
FN-Tablelands Cooktown | 3EVE_Evelyn 66 kV | Limiting Line Name | TR_LINE 4423_1 | TR_LINE 4423_1 | TR_LINE 178961_1 | TR_LINE 178961_1 | TR_LINE 178961_1
FN-Tablelands Cooktown | 3EVE_Evelyn 66 kV | Loading (A) | 6.9517 | 7.3094 | 5.3365 | 6.997 | 8.7461
FN-Tablelands Cooktown | 3EVE_Evelyn 66 kV | Loading (MVA) | 0.83335 | 0.87876 | 0.64348 | 0.8458 | 1.0599
FN-Tablelands Cooktown | 3EVE_Evelyn 66 kV | Loading (MW) | 0.021261 | 0.26518 | 0.51967 | 0.75569 | 0.98957
FN-Tablelands Cooktown | 3EVE_Evelyn 66 kV | Power Factor | 0.025513 | 0.30087 | 0.80759 | 0.89346 | 0.93362
FN-Tablelands Cooktown | 3EVE_Evelyn 66 kV | Rating (A) | 260 | 260 | 169 | 169 | 169
FN-Tablelands Cooktown | 3EVE_Evelyn 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Tablelands Cooktown | 3EVE_Evelyn 66 kV | Min Voltage at Constrained Conductor | 69.2104 | 69.4103 | 69.6173 | 69.7905 | 69.968
FN-Tablelands Cooktown | 3EVE_Evelyn 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
FN-Tablelands Cooktown | 3HLA_Helenvale 66 kV | % of Rated A | 3.826% | 3.502% | 3.272% | 3.118% | 3.024%
FN-Tablelands Cooktown | 3HLA_Helenvale 66 kV | Limiting Line Name | TR_LINE 39200_1 | TR_LINE 39200_1 | TR_LINE 39200_1 | TR_LINE 39200_1 | TR_LINE 39200_1
FN-Tablelands Cooktown | 3HLA_Helenvale 66 kV | Loading (A) | 14.4617 | 13.2358 | 12.3697 | 11.787 | 11.4315
FN-Tablelands Cooktown | 3HLA_Helenvale 66 kV | Loading (MVA) | 1.7272 | 1.5855 | 1.4775 | 1.4113 | 1.3721
FN-Tablelands Cooktown | 3HLA_Helenvale 66 kV | Loading (MW) | 1.1174 | 0.86322 | 0.6472 | 0.45431 | 0.27153
FN-Tablelands Cooktown | 3HLA_Helenvale 66 kV | Power Factor | 0.64694 | 0.54445 | 0.43805 | 0.3219 | 0.19789
FN-Tablelands Cooktown | 3HLA_Helenvale 66 kV | Rating (A) | 378 | 378 | 378 | 378 | 378
FN-Tablelands Cooktown | 3HLA_Helenvale 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Tablelands Cooktown | 3HLA_Helenvale 66 kV | Min Voltage at Constrained Conductor | 68.9544 | 69.1598 | 68.9603 | 69.1301 | 69.3003
FN-Tablelands Cooktown | 3HLA_Helenvale 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
FN-Tablelands Cooktown | 3MA2_Mareeba No 2 66 kV | % of Rated A | 18.74% | 18.93% | 19.04% | 19.51% | 20.08%
FN-Tablelands Cooktown | 3MA2_Mareeba No 2 66 kV | Limiting Line Name | TR_LINE 5351_1 | TR_LINE 5351_1 | TR_LINE 5351_1 | TR_LINE 5351_1 | TR_LINE 5351_1
FN-Tablelands Cooktown | 3MA2_Mareeba No 2 66 kV | Loading (A) | 31.6744 | 31.9922 | 32.177 | 32.9677 | 33.9328
FN-Tablelands Cooktown | 3MA2_Mareeba No 2 66 kV | Loading (MVA) | 3.7936 | 3.8402 | 3.862 | 3.9632 | 4.0857
FN-Tablelands Cooktown | 3MA2_Mareeba No 2 66 kV | Loading (MW) | 0.1945 | 0.34161 | 0.7335 | 1.1104 | 1.4605
FN-Tablelands Cooktown | 3MA2_Mareeba No 2 66 kV | Power Factor | 0.051246 | 0.088841 | 0.18981 | 0.28007 | 0.35733
FN-Tablelands Cooktown | 3MA2_Mareeba No 2 66 kV | Rating (A) | 169 | 169 | 169 | 169 | 169
FN-Tablelands Cooktown | 3MA2_Mareeba No 2 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Tablelands Cooktown | 3MA2_Mareeba No 2 66 kV | Min Voltage at Constrained Conductor | 69.1482 | 69.3021 | 69.2954 | 69.4055 | 69.517
FN-Tablelands Cooktown | 3MA2_Mareeba No 2 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
FN-Tablelands Cooktown | 3MO1_Mossman No 1 66 kV | % of Rated A | 23.1% | 23.17% | 23.83% | 24.48% | 25.25%
FN-Tablelands Cooktown | 3MO1_Mossman No 1 66 kV | Limiting Line Name | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1 | TR_LINE 2081_1
FN-Tablelands Cooktown | 3MO1_Mossman No 1 66 kV | Loading (A) | 30.491 | 30.586 | 31.4576 | 32.308 | 33.3338
FN-Tablelands Cooktown | 3MO1_Mossman No 1 66 kV | Loading (MVA) | 3.6605 | 3.6815 | 3.7851 | 3.8941 | 4.0248
FN-Tablelands Cooktown | 3MO1_Mossman No 1 66 kV | Loading (MW) | 0.10084 | 0.38704 | 0.85021 | 1.2297 | 1.5824
FN-Tablelands Cooktown | 3MO1_Mossman No 1 66 kV | Power Factor | 0.027451 | 0.105 | 0.22449 | 0.31565 | 0.39302
FN-Tablelands Cooktown | 3MO1_Mossman No 1 66 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
FN-Tablelands Cooktown | 3MO1_Mossman No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Tablelands Cooktown | 3MO1_Mossman No 1 66 kV | Min Voltage at Constrained Conductor | 69.3119 | 69.4924 | 69.4682 | 69.5889 | 69.7101
FN-Tablelands Cooktown | 3MO1_Mossman No 1 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
FN-Tablelands Cooktown | 3MO2_Mossman No 2 66 kV | % of Rated A | 4.906% | 6.188% | 3.673% | 3.678% | 3.684%
FN-Tablelands Cooktown | 3MO2_Mossman No 2 66 kV | Limiting Line Name | TR_LINE 2062_3 | TR_LINE 2062_3 | TR_LINE 2062_3 | TR_LINE 2062_3 | TR_LINE 2062_3
FN-Tablelands Cooktown | 3MO2_Mossman No 2 66 kV | Loading (A) | 8.2907 | 10.457 | 6.2065 | 6.2164 | 6.2264
FN-Tablelands Cooktown | 3MO2_Mossman No 2 66 kV | Loading (MVA) | 0.99296 | 1.2552 | 0.74493 | 0.7473 | 0.7497
FN-Tablelands Cooktown | 3MO2_Mossman No 2 66 kV | Loading (MW) | 0.15108 | 0.78328 | 0.00058869 | 0.00059056 | 0.00059246
FN-Tablelands Cooktown | 3MO2_Mossman No 2 66 kV | Power Factor | 0.15214 | 0.62402 | 0.00078611 | 0.00078611 | 0.00078611
FN-Tablelands Cooktown | 3MO2_Mossman No 2 66 kV | Rating (A) | 169 | 169 | 169 | 169 | 169
FN-Tablelands Cooktown | 3MO2_Mossman No 2 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Tablelands Cooktown | 3MO2_Mossman No 2 66 kV | Min Voltage at Constrained Conductor | 69.1482 | 69.3021 | 69.2954 | 69.4055 | 69.517
FN-Tablelands Cooktown | 3MO2_Mossman No 2 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
FN-Tablelands Cooktown | 3MTG_Mt Garnet 66 kV | % of Rated A | 5.759% | 5.622% | 5.509% | 5.425% | 5.358%
FN-Tablelands Cooktown | 3MTG_Mt Garnet 66 kV | Limiting Line Name | TR_LINE 169447_1 | TR_LINE 169447_1 | TR_LINE 169447_1 | TR_LINE 169447_1 | TR_LINE 169447_1
FN-Tablelands Cooktown | 3MTG_Mt Garnet 66 kV | Loading (A) | 9.7325 | 9.5006 | 9.31 | 9.1675 | 9.0551
FN-Tablelands Cooktown | 3MTG_Mt Garnet 66 kV | Loading (MVA) | 1.1696 | 1.1452 | 1.1228 | 1.108 | 1.0969
FN-Tablelands Cooktown | 3MTG_Mt Garnet 66 kV | Loading (MW) | 0.57665 | 0.51155 | 0.4554 | 0.40523 | 0.35958
FN-Tablelands Cooktown | 3MTG_Mt Garnet 66 kV | Power Factor | 0.49304 | 0.44671 | 0.40559 | 0.36572 | 0.32783
FN-Tablelands Cooktown | 3MTG_Mt Garnet 66 kV | Rating (A) | 169 | 169 | 169 | 169 | 169
FN-Tablelands Cooktown | 3MTG_Mt Garnet 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Tablelands Cooktown | 3MTG_Mt Garnet 66 kV | Min Voltage at Constrained Conductor | 69.3813 | 69.5906 | 69.6292 | 69.7804 | 69.9357
FN-Tablelands Cooktown | 3MTG_Mt Garnet 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
FN-Tablelands Cooktown | 3RA1_Ravenshoe No 1 66 kV | % of Rated A | 1.859% | 1.956% | 2.201% | 2.511% | 2.855%
FN-Tablelands Cooktown | 3RA1_Ravenshoe No 1 66 kV | Limiting Line Name | TR_LINE 178964_1 | TR_LINE 178964_1 | TR_LINE 178964_1 | TR_LINE 178964_1 | TR_LINE 178964_1
FN-Tablelands Cooktown | 3RA1_Ravenshoe No 1 66 kV | Loading (A) | 3.1424 | 3.306 | 3.7204 | 4.2434 | 4.8248
FN-Tablelands Cooktown | 3RA1_Ravenshoe No 1 66 kV | Loading (MVA) | 0.37729 | 0.39828 | 0.44861 | 0.51295 | 0.5847
FN-Tablelands Cooktown | 3RA1_Ravenshoe No 1 66 kV | Loading (MW) | 0.017386 | 0.12114 | 0.2387 | 0.3431 | 0.44205
FN-Tablelands Cooktown | 3RA1_Ravenshoe No 1 66 kV | Power Factor | 0.046082 | 0.30416 | 0.53209 | 0.66888 | 0.75602
FN-Tablelands Cooktown | 3RA1_Ravenshoe No 1 66 kV | Rating (A) | 169 | 169 | 169 | 169 | 169
FN-Tablelands Cooktown | 3RA1_Ravenshoe No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Tablelands Cooktown | 3RA1_Ravenshoe No 1 66 kV | Min Voltage at Constrained Conductor | 69.3186 | 69.5546 | 69.6175 | 69.7908 | 69.9683
FN-Tablelands Cooktown | 3RA1_Ravenshoe No 1 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
FN-Tablelands Cooktown | 7200_Craiglie No 2 132 kV | % of Rated A | 13.23% | 13.06% | 8.776% | 8.857% | 9.15%
FN-Tablelands Cooktown | 7200_Craiglie No 2 132 kV | Limiting Line Name | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1 | TR_LINE 3956_1
FN-Tablelands Cooktown | 7200_Craiglie No 2 132 kV | Loading (A) | 59.7854 | 59.0107 | 39.668 | 40.0355 | 41.3578
FN-Tablelands Cooktown | 7200_Craiglie No 2 132 kV | Loading (MVA) | 14.9051 | 14.7428 | 9.9121 | 10.0191 | 10.3656
FN-Tablelands Cooktown | 7200_Craiglie No 2 132 kV | Loading (MW) | 4.0672 | 2.9485 | 0.30891 | 1.2327 | 2.8747
FN-Tablelands Cooktown | 7200_Craiglie No 2 132 kV | Power Factor | 0.27287 | 0.2 | 0.031165 | 0.12273 | 0.27702
FN-Tablelands Cooktown | 7200_Craiglie No 2 132 kV | Rating (A) | 452 | 452 | 452 | 452 | 452
FN-Tablelands Cooktown | 7200_Craiglie No 2 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Tablelands Cooktown | 7200_Craiglie No 2 132 kV | Min Voltage at Constrained Conductor | 143.9392 | 144.2415 | 144.2665 | 144.4854 | 144.7022
FN-Tablelands Cooktown | 7200_Craiglie No 2 132 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
FN-Tablelands Cooktown | 7201_Craiglie No 1 132 kV | % of Rated A | 5.991% | 5.685% | 2.111% | 3.804% | 5.843%
FN-Tablelands Cooktown | 7201_Craiglie No 1 132 kV | Limiting Line Name | TR_LINE 3957_2 | TR_LINE 3957_2 | TR_LINE 38738_a | TR_LINE 38738_a | TR_LINE 38738_a
FN-Tablelands Cooktown | 7201_Craiglie No 1 132 kV | Loading (A) | 27.0792 | 25.6977 | 8.0024 | 14.4172 | 22.1465
FN-Tablelands Cooktown | 7201_Craiglie No 1 132 kV | Loading (MVA) | 6.7511 | 6.4201 | 2.0163 | 3.6407 | 5.6052
FN-Tablelands Cooktown | 7201_Craiglie No 1 132 kV | Loading (MW) | 3.4454 | 2.5916 | 1.4224 | 3.3643 | 5.445
FN-Tablelands Cooktown | 7201_Craiglie No 1 132 kV | Power Factor | 0.51034 | 0.40366 | 0.70543 | 0.924 | 0.97131
FN-Tablelands Cooktown | 7201_Craiglie No 1 132 kV | Rating (A) | 452 | 452 | 379 | 379 | 379
FN-Tablelands Cooktown | 7201_Craiglie No 1 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Tablelands Cooktown | 7201_Craiglie No 1 132 kV | Min Voltage at Constrained Conductor | 143.9392 | 144.2415 | 145.4683 | 145.7963 | 146.1265
FN-Tablelands Cooktown | 7201_Craiglie No 1 132 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
FN-Tablelands Cooktown | 7285_4LAK (Lakeland) 132kV | % of Rated A | 7.978% | 7.982% | 7.949% | 7.96% | 7.976%
FN-Tablelands Cooktown | 7285_4LAK (Lakeland) 132kV | Limiting Line Name | TR_LINE 37686_1 | TR_LINE 37686_1 | TR_LINE 37686_1 | TR_LINE 37686_1 | TR_LINE 37686_1
FN-Tablelands Cooktown | 7285_4LAK (Lakeland) 132kV | Loading (A) | 40.5285 | 40.5464 | 40.3784 | 40.4362 | 40.5177
FN-Tablelands Cooktown | 7285_4LAK (Lakeland) 132kV | Loading (MVA) | 10.2209 | 10.2528 | 10.1783 | 10.2158 | 10.2595
FN-Tablelands Cooktown | 7285_4LAK (Lakeland) 132kV | Loading (MW) | 1.2522 | 0.94585 | 0.68539 | 0.45249 | 0.23214
FN-Tablelands Cooktown | 7285_4LAK (Lakeland) 132kV | Power Factor | 0.12251 | 0.092252 | 0.067339 | 0.044294 | 0.022627
FN-Tablelands Cooktown | 7285_4LAK (Lakeland) 132kV | Rating (A) | 508 | 508 | 508 | 508 | 508
FN-Tablelands Cooktown | 7285_4LAK (Lakeland) 132kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Tablelands Cooktown | 7285_4LAK (Lakeland) 132kV | Min Voltage at Constrained Conductor | 145.6023 | 145.992 | 145.5338 | 145.8611 | 146.1906
FN-Tablelands Cooktown | 7285_4LAK (Lakeland) 132kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
FN-Tablelands Cooktown | Mungana 66 kV | % of Rated A | 9.719% | 9.679% | 9.662% | 9.627% | 9.588%
FN-Tablelands Cooktown | Mungana 66 kV | Limiting Line Name | TR_LINE 104012_1 | TR_LINE 104012_1 | TR_LINE 104012_1 | TR_LINE 104012_1 | TR_LINE 104012_1
FN-Tablelands Cooktown | Mungana 66 kV | Loading (A) | 44.4144 | 44.2327 | 44.1573 | 43.9944 | 43.817
FN-Tablelands Cooktown | Mungana 66 kV | Loading (MVA) | 5.2156 | 5.2156 | 5.2156 | 5.2156 | 5.2155
FN-Tablelands Cooktown | Mungana 66 kV | Loading (MW) | 5.2127 | 5.2126 | 5.2126 | 5.2125 | 5.2124
FN-Tablelands Cooktown | Mungana 66 kV | Power Factor | 0.99944 | 0.99942 | 0.99942 | 0.99941 | 0.99939
FN-Tablelands Cooktown | Mungana 66 kV | Rating (A) | 457 | 457 | 457 | 457 | 457
FN-Tablelands Cooktown | Mungana 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
FN-Tablelands Cooktown | Mungana 66 kV | Min Voltage at Constrained Conductor | 67.7866 | 68.0647 | 68.1807 | 68.4329 | 68.7097
FN-Tablelands Cooktown | Mungana 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
FN-Tablelands Cooktown | TURK_YALK (Ex 7201) | % of Rated A |  |  | 8.76% | 8.842% | 9.133%
FN-Tablelands Cooktown | TURK_YALK (Ex 7201) | Limiting Line Name |  |  | TR_LINE 3957_2 | TR_LINE 3957_2 | TR_LINE 3957_2
FN-Tablelands Cooktown | TURK_YALK (Ex 7201) | Loading (A) |  |  | 39.5937 | 39.9643 | 41.2796
FN-Tablelands Cooktown | TURK_YALK (Ex 7201) | Loading (MVA) |  |  | 9.8935 | 10.0013 | 10.346
FN-Tablelands Cooktown | TURK_YALK (Ex 7201) | Loading (MW) |  |  | 0.29204 | 1.2373 | 2.8688
FN-Tablelands Cooktown | TURK_YALK (Ex 7201) | Power Factor |  |  | 0.029518 | 0.12371 | 0.27728
FN-Tablelands Cooktown | TURK_YALK (Ex 7201) | Rating (A) |  |  | 452 | 452 | 452
FN-Tablelands Cooktown | TURK_YALK (Ex 7201) | Time |  |  | 12:00:00 | 12:00:00 | 12:00:00
FN-Tablelands Cooktown | TURK_YALK (Ex 7201) | Min Voltage at Constrained Conductor |  |  | 144.2665 | 144.4854 | 144.7022
FN-Tablelands Cooktown | TURK_YALK (Ex 7201) | Contingency Outage |  |  | _NNC | _NNC | _NNC
Interstitial Grid | 7194_Gladstone PS - Boat Creek 132 kV | % of Rated A | 1.081% | 1.033% | 0.9741% | 0.9175% | 0.8916%
Interstitial Grid | 7194_Gladstone PS - Boat Creek 132 kV | Limiting Line Name | Subtrans_GLNO_CALI_LINE_1 | Subtrans_GLNO_CALI_LINE_1 | Subtrans_GLNO_CALI_LINE_1 | Subtrans_GLNO_CALI_LINE_1 | Subtrans_GLNO_CALI_LINE_1
Interstitial Grid | 7194_Gladstone PS - Boat Creek 132 kV | Loading (A) | 54.0596 | 51.6588 | 48.7041 | 45.8737 | 44.5784
Interstitial Grid | 7194_Gladstone PS - Boat Creek 132 kV | Loading (MVA) | 13.1054 | 12.5431 | 11.8252 | 11.1049 | 10.7778
Interstitial Grid | 7194_Gladstone PS - Boat Creek 132 kV | Loading (MW) | 12.9464 | 12.372 | 11.647 | 10.9234 | 10.7699
Interstitial Grid | 7194_Gladstone PS - Boat Creek 132 kV | Power Factor | 0.98787 | 0.98636 | 0.98493 | 0.98365 | 0.99926
Interstitial Grid | 7194_Gladstone PS - Boat Creek 132 kV | Rating (A) | 5000 | 5000 | 5000 | 5000 | 5000
Interstitial Grid | 7194_Gladstone PS - Boat Creek 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
Interstitial Grid | 7194_Gladstone PS - Boat Creek 132 kV | Min Voltage at Constrained Conductor | 139.9644 | 140.1842 | 140.179 | 139.7623 | 139.5874
Interstitial Grid | 7194_Gladstone PS - Boat Creek 132 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
Interstitial Grid | 7195_Gladstone PS - Boat Creek 132 kV | % of Rated A
Interstitial Grid | 7195_Gladstone PS - Boat Creek 132 kV | Limiting Line Name
Interstitial Grid | 7195_Gladstone PS - Boat Creek 132 kV | Loading (A)
Interstitial Grid | 7195_Gladstone PS - Boat Creek 132 kV | Loading (MVA)
Interstitial Grid | 7195_Gladstone PS - Boat Creek 132 kV | Loading (MW)
Interstitial Grid | 7195_Gladstone PS - Boat Creek 132 kV | Power Factor
Interstitial Grid | 7195_Gladstone PS - Boat Creek 132 kV | Rating (A)
Interstitial Grid | 7195_Gladstone PS - Boat Creek 132 kV | Time
Interstitial Grid | 7195_Gladstone PS - Boat Creek 132 kV | Min Voltage at Constrained Conductor
Interstitial Grid | 7195_Gladstone PS - Boat Creek 132 kV | Contingency Outage
MK-Mackay Area | 14109_Marian Mill 11 kV | % of Rated A | 0.2691% | 0.2695% | 0.2697% | 0.2699% | 0.2701%
MK-Mackay Area | 14109_Marian Mill 11 kV | Limiting Line Name | HV_CABLE 461202_1 | HV_CABLE 461202_1 | HV_CABLE 461202_1 | HV_CABLE 461202_1 | HV_CABLE 461202_1
MK-Mackay Area | 14109_Marian Mill 11 kV | Loading (A) | 0.84769 | 0.84885 | 0.84969 | 0.8503 | 0.85072
MK-Mackay Area | 14109_Marian Mill 11 kV | Loading (MVA) | 0.01628 | 0.016325 | 0.016357 | 0.016381 | 0.016397
MK-Mackay Area | 14109_Marian Mill 11 kV | Loading (MW) | 0.00032182 | 0.0003227 | 0.00032334 | 0.00032381 | 0.00032412
MK-Mackay Area | 14109_Marian Mill 11 kV | Power Factor | 0.019651 | 0.019651 | 0.019651 | 0.019651 | 0.019651
MK-Mackay Area | 14109_Marian Mill 11 kV | Rating (A) | 315 | 315 | 315 | 315 | 315
MK-Mackay Area | 14109_Marian Mill 11 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK-Mackay Area | 14109_Marian Mill 11 kV | Min Voltage at Constrained Conductor | 11.0882 | 11.1034 | 11.1144 | 11.1224 | 11.1278
MK-Mackay Area | 14109_Marian Mill 11 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
MK-Mackay Area | 231_Carmila 33 kV | % of Rated A | 5.702% | 5.688% | 5.677% | 5.666% | 5.656%
MK-Mackay Area | 231_Carmila 33 kV | Limiting Line Name | TR_LINE 211924_1 | TR_LINE 211924_1 | TR_LINE 211924_1 | TR_LINE 211924_1 | TR_LINE 211924_1
MK-Mackay Area | 231_Carmila 33 kV | Loading (A) | 11.0055 | 10.9785 | 10.9557 | 10.9356 | 10.9166
MK-Mackay Area | 231_Carmila 33 kV | Loading (MVA) | 0.65783 | 0.6579 | 0.65796 | 0.65801 | 0.65807
MK-Mackay Area | 231_Carmila 33 kV | Loading (MW) | 0.54403 | 0.54405 | 0.54407 | 0.54409 | 0.5441
MK-Mackay Area | 231_Carmila 33 kV | Power Factor | 0.82698 | 0.82692 | 0.82687 | 0.82683 | 0.82679
MK-Mackay Area | 231_Carmila 33 kV | Rating (A) | 193 | 193 | 193 | 193 | 193
MK-Mackay Area | 231_Carmila 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK-Mackay Area | 231_Carmila 33 kV | Min Voltage at Constrained Conductor | 34.5097 | 34.5982 | 34.6737 | 34.7402 | 34.8034
MK-Mackay Area | 231_Carmila 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
MK-Mackay Area | 247_Mill 11 kV | % of Rated A | 1.833% | 1.853% | 1.851% | 1.849% | 1.847%
MK-Mackay Area | 247_Mill 11 kV | Limiting Line Name | HV_LINE 141313_1 | HV_LINE 141313_1 | HV_LINE 141313_1 | HV_LINE 141313_1 | HV_LINE 141313_1
MK-Mackay Area | 247_Mill 11 kV | Loading (A) | 6.1967 | 6.2635 | 6.2563 | 6.2501 | 6.2442
MK-Mackay Area | 247_Mill 11 kV | Loading (MVA) | 0.12154 | 0.12153 | 0.12153 | 0.12153 | 0.12153
MK-Mackay Area | 247_Mill 11 kV | Loading (MW) | 0.1014 | 0.10141 | 0.10141 | 0.10141 | 0.10141
MK-Mackay Area | 247_Mill 11 kV | Power Factor | 0.83432 | 0.83441 | 0.8344 | 0.83439 | 0.83438
MK-Mackay Area | 247_Mill 11 kV | Rating (A) | 338 | 338 | 338 | 338 | 338
MK-Mackay Area | 247_Mill 11 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK-Mackay Area | 247_Mill 11 kV | Min Voltage at Constrained Conductor | 11.3238 | 11.2025 | 11.2154 | 11.2267 | 11.2372
MK-Mackay Area | 247_Mill 11 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
MK-Mackay Area | 3045_Sarina No 1 33 kV | % of Rated A | 26.13% | 26.52% | 26.94% | 27.37% | 27.83%
MK-Mackay Area | 3045_Sarina No 1 33 kV | Limiting Line Name | TR_LINE 12173_1 | TR_LINE 12173_1 | TR_LINE 12173_1 | TR_LINE 12173_1 | TR_LINE 12173_1
MK-Mackay Area | 3045_Sarina No 1 33 kV | Loading (A) | 78.1168 | 79.3052 | 80.5636 | 81.8408 | 83.205
MK-Mackay Area | 3045_Sarina No 1 33 kV | Loading (MVA) | 4.8468 | 4.9281 | 5.0129 | 5.0982 | 5.1888
MK-Mackay Area | 3045_Sarina No 1 33 kV | Loading (MW) | 0.83183 | 1.1485 | 1.4254 | 1.6708 | 1.9068
MK-Mackay Area | 3045_Sarina No 1 33 kV | Power Factor | 0.17145 | 0.23289 | 0.28419 | 0.32757 | 0.36734
MK-Mackay Area | 3045_Sarina No 1 33 kV | Rating (A) | 299 | 299 | 299 | 299 | 299
MK-Mackay Area | 3045_Sarina No 1 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK-Mackay Area | 3045_Sarina No 1 33 kV | Min Voltage at Constrained Conductor | 35.8182 | 35.8729 | 35.9197 | 35.9604 | 35.9987
MK-Mackay Area | 3045_Sarina No 1 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
MK-Mackay Area | 3046_Rosella 33 kV | % of Rated A | 0.3101% | 1.343% | 2.707% | 4.164% | 5.771%
MK-Mackay Area | 3046_Rosella 33 kV | Limiting Line Name | TR_CABLE 6962_1 | TR_CABLE 6962_1 | TR_CABLE 6962_1 | TR_CABLE 6962_1 | TR_CABLE 7121_1
MK-Mackay Area | 3046_Rosella 33 kV | Loading (A) | 1.2683 | 5.4919 | 11.0726 | 17.0306 | 23.6036
MK-Mackay Area | 3046_Rosella 33 kV | Loading (MVA) | 0.07635 | 0.33062 | 0.66659 | 1.0253 | 1.4264
MK-Mackay Area | 3046_Rosella 33 kV | Loading (MW) | 0.0029356 | 0.32239 | 0.66331 | 1.0239 | 1.4262
MK-Mackay Area | 3046_Rosella 33 kV | Power Factor | 0.03845 | 0.9742 | 0.99462 | 0.99837 | 0.99983
MK-Mackay Area | 3046_Rosella 33 kV | Rating (A) | 409 | 409 | 409 | 409 | 409
MK-Mackay Area | 3046_Rosella 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK-Mackay Area | 3046_Rosella 33 kV | Min Voltage at Constrained Conductor | 34.756 | 34.757 | 34.7575 | 34.7577 | 34.8904
MK-Mackay Area | 3046_Rosella 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
MK-Mackay Area | 3047_Sarina No 2 33 kV | % of Rated A | 2.003% | 3.564% | 5.067% | 6.453% | 7.796%
MK-Mackay Area | 3047_Sarina No 2 33 kV | Limiting Line Name | TR_LINE 11717_1 | TR_LINE 11717_1 | TR_LINE 11717_1 | TR_LINE 11717_1 | TR_LINE 11717_1
MK-Mackay Area | 3047_Sarina No 2 33 kV | Loading (A) | 7.6119 | 13.5421 | 19.2553 | 24.5217 | 29.6239
MK-Mackay Area | 3047_Sarina No 2 33 kV | Loading (MVA) | 0.45919 | 0.81777 | 1.1638 | 1.4832 | 1.7932
MK-Mackay Area | 3047_Sarina No 2 33 kV | Loading (MW) | 0.32604 | 0.75434 | 1.1226 | 1.4532 | 1.7702
MK-Mackay Area | 3047_Sarina No 2 33 kV | Power Factor | 0.71 | 0.92238 | 0.96453 | 0.97964 | 0.9871
MK-Mackay Area | 3047_Sarina No 2 33 kV | Rating (A) | 380 | 380 | 380 | 380 | 380
MK-Mackay Area | 3047_Sarina No 2 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK-Mackay Area | 3047_Sarina No 2 33 kV | Min Voltage at Constrained Conductor | 34.8286 | 34.8646 | 34.8948 | 34.9214 | 34.9463
MK-Mackay Area | 3047_Sarina No 2 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
MK-Mackay Area | 3053_Mt Bassett 33 kV | % of Rated A | 2.465% | 0.7577% | 1.94% | 3.921% | 6.101%
MK-Mackay Area | 3053_Mt Bassett 33 kV | Limiting Line Name | TR_LINE 11627_1 | TR_CABLE 318_1 | TR_LINE 11627_1 | TR_LINE 11627_1 | TR_LINE 11627_1
MK-Mackay Area | 3053_Mt Bassett 33 kV | Loading (A) | 5.7937 | 2.9474 | 4.5588 | 9.2144 | 14.3371
MK-Mackay Area | 3053_Mt Bassett 33 kV | Loading (MVA) | 0.3441 | 0.1753 | 0.2715 | 0.54934 | 0.85554
MK-Mackay Area | 3053_Mt Bassett 33 kV | Loading (MW) | 0.33665 | 0.034714 | 0.25098 | 0.53714 | 0.84655
MK-Mackay Area | 3053_Mt Bassett 33 kV | Power Factor | 0.97835 | 0.19803 | 0.92426 | 0.97747 | 0.98896
MK-Mackay Area | 3053_Mt Bassett 33 kV | Rating (A) | 235 | 389 | 235 | 235 | 235
MK-Mackay Area | 3053_Mt Bassett 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK-Mackay Area | 3053_Mt Bassett 33 kV | Min Voltage at Constrained Conductor | 34.2853 | 34.3376 | 34.384 | 34.4201 | 34.4523
MK-Mackay Area | 3053_Mt Bassett 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
MK-Mackay Area | 340_MK3-1 Farleigh 33 kV | % of Rated A | 2.268% | 2.275% | 2.281% | 2.286% | 2.291%
MK-Mackay Area | 340_MK3-1 Farleigh 33 kV | Limiting Line Name | TR_LINE 11332_1 | TR_LINE 11332_1 | TR_LINE 11332_1 | TR_LINE 11332_1 | TR_LINE 11332_1
MK-Mackay Area | 340_MK3-1 Farleigh 33 kV | Loading (A) | 3.9004 | 3.9131 | 3.9235 | 3.9324 | 3.9405
MK-Mackay Area | 340_MK3-1 Farleigh 33 kV | Loading (MVA) | 0.23348 | 0.235 | 0.23625 | 0.23733 | 0.2383
MK-Mackay Area | 340_MK3-1 Farleigh 33 kV | Loading (MW) | 0.0042898 | 0.0043179 | 0.0043408 | 0.0043606 | 0.0043785
MK-Mackay Area | 340_MK3-1 Farleigh 33 kV | Power Factor | 0.018374 | 0.018374 | 0.018374 | 0.018374 | 0.018374
MK-Mackay Area | 340_MK3-1 Farleigh 33 kV | Rating (A) | 172 | 172 | 172 | 172 | 172
MK-Mackay Area | 340_MK3-1 Farleigh 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK-Mackay Area | 340_MK3-1 Farleigh 33 kV | Min Voltage at Constrained Conductor | 34.5604 | 34.673 | 34.7652 | 34.8441 | 34.9156
MK-Mackay Area | 340_MK3-1 Farleigh 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
MK-Mackay Area | 341_Tennyson St No 2 33 kV | % of Rated A | 15.42% | 13.96% | 12.84% | 11.97% | 11.36%
MK-Mackay Area | 341_Tennyson St No 2 33 kV | Limiting Line Name | TR_CABLE 253_1 | TR_CABLE 253_1 | TR_CABLE 253_1 | TR_CABLE 253_1 | TR_CABLE 253_1
MK-Mackay Area | 341_Tennyson St No 2 33 kV | Loading (A) | 53.9838 | 48.8504 | 44.9242 | 41.8904 | 39.7594
MK-Mackay Area | 341_Tennyson St No 2 33 kV | Loading (MVA) | 3.2065 | 2.905 | 2.674 | 2.4953 | 2.3699
MK-Mackay Area | 341_Tennyson St No 2 33 kV | Loading (MW) | 2.1335 | 1.66 | 1.2348 | 0.82064 | 0.3939
MK-Mackay Area | 341_Tennyson St No 2 33 kV | Power Factor | 0.66537 | 0.57141 | 0.46176 | 0.32887 | 0.16621
MK-Mackay Area | 341_Tennyson St No 2 33 kV | Rating (A) | 350 | 350 | 350 | 350 | 350
MK-Mackay Area | 341_Tennyson St No 2 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK-Mackay Area | 341_Tennyson St No 2 33 kV | Min Voltage at Constrained Conductor | 34.2933 | 34.3337 | 34.3655 | 34.3915 | 34.4131
MK-Mackay Area | 341_Tennyson St No 2 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
MK-Mackay Area | 342_South Mackay 33 kV | % of Rated A | 55.05% | 54.96% | 55.88% | 57.71% | 60.42%
MK-Mackay Area | 342_South Mackay 33 kV | Limiting Line Name | TR_LINE 12122806_1 | TR_LINE 12122806_1 | TR_LINE 12122806_1 | TR_LINE 12122806_1 | TR_LINE 12122806_1
MK-Mackay Area | 342_South Mackay 33 kV | Loading (A) | 186.0743 | 185.7485 | 188.8865 | 195.0438 | 204.2205
MK-Mackay Area | 342_South Mackay 33 kV | Loading (MVA) | 11.0551 | 11.049 | 11.2462 | 11.6218 | 12.1765
MK-Mackay Area | 342_South Mackay 33 kV | Loading (MW) | 1.248 | 0.40677 | 1.9774 | 3.5152 | 5.0916
MK-Mackay Area | 342_South Mackay 33 kV | Power Factor | 0.11277 | 0.03671 | 0.17576 | 0.30244 | 0.41815
MK-Mackay Area | 342_South Mackay 33 kV | Rating (A) | 338 | 338 | 338 | 338 | 338
MK-Mackay Area | 342_South Mackay 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK-Mackay Area | 342_South Mackay 33 kV | Min Voltage at Constrained Conductor | 34.2933 | 34.3337 | 34.3655 | 34.3915 | 34.4131
MK-Mackay Area | 342_South Mackay 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
MK-Mackay Area | 343_Pleystowe 33 kV | % of Rated A | 7.938% | 10.46% | 12.62% | 14.53% | 16.34%
MK-Mackay Area | 343_Pleystowe 33 kV | Limiting Line Name | TR_LINE 114413_2 | TR_LINE 114413_2 | TR_LINE 114413_2 | TR_LINE 114413_2 | TR_LINE 114413_2
MK-Mackay Area | 343_Pleystowe 33 kV | Loading (A) | 17.4641 | 23.0212 | 27.7631 | 31.9609 | 35.9437
MK-Mackay Area | 343_Pleystowe 33 kV | Loading (MVA) | 1.0373 | 1.369 | 1.6525 | 1.9039 | 2.1425
MK-Mackay Area | 343_Pleystowe 33 kV | Loading (MW) | 0.99121 | 1.3362 | 1.6271 | 1.8833 | 2.1256
MK-Mackay Area | 343_Pleystowe 33 kV | Power Factor | 0.95552 | 0.97599 | 0.98456 | 0.98918 | 0.99211
MK-Mackay Area | 343_Pleystowe 33 kV | Rating (A) | 220 | 220 | 220 | 220 | 220
MK-Mackay Area | 343_Pleystowe 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK-Mackay Area | 343_Pleystowe 33 kV | Min Voltage at Constrained Conductor | 34.2933 | 34.3337 | 34.3655 | 34.3915 | 34.4131
MK-Mackay Area | 343_Pleystowe 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
MK-Mackay Area | 344_West Mackay 2 33 kV | % of Rated A | 4.31% | 3.528% | 2.881% | 2.313% | 1.793%
MK-Mackay Area | 344_West Mackay 2 33 kV | Limiting Line Name | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1 | TR_CABLE 19_1
MK-Mackay Area | 344_West Mackay 2 33 kV | Loading (A) | 26.936 | 22.053 | 18.0079 | 14.4536 | 11.2072
MK-Mackay Area | 344_West Mackay 2 33 kV | Loading (MVA) | 1.5999 | 1.3114 | 1.0719 | 0.86097 | 0.66801
MK-Mackay Area | 344_West Mackay 2 33 kV | Loading (MW) | 1.5997 | 1.3111 | 1.0713 | 0.86012 | 0.66679
MK-Mackay Area | 344_West Mackay 2 33 kV | Power Factor | 0.99987 | 0.99971 | 0.99945 | 0.99901 | 0.99818
MK-Mackay Area | 344_West Mackay 2 33 kV | Rating (A) | 625 | 625 | 625 | 625 | 625
MK-Mackay Area | 344_West Mackay 2 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK-Mackay Area | 344_West Mackay 2 33 kV | Min Voltage at Constrained Conductor | 34.2923 | 34.3329 | 34.3649 | 34.391 | 34.4127
MK-Mackay Area | 344_West Mackay 2 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
MK-Mackay Area | 346_Ritchies Rd 33 kV | % of Rated A | 5.907% | 7.798% | 9.409% | 10.84% | 12.19%
MK-Mackay Area | 346_Ritchies Rd 33 kV | Limiting Line Name | TR_LINE 11501_1 | TR_LINE 11501_1 | TR_LINE 11501_1 | TR_LINE 11501_1 | TR_LINE 11501_1
MK-Mackay Area | 346_Ritchies Rd 33 kV | Loading (A) | 12.9945 | 17.1545 | 20.7005 | 23.8379 | 26.8138
MK-Mackay Area | 346_Ritchies Rd 33 kV | Loading (MVA) | 0.77184 | 1.0201 | 1.2322 | 1.42 | 1.5983
MK-Mackay Area | 346_Ritchies Rd 33 kV | Loading (MW) | 0.74083 | 0.99827 | 1.2153 | 1.4065 | 1.5874
MK-Mackay Area | 346_Ritchies Rd 33 kV | Power Factor | 0.9598 | 0.97853 | 0.98632 | 0.9905 | 0.99315
MK-Mackay Area | 346_Ritchies Rd 33 kV | Rating (A) | 220 | 220 | 220 | 220 | 220
MK-Mackay Area | 346_Ritchies Rd 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK-Mackay Area | 346_Ritchies Rd 33 kV | Min Voltage at Constrained Conductor | 34.2933 | 34.3337 | 34.3655 | 34.3915 | 34.4131
MK-Mackay Area | 346_Ritchies Rd 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
MK-Mackay Area | 347_Mt Bassett 33 kV | % of Rated A | 1.418% | 2.429% | 5.763% | 9.156% | 12.84%
MK-Mackay Area | 347_Mt Bassett 33 kV | Limiting Line Name | TR_CABLE 22_1 | TR_CABLE 22_1 | TR_CABLE 4883_1 | TR_CABLE 4883_1 | TR_CABLE 4883_1
MK-Mackay Area | 347_Mt Bassett 33 kV | Loading (A) | 3.6165 | 6.1934 | 14.6964 | 23.3477 | 32.7504
MK-Mackay Area | 347_Mt Bassett 33 kV | Loading (MVA) | 0.2148 | 0.36833 | 0.87501 | 1.3913 | 1.9532
MK-Mackay Area | 347_Mt Bassett 33 kV | Loading (MW) | 0.18543 | 0.3569 | 0.87097 | 1.3871 | 1.9483
MK-Mackay Area | 347_Mt Bassett 33 kV | Power Factor | 0.86326 | 0.96856 | 0.99538 | 0.99698 | 0.99749
MK-Mackay Area | 347_Mt Bassett 33 kV | Rating (A) | 255 | 255 | 255 | 255 | 255
MK-Mackay Area | 347_Mt Bassett 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK-Mackay Area | 347_Mt Bassett 33 kV | Min Voltage at Constrained Conductor | 34.2921 | 34.336 | 34.3746 | 34.4055 | 34.4322
MK-Mackay Area | 347_Mt Bassett 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
MK-Mackay Area | 348_Farleigh 33 kV | % of Rated A | 5.633% | 7.678% | 9.456% | 11.05% | 12.59%
MK-Mackay Area | 348_Farleigh 33 kV | Limiting Line Name | TR_LINE 13162_1 | TR_LINE 13162_1 | TR_LINE 13162_1 | TR_LINE 13162_1 | TR_LINE 13162_1
MK-Mackay Area | 348_Farleigh 33 kV | Loading (A) | 10.9287 | 14.8962 | 18.3446 | 21.4459 | 24.4313
MK-Mackay Area | 348_Farleigh 33 kV | Loading (MVA) | 0.6525 | 0.8916 | 1.1002 | 1.2884 | 1.4701
MK-Mackay Area | 348_Farleigh 33 kV | Loading (MW) | 0.596 | 0.85236 | 1.0699 | 1.2639 | 1.4497
MK-Mackay Area | 348_Farleigh 33 kV | Power Factor | 0.91338 | 0.95596 | 0.97239 | 0.9809 | 0.98613
MK-Mackay Area | 348_Farleigh 33 kV | Rating (A) | 194 | 194 | 194 | 194 | 194
MK-Mackay Area | 348_Farleigh 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK-Mackay Area | 348_Farleigh 33 kV | Min Voltage at Constrained Conductor | 34.4705 | 34.5568 | 34.6268 | 34.6862 | 34.7391
MK-Mackay Area | 348_Farleigh 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
MK-Mackay Area | 349_Pioneer Valley - Pinnacle 66 kV | % of Rated A | 8.211% | 10.83% | 13.16% | 15.3% | 17.44%
MK-Mackay Area | 349_Pioneer Valley - Pinnacle 66 kV | Limiting Line Name | TR_LINE 9352_1 | TR_LINE 9352_1 | TR_LINE 9352_1 | TR_LINE 9352_1 | TR_LINE 9352_1
MK-Mackay Area | 349_Pioneer Valley - Pinnacle 66 kV | Loading (A) | 13.7941 | 18.1978 | 22.1142 | 25.6989 | 29.2952
MK-Mackay Area | 349_Pioneer Valley - Pinnacle 66 kV | Loading (MVA) | 1.6671 | 2.2017 | 2.6777 | 3.1135 | 3.5504
MK-Mackay Area | 349_Pioneer Valley - Pinnacle 66 kV | Loading (MW) | 1.6666 | 2.2016 | 2.6777 | 3.1133 | 3.5498
MK-Mackay Area | 349_Pioneer Valley - Pinnacle 66 kV | Power Factor | 0.99973 | 0.99997 | 1 | 0.99995 | 0.99985
MK-Mackay Area | 349_Pioneer Valley - Pinnacle 66 kV | Rating (A) | 168 | 168 | 168 | 168 | 168
MK-Mackay Area | 349_Pioneer Valley - Pinnacle 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK-Mackay Area | 349_Pioneer Valley - Pinnacle 66 kV | Min Voltage at Constrained Conductor | 69.7746 | 69.8519 | 69.9072 | 69.9457 | 69.9695
MK-Mackay Area | 349_Pioneer Valley - Pinnacle 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
MK-Mackay Area | 351_Alligator Creek 33 kV | % of Rated A | 0.2409% | 2.292% | 4.696% | 7.239% | 10.04%
MK-Mackay Area | 351_Alligator Creek 33 kV | Limiting Line Name | TR_LINE 66244_3 | TR_LINE 93922_3 | TR_LINE 93922_3 | TR_CABLE 7120_1 | TR_CABLE 7120_1
MK-Mackay Area | 351_Alligator Creek 33 kV | Loading (A) | 0.6144 | 5.3638 | 10.9879 | 16.9394 | 23.4829
MK-Mackay Area | 351_Alligator Creek 33 kV | Loading (MVA) | 0.037004 | 0.32379 | 0.6646 | 1.027 | 1.4264
MK-Mackay Area | 351_Alligator Creek 33 kV | Loading (MW) | 0.0026229 | 0.32261 | 0.66421 | 1.027 | 1.4262
MK-Mackay Area | 351_Alligator Creek 33 kV | Power Factor | 0.070883 | 0.99635 | 0.9994 | 0.99991 | 0.99983
MK-Mackay Area | 351_Alligator Creek 33 kV | Rating (A) | 255 | 234 | 234 | 234 | 234
MK-Mackay Area | 351_Alligator Creek 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK-Mackay Area | 351_Alligator Creek 33 kV | Min Voltage at Constrained Conductor | 34.7723 | 34.8524 | 34.9206 | 35.005 | 35.07
MK-Mackay Area | 351_Alligator Creek 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
MK-Mackay Area | 360_Pinnacle-Crediton/Eungella Dam 66 kV | % of Rated A | 9.563% | 9.272% | 9.016% | 8.786% | 8.565%
MK-Mackay Area | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Limiting Line Name | TR_LINE 10229_1 | TR_LINE 10229_1 | TR_LINE 10229_1 | TR_LINE 10229_1 | TR_LINE 10229_1
MK-Mackay Area | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Loading (A) | 8.798 | 8.5307 | 8.2949 | 8.0836 | 7.88
MK-Mackay Area | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Loading (MVA) | 1.0656 | 1.0346 | 1.0071 | 0.98224 | 0.95805
MK-Mackay Area | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Loading (MW) | 0.88069 | 0.84167 | 0.80665 | 0.77478 | 0.74362
MK-Mackay Area | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Power Factor | 0.82651 | 0.81348 | 0.80095 | 0.78879 | 0.77618
MK-Mackay Area | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Rating (A) | 92 | 92 | 92 | 92 | 92
MK-Mackay Area | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK-Mackay Area | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Min Voltage at Constrained Conductor | 69.9242 | 70.0239 | 70.0983 | 70.1535 | 70.1932
MK-Mackay Area | 360_Pinnacle-Crediton/Eungella Dam 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
MK-Mackay Area | 364_West Mackay No 1 33 kV | % of Rated A | 9.283% | 7.598% | 6.202% | 4.974% | 3.853%
MK-Mackay Area | 364_West Mackay No 1 33 kV | Limiting Line Name | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1 | TR_LINE 11243_1
MK-Mackay Area | 364_West Mackay No 1 33 kV | Loading (A) | 26.9203 | 22.0335 | 17.9844 | 14.4253 | 11.1726
MK-Mackay Area | 364_West Mackay No 1 33 kV | Loading (MVA) | 1.5989 | 1.3102 | 1.0704 | 0.85926 | 0.66593
MK-Mackay Area | 364_West Mackay No 1 33 kV | Loading (MW) | 1.5988 | 1.3102 | 1.0704 | 0.85925 | 0.66592
MK-Mackay Area | 364_West Mackay No 1 33 kV | Power Factor | 0.99995 | 0.99996 | 0.99998 | 0.99998 | 0.99999
MK-Mackay Area | 364_West Mackay No 1 33 kV | Rating (A) | 290 | 290 | 290 | 290 | 290
MK-Mackay Area | 364_West Mackay No 1 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK-Mackay Area | 364_West Mackay No 1 33 kV | Min Voltage at Constrained Conductor | 34.2911 | 34.3319 | 34.3641 | 34.3904 | 34.4122
MK-Mackay Area | 364_West Mackay No 1 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
MK-Mackay Area | 365_Tennyson St No 1 33 kV | % of Rated A | 1.927% | 1.734% | 1.588% | 1.479% | 1.406%
MK-Mackay Area | 365_Tennyson St No 1 33 kV | Limiting Line Name | TR_CABLE 7286_1 | TR_CABLE 7286_1 | TR_CABLE 7286_1 | TR_CABLE 7286_1 | TR_CABLE 7286_1
MK-Mackay Area | 365_Tennyson St No 1 33 kV | Loading (A) | 12.8172 | 11.5331 | 10.5634 | 9.8335 | 9.3531
MK-Mackay Area | 365_Tennyson St No 1 33 kV | Loading (MVA) | 0.76131 | 0.68585 | 0.62876 | 0.58576 | 0.55749
MK-Mackay Area | 365_Tennyson St No 1 33 kV | Loading (MW) | 0.71515 | 0.60935 | 0.51395 | 0.42064 | 0.32405
MK-Mackay Area | 365_Tennyson St No 1 33 kV | Power Factor | 0.93937 | 0.88847 | 0.81741 | 0.71811 | 0.58126
MK-Mackay Area | 365_Tennyson St No 1 33 kV | Rating (A) | 665 | 665 | 665 | 665 | 665
MK-Mackay Area | 365_Tennyson St No 1 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK-Mackay Area | 365_Tennyson St No 1 33 kV | Min Voltage at Constrained Conductor | 34.2932 | 34.3336 | 34.3655 | 34.3915 | 34.4131
MK-Mackay Area | 365_Tennyson St No 1 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
MK-Mackay Area | 367_Pioneer Valley - Greenmount 66 kV | % of Rated A | 0.0649% | 0.06494% | 0.06497% | 0.06498% | 0.06498%
MK-Mackay Area | 367_Pioneer Valley - Greenmount 66 kV | Limiting Line Name | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1 | TR_LINE 9264_1
MK-Mackay Area | 367_Pioneer Valley - Greenmount 66 kV | Loading (A) | 0.16354 | 0.16365 | 0.16372 | 0.16375 | 0.16376
MK-Mackay Area | 367_Pioneer Valley - Greenmount 66 kV | Loading (MVA) | 0.019725 | 0.019752 | 0.019769 | 0.019777 | 0.019777
MK-Mackay Area | 367_Pioneer Valley - Greenmount 66 kV | Loading (MW) | 8.0369e-08 | 8.0432e-08 | 8.0488e-08 | 8.0532e-08 | 8.0574e-08
MK-Mackay Area | 367_Pioneer Valley - Greenmount 66 kV | Power Factor | 4.0744e-06 | 4.0721e-06 | 4.0715e-06 | 4.072e-06 | 4.0741e-06
MK-Mackay Area | 367_Pioneer Valley - Greenmount 66 kV | Rating (A) | 252 | 252 | 252 | 252 | 252
MK-Mackay Area | 367_Pioneer Valley - Greenmount 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK-Mackay Area | 367_Pioneer Valley - Greenmount 66 kV | Min Voltage at Constrained Conductor | 69.6368 | 69.684 | 69.7129 | 69.7278 | 69.7284
MK-Mackay Area | 367_Pioneer Valley - Greenmount 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
MK-Mackay Area | 372_Pioneer Valley-McKinley Creek 33 kV | % of Rated A | 2.732% | 3.437% | 4.042% | 4.592% | 5.123%
MK-Mackay Area | 372_Pioneer Valley-McKinley Creek 33 kV | Limiting Line Name | TR_LINE 9963_1 | TR_LINE 9963_1 | TR_LINE 9963_1 | TR_LINE 9963_1 | TR_LINE 9963_1
MK-Mackay Area | 372_Pioneer Valley-McKinley Creek 33 kV | Loading (A) | 5.3279 | 6.7026 | 7.8811 | 8.954 | 9.9895
MK-Mackay Area | 372_Pioneer Valley-McKinley Creek 33 kV | Loading (MVA) | 0.64292 | 0.80942 | 0.95221 | 1.0821 | 1.2073
MK-Mackay Area | 372_Pioneer Valley-McKinley Creek 33 kV | Loading (MW) | 0.62897 | 0.79877 | 0.94354 | 1.0749 | 1.2012
MK-Mackay Area | 372_Pioneer Valley-McKinley Creek 33 kV | Power Factor | 0.97813 | 0.98663 | 0.99064 | 0.993 | 0.99459
MK-Mackay Area | 372_Pioneer Valley-McKinley Creek 33 kV | Rating (A) | 195 | 195 | 195 | 195 | 195
MK-Mackay Area | 372_Pioneer Valley-McKinley Creek 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK-Mackay Area | 372_Pioneer Valley-McKinley Creek 33 kV | Min Voltage at Constrained Conductor | 69.6698 | 69.7225 | 69.7562 | 69.7754 | 69.78
MK-Mackay Area | 372_Pioneer Valley-McKinley Creek 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
MK-Mackay Area | 387_Mackay-Alfred Street 1 33 kV | % of Rated A | 23.68% | 22.55% | 21.64% | 20.86% | 20.15%
MK-Mackay Area | 387_Mackay-Alfred Street 1 33 kV | Limiting Line Name | TR_CABLE 2967_1 | TR_CABLE 2967_1 | TR_CABLE 2967_1 | TR_CABLE 2967_1 | TR_CABLE 2967_1
MK-Mackay Area | 387_Mackay-Alfred Street 1 33 kV | Loading (A) | 102.0438 | 97.1853 | 93.2823 | 89.8956 | 86.8642
MK-Mackay Area | 387_Mackay-Alfred Street 1 33 kV | Loading (MVA) | 6.0612 | 5.7794 | 5.5524 | 5.3549 | 5.1776
MK-Mackay Area | 387_Mackay-Alfred Street 1 33 kV | Loading (MW) | 3.7168 | 3.2363 | 2.8178 | 2.4216 | 2.0306
MK-Mackay Area | 387_Mackay-Alfred Street 1 33 kV | Power Factor | 0.61322 | 0.55997 | 0.5075 | 0.45223 | 0.39219
MK-Mackay Area | 387_Mackay-Alfred Street 1 33 kV | Rating (A) | 431 | 431 | 431 | 431 | 431
MK-Mackay Area | 387_Mackay-Alfred Street 1 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK-Mackay Area | 387_Mackay-Alfred Street 1 33 kV | Min Voltage at Constrained Conductor | 34.2933 | 34.3337 | 34.3655 | 34.3915 | 34.4131
MK-Mackay Area | 387_Mackay-Alfred Street 1 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
MK-Mackay Area | 395_Tennyson Street-Alfred Street 33 kV | % of Rated A | 4.604% | 5.135% | 5.841% | 6.696% | 7.731%
MK-Mackay Area | 395_Tennyson Street-Alfred Street 33 kV | Limiting Line Name | TR_CABLE 2960_1 | TR_CABLE 2960_1 | TR_CABLE 2960_1 | TR_CABLE 2960_1 | TR_CABLE 2960_1
MK-Mackay Area | 395_Tennyson Street-Alfred Street 33 kV | Loading (A) | 30.9365 | 34.5048 | 39.254 | 44.9994 | 51.95
MK-Mackay Area | 395_Tennyson Street-Alfred Street 33 kV | Loading (MVA) | 1.8375 | 2.0521 | 2.3369 | 2.6812 | 3.0975
MK-Mackay Area | 395_Tennyson Street-Alfred Street 33 kV | Loading (MW) | 0.38903 | 0.89197 | 1.3646 | 1.8434 | 2.3648
MK-Mackay Area | 395_Tennyson Street-Alfred Street 33 kV | Power Factor | 0.21172 | 0.43467 | 0.58396 | 0.68754 | 0.76345
MK-Mackay Area | 395_Tennyson Street-Alfred Street 33 kV | Rating (A) | 672 | 672 | 672 | 672 | 672
MK-Mackay Area | 395_Tennyson Street-Alfred Street 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK-Mackay Area | 395_Tennyson Street-Alfred Street 33 kV | Min Voltage at Constrained Conductor | 34.2922 | 34.336 | 34.3709 | 34.3993 | 34.4226
MK-Mackay Area | 395_Tennyson Street-Alfred Street 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
MK-Mackay Area | 422_North Mackay No 1 33 kV | % of Rated A | 23.1% | 30.08% | 36.87% | 43.24% | 49.72%
MK-Mackay Area | 422_North Mackay No 1 33 kV | Limiting Line Name | TR_LINE 97201_1 | TR_LINE 97201_1 | TR_LINE 11650_2 | TR_LINE 11650_2 | TR_LINE 11650_2
MK-Mackay Area | 422_North Mackay No 1 33 kV | Loading (A) | 144.3563 | 187.9977 | 135.2985 | 158.6834 | 182.4631
MK-Mackay Area | 422_North Mackay No 1 33 kV | Loading (MVA) | 8.6639 | 11.301 | 8.2302 | 9.6754 | 11.147
MK-Mackay Area | 422_North Mackay No 1 33 kV | Loading (MW) | 7.5949 | 10.5562 | 8.227 | 9.6702 | 11.1392
MK-Mackay Area | 422_North Mackay No 1 33 kV | Power Factor | 0.87662 | 0.9341 | 0.99961 | 0.99946 | 0.99929
MK-Mackay Area | 422_North Mackay No 1 33 kV | Rating (A) | 625 | 625 | 367 | 367 | 367
MK-Mackay Area | 422_North Mackay No 1 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK-Mackay Area | 422_North Mackay No 1 33 kV | Min Voltage at Constrained Conductor | 34.6467 | 34.7007 | 35.118 | 35.2003 | 35.2685
MK-Mackay Area | 422_North Mackay No 1 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
MK-Mackay Area | 423_North Mackay No 2 33 kV | % of Rated A | 13.93% | 15.82% | 17.92% | 20.24% | 22.92%
MK-Mackay Area | 423_North Mackay No 2 33 kV | Limiting Line Name | TR_CABLE 6563_1 | TR_CABLE 6563_1 | TR_CABLE 6563_1 | TR_CABLE 6563_1 | TR_CABLE 6563_1
MK-Mackay Area | 423_North Mackay No 2 33 kV | Loading (A) | 85.2395 | 96.8385 | 109.6807 | 123.8394 | 140.2788
MK-Mackay Area | 423_North Mackay No 2 33 kV | Loading (MVA) | 5.1126 | 5.8176 | 6.5968 | 7.4546 | 8.4486
MK-Mackay Area | 423_North Mackay No 2 33 kV | Loading (MW) | 2.8265 | 3.9863 | 5.087 | 6.1942 | 7.4019
MK-Mackay Area | 423_North Mackay No 2 33 kV | Power Factor | 0.55282 | 0.68519 | 0.77111 | 0.8309 | 0.87608
MK-Mackay Area | 423_North Mackay No 2 33 kV | Rating (A) | 612 | 612 | 612 | 612 | 612
MK-Mackay Area | 423_North Mackay No 2 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK-Mackay Area | 423_North Mackay No 2 33 kV | Min Voltage at Constrained Conductor | 34.6289 | 34.6846 | 34.7249 | 34.7539 | 34.7723
MK-Mackay Area | 423_North Mackay No 2 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
MK-Mackay Area | 430_Mackay-Alfred Street 2 33 kV | % of Rated A | 17.16% | 16.35% | 15.69% | 15.13% | 14.62%
MK-Mackay Area | 430_Mackay-Alfred Street 2 33 kV | Limiting Line Name | TR_CABLE 8887_1 | TR_CABLE 8887_1 | TR_CABLE 8887_1 | TR_CABLE 8887_1 | TR_CABLE 8887_1
MK-Mackay Area | 430_Mackay-Alfred Street 2 33 kV | Loading (A) | 99.3632 | 94.6508 | 90.8657 | 87.5816 | 84.6422
MK-Mackay Area | 430_Mackay-Alfred Street 2 33 kV | Loading (MVA) | 5.9019 | 5.6287 | 5.4086 | 5.2171 | 5.0451
MK-Mackay Area | 430_Mackay-Alfred Street 2 33 kV | Loading (MW) | 3.6125 | 3.1455 | 2.7388 | 2.3538 | 1.9737
MK-Mackay Area | 430_Mackay-Alfred Street 2 33 kV | Power Factor | 0.61208 | 0.55883 | 0.50638 | 0.45117 | 0.39122
MK-Mackay Area | 430_Mackay-Alfred Street 2 33 kV | Rating (A) | 579 | 579 | 579 | 579 | 579
MK-Mackay Area | 430_Mackay-Alfred Street 2 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK-Mackay Area | 430_Mackay-Alfred Street 2 33 kV | Min Voltage at Constrained Conductor | 34.2933 | 34.3337 | 34.3655 | 34.3915 | 34.4131
MK-Mackay Area | 430_Mackay-Alfred Street 2 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
MK-Mackay Area | PV 6/4_Glenella No 2 66 kV | % of Rated A | 4.996% | 5.981% | 7.715% | 9.777% | 12.14%
MK-Mackay Area | PV 6/4_Glenella No 2 66 kV | Limiting Line Name | TR_LINE 105536_1 | TR_LINE 105536_1 | TR_LINE 105536_1 | TR_LINE 105536_1 | TR_LINE 105536_1
MK-Mackay Area | PV 6/4_Glenella No 2 66 kV | Loading (A) | 40.4159 | 48.3879 | 62.4141 | 79.0993 | 98.1963
MK-Mackay Area | PV 6/4_Glenella No 2 66 kV | Loading (MVA) | 4.8747 | 5.8402 | 7.5363 | 9.553 | 11.8595
MK-Mackay Area | PV 6/4_Glenella No 2 66 kV | Loading (MW) | 0.81902 | 3.5539 | 6.1158 | 8.6219 | 11.2561
MK-Mackay Area | PV 6/4_Glenella No 2 66 kV | Power Factor | 0.16801 | 0.60852 | 0.81151 | 0.90253 | 0.94912
MK-Mackay Area | PV 6/4_Glenella No 2 66 kV | Rating (A) | 809 | 809 | 809 | 809 | 809
MK-Mackay Area | PV 6/4_Glenella No 2 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK-Mackay Area | PV 6/4_Glenella No 2 66 kV | Min Voltage at Constrained Conductor | 69.6368 | 69.684 | 69.7129 | 69.7278 | 69.7284
MK-Mackay Area | PV 6/4_Glenella No 2 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
MK-Mackay Area | PV 6/5_Glenella No 1 66 kV | % of Rated A | 11.14% | 13.6% | 15.97% | 18.33% | 20.85%
MK-Mackay Area | PV 6/5_Glenella No 1 66 kV | Limiting Line Name | TR_LINE 105066_1 | TR_LINE 105066_1 | TR_LINE 105066_1 | TR_LINE 105066_1 | TR_LINE 105066_1
MK-Mackay Area | PV 6/5_Glenella No 1 66 kV | Loading (A) | 90.0897 | 109.9836 | 129.1756 | 148.304 | 168.6961
MK-Mackay Area | PV 6/5_Glenella No 1 66 kV | Loading (MVA) | 10.9304 | 13.3627 | 15.7104 | 18.0497 | 20.541
MK-Mackay Area | PV 6/5_Glenella No 1 66 kV | Loading (MW) | 9.8881 | 12.5829 | 15.1116 | 17.5893 | 20.1981
MK-Mackay Area | PV 6/5_Glenella No 1 66 kV | Power Factor | 0.90463 | 0.94164 | 0.96189 | 0.97449 | 0.98331
MK-Mackay Area | PV 6/5_Glenella No 1 66 kV | Rating (A) | 809 | 809 | 809 | 809 | 809
MK-Mackay Area | PV 6/5_Glenella No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK-Mackay Area | PV 6/5_Glenella No 1 66 kV | Min Voltage at Constrained Conductor | 70.049 | 70.146 | 70.2161 | 70.2662 | 70.2981
MK-Mackay Area | PV 6/5_Glenella No 1 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
MK-Moranbah | 6328_Broadlea - Moorvale 66 kV | % of Rated A | 5.41% | 5.41% | 5.411% | 5.412% | 5.418%
MK-Moranbah | 6328_Broadlea - Moorvale 66 kV | Limiting Line Name | TR_LINE 36093_1 | TR_LINE 36093_1 | TR_LINE 36093_1 | TR_LINE 36093_1 | TR_LINE 36093_1
MK-Moranbah | 6328_Broadlea - Moorvale 66 kV | Loading (A) | 20.8841 | 20.8815 | 20.8851 | 20.8913 | 20.9135
MK-Moranbah | 6328_Broadlea - Moorvale 66 kV | Loading (MVA) | 2.5038 | 2.5035 | 2.5039 | 2.5047 | 2.5073
MK-Moranbah | 6328_Broadlea - Moorvale 66 kV | Loading (MW) | 2.5033 | 2.503 | 2.5035 | 2.5042 | 2.5069
MK-Moranbah | 6328_Broadlea - Moorvale 66 kV | Power Factor | 0.9998 | 0.9998 | 0.9998 | 0.9998 | 0.9998
MK-Moranbah | 6328_Broadlea - Moorvale 66 kV | Rating (A) | 386 | 386 | 386 | 386 | 386
MK-Moranbah | 6328_Broadlea - Moorvale 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK-Moranbah | 6328_Broadlea - Moorvale 66 kV | Min Voltage at Constrained Conductor | 69.2195 | 69.2195 | 69.2195 | 69.2194 | 69.2193
MK-Moranbah | 6328_Broadlea - Moorvale 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
MK-Moranbah | 6330 Broadlea - Millennium 66 kV | % of Rated A | 39.43% | 39.43% | 39.43% | 39.43% | 39.43%
MK-Moranbah | 6330 Broadlea - Millennium 66 kV | Limiting Line Name | TR_LINE 63688_1 | TR_LINE 63688_1 | TR_LINE 63688_1 | TR_LINE 63688_1 | TR_LINE 63688_1
MK-Moranbah | 6330 Broadlea - Millennium 66 kV | Loading (A) | 277.9832 | 277.9832 | 277.9832 | 277.9833 | 277.9835
MK-Moranbah | 6330 Broadlea - Millennium 66 kV | Loading (MVA) | 33.3516 | 33.3516 | 33.3516 | 33.3516 | 33.3516
MK-Moranbah | 6330 Broadlea - Millennium 66 kV | Loading (MW) | 33.3514 | 33.3514 | 33.3514 | 33.3514 | 33.3514
MK-Moranbah | 6330 Broadlea - Millennium 66 kV | Power Factor | 1 | 1 | 1 | 1 | 1
MK-Moranbah | 6330 Broadlea - Millennium 66 kV | Rating (A) | 705 | 705 | 705 | 705 | 705
MK-Moranbah | 6330 Broadlea - Millennium 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK-Moranbah | 6330 Broadlea - Millennium 66 kV | Min Voltage at Constrained Conductor | 69.2076 | 69.2076 | 69.2076 | 69.2076 | 69.2075
MK-Moranbah | 6330 Broadlea - Millennium 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
MK-Moranbah | 7366_Moranbah - Broadlea 132 kV | % of Rated A | 31.81% | 31.81% | 31.81% | 31.81% | 31.81%
MK-Moranbah | 7366_Moranbah - Broadlea 132 kV | Limiting Line Name | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1 | TR_LINE 140655_1
MK-Moranbah | 7366_Moranbah - Broadlea 132 kV | Loading (A) | 224.2411 | 224.2397 | 224.2415 | 224.2447 | 224.2559
MK-Moranbah | 7366_Moranbah - Broadlea 132 kV | Loading (MVA) | 53.8906 | 53.8903 | 53.8907 | 53.8915 | 53.8942
MK-Moranbah | 7366_Moranbah - Broadlea 132 kV | Loading (MW) | 53.8656 | 53.8653 | 53.8657 | 53.8665 | 53.8691
MK-Moranbah | 7366_Moranbah - Broadlea 132 kV | Power Factor | 0.99954 | 0.99954 | 0.99954 | 0.99954 | 0.99954
MK-Moranbah | 7366_Moranbah - Broadlea 132 kV | Rating (A) | 705 | 705 | 705 | 705 | 705
MK-Moranbah | 7366_Moranbah - Broadlea 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK-Moranbah | 7366_Moranbah - Broadlea 132 kV | Min Voltage at Constrained Conductor | 138.7478 | 138.7478 | 138.7478 | 138.7478 | 138.7477
MK-Moranbah | 7366_Moranbah - Broadlea 132 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
MK-Newlands | 232_Newlands-Glenden 66 kV | % of Rated A | 3.742% | 3.731% | 3.726% | 3.735% | 3.758%
MK-Newlands | 232_Newlands-Glenden 66 kV | Limiting Line Name | TR_LINE 10181_1 | TR_LINE 10181_1 | TR_LINE 10181_1 | TR_LINE 10181_1 | TR_LINE 10181_1
MK-Newlands | 232_Newlands-Glenden 66 kV | Loading (A) | 4.3412 | 4.3281 | 4.3222 | 4.3322 | 4.3592
MK-Newlands | 232_Newlands-Glenden 66 kV | Loading (MVA) | 0.51481 | 0.51328 | 0.51258 | 0.51378 | 0.51699
MK-Newlands | 232_Newlands-Glenden 66 kV | Loading (MW) | 0.42959 | 0.42773 | 0.42688 | 0.42832 | 0.43219
MK-Newlands | 232_Newlands-Glenden 66 kV | Power Factor | 0.83446 | 0.83333 | 0.8328 | 0.83366 | 0.83597
MK-Newlands | 232_Newlands-Glenden 66 kV | Rating (A) | 116 | 116 | 116 | 116 | 116
MK-Newlands | 232_Newlands-Glenden 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK-Newlands | 232_Newlands-Glenden 66 kV | Min Voltage at Constrained Conductor | 68.4664 | 68.4683 | 68.4697 | 68.4708 | 68.4717
MK-Newlands | 232_Newlands-Glenden 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
MK-Newlands | NL-WR-1_Newlands-Wirralie 1 66 kV | % of Rated A | 5.16% | 5.159% | 5.159% | 5.159% | 5.159%
MK-Newlands | NL-WR-1_Newlands-Wirralie 1 66 kV | Limiting Line Name | TR_LINE 180753_1 | TR_LINE 180753_1 | TR_LINE 180753_1 | TR_LINE 180753_1 | TR_LINE 180753_1
MK-Newlands | NL-WR-1_Newlands-Wirralie 1 66 kV | Loading (A) | 9.7011 | 9.6993 | 9.699 | 9.6991 | 9.6993
MK-Newlands | NL-WR-1_Newlands-Wirralie 1 66 kV | Loading (MVA) | 1.1504 | 1.1502 | 1.1502 | 1.1503 | 1.1503
MK-Newlands | NL-WR-1_Newlands-Wirralie 1 66 kV | Loading (MW) | 0.043394 | 0.026152 | 0.017319 | 0.013038 | 0.011228
MK-Newlands | NL-WR-1_Newlands-Wirralie 1 66 kV | Power Factor | 0.03772 | 0.022736 | 0.015057 | 0.011335 | 0.0097609
MK-Newlands | NL-WR-1_Newlands-Wirralie 1 66 kV | Rating (A) | 188 | 188 | 188 | 188 | 188
MK-Newlands | NL-WR-1_Newlands-Wirralie 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
MK-Newlands | NL-WR-1_Newlands-Wirralie 1 66 kV | Min Voltage at Constrained Conductor | 68.4664 | 68.4683 | 68.4697 | 68.4708 | 68.4717
MK-Newlands | NL-WR-1_Newlands-Wirralie 1 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Collinsville | 2031 Collinsville-PS-Collinsville 33 kV | % of Rated A | 24.83% | 23.99% | 23.21% | 22.48% | 21.72%
NQ-Collinsville | 2031 Collinsville-PS-Collinsville 33 kV | Limiting Line Name | TR_CABLE 4177_1 | TR_CABLE 4177_1 | TR_CABLE 4177_1 | TR_CABLE 4177_1 | TR_CABLE 4177_1
NQ-Collinsville | 2031 Collinsville-PS-Collinsville 33 kV | Loading (A) | 172.1 | 166.2297 | 160.8232 | 155.7746 | 150.515
NQ-Collinsville | 2031 Collinsville-PS-Collinsville 33 kV | Loading (MVA) | 10.3333 | 9.9858 | 9.6624 | 9.3582 | 9.0426
NQ-Collinsville | 2031 Collinsville-PS-Collinsville 33 kV | Loading (MW) | 10.3267 | 9.979 | 9.6554 | 9.3509 | 9.0351
NQ-Collinsville | 2031 Collinsville-PS-Collinsville 33 kV | Power Factor | 0.99937 | 0.99932 | 0.99928 | 0.99923 | 0.99917
NQ-Collinsville | 2031 Collinsville-PS-Collinsville 33 kV | Rating (A) | 693 | 693 | 693 | 693 | 693
NQ-Collinsville | 2031 Collinsville-PS-Collinsville 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Collinsville | 2031 Collinsville-PS-Collinsville 33 kV | Min Voltage at Constrained Conductor | 34.6602 | 34.6778 | 34.683 | 34.6796 | 34.6814
NQ-Collinsville | 2031 Collinsville-PS-Collinsville 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Collinsville | 3000 Collinsville No 1 33 kV | % of Rated A | 1.683e-07% | 1.612e-07% | 1.547e-07% | 1.486e-07% | 1.422e-07%
NQ-Collinsville | 3000 Collinsville No 1 33 kV | Limiting Line Name | Link_COLL_EB04Q02_COLLINSVILLE NO 1 | Link_COLL_EB04Q02_COLLINSVILLE NO 1 | Link_COLL_EB04Q02_COLLINSVILLE NO 1 | Link_COLL_EB04Q02_COLLINSVILLE NO 1 | Link_COLL_EB04Q02_COLLINSVILLE NO 1
NQ-Collinsville | 3000 Collinsville No 1 33 kV | Loading (A) | 8.4161e-06 | 8.0617e-06 | 7.7347e-06 | 7.429e-06 | 7.1108e-06
NQ-Collinsville | 3000 Collinsville No 1 33 kV | Loading (MVA) | 5.0525e-07 | 4.8421e-07 | 4.6465e-07 | 4.4624e-07 | 4.2714e-07
NQ-Collinsville | 3000 Collinsville No 1 33 kV | Loading (MW) | 5.0506e-07 | 4.8402e-07 | 4.6445e-07 | 4.4603e-07 | 4.2693e-07
NQ-Collinsville | 3000 Collinsville No 1 33 kV | Power Factor | 0.99964 | 0.9996 | 0.99957 | 0.99953 | 0.99949
NQ-Collinsville | 3000 Collinsville No 1 33 kV | Rating (A) | 5000 | 5000 | 5000 | 5000 | 5000
NQ-Collinsville | 3000 Collinsville No 1 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Collinsville | 3000 Collinsville No 1 33 kV | Min Voltage at Constrained Conductor | 34.6602 | 34.6778 | 34.683 | 34.6796 | 34.6814
NQ-Collinsville | 3000 Collinsville No 1 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Collinsville | 3001 Collinsville No 1 33 kV | % of Rated A | 2.165% | 2.164% | 2.164% | 2.164% | 2.164%
NQ-Collinsville | 3001 Collinsville No 1 33 kV | Limiting Line Name | Link_COLL_EB06Q02_COLLINSVILLE NO 3 | Link_COLL_EB06Q02_COLLINSVILLE NO 3 | Link_COLL_EB06Q02_COLLINSVILLE NO 3 | Link_COLL_EB06Q02_COLLINSVILLE NO 3 | Link_COLL_EB06Q02_COLLINSVILLE NO 3
NQ-Collinsville | 3001 Collinsville No 1 33 kV | Loading (A) | 108.2733 | 108.2185 | 108.202 | 108.2127 | 108.2073
NQ-Collinsville | 3001 Collinsville No 1 33 kV | Loading (MVA) | 6.5 | 6.5 | 6.5 | 6.5 | 6.5
NQ-Collinsville | 3001 Collinsville No 1 33 kV | Loading (MW) | 6.5 | 6.5 | 6.5 | 6.5 | 6.5
NQ-Collinsville | 3001 Collinsville No 1 33 kV | Power Factor | 1 | 1 | 1 | 1 | 1
NQ-Collinsville | 3001 Collinsville No 1 33 kV | Rating (A) | 5000 | 5000 | 5000 | 5000 | 5000
NQ-Collinsville | 3001 Collinsville No 1 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Collinsville | 3001 Collinsville No 1 33 kV | Min Voltage at Constrained Conductor | 34.6602 | 34.6778 | 34.683 | 34.6796 | 34.6814
NQ-Collinsville | 3001 Collinsville No 1 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Collinsville | 3218 Collinsville No 4 33 kV | % of Rated A | 1.683e-07% | 1.612e-07% | 1.547e-07% | 1.486e-07% | 1.422e-07%
NQ-Collinsville | 3218 Collinsville No 4 33 kV | Limiting Line Name | Link_COLL_EB02Q02_COLLINSVILLE NO 4 | Link_COLL_EB02Q02_COLLINSVILLE NO 4 | Link_COLL_EB02Q02_COLLINSVILLE NO 4 | Link_COLL_EB02Q02_COLLINSVILLE NO 4 | Link_COLL_EB02Q02_COLLINSVILLE NO 4
NQ-Collinsville | 3218 Collinsville No 4 33 kV | Loading (A) | 8.4161e-06 | 8.0617e-06 | 7.7347e-06 | 7.429e-06 | 7.1108e-06
NQ-Collinsville | 3218 Collinsville No 4 33 kV | Loading (MVA) | 5.0525e-07 | 4.8421e-07 | 4.6465e-07 | 4.4624e-07 | 4.2714e-07
NQ-Collinsville | 3218 Collinsville No 4 33 kV | Loading (MW) | 5.0506e-07 | 4.8402e-07 | 4.6445e-07 | 4.4603e-07 | 4.2693e-07
NQ-Collinsville | 3218 Collinsville No 4 33 kV | Power Factor | 0.99964 | 0.9996 | 0.99957 | 0.99953 | 0.99949
NQ-Collinsville | 3218 Collinsville No 4 33 kV | Rating (A) | 5000 | 5000 | 5000 | 5000 | 5000
NQ-Collinsville | 3218 Collinsville No 4 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Collinsville | 3218 Collinsville No 4 33 kV | Min Voltage at Constrained Conductor | 34.6602 | 34.6778 | 34.683 | 34.6796 | 34.6814
NQ-Collinsville | 3218 Collinsville No 4 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Collinsville | 7308_Stony Creek - Havilah 132 kV | % of Rated A | 1% | 1% | 1% | 1% | 0.9999%
NQ-Collinsville | 7308_Stony Creek - Havilah 132 kV | Limiting Line Name | TR_LINE 67629_1 | TR_LINE 67629_1 | TR_LINE 67629_1 | TR_LINE 67629_1 | TR_LINE 67629_1
NQ-Collinsville | 7308_Stony Creek - Havilah 132 kV | Loading (A) | 4.3715 | 4.3719 | 4.3713 | 4.3702 | 4.3694
NQ-Collinsville | 7308_Stony Creek - Havilah 132 kV | Loading (MVA) | 1.0647 | 1.0649 | 1.0645 | 1.0639 | 1.0634
NQ-Collinsville | 7308_Stony Creek - Havilah 132 kV | Loading (MW) | 0.39484 | 0.39484 | 0.39484 | 0.39484 | 0.39484
NQ-Collinsville | 7308_Stony Creek - Havilah 132 kV | Power Factor | 0.37086 | 0.37078 | 0.37091 | 0.37113 | 0.37129
NQ-Collinsville | 7308_Stony Creek - Havilah 132 kV | Rating (A) | 437 | 437 | 437 | 437 | 437
NQ-Collinsville | 7308_Stony Creek - Havilah 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Collinsville | 7308_Stony Creek - Havilah 132 kV | Min Voltage at Constrained Conductor | 140.6099 | 140.6267 | 140.5989 | 140.5494 | 140.5148
NQ-Collinsville | 7308_Stony Creek - Havilah 132 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Collinsville | 7309_Stony Creek - Fig Tree 132 kV | % of Rated A | 0.9554% | 0.9555% | 0.9553% | 0.955% | 0.9548%
NQ-Collinsville | 7309_Stony Creek - Fig Tree 132 kV | Limiting Line Name | TR_LINE 67630_1 | TR_LINE 67630_1 | TR_LINE 67630_1 | TR_LINE 67630_1 | TR_LINE 67630_1
NQ-Collinsville | 7309_Stony Creek - Fig Tree 132 kV | Loading (A) | 4.3184 | 4.3188 | 4.3181 | 4.3168 | 4.3159
NQ-Collinsville | 7309_Stony Creek - Fig Tree 132 kV | Loading (MVA) | 1.0517 | 1.0519 | 1.0516 | 1.0509 | 1.0504
NQ-Collinsville | 7309_Stony Creek - Fig Tree 132 kV | Loading (MW) | 0.29422 | 0.29422 | 0.29422 | 0.29422 | 0.29422
NQ-Collinsville | 7309_Stony Creek - Fig Tree 132 kV | Power Factor | 0.27975 | 0.27969 | 0.27979 | 0.27997 | 0.2801
NQ-Collinsville | 7309_Stony Creek - Fig Tree 132 kV | Rating (A) | 452 | 452 | 452 | 452 | 452
NQ-Collinsville | 7309_Stony Creek - Fig Tree 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Collinsville | 7309_Stony Creek - Fig Tree 132 kV | Min Voltage at Constrained Conductor | 140.6092 | 140.626 | 140.5983 | 140.5487 | 140.5141
NQ-Collinsville | 7309_Stony Creek - Fig Tree 132 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Collinsville | COLL-02 Collinsville No 2 (33 kV) | % of Rated A | 2.669% | 2.67% | 2.67% | 2.67% | 2.67%
NQ-Collinsville | COLL-02 Collinsville No 2 (33 kV) | Limiting Line Name | HV_LINE 2010332_1 | HV_LINE 2010332_1 | HV_LINE 2010332_1 | HV_LINE 2010332_1 | HV_LINE 2010332_1
NQ-Collinsville | COLL-02 Collinsville No 2 (33 kV) | Loading (A) | 5.2039 | 5.2065 | 5.2073 | 5.2068 | 5.2071
NQ-Collinsville | COLL-02 Collinsville No 2 (33 kV) | Loading (MVA) | 0.31243 | 0.31274 | 0.31284 | 0.31278 | 0.31281
NQ-Collinsville | COLL-02 Collinsville No 2 (33 kV) | Loading (MW) | 0.00051469 | 0.00051521 | 0.00051537 | 0.00051527 | 0.00051532
NQ-Collinsville | COLL-02 Collinsville No 2 (33 kV) | Power Factor | 0.0015748 | 0.0015748 | 0.0015748 | 0.0015748 | 0.0015748
NQ-Collinsville | COLL-02 Collinsville No 2 (33 kV) | Rating (A) | 195 | 195 | 195 | 195 | 195
NQ-Collinsville | COLL-02 Collinsville No 2 (33 kV) | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Collinsville | COLL-02 Collinsville No 2 (33 kV) | Min Voltage at Constrained Conductor | 34.6624 | 34.6799 | 34.6852 | 34.6818 | 34.6835
NQ-Collinsville | COLL-02 Collinsville No 2 (33 kV) | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Ingham | 6321_Lucinda 66 kV | % of Rated A | 1.381% | 1.416% | 1.463% | 1.517% | 1.568%
NQ-Ingham | 6321_Lucinda 66 kV | Limiting Line Name | TR_LINE 135526_1 | TR_LINE 135526_1 | TR_LINE 135526_1 | TR_LINE 135526_1 | TR_LINE 135526_1
NQ-Ingham | 6321_Lucinda 66 kV | Loading (A) | 2.7475 | 2.8181 | 2.9113 | 3.0189 | 3.1203
NQ-Ingham | 6321_Lucinda 66 kV | Loading (MVA) | 0.32592 | 0.33426 | 0.34479 | 0.35748 | 0.36942
NQ-Ingham | 6321_Lucinda 66 kV | Loading (MW) | 0.036401 | 0.083345 | 0.12115 | 0.15387 | 0.1802
NQ-Ingham | 6321_Lucinda 66 kV | Power Factor | 0.11169 | 0.24934 | 0.35137 | 0.43044 | 0.48779
NQ-Ingham | 6321_Lucinda 66 kV | Rating (A) | 199 | 199 | 199 | 199 | 199
NQ-Ingham | 6321_Lucinda 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Ingham | 6321_Lucinda 66 kV | Min Voltage at Constrained Conductor | 68.4856 | 68.4821 | 68.3767 | 68.3667 | 68.3529
NQ-Ingham | 6321_Lucinda 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Ingham | 6322 66kV VICTORIA SUGAR MILL FDR | % of Rated A | 1.198e-08% | 1.198e-08% | 1.196e-08% | 1.196e-08% | 1.196e-08%
NQ-Ingham | 6322 66kV VICTORIA SUGAR MILL FDR | Limiting Line Name | Line | Line | Line | Line | Line
NQ-Ingham | 6322 66kV VICTORIA SUGAR MILL FDR | Loading (A) | 5.9909e-07 | 5.9906e-07 | 5.9814e-07 | 5.9805e-07 | 5.9793e-07
NQ-Ingham | 6322 66kV VICTORIA SUGAR MILL FDR | Loading (MVA) | 1.1844e-08 | 1.1843e-08 | 1.1806e-08 | 1.1803e-08 | 1.1798e-08
NQ-Ingham | 6322 66kV VICTORIA SUGAR MILL FDR | Loading (MW) | 1.1844e-08 | 1.1843e-08 | 1.1806e-08 | 1.1803e-08 | 1.1798e-08
NQ-Ingham | 6322 66kV VICTORIA SUGAR MILL FDR | Power Factor | 1 | 1 | 1 | 1 | 1
NQ-Ingham | 6322 66kV VICTORIA SUGAR MILL FDR | Rating (A) | 5000 | 5000 | 5000 | 5000 | 5000
NQ-Ingham | 6322 66kV VICTORIA SUGAR MILL FDR | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Ingham | 6322 66kV VICTORIA SUGAR MILL FDR | Min Voltage at Constrained Conductor | 11.4143 | 11.4137 | 11.3961 | 11.3944 | 11.3921
NQ-Ingham | 6322 66kV VICTORIA SUGAR MILL FDR | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Ingham | IN-GR_Ingham-Black River/Greenvale 66 kV | % of Rated A | 22.83% | 22.82% | 22.79% | 22.78% | 22.78%
NQ-Ingham | IN-GR_Ingham-Black River/Greenvale 66 kV | Limiting Line Name | TR_LINE 217286_1 | TR_LINE 217286_1 | TR_LINE 217286_1 | TR_LINE 217286_1 | TR_LINE 217286_1
NQ-Ingham | IN-GR_Ingham-Black River/Greenvale 66 kV | Loading (A) | 15.7495 | 15.7472 | 15.7226 | 15.7202 | 15.7173
NQ-Ingham | IN-GR_Ingham-Black River/Greenvale 66 kV | Loading (MVA) | 1.8823 | 1.882 | 1.8763 | 1.8758 | 1.8752
NQ-Ingham | IN-GR_Ingham-Black River/Greenvale 66 kV | Loading (MW) | 0.099414 | 0.088652 | 0.080618 | 0.074311 | 0.069445
NQ-Ingham | IN-GR_Ingham-Black River/Greenvale 66 kV | Power Factor | 0.05281 | 0.047099 | 0.042959 | 0.039607 | 0.037024
NQ-Ingham | IN-GR_Ingham-Black River/Greenvale 66 kV | Rating (A) | 69 | 69 | 69 | 69 | 69
NQ-Ingham | IN-GR_Ingham-Black River/Greenvale 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Ingham | IN-GR_Ingham-Black River/Greenvale 66 kV | Min Voltage at Constrained Conductor | 69.0003 | 69.0005 | 68.8991 | 68.893 | 68.8832
NQ-Ingham | IN-GR_Ingham-Black River/Greenvale 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Ingham | IN-LA-1_Ingham-Lannercost No 1 66 kV | % of Rated A | 1.343% | 1.307% | 1.29% | 1.284% | 1.282%
NQ-Ingham | IN-LA-1_Ingham-Lannercost No 1 66 kV | Limiting Line Name | TR_LINE 31685_1 | TR_LINE 31685_1 | TR_LINE 31685_1 | TR_LINE 31685_1 | TR_LINE 31685_1
NQ-Ingham | IN-LA-1_Ingham-Lannercost No 1 66 kV | Loading (A) | 2.6195 | 2.5486 | 2.515 | 2.5031 | 2.4991
NQ-Ingham | IN-LA-1_Ingham-Lannercost No 1 66 kV | Loading (MVA) | 0.31205 | 0.30358 | 0.29911 | 0.29765 | 0.29711
NQ-Ingham | IN-LA-1_Ingham-Lannercost No 1 66 kV | Loading (MW) | 0.092208 | 0.057113 | 0.033066 | 0.016294 | 0.0041629
NQ-Ingham | IN-LA-1_Ingham-Lannercost No 1 66 kV | Power Factor | 0.29549 | 0.18813 | 0.11055 | 0.054741 | 0.014011
NQ-Ingham | IN-LA-1_Ingham-Lannercost No 1 66 kV | Rating (A) | 195 | 195 | 195 | 195 | 195
NQ-Ingham | IN-LA-1_Ingham-Lannercost No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Ingham | IN-LA-1_Ingham-Lannercost No 1 66 kV | Min Voltage at Constrained Conductor | 68.779 | 68.7731 | 68.6664 | 68.6549 | 68.6398
NQ-Ingham | IN-LA-1_Ingham-Lannercost No 1 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Ingham | IN-VC-1_Ingham-Victoria No 1 66 kV | % of Rated A | 27.02% | 26.82% | 26.7% | 26.57% | 26.46%
NQ-Ingham | IN-VC-1_Ingham-Victoria No 1 66 kV | Limiting Line Name | TR_LINE 31692_2 | TR_LINE 31692_2 | TR_LINE 31692_2 | TR_LINE 31692_2 | TR_LINE 31692_2
NQ-Ingham | IN-VC-1_Ingham-Victoria No 1 66 kV | Loading (A) | 53.7645 | 53.3723 | 53.1354 | 52.8673 | 52.6561
NQ-Ingham | IN-VC-1_Ingham-Victoria No 1 66 kV | Loading (MVA) | 6.4049 | 6.3576 | 6.3196 | 6.2867 | 6.2602
NQ-Ingham | IN-VC-1_Ingham-Victoria No 1 66 kV | Loading (MW) | 6.3925 | 6.3452 | 6.3071 | 6.2741 | 6.2476
NQ-Ingham | IN-VC-1_Ingham-Victoria No 1 66 kV | Power Factor | 0.99807 | 0.99804 | 0.99803 | 0.998 | 0.99799
NQ-Ingham | IN-VC-1_Ingham-Victoria No 1 66 kV | Rating (A) | 199 | 199 | 199 | 199 | 199
NQ-Ingham | IN-VC-1_Ingham-Victoria No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Ingham | IN-VC-1_Ingham-Victoria No 1 66 kV | Min Voltage at Constrained Conductor | 68.7778 | 68.772 | 68.6652 | 68.6537 | 68.6387
NQ-Ingham | IN-VC-1_Ingham-Victoria No 1 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Ingham | MACN-02_Macknade Mill 11 kV | % of Rated A | 0.07059% | 0.06974% | 0.07049% | 0.07049% | 0.07048%
NQ-Ingham | MACN-02_Macknade Mill 11 kV | Limiting Line Name | HV_CABLE MACN-02 12148046 | HV_CABLE MACN-02 12148046 | HV_CABLE MACN-02 12148046 | HV_CABLE MACN-02 12148046 | HV_CABLE MACN-02 12148046
NQ-Ingham | MACN-02_Macknade Mill 11 kV | Loading (A) | 0.28237 | 0.27898 | 0.28197 | 0.28194 | 0.2819
NQ-Ingham | MACN-02_Macknade Mill 11 kV | Loading (MVA) | 0.0054482 | 0.0053181 | 0.0054326 | 0.0054317 | 0.00543
NQ-Ingham | MACN-02_Macknade Mill 11 kV | Loading (MW) | 0.00010741 | 0.00010484 | 0.0001071 | 0.00010708 | 0.00010705
NQ-Ingham | MACN-02_Macknade Mill 11 kV | Power Factor | 0.019005 | 0.019005 | 0.019005 | 0.019005 | 0.019005
NQ-Ingham | MACN-02_Macknade Mill 11 kV | Rating (A) | 400 | 400 | 400 | 400 | 400
NQ-Ingham | MACN-02_Macknade Mill 11 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Ingham | MACN-02_Macknade Mill 11 kV | Min Voltage at Constrained Conductor | 11.1396 | 11.0058 | 11.1237 | 11.1228 | 11.1211
NQ-Ingham | MACN-02_Macknade Mill 11 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-King Creek | 7307_King Creek - Blue Valley 132 kV | % of Rated A | 0.9523% | 0.9524% | 0.9523% | 0.9521% | 0.9519%
NQ-King Creek | 7307_King Creek - Blue Valley 132 kV | Limiting Line Name | TR_LINE 62480_2 | TR_LINE 62480_2 | TR_LINE 62480_2 | TR_LINE 62480_2 | TR_LINE 62480_2
NQ-King Creek | 7307_King Creek - Blue Valley 132 kV | Loading (A) | 4.3045 | 4.3047 | 4.3042 | 4.3034 | 4.3026
NQ-King Creek | 7307_King Creek - Blue Valley 132 kV | Loading (MVA) | 1.0508 | 1.0508 | 1.0506 | 1.0502 | 1.0498
NQ-King Creek | 7307_King Creek - Blue Valley 132 kV | Loading (MW) | 0.0023113 | 0.0023113 | 0.0023113 | 0.0023113 | 0.0023113
NQ-King Creek | 7307_King Creek - Blue Valley 132 kV | Power Factor | 0.0021997 | 0.0021995 | 0.0022 | 0.0022008 | 0.0022016
NQ-King Creek | 7307_King Creek - Blue Valley 132 kV | Rating (A) | 452 | 452 | 452 | 452 | 452
NQ-King Creek | 7307_King Creek - Blue Valley 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-King Creek | 7307_King Creek - Blue Valley 132 kV | Min Voltage at Constrained Conductor | 140.9334 | 140.9392 | 140.922 | 140.8973 | 140.8697
NQ-King Creek | 7307_King Creek - Blue Valley 132 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-MK-Proserpine Bowen | 118_Cannonvale No 2 66 kV | % of Rated A | 45.72% | 27.81% | 27.6% | 29.44% | 33.53%
NQ-MK-Proserpine Bowen | 118_Cannonvale No 2 66 kV | Limiting Line Name | TR_CABLE 7280_1 | TR_CABLE 7280_1 | TR_CABLE 7280_1 | TR_CABLE 7280_1 | TR_CABLE 7280_1
NQ-MK-Proserpine Bowen | 118_Cannonvale No 2 66 kV | Loading (A) | 88.2467 | 53.6662 | 53.2664 | 56.8207 | 64.7176
NQ-MK-Proserpine Bowen | 118_Cannonvale No 2 66 kV | Loading (MVA) | 10.2216 | 6.2565 | 6.2242 | 6.6301 | 7.5662
NQ-MK-Proserpine Bowen | 118_Cannonvale No 2 66 kV | Loading (MW) | 0.42249 | 1.11 | 0.71866 | 2.5797 | 4.5897
NQ-MK-Proserpine Bowen | 118_Cannonvale No 2 66 kV | Power Factor | 0.040867 | 0.17741 | 0.11473 | 0.38839 | 0.60599
NQ-MK-Proserpine Bowen | 118_Cannonvale No 2 66 kV | Rating (A) | 193 | 193 | 193 | 193 | 193
NQ-MK-Proserpine Bowen | 118_Cannonvale No 2 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-MK-Proserpine Bowen | 118_Cannonvale No 2 66 kV | Min Voltage at Constrained Conductor | 66.8747 | 67.3082 | 67.4632 | 67.3676 | 67.4989
NQ-MK-Proserpine Bowen | 118_Cannonvale No 2 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-MK-Proserpine Bowen | 119_Cannonvale No 1 66 kV | % of Rated A | 28.63% | 28.54% | 29.02% | 31.77% | 36.88%
NQ-MK-Proserpine Bowen | 119_Cannonvale No 1 66 kV | Limiting Line Name | TR_LINE 13015_1 | TR_LINE 13015_1 | TR_LINE 13015_1 | TR_LINE 13015_1 | TR_LINE 13015_1
NQ-MK-Proserpine Bowen | 119_Cannonvale No 1 66 kV | Loading (A) | 52.9618 | 52.8005 | 53.6815 | 58.7743 | 68.2311
NQ-MK-Proserpine Bowen | 119_Cannonvale No 1 66 kV | Loading (MVA) | 6.1252 | 6.1657 | 6.2861 | 6.8759 | 8.0017
NQ-MK-Proserpine Bowen | 119_Cannonvale No 1 66 kV | Loading (MW) | 5.8786 | 0.53224 | 1.3692 | 3.3078 | 5.4051
NQ-MK-Proserpine Bowen | 119_Cannonvale No 1 66 kV | Power Factor | 0.95975 | 0.086068 | 0.21739 | 0.48061 | 0.67496
NQ-MK-Proserpine Bowen | 119_Cannonvale No 1 66 kV | Rating (A) | 185 | 185 | 185 | 185 | 185
NQ-MK-Proserpine Bowen | 119_Cannonvale No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-MK-Proserpine Bowen | 119_Cannonvale No 1 66 kV | Min Voltage at Constrained Conductor | 66.7577 | 67.4194 | 67.6075 | 67.5434 | 67.7077
NQ-MK-Proserpine Bowen | 119_Cannonvale No 1 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-MK-Proserpine Bowen | 120_Prosperpine - Calen 66 kV | % of Rated A | 10.57% | 11.93% | 13.15% | 14.29% | 15.38%
NQ-MK-Proserpine Bowen | 120_Prosperpine - Calen 66 kV | Limiting Line Name | TR_LINE 89457_1 | TR_LINE 89457_1 | TR_LINE 89457_1 | TR_LINE 89457_1 | TR_LINE 89457_1
NQ-MK-Proserpine Bowen | 120_Prosperpine - Calen 66 kV | Loading (A) | 13.9505 | 15.7483 | 17.3567 | 18.868 | 20.299
NQ-MK-Proserpine Bowen | 120_Prosperpine - Calen 66 kV | Loading (MVA) | 1.6159 | 1.836 | 2.0281 | 2.2016 | 2.3732
NQ-MK-Proserpine Bowen | 120_Prosperpine - Calen 66 kV | Loading (MW) | 1.2258 | 1.4956 | 1.7245 | 1.9286 | 2.1217
NQ-MK-Proserpine Bowen | 120_Prosperpine - Calen 66 kV | Power Factor | 0.75855 | 0.81462 | 0.85027 | 0.87599 | 0.894
NQ-MK-Proserpine Bowen | 120_Prosperpine - Calen 66 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
NQ-MK-Proserpine Bowen | 120_Prosperpine - Calen 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-MK-Proserpine Bowen | 120_Prosperpine - Calen 66 kV | Min Voltage at Constrained Conductor | 66.8747 | 67.3082 | 67.4632 | 67.3676 | 67.4989
NQ-MK-Proserpine Bowen | 120_Prosperpine - Calen 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-MK-Proserpine Bowen | 122_Daydream/South Molle 11 kV | % of Rated A | 2.403% | 2.433% | 2.446% | 2.45% | 2.462%
NQ-MK-Proserpine Bowen | 122_Daydream/South Molle 11 kV | Limiting Line Name | HV_LINE 2563705_1 | HV_LINE 2563705_1 | HV_LINE 2563705_1 | HV_LINE 2563705_1 | HV_LINE 2563705_1
NQ-MK-Proserpine Bowen | 122_Daydream/South Molle 11 kV | Loading (A) | 1.8741 | 1.8979 | 1.9079 | 1.9107 | 1.9201
NQ-MK-Proserpine Bowen | 122_Daydream/South Molle 11 kV | Loading (MVA) | 0.035877 | 0.036793 | 0.037182 | 0.03729 | 0.03766
NQ-MK-Proserpine Bowen | 122_Daydream/South Molle 11 kV | Loading (MW) | 0.00071898 | 0.00073734 | 0.00074512 | 0.0007473 | 0.0007547
NQ-MK-Proserpine Bowen | 122_Daydream/South Molle 11 kV | Power Factor | 0.020029 | 0.020029 | 0.020029 | 0.020029 | 0.020029
NQ-MK-Proserpine Bowen | 122_Daydream/South Molle 11 kV | Rating (A) | 78 | 78 | 78 | 78 | 78
NQ-MK-Proserpine Bowen | 122_Daydream/South Molle 11 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-MK-Proserpine Bowen | 122_Daydream/South Molle 11 kV | Min Voltage at Constrained Conductor | 11.0525 | 11.1928 | 11.2517 | 11.2681 | 11.3237
NQ-MK-Proserpine Bowen | 122_Daydream/South Molle 11 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-MK-Proserpine Bowen | 124_Hamilton Island 22 kV | % of Rated A | 1.571% | 1.591% | 1.599% | 1.601% | 1.609%
NQ-MK-Proserpine Bowen | 124_Hamilton Island 22 kV | Limiting Line Name | HV_LINE 136005_1 | HV_LINE 136005_1 | HV_LINE 136005_1 | HV_LINE 136005_1 | HV_LINE 136005_1
NQ-MK-Proserpine Bowen | 124_Hamilton Island 22 kV | Loading (A) | 1.2253 | 1.2408 | 1.2473 | 1.2491 | 1.2551
NQ-MK-Proserpine Bowen | 124_Hamilton Island 22 kV | Loading (MVA) | 0.046848 | 0.048043 | 0.048545 | 0.04868 | 0.049156
NQ-MK-Proserpine Bowen | 124_Hamilton Island 22 kV | Loading (MW) | 0.00093648 | 0.00096037 | 0.00097042 | 0.00097312 | 0.00098263
NQ-MK-Proserpine Bowen | 124_Hamilton Island 22 kV | Power Factor | 0.01999 | 0.01999 | 0.01999 | 0.01999 | 0.01999
NQ-MK-Proserpine Bowen | 124_Hamilton Island 22 kV | Rating (A) | 78 | 78 | 78 | 78 | 78
NQ-MK-Proserpine Bowen | 124_Hamilton Island 22 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-MK-Proserpine Bowen | 124_Hamilton Island 22 kV | Min Voltage at Constrained Conductor | 22.0739 | 22.3536 | 22.4702 | 22.5015 | 22.6112
NQ-MK-Proserpine Bowen | 124_Hamilton Island 22 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-MK-Proserpine Bowen | 125_Hayman Island 22 kV | % of Rated A | 48.6% | 47.98% | 47.72% | 47.65% | 47.41%
NQ-MK-Proserpine Bowen | 125_Hayman Island 22 kV | Limiting Line Name | HV_LINE 11597319_1 | HV_LINE 11597319_1 | HV_LINE 11597319_1 | HV_LINE 11597319_1 | HV_LINE 11597319_1
NQ-MK-Proserpine Bowen | 125_Hayman Island 22 kV | Loading (A) | 37.9086 | 37.421 | 37.2215 | 37.1684 | 36.9832
NQ-MK-Proserpine Bowen | 125_Hayman Island 22 kV | Loading (MVA) | 1.4494 | 1.4489 | 1.4486 | 1.4486 | 1.4484
NQ-MK-Proserpine Bowen | 125_Hayman Island 22 kV | Loading (MW) | 1.4493 | 1.4488 | 1.4486 | 1.4486 | 1.4484
NQ-MK-Proserpine Bowen | 125_Hayman Island 22 kV | Power Factor | 0.99999 | 0.99998 | 0.99998 | 0.99998 | 0.99997
NQ-MK-Proserpine Bowen | 125_Hayman Island 22 kV | Rating (A) | 78 | 78 | 78 | 78 | 78
NQ-MK-Proserpine Bowen | 125_Hayman Island 22 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-MK-Proserpine Bowen | 125_Hayman Island 22 kV | Min Voltage at Constrained Conductor | 22.0613 | 22.3412 | 22.4579 | 22.4892 | 22.599
NQ-MK-Proserpine Bowen | 125_Hayman Island 22 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-MK-Proserpine Bowen | 426_Mt Rooper 66 kV | % of Rated A | 22.64% | 21.77% | 21.32% | 20.9% | 20.34%
NQ-MK-Proserpine Bowen | 426_Mt Rooper 66 kV | Limiting Line Name | TR_LINE 97526_1 | TR_LINE 97526_1 | TR_LINE 97526_1 | TR_LINE 97526_1 | TR_LINE 97526_1
NQ-MK-Proserpine Bowen | 426_Mt Rooper 66 kV | Loading (A) | 56.3786 | 54.2182 | 53.084 | 52.0457 | 50.6406
NQ-MK-Proserpine Bowen | 426_Mt Rooper 66 kV | Loading (MVA) | 6.4884 | 6.3965 | 6.2949 | 6.1801 | 6.042
NQ-MK-Proserpine Bowen | 426_Mt Rooper 66 kV | Loading (MW) | 6.4753 | 6.3808 | 6.2781 | 6.1627 | 6.0236
NQ-MK-Proserpine Bowen | 426_Mt Rooper 66 kV | Power Factor | 0.99798 | 0.99754 | 0.99734 | 0.99719 | 0.99694
NQ-MK-Proserpine Bowen | 426_Mt Rooper 66 kV | Rating (A) | 249 | 249 | 249 | 249 | 249
NQ-MK-Proserpine Bowen | 426_Mt Rooper 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-MK-Proserpine Bowen | 426_Mt Rooper 66 kV | Min Voltage at Constrained Conductor | 66.4444 | 68.114 | 68.464 | 68.5559 | 68.8843
NQ-MK-Proserpine Bowen | 426_Mt Rooper 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-MK-Proserpine Bowen | CANN_JUPO (Ex119&118) | % of Rated A |  | 15.46% | 12.64% | 9.845% | 7.054%
NQ-MK-Proserpine Bowen | CANN_JUPO (Ex119&118) | Limiting Line Name |  | TR_CABLE 17_1 | TR_CABLE 17_1 | TR_CABLE 17_1 | TR_CABLE 17_1
NQ-MK-Proserpine Bowen | CANN_JUPO (Ex119&118) | Loading (A) |  | 43.2836 | 35.3986 | 27.5652 | 19.7518
NQ-MK-Proserpine Bowen | CANN_JUPO (Ex119&118) | Loading (MVA) |  | 5.1089 | 4.1992 | 3.274 | 2.357
NQ-MK-Proserpine Bowen | CANN_JUPO (Ex119&118) | Loading (MW) |  | 4.8976 | 3.9388 | 2.9442 | 1.8885
NQ-MK-Proserpine Bowen | CANN_JUPO (Ex119&118) | Power Factor |  | 0.95864 | 0.93799 | 0.89927 | 0.80126
NQ-MK-Proserpine Bowen | CANN_JUPO (Ex119&118) | Rating (A) |  | 280 | 280 | 280 | 280
NQ-MK-Proserpine Bowen | CANN_JUPO (Ex119&118) | Time |  | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-MK-Proserpine Bowen | CANN_JUPO (Ex119&118) | Min Voltage at Constrained Conductor |  | 68.1428 | 68.4862 | 68.5715 | 68.8931
NQ-MK-Proserpine Bowen | CANN_JUPO (Ex119&118) | Contingency Outage |  | _NNC | _NNC | _NNC | _NNC
NQ-MK-Proserpine Bowen | ME-BN-1_Merinda - Bowen No 1 66 kV | % of Rated A | 29.58% | 30.14% | 30.62% | 30.99% | 31.62%
NQ-MK-Proserpine Bowen | ME-BN-1_Merinda - Bowen No 1 66 kV | Limiting Line Name | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1 | TR_LINE 102321_1
NQ-MK-Proserpine Bowen | ME-BN-1_Merinda - Bowen No 1 66 kV | Loading (A) | 57.6853 | 58.7818 | 59.7126 | 60.4328 | 61.6535
NQ-MK-Proserpine Bowen | ME-BN-1_Merinda - Bowen No 1 66 kV | Loading (MVA) | 6.6982 | 6.8839 | 7.0013 | 7.0447 | 7.1932
NQ-MK-Proserpine Bowen | ME-BN-1_Merinda - Bowen No 1 66 kV | Loading (MW) | 0.40807 | 1.04 | 1.5741 | 2.044 | 2.4861
NQ-MK-Proserpine Bowen | ME-BN-1_Merinda - Bowen No 1 66 kV | Power Factor | 0.060888 | 0.15104 | 0.22479 | 0.29012 | 0.34558
NQ-MK-Proserpine Bowen | ME-BN-1_Merinda - Bowen No 1 66 kV | Rating (A) | 195 | 195 | 195 | 195 | 195
NQ-MK-Proserpine Bowen | ME-BN-1_Merinda - Bowen No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-MK-Proserpine Bowen | ME-BN-1_Merinda - Bowen No 1 66 kV | Min Voltage at Constrained Conductor | 67.04 | 67.6128 | 67.6943 | 67.3023 | 67.3606
NQ-MK-Proserpine Bowen | ME-BN-1_Merinda - Bowen No 1 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-MK-Proserpine Bowen | ME-PR-1_Merinda - Proserpine No 1 66 kV | % of Rated A | 5.364% | 7.326% | 7.554% | 6.71% | 7.546%
NQ-MK-Proserpine Bowen | ME-PR-1_Merinda - Proserpine No 1 66 kV | Limiting Line Name | TR_LINE 175214_1 | TR_LINE 175214_1 | TR_LINE 175214_1 | TR_LINE 175214_1 | TR_LINE 175214_1
NQ-MK-Proserpine Bowen | ME-PR-1_Merinda - Proserpine No 1 66 kV | Loading (A) | 10.3524 | 14.1391 | 14.5801 | 12.9497 | 14.5632
NQ-MK-Proserpine Bowen | ME-PR-1_Merinda - Proserpine No 1 66 kV | Loading (MVA) | 1.1991 | 1.6484 | 1.7037 | 1.511 | 1.7026
NQ-MK-Proserpine Bowen | ME-PR-1_Merinda - Proserpine No 1 66 kV | Loading (MW) | 0.46003 | 0.58154 | 0.81529 | 1.1753 | 1.4348
NQ-MK-Proserpine Bowen | ME-PR-1_Merinda - Proserpine No 1 66 kV | Power Factor | 0.38363 | 0.3528 | 0.47854 | 0.77781 | 0.84268
NQ-MK-Proserpine Bowen | ME-PR-1_Merinda - Proserpine No 1 66 kV | Rating (A) | 193 | 193 | 193 | 193 | 193
NQ-MK-Proserpine Bowen | ME-PR-1_Merinda - Proserpine No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-MK-Proserpine Bowen | ME-PR-1_Merinda - Proserpine No 1 66 kV | Min Voltage at Constrained Conductor | 66.8751 | 67.3087 | 67.4636 | 67.3677 | 67.4989
NQ-MK-Proserpine Bowen | ME-PR-1_Merinda - Proserpine No 1 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-MK-Proserpine Bowen | PR-BN-1_Proserpine - Bowen No 1 66 kV | % of Rated A | 2.684% | 2.708% | 2.713% | 2.698% | 2.702%
NQ-MK-Proserpine Bowen | PR-BN-1_Proserpine - Bowen No 1 66 kV | Limiting Line Name | TR_LINE 175048_1 | TR_LINE 175048_1 | TR_LINE 175048_1 | TR_LINE 175048_1 | TR_LINE 175048_1
NQ-MK-Proserpine Bowen | PR-BN-1_Proserpine - Bowen No 1 66 kV | Loading (A) | 7.9436 | 8.016 | 8.0296 | 7.9866 | 7.9967
NQ-MK-Proserpine Bowen | PR-BN-1_Proserpine - Bowen No 1 66 kV | Loading (MVA) | 0.92815 | 0.94515 | 0.94835 | 0.93823 | 0.9406
NQ-MK-Proserpine Bowen | PR-BN-1_Proserpine - Bowen No 1 66 kV | Loading (MW) | 0.0010956 | 0.0011157 | 0.0011195 | 0.0011075 | 0.0011103
NQ-MK-Proserpine Bowen | PR-BN-1_Proserpine - Bowen No 1 66 kV | Power Factor | 0.0011794 | 0.0011794 | 0.0011794 | 0.0011794 | 0.0011794
NQ-MK-Proserpine Bowen | PR-BN-1_Proserpine - Bowen No 1 66 kV | Rating (A) | 296 | 296 | 296 | 296 | 296
NQ-MK-Proserpine Bowen | PR-BN-1_Proserpine - Bowen No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-MK-Proserpine Bowen | PR-BN-1_Proserpine - Bowen No 1 66 kV | Min Voltage at Constrained Conductor | 67.4589 | 68.0741 | 68.1889 | 67.8242 | 67.9099
NQ-MK-Proserpine Bowen | PR-BN-1_Proserpine - Bowen No 1 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-MK-Proserpine Bowen | PROS-KECR-1_Proserpine No 1 66 kV | % of Rated A | 5.1% | 6.232% | 7.203% | 8.084% | 8.89%
NQ-MK-Proserpine Bowen | PROS-KECR-1_Proserpine No 1 66 kV | Limiting Line Name | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1 | TR_LINE 34478_1
NQ-MK-Proserpine Bowen | PROS-KECR-1_Proserpine No 1 66 kV | Loading (A) | 9.0267 | 11.0301 | 12.7488 | 14.3083 | 15.7358
NQ-MK-Proserpine Bowen | PROS-KECR-1_Proserpine No 1 66 kV | Loading (MVA) | 1.0456 | 1.2859 | 1.4897 | 1.6696 | 1.8397
NQ-MK-Proserpine Bowen | PROS-KECR-1_Proserpine No 1 66 kV | Loading (MW) | 1.0455 | 1.2858 | 1.4896 | 1.6694 | 1.8395
NQ-MK-Proserpine Bowen | PROS-KECR-1_Proserpine No 1 66 kV | Power Factor | 0.99996 | 0.99994 | 0.99991 | 0.99989 | 0.99987
NQ-MK-Proserpine Bowen | PROS-KECR-1_Proserpine No 1 66 kV | Rating (A) | 177 | 177 | 177 | 177 | 177
NQ-MK-Proserpine Bowen | PROS-KECR-1_Proserpine No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-MK-Proserpine Bowen | PROS-KECR-1_Proserpine No 1 66 kV | Min Voltage at Constrained Conductor | 66.8752 | 67.3089 | 67.4639 | 67.3684 | 67.4998
NQ-MK-Proserpine Bowen | PROS-KECR-1_Proserpine No 1 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-MK-Proserpine Bowen | PROS-KECR-2_Proserpine No 2 66 kV | % of Rated A | 10.19% | 12.46% | 14.4% | 16.15% | 17.76%
NQ-MK-Proserpine Bowen | PROS-KECR-2_Proserpine No 2 66 kV | Limiting Line Name | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1 | TR_LINE 34477_1
NQ-MK-Proserpine Bowen | PROS-KECR-2_Proserpine No 2 66 kV | Loading (A) | 18.0442 | 22.0465 | 25.4793 | 28.5935 | 31.4437
NQ-MK-Proserpine Bowen | PROS-KECR-2_Proserpine No 2 66 kV | Loading (MVA) | 2.0901 | 2.5703 | 2.9773 | 3.3365 | 3.6763
NQ-MK-Proserpine Bowen | PROS-KECR-2_Proserpine No 2 66 kV | Loading (MW) | 2.09 | 2.5701 | 2.9771 | 3.3362 | 3.6758
NQ-MK-Proserpine Bowen | PROS-KECR-2_Proserpine No 2 66 kV | Power Factor | 0.99996 | 0.99994 | 0.99991 | 0.99989 | 0.99987
NQ-MK-Proserpine Bowen | PROS-KECR-2_Proserpine No 2 66 kV | Rating (A) | 177 | 177 | 177 | 177 | 177
NQ-MK-Proserpine Bowen | PROS-KECR-2_Proserpine No 2 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-MK-Proserpine Bowen | PROS-KECR-2_Proserpine No 2 66 kV | Min Voltage at Constrained Conductor | 66.8756 | 67.3093 | 67.4644 | 67.369 | 67.5005
NQ-MK-Proserpine Bowen | PROS-KECR-2_Proserpine No 2 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Mount Isa | 7018_Mica Creek C - Chumvale 220 kV | % of Rated A | 15.05% | 14.95% | 14.83% | 14.68% | 14.51%
NQ-Mount Isa | 7018_Mica Creek C - Chumvale 220 kV | Limiting Line Name | TR_LINE 3024_1 | TR_LINE 3024_1 | TR_LINE 3024_1 | TR_LINE 3024_1 | TR_LINE 3024_1
NQ-Mount Isa | 7018_Mica Creek C - Chumvale 220 kV | Loading (A) | 128.6983 | 127.796 | 126.7578 | 125.5392 | 124.0743
NQ-Mount Isa | 7018_Mica Creek C - Chumvale 220 kV | Loading (MVA) | 53.5187 | 53.1468 | 52.7184 | 52.215 | 51.5547
NQ-Mount Isa | 7018_Mica Creek C - Chumvale 220 kV | Loading (MW) | 41.8751 | 41.366 | 40.7812 | 40.0965 | 39.2808
NQ-Mount Isa | 7018_Mica Creek C - Chumvale 220 kV | Power Factor | 0.78244 | 0.77833 | 0.77357 | 0.76791 | 0.76193
NQ-Mount Isa | 7018_Mica Creek C - Chumvale 220 kV | Rating (A) | 855 | 855 | 855 | 855 | 855
NQ-Mount Isa | 7018_Mica Creek C - Chumvale 220 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Mount Isa | 7018_Mica Creek C - Chumvale 220 kV | Min Voltage at Constrained Conductor | 240.089 | 240.1039 | 240.1193 | 240.1351 | 239.8973
NQ-Mount Isa | 7018_Mica Creek C - Chumvale 220 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Mount Isa | CH-CC-1_Chumvale-Cloncurry 66 kV | % of Rated A | 2.898% | 1.949% | 4.013% | 6.761% | 10.35%
NQ-Mount Isa | CH-CC-1_Chumvale-Cloncurry 66 kV | Limiting Line Name | TR_LINE 34857_1 | TR_LINE 172154_1 | TR_LINE 34531_1 | TR_LINE 34531_1 | TR_LINE 34857_1
NQ-Mount Isa | CH-CC-1_Chumvale-Cloncurry 66 kV | Loading (A) | 4.7245 | 3.1769 | 6.8213 | 11.4939 | 16.8659
NQ-Mount Isa | CH-CC-1_Chumvale-Cloncurry 66 kV | Loading (MVA) | 0.56929 | 0.38289 | 0.82272 | 1.3874 | 2.0315
NQ-Mount Isa | CH-CC-1_Chumvale-Cloncurry 66 kV | Loading (MW) | 0.54518 | 0.38289 | 0.82154 | 1.3869 | 2.0273
NQ-Mount Isa | CH-CC-1_Chumvale-Cloncurry 66 kV | Power Factor | 0.95764 | 0.99998 | 0.99857 | 0.99968 | 0.99786
NQ-Mount Isa | CH-CC-1_Chumvale-Cloncurry 66 kV | Rating (A) | 163 | 163 | 170 | 170 | 163
NQ-Mount Isa | CH-CC-1_Chumvale-Cloncurry 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Mount Isa | CH-CC-1_Chumvale-Cloncurry 66 kV | Min Voltage at Constrained Conductor | 69.5694 | 69.5854 | 69.6339 | 69.6884 | 69.5427
NQ-Mount Isa | CH-CC-1_Chumvale-Cloncurry 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Mount Isa | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | % of Rated A | 15.56% | 15.57% | 15.57% | 15.57% | 15.74%
NQ-Mount Isa | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Limiting Line Name | TR_LINE 234732_1 | TR_LINE 234732_1 | TR_LINE 234732_1 | TR_LINE 234732_1 | TR_LINE 234732_1
NQ-Mount Isa | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Loading (A) | 12.9187 | 12.9195 | 12.9203 | 12.921 | 13.0654
NQ-Mount Isa | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Loading (MVA) | 1.6174 | 1.6176 | 1.6178 | 1.618 | 1.6544
NQ-Mount Isa | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Loading (MW) | 0.10932 | 0.10932 | 0.10932 | 0.10932 | 0.10952
NQ-Mount Isa | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Power Factor | 0.06759 | 0.067582 | 0.067574 | 0.067567 | 0.066202
NQ-Mount Isa | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Rating (A) | 83 | 83 | 83 | 83 | 83
NQ-Mount Isa | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Mount Isa | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Min Voltage at Constrained Conductor | 72.2831 | 72.2879 | 72.2922 | 72.2964 | 73.1062
NQ-Mount Isa | DR-CC-1_Duchess Road-Cloncurry 1 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Mount Isa | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | % of Rated A | 1.327% | 1.092% | 0.9094% | 0.7668% | 0.6593%
NQ-Mount Isa | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Limiting Line Name | TR_LINE 174405_1 | TR_LINE 174405_1 | TR_LINE 174405_1 | TR_LINE 174405_1 | TR_LINE 174405_1
NQ-Mount Isa | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Loading (A) | 5.0962 | 4.1938 | 3.4923 | 2.9444 | 2.5317
NQ-Mount Isa | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Loading (MVA) | 1.2271 | 1.0099 | 0.84098 | 0.70908 | 0.60906
NQ-Mount Isa | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Loading (MW) | 1.1397 | 0.90112 | 0.70628 | 0.54221 | 0.40345
NQ-Mount Isa | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Power Factor | 0.92875 | 0.89231 | 0.83984 | 0.76467 | 0.66242
NQ-Mount Isa | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Rating (A) | 384 | 384 | 384 | 384 | 384
NQ-Mount Isa | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Mount Isa | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Min Voltage at Constrained Conductor | 139.0219 | 139.027 | 139.032 | 139.0371 | 138.8968
NQ-Mount Isa | MICB-DURO 1_Mica Creek B-DURO 1 132 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Mount Isa | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | % of Rated A | 3.321% | 3.136% | 3.009% | 2.919% | 2.911%
NQ-Mount Isa | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Limiting Line Name | TR_LINE 174422_1 | TR_LINE 174422_1 | TR_LINE 174422_1 | TR_LINE 174422_1 | TR_LINE 174422_1
NQ-Mount Isa | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Loading (A) | 9.2642 | 8.7508 | 8.3947 | 8.1449 | 8.1206
NQ-Mount Isa | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Loading (MVA) | 2.2308 | 2.1073 | 2.0216 | 1.9615 | 1.9537
NQ-Mount Isa | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Loading (MW) | 1.2522 | 1.0136 | 0.81879 | 0.65471 | 0.51622
NQ-Mount Isa | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Power Factor | 0.56133 | 0.48102 | 0.40502 | 0.33378 | 0.26423
NQ-Mount Isa | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Rating (A) | 279 | 279 | 279 | 279 | 279
NQ-Mount Isa | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Mount Isa | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Min Voltage at Constrained Conductor | 139.0248 | 139.0299 | 139.0349 | 139.04 | 138.8997
NQ-Mount Isa | MICB-DURO 2_Mica Creek B-DURO 2 132 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Mount Isa | MICC-MICB No 1 132 kV | % of Rated A | 35.71% | 35.63% | 35.53% | 35.42% | 35.26%
NQ-Mount Isa | MICC-MICB No 1 132 kV | Limiting Line Name | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1 | TR_LINE 163891_1
NQ-Mount Isa | MICC-MICB No 1 132 kV | Loading (A) | 186.403 | 185.9796 | 185.4879 | 184.905 | 184.0546
NQ-Mount Isa | MICC-MICB No 1 132 kV | Loading (MVA) | 44.8846 | 44.7842 | 44.6673 | 44.5285 | 44.2789
NQ-Mount Isa | MICC-MICB No 1 132 kV | Loading (MW) | 22.6854 | 22.4311 | 22.1389 | 21.7968 | 21.389
NQ-Mount Isa | MICC-MICB No 1 132 kV | Power Factor | 0.50542 | 0.50087 | 0.49564 | 0.4895 | 0.48305
NQ-Mount Isa | MICC-MICB No 1 132 kV | Rating (A) | 522 | 522 | 522 | 522 | 522
NQ-Mount Isa | MICC-MICB No 1 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Mount Isa | MICC-MICB No 1 132 kV | Min Voltage at Constrained Conductor | 139.022 | 139.0268 | 139.0316 | 139.0366 | 138.8961
NQ-Mount Isa | MICC-MICB No 1 132 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Mount Isa | MICC-MICB No 2 132 kV | % of Rated A | 35.83% | 35.75% | 35.66% | 35.55% | 35.38%
NQ-Mount Isa | MICC-MICB No 2 132 kV | Limiting Line Name | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1 | TR_LINE 163892_1
NQ-Mount Isa | MICC-MICB No 2 132 kV | Loading (A) | 187.0499 | 186.625 | 186.1316 | 185.5466 | 184.6932
NQ-Mount Isa | MICC-MICB No 2 132 kV | Loading (MVA) | 45.0403 | 44.9396 | 44.8223 | 44.683 | 44.4326
NQ-Mount Isa | MICC-MICB No 2 132 kV | Loading (MW) | 22.764 | 22.5088 | 22.2157 | 21.8724 | 21.4632
NQ-Mount Isa | MICC-MICB No 2 132 kV | Power Factor | 0.50541 | 0.50087 | 0.49564 | 0.4895 | 0.48305
NQ-Mount Isa | MICC-MICB No 2 132 kV | Rating (A) | 522 | 522 | 522 | 522 | 522
NQ-Mount Isa | MICC-MICB No 2 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Mount Isa | MICC-MICB No 2 132 kV | Min Voltage at Constrained Conductor | 139.022 | 139.0268 | 139.0316 | 139.0366 | 138.8961
NQ-Mount Isa | MICC-MICB No 2 132 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Townsville Burdekin West | 6127_Bohle-Black River 1 66 kV | % of Rated A | 7.892% | 10.84% | 13.76% | 16.97% | 20.48%
NQ-Townsville Burdekin West | 6127_Bohle-Black River 1 66 kV | Limiting Line Name | TR_LINE 162720_1 | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1 | TR_LINE 68120_1
NQ-Townsville Burdekin West | 6127_Bohle-Black River 1 66 kV | Loading (A) | 57.5292 | 79.0169 | 100.2989 | 123.7283 | 149.2838
NQ-Townsville Burdekin West | 6127_Bohle-Black River 1 66 kV | Loading (MVA) | 6.8813 | 9.4723 | 12.1592 | 15.0087 | 18.1147
NQ-Townsville Burdekin West | 6127_Bohle-Black River 1 66 kV | Loading (MW) | 6.8794 | 9.4706 | 12.1483 | 14.9755 | 18.0392
NQ-Townsville Burdekin West | 6127_Bohle-Black River 1 66 kV | Power Factor | 0.99972 | 0.99982 | 0.9991 | 0.99778 | 0.99583
NQ-Townsville Burdekin West | 6127_Bohle-Black River 1 66 kV | Rating (A) | 729 | 729 | 729 | 729 | 729
NQ-Townsville Burdekin West | 6127_Bohle-Black River 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | 6127_Bohle-Black River 1 66 kV | Min Voltage at Constrained Conductor | 69.0592 | 69.2108 | 69.9917 | 70.0348 | 70.0578
NQ-Townsville Burdekin West | 6127_Bohle-Black River 1 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Townsville Burdekin West | 6266_Bohle-Black River No 2 66 kV | % of Rated A | 7.979% | 10.96% | 13.91% | 17.16% | 20.71%
NQ-Townsville Burdekin West | 6266_Bohle-Black River No 2 66 kV | Limiting Line Name | TR_LINE 96351_1 | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1 | TR_LINE 162727_1
NQ-Townsville Burdekin West | 6266_Bohle-Black River No 2 66 kV | Loading (A) | 58.164 | 79.8949 | 101.4131 | 125.1026 | 150.9417
NQ-Townsville Burdekin West | 6266_Bohle-Black River No 2 66 kV | Loading (MVA) | 6.9616 | 9.5776 | 12.2943 | 15.1756 | 18.316
NQ-Townsville Burdekin West | 6266_Bohle-Black River No 2 66 kV | Loading (MW) | 6.9613 | 9.5748 | 12.2804 | 15.1365 | 18.2309
NQ-Townsville Burdekin West | 6266_Bohle-Black River No 2 66 kV | Power Factor | 0.99983 | 0.99971 | 0.99887 | 0.99743 | 0.99535
NQ-Townsville Burdekin West | 6266_Bohle-Black River No 2 66 kV | Rating (A) | 729 | 729 | 729 | 729 | 729
NQ-Townsville Burdekin West | 6266_Bohle-Black River No 2 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | 6266_Bohle-Black River No 2 66 kV | Min Voltage at Constrained Conductor | 69.0595 | 69.2101 | 69.9908 | 70.0338 | 70.0567
NQ-Townsville Burdekin West | 6266_Bohle-Black River No 2 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Townsville Burdekin West | 6299_Townsville Port 66 kV | % of Rated A | 17.27% | 16.43% | 9.487% | 8.23% | 6.974%
NQ-Townsville Burdekin West | 6299_Townsville Port 66 kV | Limiting Line Name | TR_LINE 96490_1 | TR_LINE 96490_1 | TR_LINE 96490_1 | TR_LINE 96490_1 | TR_LINE 96490_1
NQ-Townsville Burdekin West | 6299_Townsville Port 66 kV | Loading (A) | 188.6034 | 179.3875 | 103.5965 | 89.8698 | 76.1602
NQ-Townsville Burdekin West | 6299_Townsville Port 66 kV | Loading (MVA) | 22.4358 | 21.335 | 12.4723 | 10.8177 | 9.1648
NQ-Townsville Burdekin West | 6299_Townsville Port 66 kV | Loading (MW) | 13.1176 | 11.5855 | 9.8346 | 7.8731 | 5.8064
NQ-Townsville Burdekin West | 6299_Townsville Port 66 kV | Power Factor | 0.58467 | 0.54302 | 0.78852 | 0.7278 | 0.63356
NQ-Townsville Burdekin West | 6299_Townsville Port 66 kV | Rating (A) | 1092 | 1092 | 1092 | 1092 | 1092
NQ-Townsville Burdekin West | 6299_Townsville Port 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | 6299_Townsville Port 66 kV | Min Voltage at Constrained Conductor | 68.6796 | 68.6651 | 69.5092 | 69.4964 | 69.4758
NQ-Townsville Burdekin West | 6299_Townsville Port 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Townsville Burdekin West | 6312_Merinda - Home Hill 66 kV | % of Rated A | 6.761% | 6.478% | 6.471% | 6.464% | 6.459%
NQ-Townsville Burdekin West | 6312_Merinda - Home Hill 66 kV | Limiting Line Name | TR_LINE 32515_1 | TR_LINE 180012_1 | TR_LINE 180012_1 | TR_LINE 180012_1 | TR_LINE 180012_1
NQ-Townsville Burdekin West | 6312_Merinda - Home Hill 66 kV | Loading (A) | 17.4434 | 11.3365 | 11.3245 | 11.3128 | 11.3032
NQ-Townsville Burdekin West | 6312_Merinda - Home Hill 66 kV | Loading (MVA) | 2.0573 | 1.3412 | 1.343 | 1.3449 | 1.3474
NQ-Townsville Burdekin West | 6312_Merinda - Home Hill 66 kV | Loading (MW) | 1.5039 | 1.0823 | 1.0817 | 1.0812 | 1.081
NQ-Townsville Burdekin West | 6312_Merinda - Home Hill 66 kV | Power Factor | 0.73101 | 0.80701 | 0.80548 | 0.80392 | 0.8023
NQ-Townsville Burdekin West | 6312_Merinda - Home Hill 66 kV | Rating (A) | 258 | 175 | 175 | 175 | 175
NQ-Townsville Burdekin West | 6312_Merinda - Home Hill 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | 6312_Merinda - Home Hill 66 kV | Min Voltage at Constrained Conductor | 68.092 | 68.3043 | 68.4674 | 68.6351 | 68.8243
NQ-Townsville Burdekin West | 6312_Merinda - Home Hill 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Townsville Burdekin West | 6325_Oonoonba-Stuart 66 kV | % of Rated A | 13.65% | 10.28% | 11.77% | 9.604% | 8.338%
NQ-Townsville Burdekin West | 6325_Oonoonba-Stuart 66 kV | Limiting Line Name | TR_LINE 31738_1 | TR_LINE 31738_1 | TR_LINE 31738_1 | TR_LINE 31738_1 | TR_LINE 31738_1
NQ-Townsville Burdekin West | 6325_Oonoonba-Stuart 66 kV | Loading (A) | 44.3756 | 33.4153 | 38.2649 | 31.2118 | 27.0995
NQ-Townsville Burdekin West | 6325_Oonoonba-Stuart 66 kV | Loading (MVA) | 5.3041 | 3.9941 | 4.6064 | 3.7568 | 3.2611
NQ-Townsville Burdekin West | 6325_Oonoonba-Stuart 66 kV | Loading (MW) | 4.4558 | 2.9408 | 2.6887 | 1.3149 | 0.065803
NQ-Townsville Burdekin West | 6325_Oonoonba-Stuart 66 kV | Power Factor | 0.84006 | 0.73627 | 0.58368 | 0.34999 | 0.020165
NQ-Townsville Burdekin West | 6325_Oonoonba-Stuart 66 kV | Rating (A) | 325 | 325 | 325 | 325 | 325
NQ-Townsville Burdekin West | 6325_Oonoonba-Stuart 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | 6325_Oonoonba-Stuart 66 kV | Min Voltage at Constrained Conductor | 69.0086 | 69.0109 | 69.5025 | 69.4927 | 69.4771
NQ-Townsville Burdekin West | 6325_Oonoonba-Stuart 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Townsville Burdekin West | 6382 JACR-HUGH 132kV | % of Rated A | 34.89% | 34.88% | 35.44% | 35.19% | 34.86%
NQ-Townsville Burdekin West | 6382 JACR-HUGH 132kV | Limiting Line Name | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line | KEP2 - HUGH 66kV line
NQ-Townsville Burdekin West | 6382 JACR-HUGH 132kV | Loading (A) | 49.5382 | 49.5347 | 50.3226 | 49.9736 | 49.4956
NQ-Townsville Burdekin West | 6382 JACR-HUGH 132kV | Loading (MVA) | 5.8508 | 5.8551 | 5.9169 | 5.8769 | 5.8249
NQ-Townsville Burdekin West | 6382 JACR-HUGH 132kV | Loading (MW) | 1.0786 | 0.81585 | 2.5478 | 2.3116 | 2.0694
NQ-Townsville Burdekin West | 6382 JACR-HUGH 132kV | Power Factor | 0.18436 | 0.13763 | 0.4306 | 0.39334 | 0.35526
NQ-Townsville Burdekin West | 6382 JACR-HUGH 132kV | Rating (A) | 142 | 142 | 142 | 142 | 142
NQ-Townsville Burdekin West | 6382 JACR-HUGH 132kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | 6382 JACR-HUGH 132kV | Min Voltage at Constrained Conductor | 68.1888 | 68.2438 | 67.8843 | 67.8967 | 67.9458
NQ-Townsville Burdekin West | 6382 JACR-HUGH 132kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Townsville Burdekin West | 6383 CARI-CPRE 66kV | % of Rated A | 14.86% | 15.44% | 13.61% | 13.78% | 13.98%
NQ-Townsville Burdekin West | 6383 CARI-CPRE 66kV | Limiting Line Name | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1 | TR_LINE 51339306_1
NQ-Townsville Burdekin West | 6383 CARI-CPRE 66kV | Loading (A) | 46.3642 | 48.1582 | 42.4544 | 42.9885 | 43.6158
NQ-Townsville Burdekin West | 6383 CARI-CPRE 66kV | Loading (MVA) | 5.463 | 5.6766 | 4.9937 | 5.0575 | 5.1329
NQ-Townsville Burdekin West | 6383 CARI-CPRE 66kV | Loading (MW) | 1.2058 | 0.94393 | 2.6747 | 2.4368 | 2.1942
NQ-Townsville Burdekin West | 6383 CARI-CPRE 66kV | Power Factor | 0.22069 | 0.16626 | 0.53559 | 0.48179 | 0.42745
NQ-Townsville Burdekin West | 6383 CARI-CPRE 66kV | Rating (A) | 312 | 312 | 312 | 312 | 312
NQ-Townsville Burdekin West | 6383 CARI-CPRE 66kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | 6383 CARI-CPRE 66kV | Min Voltage at Constrained Conductor | 68.0282 | 68.0544 | 67.9116 | 67.9242 | 67.9452
NQ-Townsville Burdekin West | 6383 CARI-CPRE 66kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Townsville Burdekin West | 7182 Ross - Milchester | % of Rated A | 26.52% | 25.81% | 27.1% | 26.43% | 25.74%
NQ-Townsville Burdekin West | 7182 Ross - Milchester | Limiting Line Name | TR_LINE 31626_1 | TR_LINE 31626_1 | TR_LINE 31626_1 | TR_LINE 31626_1 | TR_LINE 31626_1
NQ-Townsville Burdekin West | 7182 Ross - Milchester | Loading (A) | 88.298 | 85.9322 | 90.2305 | 87.9961 | 85.7051
NQ-Townsville Burdekin West | 7182 Ross - Milchester | Loading (MVA) | 21.2039 | 20.6353 | 21.6619 | 21.1248 | 20.574
NQ-Townsville Burdekin West | 7182 Ross - Milchester | Loading (MW) | 12.9836 | 12.1586 | 13.2626 | 12.5285 | 11.7691
NQ-Townsville Burdekin West | 7182 Ross - Milchester | Power Factor | 0.61232 | 0.58921 | 0.61225 | 0.59307 | 0.57204
NQ-Townsville Burdekin West | 7182 Ross - Milchester | Rating (A) | 333 | 333 | 333 | 333 | 333
NQ-Townsville Burdekin West | 7182 Ross - Milchester | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | 7182 Ross - Milchester | Min Voltage at Constrained Conductor | 138.6452 | 138.6422 | 138.6063 | 138.6018 | 138.5964
NQ-Townsville Burdekin West | 7182 Ross - Milchester | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Townsville Burdekin West | 7460 CPRE-JACR 132kV | % of Rated A | 19.19% | 19.24% | 19.31% | 18.98% | 18.92%
NQ-Townsville Burdekin West | 7460 CPRE-JACR 132kV | Limiting Line Name | TR_LINE 51339257_1 | TR_LINE 51339257_1 | TR_LINE 51339257_1 | TR_LINE 51339257_1 | TR_LINE 51339257_1
NQ-Townsville Burdekin West | 7460 CPRE-JACR 132kV | Loading (A) | 33.204 | 33.2827 | 33.4002 | 32.828 | 32.7256
NQ-Townsville Burdekin West | 7460 CPRE-JACR 132kV | Loading (MVA) | 7.8354 | 7.8561 | 7.8715 | 7.7369 | 7.7145
NQ-Townsville Burdekin West | 7460 CPRE-JACR 132kV | Loading (MW) | 1.1496 | 0.88674 | 2.6224 | 2.3841 | 2.1409
NQ-Townsville Burdekin West | 7460 CPRE-JACR 132kV | Power Factor | 0.14672 | 0.11287 | 0.33316 | 0.30815 | 0.27752
NQ-Townsville Burdekin West | 7460 CPRE-JACR 132kV | Rating (A) | 173 | 173 | 173 | 173 | 173
NQ-Townsville Burdekin West | 7460 CPRE-JACR 132kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | 7460 CPRE-JACR 132kV | Min Voltage at Constrained Conductor | 136.2423 | 136.2787 | 136.0651 | 136.0693 | 136.0999
NQ-Townsville Burdekin West | 7460 CPRE-JACR 132kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Townsville Burdekin West | AV-CB-1_Aitkenvale-Cranbrook 66 kV | % of Rated A | 8.694% | 9.092% | 4.398% | 4.237% | 4.027%
NQ-Townsville Burdekin West | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Limiting Line Name | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1 | TR_LINE 31654_1
NQ-Townsville Burdekin West | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Loading (A) | 28.9526 | 30.2765 | 14.6446 | 14.1105 | 13.4094
NQ-Townsville Burdekin West | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Loading (MVA) | 3.4579 | 3.6176 | 1.7682 | 1.704 | 1.6193
NQ-Townsville Burdekin West | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Loading (MW) | 1.3034 | 1.4185 | 1.6374 | 1.605 | 1.5483
NQ-Townsville Burdekin West | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Power Factor | 0.37693 | 0.39211 | 0.92597 | 0.94191 | 0.95616
NQ-Townsville Burdekin West | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Rating (A) | 333 | 333 | 333 | 333 | 333
NQ-Townsville Burdekin West | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Min Voltage at Constrained Conductor | 68.9551 | 68.9853 | 69.7116 | 69.7207 | 69.7198
NQ-Townsville Burdekin West | AV-CB-1_Aitkenvale-Cranbrook 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Townsville Burdekin West | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | % of Rated A | 2.289% | 0.9313% | 7.734% | 7.685% | 7.718%
NQ-Townsville Burdekin West | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Limiting Line Name | TR_LINE 34618_1 | TR_LINE 34618_1 | TR_LINE 34618_1 | TR_LINE 34618_1 | TR_LINE 34618_1
NQ-Townsville Burdekin West | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Loading (A) | 10.5303 | 4.2841 | 35.5755 | 35.3492 | 35.5038
NQ-Townsville Burdekin West | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Loading (MVA) | 1.2583 | 0.51211 | 4.2872 | 4.2604 | 4.279
NQ-Townsville Burdekin West | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Loading (MW) | 1.2151 | 0.46557 | 0.307 | 0.79659 | 1.2605
NQ-Townsville Burdekin West | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Power Factor | 0.96564 | 0.90911 | 0.071537 | 0.1869 | 0.29451
NQ-Townsville Burdekin West | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Rating (A) | 460 | 460 | 460 | 460 | 460
NQ-Townsville Burdekin West | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Min Voltage at Constrained Conductor | 68.989 | 69.0161 | 69.5772 | 69.585 | 69.5833
NQ-Townsville Burdekin West | AV-GA-1_Garbutt-Aitkenvale No 1 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Townsville Burdekin West | AY-EA-1_Ayr - East Ayr No 1 66 kV | % of Rated A | 8.558% | 7.996% | 7.401% | 6.755% | 6.049%
NQ-Townsville Burdekin West | AY-EA-1_Ayr - East Ayr No 1 66 kV | Limiting Line Name | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1 | TR_LINE 45324_1
NQ-Townsville Burdekin West | AY-EA-1_Ayr - East Ayr No 1 66 kV | Loading (A) | 22.1651 | 20.7096 | 19.168 | 17.4965 | 15.6669
NQ-Townsville Burdekin West | AY-EA-1_Ayr - East Ayr No 1 66 kV | Loading (MVA) | 2.6119 | 2.4452 | 2.2677 | 2.0739 | 1.8609
NQ-Townsville Burdekin West | AY-EA-1_Ayr - East Ayr No 1 66 kV | Loading (MW) | 2.237 | 2.0452 | 1.8342 | 1.5962 | 1.3182
NQ-Townsville Burdekin West | AY-EA-1_Ayr - East Ayr No 1 66 kV | Power Factor | 0.85628 | 0.83625 | 0.80868 | 0.76948 | 0.70821
NQ-Townsville Burdekin West | AY-EA-1_Ayr - East Ayr No 1 66 kV | Rating (A) | 259 | 259 | 259 | 259 | 259
NQ-Townsville Burdekin West | AY-EA-1_Ayr - East Ayr No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | AY-EA-1_Ayr - East Ayr No 1 66 kV | Min Voltage at Constrained Conductor | 68.033 | 68.1668 | 68.3034 | 68.4358 | 68.5778
NQ-Townsville Burdekin West | AY-EA-1_Ayr - East Ayr No 1 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Townsville Burdekin West | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | % of Rated A | 13.56% | 13.81% | 14.39% | 15.54% | 17.42%
NQ-Townsville Burdekin West | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Limiting Line Name | TR_LINE 33601_1 | TR_LINE 33601_1 | TR_LINE 33601_1 | TR_LINE 33601_1 | TR_LINE 33601_1
NQ-Townsville Burdekin West | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Loading (A) | 34.9837 | 35.6201 | 37.1324 | 40.0868 | 44.9514
NQ-Townsville Burdekin West | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Loading (MVA) | 4.1259 | 4.2097 | 4.398 | 4.7585 | 5.3493
NQ-Townsville Burdekin West | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Loading (MW) | 3.3885 | 3.5032 | 3.7313 | 4.1422 | 4.7886
NQ-Townsville Burdekin West | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Power Factor | 0.82126 | 0.83218 | 0.8484 | 0.87048 | 0.89518
NQ-Townsville Burdekin West | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Rating (A) | 258 | 258 | 258 | 258 | 258
NQ-Townsville Burdekin West | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Min Voltage at Constrained Conductor | 68.092 | 68.2328 | 68.3792 | 68.5275 | 68.6933
NQ-Townsville Burdekin West | AY-HH-1_Ayr-HOHI/Jarvisfield No 1 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Townsville Burdekin West | BC-IN-1_Black River - Ingham No 1 66 kV | % of Rated A | 7.444% | 9.803% | 11.78% | 13.69% | 15.59%
NQ-Townsville Burdekin West | BC-IN-1_Black River - Ingham No 1 66 kV | Limiting Line Name | TR_LINE 214252_1 | TR_LINE 214252_1 | TR_LINE 214252_1 | TR_LINE 214252_1 | TR_LINE 214252_1
NQ-Townsville Burdekin West | BC-IN-1_Black River - Ingham No 1 66 kV | Loading (A) | 14.0696 | 18.5271 | 22.2655 | 25.8704 | 29.4722
NQ-Townsville Burdekin West | BC-IN-1_Black River - Ingham No 1 66 kV | Loading (MVA) | 1.6853 | 2.2222 | 2.701 | 3.1404 | 3.5792
NQ-Townsville Burdekin West | BC-IN-1_Black River - Ingham No 1 66 kV | Loading (MW) | 1.624 | 2.1799 | 2.6683 | 3.1161 | 3.5615
NQ-Townsville Burdekin West | BC-IN-1_Black River - Ingham No 1 66 kV | Power Factor | 0.96319 | 0.98045 | 0.98728 | 0.99152 | 0.99424
NQ-Townsville Burdekin West | BC-IN-1_Black River - Ingham No 1 66 kV | Rating (A) | 189 | 189 | 189 | 189 | 189
NQ-Townsville Burdekin West | BC-IN-1_Black River - Ingham No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | BC-IN-1_Black River - Ingham No 1 66 kV | Min Voltage at Constrained Conductor | 69.159 | 69.249 | 70.0363 | 70.0854 | 70.1143
NQ-Townsville Burdekin West | BC-IN-1_Black River - Ingham No 1 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Townsville Burdekin West | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | % of Rated A | 2.941% | 2.906% | 2.91% | 2.901% | 2.898%
NQ-Townsville Burdekin West | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | Limiting Line Name | TR_CABLE 4808_1 | TR_CABLE 4808_1 | TR_CABLE 4808_1 | TR_CABLE 4808_1 | TR_CABLE 4808_1
NQ-Townsville Burdekin West | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | Loading (A) | 23.3498 | 23.0758 | 23.104 | 23.0361 | 23.0121
NQ-Townsville Burdekin West | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | Loading (MVA) | 2.7901 | 2.7585 | 2.7843 | 2.7764 | 2.7735
NQ-Townsville Burdekin West | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | Loading (MW) | 0.60296 | 0.41232 | 0.25447 | 0.1269 | 0.010196
NQ-Townsville Burdekin West | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | Power Factor | 0.2161 | 0.14947 | 0.091396 | 0.045707 | 0.00095976
NQ-Townsville Burdekin West | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | Rating (A) | 794 | 794 | 794 | 794 | 794
NQ-Townsville Burdekin West | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | Min Voltage at Constrained Conductor | 68.9894 | 69.0161 | 69.5772 | 69.585 | 69.5833
NQ-Townsville Burdekin West | BEGA 1_Garbutt-Belgian Gardens No1 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Townsville Burdekin West | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | % of Rated A | 2.923% | 2.888% | 2.892% | 2.883% | 2.88%
NQ-Townsville Burdekin West | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | Limiting Line Name | TR_CABLE 16086_1 | TR_CABLE 16086_1 | TR_CABLE 16086_1 | TR_CABLE 16086_1 | TR_CABLE 16086_1
NQ-Townsville Burdekin West | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | Loading (A) | 23.2094 | 22.9333 | 22.9589 | 22.8902 | 22.8658
NQ-Townsville Burdekin West | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | Loading (MVA) | 2.7734 | 2.7414 | 2.7668 | 2.7588 | 2.7558
NQ-Townsville Burdekin West | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | Loading (MW) | 0.60247 | 0.41192 | 0.25414 | 0.12663 | 0.0099817
NQ-Townsville Burdekin West | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | Power Factor | 0.21723 | 0.15026 | 0.091854 | 0.045901 | 0.0006047
NQ-Townsville Burdekin West | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | Rating (A) | 794 | 794 | 794 | 794 | 794
NQ-Townsville Burdekin West | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | Min Voltage at Constrained Conductor | 68.9894 | 69.0161 | 69.5772 | 69.585 | 69.5833
NQ-Townsville Burdekin West | BEGA 2_Garbutt-Belgian Gardens No2 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Townsville Burdekin West | BO-DG-1_Bohle-Dan Gleeson 66 kV | % of Rated A | 16.42% | 21.17% | 24.44% | 30.56% | 37.17%
NQ-Townsville Burdekin West | BO-DG-1_Bohle-Dan Gleeson 66 kV | Limiting Line Name | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1 | TR_CABLE 3768_1
NQ-Townsville Burdekin West | BO-DG-1_Bohle-Dan Gleeson 66 kV | Loading (A) | 73.3855 | 94.6256 | 109.2501 | 136.6096 | 166.1583
NQ-Townsville Burdekin West | BO-DG-1_Bohle-Dan Gleeson 66 kV | Loading (MVA) | 8.7403 | 11.2753 | 13.1834 | 16.4869 | 20.0533
NQ-Townsville Burdekin West | BO-DG-1_Bohle-Dan Gleeson 66 kV | Loading (MW) | 6.8019 | 9.9656 | 13.1027 | 16.4627 | 20.0533
NQ-Townsville Burdekin West | BO-DG-1_Bohle-Dan Gleeson 66 kV | Power Factor | 0.77763 | 0.88336 | 0.99346 | 0.99817 | 0.9999
NQ-Townsville Burdekin West | BO-DG-1_Bohle-Dan Gleeson 66 kV | Rating (A) | 447 | 447 | 447 | 447 | 447
NQ-Townsville Burdekin West | BO-DG-1_Bohle-Dan Gleeson 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | BO-DG-1_Bohle-Dan Gleeson 66 kV | Min Voltage at Constrained Conductor | 68.7633 | 68.7954 | 69.6698 | 69.6781 | 69.6747
NQ-Townsville Burdekin West | BO-DG-1_Bohle-Dan Gleeson 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Townsville Burdekin West | CHTO_Clare South - Charters Towers 66 kV | % of Rated A | 55.56% | 55.56% | 55.52% | 55.52% | 55.53%
NQ-Townsville Burdekin West | CHTO_Clare South - Charters Towers 66 kV | Limiting Line Name | TR_LINE 33612_1 | TR_LINE 33612_1 | TR_LINE 33612_1 | TR_LINE 33612_1 | TR_LINE 33612_1
NQ-Townsville Burdekin West | CHTO_Clare South - Charters Towers 66 kV | Loading (A) | 110.5739 | 110.5563 | 110.4927 | 110.4927 | 110.4999
NQ-Townsville Burdekin West | CHTO_Clare South - Charters Towers 66 kV | Loading (MVA) | 12.7158 | 12.7158 | 12.7157 | 12.7157 | 12.7157
NQ-Townsville Burdekin West | CHTO_Clare South - Charters Towers 66 kV | Loading (MW) | 12.7075 | 12.7074 | 12.7074 | 12.7074 | 12.7074
NQ-Townsville Burdekin West | CHTO_Clare South - Charters Towers 66 kV | Power Factor | 0.99935 | 0.99935 | 0.99935 | 0.99935 | 0.99935
NQ-Townsville Burdekin West | CHTO_Clare South - Charters Towers 66 kV | Rating (A) | 199 | 199 | 199 | 199 | 199
NQ-Townsville Burdekin West | CHTO_Clare South - Charters Towers 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | CHTO_Clare South - Charters Towers 66 kV | Min Voltage at Constrained Conductor | 66.3803 | 66.3908 | 66.4288 | 66.4288 | 66.4245
NQ-Townsville Burdekin West | CHTO_Clare South - Charters Towers 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Townsville Burdekin West | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | % of Rated A | 6.9% | 6.529% | 7.685% | 10.23% | 14.02%
NQ-Townsville Burdekin West | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Limiting Line Name | TR_LINE 102266_1 | TR_LINE 102266_1 | TR_LINE 102266_1 | TR_LINE 102266_1 | TR_LINE 102266_1
NQ-Townsville Burdekin West | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Loading (A) | 21.5293 | 20.3699 | 23.9781 | 31.9234 | 43.7435
NQ-Townsville Burdekin West | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Loading (MVA) | 2.5267 | 2.3908 | 2.8146 | 3.7471 | 5.134
NQ-Townsville Burdekin West | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Loading (MW) | 0.89708 | 0.29593 | 1.5366 | 2.9481 | 4.6289
NQ-Townsville Burdekin West | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Power Factor | 0.35503 | 0.12376 | 0.54591 | 0.78675 | 0.90158
NQ-Townsville Burdekin West | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Rating (A) | 312 | 312 | 312 | 312 | 312
NQ-Townsville Burdekin West | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Min Voltage at Constrained Conductor | 67.7598 | 67.7622 | 67.7708 | 67.768 | 67.7613
NQ-Townsville Burdekin West | CLSO-HOHI-1_Clare South-HOHI No 1 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Townsville Burdekin West | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | % of Rated A | 10.98% | 10.25% | 12.55% | 17.39% | 24.37%
NQ-Townsville Burdekin West | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Limiting Line Name | TR_LINE 147761_2 | TR_LINE 147761_2 | TR_LINE 147761_2 | TR_LINE 147761_2 | TR_LINE 147761_2
NQ-Townsville Burdekin West | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Loading (A) | 18.5509 | 17.3266 | 21.2137 | 29.3899 | 41.1783
NQ-Townsville Burdekin West | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Loading (MVA) | 2.1836 | 2.0421 | 2.5037 | 3.4735 | 4.8741
NQ-Townsville Burdekin West | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Loading (MW) | 0.7356 | 0.40961 | 1.6024 | 2.962 | 4.5846
NQ-Townsville Burdekin West | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Power Factor | 0.33688 | 0.20055 | 0.63997 | 0.85269 | 0.94051
NQ-Townsville Burdekin West | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Rating (A) | 169 | 169 | 169 | 169 | 169
NQ-Townsville Burdekin West | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Min Voltage at Constrained Conductor | 67.9575 | 68.0461 | 68.1416 | 68.2349 | 68.3386
NQ-Townsville Burdekin West | CLSO-HOHI-2_Clare South-HOHI No 2 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Townsville Burdekin West | CR-HU-1_Cape River-Hughenden No 1 66 kV | % of Rated A | 15.13% | 14.87% | 16.87% | 16.4% | 16.04%
NQ-Townsville Burdekin West | CR-HU-1_Cape River-Hughenden No 1 66 kV | Limiting Line Name | TR_LINE 53284_2 | TR_LINE 53284_2 | TR_LINE 53284_2 | TR_LINE 53284_2 | TR_LINE 53284_2
NQ-Townsville Burdekin West | CR-HU-1_Cape River-Hughenden No 1 66 kV | Loading (A) | 21.6335 | 21.267 | 24.1245 | 23.4577 | 22.94
NQ-Townsville Burdekin West | CR-HU-1_Cape River-Hughenden No 1 66 kV | Loading (MVA) | 2.5492 | 2.507 | 2.8378 | 2.7599 | 2.6998
NQ-Townsville Burdekin West | CR-HU-1_Cape River-Hughenden No 1 66 kV | Loading (MW) | 0.70614 | 0.58302 | 1.4073 | 1.3015 | 1.1868
NQ-Townsville Burdekin West | CR-HU-1_Cape River-Hughenden No 1 66 kV | Power Factor | 0.27701 | 0.23256 | 0.49589 | 0.47157 | 0.43959
NQ-Townsville Burdekin West | CR-HU-1_Cape River-Hughenden No 1 66 kV | Rating (A) | 143 | 143 | 143 | 143 | 143
NQ-Townsville Burdekin West | CR-HU-1_Cape River-Hughenden No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | CR-HU-1_Cape River-Hughenden No 1 66 kV | Min Voltage at Constrained Conductor | 68.0316 | 68.0579 | 67.9148 | 67.9274 | 67.9485
NQ-Townsville Burdekin West | CR-HU-1_Cape River-Hughenden No 1 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Townsville Burdekin West | CS-ML-1_Clare South - Millaroo 66 kV | % of Rated A | 2.624% | 3.197% | 3.972% | 4.889% | 5.935%
NQ-Townsville Burdekin West | CS-ML-1_Clare South - Millaroo 66 kV | Limiting Line Name | TR_LINE 102260_1 | TR_LINE 102260_1 | TR_LINE 102260_1 | TR_LINE 102260_1 | TR_LINE 102260_1
NQ-Townsville Burdekin West | CS-ML-1_Clare South - Millaroo 66 kV | Loading (A) | 5.1168 | 6.2349 | 7.7444 | 9.5336 | 11.574
NQ-Townsville Burdekin West | CS-ML-1_Clare South - Millaroo 66 kV | Loading (MVA) | 0.60052 | 0.73175 | 0.90903 | 1.119 | 1.3583
NQ-Townsville Burdekin West | CS-ML-1_Clare South - Millaroo 66 kV | Loading (MW) | 0.30204 | 0.51716 | 0.74877 | 0.9951 | 1.2605
NQ-Townsville Burdekin West | CS-ML-1_Clare South - Millaroo 66 kV | Power Factor | 0.50297 | 0.70673 | 0.8237 | 0.88928 | 0.92796
NQ-Townsville Burdekin West | CS-ML-1_Clare South - Millaroo 66 kV | Rating (A) | 195 | 195 | 195 | 195 | 195
NQ-Townsville Burdekin West | CS-ML-1_Clare South - Millaroo 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | CS-ML-1_Clare South - Millaroo 66 kV | Min Voltage at Constrained Conductor | 67.7585 | 67.7604 | 67.7685 | 67.7653 | 67.758
NQ-Townsville Burdekin West | CS-ML-1_Clare South - Millaroo 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Townsville Burdekin West | CT-CR-1_Charters Towers-CARI No 1 66 kV | % of Rated A | 6.25% | 6.441% | 8.578% | 7.813% | 7.188%
NQ-Townsville Burdekin West | CT-CR-1_Charters Towers-CARI No 1 66 kV | Limiting Line Name | TR_LINE 64805_1 | TR_LINE 64805_1 | TR_LINE 31871_1 | TR_LINE 31871_1 | TR_LINE 64805_1
NQ-Townsville Burdekin West | CT-CR-1_Charters Towers-CARI No 1 66 kV | Loading (A) | 11.7503 | 12.1083 | 15.7828 | 14.3761 | 13.5138
NQ-Townsville Burdekin West | CT-CR-1_Charters Towers-CARI No 1 66 kV | Loading (MVA) | 1.3846 | 1.4273 | 1.8856 | 1.7175 | 1.5904
NQ-Townsville Burdekin West | CT-CR-1_Charters Towers-CARI No 1 66 kV | Loading (MW) | 0.80375 | 0.65916 | 1.6919 | 1.5607 | 1.4043
NQ-Townsville Burdekin West | CT-CR-1_Charters Towers-CARI No 1 66 kV | Power Factor | 0.57949 | 0.46078 | 0.89729 | 0.90867 | 0.88178
NQ-Townsville Burdekin West | CT-CR-1_Charters Towers-CARI No 1 66 kV | Rating (A) | 188 | 188 | 184 | 184 | 188
NQ-Townsville Burdekin West | CT-CR-1_Charters Towers-CARI No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | CT-CR-1_Charters Towers-CARI No 1 66 kV | Min Voltage at Constrained Conductor | 68.0316 | 68.0579 | 68.9706 | 68.9714 | 67.9485
NQ-Townsville Burdekin West | CT-CR-1_Charters Towers-CARI No 1 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Townsville Burdekin West | CT-MR-1_Millchester-CHTO No 1 66 kV | % of Rated A | 17.54% | 16.96% | 16.33% | 15.93% | 15.61%
NQ-Townsville Burdekin West | CT-MR-1_Millchester-CHTO No 1 66 kV | Limiting Line Name | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1 | TR_LINE 178657_1
NQ-Townsville Burdekin West | CT-MR-1_Millchester-CHTO No 1 66 kV | Loading (A) | 48.7508 | 47.1501 | 45.3861 | 44.2908 | 43.3849
NQ-Townsville Burdekin West | CT-MR-1_Millchester-CHTO No 1 66 kV | Loading (MVA) | 5.8164 | 5.6268 | 5.4222 | 5.2914 | 5.183
NQ-Townsville Burdekin West | CT-MR-1_Millchester-CHTO No 1 66 kV | Loading (MW) | 4.3737 | 4.054 | 3.7412 | 3.4322 | 3.0955
NQ-Townsville Burdekin West | CT-MR-1_Millchester-CHTO No 1 66 kV | Power Factor | 0.75193 | 0.72046 | 0.68994 | 0.6486 | 0.59721
NQ-Townsville Burdekin West | CT-MR-1_Millchester-CHTO No 1 66 kV | Rating (A) | 278 | 278 | 278 | 278 | 278
NQ-Townsville Burdekin West | CT-MR-1_Millchester-CHTO No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | CT-MR-1_Millchester-CHTO No 1 66 kV | Min Voltage at Constrained Conductor | 68.883 | 68.8993 | 68.9757 | 68.9764 | 68.9737
NQ-Townsville Burdekin West | CT-MR-1_Millchester-CHTO No 1 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Townsville Burdekin West | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | % of Rated A | 15.82% | 15.95% | 8.457% | 8.532% | 8.683%
NQ-Townsville Burdekin West | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Limiting Line Name | TR_LINE 126322_1 | TR_LINE 126322_1 | TR_LINE 126322_1 | TR_LINE 126322_1 | TR_LINE 126322_1
NQ-Townsville Burdekin West | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Loading (A) | 71.5285 | 72.0819 | 38.2264 | 38.565 | 39.2449
NQ-Townsville Burdekin West | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Loading (MVA) | 8.5305 | 8.5998 | 4.6144 | 4.6556 | 4.7374
NQ-Townsville Burdekin West | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Loading (MW) | 1.4203 | 1.0057 | 0.77688 | 0.34937 | 0.077195
NQ-Townsville Burdekin West | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Power Factor | 0.16644 | 0.11688 | 0.16836 | 0.075042 | 0.016242
NQ-Townsville Burdekin West | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Rating (A) | 452 | 452 | 452 | 452 | 452
NQ-Townsville Burdekin West | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Min Voltage at Constrained Conductor | 68.8545 | 68.8811 | 69.6937 | 69.6989 | 69.694
NQ-Townsville Burdekin West | DG-CB-1_Dan Gleeson-Cranbrook No 1 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Townsville Burdekin West | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | % of Rated A | 5.543% | 5.71% | 3.982% | 4.012% | 4.16%
NQ-Townsville Burdekin West | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Limiting Line Name | TR_LINE 172527_2 | TR_LINE 172527_2 | TR_LINE 32461_1 | TR_LINE 32461_1 | TR_LINE 32461_1
NQ-Townsville Burdekin West | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Loading (A) | 30.5394 | 31.4615 | 21.9422 | 22.1079 | 22.9199
NQ-Townsville Burdekin West | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Loading (MVA) | 3.6359 | 3.7469 | 2.6447 | 2.6649 | 2.7626
NQ-Townsville Burdekin West | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Loading (MW) | 1.3147 | 1.2583 | 2.5383 | 2.5993 | 2.7332
NQ-Townsville Burdekin West | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Power Factor | 0.36152 | 0.33578 | 0.95975 | 0.97539 | 0.98937
NQ-Townsville Burdekin West | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Rating (A) | 551 | 551 | 551 | 551 | 551
NQ-Townsville Burdekin West | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Min Voltage at Constrained Conductor | 68.7367 | 68.759 | 69.5883 | 69.5931 | 69.5895
NQ-Townsville Burdekin West | DG-PA-1_Dan Gleeson-Peter Arlett 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Townsville Burdekin West | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | % of Rated A | 21.31% | 22.55% | 23.4% | 24.5% | 25.66%
NQ-Townsville Burdekin West | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Limiting Line Name | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1 | TR_LINE 157868_1
NQ-Townsville Burdekin West | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Loading (A) | 53.4997 | 56.6015 | 58.7428 | 61.4901 | 64.4026
NQ-Townsville Burdekin West | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Loading (MVA) | 6.362 | 6.7328 | 7.0802 | 7.4112 | 7.761
NQ-Townsville Burdekin West | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Loading (MW) | 5.6179 | 6.0132 | 7.0492 | 7.3769 | 7.7221
NQ-Townsville Burdekin West | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Power Factor | 0.88305 | 0.89312 | 0.99563 | 0.99537 | 0.99498
NQ-Townsville Burdekin West | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Rating (A) | 251 | 251 | 251 | 251 | 251
NQ-Townsville Burdekin West | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Min Voltage at Constrained Conductor | 68.6563 | 68.676 | 69.5871 | 69.5862 | 69.5753
NQ-Townsville Burdekin West | DG-RM-1_Dan Gleeson-Rasmussen 1 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Townsville Burdekin West | EAAY_Clare South - East Ayr 66 kV | % of Rated A | 12% | 10.23% | 9.656% | 10.63% | 13.28%
NQ-Townsville Burdekin West | EAAY_Clare South - East Ayr 66 kV | Limiting Line Name | TR_LINE 183529_1 | TR_LINE 183529_1 | TR_LINE 183529_1 | TR_LINE 183529_1 | TR_LINE 183529_1
NQ-Townsville Burdekin West | EAAY_Clare South - East Ayr 66 kV | Loading (A) | 25.2032 | 21.4745 | 20.2767 | 22.3144 | 27.885
NQ-Townsville Burdekin West | EAAY_Clare South - East Ayr 66 kV | Loading (MVA) | 2.9724 | 2.5366 | 2.3989 | 2.644 | 3.3093
NQ-Townsville Burdekin West | EAAY_Clare South - East Ayr 66 kV | Loading (MW) | 1.8248 | 0.87975 | 0.069673 | 1.1054 | 2.2941
NQ-Townsville Burdekin West | EAAY_Clare South - East Ayr 66 kV | Power Factor | 0.61392 | 0.34682 | 0.029009 | 0.41803 | 0.69317
NQ-Townsville Burdekin West | EAAY_Clare South - East Ayr 66 kV | Rating (A) | 210 | 210 | 210 | 210 | 210
NQ-Townsville Burdekin West | EAAY_Clare South - East Ayr 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | EAAY_Clare South - East Ayr 66 kV | Min Voltage at Constrained Conductor | 68.0921 | 68.1979 | 68.3067 | 68.4091 | 68.5177
NQ-Townsville Burdekin West | EAAY_Clare South - East Ayr 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Townsville Burdekin West | GA-BO-1_Garbutt-Bohle No 1 66 kV | % of Rated A | 12.83% | 18.28% | 23.32% | 28.59% | 34.26%
NQ-Townsville Burdekin West | GA-BO-1_Garbutt-Bohle No 1 66 kV | Limiting Line Name | TR_LINE 32140_1 | TR_LINE 32140_1 | TR_LINE 128084_1 | TR_LINE 128084_1 | TR_LINE 32140_1
NQ-Townsville Burdekin West | GA-BO-1_Garbutt-Bohle No 1 66 kV | Loading (A) | 70.6844 | 100.7475 | 128.4725 | 157.5244 | 188.7477
NQ-Townsville Burdekin West | GA-BO-1_Garbutt-Bohle No 1 66 kV | Loading (MVA) | 8.4548 | 12.0628 | 15.4829 | 18.9864 | 22.8697
NQ-Townsville Burdekin West | GA-BO-1_Garbutt-Bohle No 1 66 kV | Loading (MW) | 8.3041 | 11.8969 | 15.4482 | 18.9838 | 22.8662
NQ-Townsville Burdekin West | GA-BO-1_Garbutt-Bohle No 1 66 kV | Power Factor | 0.98217 | 0.98625 | 0.99776 | 0.99986 | 0.99984
NQ-Townsville Burdekin West | GA-BO-1_Garbutt-Bohle No 1 66 kV | Rating (A) | 551 | 551 | 551 | 551 | 551
NQ-Townsville Burdekin West | GA-BO-1_Garbutt-Bohle No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | GA-BO-1_Garbutt-Bohle No 1 66 kV | Min Voltage at Constrained Conductor | 69.059 | 69.1274 | 69.5772 | 69.585 | 69.9537
NQ-Townsville Burdekin West | GA-BO-1_Garbutt-Bohle No 1 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Townsville Burdekin West | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | % of Rated A | 10.83% | 11.62% | 16.14% | 16.79% | 17.57%
NQ-Townsville Burdekin West | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Limiting Line Name | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1 | TR_LINE 36521_1
NQ-Townsville Burdekin West | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Loading (A) | 37.3662 | 40.094 | 55.6796 | 57.9294 | 60.6026
NQ-Townsville Burdekin West | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Loading (MVA) | 4.4648 | 4.7929 | 6.7101 | 6.9824 | 7.3049
NQ-Townsville Burdekin West | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Loading (MW) | 3.5052 | 4.0365 | 5.6327 | 6.0728 | 6.5554
NQ-Townsville Burdekin West | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Power Factor | 0.78507 | 0.84219 | 0.83942 | 0.86973 | 0.8974
NQ-Townsville Burdekin West | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Rating (A) | 345 | 345 | 345 | 345 | 345
NQ-Townsville Burdekin West | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Min Voltage at Constrained Conductor | 68.9866 | 69.017 | 69.5783 | 69.5886 | 69.5899
NQ-Townsville Burdekin West | GA-HP-1_Garbutt-Hermit Park No 1 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Townsville Burdekin West | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | % of Rated A | 18.5% | 18.2% | 17.86% | 17.69% | 17.6%
NQ-Townsville Burdekin West | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Limiting Line Name | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1 | TR_LINE 32540_1
NQ-Townsville Burdekin West | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Loading (A) | 31.2573 | 30.7658 | 30.1816 | 29.9008 | 29.747
NQ-Townsville Burdekin West | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Loading (MVA) | 3.7345 | 3.6773 | 3.6368 | 3.6034 | 3.5847
NQ-Townsville Burdekin West | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Loading (MW) | 3.6515 | 3.5923 | 3.5471 | 3.5125 | 3.4932
NQ-Townsville Burdekin West | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Power Factor | 0.97777 | 0.97689 | 0.97534 | 0.97478 | 0.97447
NQ-Townsville Burdekin West | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Rating (A) | 169 | 169 | 169 | 169 | 169
NQ-Townsville Burdekin West | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Min Voltage at Constrained Conductor | 68.9797 | 69.0067 | 69.5682 | 69.5761 | 69.5744
NQ-Townsville Burdekin West | GA-NS-1_Garbutt-Neil Smith No 1 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Townsville Burdekin West | GA-TP-1_Garbutt-Townsville Port 1 66 kV | % of Rated A | 38.48% | 34.66% | 17.97% | 14.53% | 11.26%
NQ-Townsville Burdekin West | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Limiting Line Name | TR_LINE 161962_1 | TR_LINE 161962_1 | TR_LINE 161962_1 | TR_LINE 161962_1 | TR_LINE 161962_1
NQ-Townsville Burdekin West | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Loading (A) | 99.2888 | 89.4298 | 46.3661 | 37.4862 | 29.0386
NQ-Townsville Burdekin West | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Loading (MVA) | 11.8294 | 10.6532 | 5.5849 | 4.5146 | 3.4962
NQ-Townsville Burdekin West | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Loading (MW) | 6.2896 | 4.3314 | 4.0909 | 2.8503 | 1.5536
NQ-Townsville Burdekin West | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Power Factor | 0.53163 | 0.40653 | 0.73249 | 0.63135 | 0.44438
NQ-Townsville Burdekin West | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Rating (A) | 258 | 258 | 258 | 258 | 258
NQ-Townsville Burdekin West | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Min Voltage at Constrained Conductor | 68.7863 | 68.7763 | 69.5428 | 69.5316 | 69.5121
NQ-Townsville Burdekin West | GA-TP-1_Garbutt-Townsville Port 1 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Townsville Burdekin West | GARB-12 11kV | % of Rated A | 0.6938% | 0.6942% | 0.6917% | 0.6919% | 0.692%
NQ-Townsville Burdekin West | GARB-12 11kV | Limiting Line Name | HV_CABLE 14927_1 | HV_CABLE 14927_1 | HV_CABLE 14927_1 | HV_CABLE 14927_1 | HV_CABLE 14927_1
NQ-Townsville Burdekin West | GARB-12 11kV | Loading (A) | 2.7752 | 2.7766 | 2.767 | 2.7676 | 2.7679
NQ-Townsville Burdekin West | GARB-12 11kV | Loading (MVA) | 0.05201 | 0.052063 | 0.051702 | 0.051725 | 0.051736
NQ-Townsville Burdekin West | GARB-12 11kV | Loading (MW) | 0.0010416 | 0.0010427 | 0.0010355 | 0.0010359 | 0.0010361
NQ-Townsville Burdekin West | GARB-12 11kV | Power Factor | 0.020021 | 0.020021 | 0.020021 | 0.020021 | 0.020021
NQ-Townsville Burdekin West | GARB-12 11kV | Rating (A) | 400 | 400 | 400 | 400 | 400
NQ-Townsville Burdekin West | GARB-12 11kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | GARB-12 11kV | Min Voltage at Constrained Conductor | 10.8201 | 10.8256 | 10.788 | 10.7904 | 10.7916
NQ-Townsville Burdekin West | GARB-12 11kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Townsville Burdekin West | GI-AY-1_Giru - Ayr 1 66 kV | % of Rated A | 4.334% | 5.53% | 6.923% | 8.431% | 10.06%
NQ-Townsville Burdekin West | GI-AY-1_Giru - Ayr 1 66 kV | Limiting Line Name | TR_LINE 170050_1 | TR_LINE 170050_1 | TR_LINE 170050_1 | TR_LINE 170050_1 | TR_LINE 170050_1
NQ-Townsville Burdekin West | GI-AY-1_Giru - Ayr 1 66 kV | Loading (A) | 8.1911 | 10.4519 | 13.0851 | 15.9355 | 19.0192
NQ-Townsville Burdekin West | GI-AY-1_Giru - Ayr 1 66 kV | Loading (MVA) | 0.96522 | 1.234 | 1.548 | 1.8889 | 2.2591
NQ-Townsville Burdekin West | GI-AY-1_Giru - Ayr 1 66 kV | Loading (MW) | 0.59834 | 0.97521 | 1.3531 | 1.7359 | 2.1366
NQ-Townsville Burdekin West | GI-AY-1_Giru - Ayr 1 66 kV | Power Factor | 0.6199 | 0.79025 | 0.8741 | 0.91901 | 0.94576
NQ-Townsville Burdekin West | GI-AY-1_Giru - Ayr 1 66 kV | Rating (A) | 189 | 189 | 189 | 189 | 189
NQ-Townsville Burdekin West | GI-AY-1_Giru - Ayr 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | GI-AY-1_Giru - Ayr 1 66 kV | Min Voltage at Constrained Conductor | 68.0333 | 68.1672 | 68.3038 | 68.4362 | 68.5783
NQ-Townsville Burdekin West | GI-AY-1_Giru - Ayr 1 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Townsville Burdekin West | HP-OO_Hermit park - Oonoonba 66 kV | % of Rated A | 16.43% | 15.51% | 18.31% | 17.45% | 16.65%
NQ-Townsville Burdekin West | HP-OO_Hermit park - Oonoonba 66 kV | Limiting Line Name | TR_LINE 106404_1 | TR_LINE 106404_1 | TR_LINE 106404_1 | TR_LINE 106404_1 | TR_LINE 106404_1
NQ-Townsville Burdekin West | HP-OO_Hermit park - Oonoonba 66 kV | Loading (A) | 56.6797 | 53.4947 | 63.1585 | 60.2033 | 57.4439
NQ-Townsville Burdekin West | HP-OO_Hermit park - Oonoonba 66 kV | Loading (MVA) | 6.775 | 6.3973 | 7.6121 | 7.2575 | 6.9256
NQ-Townsville Burdekin West | HP-OO_Hermit park - Oonoonba 66 kV | Loading (MW) | 6.1646 | 5.8247 | 6.6482 | 6.3511 | 6.0944
NQ-Townsville Burdekin West | HP-OO_Hermit park - Oonoonba 66 kV | Power Factor | 0.9099 | 0.91049 | 0.87338 | 0.87512 | 0.87997
NQ-Townsville Burdekin West | HP-OO_Hermit park - Oonoonba 66 kV | Rating (A) | 345 | 345 | 345 | 345 | 345
NQ-Townsville Burdekin West | HP-OO_Hermit park - Oonoonba 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | HP-OO_Hermit park - Oonoonba 66 kV | Min Voltage at Constrained Conductor | 69.0093 | 69.042 | 69.5831 | 69.598 | 69.6058
NQ-Townsville Burdekin West | HP-OO_Hermit park - Oonoonba 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Townsville Burdekin West | HU-RI-1_Hughenden-Richmond No 1 66 kV | % of Rated A | 11.15% | 11.12% | 13.85% | 13.63% | 13.43%
NQ-Townsville Burdekin West | HU-RI-1_Hughenden-Richmond No 1 66 kV | Limiting Line Name | TR_LINE 163222_1 | TR_LINE 163222_1 | TR_LINE 163222_1 | TR_LINE 163222_1 | TR_LINE 163222_1
NQ-Townsville Burdekin West | HU-RI-1_Hughenden-Richmond No 1 66 kV | Loading (A) | 31.7856 | 31.7044 | 39.4817 | 38.8576 | 38.2815
NQ-Townsville Burdekin West | HU-RI-1_Hughenden-Richmond No 1 66 kV | Loading (MVA) | 3.8014 | 3.7966 | 4.683 | 4.6122 | 4.5493
NQ-Townsville Burdekin West | HU-RI-1_Hughenden-Richmond No 1 66 kV | Loading (MW) | 0.59615 | 0.44136 | 3.1883 | 3.061 | 2.939
NQ-Townsville Burdekin West | HU-RI-1_Hughenden-Richmond No 1 66 kV | Power Factor | 0.15682 | 0.11625 | 0.68083 | 0.66368 | 0.64604
NQ-Townsville Burdekin West | HU-RI-1_Hughenden-Richmond No 1 66 kV | Rating (A) | 285 | 285 | 285 | 285 | 285
NQ-Townsville Burdekin West | HU-RI-1_Hughenden-Richmond No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | HU-RI-1_Hughenden-Richmond No 1 66 kV | Min Voltage at Constrained Conductor | 69.0478 | 69.1385 | 68.4809 | 68.5291 | 68.611
NQ-Townsville Burdekin West | HU-RI-1_Hughenden-Richmond No 1 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Townsville Burdekin West | HU-WI-1 Hughenden-Winton No 1 66 kV | % of Rated A | 10.39% | 10.32% | 10.16% | 10.09% | 10.01%
NQ-Townsville Burdekin West | HU-WI-1 Hughenden-Winton No 1 66 kV | Limiting Line Name | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2 | TR_LINE 33076_2
NQ-Townsville Burdekin West | HU-WI-1 Hughenden-Winton No 1 66 kV | Loading (A) | 27.2231 | 27.0445 | 26.6215 | 26.4254 | 26.2345
NQ-Townsville Burdekin West | HU-WI-1 Hughenden-Winton No 1 66 kV | Loading (MVA) | 3.2495 | 3.2323 | 3.1543 | 3.1331 | 3.1141
NQ-Townsville Burdekin West | HU-WI-1 Hughenden-Winton No 1 66 kV | Loading (MW) | 0.87877 | 0.75163 | 0.61658 | 0.46439 | 0.27864
NQ-Townsville Burdekin West | HU-WI-1 Hughenden-Winton No 1 66 kV | Power Factor | 0.27043 | 0.23254 | 0.19547 | 0.14822 | 0.089478
NQ-Townsville Burdekin West | HU-WI-1 Hughenden-Winton No 1 66 kV | Rating (A) | 262 | 262 | 262 | 262 | 262
NQ-Townsville Burdekin West | HU-WI-1 Hughenden-Winton No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | HU-WI-1 Hughenden-Winton No 1 66 kV | Min Voltage at Constrained Conductor | 68.9162 | 69.0036 | 68.4079 | 68.453 | 68.532
NQ-Townsville Burdekin West | HU-WI-1 Hughenden-Winton No 1 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Townsville Burdekin West | HUGH-HU-20 | % of Rated A | 2.845e-08% | 2.79e-08% | 2.453e-06% | 4.377e-06% | 3.498e-06%
NQ-Townsville Burdekin West | HUGH-HU-20 | Limiting Line Name | Link_HUGH_B624_HU-20 TORRENS CK | Link_HUGH_B624_HU-20 TORRENS CK | Link_HUGH_B624_HU-20 TORRENS CK | Link_HUGH_B624_HU-20 TORRENS CK | Link_HUGH_B624_HU-20 TORRENS CK
NQ-Townsville Burdekin West | HUGH-HU-20 | Loading (A) | 1.4225e-06 | 1.3948e-06 | 0.00012265 | 0.00021883 | 0.00017489
NQ-Townsville Burdekin West | HUGH-HU-20 | Loading (MVA) | 8.1824e-08 | 8.0336e-08 | 7.0034e-06 | 1.2504e-05 | 1.0005e-05
NQ-Townsville Burdekin West | HUGH-HU-20 | Loading (MW) | 8.1824e-08 | 8.0336e-08 | 6.788e-07 | 3.663e-06 | 2.2418e-06
NQ-Townsville Burdekin West | HUGH-HU-20 | Power Factor | 1 | 1 | 0.096923 | 0.29295 | 0.22407
NQ-Townsville Burdekin West | HUGH-HU-20 | Rating (A) | 5000 | 5000 | 5000 | 5000 | 5000
NQ-Townsville Burdekin West | HUGH-HU-20 | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | HUGH-HU-20 | Min Voltage at Constrained Conductor | 33.21 | 33.2533 | 32.967 | 32.9894 | 33.028
NQ-Townsville Burdekin West | HUGH-HU-20 | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Townsville Burdekin West | HUGH-HU-40 | % of Rated A | 3.873e-09% | 3.879e-09% | 3.845e-09% | 3.848e-09% | 3.852e-09%
NQ-Townsville Burdekin West | HUGH-HU-40 | Limiting Line Name | Link_HUGH_D624_HU-40 RICHMOND | Link_HUGH_D624_HU-40 RICHMOND | Link_HUGH_D624_HU-40 RICHMOND | Link_HUGH_D624_HU-40 RICHMOND | Link_HUGH_D624_HU-40 RICHMOND
NQ-Townsville Burdekin West | HUGH-HU-40 | Loading (A) | 1.9367e-07 | 1.9393e-07 | 1.9226e-07 | 1.9239e-07 | 1.9261e-07
NQ-Townsville Burdekin West | HUGH-HU-40 | Loading (MVA) | 1.114e-08 | 1.1169e-08 | 1.0978e-08 | 1.0993e-08 | 1.1019e-08
NQ-Townsville Burdekin West | HUGH-HU-40 | Loading (MW) | 1.114e-08 | 1.1169e-08 | 1.0978e-08 | 1.0993e-08 | 1.1019e-08
NQ-Townsville Burdekin West | HUGH-HU-40 | Power Factor | 1 | 1 | 1 | 1 | 1
NQ-Townsville Burdekin West | HUGH-HU-40 | Rating (A) | 5000 | 5000 | 5000 | 5000 | 5000
NQ-Townsville Burdekin West | HUGH-HU-40 | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | HUGH-HU-40 | Min Voltage at Constrained Conductor | 33.21 | 33.2533 | 32.967 | 32.9894 | 33.028
NQ-Townsville Burdekin West | HUGH-HU-40 | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Townsville Burdekin West | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | % of Rated A | 7.291% | 8.082% | 9.329% | 11.21% | 13.91%
NQ-Townsville Burdekin West | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Limiting Line Name | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1 | TR_LINE 32557_1
NQ-Townsville Burdekin West | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Loading (A) | 12.3212 | 13.6592 | 15.7655 | 18.9375 | 23.4997
NQ-Townsville Burdekin West | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Loading (MVA) | 1.4544 | 1.6154 | 1.8681 | 2.248 | 2.7951
NQ-Townsville Burdekin West | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Loading (MW) | 0.65567 | 0.96532 | 1.3383 | 1.8152 | 2.4362
NQ-Townsville Burdekin West | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Power Factor | 0.45081 | 0.59757 | 0.71643 | 0.80745 | 0.87159
NQ-Townsville Burdekin West | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Rating (A) | 169 | 169 | 169 | 169 | 169
NQ-Townsville Burdekin West | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Min Voltage at Constrained Conductor | 68.1514 | 68.2798 | 68.4106 | 68.5363 | 68.6704
NQ-Townsville Burdekin West | JA-EA-1_Jarvisfield-East Ayr No 1 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Townsville Burdekin West | KA-AY-01_Ayr - Kalamia No 1 66 kV | % of Rated A | 0.7989% | 0.8211% | 0.8812% | 0.9576% | 1.041%
NQ-Townsville Burdekin West | KA-AY-01_Ayr - Kalamia No 1 66 kV | Limiting Line Name | TR_LINE 31747_1 | TR_LINE 31747_1 | TR_LINE 31747_1 | TR_LINE 31747_1 | TR_LINE 31747_1
NQ-Townsville Burdekin West | KA-AY-01_Ayr - Kalamia No 1 66 kV | Loading (A) | 1.5899 | 1.634 | 1.7536 | 1.9056 | 2.0717
NQ-Townsville Burdekin West | KA-AY-01_Ayr - Kalamia No 1 66 kV | Loading (MVA) | 0.18734 | 0.19293 | 0.20746 | 0.22588 | 0.24608
NQ-Townsville Burdekin West | KA-AY-01_Ayr - Kalamia No 1 66 kV | Loading (MW) | 0.0083504 | 0.043791 | 0.086435 | 0.12329 | 0.15641
NQ-Townsville Burdekin West | KA-AY-01_Ayr - Kalamia No 1 66 kV | Power Factor | 0.044573 | 0.22698 | 0.41662 | 0.54583 | 0.63562
NQ-Townsville Burdekin West | KA-AY-01_Ayr - Kalamia No 1 66 kV | Rating (A) | 199 | 199 | 199 | 199 | 199
NQ-Townsville Burdekin West | KA-AY-01_Ayr - Kalamia No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | KA-AY-01_Ayr - Kalamia No 1 66 kV | Min Voltage at Constrained Conductor | 68.033 | 68.1668 | 68.3034 | 68.4358 | 68.5778
NQ-Townsville Burdekin West | KA-AY-01_Ayr - Kalamia No 1 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Townsville Burdekin West | MAFU-07_Max Fulton No 7 11 kV | % of Rated A | 1.181% | 1.18% | 1.18% | 1.18% | 1.18%
NQ-Townsville Burdekin West | MAFU-07_Max Fulton No 7 11 kV | Limiting Line Name | HV_CABLE MF-07A 12159603 | HV_CABLE MF-07A 12159603 | HV_CABLE MF-07A 12159603 | HV_CABLE MF-07A 12159603 | HV_CABLE MF-07A 12159603
NQ-Townsville Burdekin West | MAFU-07_Max Fulton No 7 11 kV | Loading (A) | 3.7194 | 3.718 | 3.7184 | 3.718 | 3.7171
NQ-Townsville Burdekin West | MAFU-07_Max Fulton No 7 11 kV | Loading (MVA) | 0.072756 | 0.072702 | 0.072717 | 0.0727 | 0.072666
NQ-Townsville Burdekin West | MAFU-07_Max Fulton No 7 11 kV | Loading (MW) | 0.0014566 | 0.0014555 | 0.0014558 | 0.0014555 | 0.0014548
NQ-Townsville Burdekin West | MAFU-07_Max Fulton No 7 11 kV | Power Factor | 0.020019 | 0.020019 | 0.020019 | 0.020019 | 0.020019
NQ-Townsville Burdekin West | MAFU-07_Max Fulton No 7 11 kV | Rating (A) | 315 | 315 | 315 | 315 | 315
NQ-Townsville Burdekin West | MAFU-07_Max Fulton No 7 11 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | MAFU-07_Max Fulton No 7 11 kV | Min Voltage at Constrained Conductor | 11.2937 | 11.2895 | 11.2907 | 11.2893 | 11.2867
NQ-Townsville Burdekin West | MAFU-07_Max Fulton No 7 11 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Townsville Burdekin West | MF-TP-1_Max Fulton-TOPO No 1 66 kV | % of Rated A | 3.568% | 5.315% | 4.528% | 3.837% | 3.14%
NQ-Townsville Burdekin West | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Limiting Line Name | TR_LINE 121605_1 | TR_LINE 121605_1 | TR_LINE 121605_1 | TR_LINE 121605_1 | TR_LINE 121605_1
NQ-Townsville Burdekin West | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Loading (A) | 9.2045 | 13.7137 | 11.6817 | 9.8986 | 8.1003
NQ-Townsville Burdekin West | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Loading (MVA) | 1.0953 | 1.6315 | 1.4065 | 1.1916 | 0.97487
NQ-Townsville Burdekin West | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Loading (MW) | 1.0711 | 1.6164 | 1.3875 | 1.1686 | 0.94595
NQ-Townsville Burdekin West | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Power Factor | 0.9779 | 0.99077 | 0.98648 | 0.98064 | 0.97033
NQ-Townsville Burdekin West | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Rating (A) | 258 | 258 | 258 | 258 | 258
NQ-Townsville Burdekin West | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Min Voltage at Constrained Conductor | 68.6998 | 68.6838 | 69.5153 | 69.5031 | 69.483
NQ-Townsville Burdekin West | MF-TP-1_Max Fulton-TOPO No 1 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Townsville Burdekin West | MF-TP-2_Max Fulton-TOPO No 2 66 kV | % of Rated A | 15.01% | 15.5% | 15.11% | 14.93% | 14.77%
NQ-Townsville Burdekin West | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Limiting Line Name | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1 | TR_LINE 31763_1
NQ-Townsville Burdekin West | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Loading (A) | 38.7368 | 39.9784 | 38.9867 | 38.5077 | 38.0951
NQ-Townsville Burdekin West | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Loading (MVA) | 4.6108 | 4.7575 | 4.6956 | 4.6371 | 4.5861
NQ-Townsville Burdekin West | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Loading (MW) | 1.0779 | 1.6232 | 1.3943 | 1.1754 | 0.95276
NQ-Townsville Burdekin West | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Power Factor | 0.23377 | 0.34118 | 0.29694 | 0.25347 | 0.20775
NQ-Townsville Burdekin West | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Rating (A) | 258 | 258 | 258 | 258 | 258
NQ-Townsville Burdekin West | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Min Voltage at Constrained Conductor | 68.722 | 68.7064 | 69.5374 | 69.525 | 69.5048
NQ-Townsville Burdekin West | MF-TP-2_Max Fulton-TOPO No 2 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Townsville Burdekin West | MOPA_Clare South - Mona Park 66 kV | % of Rated A | 12.36% | 10.8% | 10.62% | 12.16% | 15.47%
NQ-Townsville Burdekin West | MOPA_Clare South - Mona Park 66 kV | Limiting Line Name | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1 | TR_LINE 102255_1
NQ-Townsville Burdekin West | MOPA_Clare South - Mona Park 66 kV | Loading (A) | 25.9551 | 22.6829 | 22.3115 | 25.5384 | 32.4974
NQ-Townsville Burdekin West | MOPA_Clare South - Mona Park 66 kV | Loading (MVA) | 3.0461 | 2.6622 | 2.6189 | 2.9975 | 3.8139
NQ-Townsville Burdekin West | MOPA_Clare South - Mona Park 66 kV | Loading (MW) | 1.6205 | 0.60335 | 0.42692 | 1.5666 | 2.8854
NQ-Townsville Burdekin West | MOPA_Clare South - Mona Park 66 kV | Power Factor | 0.532 | 0.22664 | 0.16301 | 0.52261 | 0.75653
NQ-Townsville Burdekin West | MOPA_Clare South - Mona Park 66 kV | Rating (A) | 210 | 210 | 210 | 210 | 210
NQ-Townsville Burdekin West | MOPA_Clare South - Mona Park 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | MOPA_Clare South - Mona Park 66 kV | Min Voltage at Constrained Conductor | 67.7585 | 67.7604 | 67.7685 | 67.7653 | 67.758
NQ-Townsville Burdekin West | MOPA_Clare South - Mona Park 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Townsville Burdekin West | MP-AY-1 Mona Park - Ayr No 1 66 kV | % of Rated A | 13.37% | 11.09% | 9.494% | 8.879% | 9.785%
NQ-Townsville Burdekin West | MP-AY-1 Mona Park - Ayr No 1 66 kV | Limiting Line Name | TR_LINE 32534_1 | TR_LINE 32534_1 | TR_LINE 32534_1 | TR_LINE 32534_1 | TR_LINE 32534_1
NQ-Townsville Burdekin West | MP-AY-1 Mona Park - Ayr No 1 66 kV | Loading (A) | 26.5973 | 22.0749 | 18.8927 | 17.6695 | 19.4721
NQ-Townsville Burdekin West | MP-AY-1 Mona Park - Ayr No 1 66 kV | Loading (MVA) | 3.1301 | 2.6006 | 2.2282 | 2.0861 | 2.3014
NQ-Townsville Burdekin West | MP-AY-1 Mona Park - Ayr No 1 66 kV | Loading (MW) | 2.3326 | 1.5353 | 0.74343 | 0.10207 | 1.0568
NQ-Townsville Burdekin West | MP-AY-1 Mona Park - Ayr No 1 66 kV | Power Factor | 0.74521 | 0.59035 | 0.33365 | 0.048923 | 0.45919
NQ-Townsville Burdekin West | MP-AY-1 Mona Park - Ayr No 1 66 kV | Rating (A) | 199 | 199 | 199 | 199 | 199
NQ-Townsville Burdekin West | MP-AY-1 Mona Park - Ayr No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | MP-AY-1 Mona Park - Ayr No 1 66 kV | Min Voltage at Constrained Conductor | 67.9448 | 68.0164 | 68.0926 | 68.1629 | 68.2376
NQ-Townsville Burdekin West | MP-AY-1 Mona Park - Ayr No 1 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Townsville Burdekin West | MR-CR-1_Millchester-Cape River 1 66 kV | % of Rated A | 11.58% | 11.54% | 15.15% | 14.39% | 13.67%
NQ-Townsville Burdekin West | MR-CR-1_Millchester-Cape River 1 66 kV | Limiting Line Name | TR_LINE 198899_1 | TR_LINE 198899_1 | TR_LINE 198899_1 | TR_LINE 198899_1 | TR_LINE 198899_1
NQ-Townsville Burdekin West | MR-CR-1_Millchester-Cape River 1 66 kV | Loading (A) | 17.9471 | 17.8923 | 23.4762 | 22.309 | 21.1833
NQ-Townsville Burdekin West | MR-CR-1_Millchester-Cape River 1 66 kV | Loading (MVA) | 2.1148 | 2.1091 | 2.7615 | 2.6247 | 2.4931
NQ-Townsville Burdekin West | MR-CR-1_Millchester-Cape River 1 66 kV | Loading (MW) | 1.1879 | 0.9328 | 2.4731 | 2.2483 | 2.018
NQ-Townsville Burdekin West | MR-CR-1_Millchester-Cape River 1 66 kV | Power Factor | 0.56167 | 0.44222 | 0.8955 | 0.85653 | 0.80938
NQ-Townsville Burdekin West | MR-CR-1_Millchester-Cape River 1 66 kV | Rating (A) | 155 | 155 | 155 | 155 | 155
NQ-Townsville Burdekin West | MR-CR-1_Millchester-Cape River 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | MR-CR-1_Millchester-Cape River 1 66 kV | Min Voltage at Constrained Conductor | 68.0316 | 68.0579 | 67.9148 | 67.9274 | 67.9485
NQ-Townsville Burdekin West | MR-CR-1_Millchester-Cape River 1 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Townsville Burdekin West | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | % of Rated A | 30.02% | 30.02% | 29.99% | 29.99% | 29.99%
NQ-Townsville Burdekin West | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Limiting Line Name | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 49923_1 | TR_LINE 49923_1
NQ-Townsville Burdekin West | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Loading (A) | 56.4466 | 56.4364 | 56.3745 | 56.3767 | 56.3814
NQ-Townsville Burdekin West | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Loading (MVA) | 6.6748 | 6.6748 | 6.6744 | 6.6744 | 6.6745
NQ-Townsville Burdekin West | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Loading (MW) | 6.6744 | 6.6744 | 6.6741 | 6.6741 | 6.6741
NQ-Townsville Burdekin West | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Power Factor | 0.99852 | 0.99852 | 0.99853 | 0.99853 | 0.99852
NQ-Townsville Burdekin West | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Rating (A) | 188 | 188 | 188 | 188 | 188
NQ-Townsville Burdekin West | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Min Voltage at Constrained Conductor | 66.9894 | 67.0014 | 67.0741 | 67.0715 | 67.0659
NQ-Townsville Burdekin West | MR-LE-1_Millchester-Mt Leyshon 1 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Townsville Burdekin West | PA-RP-1_Peter Arlett-Ross Plains 66 kV | % of Rated A | 23.5% | 21.09% | 19.35% | 16.81% | 14.26%
NQ-Townsville Burdekin West | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Limiting Line Name | TR_LINE 32958_1 | TR_LINE 32958_1 | TR_LINE 45760_1 | TR_LINE 45760_1 | TR_LINE 45760_1
NQ-Townsville Burdekin West | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Loading (A) | 60.6367 | 54.4093 | 49.9231 | 43.3739 | 36.7922
NQ-Townsville Burdekin West | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Loading (MVA) | 7.2302 | 6.4896 | 6.022 | 5.2318 | 4.4373
NQ-Townsville Burdekin West | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Loading (MW) | 6.409 | 5.4997 | 5.9615 | 5.1815 | 4.4019
NQ-Townsville Burdekin West | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Power Factor | 0.88626 | 0.84732 | 0.98996 | 0.99038 | 0.992
NQ-Townsville Burdekin West | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Rating (A) | 258 | 258 | 258 | 258 | 258
NQ-Townsville Burdekin West | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Min Voltage at Constrained Conductor | 68.8425 | 68.8629 | 69.6414 | 69.6397 | 69.6304
NQ-Townsville Burdekin West | PA-RP-1_Peter Arlett-Ross Plains 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Townsville Burdekin West | PEAR-01_Hospital 3 11kV | % of Rated A | 0.3983% | 0.3986% | 0.3983% | 0.3984% | 0.3985%
NQ-Townsville Burdekin West | PEAR-01_Hospital 3 11kV | Limiting Line Name | PEAR-01 FEEDER C | PEAR-01 FEEDER C | PEAR-01 FEEDER C | PEAR-01 FEEDER C | PEAR-01 FEEDER C
NQ-Townsville Burdekin West | PEAR-01_Hospital 3 11kV | Loading (A) | 1.9279 | 1.929 | 1.9276 | 1.9282 | 1.9286
NQ-Townsville Burdekin West | PEAR-01_Hospital 3 11kV | Loading (MVA) | 0.037781 | 0.037828 | 0.037773 | 0.037795 | 0.037809
NQ-Townsville Burdekin West | PEAR-01_Hospital 3 11kV | Loading (MW) | 0.00075581 | 0.00075674 | 0.00075564 | 0.00075609 | 0.00075636
NQ-Townsville Burdekin West | PEAR-01_Hospital 3 11kV | Power Factor | 0.020005 | 0.020005 | 0.020005 | 0.020005 | 0.020005
NQ-Townsville Burdekin West | PEAR-01_Hospital 3 11kV | Rating (A) | 484 | 484 | 484 | 484 | 484
NQ-Townsville Burdekin West | PEAR-01_Hospital 3 11kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | PEAR-01_Hospital 3 11kV | Min Voltage at Constrained Conductor | 11.3146 | 11.3215 | 11.3133 | 11.3167 | 11.3187
NQ-Townsville Burdekin West | PEAR-01_Hospital 3 11kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Townsville Burdekin West | PEAR-06_Hospital 1 11kV | % of Rated A | 0.5623% | 0.5627% | 0.5623% | 0.5624% | 0.5625%
NQ-Townsville Burdekin West | PEAR-06_Hospital 1 11kV | Limiting Line Name | PEAR-06 FEEDER A | PEAR-06 FEEDER A | PEAR-06 FEEDER A | PEAR-06 FEEDER A | PEAR-06 FEEDER A
NQ-Townsville Burdekin West | PEAR-06_Hospital 1 11kV | Loading (A) | 2.7217 | 2.7233 | 2.7213 | 2.7222 | 2.7226
NQ-Townsville Burdekin West | PEAR-06_Hospital 1 11kV | Loading (MVA) | 0.053338 | 0.053403 | 0.053326 | 0.053357 | 0.053376
NQ-Townsville Burdekin West | PEAR-06_Hospital 1 11kV | Loading (MW) | 0.0032729 | 0.0032769 | 0.0032721 | 0.0032741 | 0.0032752
NQ-Townsville Burdekin West | PEAR-06_Hospital 1 11kV | Power Factor | 0.061361 | 0.061361 | 0.061361 | 0.061361 | 0.061361
NQ-Townsville Burdekin West | PEAR-06_Hospital 1 11kV | Rating (A) | 484 | 484 | 484 | 484 | 484
NQ-Townsville Burdekin West | PEAR-06_Hospital 1 11kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | PEAR-06_Hospital 1 11kV | Min Voltage at Constrained Conductor | 11.3146 | 11.3215 | 11.3133 | 11.3167 | 11.3187
NQ-Townsville Burdekin West | PEAR-06_Hospital 1 11kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Townsville Burdekin West | PEAR-12_Hospital 2 11kV | % of Rated A | 0.3932% | 0.3934% | 0.3931% | 0.3932% | 0.3933%
NQ-Townsville Burdekin West | PEAR-12_Hospital 2 11kV | Limiting Line Name | PEAR-12 FEEDER B | PEAR-12 FEEDER B | PEAR-12 FEEDER B | PEAR-12 FEEDER B | PEAR-12 FEEDER B
NQ-Townsville Burdekin West | PEAR-12_Hospital 2 11kV | Loading (A) | 1.903 | 1.9041 | 1.9028 | 1.9033 | 1.9037
NQ-Townsville Burdekin West | PEAR-12_Hospital 2 11kV | Loading (MVA) | 0.037293 | 0.037339 | 0.037285 | 0.037307 | 0.037321
NQ-Townsville Burdekin West | PEAR-12_Hospital 2 11kV | Loading (MW) | 0.00074603 | 0.00074695 | 0.00074586 | 0.00074631 | 0.00074657
NQ-Townsville Burdekin West | PEAR-12_Hospital 2 11kV | Power Factor | 0.020004 | 0.020004 | 0.020004 | 0.020004 | 0.020004
NQ-Townsville Burdekin West | PEAR-12_Hospital 2 11kV | Rating (A) | 484 | 484 | 484 | 484 | 484
NQ-Townsville Burdekin West | PEAR-12_Hospital 2 11kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | PEAR-12_Hospital 2 11kV | Min Voltage at Constrained Conductor | 11.3146 | 11.3215 | 11.3133 | 11.3167 | 11.3187
NQ-Townsville Burdekin West | PEAR-12_Hospital 2 11kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Townsville Burdekin West | RI-10_Richmond No 10 33 kV | % of Rated A | 3.883e-09% | 3.891e-09% | 3.798e-09% | 3.804e-09% | 3.811e-09%
NQ-Townsville Burdekin West | RI-10_Richmond No 10 33 kV | Limiting Line Name | Link_RICH_RICH-A624_RI-10 RICHMOND 33KV | Link_RICH_RICH-A624_RI-10 RICHMOND 33KV | Link_RICH_RICH-A624_RI-10 RICHMOND 33KV | Link_RICH_RICH-A624_RI-10 RICHMOND 33KV | Link_RICH_RICH-A624_RI-10 RICHMOND 33KV
NQ-Townsville Burdekin West | RI-10_Richmond No 10 33 kV | Loading (A) | 1.9417e-07 | 1.9457e-07 | 1.8992e-07 | 1.9019e-07 | 1.9056e-07
NQ-Townsville Burdekin West | RI-10_Richmond No 10 33 kV | Loading (MVA) | 1.1197e-08 | 1.1244e-08 | 1.0713e-08 | 1.0744e-08 | 1.0785e-08
NQ-Townsville Burdekin West | RI-10_Richmond No 10 33 kV | Loading (MW) | 1.1197e-08 | 1.1244e-08 | 1.0713e-08 | 1.0744e-08 | 1.0785e-08
NQ-Townsville Burdekin West | RI-10_Richmond No 10 33 kV | Power Factor | 1 | 1 | 1 | 1 | 1
NQ-Townsville Burdekin West | RI-10_Richmond No 10 33 kV | Rating (A) | 5000 | 5000 | 5000 | 5000 | 5000
NQ-Townsville Burdekin West | RI-10_Richmond No 10 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | RI-10_Richmond No 10 33 kV | Min Voltage at Constrained Conductor | 33.2946 | 33.364 | 32.566 | 32.6133 | 32.6761
NQ-Townsville Burdekin West | RI-10_Richmond No 10 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Townsville Burdekin West | RI-20_Richmond No 20 33 kV | % of Rated A | 3.883e-09% | 3.891e-09% | 3.798e-09% | 3.804e-09% | 3.811e-09%
NQ-Townsville Burdekin West | RI-20_Richmond No 20 33 kV | Limiting Line Name | Link_RICH_RICH-B624_RI-20 JULIA CREEK 33 | Link_RICH_RICH-B624_RI-20 JULIA CREEK 33 | Link_RICH_RICH-B624_RI-20 JULIA CREEK 33 | Link_RICH_RICH-B624_RI-20 JULIA CREEK 33 | Link_RICH_RICH-B624_RI-20 JULIA CREEK 33
NQ-Townsville Burdekin West | RI-20_Richmond No 20 33 kV | Loading (A) | 1.9417e-07 | 1.9457e-07 | 1.8992e-07 | 1.9019e-07 | 1.9056e-07
NQ-Townsville Burdekin West | RI-20_Richmond No 20 33 kV | Loading (MVA) | 1.1197e-08 | 1.1244e-08 | 1.0713e-08 | 1.0744e-08 | 1.0785e-08
NQ-Townsville Burdekin West | RI-20_Richmond No 20 33 kV | Loading (MW) | 1.1197e-08 | 1.1244e-08 | 1.0713e-08 | 1.0744e-08 | 1.0785e-08
NQ-Townsville Burdekin West | RI-20_Richmond No 20 33 kV | Power Factor | 1 | 1 | 1 | 1 | 1
NQ-Townsville Burdekin West | RI-20_Richmond No 20 33 kV | Rating (A) | 5000 | 5000 | 5000 | 5000 | 5000
NQ-Townsville Burdekin West | RI-20_Richmond No 20 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | RI-20_Richmond No 20 33 kV | Min Voltage at Constrained Conductor | 33.2946 | 33.364 | 32.566 | 32.6133 | 32.6761
NQ-Townsville Burdekin West | RI-20_Richmond No 20 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Townsville Burdekin West | RI-50_Richmond No 50 33 kV | % of Rated A | 3.883e-09% | 3.891e-09% | 3.798e-09% | 3.804e-09% | 3.811e-09%
NQ-Townsville Burdekin West | RI-50_Richmond No 50 33 kV | Limiting Line Name | Link_RICH_RICH E624_RI-50 JULIA CREEK NO | Link_RICH_RICH E624_RI-50 JULIA CREEK NO | Link_RICH_RICH E624_RI-50 JULIA CREEK NO | Link_RICH_RICH E624_RI-50 JULIA CREEK NO | Link_RICH_RICH E624_RI-50 JULIA CREEK NO
NQ-Townsville Burdekin West | RI-50_Richmond No 50 33 kV | Loading (A) | 1.9417e-07 | 1.9457e-07 | 1.8992e-07 | 1.9019e-07 | 1.9056e-07
NQ-Townsville Burdekin West | RI-50_Richmond No 50 33 kV | Loading (MVA) | 1.1197e-08 | 1.1244e-08 | 1.0713e-08 | 1.0744e-08 | 1.0785e-08
NQ-Townsville Burdekin West | RI-50_Richmond No 50 33 kV | Loading (MW) | 1.1197e-08 | 1.1244e-08 | 1.0713e-08 | 1.0744e-08 | 1.0785e-08
NQ-Townsville Burdekin West | RI-50_Richmond No 50 33 kV | Power Factor | 1 | 1 | 1 | 1 | 1
NQ-Townsville Burdekin West | RI-50_Richmond No 50 33 kV | Rating (A) | 5000 | 5000 | 5000 | 5000 | 5000
NQ-Townsville Burdekin West | RI-50_Richmond No 50 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | RI-50_Richmond No 50 33 kV | Min Voltage at Constrained Conductor | 33.2946 | 33.364 | 32.566 | 32.6133 | 32.6761
NQ-Townsville Burdekin West | RI-50_Richmond No 50 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Townsville Burdekin West | RI-JC-1_Richmond-Julia Creek No 1 66 kV | % of Rated A | 5.191% | 5.194% | 6.313% | 6.297% | 6.289%
NQ-Townsville Burdekin West | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Limiting Line Name | TR_LINE 32331_1 | TR_LINE 32331_1 | TR_LINE 32331_1 | TR_LINE 32331_1 | TR_LINE 32331_1
NQ-Townsville Burdekin West | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Loading (A) | 18.4284 | 18.4378 | 22.4116 | 22.3532 | 22.3266
NQ-Townsville Burdekin West | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Loading (MVA) | 2.2585 | 2.2642 | 2.6884 | 2.6851 | 2.6869
NQ-Townsville Burdekin West | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Loading (MW) | 0.35418 | 0.32683 | 1.7422 | 1.7285 | 1.7205
NQ-Townsville Burdekin West | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Power Factor | 0.15682 | 0.14434 | 0.64802 | 0.64372 | 0.64034
NQ-Townsville Burdekin West | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Rating (A) | 355 | 355 | 355 | 355 | 355
NQ-Townsville Burdekin West | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Min Voltage at Constrained Conductor | 70.7582 | 70.9012 | 69.2574 | 69.353 | 69.4815
NQ-Townsville Burdekin West | RI-JC-1_Richmond-Julia Creek No 1 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Townsville Burdekin West | ST-GI-1_Stuart-Giru 66 kV | % of Rated A | 2.965% | 2.922% | 2.895% | 2.879% | 2.868%
NQ-Townsville Burdekin West | ST-GI-1_Stuart-Giru 66 kV | Limiting Line Name | TR_LINE 162083_1 | TR_LINE 162083_1 | TR_LINE 162083_1 | TR_LINE 162083_1 | TR_LINE 162083_1
NQ-Townsville Burdekin West | ST-GI-1_Stuart-Giru 66 kV | Loading (A) | 2.9062 | 2.8637 | 2.8367 | 2.8214 | 2.8105
NQ-Townsville Burdekin West | ST-GI-1_Stuart-Giru 66 kV | Loading (MVA) | 0.34742 | 0.34236 | 0.34155 | 0.33966 | 0.33827
NQ-Townsville Burdekin West | ST-GI-1_Stuart-Giru 66 kV | Loading (MW) | 0.25958 | 0.25269 | 0.24842 | 0.24585 | 0.24402
NQ-Townsville Burdekin West | ST-GI-1_Stuart-Giru 66 kV | Power Factor | 0.74718 | 0.73807 | 0.72734 | 0.72383 | 0.72136
NQ-Townsville Burdekin West | ST-GI-1_Stuart-Giru 66 kV | Rating (A) | 98 | 98 | 98 | 98 | 98
NQ-Townsville Burdekin West | ST-GI-1_Stuart-Giru 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | ST-GI-1_Stuart-Giru 66 kV | Min Voltage at Constrained Conductor | 69.0179 | 69.021 | 69.5138 | 69.5042 | 69.4889
NQ-Townsville Burdekin West | ST-GI-1_Stuart-Giru 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Townsville Burdekin West | ST-GI-1_Stuart-Giru 66 kV To T Only | % of Rated A | 1.981% | 1.988% | 1.995% | 2.002% | 2.01%
NQ-Townsville Burdekin West | ST-GI-1_Stuart-Giru 66 kV To T Only | Limiting Line Name | TR_LINE 195987_1 | TR_LINE 195987_1 | TR_LINE 195987_1 | TR_LINE 195987_1 | TR_LINE 195987_1
NQ-Townsville Burdekin West | ST-GI-1_Stuart-Giru 66 kV To T Only | Loading (A) | 2.6145 | 2.624 | 2.6336 | 2.6431 | 2.6531
NQ-Townsville Burdekin West | ST-GI-1_Stuart-Giru 66 kV To T Only | Loading (MVA) | 0.30944 | 0.31169 | 0.31398 | 0.31625 | 0.31866
NQ-Townsville Burdekin West | ST-GI-1_Stuart-Giru 66 kV To T Only | Loading (MW) | 8.0669e-05 | 8.1255e-05 | 8.1851e-05 | 8.2442e-05 | 8.3072e-05
NQ-Townsville Burdekin West | ST-GI-1_Stuart-Giru 66 kV To T Only | Power Factor | 0.00024573 | 0.00024573 | 0.00024573 | 0.00024573 | 0.00024573
NQ-Townsville Burdekin West | ST-GI-1_Stuart-Giru 66 kV To T Only | Rating (A) | 132 | 132 | 132 | 132 | 132
NQ-Townsville Burdekin West | ST-GI-1_Stuart-Giru 66 kV To T Only | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | ST-GI-1_Stuart-Giru 66 kV To T Only | Min Voltage at Constrained Conductor | 68.3339 | 68.5816 | 68.8327 | 69.0809 | 69.3442
NQ-Townsville Burdekin West | ST-GI-1_Stuart-Giru 66 kV To T Only | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Townsville Burdekin West | ST-RM-1_Stuart-Rasmussen 66 kV | % of Rated A | 2.465% | 1.488% | 3.61% | 3.259% | 3.099%
NQ-Townsville Burdekin West | ST-RM-1_Stuart-Rasmussen 66 kV | Limiting Line Name | TR_LINE 32143_1 | TR_LINE 32143_1 | TR_LINE 32428_1 | TR_LINE 32428_1 | TR_LINE 32428_1
NQ-Townsville Burdekin West | ST-RM-1_Stuart-Rasmussen 66 kV | Loading (A) | 13.5811 | 8.1968 | 19.8916 | 17.9558 | 17.0777
NQ-Townsville Burdekin West | ST-RM-1_Stuart-Rasmussen 66 kV | Loading (MVA) | 1.6206 | 0.97851 | 2.3946 | 2.1613 | 2.0551
NQ-Townsville Burdekin West | ST-RM-1_Stuart-Rasmussen 66 kV | Loading (MW) | 1.5568 | 0.82506 | 0.86983 | 0.28007 | 0.29834
NQ-Townsville Burdekin West | ST-RM-1_Stuart-Rasmussen 66 kV | Power Factor | 0.96066 | 0.84318 | 0.36325 | 0.12959 | 0.1443
NQ-Townsville Burdekin West | ST-RM-1_Stuart-Rasmussen 66 kV | Rating (A) | 551 | 551 | 551 | 551 | 551
NQ-Townsville Burdekin West | ST-RM-1_Stuart-Rasmussen 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | ST-RM-1_Stuart-Rasmussen 66 kV | Min Voltage at Constrained Conductor | 68.8941 | 68.9227 | 69.5025 | 69.4927 | 69.4771
NQ-Townsville Burdekin West | ST-RM-1_Stuart-Rasmussen 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Townsville Burdekin West | ST-RP-1_Stuart-Ross Plains 66 kV | % of Rated A | 8.05% | 6.51% | 8.608% | 7.554% | 6.55%
NQ-Townsville Burdekin West | ST-RP-1_Stuart-Ross Plains 66 kV | Limiting Line Name | TR_LINE 32425_1 | TR_LINE 32425_1 | TR_LINE 32425_1 | TR_LINE 32425_1 | TR_LINE 32425_1
NQ-Townsville Burdekin West | ST-RP-1_Stuart-Ross Plains 66 kV | Loading (A) | 54.6581 | 44.2052 | 58.4504 | 51.2939 | 44.4777
NQ-Townsville Burdekin West | ST-RP-1_Stuart-Ross Plains 66 kV | Loading (MVA) | 6.5331 | 5.2839 | 7.0364 | 6.174 | 5.3523
NQ-Townsville Burdekin West | ST-RP-1_Stuart-Ross Plains 66 kV | Loading (MW) | 6.5303 | 5.2828 | 5.456 | 4.408 | 3.3638
NQ-Townsville Burdekin West | ST-RP-1_Stuart-Ross Plains 66 kV | Power Factor | 0.99957 | 0.99979 | 0.7754 | 0.71396 | 0.62847
NQ-Townsville Burdekin West | ST-RP-1_Stuart-Ross Plains 66 kV | Rating (A) | 679 | 679 | 679 | 679 | 679
NQ-Townsville Burdekin West | ST-RP-1_Stuart-Ross Plains 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | ST-RP-1_Stuart-Ross Plains 66 kV | Min Voltage at Constrained Conductor | 69.0082 | 69.0105 | 69.5025 | 69.4927 | 69.4771
NQ-Townsville Burdekin West | ST-RP-1_Stuart-Ross Plains 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Townsville Burdekin West | ST-TOPO-1_Stuart-Townsville Port 66 kV | % of Rated A | 10.6% | 11.26% | 11.11% | 11.03% | 11.11%
NQ-Townsville Burdekin West | ST-TOPO-1_Stuart-Townsville Port 66 kV | Limiting Line Name | TR_LINE 31745_1 | TR_LINE 31745_1 | TR_LINE 31745_2 | TR_LINE 31745_2 | TR_LINE 31745_2
NQ-Townsville Burdekin West | ST-TOPO-1_Stuart-Townsville Port 66 kV | Loading (A) | 26.6104 | 28.2748 | 27.878 | 27.6791 | 27.8749
NQ-Townsville Burdekin West | ST-TOPO-1_Stuart-Townsville Port 66 kV | Loading (MVA) | 3.1678 | 3.3652 | 3.3564 | 3.3318 | 3.3544
NQ-Townsville Burdekin West | ST-TOPO-1_Stuart-Townsville Port 66 kV | Loading (MW) | 1.7881 | 2.11 | 2.852 | 2.8461 | 2.8922
NQ-Townsville Burdekin West | ST-TOPO-1_Stuart-Townsville Port 66 kV | Power Factor | 0.56443 | 0.62696 | 0.84973 | 0.85423 | 0.86221
NQ-Townsville Burdekin West | ST-TOPO-1_Stuart-Townsville Port 66 kV | Rating (A) | 251 | 251 | 251 | 251 | 251
NQ-Townsville Burdekin West | ST-TOPO-1_Stuart-Townsville Port 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | ST-TOPO-1_Stuart-Townsville Port 66 kV | Min Voltage at Constrained Conductor | 68.7294 | 68.7159 | 69.5097 | 69.4974 | 69.4772
NQ-Townsville Burdekin West | ST-TOPO-1_Stuart-Townsville Port 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Townsville Burdekin West | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | % of Rated A | 13.56% | 11.49% | 9.224% | 8.114% | 7.391%
NQ-Townsville Burdekin West | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Limiting Line Name | TR_LINE 157896_1 | TR_LINE 157896_1 | TR_LINE 157896_1 | TR_LINE 157896_1 | TR_LINE 157896_1
NQ-Townsville Burdekin West | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Loading (A) | 124.8803 | 105.835 | 84.9536 | 74.7307 | 68.0719
NQ-Townsville Burdekin West | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Loading (MVA) | 14.9264 | 12.6502 | 10.2207 | 8.9894 | 8.1865
NQ-Townsville Burdekin West | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Loading (MW) | 14.6857 | 12.395 | 5.2359 | 2.8964 | 0.36372
NQ-Townsville Burdekin West | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Power Factor | 0.98387 | 0.97983 | 0.51229 | 0.3222 | 0.044425
NQ-Townsville Burdekin West | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Rating (A) | 921 | 921 | 921 | 921 | 921
NQ-Townsville Burdekin West | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Min Voltage at Constrained Conductor | 69.0082 | 69.0091 | 69.4604 | 69.4497 | 69.4336
NQ-Townsville Burdekin West | ST-TS-1_TOSO-Stuart No 1 (607) 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Townsville Burdekin West | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | % of Rated A | 13.78% | 11.68% | 9.373% | 8.245% | 7.51%
NQ-Townsville Burdekin West | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Limiting Line Name | TR_LINE 157898_1 | TR_LINE 157898_1 | TR_LINE 157898_1 | TR_LINE 157898_1 | TR_LINE 157898_1
NQ-Townsville Burdekin West | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Loading (A) | 126.8961 | 107.5434 | 86.325 | 75.937 | 69.1707
NQ-Townsville Burdekin West | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Loading (MVA) | 15.1675 | 12.8545 | 10.3856 | 9.1344 | 8.3186
NQ-Townsville Burdekin West | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Loading (MW) | 14.9451 | 12.6162 | 5.3949 | 3.0154 | 0.4391
NQ-Townsville Burdekin West | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Power Factor | 0.98533 | 0.98147 | 0.51946 | 0.33011 | 0.052782
NQ-Townsville Burdekin West | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Rating (A) | 921 | 921 | 921 | 921 | 921
NQ-Townsville Burdekin West | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Min Voltage at Constrained Conductor | 69.0089 | 69.0096 | 69.46 | 69.4493 | 69.433
NQ-Townsville Burdekin West | ST-TS-2_TOSO-Stuart No 2 (608) 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Townsville Burdekin West | ST-WO-1_Stuart-Woodstock South 1 66 kV | % of Rated A | 36.94% | 36.39% | 41.32% | 41.02% | 40.78%
NQ-Townsville Burdekin West | ST-WO-1_Stuart-Woodstock South 1 66 kV | Limiting Line Name | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1 | TR_LINE 162186_1
NQ-Townsville Burdekin West | ST-WO-1_Stuart-Woodstock South 1 66 kV | Loading (A) | 48.7617 | 48.0375 | 54.5433 | 54.1414 | 53.8351
NQ-Townsville Burdekin West | ST-WO-1_Stuart-Woodstock South 1 66 kV | Loading (MVA) | 5.8309 | 5.7462 | 6.5613 | 6.5135 | 6.4766
NQ-Townsville Burdekin West | ST-WO-1_Stuart-Woodstock South 1 66 kV | Loading (MW) | 3.9445 | 3.8343 | 4.634 | 4.5635 | 4.5005
NQ-Townsville Burdekin West | ST-WO-1_Stuart-Woodstock South 1 66 kV | Power Factor | 0.67648 | 0.66727 | 0.70626 | 0.70062 | 0.69489
NQ-Townsville Burdekin West | ST-WO-1_Stuart-Woodstock South 1 66 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
NQ-Townsville Burdekin West | ST-WO-1_Stuart-Woodstock South 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | ST-WO-1_Stuart-Woodstock South 1 66 kV | Min Voltage at Constrained Conductor | 69.0394 | 69.0626 | 69.4404 | 69.449 | 69.4516
NQ-Townsville Burdekin West | ST-WO-1_Stuart-Woodstock South 1 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Townsville Burdekin West | TOPO-08_Townsville Port No 8 11 kV | % of Rated A | 0.326% | 0.3259% | 0.3299% | 0.3299% | 0.3298%
NQ-Townsville Burdekin West | TOPO-08_Townsville Port No 8 11 kV | Limiting Line Name | HV_CABLE TOPO-08A 12159494 | HV_CABLE TOPO-08A 12159494 | HV_CABLE TOPO-08A 12159494 | HV_CABLE TOPO-08A 12159494 | HV_CABLE TOPO-08A 12159494
NQ-Townsville Burdekin West | TOPO-08_Townsville Port No 8 11 kV | Loading (A) | 1.8255 | 1.8252 | 1.8475 | 1.8472 | 1.8468
NQ-Townsville Burdekin West | TOPO-08_Townsville Port No 8 11 kV | Loading (MVA) | 0.034464 | 0.034455 | 0.035299 | 0.03529 | 0.035274
NQ-Townsville Burdekin West | TOPO-08_Townsville Port No 8 11 kV | Loading (MW) | 0.00068947 | 0.00068928 | 0.00070617 | 0.000706 | 0.00070566
NQ-Townsville Burdekin West | TOPO-08_Townsville Port No 8 11 kV | Power Factor | 0.020001 | 0.020001 | 0.020001 | 0.020001 | 0.020001
NQ-Townsville Burdekin West | TOPO-08_Townsville Port No 8 11 kV | Rating (A) | 560 | 560 | 560 | 560 | 560
NQ-Townsville Burdekin West | TOPO-08_Townsville Port No 8 11 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | TOPO-08_Townsville Port No 8 11 kV | Min Voltage at Constrained Conductor | 10.9001 | 10.8986 | 11.0313 | 11.0299 | 11.0273
NQ-Townsville Burdekin West | TOPO-08_Townsville Port No 8 11 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Townsville Burdekin West | TP-NS-1_Townsville Port-NESM No 1 66 kV | % of Rated A | 12.17% | 11.98% | 11.72% | 11.61% | 11.55%
NQ-Townsville Burdekin West | TP-NS-1_Townsville Port-NESM No 1 66 kV | Limiting Line Name | TR_LINE 56322_1 | TR_LINE 56322_1 | TR_LINE 56322_1 | TR_LINE 56322_1 | TR_LINE 56322_1
NQ-Townsville Burdekin West | TP-NS-1_Townsville Port-NESM No 1 66 kV | Loading (A) | 31.3949 | 30.9186 | 30.2286 | 29.9559 | 29.8094
NQ-Townsville Burdekin West | TP-NS-1_Townsville Port-NESM No 1 66 kV | Loading (MVA) | 3.7357 | 3.6782 | 3.6396 | 3.6062 | 3.5874
NQ-Townsville Burdekin West | TP-NS-1_Townsville Port-NESM No 1 66 kV | Loading (MW) | 3.6504 | 3.5912 | 3.5462 | 3.5116 | 3.4924
NQ-Townsville Burdekin West | TP-NS-1_Townsville Port-NESM No 1 66 kV | Power Factor | 0.97717 | 0.97634 | 0.97433 | 0.97378 | 0.9735
NQ-Townsville Burdekin West | TP-NS-1_Townsville Port-NESM No 1 66 kV | Rating (A) | 258 | 258 | 258 | 258 | 258
NQ-Townsville Burdekin West | TP-NS-1_Townsville Port-NESM No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | TP-NS-1_Townsville Port-NESM No 1 66 kV | Min Voltage at Constrained Conductor | 68.6943 | 68.6799 | 69.5111 | 69.4985 | 69.4779
NQ-Townsville Burdekin West | TP-NS-1_Townsville Port-NESM No 1 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
NQ-Townsville Burdekin West | WO-CT-1_Woodstock-CHTO No 1 66 kV | % of Rated A | 25.95% | 25.9% | 29.7% | 29.77% | 29.86%
NQ-Townsville Burdekin West | WO-CT-1_Woodstock-CHTO No 1 66 kV | Limiting Line Name | TR_LINE 32389_1 | TR_LINE 32389_1 | TR_LINE 32389_1 | TR_LINE 32389_1 | TR_LINE 32389_1
NQ-Townsville Burdekin West | WO-CT-1_Woodstock-CHTO No 1 66 kV | Loading (A) | 49.0406 | 48.9469 | 56.1421 | 56.2569 | 56.4444
NQ-Townsville Burdekin West | WO-CT-1_Woodstock-CHTO No 1 66 kV | Loading (MVA) | 5.8644 | 5.8555 | 6.7518 | 6.7665 | 6.7893
NQ-Townsville Burdekin West | WO-CT-1_Woodstock-CHTO No 1 66 kV | Loading (MW) | 4.0681 | 4.0701 | 4.9595 | 4.9765 | 4.9974
NQ-Townsville Burdekin West | WO-CT-1_Woodstock-CHTO No 1 66 kV | Power Factor | 0.6937 | 0.6951 | 0.73455 | 0.73546 | 0.73608
NQ-Townsville Burdekin West | WO-CT-1_Woodstock-CHTO No 1 66 kV | Rating (A) | 189 | 189 | 189 | 189 | 189
NQ-Townsville Burdekin West | WO-CT-1_Woodstock-CHTO No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
NQ-Townsville Burdekin West | WO-CT-1_Woodstock-CHTO No 1 66 kV | Min Voltage at Constrained Conductor | 69.0208 | 69.0459 | 69.3501 | 69.357 | 69.3584
NQ-Townsville Burdekin West | WO-CT-1_Woodstock-CHTO No 1 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Bulli Creek Waggamba | 7235_Bulli Creek - Waggamba 132 kV | % of Rated A | 5.852% | 5.852% | 5.308% | 5.334% | 5.334%
SW-Bulli Creek Waggamba | 7235_Bulli Creek - Waggamba 132 kV | Limiting Line Name | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1 | TR_LINE 90590_1
SW-Bulli Creek Waggamba | 7235_Bulli Creek - Waggamba 132 kV | Loading (A) | 38.038 | 38.0376 | 34.4998 | 34.6705 | 34.671
SW-Bulli Creek Waggamba | 7235_Bulli Creek - Waggamba 132 kV | Loading (MVA) | 9.1212 | 9.1203 | 8.2702 | 8.4215 | 8.4219
SW-Bulli Creek Waggamba | 7235_Bulli Creek - Waggamba 132 kV | Loading (MW) | 6.1836 | 6.1836 | 4.7826 | 4.7824 | 4.7824
SW-Bulli Creek Waggamba | 7235_Bulli Creek - Waggamba 132 kV | Power Factor | 0.67793 | 0.67799 | 0.57828 | 0.56786 | 0.56784
SW-Bulli Creek Waggamba | 7235_Bulli Creek - Waggamba 132 kV | Rating (A) | 650 | 650 | 650 | 650 | 650
SW-Bulli Creek Waggamba | 7235_Bulli Creek - Waggamba 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Bulli Creek Waggamba | 7235_Bulli Creek - Waggamba 132 kV | Min Voltage at Constrained Conductor | 138.4436 | 138.4319 | 138.4011 | 140.239 | 140.244
SW-Bulli Creek Waggamba | 7235_Bulli Creek - Waggamba 132 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Chinchilla Western Network | 3196_Tara 33 kV | % of Rated A | 8.832% | 8.63% | 8.491% | 8.391% | 8.318%
SW-Chinchilla Western Network | 3196_Tara 33 kV | Limiting Line Name | TR_LINE 27355_1 | TR_LINE 27355_1 | TR_LINE 27355_1 | TR_LINE 27355_1 | TR_LINE 27355_1
SW-Chinchilla Western Network | 3196_Tara 33 kV | Loading (A) | 8.2135 | 8.0257 | 7.8965 | 7.8039 | 7.7353
SW-Chinchilla Western Network | 3196_Tara 33 kV | Loading (MVA) | 0.47191 | 0.46159 | 0.45451 | 0.4495 | 0.44591
SW-Chinchilla Western Network | 3196_Tara 33 kV | Loading (MW) | 0.2051 | 0.17538 | 0.15176 | 0.13196 | 0.11443
SW-Chinchilla Western Network | 3196_Tara 33 kV | Power Factor | 0.43462 | 0.37994 | 0.33389 | 0.29357 | 0.25662
SW-Chinchilla Western Network | 3196_Tara 33 kV | Rating (A) | 93 | 93 | 93 | 93 | 93
SW-Chinchilla Western Network | 3196_Tara 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Chinchilla Western Network | 3196_Tara 33 kV | Min Voltage at Constrained Conductor | 33.1716 | 33.2059 | 33.2313 | 33.2553 | 33.282
SW-Chinchilla Western Network | 3196_Tara 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Chinchilla Western Network | 3203_Miles 33 kV | % of Rated A | 14.16% | 9.309% | 5.071% | 2.065% | 3.751%
SW-Chinchilla Western Network | 3203_Miles 33 kV | Limiting Line Name | HV_CABLE 219934_1 | HV_CABLE 219934_1 | HV_CABLE 219934_1 | HV_CABLE 219934_1 | HV_CABLE 219934_1
SW-Chinchilla Western Network | 3203_Miles 33 kV | Loading (A) | 25.6358 | 16.8499 | 9.1789 | 3.7376 | 6.7894
SW-Chinchilla Western Network | 3203_Miles 33 kV | Loading (MVA) | 1.5027 | 0.97599 | 0.53177 | 0.21657 | 0.39345
SW-Chinchilla Western Network | 3203_Miles 33 kV | Loading (MW) | 1.4859 | 0.95124 | 0.4865 | 0.064148 | 0.3421
SW-Chinchilla Western Network | 3203_Miles 33 kV | Power Factor | 0.98882 | 0.97464 | 0.91486 | 0.2962 | 0.86881
SW-Chinchilla Western Network | 3203_Miles 33 kV | Rating (A) | 181 | 181 | 181 | 181 | 181
SW-Chinchilla Western Network | 3203_Miles 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Chinchilla Western Network | 3203_Miles 33 kV | Min Voltage at Constrained Conductor | 33.8416 | 33.4416 | 33.4485 | 33.4537 | 33.4579
SW-Chinchilla Western Network | 3203_Miles 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Chinchilla Western Network | F001R_Yuleba 33 kV | % of Rated A | 16.25% | 16.25% | 16.24% | 16.24% | 16.23%
SW-Chinchilla Western Network | F001R_Yuleba 33 kV | Limiting Line Name | TR_LINE 28050_1 | TR_LINE 28050_1 | TR_LINE 28050_1 | TR_LINE 28050_1 | TR_LINE 28050_1
SW-Chinchilla Western Network | F001R_Yuleba 33 kV | Loading (A) | 15.1163 | 15.1104 | 15.1012 | 15.1005 | 15.0957
SW-Chinchilla Western Network | F001R_Yuleba 33 kV | Loading (MVA) | 0.84343 | 0.84338 | 0.84329 | 0.84371 | 0.84367
SW-Chinchilla Western Network | F001R_Yuleba 33 kV | Loading (MW) | 0.7966 | 0.79661 | 0.79661 | 0.79643 | 0.79643
SW-Chinchilla Western Network | F001R_Yuleba 33 kV | Power Factor | 0.94448 | 0.94454 | 0.94465 | 0.94396 | 0.94401
SW-Chinchilla Western Network | F001R_Yuleba 33 kV | Rating (A) | 93 | 93 | 93 | 93 | 93
SW-Chinchilla Western Network | F001R_Yuleba 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Chinchilla Western Network | F001R_Yuleba 33 kV | Min Voltage at Constrained Conductor | 32.214 | 32.2244 | 32.2406 | 32.2584 | 32.2669
SW-Chinchilla Western Network | F001R_Yuleba 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Chinchilla Western Network | F022R_Brucedale 33 kV | % of Rated A | 11.51% | 11.5% | 11.5% | 11.49% | 11.48%
SW-Chinchilla Western Network | F022R_Brucedale 33 kV | Limiting Line Name | TR_LINE 22816_1 | TR_LINE 22816_1 | TR_LINE 22816_1 | TR_LINE 22816_1 | TR_LINE 22816_1
SW-Chinchilla Western Network | F022R_Brucedale 33 kV | Loading (A) | 10.7012 | 10.697 | 10.6905 | 10.6834 | 10.68
SW-Chinchilla Western Network | F022R_Brucedale 33 kV | Loading (MVA) | 0.59695 | 0.59691 | 0.59684 | 0.59678 | 0.59674
SW-Chinchilla Western Network | F022R_Brucedale 33 kV | Loading (MW) | 0.58834 | 0.58833 | 0.58832 | 0.5883 | 0.5883
SW-Chinchilla Western Network | F022R_Brucedale 33 kV | Power Factor | 0.98535 | 0.9854 | 0.98548 | 0.98557 | 0.98562
SW-Chinchilla Western Network | F022R_Brucedale 33 kV | Rating (A) | 93 | 93 | 93 | 93 | 93
SW-Chinchilla Western Network | F022R_Brucedale 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Chinchilla Western Network | F022R_Brucedale 33 kV | Min Voltage at Constrained Conductor | 32.2064 | 32.2169 | 32.2331 | 32.2509 | 32.2594
SW-Chinchilla Western Network | F022R_Brucedale 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Chinchilla Western Network | F049R_Roma North 33 kV | % of Rated A | 26.94% | 26.94% | 26.94% | 26.94% | 26.94%
SW-Chinchilla Western Network | F049R_Roma North 33 kV | Limiting Line Name | TR_LINE 22900_1 | TR_LINE 22900_1 | TR_LINE 22900_1 | TR_LINE 22900_1 | TR_LINE 22900_1
SW-Chinchilla Western Network | F049R_Roma North 33 kV | Loading (A) | 25.0516 | 25.0516 | 25.0516 | 25.0516 | 25.0516
SW-Chinchilla Western Network | F049R_Roma North 33 kV | Loading (MVA) | 1.3997 | 1.3997 | 1.3997 | 1.3997 | 1.3997
SW-Chinchilla Western Network | F049R_Roma North 33 kV | Loading (MW) | 1.3346 | 1.3346 | 1.3346 | 1.3346 | 1.3346
SW-Chinchilla Western Network | F049R_Roma North 33 kV | Power Factor | 0.95355 | 0.95355 | 0.95355 | 0.95355 | 0.95355
SW-Chinchilla Western Network | F049R_Roma North 33 kV | Rating (A) | 93 | 93 | 93 | 93 | 93
SW-Chinchilla Western Network | F049R_Roma North 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Chinchilla Western Network | F049R_Roma North 33 kV | Min Voltage at Constrained Conductor | 32.2 | 32.2 | 32.2 | 32.2 | 32.2
SW-Chinchilla Western Network | F049R_Roma North 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Chinchilla Western Network | F060T_Tara 33 kV | % of Rated A | 8.915% | 8.747% | 8.636% | 8.56% | 8.507%
SW-Chinchilla Western Network | F060T_Tara 33 kV | Limiting Line Name | TR_LINE 104801_2 | TR_LINE 104801_2 | TR_LINE 104801_2 | TR_LINE 104801_2 | TR_LINE 104801_2
SW-Chinchilla Western Network | F060T_Tara 33 kV | Loading (A) | 8.2909 | 8.1346 | 8.0312 | 7.9606 | 7.9118
SW-Chinchilla Western Network | F060T_Tara 33 kV | Loading (MVA) | 0.47362 | 0.46518 | 0.45962 | 0.45591 | 0.45348
SW-Chinchilla Western Network | F060T_Tara 33 kV | Loading (MW) | 0.17702 | 0.1473 | 0.12368 | 0.10388 | 0.086354
SW-Chinchilla Western Network | F060T_Tara 33 kV | Power Factor | 0.37375 | 0.31665 | 0.26909 | 0.22786 | 0.19042
SW-Chinchilla Western Network | F060T_Tara 33 kV | Rating (A) | 93 | 93 | 93 | 93 | 93
SW-Chinchilla Western Network | F060T_Tara 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Chinchilla Western Network | F060T_Tara 33 kV | Min Voltage at Constrained Conductor | 32.9815 | 33.0159 | 33.0414 | 33.0655 | 33.0923
SW-Chinchilla Western Network | F060T_Tara 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Chinchilla Western Network | F067C_Kogan 33 kV | % of Rated A | 51.92% | 51.89% | 51.83% | 51.81% | 52.6%
SW-Chinchilla Western Network | F067C_Kogan 33 kV | Limiting Line Name | TR_LINE 28354_1 | TR_LINE 28354_1 | TR_LINE 28354_1 | TR_LINE 28354_1 | TR_LINE 28354_1
SW-Chinchilla Western Network | F067C_Kogan 33 kV | Loading (A) | 48.2857 | 48.2592 | 48.1982 | 48.1827 | 48.9151
SW-Chinchilla Western Network | F067C_Kogan 33 kV | Loading (MVA) | 2.76 | 2.7607 | 2.7595 | 2.7603 | 2.7628
SW-Chinchilla Western Network | F067C_Kogan 33 kV | Loading (MW) | 2.7359 | 2.7363 | 2.7356 | 2.736 | 2.7381
SW-Chinchilla Western Network | F067C_Kogan 33 kV | Power Factor | 0.99128 | 0.99112 | 0.99133 | 0.99117 | 0.99105
SW-Chinchilla Western Network | F067C_Kogan 33 kV | Rating (A) | 93 | 93 | 93 | 93 | 93
SW-Chinchilla Western Network | F067C_Kogan 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Chinchilla Western Network | F067C_Kogan 33 kV | Min Voltage at Constrained Conductor | 32.9891 | 33.0164 | 33.0431 | 33.0636 | 32.5975
SW-Chinchilla Western Network | F067C_Kogan 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Chinchilla Western Network | F069C_Brigalow 33 kV | % of Rated A | 9.58% | 20.5% | 31.31% | 42.3% | 55.06%
SW-Chinchilla Western Network | F069C_Brigalow 33 kV | Limiting Line Name | TR_LINE 28408_1 | TR_LINE 28408_1 | TR_LINE 28408_1 | TR_LINE 27354_1 | TR_LINE 27354_1
SW-Chinchilla Western Network | F069C_Brigalow 33 kV | Loading (A) | 8.4301 | 18.0437 | 27.5558 | 37.2205 | 48.4571
SW-Chinchilla Western Network | F069C_Brigalow 33 kV | Loading (MVA) | 0.49151 | 1.0544 | 1.6137 | 2.1841 | 2.8093
SW-Chinchilla Western Network | F069C_Brigalow 33 kV | Loading (MW) | 0.48832 | 1.0538 | 1.6137 | 2.1837 | 2.8069
SW-Chinchilla Western Network | F069C_Brigalow 33 kV | Power Factor | 0.99351 | 0.99939 | 1 | 0.99981 | 0.99913
SW-Chinchilla Western Network | F069C_Brigalow 33 kV | Rating (A) | 88 | 88 | 88 | 88 | 88
SW-Chinchilla Western Network | F069C_Brigalow 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Chinchilla Western Network | F069C_Brigalow 33 kV | Min Voltage at Constrained Conductor | 33.6619 | 33.7393 | 33.8105 | 33.8773 | 33.4702
SW-Chinchilla Western Network | F069C_Brigalow 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Chinchilla Western Network | F071C RYWUNG | % of Rated A | 3.121% | 3.124% | 3.127% | 3.129% | 3.137%
SW-Chinchilla Western Network | F071C RYWUNG | Limiting Line Name | TR_LINE 199202_1 | TR_LINE 199202_1 | TR_LINE 199202_1 | TR_LINE 199202_1 | TR_LINE 199202_1
SW-Chinchilla Western Network | F071C RYWUNG | Loading (A) | 2.7466 | 2.7492 | 2.7516 | 2.7537 | 2.7607
SW-Chinchilla Western Network | F071C RYWUNG | Loading (MVA) | 0.15967 | 0.15997 | 0.16024 | 0.16048 | 0.15872
SW-Chinchilla Western Network | F071C RYWUNG | Loading (MW) | 0.0082061 | 0.0082091 | 0.0082117 | 0.008214 | 0.0081965
SW-Chinchilla Western Network | F071C RYWUNG | Power Factor | 0.051395 | 0.051315 | 0.051245 | 0.051184 | 0.05164
SW-Chinchilla Western Network | F071C RYWUNG | Rating (A) | 88 | 88 | 88 | 88 | 88
SW-Chinchilla Western Network | F071C RYWUNG | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Chinchilla Western Network | F071C RYWUNG | Min Voltage at Constrained Conductor | 33.5633 | 33.5948 | 33.6227 | 33.647 | 33.1942
SW-Chinchilla Western Network | F071C RYWUNG | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Chinchilla Western Network | F073C_Fairymeadow 33 kV | % of Rated A | 3.852% | 3.85% | 3.848% | 3.852% | 3.898%
SW-Chinchilla Western Network | F073C_Fairymeadow 33 kV | Limiting Line Name | TR_LINE 174241_1 | TR_LINE 174241_1 | TR_LINE 174241_1 | TR_LINE 177654_1 | TR_LINE 174241_1
SW-Chinchilla Western Network | F073C_Fairymeadow 33 kV | Loading (A) | 3.5823 | 3.5803 | 3.5784 | 3.5824 | 3.6249
SW-Chinchilla Western Network | F073C_Fairymeadow 33 kV | Loading (MVA) | 0.20824 | 0.20829 | 0.20834 | 0.20324 | 0.20831
SW-Chinchilla Western Network | F073C_Fairymeadow 33 kV | Loading (MW) | 0.20354 | 0.20355 | 0.20355 | 0.20313 | 0.20361
SW-Chinchilla Western Network | F073C_Fairymeadow 33 kV | Power Factor | 0.97745 | 0.97723 | 0.97704 | 0.9994 | 0.97743
SW-Chinchilla Western Network | F073C_Fairymeadow 33 kV | Rating (A) | 93 | 93 | 93 | 93 | 93
SW-Chinchilla Western Network | F073C_Fairymeadow 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Chinchilla Western Network | F073C_Fairymeadow 33 kV | Min Voltage at Constrained Conductor | 33.5598 | 33.5878 | 33.6126 | 32.7556 | 33.1768
SW-Chinchilla Western Network | F073C_Fairymeadow 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Chinchilla Western Network | F074C_Miles-Condamine 33 kV | % of Rated A | 8.524% | 8.399% | 8.305% | 8.231% | 8.172%
SW-Chinchilla Western Network | F074C_Miles-Condamine 33 kV | Limiting Line Name | TR_LINE 138809_5 | TR_LINE 138809_5 | TR_LINE 138809_5 | TR_LINE 138809_5 | TR_LINE 138809_5
SW-Chinchilla Western Network | F074C_Miles-Condamine 33 kV | Loading (A) | 12.1891 | 12.0105 | 11.876 | 11.7699 | 11.6863
SW-Chinchilla Western Network | F074C_Miles-Condamine 33 kV | Loading (MVA) | 0.68985 | 0.68046 | 0.67343 | 0.66791 | 0.66361
SW-Chinchilla Western Network | F074C_Miles-Condamine 33 kV | Loading (MW) | 0.68789 | 0.67833 | 0.67121 | 0.66561 | 0.66123
SW-Chinchilla Western Network | F074C_Miles-Condamine 33 kV | Power Factor | 0.99716 | 0.99688 | 0.99671 | 0.99655 | 0.99641
SW-Chinchilla Western Network | F074C_Miles-Condamine 33 kV | Rating (A) | 143 | 143 | 143 | 143 | 143
SW-Chinchilla Western Network | F074C_Miles-Condamine 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Chinchilla Western Network | F074C_Miles-Condamine 33 kV | Min Voltage at Constrained Conductor | 32.6681 | 32.7026 | 32.7314 | 32.7561 | 32.7782
SW-Chinchilla Western Network | F074C_Miles-Condamine 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Chinchilla Western Network | F075S_St George Town 33 kV | % of Rated A | 3.391% | 2.906% | 2.541% | 2.246% | 2.028%
SW-Chinchilla Western Network | F075S_St George Town 33 kV | Limiting Line Name | TR_CABLE 16563_1 | TR_CABLE 16563_1 | TR_CABLE 16563_1 | TR_CABLE 16563_1 | TR_CABLE 16563_1
SW-Chinchilla Western Network | F075S_St George Town 33 kV | Loading (A) | 5.5616 | 4.7664 | 4.1678 | 3.6837 | 3.3259
SW-Chinchilla Western Network | F075S_St George Town 33 kV | Loading (MVA) | 0.31738 | 0.27193 | 0.23775 | 0.2101 | 0.18966
SW-Chinchilla Western Network | F075S_St George Town 33 kV | Loading (MW) | 0.31504 | 0.26917 | 0.23456 | 0.20646 | 0.1856
SW-Chinchilla Western Network | F075S_St George Town 33 kV | Power Factor | 0.99264 | 0.98983 | 0.98656 | 0.98265 | 0.97859
SW-Chinchilla Western Network | F075S_St George Town 33 kV | Rating (A) | 164 | 164 | 164 | 164 | 164
SW-Chinchilla Western Network | F075S_St George Town 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Chinchilla Western Network | F075S_St George Town 33 kV | Min Voltage at Constrained Conductor | 32.9468 | 32.9395 | 32.9351 | 32.9291 | 32.9242
SW-Chinchilla Western Network | F075S_St George Town 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Chinchilla Western Network | F076C_Dulacca 33 kV | % of Rated A | 2.457% | 2.429% | 2.431% | 2.433% | 2.434%
SW-Chinchilla Western Network | F076C_Dulacca 33 kV | Limiting Line Name | TR_LINE 27218_1 | TR_LINE 27218_1 | TR_LINE 27218_1 | TR_LINE 27218_1 | TR_LINE 27218_1
SW-Chinchilla Western Network | F076C_Dulacca 33 kV | Loading (A) | 2.85 | 2.8182 | 2.8204 | 2.8223 | 2.824
SW-Chinchilla Western Network | F076C_Dulacca 33 kV | Loading (MVA) | 0.16682 | 0.16312 | 0.16337 | 0.16359 | 0.16379
SW-Chinchilla Western Network | F076C_Dulacca 33 kV | Loading (MW) | 0.080505 | 0.080483 | 0.080485 | 0.080486 | 0.080487
SW-Chinchilla Western Network | F076C_Dulacca 33 kV | Power Factor | 0.48258 | 0.49341 | 0.49265 | 0.492 | 0.4914
SW-Chinchilla Western Network | F076C_Dulacca 33 kV | Rating (A) | 116 | 116 | 116 | 116 | 116
SW-Chinchilla Western Network | F076C_Dulacca 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Chinchilla Western Network | F076C_Dulacca 33 kV | Min Voltage at Constrained Conductor | 33.795 | 33.4167 | 33.443 | 33.4656 | 33.4861
SW-Chinchilla Western Network | F076C_Dulacca 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Chinchilla Western Network | F077C_Wandoan 33 kV | % of Rated A | 12.5% | 12.48% | 12.47% | 12.45% | 12.44%
SW-Chinchilla Western Network | F077C_Wandoan 33 kV | Limiting Line Name | TR_CABLE 126_1 | TR_CABLE 126_1 | TR_CABLE 126_1 | TR_CABLE 126_1 | TR_CABLE 126_1
SW-Chinchilla Western Network | F077C_Wandoan 33 kV | Loading (A) | 12.4993 | 12.482 | 12.4669 | 12.4539 | 12.4422
SW-Chinchilla Western Network | F077C_Wandoan 33 kV | Loading (MVA) | 0.70805 | 0.70805 | 0.70805 | 0.70805 | 0.70805
SW-Chinchilla Western Network | F077C_Wandoan 33 kV | Loading (MW) | 0.58834 | 0.58834 | 0.58834 | 0.58834 | 0.58834
SW-Chinchilla Western Network | F077C_Wandoan 33 kV | Power Factor | 0.83068 | 0.83068 | 0.83068 | 0.83068 | 0.83068
SW-Chinchilla Western Network | F077C_Wandoan 33 kV | Rating (A) | 100 | 100 | 100 | 100 | 100
SW-Chinchilla Western Network | F077C_Wandoan 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Chinchilla Western Network | F077C_Wandoan 33 kV | Min Voltage at Constrained Conductor | 32.7054 | 32.7507 | 32.7903 | 32.8245 | 32.8555
SW-Chinchilla Western Network | F077C_Wandoan 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Chinchilla Western Network | F077S_Main Camp 33 kV | % of Rated A | 80.94% | 80.96% | 80.98% | 80.99% | 81.01%
SW-Chinchilla Western Network | F077S_Main Camp 33 kV | Limiting Line Name | TR_CABLE 16560_1 | TR_CABLE 16560_1 | TR_CABLE 16560_1 | TR_CABLE 16560_1 | TR_CABLE 16560_1
SW-Chinchilla Western Network | F077S_Main Camp 33 kV | Loading (A) | 80.9396 | 80.9624 | 80.9759 | 80.9944 | 81.0097
SW-Chinchilla Western Network | F077S_Main Camp 33 kV | Loading (MVA) | 4.6188 | 4.6191 | 4.6192 | 4.6194 | 4.6196
SW-Chinchilla Western Network | F077S_Main Camp 33 kV | Loading (MW) | 4.0936 | 4.0936 | 4.0936 | 4.0937 | 4.0937
SW-Chinchilla Western Network | F077S_Main Camp 33 kV | Power Factor | 0.88623 | 0.88619 | 0.88617 | 0.88613 | 0.88611
SW-Chinchilla Western Network | F077S_Main Camp 33 kV | Rating (A) | 100 | 100 | 100 | 100 | 100
SW-Chinchilla Western Network | F077S_Main Camp 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Chinchilla Western Network | F077S_Main Camp 33 kV | Min Voltage at Constrained Conductor | 32.9463 | 32.9389 | 32.9346 | 32.9286 | 32.9237
SW-Chinchilla Western Network | F077S_Main Camp 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Chinchilla Western Network | F078S_Beardmore Dam 33 kV | % of Rated A | 3.511% | 3.512% | 3.512% | 3.512% | 3.513%
SW-Chinchilla Western Network | F078S_Beardmore Dam 33 kV | Limiting Line Name | TR_CABLE 4960_1 | TR_CABLE 4960_1 | TR_CABLE 4960_1 | TR_CABLE 4960_1 | TR_CABLE 4960_1
SW-Chinchilla Western Network | F078S_Beardmore Dam 33 kV | Loading (A) | 3.5109 | 3.5115 | 3.5118 | 3.5123 | 3.5127
SW-Chinchilla Western Network | F078S_Beardmore Dam 33 kV | Loading (MVA) | 0.19991 | 0.1999 | 0.1999 | 0.1999 | 0.1999
SW-Chinchilla Western Network | F078S_Beardmore Dam 33 kV | Loading (MW) | 0.18025 | 0.18025 | 0.18025 | 0.18025 | 0.18025
SW-Chinchilla Western Network | F078S_Beardmore Dam 33 kV | Power Factor | 0.90143 | 0.90144 | 0.90144 | 0.90145 | 0.90146
SW-Chinchilla Western Network | F078S_Beardmore Dam 33 kV | Rating (A) | 100 | 100 | 100 | 100 | 100
SW-Chinchilla Western Network | F078S_Beardmore Dam 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Chinchilla Western Network | F078S_Beardmore Dam 33 kV | Min Voltage at Constrained Conductor | 32.8733 | 32.8675 | 32.8645 | 32.8597 | 32.856
SW-Chinchilla Western Network | F078S_Beardmore Dam 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Chinchilla Western Network | F079S_St George Meatworks 33 kV | % of Rated A | 24.61% | 23.53% | 22.58% | 21.7% | 20.85%
SW-Chinchilla Western Network | F079S_St George Meatworks 33 kV | Limiting Line Name | TR_CABLE 16561_1 | TR_CABLE 16561_1 | TR_CABLE 16561_1 | TR_CABLE 16561_1 | TR_CABLE 16561_1
SW-Chinchilla Western Network | F079S_St George Meatworks 33 kV | Loading (A) | 24.6123 | 23.5317 | 22.5766 | 21.704 | 20.848
SW-Chinchilla Western Network | F079S_St George Meatworks 33 kV | Loading (MVA) | 1.4045 | 1.3426 | 1.2879 | 1.2379 | 1.1889
SW-Chinchilla Western Network | F079S_St George Meatworks 33 kV | Loading (MW) | 1.3486 | 1.2843 | 1.2273 | 1.1751 | 1.1238
SW-Chinchilla Western Network | F079S_St George Meatworks 33 kV | Power Factor | 0.96023 | 0.95662 | 0.95299 | 0.94931 | 0.94526
SW-Chinchilla Western Network | F079S_St George Meatworks 33 kV | Rating (A) | 100 | 100 | 100 | 100 | 100
SW-Chinchilla Western Network | F079S_St George Meatworks 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Chinchilla Western Network | F079S_St George Meatworks 33 kV | Min Voltage at Constrained Conductor | 32.9467 | 32.9394 | 32.9351 | 32.9291 | 32.9242
SW-Chinchilla Western Network | F079S_St George Meatworks 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Chinchilla Western Network | F081S_Noondoo 33 kV | % of Rated A | 45.5% | 45.51% | 45.51% | 45.52% | 45.53%
SW-Chinchilla Western Network | F081S_Noondoo 33 kV | Limiting Line Name | TR_CABLE 16562_1 | TR_CABLE 16562_1 | TR_CABLE 16562_1 | TR_CABLE 16562_1 | TR_CABLE 16562_1
SW-Chinchilla Western Network | F081S_Noondoo 33 kV | Loading (A) | 45.4985 | 45.5079 | 45.5135 | 45.5211 | 45.5274
SW-Chinchilla Western Network | F081S_Noondoo 33 kV | Loading (MVA) | 2.5964 | 2.5964 | 2.5963 | 2.5963 | 2.5963
SW-Chinchilla Western Network | F081S_Noondoo 33 kV | Loading (MW) | 2.5685 | 2.5686 | 2.5686 | 2.5686 | 2.5686
SW-Chinchilla Western Network | F081S_Noondoo 33 kV | Power Factor | 0.98926 | 0.98929 | 0.98931 | 0.98934 | 0.98935
SW-Chinchilla Western Network | F081S_Noondoo 33 kV | Rating (A) | 100 | 100 | 100 | 100 | 100
SW-Chinchilla Western Network | F081S_Noondoo 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Chinchilla Western Network | F081S_Noondoo 33 kV | Min Voltage at Constrained Conductor | 32.9466 | 32.9392 | 32.9349 | 32.9289 | 32.924
SW-Chinchilla Western Network | F081S_Noondoo 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Chinchilla Western Network | F083C_Chinchilla 33 kV | % of Rated A | 0.9947% | 2.773% | 5.521% | 8.159% | 10.99%
SW-Chinchilla Western Network | F083C_Chinchilla 33 kV | Limiting Line Name | TR_LINE 195206_2 | TR_LINE 27121_1 | TR_LINE 27121_1 | TR_LINE 27121_1 | TR_LINE 27121_1
SW-Chinchilla Western Network | F083C_Chinchilla 33 kV | Loading (A) | 3.3222 | 9.2605 | 18.4401 | 27.2522 | 36.7029
SW-Chinchilla Western Network | F083C_Chinchilla 33 kV | Loading (MVA) | 0.19312 | 0.53875 | 1.0736 | 1.5877 | 2.1093
SW-Chinchilla Western Network | F083C_Chinchilla 33 kV | Loading (MW) | 0.10455 | 0.51379 | 1.0618 | 1.5803 | 2.1046
SW-Chinchilla Western Network | F083C_Chinchilla 33 kV | Power Factor | 0.5414 | 0.95365 | 0.98902 | 0.99536 | 0.99774
SW-Chinchilla Western Network | F083C_Chinchilla 33 kV | Rating (A) | 334 | 334 | 334 | 334 | 334
SW-Chinchilla Western Network | F083C_Chinchilla 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Chinchilla Western Network | F083C_Chinchilla 33 kV | Min Voltage at Constrained Conductor | 33.5612 | 33.5888 | 33.6135 | 33.6347 | 33.1788
SW-Chinchilla Western Network | F083C_Chinchilla 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Chinchilla Western Network | F083S_Dirrabandi Town 33 kV | % of Rated A | 12.7% | 12.7% | 12.71% | 12.71% | 12.71%
SW-Chinchilla Western Network | F083S_Dirrabandi Town 33 kV | Limiting Line Name | TR_LINE 27419_1 | TR_LINE 27419_1 | TR_LINE 27419_1 | TR_LINE 27419_1 | TR_LINE 27419_1
SW-Chinchilla Western Network | F083S_Dirrabandi Town 33 kV | Loading (A) | 9.2717 | 9.2741 | 9.2754 | 9.2774 | 9.2789
SW-Chinchilla Western Network | F083S_Dirrabandi Town 33 kV | Loading (MVA) | 0.5165 | 0.5165 | 0.51651 | 0.51651 | 0.51651
SW-Chinchilla Western Network | F083S_Dirrabandi Town 33 kV | Loading (MW) | 0.45763 | 0.45763 | 0.45763 | 0.45763 | 0.45763
SW-Chinchilla Western Network | F083S_Dirrabandi Town 33 kV | Power Factor | 0.88542 | 0.88541 | 0.8854 | 0.8854 | 0.88539
SW-Chinchilla Western Network | F083S_Dirrabandi Town 33 kV | Rating (A) | 73 | 73 | 73 | 73 | 73
SW-Chinchilla Western Network | F083S_Dirrabandi Town 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Chinchilla Western Network | F083S_Dirrabandi Town 33 kV | Min Voltage at Constrained Conductor | 32.1624 | 32.1545 | 32.1499 | 32.1434 | 32.1382
SW-Chinchilla Western Network | F083S_Dirrabandi Town 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Chinchilla Western Network | F106R_Roma East 33 kV | % of Rated A | 4.486% | 3.391% | 12.39% | 11.61% | 10.94%
SW-Chinchilla Western Network | F106R_Roma East 33 kV | Limiting Line Name | TR_LINE 44567_2 | TR_LINE 44567_2 | TR_LINE 44567_2 | TR_LINE 44567_2 | TR_LINE 44567_2
SW-Chinchilla Western Network | F106R_Roma East 33 kV | Loading (A) | 11.4841 | 8.6799 | 31.7267 | 29.729 | 27.9991
SW-Chinchilla Western Network | F106R_Roma East 33 kV | Loading (MVA) | 0.64029 | 0.48419 | 1.768 | 1.6578 | 1.562
SW-Chinchilla Western Network | F106R_Roma East 33 kV | Loading (MW) | 0.63994 | 0.48376 | 1.7676 | 1.6575 | 1.5616
SW-Chinchilla Western Network | F106R_Roma East 33 kV | Power Factor | 0.99942 | 0.99907 | 0.99976 | 0.99976 | 0.99976
SW-Chinchilla Western Network | F106R_Roma East 33 kV | Rating (A) | 256 | 256 | 256 | 256 | 256
SW-Chinchilla Western Network | F106R_Roma East 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Chinchilla Western Network | F106R_Roma East 33 kV | Min Voltage at Constrained Conductor | 32.1892 | 32.2061 | 32.1697 | 32.1921 | 32.2046
SW-Chinchilla Western Network | F106R_Roma East 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Chinchilla Western Network | F127R_Roma West 33 kV | % of Rated A | 4.663% | 3.391% | 2.33% | 1.397% | 0.5948%
SW-Chinchilla Western Network | F127R_Roma West 33 kV | Limiting Line Name | TR_LINE 125467_1 | TR_LINE 125467_1 | TR_LINE 125467_1 | TR_LINE 125467_1 | TR_LINE 125467_1
SW-Chinchilla Western Network | F127R_Roma West 33 kV | Loading (A) | 5.4091 | 3.9338 | 2.7028 | 1.6202 | 0.68991
SW-Chinchilla Western Network | F127R_Roma West 33 kV | Loading (MVA) | 0.30174 | 0.21953 | 0.15092 | 0.090525 | 0.03856
SW-Chinchilla Western Network | F127R_Roma West 33 kV | Loading (MW) | 0.30113 | 0.21864 | 0.14957 | 0.088206 | 0.032684
SW-Chinchilla Western Network | F127R_Roma West 33 kV | Power Factor | 0.99798 | 0.99594 | 0.99106 | 0.97439 | 0.84762
SW-Chinchilla Western Network | F127R_Roma West 33 kV | Rating (A) | 116 | 116 | 116 | 116 | 116
SW-Chinchilla Western Network | F127R_Roma West 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Chinchilla Western Network | F127R_Roma West 33 kV | Min Voltage at Constrained Conductor | 32.2064 | 32.2198 | 32.2383 | 32.2582 | 32.2687
SW-Chinchilla Western Network | F127R_Roma West 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Chinchilla Western Network | F187R_Mungallala 33 kV | % of Rated A | 0.0007836% | 0.0007861% | 0.0007969% | 0.0008025% | 0.0008059%
SW-Chinchilla Western Network | F187R_Mungallala 33 kV | Limiting Line Name | TR_LINE 12064483_1 | TR_LINE 12064483_1 | TR_LINE 12064483_1 | TR_LINE 12064483_1 | TR_LINE 12064483_1
SW-Chinchilla Western Network | F187R_Mungallala 33 kV | Loading (A) | 0.002006 | 0.0020124 | 0.0020401 | 0.0020544 | 0.002063
SW-Chinchilla Western Network | F187R_Mungallala 33 kV | Loading (MVA) | 0.00011294 | 0.00011367 | 0.00011681 | 0.00011846 | 0.00011946
SW-Chinchilla Western Network | F187R_Mungallala 33 kV | Loading (MW) | 1.0676e-08 | 1.0739e-08 | 1.1038e-08 | 1.1204e-08 | 1.1294e-08
SW-Chinchilla Western Network | F187R_Mungallala 33 kV | Power Factor | 9.4529e-05 | 9.4451e-05 | 9.4495e-05 | 9.4578e-05 | 9.4536e-05
SW-Chinchilla Western Network | F187R_Mungallala 33 kV | Rating (A) | 256 | 256 | 256 | 256 | 256
SW-Chinchilla Western Network | F187R_Mungallala 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Chinchilla Western Network | F187R_Mungallala 33 kV | Min Voltage at Constrained Conductor | 32.5064 | 32.6103 | 33.0588 | 33.2909 | 33.4307
SW-Chinchilla Western Network | F187R_Mungallala 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Chinchilla Western Network | F217R_St George 66 kV | % of Rated A | 21.51% | 21.22% | 21.02% | 20.8% | 20.61%
SW-Chinchilla Western Network | F217R_St George 66 kV | Limiting Line Name | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1 | TR_LINE 44241_1
SW-Chinchilla Western Network | F217R_St George 66 kV | Loading (A) | 96.1408 | 94.8736 | 93.9511 | 92.9817 | 92.1442
SW-Chinchilla Western Network | F217R_St George 66 kV | Loading (MVA) | 10.7823 | 10.6427 | 10.5375 | 10.432 | 10.34
SW-Chinchilla Western Network | F217R_St George 66 kV | Loading (MW) | 9.259 | 9.1227 | 9.0121 | 8.9124 | 8.8235
SW-Chinchilla Western Network | F217R_St George 66 kV | Power Factor | 0.85872 | 0.85718 | 0.85524 | 0.85433 | 0.85334
SW-Chinchilla Western Network | F217R_St George 66 kV | Rating (A) | 447 | 447 | 447 | 447 | 447
SW-Chinchilla Western Network | F217R_St George 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Chinchilla Western Network | F217R_St George 66 kV | Min Voltage at Constrained Conductor | 64.7504 | 64.7657 | 64.7553 | 64.7755 | 64.7878
SW-Chinchilla Western Network | F217R_St George 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Toowoomba Dalby Warwick | 3153_Cecil Plains Road 33 kV | % of Rated A | 65.74% | 65.68% | 65.63% | 65.59% | 65.55%
SW-Toowoomba Dalby Warwick | 3153_Cecil Plains Road 33 kV | Limiting Line Name | TR_LINE 183124_2 | TR_LINE 183124_2 | TR_LINE 183124_2 | TR_LINE 183124_2 | TR_LINE 183124_2
SW-Toowoomba Dalby Warwick | 3153_Cecil Plains Road 33 kV | Loading (A) | 61.1341 | 61.0795 | 61.0402 | 61.0027 | 60.9591
SW-Toowoomba Dalby Warwick | 3153_Cecil Plains Road 33 kV | Loading (MVA) | 3.5865 | 3.5864 | 3.5863 | 3.5862 | 3.5861
SW-Toowoomba Dalby Warwick | 3153_Cecil Plains Road 33 kV | Loading (MW) | 3.5687 | 3.5687 | 3.5686 | 3.5686 | 3.5685
SW-Toowoomba Dalby Warwick | 3153_Cecil Plains Road 33 kV | Power Factor | 0.99505 | 0.99506 | 0.99508 | 0.99509 | 0.99511
SW-Toowoomba Dalby Warwick | 3153_Cecil Plains Road 33 kV | Rating (A) | 93 | 93 | 93 | 93 | 93
SW-Toowoomba Dalby Warwick | 3153_Cecil Plains Road 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | 3153_Cecil Plains Road 33 kV | Min Voltage at Constrained Conductor | 33.8684 | 33.8974 | 33.9183 | 33.9383 | 33.9616
SW-Toowoomba Dalby Warwick | 3153_Cecil Plains Road 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Toowoomba Dalby Warwick | 3154_Central Dalby 1 33 kV | % of Rated A | 3.689% | 2.247% | 1.035% | 0.4315% | 1.307%
SW-Toowoomba Dalby Warwick | 3154_Central Dalby 1 33 kV | Limiting Line Name | TR_CABLE 4402_1 | TR_CABLE 4402_1 | TR_CABLE 5202_1 | TR_CABLE 5202_1 | TR_CABLE 4402_1
SW-Toowoomba Dalby Warwick | 3154_Central Dalby 1 33 kV | Loading (A) | 16.5984 | 10.1126 | 5.1745 | 2.1576 | 5.8793
SW-Toowoomba Dalby Warwick | 3154_Central Dalby 1 33 kV | Loading (MVA) | 0.97302 | 0.59351 | 0.30402 | 0.12684 | 0.34597
SW-Toowoomba Dalby Warwick | 3154_Central Dalby 1 33 kV | Loading (MW) | 0.97068 | 0.5922 | 0.2654 | 0.03857 | 0.33541
SW-Toowoomba Dalby Warwick | 3154_Central Dalby 1 33 kV | Power Factor | 0.9976 | 0.99779 | 0.87295 | 0.28857 | 0.96949
SW-Toowoomba Dalby Warwick | 3154_Central Dalby 1 33 kV | Rating (A) | 450 | 450 | 500 | 500 | 450
SW-Toowoomba Dalby Warwick | 3154_Central Dalby 1 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | 3154_Central Dalby 1 33 kV | Min Voltage at Constrained Conductor | 33.8445 | 33.8845 | 33.9218 | 33.9419 | 33.9744
SW-Toowoomba Dalby Warwick | 3154_Central Dalby 1 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Toowoomba Dalby Warwick | 3178_Wilkie Creek 33 kV | % of Rated A | 4.148% | 4.152% | 4.154% | 4.157% | 4.16%
SW-Toowoomba Dalby Warwick | 3178_Wilkie Creek 33 kV | Limiting Line Name | TR_CABLE 3771_1 | TR_CABLE 3771_1 | TR_CABLE 3771_1 | TR_CABLE 3771_1 | TR_CABLE 3771_1
SW-Toowoomba Dalby Warwick | 3178_Wilkie Creek 33 kV | Loading (A) | 3.8577 | 3.861 | 3.8635 | 3.8659 | 3.8686
SW-Toowoomba Dalby Warwick | 3178_Wilkie Creek 33 kV | Loading (MVA) | 0.22131 | 0.22169 | 0.22197 | 0.22224 | 0.22256
SW-Toowoomba Dalby Warwick | 3178_Wilkie Creek 33 kV | Loading (MW) | 0.0082268 | 0.0082294 | 0.0082314 | 0.0082333 | 0.0082355
SW-Toowoomba Dalby Warwick | 3178_Wilkie Creek 33 kV | Power Factor | 0.037173 | 0.037121 | 0.037083 | 0.037046 | 0.037004
SW-Toowoomba Dalby Warwick | 3178_Wilkie Creek 33 kV | Rating (A) | 93 | 93 | 93 | 93 | 93
SW-Toowoomba Dalby Warwick | 3178_Wilkie Creek 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | 3178_Wilkie Creek 33 kV | Min Voltage at Constrained Conductor | 33.122 | 33.1504 | 33.1711 | 33.1913 | 33.2145
SW-Toowoomba Dalby Warwick | 3178_Wilkie Creek 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Toowoomba Dalby Warwick | 3282_Killarney 33kV | % of Rated A | 4.988% | 5.675% | 6.234% | 6.71% | 7.118%
SW-Toowoomba Dalby Warwick | 3282_Killarney 33kV | Limiting Line Name | TR_LINE 23736_3 | TR_LINE 23736_3 | TR_LINE 23736_3 | TR_LINE 23736_3 | TR_LINE 23736_3
SW-Toowoomba Dalby Warwick | 3282_Killarney 33kV | Loading (A) | 5.7861 | 6.5825 | 7.2316 | 7.7831 | 8.2567
SW-Toowoomba Dalby Warwick | 3282_Killarney 33kV | Loading (MVA) | 0.35302 | 0.40174 | 0.44138 | 0.47509 | 0.50417
SW-Toowoomba Dalby Warwick | 3282_Killarney 33kV | Loading (MW) | 0.31933 | 0.37292 | 0.41572 | 0.4517 | 0.48248
SW-Toowoomba Dalby Warwick | 3282_Killarney 33kV | Power Factor | 0.90353 | 0.92707 | 0.94056 | 0.94936 | 0.95548
SW-Toowoomba Dalby Warwick | 3282_Killarney 33kV | Rating (A) | 116 | 116 | 116 | 116 | 116
SW-Toowoomba Dalby Warwick | 3282_Killarney 33kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | 3282_Killarney 33kV | Min Voltage at Constrained Conductor | 35.2257 | 35.237 | 35.2382 | 35.2425 | 35.2545
SW-Toowoomba Dalby Warwick | 3282_Killarney 33kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Toowoomba Dalby Warwick | 3283_Allora 33kV | % of Rated A | 13.54% | 14.83% | 15.84% | 16.68% | 17.38%
SW-Toowoomba Dalby Warwick | 3283_Allora 33kV | Limiting Line Name | TR_LINE ALLORA-pole2134509_a | TR_LINE ALLORA-pole2134509_a | TR_LINE ALLORA-pole2134509_a | TR_LINE ALLORA-pole2134509_a | TR_LINE ALLORA-pole2134509_a
SW-Toowoomba Dalby Warwick | 3283_Allora 33kV | Loading (A) | 22.3416 | 24.4678 | 26.1361 | 27.5187 | 28.6705
SW-Toowoomba Dalby Warwick | 3283_Allora 33kV | Loading (MVA) | 1.3836 | 1.5179 | 1.6232 | 1.7108 | 1.7843
SW-Toowoomba Dalby Warwick | 3283_Allora 33kV | Loading (MW) | 1.3835 | 1.5178 | 1.623 | 1.7106 | 1.7841
SW-Toowoomba Dalby Warwick | 3283_Allora 33kV | Power Factor | 0.99993 | 0.99992 | 0.99991 | 0.9999 | 0.99989
SW-Toowoomba Dalby Warwick | 3283_Allora 33kV | Rating (A) | 165 | 165 | 165 | 165 | 165
SW-Toowoomba Dalby Warwick | 3283_Allora 33kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | 3283_Allora 33kV | Min Voltage at Constrained Conductor | 35.7549 | 35.816 | 35.8562 | 35.8928 | 35.9317
SW-Toowoomba Dalby Warwick | 3283_Allora 33kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Toowoomba Dalby Warwick | 3900_Peranga 33 kV | % of Rated A | 5.983% | 6.17% | 6.319% | 6.444% | 6.531%
SW-Toowoomba Dalby Warwick | 3900_Peranga 33 kV | Limiting Line Name | TR_CABLE 9120_1 | TR_CABLE 9120_1 | TR_CABLE 9120_1 | TR_CABLE 9120_1 | TR_CABLE 9120_1
SW-Toowoomba Dalby Warwick | 3900_Peranga 33 kV | Loading (A) | 5.9827 | 6.1705 | 6.3185 | 6.4443 | 6.5306
SW-Toowoomba Dalby Warwick | 3900_Peranga 33 kV | Loading (MVA) | 0.34818 | 0.3591 | 0.36768 | 0.37498 | 0.38001
SW-Toowoomba Dalby Warwick | 3900_Peranga 33 kV | Loading (MW) | 0.27893 | 0.29262 | 0.30323 | 0.31216 | 0.31826
SW-Toowoomba Dalby Warwick | 3900_Peranga 33 kV | Power Factor | 0.80059 | 0.81437 | 0.82422 | 0.83199 | 0.83703
SW-Toowoomba Dalby Warwick | 3900_Peranga 33 kV | Rating (A) | 100 | 100 | 100 | 100 | 100
SW-Toowoomba Dalby Warwick | 3900_Peranga 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | 3900_Peranga 33 kV | Min Voltage at Constrained Conductor | 33.6005 | 33.5996 | 33.5963 | 33.5944 | 33.5956
SW-Toowoomba Dalby Warwick | 3900_Peranga 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Toowoomba Dalby Warwick | 7233_Middle Ridge-Torrington 110 kV | % of Rated A | 2.305% | 3.406% | 4.497% | 4.414% | 3.637%
SW-Toowoomba Dalby Warwick | 7233_Middle Ridge-Torrington 110 kV | Limiting Line Name | TR_LINE 27024_1 | TR_LINE 27024_1 | TR_LINE 27024_1 | TR_LINE 27024_1 | TR_LINE 27024_1
SW-Toowoomba Dalby Warwick | 7233_Middle Ridge-Torrington 110 kV | Loading (A) | 20.2351 | 29.9074 | 39.4797 | 38.7563 | 31.9326
SW-Toowoomba Dalby Warwick | 7233_Middle Ridge-Torrington 110 kV | Loading (MVA) | 4.0428 | 5.974 | 7.883 | 7.7367 | 6.3748
SW-Toowoomba Dalby Warwick | 7233_Middle Ridge-Torrington 110 kV | Loading (MW) | 3.1042 | 5.4623 | 7.5711 | 7.4787 | 5.6554
SW-Toowoomba Dalby Warwick | 7233_Middle Ridge-Torrington 110 kV | Power Factor | 0.76768 | 0.91409 | 0.96009 | 0.96631 | 0.88688
SW-Toowoomba Dalby Warwick | 7233_Middle Ridge-Torrington 110 kV | Rating (A) | 878 | 878 | 878 | 878 | 878
SW-Toowoomba Dalby Warwick | 7233_Middle Ridge-Torrington 110 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | 7233_Middle Ridge-Torrington 110 kV | Min Voltage at Constrained Conductor | 115.3487 | 115.3254 | 115.2809 | 115.2536 | 115.2576
SW-Toowoomba Dalby Warwick | 7233_Middle Ridge-Torrington 110 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Toowoomba Dalby Warwick | 7234_Middle Ridge-Torrington 110 kV | % of Rated A | 2.379% | 3.523% | 4.654% | 4.569% | 3.761%
SW-Toowoomba Dalby Warwick | 7234_Middle Ridge-Torrington 110 kV | Limiting Line Name | TR_LINE 27022_1 | TR_LINE 27022_1 | TR_LINE 27022_1 | TR_LINE 27022_1 | TR_LINE 27022_1
SW-Toowoomba Dalby Warwick | 7234_Middle Ridge-Torrington 110 kV | Loading (A) | 20.8885 | 30.9319 | 40.8613 | 40.1141 | 33.0244
SW-Toowoomba Dalby Warwick | 7234_Middle Ridge-Torrington 110 kV | Loading (MVA) | 4.1733 | 6.1786 | 8.1589 | 8.0078 | 6.5927
SW-Toowoomba Dalby Warwick | 7234_Middle Ridge-Torrington 110 kV | Loading (MW) | 3.2231 | 5.6654 | 7.8493 | 7.7528 | 5.8673
SW-Toowoomba Dalby Warwick | 7234_Middle Ridge-Torrington 110 kV | Power Factor | 0.77213 | 0.91666 | 0.9617 | 0.9678 | 0.88968
SW-Toowoomba Dalby Warwick | 7234_Middle Ridge-Torrington 110 kV | Rating (A) | 878 | 878 | 878 | 878 | 878
SW-Toowoomba Dalby Warwick | 7234_Middle Ridge-Torrington 110 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | 7234_Middle Ridge-Torrington 110 kV | Min Voltage at Constrained Conductor | 115.3487 | 115.3254 | 115.2809 | 115.2536 | 115.2576
SW-Toowoomba Dalby Warwick | 7234_Middle Ridge-Torrington 110 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Toowoomba Dalby Warwick | 728_Middle Ridge-South Toowoomba 110 kV | % of Rated A | 9.348% | 9.163% | 9.009% | 8.852% | 8.717%
SW-Toowoomba Dalby Warwick | 728_Middle Ridge-South Toowoomba 110 kV | Limiting Line Name | TR_LINE 12070761_1 | TR_LINE 12070761_1 | TR_LINE 12070761_1 | TR_LINE 12070761_1 | TR_LINE 12070761_1
SW-Toowoomba Dalby Warwick | 728_Middle Ridge-South Toowoomba 110 kV | Loading (A) | 96.1948 | 94.2828 | 92.7041 | 91.0832 | 89.6968
SW-Toowoomba Dalby Warwick | 728_Middle Ridge-South Toowoomba 110 kV | Loading (MVA) | 19.2318 | 18.846 | 18.5235 | 18.1956 | 17.9195
SW-Toowoomba Dalby Warwick | 728_Middle Ridge-South Toowoomba 110 kV | Loading (MW) | 8.653 | 7.6801 | 6.8021 | 5.7609 | 4.6873
SW-Toowoomba Dalby Warwick | 728_Middle Ridge-South Toowoomba 110 kV | Power Factor | 0.44993 | 0.40752 | 0.36721 | 0.31661 | 0.26158
SW-Toowoomba Dalby Warwick | 728_Middle Ridge-South Toowoomba 110 kV | Rating (A) | 1029 | 1029 | 1029 | 1029 | 1029
SW-Toowoomba Dalby Warwick | 728_Middle Ridge-South Toowoomba 110 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | 728_Middle Ridge-South Toowoomba 110 kV | Min Voltage at Constrained Conductor | 115.427 | 115.4054 | 115.3623 | 115.3366 | 115.3421
SW-Toowoomba Dalby Warwick | 728_Middle Ridge-South Toowoomba 110 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Toowoomba Dalby Warwick | 730_Middle Ridge-South Toowoomba 110 kV | % of Rated A | 9.349% | 9.164% | 9.011% | 8.853% | 8.719%
SW-Toowoomba Dalby Warwick | 730_Middle Ridge-South Toowoomba 110 kV | Limiting Line Name | TR_LINE 12070768_1 | TR_LINE 12070768_1 | TR_LINE 12070768_1 | TR_LINE 12070768_1 | TR_LINE 12070768_1
SW-Toowoomba Dalby Warwick | 730_Middle Ridge-South Toowoomba 110 kV | Loading (A) | 96.2054 | 94.2969 | 92.7208 | 91.1014 | 89.7157
SW-Toowoomba Dalby Warwick | 730_Middle Ridge-South Toowoomba 110 kV | Loading (MVA) | 19.2339 | 18.8489 | 18.5269 | 18.1993 | 17.9233
SW-Toowoomba Dalby Warwick | 730_Middle Ridge-South Toowoomba 110 kV | Loading (MW) | 8.6575 | 7.6864 | 6.81 | 5.7704 | 4.6986
SW-Toowoomba Dalby Warwick | 730_Middle Ridge-South Toowoomba 110 kV | Power Factor | 0.45011 | 0.40779 | 0.36757 | 0.31707 | 0.26215
SW-Toowoomba Dalby Warwick | 730_Middle Ridge-South Toowoomba 110 kV | Rating (A) | 1029 | 1029 | 1029 | 1029 | 1029
SW-Toowoomba Dalby Warwick | 730_Middle Ridge-South Toowoomba 110 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | 730_Middle Ridge-South Toowoomba 110 kV | Min Voltage at Constrained Conductor | 115.4272 | 115.4057 | 115.3626 | 115.3369 | 115.3424
SW-Toowoomba Dalby Warwick | 730_Middle Ridge-South Toowoomba 110 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Toowoomba Dalby Warwick | 7314_Dalby East 110 kV | % of Rated A | 4.573% | 4.574% | 4.574% | 4.574% | 4.576%
SW-Toowoomba Dalby Warwick | 7314_Dalby East 110 kV | Limiting Line Name | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1 | TR_LINE 56731_1
SW-Toowoomba Dalby Warwick | 7314_Dalby East 110 kV | Loading (A) | 12.6683 | 12.6686 | 12.6691 | 12.6713 | 12.6761
SW-Toowoomba Dalby Warwick | 7314_Dalby East 110 kV | Loading (MVA) | 2.515 | 2.5171 | 2.5187 | 2.5206 | 2.5232
SW-Toowoomba Dalby Warwick | 7314_Dalby East 110 kV | Loading (MW) | 0.31468 | 0.28491 | 0.26125 | 0.24143 | 0.22389
SW-Toowoomba Dalby Warwick | 7314_Dalby East 110 kV | Power Factor | 0.12512 | 0.11319 | 0.10372 | 0.095784 | 0.08873
SW-Toowoomba Dalby Warwick | 7314_Dalby East 110 kV | Rating (A) | 277 | 277 | 277 | 277 | 277
SW-Toowoomba Dalby Warwick | 7314_Dalby East 110 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | 7314_Dalby East 110 kV | Min Voltage at Constrained Conductor | 114.6192 | 114.7125 | 114.7804 | 114.8467 | 114.9243
SW-Toowoomba Dalby Warwick | 7314_Dalby East 110 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Toowoomba Dalby Warwick | 7448_South Toowoomba-TWCE 110 kV | % of Rated A | 11.55% | 11.17% | 10.77% | 10.32% | 9.827%
SW-Toowoomba Dalby Warwick | 7448_South Toowoomba-TWCE 110 kV | Limiting Line Name | TR_CABLE 13760_1 | TR_CABLE 13760_1 | TR_CABLE 13760_1 | TR_CABLE 13760_1 | TR_CABLE 13760_1
SW-Toowoomba Dalby Warwick | 7448_South Toowoomba-TWCE 110 kV | Loading (A) | 48.5072 | 46.9234 | 45.2301 | 43.3572 | 41.2714
SW-Toowoomba Dalby Warwick | 7448_South Toowoomba-TWCE 110 kV | Loading (MVA) | 9.714 | 9.3953 | 9.053 | 8.6764 | 8.2596
SW-Toowoomba Dalby Warwick | 7448_South Toowoomba-TWCE 110 kV | Loading (MW) | 7.7728 | 7.3416 | 6.8681 | 6.3264 | 5.6936
SW-Toowoomba Dalby Warwick | 7448_South Toowoomba-TWCE 110 kV | Power Factor | 0.80017 | 0.78142 | 0.75865 | 0.72915 | 0.68933
SW-Toowoomba Dalby Warwick | 7448_South Toowoomba-TWCE 110 kV | Rating (A) | 420 | 420 | 420 | 420 | 420
SW-Toowoomba Dalby Warwick | 7448_South Toowoomba-TWCE 110 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | 7448_South Toowoomba-TWCE 110 kV | Min Voltage at Constrained Conductor | 115.619 | 115.6 | 115.5592 | 115.5362 | 115.5445
SW-Toowoomba Dalby Warwick | 7448_South Toowoomba-TWCE 110 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Toowoomba Dalby Warwick | 7449 South Toowoomba-TWCE 110 kV | % of Rated A | 8.623% | 8.496% | 8.361% | 8.216% | 8.06%
SW-Toowoomba Dalby Warwick | 7449 South Toowoomba-TWCE 110 kV | Limiting Line Name | TR_CABLE 13761_1 | TR_CABLE 13761_1 | TR_CABLE 13761_1 | TR_CABLE 13761_1 | TR_CABLE 13761_1
SW-Toowoomba Dalby Warwick | 7449 South Toowoomba-TWCE 110 kV | Loading (A) | 36.2176 | 35.6821 | 35.1161 | 34.5067 | 33.8506
SW-Toowoomba Dalby Warwick | 7449 South Toowoomba-TWCE 110 kV | Loading (MVA) | 7.2529 | 7.1445 | 7.0287 | 6.9053 | 6.7745
SW-Toowoomba Dalby Warwick | 7449 South Toowoomba-TWCE 110 kV | Loading (MW) | 3.9458 | 3.7305 | 3.4939 | 3.2233 | 2.9073
SW-Toowoomba Dalby Warwick | 7449 South Toowoomba-TWCE 110 kV | Power Factor | 0.54404 | 0.52215 | 0.49709 | 0.46679 | 0.42915
SW-Toowoomba Dalby Warwick | 7449 South Toowoomba-TWCE 110 kV | Rating (A) | 420 | 420 | 420 | 420 | 420
SW-Toowoomba Dalby Warwick | 7449 South Toowoomba-TWCE 110 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | 7449 South Toowoomba-TWCE 110 kV | Min Voltage at Constrained Conductor | 115.6192 | 115.6002 | 115.5594 | 115.5363 | 115.5445
SW-Toowoomba Dalby Warwick | 7449 South Toowoomba-TWCE 110 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Toowoomba Dalby Warwick | 790_Warwick-Stanthorpe 110 kV | % of Rated A | 20.84% | 20.99% | 21.12% | 21.25% | 21.35%
SW-Toowoomba Dalby Warwick | 790_Warwick-Stanthorpe 110 kV | Limiting Line Name | TR_LINE 198182_1 | TR_LINE 198182_1 | TR_LINE 198182_1 | TR_LINE 198182_1 | TR_LINE 198182_1
SW-Toowoomba Dalby Warwick | 790_Warwick-Stanthorpe 110 kV | Loading (A) | 26.4625 | 26.6592 | 26.8276 | 26.9831 | 27.1155
SW-Toowoomba Dalby Warwick | 790_Warwick-Stanthorpe 110 kV | Loading (MVA) | 5.5082 | 5.5527 | 5.5892 | 5.6234 | 5.6537
SW-Toowoomba Dalby Warwick | 790_Warwick-Stanthorpe 110 kV | Loading (MW) | 0.92951 | 1.1382 | 1.2984 | 1.4303 | 1.5307
SW-Toowoomba Dalby Warwick | 790_Warwick-Stanthorpe 110 kV | Power Factor | 0.16874 | 0.20498 | 0.23229 | 0.25434 | 0.27073
SW-Toowoomba Dalby Warwick | 790_Warwick-Stanthorpe 110 kV | Rating (A) | 127 | 127 | 127 | 127 | 127
SW-Toowoomba Dalby Warwick | 790_Warwick-Stanthorpe 110 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | 790_Warwick-Stanthorpe 110 kV | Min Voltage at Constrained Conductor | 120.1773 | 120.2523 | 120.2842 | 120.3217 | 120.3799
SW-Toowoomba Dalby Warwick | 790_Warwick-Stanthorpe 110 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Toowoomba Dalby Warwick | F008D_Central Dalby 2 33 kV | % of Rated A | 3.54% | 2.179% | 1.025% | 0.396% | 1.262%
SW-Toowoomba Dalby Warwick | F008D_Central Dalby 2 33 kV | Limiting Line Name | TR_CABLE 5204_1 | TR_CABLE 5204_1 | TR_CABLE 5204_1 | TR_CABLE 5204_1 | TR_CABLE 5204_1
SW-Toowoomba Dalby Warwick | F008D_Central Dalby 2 33 kV | Loading (A) | 17.6999 | 10.8967 | 5.1275 | 1.98 | 6.3119
SW-Toowoomba Dalby Warwick | F008D_Central Dalby 2 33 kV | Loading (MVA) | 1.0384 | 0.63984 | 0.30126 | 0.1164 | 0.37133
SW-Toowoomba Dalby Warwick | F008D_Central Dalby 2 33 kV | Loading (MW) | 1.0349 | 0.63232 | 0.28215 | 0.041146 | 0.35573
SW-Toowoomba Dalby Warwick | F008D_Central Dalby 2 33 kV | Power Factor | 0.99662 | 0.98825 | 0.93656 | 0.33677 | 0.95276
SW-Toowoomba Dalby Warwick | F008D_Central Dalby 2 33 kV | Rating (A) | 500 | 500 | 500 | 500 | 500
SW-Toowoomba Dalby Warwick | F008D_Central Dalby 2 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F008D_Central Dalby 2 33 kV | Min Voltage at Constrained Conductor | 33.8711 | 33.9005 | 33.9217 | 33.9419 | 33.9652
SW-Toowoomba Dalby Warwick | F008D_Central Dalby 2 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Toowoomba Dalby Warwick | F019D_West Dalby No 1 33 kV | % of Rated A | 7.016% | 5.466% | 4.127% | 2.914% | 1.767%
SW-Toowoomba Dalby Warwick | F019D_West Dalby No 1 33 kV | Limiting Line Name | TR_LINE 58890_1 | TR_LINE 58890_1 | TR_LINE 58890_1 | TR_LINE 58890_1 | TR_LINE 58890_1
SW-Toowoomba Dalby Warwick | F019D_West Dalby No 1 33 kV | Loading (A) | 26.3111 | 20.498 | 15.4771 | 10.9288 | 6.6254
SW-Toowoomba Dalby Warwick | F019D_West Dalby No 1 33 kV | Loading (MVA) | 1.5422 | 1.2027 | 0.90879 | 0.64219 | 0.38964
SW-Toowoomba Dalby Warwick | F019D_West Dalby No 1 33 kV | Loading (MW) | 1.5342 | 1.1926 | 0.89524 | 0.62218 | 0.35474
SW-Toowoomba Dalby Warwick | F019D_West Dalby No 1 33 kV | Power Factor | 0.9945 | 0.99132 | 0.98488 | 0.96869 | 0.91035
SW-Toowoomba Dalby Warwick | F019D_West Dalby No 1 33 kV | Rating (A) | 375 | 375 | 375 | 375 | 375
SW-Toowoomba Dalby Warwick | F019D_West Dalby No 1 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F019D_West Dalby No 1 33 kV | Min Voltage at Constrained Conductor | 33.8395 | 33.8748 | 33.901 | 33.9258 | 33.9537
SW-Toowoomba Dalby Warwick | F019D_West Dalby No 1 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Toowoomba Dalby Warwick | F039D_West Dalby No 2 33 kV | % of Rated A | 20.61% | 19.76% | 19.02% | 18.33% | 17.65%
SW-Toowoomba Dalby Warwick | F039D_West Dalby No 2 33 kV | Limiting Line Name | TR_CABLE 139_1 | TR_CABLE 139_1 | TR_CABLE 139_1 | TR_CABLE 139_1 | TR_CABLE 139_1
SW-Toowoomba Dalby Warwick | F039D_West Dalby No 2 33 kV | Loading (A) | 58.5466 | 56.1226 | 54.0103 | 52.0609 | 50.1307
SW-Toowoomba Dalby Warwick | F039D_West Dalby No 2 33 kV | Loading (MVA) | 3.4279 | 3.2901 | 3.1692 | 3.0575 | 2.9469
SW-Toowoomba Dalby Warwick | F039D_West Dalby No 2 33 kV | Loading (MW) | 3.4263 | 3.2882 | 3.1672 | 3.0552 | 2.9446
SW-Toowoomba Dalby Warwick | F039D_West Dalby No 2 33 kV | Power Factor | 0.99936 | 0.99928 | 0.9992 | 0.9991 | 0.99901
SW-Toowoomba Dalby Warwick | F039D_West Dalby No 2 33 kV | Rating (A) | 284 | 284 | 284 | 284 | 284
SW-Toowoomba Dalby Warwick | F039D_West Dalby No 2 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F039D_West Dalby No 2 33 kV | Min Voltage at Constrained Conductor | 33.8043 | 33.8458 | 33.8774 | 33.907 | 33.9397
SW-Toowoomba Dalby Warwick | F039D_West Dalby No 2 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Toowoomba Dalby Warwick | F095D_Kaimkillenbun 33 kV | % of Rated A | 4.37% | 4.194% | 4.118% | 4.1% | 4.461%
SW-Toowoomba Dalby Warwick | F095D_Kaimkillenbun 33 kV | Limiting Line Name | TR_CABLE 5206_1 | TR_CABLE 5206_1 | TR_CABLE 5206_1 | TR_CABLE 5206_1 | TR_LINE 23047_1
SW-Toowoomba Dalby Warwick | F095D_Kaimkillenbun 33 kV | Loading (A) | 4.3698 | 4.194 | 4.118 | 4.1003 | 4.1487
SW-Toowoomba Dalby Warwick | F095D_Kaimkillenbun 33 kV | Loading (MVA) | 0.25637 | 0.24626 | 0.24195 | 0.24105 | 0.24453
SW-Toowoomba Dalby Warwick | F095D_Kaimkillenbun 33 kV | Loading (MW) | 0.086171 | 0.048055 | 0.018594 | 0.0059025 | 0.2445
SW-Toowoomba Dalby Warwick | F095D_Kaimkillenbun 33 kV | Power Factor | 0.33612 | 0.19514 | 0.076851 | 0.02238 | 0.99988
SW-Toowoomba Dalby Warwick | F095D_Kaimkillenbun 33 kV | Rating (A) | 100 | 100 | 100 | 100 | 93
SW-Toowoomba Dalby Warwick | F095D_Kaimkillenbun 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F095D_Kaimkillenbun 33 kV | Min Voltage at Constrained Conductor | 33.872 | 33.901 | 33.9219 | 33.9419 | 34.0298
SW-Toowoomba Dalby Warwick | F095D_Kaimkillenbun 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Toowoomba Dalby Warwick | F097D_Jandowae 33 kV | % of Rated A | 5.731% | 5.261% | 5.16% | 5.156% | 5.15%
SW-Toowoomba Dalby Warwick | F097D_Jandowae 33 kV | Limiting Line Name | TR_LINE 102880_1 | TR_LINE 102880_1 | TR_CABLE 130_1 | TR_CABLE 130_1 | TR_CABLE 130_1
SW-Toowoomba Dalby Warwick | F097D_Jandowae 33 kV | Loading (A) | 13.9269 | 12.7853 | 8.2562 | 8.2488 | 8.2408
SW-Toowoomba Dalby Warwick | F097D_Jandowae 33 kV | Loading (MVA) | 0.81534 | 0.74943 | 0.48438 | 0.48438 | 0.48437
SW-Toowoomba Dalby Warwick | F097D_Jandowae 33 kV | Loading (MW) | 0.8136 | 0.74757 | 0.40985 | 0.40985 | 0.40985
SW-Toowoomba Dalby Warwick | F097D_Jandowae 33 kV | Power Factor | 0.99787 | 0.99751 | 0.84586 | 0.84586 | 0.84587
SW-Toowoomba Dalby Warwick | F097D_Jandowae 33 kV | Rating (A) | 243 | 243 | 160 | 160 | 160
SW-Toowoomba Dalby Warwick | F097D_Jandowae 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F097D_Jandowae 33 kV | Min Voltage at Constrained Conductor | 33.8004 | 33.8422 | 33.8728 | 33.9026 | 33.9355
SW-Toowoomba Dalby Warwick | F097D_Jandowae 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Toowoomba Dalby Warwick | F099D_Warra 33 kV | % of Rated A | 58.7% | 58.63% | 58.57% | 58.52% | 58.46%
SW-Toowoomba Dalby Warwick | F099D_Warra 33 kV | Limiting Line Name | TR_CABLE 132_1 | TR_CABLE 132_1 | TR_CABLE 132_1 | TR_CABLE 132_1 | TR_CABLE 132_1
SW-Toowoomba Dalby Warwick | F099D_Warra 33 kV | Loading (A) | 58.7037 | 58.6301 | 58.5742 | 58.5223 | 58.4644
SW-Toowoomba Dalby Warwick | F099D_Warra 33 kV | Loading (MVA) | 3.4031 | 3.4031 | 3.4031 | 3.4031 | 3.4031
SW-Toowoomba Dalby Warwick | F099D_Warra 33 kV | Loading (MW) | 3.4006 | 3.4006 | 3.4006 | 3.4006 | 3.4006
SW-Toowoomba Dalby Warwick | F099D_Warra 33 kV | Power Factor | 0.99916 | 0.99916 | 0.99916 | 0.99916 | 0.99916
SW-Toowoomba Dalby Warwick | F099D_Warra 33 kV | Rating (A) | 100 | 100 | 100 | 100 | 100
SW-Toowoomba Dalby Warwick | F099D_Warra 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F099D_Warra 33 kV | Min Voltage at Constrained Conductor | 33.469 | 33.511 | 33.543 | 33.5728 | 33.606
SW-Toowoomba Dalby Warwick | F099D_Warra 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Toowoomba Dalby Warwick | F2060_Sladevale 1 33kV | % of Rated A | 7.067% | 7.23% | 7.364% | 7.48% | 7.581%
SW-Toowoomba Dalby Warwick | F2060_Sladevale 1 33kV | Limiting Line Name | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1 | TR_LINE 101656398_1
SW-Toowoomba Dalby Warwick | F2060_Sladevale 1 33kV | Loading (A) | 44.8761 | 45.9091 | 46.7593 | 47.4966 | 48.1382
SW-Toowoomba Dalby Warwick | F2060_Sladevale 1 33kV | Loading (MVA) | 2.7367 | 2.8006 | 2.8525 | 2.8979 | 2.938
SW-Toowoomba Dalby Warwick | F2060_Sladevale 1 33kV | Loading (MW) | 1.3626 | 1.4928 | 1.5946 | 1.6791 | 1.7499
SW-Toowoomba Dalby Warwick | F2060_Sladevale 1 33kV | Power Factor | 0.49791 | 0.53301 | 0.55899 | 0.57941 | 0.59561
SW-Toowoomba Dalby Warwick | F2060_Sladevale 1 33kV | Rating (A) | 635 | 635 | 635 | 635 | 635
SW-Toowoomba Dalby Warwick | F2060_Sladevale 1 33kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F2060_Sladevale 1 33kV | Min Voltage at Constrained Conductor | 35.2087 | 35.22 | 35.2211 | 35.2254 | 35.2374
SW-Toowoomba Dalby Warwick | F2060_Sladevale 1 33kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Toowoomba Dalby Warwick | F2325_Broxburn 33 kV | % of Rated A | 2.031% | 1.153% | 0.5078% | 0.7902% | 1.34%
SW-Toowoomba Dalby Warwick | F2325_Broxburn 33 kV | Limiting Line Name | TR_LINE 23767_1 | TR_LINE 60091_1 | TR_LINE 60091_1 | TR_LINE 23767_1 | TR_LINE 23767_1
SW-Toowoomba Dalby Warwick | F2325_Broxburn 33 kV | Loading (A) | 7.9017 | 3.8497 | 1.696 | 3.0738 | 5.2123
SW-Toowoomba Dalby Warwick | F2325_Broxburn 33 kV | Loading (MVA) | 0.45518 | 0.2218 | 0.097709 | 0.17709 | 0.30398
SW-Toowoomba Dalby Warwick | F2325_Broxburn 33 kV | Loading (MW) | 0.44294 | 0.21306 | 0.075398 | 0.14147 | 0.28386
SW-Toowoomba Dalby Warwick | F2325_Broxburn 33 kV | Power Factor | 0.97312 | 0.96057 | 0.77166 | 0.79885 | 0.93382
SW-Toowoomba Dalby Warwick | F2325_Broxburn 33 kV | Rating (A) | 389 | 334 | 334 | 389 | 389
SW-Toowoomba Dalby Warwick | F2325_Broxburn 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F2325_Broxburn 33 kV | Min Voltage at Constrained Conductor | 33.2584 | 33.2582 | 33.2617 | 33.2624 | 33.6706
SW-Toowoomba Dalby Warwick | F2325_Broxburn 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Toowoomba Dalby Warwick | F2450_Carrington Road 33 kV | % of Rated A | 1.816% | 2.172% | 2.45% | 2.679% | 2.857%
SW-Toowoomba Dalby Warwick | F2450_Carrington Road 33 kV | Limiting Line Name | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1 | HV_LINE_23587013_1
SW-Toowoomba Dalby Warwick | F2450_Carrington Road 33 kV | Loading (A) | 6.1189 | 7.3192 | 8.2552 | 9.028 | 9.6287
SW-Toowoomba Dalby Warwick | F2450_Carrington Road 33 kV | Loading (MVA) | 0.35963 | 0.43014 | 0.48496 | 0.53003 | 0.56623
SW-Toowoomba Dalby Warwick | F2450_Carrington Road 33 kV | Loading (MW) | 0.35958 | 0.4301 | 0.48491 | 0.52999 | 0.56619
SW-Toowoomba Dalby Warwick | F2450_Carrington Road 33 kV | Power Factor | 0.99989 | 0.99991 | 0.99991 | 0.99992 | 0.99992
SW-Toowoomba Dalby Warwick | F2450_Carrington Road 33 kV | Rating (A) | 337 | 337 | 337 | 337 | 337
SW-Toowoomba Dalby Warwick | F2450_Carrington Road 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F2450_Carrington Road 33 kV | Min Voltage at Constrained Conductor | 33.9323 | 33.9298 | 33.9165 | 33.8959 | 33.9519
SW-Toowoomba Dalby Warwick | F2450_Carrington Road 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Toowoomba Dalby Warwick | F2460_Cecil Plains 33 kV | % of Rated A | 25% | 25.04% | 25.1% | 25.16% | 25.54%
SW-Toowoomba Dalby Warwick | F2460_Cecil Plains 33 kV | Limiting Line Name | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1 | TR_LINE 23367_1
SW-Toowoomba Dalby Warwick | F2460_Cecil Plains 33 kV | Loading (A) | 35.7447 | 35.8118 | 35.889 | 35.9852 | 36.5257
SW-Toowoomba Dalby Warwick | F2460_Cecil Plains 33 kV | Loading (MVA) | 2.1058 | 2.1112 | 2.1165 | 2.123 | 2.1821
SW-Toowoomba Dalby Warwick | F2460_Cecil Plains 33 kV | Loading (MW) | 0.037657 | 0.10343 | 0.16085 | 0.21349 | 0.26474
SW-Toowoomba Dalby Warwick | F2460_Cecil Plains 33 kV | Power Factor | 0.012356 | 0.04346 | 0.070454 | 0.095003 | 0.11575
SW-Toowoomba Dalby Warwick | F2460_Cecil Plains 33 kV | Rating (A) | 143 | 143 | 143 | 143 | 143
SW-Toowoomba Dalby Warwick | F2460_Cecil Plains 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F2460_Cecil Plains 33 kV | Min Voltage at Constrained Conductor | 34.0135 | 34.036 | 34.0477 | 34.0617 | 34.4912
SW-Toowoomba Dalby Warwick | F2460_Cecil Plains 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Toowoomba Dalby Warwick | F2520_Clifton 33 kV | % of Rated A | 23.74% | 23.15% | 22.94% | 22.97% | 23.03%
SW-Toowoomba Dalby Warwick | F2520_Clifton 33 kV | Limiting Line Name | TR_LINE 188412_1 | TR_LINE 188412_1 | TR_LINE 188412_1 | TR_LINE 188412_1 | TR_LINE 188412_1
SW-Toowoomba Dalby Warwick | F2520_Clifton 33 kV | Loading (A) | 28.958 | 28.2385 | 27.9862 | 28.02 | 28.1022
SW-Toowoomba Dalby Warwick | F2520_Clifton 33 kV | Loading (MVA) | 1.7873 | 1.741 | 1.7225 | 1.7267 | 1.7341
SW-Toowoomba Dalby Warwick | F2520_Clifton 33 kV | Loading (MW) | 0.42008 | 0.1858 | 0.072544 | 0.0067126 | 0.075351
SW-Toowoomba Dalby Warwick | F2520_Clifton 33 kV | Power Factor | 0.2347 | 0.10638 | 0.04182 | 0.0035544 | 0.043119
SW-Toowoomba Dalby Warwick | F2520_Clifton 33 kV | Rating (A) | 122 | 122 | 122 | 122 | 122
SW-Toowoomba Dalby Warwick | F2520_Clifton 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F2520_Clifton 33 kV | Min Voltage at Constrained Conductor | 35.6339 | 35.5953 | 35.5347 | 35.5787 | 35.6262
SW-Toowoomba Dalby Warwick | F2520_Clifton 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Toowoomba Dalby Warwick | F2777_East Stanthorpe 33 kV | % of Rated A | 1.646% | 1.647% | 1.647% | 1.647% | 1.648%
SW-Toowoomba Dalby Warwick | F2777_East Stanthorpe 33 kV | Limiting Line Name | TR_LINE 140241_1 | TR_LINE 140241_1 | TR_LINE 140241_1 | TR_LINE 140241_1 | TR_LINE 140241_1
SW-Toowoomba Dalby Warwick | F2777_East Stanthorpe 33 kV | Loading (A) | 2.5353 | 2.5362 | 2.5364 | 2.5368 | 2.5378
SW-Toowoomba Dalby Warwick | F2777_East Stanthorpe 33 kV | Loading (MVA) | 0.15456 | 0.15467 | 0.15469 | 0.15474 | 0.15486
SW-Toowoomba Dalby Warwick | F2777_East Stanthorpe 33 kV | Loading (MW) | 7.2883e-05 | 7.2936e-05 | 7.2947e-05 | 7.297e-05 | 7.3025e-05
SW-Toowoomba Dalby Warwick | F2777_East Stanthorpe 33 kV | Power Factor | 0.00046954 | 0.00046954 | 0.00046954 | 0.00046954 | 0.00046954
SW-Toowoomba Dalby Warwick | F2777_East Stanthorpe 33 kV | Rating (A) | 154 | 154 | 154 | 154 | 154
SW-Toowoomba Dalby Warwick | F2777_East Stanthorpe 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F2777_East Stanthorpe 33 kV | Min Voltage at Constrained Conductor | 35.1963 | 35.2092 | 35.2118 | 35.2174 | 35.2307
SW-Toowoomba Dalby Warwick | F2777_East Stanthorpe 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Toowoomba Dalby Warwick | F2780_East Warwick No 1 33 kV | % of Rated A | 8.56% | 8.519% | 8.523% | 8.561% | 8.624%
SW-Toowoomba Dalby Warwick | F2780_East Warwick No 1 33 kV | Limiting Line Name | TR_LINE 23896_1 | TR_LINE 23896_1 | TR_LINE 23896_1 | TR_LINE 23896_1 | TR_LINE 23896_1
SW-Toowoomba Dalby Warwick | F2780_East Warwick No 1 33 kV | Loading (A) | 45.3665 | 45.15 | 45.1731 | 45.3711 | 45.7079
SW-Toowoomba Dalby Warwick | F2780_East Warwick No 1 33 kV | Loading (MVA) | 2.76 | 2.7476 | 2.749 | 2.7614 | 2.7828
SW-Toowoomba Dalby Warwick | F2780_East Warwick No 1 33 kV | Loading (MW) | 0.2999 | 0.080371 | 0.10599 | 0.27533 | 0.43152
SW-Toowoomba Dalby Warwick | F2780_East Warwick No 1 33 kV | Power Factor | 0.10864 | 0.029229 | 0.038533 | 0.099684 | 0.15504
SW-Toowoomba Dalby Warwick | F2780_East Warwick No 1 33 kV | Rating (A) | 530 | 530 | 530 | 530 | 530
SW-Toowoomba Dalby Warwick | F2780_East Warwick No 1 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F2780_East Warwick No 1 33 kV | Min Voltage at Constrained Conductor | 35.1242 | 35.1346 | 35.1351 | 35.1388 | 35.1503
SW-Toowoomba Dalby Warwick | F2780_East Warwick No 1 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Toowoomba Dalby Warwick | F2785_East Warwick No 2 33 kV | % of Rated A | 8.518% | 8.477% | 8.481% | 8.518% | 8.582%
SW-Toowoomba Dalby Warwick | F2785_East Warwick No 2 33 kV | Limiting Line Name | TR_LINE 23891_1 | TR_LINE 23891_1 | TR_LINE 23891_1 | TR_LINE 23891_1 | TR_LINE 23891_1
SW-Toowoomba Dalby Warwick | F2785_East Warwick No 2 33 kV | Loading (A) | 45.1432 | 44.9278 | 44.9508 | 45.1478 | 45.4829
SW-Toowoomba Dalby Warwick | F2785_East Warwick No 2 33 kV | Loading (MVA) | 2.7464 | 2.7341 | 2.7355 | 2.7478 | 2.7691
SW-Toowoomba Dalby Warwick | F2785_East Warwick No 2 33 kV | Loading (MW) | 0.29957 | 0.081132 | 0.10432 | 0.27282 | 0.42824
SW-Toowoomba Dalby Warwick | F2785_East Warwick No 2 33 kV | Power Factor | 0.10906 | 0.029649 | 0.038109 | 0.09926 | 0.15462
SW-Toowoomba Dalby Warwick | F2785_East Warwick No 2 33 kV | Rating (A) | 530 | 530 | 530 | 530 | 530
SW-Toowoomba Dalby Warwick | F2785_East Warwick No 2 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F2785_East Warwick No 2 33 kV | Min Voltage at Constrained Conductor | 35.1242 | 35.1346 | 35.1351 | 35.1388 | 35.1503
SW-Toowoomba Dalby Warwick | F2785_East Warwick No 2 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Toowoomba Dalby Warwick | F3040 Hampton Street | % of Rated A | 0.3082% | 0.3082% | 0.3081% | 0.308% | 0.3081%
SW-Toowoomba Dalby Warwick | F3040 Hampton Street | Limiting Line Name | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1 | TR_CABLE 80_1
SW-Toowoomba Dalby Warwick | F3040 Hampton Street | Loading (A) | 1.541 | 1.5409 | 1.5404 | 1.5402 | 1.5404
SW-Toowoomba Dalby Warwick | F3040 Hampton Street | Loading (MVA) | 0.093028 | 0.09301 | 0.092953 | 0.092927 | 0.09295
SW-Toowoomba Dalby Warwick | F3040 Hampton Street | Loading (MW) | 0.001311 | 0.0013108 | 0.00131 | 0.0013096 | 0.0013099
SW-Toowoomba Dalby Warwick | F3040 Hampton Street | Power Factor | 0.011534 | 0.011534 | 0.011534 | 0.011534 | 0.011534
SW-Toowoomba Dalby Warwick | F3040 Hampton Street | Rating (A) | 500 | 500 | 500 | 500 | 500
SW-Toowoomba Dalby Warwick | F3040 Hampton Street | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F3040 Hampton Street | Min Voltage at Constrained Conductor | 34.853 | 34.8497 | 34.839 | 34.8342 | 34.8385
SW-Toowoomba Dalby Warwick | F3040 Hampton Street | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Toowoomba Dalby Warwick | F3095_Highfields 33 kV | % of Rated A | 3.433% | 2.11% | 1.54% | 1.241% | 1.179%
SW-Toowoomba Dalby Warwick | F3095_Highfields 33 kV | Limiting Line Name | TR_LINE 194642_1 | TR_LINE 194642_1 | TR_LINE 24220_1 | TR_LINE 24220_1 | TR_LINE 194642_1
SW-Toowoomba Dalby Warwick | F3095_Highfields 33 kV | Loading (A) | 5.8016 | 3.5662 | 3.3264 | 2.6797 | 1.9933
SW-Toowoomba Dalby Warwick | F3095_Highfields 33 kV | Loading (MVA) | 0.34164 | 0.21001 | 0.19581 | 0.15776 | 0.11713
SW-Toowoomba Dalby Warwick | F3095_Highfields 33 kV | Loading (MW) | 0.33996 | 0.2071 | 0.19093 | 0.15154 | 0.11711
SW-Toowoomba Dalby Warwick | F3095_Highfields 33 kV | Power Factor | 0.99506 | 0.98613 | 0.97504 | 0.96053 | 0.99984
SW-Toowoomba Dalby Warwick | F3095_Highfields 33 kV | Rating (A) | 169 | 169 | 216 | 216 | 169
SW-Toowoomba Dalby Warwick | F3095_Highfields 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F3095_Highfields 33 kV | Min Voltage at Constrained Conductor | 33.9977 | 33.9989 | 33.9871 | 33.9907 | 33.925
SW-Toowoomba Dalby Warwick | F3095_Highfields 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Toowoomba Dalby Warwick | F3253_Jellicoe Street 33 kV | % of Rated A | 0.968% | 0.9682% | 0.968% | 0.9655% | 0.9651%
SW-Toowoomba Dalby Warwick | F3253_Jellicoe Street 33 kV | Limiting Line Name | TR_LINE 23977_2 | TR_LINE 23977_2 | TR_LINE 23977_2 | TR_LINE 23977_2 | TR_LINE 23977_2
SW-Toowoomba Dalby Warwick | F3253_Jellicoe Street 33 kV | Loading (A) | 2.1393 | 2.1397 | 2.1394 | 2.1338 | 2.1329
SW-Toowoomba Dalby Warwick | F3253_Jellicoe Street 33 kV | Loading (MVA) | 0.12573 | 0.12578 | 0.12573 | 0.12509 | 0.12498
SW-Toowoomba Dalby Warwick | F3253_Jellicoe Street 33 kV | Loading (MW) | 0.0022272 | 0.002228 | 0.0022273 | 0.0022158 | 0.0022139
SW-Toowoomba Dalby Warwick | F3253_Jellicoe Street 33 kV | Power Factor | 0.017714 | 0.017714 | 0.017714 | 0.017714 | 0.017714
SW-Toowoomba Dalby Warwick | F3253_Jellicoe Street 33 kV | Rating (A) | 221 | 221 | 221 | 221 | 221
SW-Toowoomba Dalby Warwick | F3253_Jellicoe Street 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F3253_Jellicoe Street 33 kV | Min Voltage at Constrained Conductor | 33.9312 | 33.9376 | 33.9319 | 33.8445 | 33.8295
SW-Toowoomba Dalby Warwick | F3253_Jellicoe Street 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Toowoomba Dalby Warwick | F3255_Jennings Street 33 kV | % of Rated A | 2.3% | 1.183% | 0.4251% | 0.8996% | 1.737%
SW-Toowoomba Dalby Warwick | F3255_Jennings Street 33 kV | Limiting Line Name | TR_CABLE 81_1 | TR_CABLE 81_1 | TR_CABLE 81_1 | TR_CABLE 81_1 | TR_CABLE 81_1
SW-Toowoomba Dalby Warwick | F3255_Jennings Street 33 kV | Loading (A) | 14.3737 | 7.3939 | 2.6567 | 5.6224 | 10.8591
SW-Toowoomba Dalby Warwick | F3255_Jennings Street 33 kV | Loading (MVA) | 0.8677 | 0.44631 | 0.16031 | 0.33923 | 0.65526
SW-Toowoomba Dalby Warwick | F3255_Jennings Street 33 kV | Loading (MW) | 0.85554 | 0.41991 | 0.045442 | 0.30391 | 0.63903
SW-Toowoomba Dalby Warwick | F3255_Jennings Street 33 kV | Power Factor | 0.98599 | 0.94086 | 0.28346 | 0.89153 | 0.97295
SW-Toowoomba Dalby Warwick | F3255_Jennings Street 33 kV | Rating (A) | 625 | 625 | 625 | 625 | 625
SW-Toowoomba Dalby Warwick | F3255_Jennings Street 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F3255_Jennings Street 33 kV | Min Voltage at Constrained Conductor | 34.8522 | 34.8494 | 34.839 | 34.8342 | 34.8385
SW-Toowoomba Dalby Warwick | F3255_Jennings Street 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Toowoomba Dalby Warwick | F3315_Sladevale 2 33kV | % of Rated A | 7.126% | 7.143% | 7.157% | 7.17% | 7.184%
SW-Toowoomba Dalby Warwick | F3315_Sladevale 2 33kV | Limiting Line Name | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1 | TR_CABLE 838234276_1
SW-Toowoomba Dalby Warwick | F3315_Sladevale 2 33kV | Loading (A) | 45.2492 | 45.3576 | 45.4447 | 45.529 | 45.6165
SW-Toowoomba Dalby Warwick | F3315_Sladevale 2 33kV | Loading (MVA) | 2.7598 | 2.7673 | 2.7727 | 2.7781 | 2.7844
SW-Toowoomba Dalby Warwick | F3315_Sladevale 2 33kV | Loading (MW) | 0.3159 | 0.36937 | 0.41206 | 0.44795 | 0.47863
SW-Toowoomba Dalby Warwick | F3315_Sladevale 2 33kV | Power Factor | 0.11325 | 0.13226 | 0.1474 | 0.16003 | 0.17069
SW-Toowoomba Dalby Warwick | F3315_Sladevale 2 33kV | Rating (A) | 635 | 635 | 635 | 635 | 635
SW-Toowoomba Dalby Warwick | F3315_Sladevale 2 33kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F3315_Sladevale 2 33kV | Min Voltage at Constrained Conductor | 35.2136 | 35.2244 | 35.2252 | 35.2292 | 35.241
SW-Toowoomba Dalby Warwick | F3315_Sladevale 2 33kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Toowoomba Dalby Warwick | F3530_Millmerran 33 kV | % of Rated A | 3.097% | 2.091% | 1.445% | 1.269% | 1.551%
SW-Toowoomba Dalby Warwick | F3530_Millmerran 33 kV | Limiting Line Name | TR_LINE 24237_1 | TR_LINE 24237_1 | TR_LINE 24237_1 | TR_LINE 24237_1 | TR_LINE 24237_1
SW-Toowoomba Dalby Warwick | F3530_Millmerran 33 kV | Loading (A) | 3.9332 | 2.6556 | 1.835 | 1.6114 | 1.9694
SW-Toowoomba Dalby Warwick | F3530_Millmerran 33 kV | Loading (MVA) | 0.22942 | 0.15499 | 0.10713 | 0.094107 | 0.115
SW-Toowoomba Dalby Warwick | F3530_Millmerran 33 kV | Loading (MW) | 0.21007 | 0.124 | 0.052544 | 0.01045 | 0.06702
SW-Toowoomba Dalby Warwick | F3530_Millmerran 33 kV | Power Factor | 0.91568 | 0.80004 | 0.49048 | 0.11105 | 0.58277
SW-Toowoomba Dalby Warwick | F3530_Millmerran 33 kV | Rating (A) | 127 | 127 | 127 | 127 | 127
SW-Toowoomba Dalby Warwick | F3530_Millmerran 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F3530_Millmerran 33 kV | Min Voltage at Constrained Conductor | 33.676 | 33.6969 | 33.7064 | 33.7178 | 33.7135
SW-Toowoomba Dalby Warwick | F3530_Millmerran 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Toowoomba Dalby Warwick | F3815 North Street No 1 33 kV | % of Rated A | 1.315% | 1.314% | 1.314% | 1.314% | 1.312%
SW-Toowoomba Dalby Warwick | F3815 North Street No 1 33 kV | Limiting Line Name | TR_LINE 181524_1 | TR_LINE 181524_1 | TR_LINE 181524_1 | TR_LINE 181524_1 | TR_LINE 181524_1
SW-Toowoomba Dalby Warwick | F3815 North Street No 1 33 kV | Loading (A) | 2.3269 | 2.3265 | 2.3256 | 2.3251 | 2.3214
SW-Toowoomba Dalby Warwick | F3815 North Street No 1 33 kV | Loading (MVA) | 0.13706 | 0.13702 | 0.13691 | 0.13686 | 0.13642
SW-Toowoomba Dalby Warwick | F3815 North Street No 1 33 kV | Loading (MW) | 0.0004376 | 0.00043745 | 0.00043712 | 0.00043694 | 0.00043553
SW-Toowoomba Dalby Warwick | F3815 North Street No 1 33 kV | Power Factor | 0.0031927 | 0.0031927 | 0.0031927 | 0.0031927 | 0.0031927
SW-Toowoomba Dalby Warwick | F3815 North Street No 1 33 kV | Rating (A) | 177 | 177 | 177 | 177 | 177
SW-Toowoomba Dalby Warwick | F3815 North Street No 1 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F3815 North Street No 1 33 kV | Min Voltage at Constrained Conductor | 34.0086 | 34.0027 | 33.9899 | 33.9827 | 33.9281
SW-Toowoomba Dalby Warwick | F3815 North Street No 1 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Toowoomba Dalby Warwick | F3820_Boundary Road 33 kV | % of Rated A | 2.121% | 2.365% | 3.339% | 6.78% | 15.78%
SW-Toowoomba Dalby Warwick | F3820_Boundary Road 33 kV | Limiting Line Name | TR_CABLE 73_1 | TR_CABLE 73_1 | TR_CABLE 73_1 | TR_CABLE 73_1 | TR_CABLE 73_1
SW-Toowoomba Dalby Warwick | F3820_Boundary Road 33 kV | Loading (A) | 14.6357 | 16.3194 | 23.0399 | 46.7799 | 108.8978
SW-Toowoomba Dalby Warwick | F3820_Boundary Road 33 kV | Loading (MVA) | 0.85973 | 0.95848 | 1.3526 | 2.7444 | 6.3989
SW-Toowoomba Dalby Warwick | F3820_Boundary Road 33 kV | Loading (MW) | 0.21644 | 0.47813 | 1.0715 | 2.6256 | 6.3657
SW-Toowoomba Dalby Warwick | F3820_Boundary Road 33 kV | Power Factor | 0.25175 | 0.49785 | 0.7915 | 0.95673 | 0.99481
SW-Toowoomba Dalby Warwick | F3820_Boundary Road 33 kV | Rating (A) | 690 | 690 | 690 | 690 | 690
SW-Toowoomba Dalby Warwick | F3820_Boundary Road 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F3820_Boundary Road 33 kV | Min Voltage at Constrained Conductor | 33.9148 | 33.9091 | 33.8934 | 33.8698 | 33.9221
SW-Toowoomba Dalby Warwick | F3820_Boundary Road 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Toowoomba Dalby Warwick | F3830_Norwin 33 kV | % of Rated A | 6.751% | 6.787% | 6.816% | 6.841% | 6.796%
SW-Toowoomba Dalby Warwick | F3830_Norwin 33 kV | Limiting Line Name | TR_LINE 23942_1 | TR_LINE 23942_1 | TR_LINE 23942_1 | TR_LINE 23942_1 | TR_LINE 23942_1
SW-Toowoomba Dalby Warwick | F3830_Norwin 33 kV | Loading (A) | 7.8317 | 7.8731 | 7.9062 | 7.9361 | 7.8832
SW-Toowoomba Dalby Warwick | F3830_Norwin 33 kV | Loading (MVA) | 0.45115 | 0.45362 | 0.45548 | 0.45722 | 0.45975
SW-Toowoomba Dalby Warwick | F3830_Norwin 33 kV | Loading (MW) | 0.40766 | 0.41037 | 0.41247 | 0.41441 | 0.41485
SW-Toowoomba Dalby Warwick | F3830_Norwin 33 kV | Power Factor | 0.90285 | 0.90393 | 0.90483 | 0.90561 | 0.90162
SW-Toowoomba Dalby Warwick | F3830_Norwin 33 kV | Rating (A) | 116 | 116 | 116 | 116 | 116
SW-Toowoomba Dalby Warwick | F3830_Norwin 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F3830_Norwin 33 kV | Min Voltage at Constrained Conductor | 33.2589 | 33.2647 | 33.2619 | 33.2628 | 33.671
SW-Toowoomba Dalby Warwick | F3830_Norwin 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Toowoomba Dalby Warwick | F3855 Omaras Road 33 kV | % of Rated A | 18.32% | 18.32% | 18.33% | 18.34% | 18.31%
SW-Toowoomba Dalby Warwick | F3855 Omaras Road 33 kV | Limiting Line Name | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1 | HV_CABLE 471924_1
SW-Toowoomba Dalby Warwick | F3855 Omaras Road 33 kV | Loading (A) | 42.6836 | 42.6907 | 42.7107 | 42.7394 | 42.6704
SW-Toowoomba Dalby Warwick | F3855 Omaras Road 33 kV | Loading (MVA) | 2.5005 | 2.5005 | 2.5005 | 2.5005 | 2.5005
SW-Toowoomba Dalby Warwick | F3855 Omaras Road 33 kV | Loading (MW) | 2.5004 | 2.5004 | 2.5004 | 2.5004 | 2.5004
SW-Toowoomba Dalby Warwick | F3855 Omaras Road 33 kV | Power Factor | 0.99997 | 0.99997 | 0.99997 | 0.99997 | 0.99997
SW-Toowoomba Dalby Warwick | F3855 Omaras Road 33 kV | Rating (A) | 233 | 233 | 233 | 233 | 233
SW-Toowoomba Dalby Warwick | F3855 Omaras Road 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F3855 Omaras Road 33 kV | Min Voltage at Constrained Conductor | 33.8214 | 33.8158 | 33.7999 | 33.7772 | 33.8319
SW-Toowoomba Dalby Warwick | F3855 Omaras Road 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Toowoomba Dalby Warwick | F3867_Pampas 33 kV | % of Rated A | 2.649% | 1.805% | 1.146% | 0.6904% | 0.6668%
SW-Toowoomba Dalby Warwick | F3867_Pampas 33 kV | Limiting Line Name | TR_CABLE 106_1 | TR_CABLE 106_1 | TR_CABLE 106_1 | TR_LINE 177041_1 | TR_LINE 177041_1
SW-Toowoomba Dalby Warwick | F3867_Pampas 33 kV | Loading (A) | 7.9467 | 5.4136 | 3.4371 | 3.6591 | 3.5342
SW-Toowoomba Dalby Warwick | F3867_Pampas 33 kV | Loading (MVA) | 0.4577 | 0.31199 | 0.19814 | 0.21081 | 0.20611
SW-Toowoomba Dalby Warwick | F3867_Pampas 33 kV | Loading (MW) | 0.44728 | 0.29614 | 0.17181 | 0.062944 | 0.030313
SW-Toowoomba Dalby Warwick | F3867_Pampas 33 kV | Power Factor | 0.97723 | 0.94921 | 0.86712 | 0.29859 | 0.14703
SW-Toowoomba Dalby Warwick | F3867_Pampas 33 kV | Rating (A) | 300 | 300 | 300 | 530 | 530
SW-Toowoomba Dalby Warwick | F3867_Pampas 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F3867_Pampas 33 kV | Min Voltage at Constrained Conductor | 33.2529 | 33.2732 | 33.2823 | 33.2624 | 33.6706
SW-Toowoomba Dalby Warwick | F3867_Pampas 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Toowoomba Dalby Warwick | F3910_Perseverence Creek 1 33 kV | % of Rated A | 9.558% | 9.558% | 9.558% | 9.558% | 9.558%
SW-Toowoomba Dalby Warwick | F3910_Perseverence Creek 1 33 kV | Limiting Line Name | TR_LINE 27829_1 | TR_LINE 27829_1 | TR_LINE 27829_1 | TR_LINE 27829_1 | TR_LINE 27829_1
SW-Toowoomba Dalby Warwick | F3910_Perseverence Creek 1 33 kV | Loading (A) | 13.66 | 13.66 | 13.66 | 13.66 | 13.66
SW-Toowoomba Dalby Warwick | F3910_Perseverence Creek 1 33 kV | Loading (MVA) | 0.80432 | 0.80432 | 0.80432 | 0.80432 | 0.80432
SW-Toowoomba Dalby Warwick | F3910_Perseverence Creek 1 33 kV | Loading (MW) | 0.80375 | 0.80375 | 0.80375 | 0.80375 | 0.80375
SW-Toowoomba Dalby Warwick | F3910_Perseverence Creek 1 33 kV | Power Factor | 0.99929 | 0.99929 | 0.99929 | 0.99929 | 0.99929
SW-Toowoomba Dalby Warwick | F3910_Perseverence Creek 1 33 kV | Rating (A) | 143 | 143 | 143 | 143 | 143
SW-Toowoomba Dalby Warwick | F3910_Perseverence Creek 1 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F3910_Perseverence Creek 1 33 kV | Min Voltage at Constrained Conductor | 34 | 34 | 34 | 34 | 34
SW-Toowoomba Dalby Warwick | F3910_Perseverence Creek 1 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Toowoomba Dalby Warwick | F3970_Pozieres 33 kV | % of Rated A | 1.563% | 1.349% | 1.228% | 1.159% | 1.132%
SW-Toowoomba Dalby Warwick | F3970_Pozieres 33 kV | Limiting Line Name | TR_LINE 23786_1 | TR_LINE 23786_1 | TR_LINE 23786_1 | TR_LINE 23786_1 | TR_LINE 23786_1
SW-Toowoomba Dalby Warwick | F3970_Pozieres 33 kV | Loading (A) | 2.5795 | 2.2258 | 2.026 | 1.9126 | 1.8672
SW-Toowoomba Dalby Warwick | F3970_Pozieres 33 kV | Loading (MVA) | 0.16878 | 0.14573 | 0.13269 | 0.1253 | 0.12238
SW-Toowoomba Dalby Warwick | F3970_Pozieres 33 kV | Loading (MW) | 0.11951 | 0.083476 | 0.057499 | 0.03707 | 0.024886
SW-Toowoomba Dalby Warwick | F3970_Pozieres 33 kV | Power Factor | 0.70808 | 0.57282 | 0.43335 | 0.29584 | 0.20335
SW-Toowoomba Dalby Warwick | F3970_Pozieres 33 kV | Rating (A) | 165 | 165 | 165 | 165 | 165
SW-Toowoomba Dalby Warwick | F3970_Pozieres 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F3970_Pozieres 33 kV | Min Voltage at Constrained Conductor | 37.7771 | 37.8011 | 37.8114 | 37.8235 | 37.842
SW-Toowoomba Dalby Warwick | F3970_Pozieres 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Toowoomba Dalby Warwick | F3980_Purrawunda 33 kV | % of Rated A | 23.25% | 23.1% | 22.99% | 22.9% | 22.89%
SW-Toowoomba Dalby Warwick | F3980_Purrawunda 33 kV | Limiting Line Name | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1 | TR_CABLE 78_1
SW-Toowoomba Dalby Warwick | F3980_Purrawunda 33 kV | Loading (A) | 49.0634 | 48.7392 | 48.5029 | 48.3214 | 48.2931
SW-Toowoomba Dalby Warwick | F3980_Purrawunda 33 kV | Loading (MVA) | 2.8821 | 2.8626 | 2.8474 | 2.8348 | 2.8377
SW-Toowoomba Dalby Warwick | F3980_Purrawunda 33 kV | Loading (MW) | 0.67306 | 0.56249 | 0.47026 | 0.38987 | 0.31809
SW-Toowoomba Dalby Warwick | F3980_Purrawunda 33 kV | Power Factor | 0.23353 | 0.1965 | 0.16515 | 0.13753 | 0.11209
SW-Toowoomba Dalby Warwick | F3980_Purrawunda 33 kV | Rating (A) | 211 | 211 | 211 | 211 | 211
SW-Toowoomba Dalby Warwick | F3980_Purrawunda 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F3980_Purrawunda 33 kV | Min Voltage at Constrained Conductor | 33.9148 | 33.9091 | 33.8934 | 33.8707 | 33.9252
SW-Toowoomba Dalby Warwick | F3980_Purrawunda 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Toowoomba Dalby Warwick | F4005_Racecourse 33 kV | % of Rated A | 2.678% | 1.741% | 0.946% | 0.2883% | 0.5729%
SW-Toowoomba Dalby Warwick | F4005_Racecourse 33 kV | Limiting Line Name | TR_CABLE 67_1 | TR_CABLE 67_1 | TR_CABLE 67_1 | TR_CABLE 67_1 | TR_CABLE 67_1
SW-Toowoomba Dalby Warwick | F4005_Racecourse 33 kV | Loading (A) | 18.9041 | 12.2895 | 6.6785 | 2.0351 | 4.0448
SW-Toowoomba Dalby Warwick | F4005_Racecourse 33 kV | Loading (MVA) | 1.1105 | 0.72179 | 0.39206 | 0.11939 | 0.23767
SW-Toowoomba Dalby Warwick | F4005_Racecourse 33 kV | Loading (MW) | 1.1071 | 0.71601 | 0.38084 | 0.074273 | 0.21991
SW-Toowoomba Dalby Warwick | F4005_Racecourse 33 kV | Power Factor | 0.99694 | 0.99199 | 0.97139 | 0.6221 | 0.92025
SW-Toowoomba Dalby Warwick | F4005_Racecourse 33 kV | Rating (A) | 706 | 706 | 706 | 706 | 706
SW-Toowoomba Dalby Warwick | F4005_Racecourse 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F4005_Racecourse 33 kV | Min Voltage at Constrained Conductor | 33.914 | 33.9087 | 33.8932 | 33.8707 | 33.9252
SW-Toowoomba Dalby Warwick | F4005_Racecourse 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Toowoomba Dalby Warwick | F4015_Ramsay Street 33 kV | % of Rated A | 2.325% | 1.143% | 0.2965% | 0.838% | 1.745%
SW-Toowoomba Dalby Warwick | F4015_Ramsay Street 33 kV | Limiting Line Name | TR_LINE 23917_1 | TR_LINE 23917_1 | TR_CABLE 86_1 | TR_LINE 23917_1 | TR_LINE 23917_1
SW-Toowoomba Dalby Warwick | F4015_Ramsay Street 33 kV | Loading (A) | 13.9475 | 6.8609 | 1.8533 | 5.0281 | 10.4687
SW-Toowoomba Dalby Warwick | F4015_Ramsay Street 33 kV | Loading (MVA) | 0.84196 | 0.41413 | 0.11183 | 0.30337 | 0.63171
SW-Toowoomba Dalby Warwick | F4015_Ramsay Street 33 kV | Loading (MW) | 0.84097 | 0.41168 | 0.043821 | 0.30018 | 0.63045
SW-Toowoomba Dalby Warwick | F4015_Ramsay Street 33 kV | Power Factor | 0.99883 | 0.99409 | 0.39185 | 0.98947 | 0.99799
SW-Toowoomba Dalby Warwick | F4015_Ramsay Street 33 kV | Rating (A) | 600 | 600 | 625 | 600 | 600
SW-Toowoomba Dalby Warwick | F4015_Ramsay Street 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F4015_Ramsay Street 33 kV | Min Voltage at Constrained Conductor | 34.8518 | 34.8492 | 34.839 | 34.8345 | 34.839
SW-Toowoomba Dalby Warwick | F4015_Ramsay Street 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Toowoomba Dalby Warwick | F4132_Shirley Road 33 kV | % of Rated A | 29.11% | 36.92% | 44.42% | 51.96% | 45.51%
SW-Toowoomba Dalby Warwick | F4132_Shirley Road 33 kV | Limiting Line Name | TR_LINE 108727_1 | TR_LINE 108727_1 | TR_LINE 108727_1 | TR_LINE 108727_1 | TR_LINE 157941_1
SW-Toowoomba Dalby Warwick | F4132_Shirley Road 33 kV | Loading (A) | 122.2469 | 155.0444 | 186.5718 | 218.2388 | 191.1281
SW-Toowoomba Dalby Warwick | F4132_Shirley Road 33 kV | Loading (MVA) | 7.2243 | 9.1702 | 11.0387 | 12.912 | 11.2387
SW-Toowoomba Dalby Warwick | F4132_Shirley Road 33 kV | Loading (MW) | 7.2239 | 9.1699 | 11.0355 | 12.9022 | 11.1809
SW-Toowoomba Dalby Warwick | F4132_Shirley Road 33 kV | Power Factor | 0.99995 | 0.99996 | 0.99971 | 0.99924 | 0.99486
SW-Toowoomba Dalby Warwick | F4132_Shirley Road 33 kV | Rating (A) | 420 | 420 | 420 | 420 | 420
SW-Toowoomba Dalby Warwick | F4132_Shirley Road 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F4132_Shirley Road 33 kV | Min Voltage at Constrained Conductor | 34.1188 | 34.1476 | 34.1594 | 34.1585 | 33.9487
SW-Toowoomba Dalby Warwick | F4132_Shirley Road 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Toowoomba Dalby Warwick | F4245_Stanthorpe 33 kV | % of Rated A | 28.43% | 28.63% | 28.79% | 28.95% | 29.08%
SW-Toowoomba Dalby Warwick | F4245_Stanthorpe 33 kV | Limiting Line Name | TR_CABLE 107_1 | TR_CABLE 107_1 | TR_CABLE 107_1 | TR_CABLE 107_1 | TR_CABLE 107_1
SW-Toowoomba Dalby Warwick | F4245_Stanthorpe 33 kV | Loading (A) | 83.0091 | 83.5927 | 84.0798 | 84.5247 | 84.914
SW-Toowoomba Dalby Warwick | F4245_Stanthorpe 33 kV | Loading (MVA) | 5.4594 | 5.5019 | 5.5359 | 5.5673 | 5.596
SW-Toowoomba Dalby Warwick | F4245_Stanthorpe 33 kV | Loading (MW) | 1.0696 | 1.2426 | 1.377 | 1.4888 | 1.5771
SW-Toowoomba Dalby Warwick | F4245_Stanthorpe 33 kV | Power Factor | 0.19584 | 0.22577 | 0.24866 | 0.26733 | 0.28174
SW-Toowoomba Dalby Warwick | F4245_Stanthorpe 33 kV | Rating (A) | 292 | 292 | 292 | 292 | 292
SW-Toowoomba Dalby Warwick | F4245_Stanthorpe 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F4245_Stanthorpe 33 kV | Min Voltage at Constrained Conductor | 37.9717 | 37.9998 | 38.0132 | 38.0279 | 38.0485
SW-Toowoomba Dalby Warwick | F4245_Stanthorpe 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Toowoomba Dalby Warwick | F4470 Vacy Street | % of Rated A | 0.4528% | 0.4527% | 0.4526% | 0.4525% | 0.4526%
SW-Toowoomba Dalby Warwick | F4470 Vacy Street | Limiting Line Name | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2 | TR_CABLE 85_2
SW-Toowoomba Dalby Warwick | F4470 Vacy Street | Loading (A) | 2.2639 | 2.2636 | 2.2629 | 2.2626 | 2.2629
SW-Toowoomba Dalby Warwick | F4470 Vacy Street | Loading (MVA) | 0.13666 | 0.13664 | 0.13655 | 0.13651 | 0.13655
SW-Toowoomba Dalby Warwick | F4470 Vacy Street | Loading (MW) | 0.0023756 | 0.0023752 | 0.0023737 | 0.0023731 | 0.0023737
SW-Toowoomba Dalby Warwick | F4470 Vacy Street | Power Factor | 0.0077606 | 0.0077605 | 0.0077605 | 0.0077605 | 0.0077605
SW-Toowoomba Dalby Warwick | F4470 Vacy Street | Rating (A) | 500 | 500 | 500 | 500 | 500
SW-Toowoomba Dalby Warwick | F4470 Vacy Street | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F4470 Vacy Street | Min Voltage at Constrained Conductor | 34.853 | 34.8497 | 34.839 | 34.8342 | 34.8385
SW-Toowoomba Dalby Warwick | F4470 Vacy Street | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Toowoomba Dalby Warwick | F4605_West Warwick 33 kV | % of Rated A | 2.415% | 3.242% | 3.918% | 4.499% | 5.014%
SW-Toowoomba Dalby Warwick | F4605_West Warwick 33 kV | Limiting Line Name | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1 | TR_LINE 24105_1
SW-Toowoomba Dalby Warwick | F4605_West Warwick 33 kV | Loading (A) | 9.3958 | 12.6126 | 15.2406 | 17.4993 | 19.5061
SW-Toowoomba Dalby Warwick | F4605_West Warwick 33 kV | Loading (MVA) | 0.57161 | 0.76754 | 0.92748 | 1.065 | 1.1876
SW-Toowoomba Dalby Warwick | F4605_West Warwick 33 kV | Loading (MW) | 0.56236 | 0.76093 | 0.92224 | 1.0607 | 1.1838
SW-Toowoomba Dalby Warwick | F4605_West Warwick 33 kV | Power Factor | 0.98381 | 0.99138 | 0.99433 | 0.99588 | 0.99682
SW-Toowoomba Dalby Warwick | F4605_West Warwick 33 kV | Rating (A) | 389 | 389 | 389 | 389 | 389
SW-Toowoomba Dalby Warwick | F4605_West Warwick 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F4605_West Warwick 33 kV | Min Voltage at Constrained Conductor | 35.1242 | 35.1346 | 35.1351 | 35.1388 | 35.1503
SW-Toowoomba Dalby Warwick | F4605_West Warwick 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Toowoomba Dalby Warwick | F4685_Wyalla Street 33 kV | % of Rated A | 2.409% | 1.558% | 0.8324% | 0.2468% | 0.5024%
SW-Toowoomba Dalby Warwick | F4685_Wyalla Street 33 kV | Limiting Line Name | TR_CABLE 71_1 | TR_CABLE 71_1 | TR_CABLE 72_1 | TR_CABLE 72_1 | TR_CABLE 72_1
SW-Toowoomba Dalby Warwick | F4685_Wyalla Street 33 kV | Loading (A) | 16.6206 | 10.7485 | 5.8766 | 1.7425 | 3.5468
SW-Toowoomba Dalby Warwick | F4685_Wyalla Street 33 kV | Loading (MVA) | 0.97598 | 0.63115 | 0.34499 | 0.10223 | 0.20841
SW-Toowoomba Dalby Warwick | F4685_Wyalla Street 33 kV | Loading (MW) | 0.97594 | 0.63101 | 0.33626 | 0.065673 | 0.19387
SW-Toowoomba Dalby Warwick | F4685_Wyalla Street 33 kV | Power Factor | 0.99992 | 0.99977 | 0.97471 | 0.64242 | 0.92575
SW-Toowoomba Dalby Warwick | F4685_Wyalla Street 33 kV | Rating (A) | 690 | 690 | 706 | 706 | 706
SW-Toowoomba Dalby Warwick | F4685_Wyalla Street 33 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F4685_Wyalla Street 33 kV | Min Voltage at Constrained Conductor | 33.9027 | 33.9017 | 33.8932 | 33.8707 | 33.9252
SW-Toowoomba Dalby Warwick | F4685_Wyalla Street 33 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Toowoomba Dalby Warwick | F5540_7244 Tangkam-Dalby 110 kV | % of Rated A | 9.192% | 8.38% | 7.731% | 7.193% | 6.736%
SW-Toowoomba Dalby Warwick | F5540_7244 Tangkam-Dalby 110 kV | Limiting Line Name | TR_LINE 24297_1 | TR_LINE 24297_1 | TR_LINE 24297_1 | TR_LINE 24297_1 | TR_LINE 24297_1
SW-Toowoomba Dalby Warwick | F5540_7244 Tangkam-Dalby 110 kV | Loading (A) | 24.2659 | 22.1225 | 20.4103 | 18.9892 | 17.7829
SW-Toowoomba Dalby Warwick | F5540_7244 Tangkam-Dalby 110 kV | Loading (MVA) | 4.8249 | 4.3983 | 4.0573 | 3.7744 | 3.5347
SW-Toowoomba Dalby Warwick | F5540_7244 Tangkam-Dalby 110 kV | Loading (MW) | 3.6881 | 3.0995 | 2.5915 | 2.1284 | 1.6787
SW-Toowoomba Dalby Warwick | F5540_7244 Tangkam-Dalby 110 kV | Power Factor | 0.76439 | 0.7047 | 0.63872 | 0.56392 | 0.47492
SW-Toowoomba Dalby Warwick | F5540_7244 Tangkam-Dalby 110 kV | Rating (A) | 264 | 264 | 264 | 264 | 264
SW-Toowoomba Dalby Warwick | F5540_7244 Tangkam-Dalby 110 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F5540_7244 Tangkam-Dalby 110 kV | Min Voltage at Constrained Conductor | 114.7876 | 114.7875 | 114.7685 | 114.7568 | 114.7589
SW-Toowoomba Dalby Warwick | F5540_7244 Tangkam-Dalby 110 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Toowoomba Dalby Warwick | F5545_7245 Tangkam-Dalby 110 kV | % of Rated A | 19.68% | 17.9% | 16.48% | 15.3% | 14.3%
SW-Toowoomba Dalby Warwick | F5545_7245 Tangkam-Dalby 110 kV | Limiting Line Name | TR_LINE 140801_1 | TR_LINE 140801_1 | TR_LINE 140801_1 | TR_LINE 140801_1 | TR_LINE 140801_1
SW-Toowoomba Dalby Warwick | F5545_7245 Tangkam-Dalby 110 kV | Loading (A) | 24.9909 | 22.7317 | 20.9269 | 19.4293 | 18.1598
SW-Toowoomba Dalby Warwick | F5545_7245 Tangkam-Dalby 110 kV | Loading (MVA) | 4.969 | 4.5195 | 4.1599 | 3.8619 | 3.6096
SW-Toowoomba Dalby Warwick | F5545_7245 Tangkam-Dalby 110 kV | Loading (MW) | 3.8853 | 3.2699 | 2.7385 | 2.2542 | 1.7836
SW-Toowoomba Dalby Warwick | F5545_7245 Tangkam-Dalby 110 kV | Power Factor | 0.7819 | 0.7235 | 0.65831 | 0.58371 | 0.49414
SW-Toowoomba Dalby Warwick | F5545_7245 Tangkam-Dalby 110 kV | Rating (A) | 127 | 127 | 127 | 127 | 127
SW-Toowoomba Dalby Warwick | F5545_7245 Tangkam-Dalby 110 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F5545_7245 Tangkam-Dalby 110 kV | Min Voltage at Constrained Conductor | 114.7881 | 114.7875 | 114.7685 | 114.7568 | 114.7589
SW-Toowoomba Dalby Warwick | F5545_7245 Tangkam-Dalby 110 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Toowoomba Dalby Warwick | F5550_733(Middle Ridge-Yarranlea) 110 kV | % of Rated A | 5.216% | 5.204% | 5.213% | 5.235% | 5.317%
SW-Toowoomba Dalby Warwick | F5550_733(Middle Ridge-Yarranlea) 110 kV | Limiting Line Name | TR_LINE 224266_1 | TR_LINE 224266_1 | TR_LINE 224266_1 | TR_LINE 224266_1 | TR_LINE 224266_1
SW-Toowoomba Dalby Warwick | F5550_733(Middle Ridge-Yarranlea) 110 kV | Loading (A) | 15.44 | 15.4048 | 15.4296 | 15.4951 | 15.7376
SW-Toowoomba Dalby Warwick | F5550_733(Middle Ridge-Yarranlea) 110 kV | Loading (MVA) | 3.0847 | 3.0771 | 3.0809 | 3.0932 | 3.1417
SW-Toowoomba Dalby Warwick | F5550_733(Middle Ridge-Yarranlea) 110 kV | Loading (MW) | 0.26969 | 0.04323 | 0.14314 | 0.30623 | 0.44853
SW-Toowoomba Dalby Warwick | F5550_733(Middle Ridge-Yarranlea) 110 kV | Power Factor | 0.087426 | 0.014049 | 0.04645 | 0.098991 | 0.14276
SW-Toowoomba Dalby Warwick | F5550_733(Middle Ridge-Yarranlea) 110 kV | Rating (A) | 296 | 296 | 296 | 296 | 296
SW-Toowoomba Dalby Warwick | F5550_733(Middle Ridge-Yarranlea) 110 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F5550_733(Middle Ridge-Yarranlea) 110 kV | Min Voltage at Constrained Conductor | 115.3487 | 115.3254 | 115.2809 | 115.2536 | 115.2576
SW-Toowoomba Dalby Warwick | F5550_733(Middle Ridge-Yarranlea) 110 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Toowoomba Dalby Warwick | F5555_734(Middle Ridge-Yarranlea) 110 kV | % of Rated A | 5.393% | 5.38% | 5.388% | 5.411% | 5.495%
SW-Toowoomba Dalby Warwick | F5555_734(Middle Ridge-Yarranlea) 110 kV | Limiting Line Name | TR_LINE 225682_1 | TR_LINE 225682_1 | TR_LINE 225682_1 | TR_LINE 225682_1 | TR_LINE 225682_1
SW-Toowoomba Dalby Warwick | F5555_734(Middle Ridge-Yarranlea) 110 kV | Loading (A) | 15.4765 | 15.4407 | 15.4647 | 15.5293 | 15.7707
SW-Toowoomba Dalby Warwick | F5555_734(Middle Ridge-Yarranlea) 110 kV | Loading (MVA) | 3.0921 | 3.0843 | 3.0879 | 3.1 | 3.1483
SW-Toowoomba Dalby Warwick | F5555_734(Middle Ridge-Yarranlea) 110 kV | Loading (MW) | 0.2637 | 0.037467 | 0.15531 | 0.31834 | 0.4609
SW-Toowoomba Dalby Warwick | F5555_734(Middle Ridge-Yarranlea) 110 kV | Power Factor | 0.085282 | 0.012148 | 0.048148 | 0.10051 | 0.14415
SW-Toowoomba Dalby Warwick | F5555_734(Middle Ridge-Yarranlea) 110 kV | Rating (A) | 287 | 287 | 287 | 287 | 287
SW-Toowoomba Dalby Warwick | F5555_734(Middle Ridge-Yarranlea) 110 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F5555_734(Middle Ridge-Yarranlea) 110 kV | Min Voltage at Constrained Conductor | 115.3487 | 115.3254 | 115.2809 | 115.2536 | 115.2576
SW-Toowoomba Dalby Warwick | F5555_734(Middle Ridge-Yarranlea) 110 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Toowoomba Dalby Warwick | F5560_735(Middle Ridge-Warwick) 110 kV | % of Rated A | 21.26% | 21.35% | 21.44% | 21.54% | 21.65%
SW-Toowoomba Dalby Warwick | F5560_735(Middle Ridge-Warwick) 110 kV | Limiting Line Name | TR_LINE 94897_1 | TR_LINE 94897_1 | TR_LINE 94897_1 | TR_LINE 94897_1 | TR_LINE 94897_1
SW-Toowoomba Dalby Warwick | F5560_735(Middle Ridge-Warwick) 110 kV | Loading (A) | 54.6484 | 54.8761 | 55.1114 | 55.366 | 55.6336
SW-Toowoomba Dalby Warwick | F5560_735(Middle Ridge-Warwick) 110 kV | Loading (MVA) | 10.9208 | 10.9641 | 11.0069 | 11.0551 | 11.1089
SW-Toowoomba Dalby Warwick | F5560_735(Middle Ridge-Warwick) 110 kV | Loading (MW) | 2.8254 | 3.2864 | 3.6603 | 3.9853 | 4.2696
SW-Toowoomba Dalby Warwick | F5560_735(Middle Ridge-Warwick) 110 kV | Power Factor | 0.25801 | 0.29903 | 0.33183 | 0.35977 | 0.38362
SW-Toowoomba Dalby Warwick | F5560_735(Middle Ridge-Warwick) 110 kV | Rating (A) | 257 | 257 | 257 | 257 | 257
SW-Toowoomba Dalby Warwick | F5560_735(Middle Ridge-Warwick) 110 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F5560_735(Middle Ridge-Warwick) 110 kV | Min Voltage at Constrained Conductor | 115.3763 | 115.353 | 115.3086 | 115.2813 | 115.2853
SW-Toowoomba Dalby Warwick | F5560_735(Middle Ridge-Warwick) 110 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
SW-Toowoomba Dalby Warwick | F5565_736(Middle Ridge-Warwick) 110 kV | % of Rated A | 8.588% | 8.638% | 8.685% | 8.735% | 8.784%
SW-Toowoomba Dalby Warwick | F5565_736(Middle Ridge-Warwick) 110 kV | Limiting Line Name | TR_LINE 141746_1 | TR_LINE 141746_1 | TR_LINE 141746_1 | TR_LINE 141746_1 | TR_LINE 141746_1
SW-Toowoomba Dalby Warwick | F5565_736(Middle Ridge-Warwick) 110 kV | Loading (A) | 67.4155 | 67.8052 | 68.1809 | 68.5666 | 68.957
SW-Toowoomba Dalby Warwick | F5565_736(Middle Ridge-Warwick) 110 kV | Loading (MVA) | 13.4689 | 13.5441 | 13.6139 | 13.6876 | 13.766
SW-Toowoomba Dalby Warwick | F5565_736(Middle Ridge-Warwick) 110 kV | Loading (MW) | 0.54633 | 0.017924 | 0.47811 | 0.87807 | 1.2266
SW-Toowoomba Dalby Warwick | F5565_736(Middle Ridge-Warwick) 110 kV | Power Factor | 0.040562 | 0.0013145 | 0.03511 | 0.064142 | 0.089097
SW-Toowoomba Dalby Warwick | F5565_736(Middle Ridge-Warwick) 110 kV | Rating (A) | 785 | 785 | 785 | 785 | 785
SW-Toowoomba Dalby Warwick | F5565_736(Middle Ridge-Warwick) 110 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
SW-Toowoomba Dalby Warwick | F5565_736(Middle Ridge-Warwick) 110 kV | Min Voltage at Constrained Conductor | 115.3487 | 115.3254 | 115.2809 | 115.2536 | 115.2576
SW-Toowoomba Dalby Warwick | F5565_736(Middle Ridge-Warwick) 110 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
WB-Korenan | 6112_Agnes Water 66 kV | % of Rated A | 3.472% | 5.344% | 7.268% | 9.253% | 11.42%
WB-Korenan | 6112_Agnes Water 66 kV | Limiting Line Name | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1 | TR_LINE 85842_1
WB-Korenan | 6112_Agnes Water 66 kV | Loading (A) | 9.8596 | 15.1767 | 20.64 | 26.2796 | 32.4194
WB-Korenan | 6112_Agnes Water 66 kV | Loading (MVA) | 1.1459 | 1.7665 | 2.4143 | 3.0748 | 3.794
WB-Korenan | 6112_Agnes Water 66 kV | Loading (MW) | 0.88122 | 1.6134 | 2.3094 | 3.0001 | 3.7411
WB-Korenan | 6112_Agnes Water 66 kV | Power Factor | 0.76901 | 0.91331 | 0.95652 | 0.9757 | 0.98603
WB-Korenan | 6112_Agnes Water 66 kV | Rating (A) | 284 | 284 | 284 | 284 | 284
WB-Korenan | 6112_Agnes Water 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Korenan | 6112_Agnes Water 66 kV | Min Voltage at Constrained Conductor | 67.1014 | 67.2006 | 67.5342 | 67.5511 | 67.5666
WB-Korenan | 6112_Agnes Water 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
WB-Korenan | 7188_Gin Gin - Korenan QR 132 kV | % of Rated A | 4.512% | 4.411% | 4.458% | 4.602% | 4.875%
WB-Korenan | 7188_Gin Gin - Korenan QR 132 kV | Limiting Line Name | TR_LINE 88330_1 | TR_LINE 88330_1 | TR_LINE 88330_1 | TR_LINE 88330_1 | TR_LINE 88330_1
WB-Korenan | 7188_Gin Gin - Korenan QR 132 kV | Loading (A) | 17.0561 | 16.6729 | 16.8518 | 17.3963 | 18.4264
WB-Korenan | 7188_Gin Gin - Korenan QR 132 kV | Loading (MVA) | 4.092 | 4.0039 | 4.0653 | 4.1961 | 4.444
WB-Korenan | 7188_Gin Gin - Korenan QR 132 kV | Loading (MW) | 0.7965 | 0.046925 | 0.66665 | 1.3694 | 2.1213
WB-Korenan | 7188_Gin Gin - Korenan QR 132 kV | Power Factor | 0.19465 | 0.01172 | 0.16306 | 0.32528 | 0.47602
WB-Korenan | 7188_Gin Gin - Korenan QR 132 kV | Rating (A) | 378 | 378 | 378 | 378 | 378
WB-Korenan | 7188_Gin Gin - Korenan QR 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Korenan | 7188_Gin Gin - Korenan QR 132 kV | Min Voltage at Constrained Conductor | 138.513 | 138.6483 | 139.2773 | 139.2596 | 139.2423
WB-Korenan | 7188_Gin Gin - Korenan QR 132 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
WB-Wide Bay | 6205_East Bundaberg-BUCE 66 kV | % of Rated A | 13.57% | 16.51% | 19.35% | 21.82% | 24.22%
WB-Wide Bay | 6205_East Bundaberg-BUCE 66 kV | Limiting Line Name | TR_LINE 176527_1 | TR_LINE 176527_1 | TR_LINE 176527_1 | TR_LINE 176527_1 | TR_LINE 176527_1
WB-Wide Bay | 6205_East Bundaberg-BUCE 66 kV | Loading (A) | 53.8647 | 65.5461 | 76.8116 | 86.6283 | 96.1667
WB-Wide Bay | 6205_East Bundaberg-BUCE 66 kV | Loading (MVA) | 6.2604 | 7.6412 | 8.8603 | 9.9991 | 11.1083
WB-Wide Bay | 6205_East Bundaberg-BUCE 66 kV | Loading (MW) | 5.5257 | 7.0277 | 8.3416 | 9.5308 | 10.6816
WB-Wide Bay | 6205_East Bundaberg-BUCE 66 kV | Power Factor | 0.88259 | 0.91965 | 0.94142 | 0.95315 | 0.96157
WB-Wide Bay | 6205_East Bundaberg-BUCE 66 kV | Rating (A) | 397 | 397 | 397 | 397 | 397
WB-Wide Bay | 6205_East Bundaberg-BUCE 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | 6205_East Bundaberg-BUCE 66 kV | Min Voltage at Constrained Conductor | 67.1019 | 67.3054 | 66.5947 | 66.6358 | 66.6841
WB-Wide Bay | 6205_East Bundaberg-BUCE 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
WB-Wide Bay | 6302_Bundaberg Central - WEBU 66 kV | % of Rated A | 27.77% | 28.87% | 30.03% | 31.63% | 33.39%
WB-Wide Bay | 6302_Bundaberg Central - WEBU 66 kV | Limiting Line Name | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1 | TR_LINE 136641_1
WB-Wide Bay | 6302_Bundaberg Central - WEBU 66 kV | Loading (A) | 110.2606 | 114.6048 | 119.2223 | 125.5676 | 132.5556
WB-Wide Bay | 6302_Bundaberg Central - WEBU 66 kV | Loading (MVA) | 12.7761 | 13.322 | 13.7156 | 14.4576 | 15.2765
WB-Wide Bay | 6302_Bundaberg Central - WEBU 66 kV | Loading (MW) | 1.7493 | 3.7447 | 5.4791 | 7.0377 | 8.5295
WB-Wide Bay | 6302_Bundaberg Central - WEBU 66 kV | Power Factor | 0.1348 | 0.27916 | 0.39782 | 0.48541 | 0.55728
WB-Wide Bay | 6302_Bundaberg Central - WEBU 66 kV | Rating (A) | 397 | 397 | 397 | 397 | 397
WB-Wide Bay | 6302_Bundaberg Central - WEBU 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | 6302_Bundaberg Central - WEBU 66 kV | Min Voltage at Constrained Conductor | 66.8471 | 67.0249 | 66.2938 | 66.315 | 66.3445
WB-Wide Bay | 6302_Bundaberg Central - WEBU 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
WB-Wide Bay | 6366_Gootchie 66 kV | % of Rated A | 22.43% | 66.83% | 72.85% | 78.4% | 84.83%
WB-Wide Bay | 6366_Gootchie 66 kV | Limiting Line Name | TR_LINE 7245_1 | TR_LINE 139374_1 | TR_LINE 139374_1 | TR_LINE 139374_1 | TR_LINE 139374_1
WB-Wide Bay | 6366_Gootchie 66 kV | Loading (A) | 29.6086 | 88.2105 | 96.1561 | 103.4902 | 111.9721
WB-Wide Bay | 6366_Gootchie 66 kV | Loading (MVA) | 3.5204 | 10.5338 | 11.4985 | 12.3825 | 13.4147
WB-Wide Bay | 6366_Gootchie 66 kV | Loading (MW) | 3.4556 | 7.672 | 8.6095 | 9.4091 | 10.4076
WB-Wide Bay | 6366_Gootchie 66 kV | Power Factor | 0.97027 | 0.72818 | 0.74857 | 0.75966 | 0.77558
WB-Wide Bay | 6366_Gootchie 66 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
WB-Wide Bay | 6366_Gootchie 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | 6366_Gootchie 66 kV | Min Voltage at Constrained Conductor | 68.6454 | 68.9428 | 69.0367 | 69.0745 | 69.1628
WB-Wide Bay | 6366_Gootchie 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
WB-Wide Bay | 7187_Gin Gin - Bundaberg 132 kV | % of Rated A | 18.95% | 18.24% | 54.16% | 54.32% | 54.57%
WB-Wide Bay | 7187_Gin Gin - Bundaberg 132 kV | Limiting Line Name | TR_LINE 6941_1 | TR_LINE 6941_1 | TR_LINE 6941_d | TR_LINE 6941_d | TR_LINE 6941_d
WB-Wide Bay | 7187_Gin Gin - Bundaberg 132 kV | Loading (A) | 128.6652 | 123.8563 | 394.8383 | 395.9855 | 397.796
WB-Wide Bay | 7187_Gin Gin - Bundaberg 132 kV | Loading (MVA) | 30.8683 | 29.7436 | 92.9975 | 93.2678 | 93.6944
WB-Wide Bay | 7187_Gin Gin - Bundaberg 132 kV | Loading (MW) | 21.4109 | 18.8827 | 9.999 | 9.999 | 9.999
WB-Wide Bay | 7187_Gin Gin - Bundaberg 132 kV | Power Factor | 0.69362 | 0.63485 | 0.10746 | 0.10714 | 0.10666
WB-Wide Bay | 7187_Gin Gin - Bundaberg 132 kV | Rating (A) | 679 | 679 | 729 | 729 | 729
WB-Wide Bay | 7187_Gin Gin - Bundaberg 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | 7187_Gin Gin - Bundaberg 132 kV | Min Voltage at Constrained Conductor | 138.513 | 138.6483 | 135.96 | 135.96 | 135.96
WB-Wide Bay | 7187_Gin Gin - Bundaberg 132 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
WB-Wide Bay | 7190_Woolooga-Mungar 132 kV | % of Rated A | 3.006% | 3.006% | 3.006% | 3.006% | 3.006%
WB-Wide Bay | 7190_Woolooga-Mungar 132 kV | Limiting Line Name | TR_LINE 223602_1 | TR_LINE 223602_1 | TR_LINE 223602_1 | TR_LINE 223602_1 | TR_LINE 223602_1
WB-Wide Bay | 7190_Woolooga-Mungar 132 kV | Loading (A) | 7.4858 | 7.4858 | 7.4858 | 7.4858 | 7.4858
WB-Wide Bay | 7190_Woolooga-Mungar 132 kV | Loading (MVA) | 1.8 | 1.8 | 1.8 | 1.8 | 1.8
WB-Wide Bay | 7190_Woolooga-Mungar 132 kV | Loading (MW) | 1.8 | 1.8 | 1.8 | 1.8 | 1.8
WB-Wide Bay | 7190_Woolooga-Mungar 132 kV | Power Factor | 1 | 1 | 1 | 1 | 1
WB-Wide Bay | 7190_Woolooga-Mungar 132 kV | Rating (A) | 249 | 249 | 249 | 249 | 249
WB-Wide Bay | 7190_Woolooga-Mungar 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | 7190_Woolooga-Mungar 132 kV | Min Voltage at Constrained Conductor | 138.8284 | 138.8284 | 138.8284 | 138.8284 | 138.8284
WB-Wide Bay | 7190_Woolooga-Mungar 132 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
WB-Wide Bay | 7204_Bundaberg - Clayton 132 kV | % of Rated A | 1.135% | 1.133% | 1.144% | 1.144% | 1.144%
WB-Wide Bay | 7204_Bundaberg - Clayton 132 kV | Limiting Line Name | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1 | TR_LINE 9229_1
WB-Wide Bay | 7204_Bundaberg - Clayton 132 kV | Loading (A) | 10.0561 | 10.0342 | 10.1369 | 10.1346 | 10.1314
WB-Wide Bay | 7204_Bundaberg - Clayton 132 kV | Loading (MVA) | 2.4542 | 2.4547 | 2.4523 | 2.4524 | 2.4524
WB-Wide Bay | 7204_Bundaberg - Clayton 132 kV | Loading (MW) | 2.4002 | 2.4002 | 2.4002 | 2.4002 | 2.4002
WB-Wide Bay | 7204_Bundaberg - Clayton 132 kV | Power Factor | 0.97793 | 0.97773 | 0.97867 | 0.97865 | 0.97862
WB-Wide Bay | 7204_Bundaberg - Clayton 132 kV | Rating (A) | 886 | 886 | 886 | 886 | 886
WB-Wide Bay | 7204_Bundaberg - Clayton 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | 7204_Bundaberg - Clayton 132 kV | Min Voltage at Constrained Conductor | 140.9002 | 141.2371 | 139.6724 | 139.7069 | 139.7548
WB-Wide Bay | 7204_Bundaberg - Clayton 132 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
WB-Wide Bay | 7215_Bundaberg - ISIS No 1 132 kV | % of Rated A | 43.36% | 45.46% | 52.98% | 52.16% | 51.27%
WB-Wide Bay | 7215_Bundaberg - ISIS No 1 132 kV | Limiting Line Name | TR_LINE 6780_2 | TR_LINE 6780_2 | TR_LINE 6780_2 | TR_LINE 6780_2 | TR_LINE 6780_2
WB-Wide Bay | 7215_Bundaberg - ISIS No 1 132 kV | Loading (A) | 107.5353 | 112.729 | 131.3814 | 129.3446 | 127.1563
WB-Wide Bay | 7215_Bundaberg - ISIS No 1 132 kV | Loading (MVA) | 26.2471 | 27.5806 | 31.7885 | 31.3035 | 30.7844
WB-Wide Bay | 7215_Bundaberg - ISIS No 1 132 kV | Loading (MW) | 25.8358 | 27.0487 | 28.5741 | 28.1647 | 27.666
WB-Wide Bay | 7215_Bundaberg - ISIS No 1 132 kV | Power Factor | 0.98433 | 0.98071 | 0.89888 | 0.89973 | 0.8987
WB-Wide Bay | 7215_Bundaberg - ISIS No 1 132 kV | Rating (A) | 248 | 248 | 248 | 248 | 248
WB-Wide Bay | 7215_Bundaberg - ISIS No 1 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | 7215_Bundaberg - ISIS No 1 132 kV | Min Voltage at Constrained Conductor | 140.3731 | 140.7544 | 139.6935 | 139.728 | 139.7758
WB-Wide Bay | 7215_Bundaberg - ISIS No 1 132 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
WB-Wide Bay | 7315_Aramara 132 kV | % of Rated A | 13.41% | 14.35% | 14.97% | 16.85% | 18.85%
WB-Wide Bay | 7315_Aramara 132 kV | Limiting Line Name | TR_LINE 88000_1 | TR_LINE 88000_1 | TR_LINE 88000_1 | TR_LINE 88000_1 | TR_LINE 88000_1
WB-Wide Bay | 7315_Aramara 132 kV | Loading (A) | 146.3835 | 156.7101 | 163.5262 | 183.996 | 205.8188
WB-Wide Bay | 7315_Aramara 132 kV | Loading (MVA) | 35.013 | 37.5519 | 39.4032 | 44.3241 | 49.5782
WB-Wide Bay | 7315_Aramara 132 kV | Loading (MW) | 31.297 | 33.157 | 38.5286 | 43.6578 | 49.033
WB-Wide Bay | 7315_Aramara 132 kV | Power Factor | 0.89385 | 0.88294 | 0.97778 | 0.98495 | 0.98899
WB-Wide Bay | 7315_Aramara 132 kV | Rating (A) | 1092 | 1092 | 1092 | 1092 | 1092
WB-Wide Bay | 7315_Aramara 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | 7315_Aramara 132 kV | Min Voltage at Constrained Conductor | 138.0944 | 138.3486 | 139.1182 | 139.0815 | 139.0716
WB-Wide Bay | 7315_Aramara 132 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
WB-Wide Bay | 7316_Aramara 132 kV | % of Rated A | 13.4% | 14.35% | 14.97% | 16.85% | 18.85%
WB-Wide Bay | 7316_Aramara 132 kV | Limiting Line Name | TR_LINE 88004_1 | TR_LINE 88004_1 | TR_LINE 88004_1 | TR_LINE 88004_1 | TR_LINE 88004_1
WB-Wide Bay | 7316_Aramara 132 kV | Loading (A) | 146.3633 | 156.6885 | 163.5034 | 183.9702 | 205.79
WB-Wide Bay | 7316_Aramara 132 kV | Loading (MVA) | 35.0081 | 37.5468 | 39.3977 | 44.3179 | 49.5713
WB-Wide Bay | 7316_Aramara 132 kV | Loading (MW) | 31.2926 | 33.1523 | 38.5232 | 43.6516 | 49.026
WB-Wide Bay | 7316_Aramara 132 kV | Power Factor | 0.89385 | 0.88294 | 0.97778 | 0.98495 | 0.98899
WB-Wide Bay | 7316_Aramara 132 kV | Rating (A) | 1092 | 1092 | 1092 | 1092 | 1092
WB-Wide Bay | 7316_Aramara 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | 7316_Aramara 132 kV | Min Voltage at Constrained Conductor | 138.0944 | 138.3486 | 139.1182 | 139.0815 | 139.0716
WB-Wide Bay | 7316_Aramara 132 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
WB-Wide Bay | 7328_Bundaberg - ISIS No 2 132 kV | % of Rated A | 43.27% | 45.36% | 52.87% | 52.05% | 51.17%
WB-Wide Bay | 7328_Bundaberg - ISIS No 2 132 kV | Limiting Line Name | TR_LINE 98484_1 | TR_LINE 98484_1 | TR_LINE 98484_1 | TR_LINE 98484_1 | TR_LINE 98484_1
WB-Wide Bay | 7328_Bundaberg - ISIS No 2 132 kV | Loading (A) | 107.3057 | 112.489 | 131.1126 | 129.0801 | 126.8966
WB-Wide Bay | 7328_Bundaberg - ISIS No 2 132 kV | Loading (MVA) | 26.1913 | 27.5221 | 31.7233 | 31.2392 | 30.7213
WB-Wide Bay | 7328_Bundaberg - ISIS No 2 132 kV | Loading (MW) | 25.7811 | 26.9917 | 28.5178 | 28.1092 | 27.6115
WB-Wide Bay | 7328_Bundaberg - ISIS No 2 132 kV | Power Factor | 0.98434 | 0.98073 | 0.89896 | 0.8998 | 0.89877
WB-Wide Bay | 7328_Bundaberg - ISIS No 2 132 kV | Rating (A) | 248 | 248 | 248 | 248 | 248
WB-Wide Bay | 7328_Bundaberg - ISIS No 2 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | 7328_Bundaberg - ISIS No 2 132 kV | Min Voltage at Constrained Conductor | 140.8956 | 141.2347 | 139.6924 | 139.727 | 139.7748
WB-Wide Bay | 7328_Bundaberg - ISIS No 2 132 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
WB-Wide Bay | 7329_Maryborough 132 kV | % of Rated A | 10.36% | 12.17% | 13.55% | 15.55% | 18.31%
WB-Wide Bay | 7329_Maryborough 132 kV | Limiting Line Name | TR_LINE 120325_1 | TR_LINE 120325_1 | TR_LINE 120325_1 | TR_LINE 120325_1 | TR_LINE 120325_1
WB-Wide Bay | 7329_Maryborough 132 kV | Loading (A) | 58.4497 | 68.6225 | 76.4223 | 87.7242 | 103.2432
WB-Wide Bay | 7329_Maryborough 132 kV | Loading (MVA) | 14.1199 | 16.6267 | 18.5396 | 21.2777 | 25.0467
WB-Wide Bay | 7329_Maryborough 132 kV | Loading (MW) | 7.9494 | 8.3914 | 12.2637 | 16.5919 | 21.2708
WB-Wide Bay | 7329_Maryborough 132 kV | Power Factor | 0.5625 | 0.50412 | 0.66085 | 0.77905 | 0.84838
WB-Wide Bay | 7329_Maryborough 132 kV | Rating (A) | 564 | 564 | 564 | 564 | 564
WB-Wide Bay | 7329_Maryborough 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | 7329_Maryborough 132 kV | Min Voltage at Constrained Conductor | 139.4724 | 139.887 | 140.0616 | 140.0374 | 140.0644
WB-Wide Bay | 7329_Maryborough 132 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
WB-Wide Bay | 7330_Maryborough 132 kV | % of Rated A | 10.36% | 12.16% | 13.54% | 15.55% | 18.3%
WB-Wide Bay | 7330_Maryborough 132 kV | Limiting Line Name | TR_LINE 7684_1 | TR_LINE 7684_1 | TR_LINE 7684_1 | TR_LINE 7684_1 | TR_LINE 7684_1
WB-Wide Bay | 7330_Maryborough 132 kV | Loading (A) | 58.4216 | 68.5898 | 76.3863 | 87.6834 | 103.1956
WB-Wide Bay | 7330_Maryborough 132 kV | Loading (MVA) | 14.1132 | 16.6189 | 18.531 | 21.268 | 25.0354
WB-Wide Bay | 7330_Maryborough 132 kV | Loading (MW) | 7.9449 | 8.3865 | 12.2571 | 16.5835 | 21.2603
WB-Wide Bay | 7330_Maryborough 132 kV | Power Factor | 0.56246 | 0.50407 | 0.6608 | 0.77901 | 0.84835
WB-Wide Bay | 7330_Maryborough 132 kV | Rating (A) | 564 | 564 | 564 | 564 | 564
WB-Wide Bay | 7330_Maryborough 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | 7330_Maryborough 132 kV | Min Voltage at Constrained Conductor | 139.4734 | 139.8882 | 140.0628 | 140.0386 | 140.0657
WB-Wide Bay | 7330_Maryborough 132 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
WB-Wide Bay | 764_Woolooga-Kilkivan No 1 132 kV | % of Rated A | 3.629% | 9.638% | 11.19% | 12.59% | 14.11%
WB-Wide Bay | 764_Woolooga-Kilkivan No 1 132 kV | Limiting Line Name | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1 | TR_LINE 7644_1
WB-Wide Bay | 764_Woolooga-Kilkivan No 1 132 kV | Loading (A) | 8.9992 | 23.9016 | 27.7503 | 31.2181 | 34.9953
WB-Wide Bay | 764_Woolooga-Kilkivan No 1 132 kV | Loading (MVA) | 2.1604 | 5.7369 | 6.6606 | 7.4927 | 8.399
WB-Wide Bay | 764_Woolooga-Kilkivan No 1 132 kV | Loading (MW) | 0.12103 | 5.0575 | 5.9332 | 6.6963 | 7.532
WB-Wide Bay | 764_Woolooga-Kilkivan No 1 132 kV | Power Factor | 0.055849 | 0.88157 | 0.89079 | 0.89371 | 0.89677
WB-Wide Bay | 764_Woolooga-Kilkivan No 1 132 kV | Rating (A) | 248 | 248 | 248 | 248 | 248
WB-Wide Bay | 764_Woolooga-Kilkivan No 1 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | 764_Woolooga-Kilkivan No 1 132 kV | Min Voltage at Constrained Conductor | 138.6 | 138.576 | 138.5748 | 138.5703 | 138.5661
WB-Wide Bay | 764_Woolooga-Kilkivan No 1 132 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
WB-Wide Bay | 765_Woolooga-Kilkivan No 2 132 kV | % of Rated A | 3.629% | 9.638% | 11.19% | 12.59% | 14.11%
WB-Wide Bay | 765_Woolooga-Kilkivan No 2 132 kV | Limiting Line Name | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1 | TR_LINE 6808_1
WB-Wide Bay | 765_Woolooga-Kilkivan No 2 132 kV | Loading (A) | 8.9989 | 23.9015 | 27.7502 | 31.218 | 34.9951
WB-Wide Bay | 765_Woolooga-Kilkivan No 2 132 kV | Loading (MVA) | 2.1603 | 5.7369 | 6.6606 | 7.4927 | 8.3989
WB-Wide Bay | 765_Woolooga-Kilkivan No 2 132 kV | Loading (MW) | 0.12102 | 5.0574 | 5.9331 | 6.6962 | 7.5319
WB-Wide Bay | 765_Woolooga-Kilkivan No 2 132 kV | Power Factor | 0.055847 | 0.88157 | 0.89079 | 0.89371 | 0.89677
WB-Wide Bay | 765_Woolooga-Kilkivan No 2 132 kV | Rating (A) | 248 | 248 | 248 | 248 | 248
WB-Wide Bay | 765_Woolooga-Kilkivan No 2 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | 765_Woolooga-Kilkivan No 2 132 kV | Min Voltage at Constrained Conductor | 138.6 | 138.576 | 138.5748 | 138.5703 | 138.5661
WB-Wide Bay | 765_Woolooga-Kilkivan No 2 132 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
WB-Wide Bay | 784_ISIS 132 kV | % of Rated A | 39.15% | 41.27% | 45.62% | 46.86% | 48.01%
WB-Wide Bay | 784_ISIS 132 kV | Limiting Line Name | TR_LINE 118475_1 | TR_LINE 118475_1 | TR_LINE 6779_1 | TR_LINE 6779_1 | TR_LINE 6779_1
WB-Wide Bay | 784_ISIS 132 kV | Loading (A) | 97.0866 | 102.349 | 113.1484 | 116.2036 | 119.0651
WB-Wide Bay | 784_ISIS 132 kV | Loading (MVA) | 23.4475 | 24.7897 | 27.4657 | 28.2106 | 28.9147
WB-Wide Bay | 784_ISIS 132 kV | Loading (MW) | 23.2654 | 24.6874 | 26.3402 | 27.1749 | 27.9128
WB-Wide Bay | 784_ISIS 132 kV | Power Factor | 0.99221 | 0.99585 | 0.95902 | 0.96329 | 0.96535
WB-Wide Bay | 784_ISIS 132 kV | Rating (A) | 248 | 248 | 248 | 248 | 248
WB-Wide Bay | 784_ISIS 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | 784_ISIS 132 kV | Min Voltage at Constrained Conductor | 139.4366 | 139.8384 | 140.1307 | 140.141 | 140.1838
WB-Wide Bay | 784_ISIS 132 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
WB-Wide Bay | 785_ISIS 132 kV | % of Rated A | 39.45% | 41.69% | 46.28% | 47.53% | 48.71%
WB-Wide Bay | 785_ISIS 132 kV | Limiting Line Name | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1 | TR_LINE 6792_1
WB-Wide Bay | 785_ISIS 132 kV | Loading (A) | 97.8322 | 103.3904 | 114.7854 | 117.8861 | 120.7898
WB-Wide Bay | 785_ISIS 132 kV | Loading (MVA) | 23.7768 | 25.1969 | 27.863 | 28.619 | 29.3336
WB-Wide Bay | 785_ISIS 132 kV | Loading (MW) | 23.7213 | 25.1779 | 26.7307 | 27.5775 | 28.3263
WB-Wide Bay | 785_ISIS 132 kV | Power Factor | 0.99765 | 0.99923 | 0.95936 | 0.96361 | 0.96566
WB-Wide Bay | 785_ISIS 132 kV | Rating (A) | 248 | 248 | 248 | 248 | 248
WB-Wide Bay | 785_ISIS 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | 785_ISIS 132 kV | Min Voltage at Constrained Conductor | 140.3162 | 140.7015 | 140.1452 | 140.1615 | 140.2077
WB-Wide Bay | 785_ISIS 132 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
WB-Wide Bay | 786_Gin Gin - Bundaberg 132 kV | % of Rated A | 45.52% | 43.82% | 24.63% | 19.76% | 15.09%
WB-Wide Bay | 786_Gin Gin - Bundaberg 132 kV | Limiting Line Name | TR_LINE 112963_1 | TR_LINE 112963_1 | TR_LINE 112963_1 | TR_LINE 112963_1 | TR_LINE 112963_1
WB-Wide Bay | 786_Gin Gin - Bundaberg 132 kV | Loading (A) | 128.8106 | 123.9968 | 69.7105 | 55.9195 | 42.6912
WB-Wide Bay | 786_Gin Gin - Bundaberg 132 kV | Loading (MVA) | 30.9032 | 29.7773 | 16.8166 | 13.488 | 10.296
WB-Wide Bay | 786_Gin Gin - Bundaberg 132 kV | Loading (MW) | 21.403 | 18.8712 | 14.8234 | 11.2619 | 7.5985
WB-Wide Bay | 786_Gin Gin - Bundaberg 132 kV | Power Factor | 0.69258 | 0.63374 | 0.88147 | 0.83495 | 0.73801
WB-Wide Bay | 786_Gin Gin - Bundaberg 132 kV | Rating (A) | 283 | 283 | 283 | 283 | 283
WB-Wide Bay | 786_Gin Gin - Bundaberg 132 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | 786_Gin Gin - Bundaberg 132 kV | Min Voltage at Constrained Conductor | 138.513 | 138.6483 | 139.2773 | 139.2596 | 139.2423
WB-Wide Bay | 786_Gin Gin - Bundaberg 132 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
WB-Wide Bay | M001_Tarong-Kingaroy East 66 kV | % of Rated A | 2.469% | 1.966% | 2.001% | 2.382% | 2.929%
WB-Wide Bay | M001_Tarong-Kingaroy East 66 kV | Limiting Line Name | TR_LINE 7977_1 | TR_LINE 7977_1 | TR_LINE 7977_1 | TR_LINE 7977_1 | TR_LINE 7977_1
WB-Wide Bay | M001_Tarong-Kingaroy East 66 kV | Loading (A) | 13.5291 | 10.7756 | 10.9662 | 13.0509 | 16.0503
WB-Wide Bay | M001_Tarong-Kingaroy East 66 kV | Loading (MVA) | 1.6395 | 1.3059 | 1.3293 | 1.5821 | 1.9459
WB-Wide Bay | M001_Tarong-Kingaroy East 66 kV | Loading (MW) | 1.0233 | 0.26031 | 0.38175 | 0.95308 | 1.4921
WB-Wide Bay | M001_Tarong-Kingaroy East 66 kV | Power Factor | 0.62418 | 0.19933 | 0.28701 | 0.6022 | 0.76655
WB-Wide Bay | M001_Tarong-Kingaroy East 66 kV | Rating (A) | 548 | 548 | 548 | 548 | 548
WB-Wide Bay | M001_Tarong-Kingaroy East 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M001_Tarong-Kingaroy East 66 kV | Min Voltage at Constrained Conductor | 69.9635 | 69.9713 | 69.986 | 69.9914 | 69.9966
WB-Wide Bay | M001_Tarong-Kingaroy East 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
WB-Wide Bay | M002_Tarong-Kingaroy West 66 kV | % of Rated A | 2.466% | 1.962% | 1.996% | 2.378% | 2.927%
WB-Wide Bay | M002_Tarong-Kingaroy West 66 kV | Limiting Line Name | TR_LINE 7252_2 | TR_LINE 7252_2 | TR_LINE 7252_2 | TR_LINE 7252_2 | TR_LINE 7252_2
WB-Wide Bay | M002_Tarong-Kingaroy West 66 kV | Loading (A) | 13.511 | 10.7493 | 10.9407 | 13.032 | 16.0385
WB-Wide Bay | M002_Tarong-Kingaroy West 66 kV | Loading (MVA) | 1.6373 | 1.3027 | 1.3262 | 1.5799 | 1.9445
WB-Wide Bay | M002_Tarong-Kingaroy West 66 kV | Loading (MW) | 1.0239 | 0.26043 | 0.38291 | 0.95516 | 1.4955
WB-Wide Bay | M002_Tarong-Kingaroy West 66 kV | Power Factor | 0.62537 | 0.19991 | 0.28788 | 0.60346 | 0.7676
WB-Wide Bay | M002_Tarong-Kingaroy West 66 kV | Rating (A) | 548 | 548 | 548 | 548 | 548
WB-Wide Bay | M002_Tarong-Kingaroy West 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M002_Tarong-Kingaroy West 66 kV | Min Voltage at Constrained Conductor | 69.9635 | 69.9713 | 69.986 | 69.9914 | 69.9966
WB-Wide Bay | M002_Tarong-Kingaroy West 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
WB-Wide Bay | M003_Kingaroy- Yarraman 66 kV | % of Rated A | 14.93% | 18.19% | 20.9% | 23.3% | 25.56%
WB-Wide Bay | M003_Kingaroy- Yarraman 66 kV | Limiting Line Name | TR_LINE 7254_1 | TR_LINE 7254_1 | TR_LINE 7254_1 | TR_LINE 7254_1 | TR_LINE 7254_1
WB-Wide Bay | M003_Kingaroy- Yarraman 66 kV | Loading (A) | 19.7139 | 24.0046 | 27.5936 | 30.7569 | 33.7338
WB-Wide Bay | M003_Kingaroy- Yarraman 66 kV | Loading (MVA) | 2.3929 | 2.916 | 3.3546 | 3.7413 | 4.109
WB-Wide Bay | M003_Kingaroy- Yarraman 66 kV | Loading (MW) | 2.3172 | 2.8629 | 3.3167 | 3.7152 | 4.0897
WB-Wide Bay | M003_Kingaroy- Yarraman 66 kV | Power Factor | 0.96531 | 0.97806 | 0.9844 | 0.98822 | 0.99086
WB-Wide Bay | M003_Kingaroy- Yarraman 66 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
WB-Wide Bay | M003_Kingaroy- Yarraman 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M003_Kingaroy- Yarraman 66 kV | Min Voltage at Constrained Conductor | 70.0785 | 70.1347 | 70.1892 | 70.2295 | 70.267
WB-Wide Bay | M003_Kingaroy- Yarraman 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
WB-Wide Bay | M004_Murgon-Kingaroy 66 kV | % of Rated A | 5.171% | 5.374% | 5.504% | 5.626% | 5.744%
WB-Wide Bay | M004_Murgon-Kingaroy 66 kV | Limiting Line Name | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1 | TR_LINE 37212_1
WB-Wide Bay | M004_Murgon-Kingaroy 66 kV | Loading (A) | 8.7385 | 9.0823 | 9.3023 | 9.5083 | 9.7077
WB-Wide Bay | M004_Murgon-Kingaroy 66 kV | Loading (MVA) | 1.0249 | 1.0818 | 1.1071 | 1.1306 | 1.1531
WB-Wide Bay | M004_Murgon-Kingaroy 66 kV | Loading (MW) | 0.35476 | 0.43638 | 0.50265 | 0.55896 | 0.60949
WB-Wide Bay | M004_Murgon-Kingaroy 66 kV | Power Factor | 0.34612 | 0.40338 | 0.454 | 0.49437 | 0.52854
WB-Wide Bay | M004_Murgon-Kingaroy 66 kV | Rating (A) | 169 | 169 | 169 | 169 | 169
WB-Wide Bay | M004_Murgon-Kingaroy 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M004_Murgon-Kingaroy 66 kV | Min Voltage at Constrained Conductor | 67.7172 | 68.7674 | 68.715 | 68.6515 | 68.5812
WB-Wide Bay | M004_Murgon-Kingaroy 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
WB-Wide Bay | M005 KINGAROY-BOONDOOMA | % of Rated A | 10.07% | 9.459% | 8.919% | 8.425% | 7.936%
WB-Wide Bay | M005 KINGAROY-BOONDOOMA | Limiting Line Name | TR_LINE 65620_1 | TR_LINE 65620_1 | TR_LINE 65620_1 | TR_LINE 65620_1 | TR_LINE 65620_1
WB-Wide Bay | M005 KINGAROY-BOONDOOMA | Loading (A) | 13.4988 | 12.6748 | 11.9517 | 11.2897 | 10.6348
WB-Wide Bay | M005 KINGAROY-BOONDOOMA | Loading (MVA) | 1.6376 | 1.539 | 1.4525 | 1.3729 | 1.294
WB-Wide Bay | M005 KINGAROY-BOONDOOMA | Loading (MW) | 1.6376 | 1.539 | 1.4525 | 1.3729 | 1.294
WB-Wide Bay | M005 KINGAROY-BOONDOOMA | Power Factor | 0.99995 | 0.99996 | 0.99996 | 0.99997 | 0.99997
WB-Wide Bay | M005 KINGAROY-BOONDOOMA | Rating (A) | 134 | 134 | 134 | 134 | 134
WB-Wide Bay | M005 KINGAROY-BOONDOOMA | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M005 KINGAROY-BOONDOOMA | Min Voltage at Constrained Conductor | 70.0355 | 70.0971 | 70.1564 | 70.2011 | 70.243
WB-Wide Bay | M005 KINGAROY-BOONDOOMA | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
WB-Wide Bay | M007_Proston 66 kV | % of Rated A | 4.929% | 5.385% | 5.776% | 6.128% | 6.459%
WB-Wide Bay | M007_Proston 66 kV | Limiting Line Name | TR_LINE 7264_1 | TR_LINE 7264_1 | TR_LINE 7264_1 | TR_LINE 7264_1 | TR_LINE 7264_1
WB-Wide Bay | M007_Proston 66 kV | Loading (A) | 4.8792 | 5.3314 | 5.7178 | 6.0668 | 6.3942
WB-Wide Bay | M007_Proston 66 kV | Loading (MVA) | 0.57243 | 0.63519 | 0.68071 | 0.7216 | 0.75977
WB-Wide Bay | M007_Proston 66 kV | Loading (MW) | 0.35504 | 0.43667 | 0.50296 | 0.55927 | 0.60981
WB-Wide Bay | M007_Proston 66 kV | Power Factor | 0.62021 | 0.68744 | 0.73885 | 0.77501 | 0.8026
WB-Wide Bay | M007_Proston 66 kV | Rating (A) | 99 | 99 | 99 | 99 | 99
WB-Wide Bay | M007_Proston 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M007_Proston 66 kV | Min Voltage at Constrained Conductor | 67.7349 | 68.7862 | 68.7343 | 68.6714 | 68.6016
WB-Wide Bay | M007_Proston 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
WB-Wide Bay | M008_Kilkivan-Murgon No 1 66 kV | % of Rated A | 4.85% | 5.15% | 5.745% | 6.415% | 7.119%
WB-Wide Bay | M008_Kilkivan-Murgon No 1 66 kV | Limiting Line Name | TR_LINE 116487_1 | TR_LINE 116487_1 | TR_LINE 7214_1 | TR_LINE 7214_1 | TR_LINE 7214_1
WB-Wide Bay | M008_Kilkivan-Murgon No 1 66 kV | Loading (A) | 8.7777 | 9.322 | 10.3983 | 11.6112 | 12.8863
WB-Wide Bay | M008_Kilkivan-Murgon No 1 66 kV | Loading (MVA) | 1.0264 | 1.1063 | 1.2322 | 1.3741 | 1.5227
WB-Wide Bay | M008_Kilkivan-Murgon No 1 66 kV | Loading (MW) | 0.086597 | 0.3365 | 0.71748 | 0.94534 | 1.1555
WB-Wide Bay | M008_Kilkivan-Murgon No 1 66 kV | Power Factor | 0.083011 | 0.30265 | 0.58216 | 0.68787 | 0.7587
WB-Wide Bay | M008_Kilkivan-Murgon No 1 66 kV | Rating (A) | 181 | 181 | 181 | 181 | 181
WB-Wide Bay | M008_Kilkivan-Murgon No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M008_Kilkivan-Murgon No 1 66 kV | Min Voltage at Constrained Conductor | 67.5116 | 68.5177 | 68.4178 | 68.323 | 68.2239
WB-Wide Bay | M008_Kilkivan-Murgon No 1 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
WB-Wide Bay | M009_Kilkivan-Murgon No 2 66 kV | % of Rated A | 5.333% | 5.661% | 6.061% | 6.535% | 7.054%
WB-Wide Bay | M009_Kilkivan-Murgon No 2 66 kV | Limiting Line Name | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1 | TR_LINE 7193_1
WB-Wide Bay | M009_Kilkivan-Murgon No 2 66 kV | Loading (A) | 9.0132 | 9.5668 | 10.2428 | 11.0442 | 11.9218
WB-Wide Bay | M009_Kilkivan-Murgon No 2 66 kV | Loading (MVA) | 1.0538 | 1.1352 | 1.2138 | 1.307 | 1.4088
WB-Wide Bay | M009_Kilkivan-Murgon No 2 66 kV | Loading (MW) | 0.097756 | 0.3539 | 0.5682 | 0.75663 | 0.93036
WB-Wide Bay | M009_Kilkivan-Murgon No 2 66 kV | Power Factor | 0.091303 | 0.31011 | 0.46618 | 0.57667 | 0.6578
WB-Wide Bay | M009_Kilkivan-Murgon No 2 66 kV | Rating (A) | 169 | 169 | 169 | 169 | 169
WB-Wide Bay | M009_Kilkivan-Murgon No 2 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M009_Kilkivan-Murgon No 2 66 kV | Min Voltage at Constrained Conductor | 67.502 | 68.5062 | 68.4178 | 68.323 | 68.2239
WB-Wide Bay | M009_Kilkivan-Murgon No 2 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
WB-Wide Bay | M010_Maryborough - Owanyilla 66 kV | % of Rated A | 15.26% | 29.21% | 31.72% | 34.22% | 35.6%
WB-Wide Bay | M010_Maryborough - Owanyilla 66 kV | Limiting Line Name | TR_LINE 199623_1 | TR_LINE 199623_1 | TR_LINE 199623_1 | TR_LINE 199623_1 | TR_LINE 199623_1
WB-Wide Bay | M010_Maryborough - Owanyilla 66 kV | Loading (A) | 37.9861 | 72.738 | 78.9948 | 85.2196 | 88.6491
WB-Wide Bay | M010_Maryborough - Owanyilla 66 kV | Loading (MVA) | 4.5014 | 8.5812 | 9.3339 | 10.0715 | 10.4918
WB-Wide Bay | M010_Maryborough - Owanyilla 66 kV | Loading (MW) | 4.3794 | 4.2965 | 5.1851 | 5.9776 | 6.2537
WB-Wide Bay | M010_Maryborough - Owanyilla 66 kV | Power Factor | 0.97285 | 0.50069 | 0.55551 | 0.59352 | 0.59606
WB-Wide Bay | M010_Maryborough - Owanyilla 66 kV | Rating (A) | 249 | 249 | 249 | 249 | 249
WB-Wide Bay | M010_Maryborough - Owanyilla 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M010_Maryborough - Owanyilla 66 kV | Min Voltage at Constrained Conductor | 68.4162 | 68.112 | 68.2189 | 68.2328 | 68.3306
WB-Wide Bay | M010_Maryborough - Owanyilla 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
WB-Wide Bay | M011_Kilkivan-Maryborough 66 kV | % of Rated A | 10.28% | 75.95% | 84.59% | 92.55% | 101.5%
WB-Wide Bay | M011_Kilkivan-Maryborough 66 kV | Limiting Line Name | TR_LINE 33838_1 | TR_LINE 42252_1 | TR_LINE 42252_1 | TR_LINE 42252_1 | TR_LINE 42252_1
WB-Wide Bay | M011_Kilkivan-Maryborough 66 kV | Loading (A) | 13.5716 | 100.2585 | 111.6545 | 122.16 | 134.0361
WB-Wide Bay | M011_Kilkivan-Maryborough 66 kV | Loading (MVA) | 1.6436 | 11.9464 | 13.3047 | 14.5511 | 15.9633
WB-Wide Bay | M011_Kilkivan-Maryborough 66 kV | Loading (MW) | 1.6432 | 9.5265 | 10.8578 | 12.0228 | 13.3785
WB-Wide Bay | M011_Kilkivan-Maryborough 66 kV | Power Factor | 0.99981 | 0.79741 | 0.81605 | 0.8262 | 0.83803
WB-Wide Bay | M011_Kilkivan-Maryborough 66 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
WB-Wide Bay | M011_Kilkivan-Maryborough 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M011_Kilkivan-Maryborough 66 kV | Min Voltage at Constrained Conductor | 69.9189 | 68.7937 | 68.7949 | 68.7692 | 68.7581
WB-Wide Bay | M011_Kilkivan-Maryborough 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
WB-Wide Bay | M012_Maryborough-Rocky St 66 kV | % of Rated A | 10.39% | 9.922% | 9.455% | 9.135% | 9.16%
WB-Wide Bay | M012_Maryborough-Rocky St 66 kV | Limiting Line Name | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1 | TR_LINE 7812_1
WB-Wide Bay | M012_Maryborough-Rocky St 66 kV | Loading (A) | 56.944 | 54.3706 | 51.8118 | 50.0602 | 50.199
WB-Wide Bay | M012_Maryborough-Rocky St 66 kV | Loading (MVA) | 6.7433 | 6.4054 | 6.1136 | 5.9081 | 5.9327
WB-Wide Bay | M012_Maryborough-Rocky St 66 kV | Loading (MW) | 2.9924 | 2.1452 | 1.4917 | 0.31868 | 0.84412
WB-Wide Bay | M012_Maryborough-Rocky St 66 kV | Power Factor | 0.44375 | 0.33491 | 0.24399 | 0.053552 | 0.14138
WB-Wide Bay | M012_Maryborough-Rocky St 66 kV | Rating (A) | 548 | 548 | 548 | 548 | 548
WB-Wide Bay | M012_Maryborough-Rocky St 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M012_Maryborough-Rocky St 66 kV | Min Voltage at Constrained Conductor | 68.3701 | 68.0178 | 68.1252 | 68.1387 | 68.2332
WB-Wide Bay | M012_Maryborough-Rocky St 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
WB-Wide Bay | M014_Torquay-Pialba 66 kV | % of Rated A | 6.338% | 7.117% | 8.028% | 9.031% | 10.56%
WB-Wide Bay | M014_Torquay-Pialba 66 kV | Limiting Line Name | TR_LINE 7168_1 | TR_LINE 7168_1 | TR_LINE 7168_1 | TR_LINE 7168_1 | TR_LINE 7168_1
WB-Wide Bay | M014_Torquay-Pialba 66 kV | Loading (A) | 38.5371 | 43.2694 | 48.8102 | 54.9102 | 64.2142
WB-Wide Bay | M014_Torquay-Pialba 66 kV | Loading (MVA) | 4.6243 | 5.1765 | 5.8586 | 6.6018 | 7.7521
WB-Wide Bay | M014_Torquay-Pialba 66 kV | Loading (MW) | 2.8793 | 3.8918 | 4.8765 | 5.8557 | 6.8717
WB-Wide Bay | M014_Torquay-Pialba 66 kV | Power Factor | 0.62265 | 0.75182 | 0.83236 | 0.88697 | 0.88642
WB-Wide Bay | M014_Torquay-Pialba 66 kV | Rating (A) | 608 | 608 | 608 | 608 | 608
WB-Wide Bay | M014_Torquay-Pialba 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M014_Torquay-Pialba 66 kV | Min Voltage at Constrained Conductor | 69.279 | 69.0703 | 69.2981 | 69.4142 | 69.6993
WB-Wide Bay | M014_Torquay-Pialba 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
WB-Wide Bay | M015_Maryborough-Howard No 1 66 kV | % of Rated A | 1.887% | 1.878% | 1.881% | 1.881% | 1.884%
WB-Wide Bay | M015_Maryborough-Howard No 1 66 kV | Limiting Line Name | TR_LINE 112139_1 | TR_LINE 112139_1 | TR_LINE 112139_1 | TR_LINE 112139_1 | TR_LINE 112139_1
WB-Wide Bay | M015_Maryborough-Howard No 1 66 kV | Loading (A) | 2.4914 | 2.4785 | 2.4824 | 2.4829 | 2.4864
WB-Wide Bay | M015_Maryborough-Howard No 1 66 kV | Loading (MVA) | 0.29503 | 0.292 | 0.29292 | 0.29304 | 0.29385
WB-Wide Bay | M015_Maryborough-Howard No 1 66 kV | Loading (MW) | 5.3368e-05 | 5.282e-05 | 5.2987e-05 | 5.3007e-05 | 5.3155e-05
WB-Wide Bay | M015_Maryborough-Howard No 1 66 kV | Power Factor | 0.00017813 | 0.00017813 | 0.00017813 | 0.00017813 | 0.00017813
WB-Wide Bay | M015_Maryborough-Howard No 1 66 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
WB-Wide Bay | M015_Maryborough-Howard No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M015_Maryborough-Howard No 1 66 kV | Min Voltage at Constrained Conductor | 68.3703 | 68.018 | 68.1255 | 68.1389 | 68.2335
WB-Wide Bay | M015_Maryborough-Howard No 1 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
WB-Wide Bay | M017_Rocky St - Maryborough City 66 kV | % of Rated A | 7.283% | 8.617% | 9.902% | 10.23% | 10.56%
WB-Wide Bay | M017_Rocky St - Maryborough City 66 kV | Limiting Line Name | TR_LINE 7924_1 | TR_LINE 7924_1 | TR_LINE 7924_1 | TR_LINE 7924_1 | TR_LINE 7924_1
WB-Wide Bay | M017_Rocky St - Maryborough City 66 kV | Loading (A) | 39.9123 | 47.2185 | 54.2622 | 56.0407 | 57.8927
WB-Wide Bay | M017_Rocky St - Maryborough City 66 kV | Loading (MVA) | 4.736 | 5.5749 | 6.4169 | 6.6296 | 6.8593
WB-Wide Bay | M017_Rocky St - Maryborough City 66 kV | Loading (MW) | 4.678 | 5.5323 | 6.3749 | 6.5864 | 6.8143
WB-Wide Bay | M017_Rocky St - Maryborough City 66 kV | Power Factor | 0.98776 | 0.99236 | 0.99345 | 0.99347 | 0.99343
WB-Wide Bay | M017_Rocky St - Maryborough City 66 kV | Rating (A) | 548 | 548 | 548 | 548 | 548
WB-Wide Bay | M017_Rocky St - Maryborough City 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M017_Rocky St - Maryborough City 66 kV | Min Voltage at Constrained Conductor | 68.4895 | 68.1398 | 68.246 | 68.2699 | 68.3746
WB-Wide Bay | M017_Rocky St - Maryborough City 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
WB-Wide Bay | M018_Maryborough-Maryborough City 66 kV | % of Rated A | 8.692% | 8.512% | 8.37% | 7.727% | 7.182%
WB-Wide Bay | M018_Maryborough-Maryborough City 66 kV | Limiting Line Name | TR_LINE 122162_1 | TR_LINE 122162_1 | TR_LINE 122162_1 | TR_LINE 122162_1 | TR_LINE 122162_1
WB-Wide Bay | M018_Maryborough-Maryborough City 66 kV | Loading (A) | 47.632 | 46.6435 | 45.8677 | 42.346 | 39.3595
WB-Wide Bay | M018_Maryborough-Maryborough City 66 kV | Loading (MVA) | 5.6406 | 5.4951 | 5.4122 | 4.9977 | 4.6516
WB-Wide Bay | M018_Maryborough-Maryborough City 66 kV | Loading (MW) | 3.796 | 3.6074 | 3.5373 | 2.8792 | 2.2377
WB-Wide Bay | M018_Maryborough-Maryborough City 66 kV | Power Factor | 0.67298 | 0.65648 | 0.65358 | 0.57612 | 0.48105
WB-Wide Bay | M018_Maryborough-Maryborough City 66 kV | Rating (A) | 548 | 548 | 548 | 548 | 548
WB-Wide Bay | M018_Maryborough-Maryborough City 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M018_Maryborough-Maryborough City 66 kV | Min Voltage at Constrained Conductor | 68.3701 | 68.0178 | 68.1252 | 68.1387 | 68.2332
WB-Wide Bay | M018_Maryborough-Maryborough City 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
WB-Wide Bay | M020_Maryborough-Torquay 66 kV | % of Rated A | 15.32% | 21.74% | 27.74% | 33.63% | 39.77%
WB-Wide Bay | M020_Maryborough-Torquay 66 kV | Limiting Line Name | TR_LINE 112154_1 | TR_LINE 112154_1 | TR_LINE 112154_1 | TR_LINE 112154_1 | TR_LINE 112154_1
WB-Wide Bay | M020_Maryborough-Torquay 66 kV | Loading (A) | 93.1245 | 132.1697 | 168.657 | 204.4415 | 241.8302
WB-Wide Bay | M020_Maryborough-Torquay 66 kV | Loading (MVA) | 11.1121 | 15.7065 | 20.0904 | 24.3738 | 28.911
WB-Wide Bay | M020_Maryborough-Torquay 66 kV | Loading (MW) | 10.5269 | 15.3927 | 19.9117 | 24.2806 | 28.8242
WB-Wide Bay | M020_Maryborough-Torquay 66 kV | Power Factor | 0.94734 | 0.98002 | 0.99111 | 0.99618 | 0.997
WB-Wide Bay | M020_Maryborough-Torquay 66 kV | Rating (A) | 608 | 608 | 608 | 608 | 608
WB-Wide Bay | M020_Maryborough-Torquay 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M020_Maryborough-Torquay 66 kV | Min Voltage at Constrained Conductor | 68.892 | 68.6094 | 68.7731 | 68.8315 | 69.0216
WB-Wide Bay | M020_Maryborough-Torquay 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
WB-Wide Bay | M022_Howard - ISIS 66 kV | % of Rated A | 7.759% | 7.237% | 6.699% | 8.951% | 11.24%
WB-Wide Bay | M022_Howard - ISIS 66 kV | Limiting Line Name | TR_LINE 118970_1 | TR_LINE 118970_1 | TR_LINE 118970_1 | TR_LINE 118970_1 | TR_LINE 118970_1
WB-Wide Bay | M022_Howard - ISIS 66 kV | Loading (A) | 42.52 | 39.6566 | 36.7111 | 49.0534 | 61.5855
WB-Wide Bay | M022_Howard - ISIS 66 kV | Loading (MVA) | 5.0305 | 4.7046 | 4.3373 | 5.8005 | 7.2888
WB-Wide Bay | M022_Howard - ISIS 66 kV | Loading (MW) | 5.0237 | 4.699 | 4.3329 | 5.7907 | 7.2707
WB-Wide Bay | M022_Howard - ISIS 66 kV | Power Factor | 0.99866 | 0.9988 | 0.99898 | 0.99831 | 0.99751
WB-Wide Bay | M022_Howard - ISIS 66 kV | Rating (A) | 548 | 548 | 548 | 548 | 548
WB-Wide Bay | M022_Howard - ISIS 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M022_Howard - ISIS 66 kV | Min Voltage at Constrained Conductor | 68.1559 | 68.3521 | 68.0794 | 68.1034 | 68.1322
WB-Wide Bay | M022_Howard - ISIS 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
WB-Wide Bay | M023_6242 (Pialba-Point Vernon) 66 kV | % of Rated A | 11.83% | 14.43% | 16.82% | 19.11% | 21.4%
WB-Wide Bay | M023_6242 (Pialba-Point Vernon) 66 kV | Limiting Line Name | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1 | TR_LINE 57687_1
WB-Wide Bay | M023_6242 (Pialba-Point Vernon) 66 kV | Loading (A) | 71.5777 | 87.3161 | 101.7759 | 115.6012 | 129.4834
WB-Wide Bay | M023_6242 (Pialba-Point Vernon) 66 kV | Loading (MVA) | 8.6066 | 10.4682 | 12.243 | 13.9304 | 15.6734
WB-Wide Bay | M023_6242 (Pialba-Point Vernon) 66 kV | Loading (MW) | 6.9487 | 9.2076 | 11.2019 | 13.0493 | 14.9112
WB-Wide Bay | M023_6242 (Pialba-Point Vernon) 66 kV | Power Factor | 0.80735 | 0.87956 | 0.91496 | 0.93675 | 0.95137
WB-Wide Bay | M023_6242 (Pialba-Point Vernon) 66 kV | Rating (A) | 605 | 605 | 605 | 605 | 605
WB-Wide Bay | M023_6242 (Pialba-Point Vernon) 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M023_6242 (Pialba-Point Vernon) 66 kV | Min Voltage at Constrained Conductor | 69.4211 | 69.2177 | 69.4509 | 69.5715 | 69.8837
WB-Wide Bay | M023_6242 (Pialba-Point Vernon) 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
WB-Wide Bay | M024_Gayndah - Mundubbera 66 kV | % of Rated A | 20.79% | 20.74% | 21.03% | 21.1% | 20.85%
WB-Wide Bay | M024_Gayndah - Mundubbera 66 kV | Limiting Line Name | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1 | TR_LINE 7715_1
WB-Wide Bay | M024_Gayndah - Mundubbera 66 kV | Loading (A) | 27.4375 | 27.3719 | 27.7637 | 27.8543 | 27.5232
WB-Wide Bay | M024_Gayndah - Mundubbera 66 kV | Loading (MVA) | 3.1844 | 3.1586 | 3.2408 | 3.2527 | 3.1654
WB-Wide Bay | M024_Gayndah - Mundubbera 66 kV | Loading (MW) | 0.25333 | 0.35554 | 0.43464 | 0.49962 | 0.54944
WB-Wide Bay | M024_Gayndah - Mundubbera 66 kV | Power Factor | 0.071935 | 0.10491 | 0.12644 | 0.1459 | 0.16584
WB-Wide Bay | M024_Gayndah - Mundubbera 66 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
WB-Wide Bay | M024_Gayndah - Mundubbera 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M024_Gayndah - Mundubbera 66 kV | Min Voltage at Constrained Conductor | 67.0077 | 66.6236 | 67.3937 | 67.4211 | 66.3995
WB-Wide Bay | M024_Gayndah - Mundubbera 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
WB-Wide Bay | M025_Eidsvold 66 kV | % of Rated A | 2.604% | 2.799% | 3.013% | 3.196% | 3.363%
WB-Wide Bay | M025_Eidsvold 66 kV | Limiting Line Name | TR_LINE 77926_1 | TR_LINE 77926_1 | TR_LINE 77926_1 | TR_LINE 77926_1 | TR_LINE 77926_1
WB-Wide Bay | M025_Eidsvold 66 kV | Loading (A) | 2.7862 | 2.9954 | 3.2234 | 3.4193 | 3.5981
WB-Wide Bay | M025_Eidsvold 66 kV | Loading (MVA) | 0.3266 | 0.34924 | 0.38025 | 0.4036 | 0.41837
WB-Wide Bay | M025_Eidsvold 66 kV | Loading (MW) | 0.12178 | 0.18001 | 0.22596 | 0.26359 | 0.29572
WB-Wide Bay | M025_Eidsvold 66 kV | Power Factor | 0.37284 | 0.51541 | 0.59423 | 0.65307 | 0.70683
WB-Wide Bay | M025_Eidsvold 66 kV | Rating (A) | 107 | 107 | 107 | 107 | 107
WB-Wide Bay | M025_Eidsvold 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M025_Eidsvold 66 kV | Min Voltage at Constrained Conductor | 67.678 | 67.3133 | 68.1068 | 68.1485 | 67.1302
WB-Wide Bay | M025_Eidsvold 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
WB-Wide Bay | M026_ISIS - Bundaberg 66 kV | % of Rated A | 11.21% | 13.6% | 15.79% | 17.77% | 19.75%
WB-Wide Bay | M026_ISIS - Bundaberg 66 kV | Limiting Line Name | TR_CABLE 3770_1 | TR_CABLE 3770_1 | TR_CABLE 3770_1 | TR_CABLE 3770_1 | TR_CABLE 3770_1
WB-Wide Bay | M026_ISIS - Bundaberg 66 kV | Loading (A) | 11.2116 | 13.6041 | 15.7908 | 17.766 | 19.7476
WB-Wide Bay | M026_ISIS - Bundaberg 66 kV | Loading (MVA) | 1.3259 | 1.6143 | 1.8673 | 2.1018 | 2.3376
WB-Wide Bay | M026_ISIS - Bundaberg 66 kV | Loading (MW) | 1.3256 | 1.6139 | 1.8666 | 2.1008 | 2.3361
WB-Wide Bay | M026_ISIS - Bundaberg 66 kV | Power Factor | 0.9998 | 0.99971 | 0.9996 | 0.9995 | 0.99938
WB-Wide Bay | M026_ISIS - Bundaberg 66 kV | Rating (A) | 100 | 100 | 100 | 100 | 100
WB-Wide Bay | M026_ISIS - Bundaberg 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M026_ISIS - Bundaberg 66 kV | Min Voltage at Constrained Conductor | 68.2765 | 68.5119 | 68.2747 | 68.3049 | 68.3416
WB-Wide Bay | M026_ISIS - Bundaberg 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
WB-Wide Bay | M026b_FORMER_ISIS - Bundaberg 66kV | % of Rated A | 0.2428% | 0.2433% | 0.2406% | 0.2406% | 0.2407%
WB-Wide Bay | M026b_FORMER_ISIS - Bundaberg 66kV | Limiting Line Name | TR_LINE 12084300_1 | TR_LINE 12084300_1 | TR_LINE 12084300_1 | TR_LINE 12084300_1 | TR_LINE 12084300_1
WB-Wide Bay | M026b_FORMER_ISIS - Bundaberg 66kV | Loading (A) | 1.0657 | 1.0682 | 1.0562 | 1.0563 | 1.0565
WB-Wide Bay | M026b_FORMER_ISIS - Bundaberg 66kV | Loading (MVA) | 0.12259 | 0.12317 | 0.12042 | 0.12044 | 0.12048
WB-Wide Bay | M026b_FORMER_ISIS - Bundaberg 66kV | Loading (MW) | 1.9235e-06 | 1.9325e-06 | 1.8895e-06 | 1.8897e-06 | 1.8904e-06
WB-Wide Bay | M026b_FORMER_ISIS - Bundaberg 66kV | Power Factor | 1.569e-05 | 1.569e-05 | 1.569e-05 | 1.569e-05 | 1.569e-05
WB-Wide Bay | M026b_FORMER_ISIS - Bundaberg 66kV | Rating (A) | 439 | 439 | 439 | 439 | 439
WB-Wide Bay | M026b_FORMER_ISIS - Bundaberg 66kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M026b_FORMER_ISIS - Bundaberg 66kV | Min Voltage at Constrained Conductor | 66.4163 | 66.5713 | 65.8264 | 65.8301 | 65.8413
WB-Wide Bay | M026b_FORMER_ISIS - Bundaberg 66kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
WB-Wide Bay | M027_ISIS - Childers 66 kV | % of Rated A | 20.46% | 10.2% | 10.66% | 11.41% | 12.36%
WB-Wide Bay | M027_ISIS - Childers 66 kV | Limiting Line Name | TR_LINE 183684_1 | TR_LINE 183684_1 | TR_LINE 183684_1 | TR_LINE 183684_1 | TR_LINE 183684_1
WB-Wide Bay | M027_ISIS - Childers 66 kV | Loading (A) | 52.794 | 26.3274 | 27.5078 | 29.4343 | 31.8995
WB-Wide Bay | M027_ISIS - Childers 66 kV | Loading (MVA) | 6.2347 | 3.1172 | 3.2447 | 3.4726 | 3.7646
WB-Wide Bay | M027_ISIS - Childers 66 kV | Loading (MW) | 2.5635 | 0.51123 | 1.125 | 1.6895 | 2.2439
WB-Wide Bay | M027_ISIS - Childers 66 kV | Power Factor | 0.41116 | 0.16317 | 0.34584 | 0.48557 | 0.59504
WB-Wide Bay | M027_ISIS - Childers 66 kV | Rating (A) | 258 | 258 | 258 | 258 | 258
WB-Wide Bay | M027_ISIS - Childers 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M027_ISIS - Childers 66 kV | Min Voltage at Constrained Conductor | 68.1823 | 68.3588 | 68.1021 | 68.1152 | 68.135
WB-Wide Bay | M027_ISIS - Childers 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
WB-Wide Bay | M028_Childers - Gayndah 66 kV | % of Rated A | 22.65% | 1.121e-08% | 1.172e-08% | 1.235e-08% | 1.305e-08%
WB-Wide Bay | M028_Childers - Gayndah 66 kV | Limiting Line Name | TR_LINE 12103276_2 | 3-Phase Link 66kV_M028 GAYNDAH_Term(1) | 3-Phase Link 66kV_M028 GAYNDAH_Term(1) | 3-Phase Link 66kV_M028 GAYNDAH_Term(1) | 3-Phase Link 66kV_M028 GAYNDAH_Term(1)
WB-Wide Bay | M028_Childers - Gayndah 66 kV | Loading (A) | 29.8968 | 5.6072e-07 | 5.8619e-07 | 6.1734e-07 | 6.5265e-07
WB-Wide Bay | M028_Childers - Gayndah 66 kV | Loading (MVA) | 3.5342 | 6.647e-08 | 6.9242e-08 | 7.295e-08 | 7.7161e-08
WB-Wide Bay | M028_Childers - Gayndah 66 kV | Loading (MW) | 2.3633 | 2.2659e-08 | 3.0899e-08 | 3.8584e-08 | 4.6143e-08
WB-Wide Bay | M028_Childers - Gayndah 66 kV | Power Factor | 0.6687 | 0.3409 | 0.44625 | 0.52891 | 0.59801
WB-Wide Bay | M028_Childers - Gayndah 66 kV | Rating (A) | 132 | 5000 | 5000 | 5000 | 5000
WB-Wide Bay | M028_Childers - Gayndah 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M028_Childers - Gayndah 66 kV | Min Voltage at Constrained Conductor | 68.2354 | 68.4408 | 68.1987 | 68.2252 | 68.258
WB-Wide Bay | M028_Childers - Gayndah 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
WB-Wide Bay | M029_Bundaberg - Farnsfield 66 kV | % of Rated A | 0.7653% | 0.7698% | 0.7643% | 0.7672% | 0.7701%
WB-Wide Bay | M029_Bundaberg - Farnsfield 66 kV | Limiting Line Name | TR_LINE 205843_1 | TR_LINE 205843_1 | TR_LINE 205843_1 | TR_LINE 205843_1 | TR_LINE 205843_1
WB-Wide Bay | M029_Bundaberg - Farnsfield 66 kV | Loading (A) | 3.9186 | 3.9414 | 3.9133 | 3.9283 | 3.9429
WB-Wide Bay | M029_Bundaberg - Farnsfield 66 kV | Loading (MVA) | 0.45078 | 0.45446 | 0.44617 | 0.44791 | 0.44966
WB-Wide Bay | M029_Bundaberg - Farnsfield 66 kV | Loading (MW) | 0.035063 | 0.051772 | 0.064822 | 0.075651 | 0.08468
WB-Wide Bay | M029_Bundaberg - Farnsfield 66 kV | Power Factor | 0.077613 | 0.11375 | 0.14511 | 0.16872 | 0.18815
WB-Wide Bay | M029_Bundaberg - Farnsfield 66 kV | Rating (A) | 512 | 512 | 512 | 512 | 512
WB-Wide Bay | M029_Bundaberg - Farnsfield 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M029_Bundaberg - Farnsfield 66 kV | Min Voltage at Constrained Conductor | 66.4163 | 66.5713 | 65.8264 | 65.8301 | 65.8413
WB-Wide Bay | M029_Bundaberg - Farnsfield 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
WB-Wide Bay | M030_Farnsfield - Childers 66 kV | % of Rated A | 17.57% | 17.46% | 17.3% | 17.27% | 17.27%
WB-Wide Bay | M030_Farnsfield - Childers 66 kV | Limiting Line Name | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1 | TR_LINE 96132_1
WB-Wide Bay | M030_Farnsfield - Childers 66 kV | Loading (A) | 23.1938 | 23.0455 | 22.8422 | 22.7901 | 22.7939
WB-Wide Bay | M030_Farnsfield - Childers 66 kV | Loading (MVA) | 2.7475 | 2.7377 | 2.7041 | 2.6991 | 2.701
WB-Wide Bay | M030_Farnsfield - Childers 66 kV | Loading (MW) | 0.53501 | 0.37558 | 0.23279 | 0.099561 | 0.034156
WB-Wide Bay | M030_Farnsfield - Childers 66 kV | Power Factor | 0.19472 | 0.13719 | 0.086088 | 0.036549 | 0.011832
WB-Wide Bay | M030_Farnsfield - Childers 66 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
WB-Wide Bay | M030_Farnsfield - Childers 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M030_Farnsfield - Childers 66 kV | Min Voltage at Constrained Conductor | 68.3926 | 68.5874 | 68.348 | 68.3777 | 68.4137
WB-Wide Bay | M030_Farnsfield - Childers 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
WB-Wide Bay | M032_Bundaberg-South Kolan No 1 66 kV | % of Rated A | 22.23% | 23.49% | 25.06% | 26.12% | 27.61%
WB-Wide Bay | M032_Bundaberg-South Kolan No 1 66 kV | Limiting Line Name | TR_LINE 138990_1 | TR_LINE 138990_1 | TR_LINE 138990_1 | TR_LINE 138990_1 | TR_LINE 138990_1
WB-Wide Bay | M032_Bundaberg-South Kolan No 1 66 kV | Loading (A) | 29.3491 | 31.0127 | 33.0835 | 34.4778 | 36.4481
WB-Wide Bay | M032_Bundaberg-South Kolan No 1 66 kV | Loading (MVA) | 3.3866 | 3.5876 | 3.7852 | 3.9453 | 4.172
WB-Wide Bay | M032_Bundaberg-South Kolan No 1 66 kV | Loading (MW) | 0.98616 | 1.5044 | 1.9437 | 2.3362 | 2.7072
WB-Wide Bay | M032_Bundaberg-South Kolan No 1 66 kV | Power Factor | 0.29119 | 0.41932 | 0.51351 | 0.59216 | 0.64889
WB-Wide Bay | M032_Bundaberg-South Kolan No 1 66 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
WB-Wide Bay | M032_Bundaberg-South Kolan No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M032_Bundaberg-South Kolan No 1 66 kV | Min Voltage at Constrained Conductor | 66.6205 | 66.7885 | 66.0561 | 66.0659 | 66.0858
WB-Wide Bay | M032_Bundaberg-South Kolan No 1 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
WB-Wide Bay | M033_Wallaville 66 kV | % of Rated A | 10.43% | 10.7% | 11.14% | 11.33% | 11.77%
WB-Wide Bay | M033_Wallaville 66 kV | Limiting Line Name | TR_LINE 214482_2 | TR_LINE 214482_2 | TR_LINE 214482_2 | TR_LINE 214482_2 | TR_LINE 214482_2
WB-Wide Bay | M033_Wallaville 66 kV | Loading (A) | 26.9098 | 27.6072 | 28.7451 | 29.2236 | 30.3607
WB-Wide Bay | M033_Wallaville 66 kV | Loading (MVA) | 3.1207 | 3.2117 | 3.3096 | 3.3666 | 3.5002
WB-Wide Bay | M033_Wallaville 66 kV | Loading (MW) | 0.34681 | 0.75627 | 1.1041 | 1.4151 | 1.7099
WB-Wide Bay | M033_Wallaville 66 kV | Power Factor | 0.11108 | 0.23543 | 0.33354 | 0.42028 | 0.48845
WB-Wide Bay | M033_Wallaville 66 kV | Rating (A) | 258 | 258 | 258 | 258 | 258
WB-Wide Bay | M033_Wallaville 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M033_Wallaville 66 kV | Min Voltage at Constrained Conductor | 66.9537 | 67.1653 | 66.4736 | 66.5108 | 66.5614
WB-Wide Bay | M033_Wallaville 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
WB-Wide Bay | M034_Monduran Dam 66 kV | % of Rated A | 1.642% | 1.644% | 1.631% | 1.639% | 1.652%
WB-Wide Bay | M034_Monduran Dam 66 kV | Limiting Line Name | TR_LINE 209283_1 | TR_LINE 209283_1 | TR_LINE 209283_1 | TR_LINE 209283_1 | TR_LINE 209283_1
WB-Wide Bay | M034_Monduran Dam 66 kV | Loading (A) | 2.168 | 2.1706 | 2.1525 | 2.1639 | 2.1812
WB-Wide Bay | M034_Monduran Dam 66 kV | Loading (MVA) | 0.25219 | 0.25339 | 0.24879 | 0.25031 | 0.25257
WB-Wide Bay | M034_Monduran Dam 66 kV | Loading (MW) | 0.017377 | 0.00065402 | 0.013978 | 0.027594 | 0.040621
WB-Wide Bay | M034_Monduran Dam 66 kV | Power Factor | 0.068905 | 0.002581 | 0.056056 | 0.11011 | 0.16069
WB-Wide Bay | M034_Monduran Dam 66 kV | Rating (A) | 132 | 132 | 132 | 132 | 132
WB-Wide Bay | M034_Monduran Dam 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M034_Monduran Dam 66 kV | Min Voltage at Constrained Conductor | 67.1605 | 67.3987 | 66.7317 | 66.7848 | 66.8541
WB-Wide Bay | M034_Monduran Dam 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
WB-Wide Bay | M035_Bundaberg-South Kolan No 2 66 kV | % of Rated A | 3.33% | 3.731% | 4.144% | 4.471% | 4.822%
WB-Wide Bay | M035_Bundaberg-South Kolan No 2 66 kV | Limiting Line Name | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1 | TR_LINE 7435_1
WB-Wide Bay | M035_Bundaberg-South Kolan No 2 66 kV | Loading (A) | 18.2462 | 20.4452 | 22.7088 | 24.5025 | 26.4261
WB-Wide Bay | M035_Bundaberg-South Kolan No 2 66 kV | Loading (MVA) | 2.1018 | 2.3608 | 2.5931 | 2.7982 | 3.0185
WB-Wide Bay | M035_Bundaberg-South Kolan No 2 66 kV | Loading (MW) | 1.3174 | 1.7018 | 2.0249 | 2.3107 | 2.58
WB-Wide Bay | M035_Bundaberg-South Kolan No 2 66 kV | Power Factor | 0.62622 | 0.72023 | 0.78017 | 0.82501 | 0.85387
WB-Wide Bay | M035_Bundaberg-South Kolan No 2 66 kV | Rating (A) | 548 | 548 | 548 | 548 | 548
WB-Wide Bay | M035_Bundaberg-South Kolan No 2 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M035_Bundaberg-South Kolan No 2 66 kV | Min Voltage at Constrained Conductor | 66.506 | 66.6666 | 65.9271 | 65.9334 | 65.9484
WB-Wide Bay | M035_Bundaberg-South Kolan No 2 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
WB-Wide Bay | M036_Bundaberg-South Bundaberg 66 kV | % of Rated A | 19.11% | 21.8% | 24.56% | 27.37% | 30.31%
WB-Wide Bay | M036_Bundaberg-South Bundaberg 66 kV | Limiting Line Name | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1 | TR_LINE 8031_1
WB-Wide Bay | M036_Bundaberg-South Bundaberg 66 kV | Loading (A) | 83.8736 | 95.6955 | 107.8371 | 120.1497 | 133.0736
WB-Wide Bay | M036_Bundaberg-South Bundaberg 66 kV | Loading (MVA) | 9.6485 | 11.0745 | 12.3855 | 13.8362 | 15.3603
WB-Wide Bay | M036_Bundaberg-South Bundaberg 66 kV | Loading (MW) | 6.1928 | 8.3978 | 10.3208 | 12.1326 | 13.9428
WB-Wide Bay | M036_Bundaberg-South Bundaberg 66 kV | Power Factor | 0.63537 | 0.75369 | 0.83099 | 0.8762 | 0.90772
WB-Wide Bay | M036_Bundaberg-South Bundaberg 66 kV | Rating (A) | 439 | 439 | 439 | 439 | 439
WB-Wide Bay | M036_Bundaberg-South Bundaberg 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M036_Bundaberg-South Bundaberg 66 kV | Min Voltage at Constrained Conductor | 66.4163 | 66.5713 | 65.8264 | 65.8301 | 65.8413
WB-Wide Bay | M036_Bundaberg-South Bundaberg 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
WB-Wide Bay | M037_South - East Bundaberg 66 kV | % of Rated A | 14.54% | 15.59% | 16.79% | 17.86% | 18.97%
WB-Wide Bay | M037_South - East Bundaberg 66 kV | Limiting Line Name | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1 | TR_LINE 73770_1
WB-Wide Bay | M037_South - East Bundaberg 66 kV | Loading (A) | 32.871 | 35.2391 | 37.9531 | 40.3555 | 42.8791
WB-Wide Bay | M037_South - East Bundaberg 66 kV | Loading (MVA) | 3.8286 | 4.1188 | 4.3912 | 4.6738 | 4.9714
WB-Wide Bay | M037_South - East Bundaberg 66 kV | Loading (MW) | 3.3099 | 3.6855 | 4.0383 | 4.3661 | 4.7001
WB-Wide Bay | M037_South - East Bundaberg 66 kV | Power Factor | 0.8645 | 0.89481 | 0.91963 | 0.93418 | 0.94543
WB-Wide Bay | M037_South - East Bundaberg 66 kV | Rating (A) | 226 | 226 | 226 | 226 | 226
WB-Wide Bay | M037_South - East Bundaberg 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M037_South - East Bundaberg 66 kV | Min Voltage at Constrained Conductor | 67.24 | 67.4662 | 66.7763 | 66.8355 | 66.9012
WB-Wide Bay | M037_South - East Bundaberg 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
WB-Wide Bay | M039_Bundaberg-West Bundaberg No 1 66 kV | % of Rated A | 11.25% | 12.03% | 12.95% | 14.18% | 15.63%
WB-Wide Bay | M039_Bundaberg-West Bundaberg No 1 66 kV | Limiting Line Name | TR_LINE 200241_1 | TR_LINE 200241_1 | TR_LINE 200241_1 | TR_LINE 200241_1 | TR_LINE 200241_1
WB-Wide Bay | M039_Bundaberg-West Bundaberg No 1 66 kV | Loading (A) | 90.6501 | 96.9231 | 104.4064 | 114.2871 | 125.9644
WB-Wide Bay | M039_Bundaberg-West Bundaberg No 1 66 kV | Loading (MVA) | 10.4281 | 11.1757 | 11.9039 | 13.0315 | 14.3657
WB-Wide Bay | M039_Bundaberg-West Bundaberg No 1 66 kV | Loading (MW) | 2.1759 | 4.4501 | 6.4884 | 8.4142 | 10.3809
WB-Wide Bay | M039_Bundaberg-West Bundaberg No 1 66 kV | Power Factor | 0.20864 | 0.39817 | 0.54504 | 0.64567 | 0.72261
WB-Wide Bay | M039_Bundaberg-West Bundaberg No 1 66 kV | Rating (A) | 806 | 806 | 806 | 806 | 806
WB-Wide Bay | M039_Bundaberg-West Bundaberg No 1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M039_Bundaberg-West Bundaberg No 1 66 kV | Min Voltage at Constrained Conductor | 66.4163 | 66.5713 | 65.8264 | 65.8301 | 65.8413
WB-Wide Bay | M039_Bundaberg-West Bundaberg No 1 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
WB-Wide Bay | M040_Bundaberg-West Bundaberg No 2 66 kV | % of Rated A | 10.83% | 11.58% | 12.48% | 13.66% | 15.05%
WB-Wide Bay | M040_Bundaberg-West Bundaberg No 2 66 kV | Limiting Line Name | TR_LINE 169764_1 | TR_LINE 169764_1 | TR_LINE 169764_1 | TR_LINE 169764_1 | TR_LINE 169764_1
WB-Wide Bay | M040_Bundaberg-West Bundaberg No 2 66 kV | Loading (A) | 87.3116 | 93.3494 | 100.5514 | 110.0622 | 121.3029
WB-Wide Bay | M040_Bundaberg-West Bundaberg No 2 66 kV | Loading (MVA) | 10.044 | 10.7636 | 11.4643 | 12.5549 | 13.8475
WB-Wide Bay | M040_Bundaberg-West Bundaberg No 2 66 kV | Loading (MW) | 2.1022 | 4.2926 | 6.2562 | 8.1119 | 10.0075
WB-Wide Bay | M040_Bundaberg-West Bundaberg No 2 66 kV | Power Factor | 0.20868 | 0.39816 | 0.545 | 0.64562 | 0.72257
WB-Wide Bay | M040_Bundaberg-West Bundaberg No 2 66 kV | Rating (A) | 806 | 806 | 806 | 806 | 806
WB-Wide Bay | M040_Bundaberg-West Bundaberg No 2 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M040_Bundaberg-West Bundaberg No 2 66 kV | Min Voltage at Constrained Conductor | 66.4163 | 66.5713 | 65.8264 | 65.8301 | 65.8413
WB-Wide Bay | M040_Bundaberg-West Bundaberg No 2 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
WB-Wide Bay | M041_West Bundaberg-Meadowvale 66 kV | % of Rated A | 14.88% | 17.68% | 20.65% | 23.36% | 26.1%
WB-Wide Bay | M041_West Bundaberg-Meadowvale 66 kV | Limiting Line Name | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1 | TR_LINE 180726_1
WB-Wide Bay | M041_West Bundaberg-Meadowvale 66 kV | Loading (A) | 33.6193 | 39.9524 | 46.6718 | 52.8009 | 58.9771
WB-Wide Bay | M041_West Bundaberg-Meadowvale 66 kV | Loading (MVA) | 3.8899 | 4.6385 | 5.3632 | 6.0735 | 6.792
WB-Wide Bay | M041_West Bundaberg-Meadowvale 66 kV | Loading (MW) | 2.9762 | 3.8722 | 4.6874 | 5.4634 | 6.255
WB-Wide Bay | M041_West Bundaberg-Meadowvale 66 kV | Power Factor | 0.76512 | 0.83479 | 0.87399 | 0.89955 | 0.92093
WB-Wide Bay | M041_West Bundaberg-Meadowvale 66 kV | Rating (A) | 226 | 226 | 226 | 226 | 226
WB-Wide Bay | M041_West Bundaberg-Meadowvale 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M041_West Bundaberg-Meadowvale 66 kV | Min Voltage at Constrained Conductor | 66.8021 | 67.0307 | 66.3376 | 66.3952 | 66.466
WB-Wide Bay | M041_West Bundaberg-Meadowvale 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
WB-Wide Bay | M042_Meadowvale-Gooburrum 66 kV | % of Rated A | 5.521% | 7.179% | 8.705% | 10% | 11.24%
WB-Wide Bay | M042_Meadowvale-Gooburrum 66 kV | Limiting Line Name | TR_LINE 7779_2 | TR_LINE 7779_2 | TR_LINE 7779_2 | TR_LINE 7779_2 | TR_LINE 7779_2
WB-Wide Bay | M042_Meadowvale-Gooburrum 66 kV | Loading (A) | 6.1289 | 7.9685 | 9.6627 | 11.1034 | 12.4785
WB-Wide Bay | M042_Meadowvale-Gooburrum 66 kV | Loading (MVA) | 0.70915 | 0.92517 | 1.1104 | 1.2772 | 1.4371
WB-Wide Bay | M042_Meadowvale-Gooburrum 66 kV | Loading (MW) | 0.69674 | 0.91622 | 1.1039 | 1.2722 | 1.4332
WB-Wide Bay | M042_Meadowvale-Gooburrum 66 kV | Power Factor | 0.98213 | 0.98984 | 0.99359 | 0.99539 | 0.99655
WB-Wide Bay | M042_Meadowvale-Gooburrum 66 kV | Rating (A) | 111 | 111 | 111 | 111 | 111
WB-Wide Bay | M042_Meadowvale-Gooburrum 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M042_Meadowvale-Gooburrum 66 kV | Min Voltage at Constrained Conductor | 66.8034 | 67.0325 | 66.3475 | 66.4127 | 66.4921
WB-Wide Bay | M042_Meadowvale-Gooburrum 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
WB-Wide Bay | M046_Tarong-Caboonbah 66 kV | % of Rated A | 4.525% | 4.525% | 4.525% | 4.525% | 4.525%
WB-Wide Bay | M046_Tarong-Caboonbah 66 kV | Limiting Line Name | TR_LINE 9243_1 | TR_LINE 9243_1 | TR_LINE 9243_1 | TR_LINE 9243_1 | TR_LINE 9243_1
WB-Wide Bay | M046_Tarong-Caboonbah 66 kV | Loading (A) | 11.2683 | 11.2678 | 11.2669 | 11.2665 | 11.2662
WB-Wide Bay | M046_Tarong-Caboonbah 66 kV | Loading (MVA) | 1.3664 | 1.3665 | 1.3667 | 1.3667 | 1.3668
WB-Wide Bay | M046_Tarong-Caboonbah 66 kV | Loading (MW) | 1.151 | 1.151 | 1.151 | 1.151 | 1.151
WB-Wide Bay | M046_Tarong-Caboonbah 66 kV | Power Factor | 0.84235 | 0.84229 | 0.84218 | 0.84214 | 0.8421
WB-Wide Bay | M046_Tarong-Caboonbah 66 kV | Rating (A) | 249 | 249 | 249 | 249 | 249
WB-Wide Bay | M046_Tarong-Caboonbah 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M046_Tarong-Caboonbah 66 kV | Min Voltage at Constrained Conductor | 70.0099 | 70.0178 | 70.0325 | 70.038 | 70.0431
WB-Wide Bay | M046_Tarong-Caboonbah 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
WB-Wide Bay | M049_ISIS - Gayndah 66 kV | % of Rated A | 17.68% | 15.06% | 15.21% | 15.04% | 14.86%
WB-Wide Bay | M049_ISIS - Gayndah 66 kV | Limiting Line Name | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2 | TR_LINE 12103475_2
WB-Wide Bay | M049_ISIS - Gayndah 66 kV | Loading (A) | 70.5245 | 60.0707 | 60.7031 | 60.0114 | 59.275
WB-Wide Bay | M049_ISIS - Gayndah 66 kV | Loading (MVA) | 8.3122 | 7.1017 | 7.1483 | 7.0672 | 6.9815
WB-Wide Bay | M049_ISIS - Gayndah 66 kV | Loading (MW) | 7.865 | 6.4952 | 6.5379 | 6.4481 | 6.3749
WB-Wide Bay | M049_ISIS - Gayndah 66 kV | Power Factor | 0.9462 | 0.91459 | 0.91461 | 0.91239 | 0.91311
WB-Wide Bay | M049_ISIS - Gayndah 66 kV | Rating (A) | 399 | 399 | 399 | 399 | 399
WB-Wide Bay | M049_ISIS - Gayndah 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M049_ISIS - Gayndah 66 kV | Min Voltage at Constrained Conductor | 67.5557 | 67.9811 | 67.712 | 67.7273 | 67.736
WB-Wide Bay | M049_ISIS - Gayndah 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
WB-Wide Bay | M051_Tarong Tie 66 kV | % of Rated A | 8.814% | 10.52% | 11.96% | 13.25% | 14.47%
WB-Wide Bay | M051_Tarong Tie 66 kV | Limiting Line Name | TR_LINE 37804_1 | TR_LINE 37804_1 | TR_LINE 37804_1 | TR_LINE 37804_1 | TR_LINE 37804_1
WB-Wide Bay | M051_Tarong Tie 66 kV | Loading (A) | 9.4314 | 11.2567 | 12.8003 | 14.1731 | 15.4786
WB-Wide Bay | M051_Tarong Tie 66 kV | Loading (MVA) | 1.1519 | 1.3775 | 1.5691 | 1.7398 | 1.9025
WB-Wide Bay | M051_Tarong Tie 66 kV | Loading (MW) | 1.1017 | 1.3387 | 1.5378 | 1.7142 | 1.8816
WB-Wide Bay | M051_Tarong Tie 66 kV | Power Factor | 0.95489 | 0.96995 | 0.97789 | 0.98284 | 0.98635
WB-Wide Bay | M051_Tarong Tie 66 kV | Rating (A) | 107 | 107 | 107 | 107 | 107
WB-Wide Bay | M051_Tarong Tie 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | M051_Tarong Tie 66 kV | Min Voltage at Constrained Conductor | 70.5113 | 70.65 | 70.7725 | 70.8721 | 70.965
WB-Wide Bay | M051_Tarong Tie 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
WB-Wide Bay | SOBU-BARG-1_SOBU-Bargara-1 66 kV | % of Rated A | 13.28% | 16.6% | 19.77% | 22.61% | 25.45%
WB-Wide Bay | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Limiting Line Name | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1 | TR_LINE 47619_1
WB-Wide Bay | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Loading (A) | 54.4277 | 68.0416 | 81.0762 | 92.6843 | 104.3647
WB-Wide Bay | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Loading (MVA) | 6.3468 | 7.9643 | 9.397 | 10.7554 | 12.1266
WB-Wide Bay | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Loading (MW) | 6.3453 | 7.9614 | 9.392 | 10.7481 | 12.116
WB-Wide Bay | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Power Factor | 0.99977 | 0.99964 | 0.99947 | 0.99931 | 0.99913
WB-Wide Bay | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Rating (A) | 410 | 410 | 410 | 410 | 410
WB-Wide Bay | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Min Voltage at Constrained Conductor | 67.3165 | 67.5694 | 66.9053 | 66.9852 | 67.0707
WB-Wide Bay | SOBU-BARG-1_SOBU-Bargara-1 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC
WB-Wide Bay | T014_Maryborough-Pialba Tee Howard 66 kV | % of Rated A | 12.19% | 17.06% | 21.66% | 26.19% | 30.95%
WB-Wide Bay | T014_Maryborough-Pialba Tee Howard 66 kV | Limiting Line Name | TR_LINE 224569_1 | TR_LINE 224569_1 | TR_LINE 224569_1 | TR_LINE 224569_1 | TR_LINE 224569_1
WB-Wide Bay | T014_Maryborough-Pialba Tee Howard 66 kV | Loading (A) | 73.7597 | 103.2249 | 131.0281 | 158.4207 | 187.2568
WB-Wide Bay | T014_Maryborough-Pialba Tee Howard 66 kV | Loading (MVA) | 8.8464 | 12.3433 | 15.7195 | 19.0358 | 22.5928
WB-Wide Bay | T014_Maryborough-Pialba Tee Howard 66 kV | Loading (MW) | 7.9765 | 11.7497 | 15.2689 | 18.687 | 22.2058
WB-Wide Bay | T014_Maryborough-Pialba Tee Howard 66 kV | Power Factor | 0.90125 | 0.95177 | 0.97134 | 0.98168 | 0.98287
WB-Wide Bay | T014_Maryborough-Pialba Tee Howard 66 kV | Rating (A) | 605 | 605 | 605 | 605 | 605
WB-Wide Bay | T014_Maryborough-Pialba Tee Howard 66 kV | Time | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00 | 12:00:00
WB-Wide Bay | T014_Maryborough-Pialba Tee Howard 66 kV | Min Voltage at Constrained Conductor | 69.2444 | 69.0049 | 69.2058 | 69.2965 | 69.5619
WB-Wide Bay | T014_Maryborough-Pialba Tee Howard 66 kV | Contingency Outage | _NNC | _NNC | _NNC | _NNC | _NNC