## Coversheet
Generation Application Checklist - Under 5MVA following NER process 5A - Class A2
This document is to be used by the Proponent and Ergon to determine whether a generation connection has included all of the required information, and to allow tracking of comments and issues.
Proponents are to make note of:
Modelling Information for Non-Registered Generators
The Power System Model Guidelines
AEMO Dynamic Model Acceptance Guideline
AEMO PSCAD v5 Factsheet
STNW1175
QECM
STNW3522
Please note this list is a general list and may not reflect all requirements in some cases. Please discuss specific questions with your project sponsor prior to application.
Release:
2025-05-27
Ver 2.6

## Application review checklist
Item | Description | Customer Check | NSP Comment | Reference | Status
Documentation completeness checklist
Class A2
1 | Ergon Energy Technical Assessment
2 | Completed Application Form
3 | Payment - does the customer wish to have an invoice issued during the completeness review?
4 | Customer's preference for Contestable Works, DCT Works
5 | Site Location and Layout drawings - Customer switchroom location - DNSP room location and size - Cable / Conductor path from property boundary to switchroom - Access easements and roadways, plant delivery route - Requirements specified in the Technical Assessment
6 | Single line diagrams of the proposed: • Connection arrangement and generating system clearly showing the connection point including primary electrical SLD for all collector circuits (if relevant), switching arrangements for each generating unit, including demonstration of break-before-make units or bumpless make-before-break switch arrangements, if applicable.
• Revenue meter location
• Protection systems including CTs, VTs, isolation points and grid protection relay(s) and settings, noting requirements to utilise an approved relay under STNW1175
• SCADA and communications SLD as required
7 | EG unit information as relevant (see the relevant tab in this document)
8 | Datasheets as relevant
9 | Evidence of standards compliance (e.g., AS/NZS4777.2, AS/NZS IEC 62116, AS/NZS IEC 60947.6.1 as relevant)
10 | A PSCAD model provided by the inverter or generator manufacturer with site-specific detail such as number of inverters (as applicable) and the proposed control system settings (including any gains, limits, ramp rates etc). The model must be PSCAD V5, compiled with Intel OneAPI Fortran Compiler: Classic 2021.x (32-bit & 64-bit). Models shall be delivered in a format that allows for maintenance for life of asset. (e.g. .dll, support files). Refer to https://www.ergon.com.au/__data/assets/pdf_file/0008/1097630/Modelling-Information-for-Non-Registered-Generators.pdf for more information
10a | For rotating machines, where a PSCAD model is not required, detailed control system block diagrams of the relevant control systems. E.g. including excitation system, OEL/UEL, AVR, governor and any site controller if applicable. Example exciter block diagram provided on "Detailed Block Diagram Example" tab.
11 | A report detailing all control system settings to be applied to the inverter or generator control system on site and justification for those settings. This should include all settings referred to in item 10 or 10a.
12 | For the active and reactive power control systems a diagram showing the location of the relevant measurement locations. E.g. Voltage droop control is the normal reactive power control strategy so the location of the voltage measurement and the reactive power measurement should be identified.
13 | A report detailing the Voltage Control Strategy of the site should be provided. This should include details of the following items where relevant; reactive power control strategy, active power control strategy, transformer tap changer control strategy, switched shunt control strategy.
14 | Draft Non Registered Generator Performance Standard, using the Ergon Energy template
15 | Communication failure control documentation, following the principles of: https://aemo.com.au/-/media/files/electricity/nem/network_connections/stage-6/communication-system-failure-guidelines.pdf?la=en
16 | If interlocking is present, evidence that the interlocking is fail-safe, in accordance with 4.17 of STNW3522
Report Requirement
Large solar-farm and battery scale inverters have a number of settings, which have a significant impact on the performance of the generating system. Likewise rotating machine generators also have a control system which governs the generator's response and performance. As such, these settings must be carefully considered with proper analysis and verification. A report validating these setting decisions must be developed, demonstrating compliance with the required access standards detailed in the technical assessment.
Non-export Systems must match their generation to the load on site. If the load changes or drops, the generation may need to ramp down to ensure the site does not export. However, this must be done in a controlled or ramped manner that ensures compliance with flicker limits and does not cause other negative voltage effects. The report should contain details of the control system used to achieve this.

## Rotating machines
Rotating machines
| Data Description | Units
1 | Type of generator | Text
2 | Connection arrangement | Text
3 | Rotor type | Text
4 | Nominal rated output | kVA, kW, kVAr
5 | Nominal terminal voltage (line to neutral) | V or kV
6 | Highest voltage (line to neutral) | V or kV
7 | Rated lightning impulse withstand voltage | kVp
8 | Rated short duration power frequency withstand voltage | kV
9 | Maximum current | kA
10 | Rated short time withstand current | kA for seconds
11 | Ambient conditions for maximum current and withstand current | Text
12 | Synchronous reactance - D Axis (Xd) | PU
13 | Synchronous reactance - Q axis (Xq) | PU
14 | Transient reactance - D Axis (X'd) | PU
15 | Transient reactance - Q Axis (X'q) | PU
16 | Subtransient reactance - D Axis (X''d) | PU
17 | Subtransient reactance - Q Axis (X''q) | PU
18 | Open circuit transient time constant - D Axis | Seconds
19 | Open circuit transient time constant - Q Axis | Seconds
20 | Open circuit subtransient time constant - D Axis | Seconds
21 | Open circuit subtransient time constant - Q Axis | Seconds
22 | Armature resistance | PU
23 | Negative sequence resistance | PU
24 | Locked Rotor impedance (resistance and reactance) | PU
25 | Zero Sequence reactance | PU
26 | Grounding impedance (resistance and reactance) | Ohms
27 | Saturation co-efficient at 1.0PU and 1.2PU | -
28 | Mechanical inertia constant | Seconds
29 | Fault contribution from the EG unit(s) at the Distribution System boundary | kA
30 | Description of the proposed voltage, active power (P) and Reactive power (Q) control system including details of the operation and performance of the system under normal conditions, fault conditions, and distribution system disturbance conditions | Text

## Detailed Block Diagram Example
The below diagram indicates the typical functions present in a synchronous machine excitation control system.
Where applicable a detailed control block diagram should be provided for each of these functions.
Reference IEEE Std 421.5-2016, Figure 1
The below diagram indicates the control system block diagram for a standard IEEE AC8C exciter. This is an example of what a detailed control block diagram should look like.
Reference IEEE Std 421.5-2016

## Inverter Energy Systems
Inverter energy systems
| Data Description | Units
1 | Inverter model and associated data sheets | Text
2 | Inverter islanding protection details | Text
3 | Inverter reactive control capabilities | Text
4 | Panel capacity | W / kW
5 | Inverter capacity | kVA
6 | Information on inverter configuration - single or three-phase systems, number of inverters, electrical schematic if embedded in sub-boards | Text and diagrams
7 | Battery details, planned operating modes and dispatch schedule as applicable | Text and diagrams